## CH 10 WQ Data
Poughkeepsie Combined Filter Effluent UVT Data | [6 empty] | Flow and UVA Data for a large drining water treatment plant |  |  | Scott's valley Water Reclamation Plant, California |  |  | California WWTP |  |  | California WWTP
in the eastern USA
| UVA 254 (cm-1) at time: | [5 empty] | Date | Flow | UVT | Date | Flow | UVT | Date | Flow | UVT | Date | UVT
DATE | 4:00 | 8:00 | 12:00 | 16:00 | 20:00 | 0:00 |  | mgd | % |  | gpm | % |  | mgd | % |  | %
2000-07-07 | 0.044 | 0.043 | 0.037 | 0.027 | 0.019 | 0.043 | 2000-01-01 | 50.252 | 91.4113 | 2002-08-01 |  | 63 | 2003-02-25 15:30 | 8.5 | 59 | 2003-11-06 07:45 | 71.3
2000-07-08 | 0.03 | 0.045 | 0.037 | 0.03 | 0.041 | 0.022 | 2000-01-02 | 42.758 | 91.4113 | 2002-08-02 |  | 62 | 2003-02-26 06:43 | 7.6 | 57 | 2003-11-06 14:45 | 71.2
2000-07-09 | 0.041 | 0.045 | 0.035 | 0.036 | 0.036 | 0.031 | 2000-01-03 | 41.044 | 91.4113 | 2002-08-03 |  | 65 | 2003-02-26 15:15 | 8.6 | 58 | 2003-11-06 20:11 | 71.1
2000-07-10 | 0.043 | 0.041 | 0.034 | 0.031 | 0.035 | 0.036 | 2000-01-04 | 42.984 | 91.4113 | 2002-08-04 |  | 63 | 2003-02-27 06:33 | 8.1 | 49 | 2003-11-07 07:45 | 71.7
2000-07-11 | 0.036 | 0.049 | 0.037 | 0.029 | 0.029 | 0.032 | 2000-01-05 | 40.449 | 91.4113 | 2002-08-05 |  | 60 | 2003-02-27 13:00 | 7.4 | 47 | 2003-11-07 21:01 | 70.7
2000-07-12 | 0.034 | 0.034 | 0.028 | 0.034 | 0.032 | 0.034 | 2000-01-06 | 42.367 | 91.4113 | 2002-08-06 |  | 63 | 2003-02-27 15:35 | 6.9 | 41 | 2003-11-08 07:36 | 71.8
2000-07-13 | 0.037 | 0.028 | 0.033 | 0.03 | 0.034 | 0.048 | 2000-01-07 | 42.623 | 91.4113 | 2002-08-07 |  | 61 | 2003-02-28 06:30 | 6.4 | 52 | 2003-11-08 14:10 | 71.9
2000-07-14 | 0.042 | N/A | OFF | 0.029 | 0.038 | 0.035 | 2000-01-08 | 41.169 | 91.4113 | 2002-08-08 |  | 61 | 2003-03-01 06:22 | 6.5 | 55 | 2003-11-08 21:10 | 69.4
2000-07-15 | 0.047 | 0.046 | 0.039 | 0.041 | 0.048 | NA | 2000-01-09 | 43.633 | 91.4113 | 2002-08-09 |  | 63 | 2003-03-01 11:30 | 8.8 | 52 | 2003-11-09 07:59 | 72.5
2000-07-16 | 0.039 | 0.037 | 0.034 | 0.032 | 0.035 | 0.038 | 2000-01-10 | 43.208 | 91.4113 | 2002-08-10 |  | 66 | 2003-03-01 16:00 | 8.7 | 56 | 2003-11-09 13:20 | 72.2
2000-07-17 | 0.039 | 0.039 | 0.031 | 0.037 | 0.038 | 0.032 | 2000-01-11 | 37.032 | 88.5931 | 2002-08-11 |  | 65 | 2003-03-02 06:50 | 7.3 | 66 | 2003-11-09 21:03 | 69.4
2000-07-18 | 0.032 | 0.035 | 0.031 | 0.027 | 0.033 | 0.032 | 2000-01-12 | 48.464 | 88.5931 | 2002-08-12 |  | 65 | 2003-03-02 12:28 | 8.3 | 66 | 2003-11-10 07:30 | 73.7
2000-07-19 | 0.043 | 0.041 | 0.039 | 0.034 | 0.037 | 0.048 | 2000-01-13 | 48.505 | 88.5931 | 2002-08-13 |  | 63 | 2003-03-02 | 8.6 | 62 | 2003-11-10 13:30 | 72.5
2000-07-20 | 0.031 | 0.043 | 0.033 | 0.028 | 0.036 | 0.041 | 2000-01-14 | 44.541 | 88.5931 | 2002-08-14 |  | 62 | 2003-03-03 06:50 | 7.6 | 65 | 2003-11-10 20:50 | 69.4
2000-07-21 | 0.032 | 0.039 | 0.048 | 0.042 | 0.038 | 0.043 | 2000-01-15 | 47.698 | 88.5931 | 2002-08-15 |  | 62 | 2003-03-03 12:15 | 8.9 | 63 | 2003-11-11 07:27 | 72.3
2000-07-22 | 0.048 | 0.048 | 0.032 | 0.031 | 0.042 | 0.038 | 2000-01-16 | 48.72 | 88.5931 | 2002-08-16 |  | 63 | 2003-03-04 06:50 | 7.4 | 62 | 2003-11-11 13:25 | 73
2000-07-23 | 0.033 | 0.042 | 0.033 | 0.039 | 0.035 | 0.041 | 2000-01-17 | 44.179 | 88.5931 | 2002-08-17 |  | 64 | 2003-03-04 16:06 | 7.1 | 63 | 2003-11-11 21:01 | 70.3
2000-07-24 | 0.042 | 0.046 | 0.04 | 0.036 | 0.036 | 0.034 | 2000-01-18 | 50.853 | 90.6358 | 2002-08-18 |  | 63 | 2003-03-05 07:00 | 7 | 65 | 2003-11-12 07:15 | 75.4
2000-07-25 | 0.039 | 0.038 | 0.033 | 0.033 | 0.034 | 0.037 | 2000-01-19 | 52.371 | 90.6358 | 2002-08-19 |  | 62 | 2003-03-05 15:45 | 6.4 | 47 | 2003-11-12 14:00 | 72.4
2000-07-26 | 0.043 | 0.046 | N/A | 0.033 | 0.029 | 0.054 | 2000-01-20 | 50.916 | 90.6358 | 2002-08-20 |  | 64 | 2003-03-06 06:43 | 6.7 | 66 | 2003-11-12 21:10 | 71.4
2000-07-27 | 0.041 | 0.039 | 0.034 | 0.035 | 0.038 | 0.038 | 2000-01-21 | 50.317 | 90.6358 | 2002-08-21 |  |  | 2003-03-06 12:18 | 7.8 | 68 | 2003-11-13 07:14 | 72
2000-07-28 | 0.04 | 0.04 | 0.047 | 0.029 | 0.031 | 0.038 | 2000-01-22 | 50.499 | 90.6358 | 2002-08-22 |  |  | 2003-03-06 15:37 | 7.2 | 67 | 2003-11-13 13:33 | 71.9
2000-07-29 | 0.035 | 0.04 | 0.042 | 0.032 | 0.029 | 0.035 | 2000-01-23 | 52.199 | 90.6358 | 2002-08-23 |  |  | 2003-03-07 06:45 | 6.7 | 65 | 2003-11-13 20:47 | 68.3
2000-07-30 | 0.036 | 0.039 | 0.027 | 0.021 | 0.042 | 0.042 | 2000-01-24 | 52.338 | 90.6358 | 2002-08-24 |  |  | 2003-03-07 12:27 | 8.2 | 66 | 2003-11-14 07:30 | 70.1
2000-07-31 | 0.038 | 0.043 | 0.054 | 0.031 | 0.038 | 0.039 | 2000-01-25 | 57.939 | 89.7222 | 2002-08-25 |  |  | 2003-03-07 15:45 | 7 | 68 | 2003-11-14 13:00 | 71.4
2000-08-01 | 0.041 | 0.043 | 0.042 | 0.041 | 0.039 | 0.047 | 2000-01-26 | 58.043 | 89.7222 | 2002-08-26 |  | 63 | 2003-03-08 06:39 | 3.4 | 65 | 2003-11-14 21:12 | 72.1
2000-08-02 | 0.046 | 0.047 | 0.042 | 0.038 | 0.035 | 0.044 | 2000-01-27 | 52.89 | 89.7222 | 2002-08-27 |  | 62 | 2003-03-08 12:32 | 8.8 | 66 | 2003-11-15 07:19 | 73.5
2000-08-03 | 0.034 | 0.038 | 0.027 | 0.044 | 0.048 | 0.042 | 2000-01-28 | 50.52 | 89.7222 | 2002-08-28 |  | 64 | 2003-03-08 15:30 | 8.9 | 67 | 2003-11-15 13:50 | 71.8
2000-08-04 | 0.041 | 0.047 | 0.047 | 0.031 | 0.05 | 0.044 | 2000-01-29 | 58.402 | 89.7222 | 2002-08-29 |  | 62 | 2003-03-09 07:15 | 7.3 | 66 | 2003-11-15 21:00 | 69.8
2000-08-05 | 0.037 | 0.042 | 0.039 | 0.032 | 0.037 | 0.04 | 2000-01-30 | 55.208 | 89.7222 | 2002-08-30 |  | 60 | 2003-03-09 16:00 | 8.6 | 70 | 2003-11-16 08:00 | 74.1
2000-08-06 | 0.049 | 0.038 | 0.04 | 0.037 | 0.043 | 0.042 | 2000-01-31 | 56.862 | 89.7222 | 2002-08-31 |  | 62 | 2003-03-10 06:45 | 7.5 | 66 | 2003-11-16 13:20 | 75.1
2000-08-07 | 0.043 | 0.045 | 0.05 | 0.042 | 0.042 | 0.047 | 2000-02-01 | 58.327 | 91.7487 | 2002-09-01 |  | 63 | 2003-03-10 15:50 | 7.8 | 67 | 2003-11-16 21:00 | 72.3
2000-08-08 | 0.043 | 0.041 | 0.04 | 0.038 | 0.041 | 0.046 | 2000-02-02 | 55.172 | 91.7487 | 2002-09-02 |  | 67 | 2003-03-11 06:45 | 7.1 | 64 | 2003-11-17 07:18 | 73.4
2000-08-09 | 0.048 | 0.046 | 0.054 | 0.048 | 0.045 | 0.078 | 2000-02-03 | 57.398 | 91.7487 | 2002-09-03 |  | 65 | 2003-03-11 12:40 | 8.5 | 65 | 2003-11-17 14:15 | 71.9
2000-08-10 | 0.051 | 0.046 | 0.048 | 0.053 | 0.056 | 0.051 | 2000-02-04 | 47.799 | 91.7487 | 2002-09-04 |  | 64 | 2003-03-11 15:44 | 7.3 | 61 | 2003-11-17 21:03 | 73.1
2000-08-11 | 0.045 | 0.053 | 0.04 | 0.032 | 0.056 | 0.03 | 2000-02-05 | 60.896 | 91.7487 | 2002-09-05 |  | 62 | 2003-03-12 06:34 | 7.3 | 65 | 2003-11-18 07:20 | 73.2
2000-08-12 | 0.045 | 0.047 | 0.027 | 0.027 | 0.029 | 0.043 | 2000-02-06 | 59.862 | 91.7487 | 2002-09-06 |  | 64 | 2003-03-12 11:30 | 8.1 | 64 | 2003-11-18 14:00 | 71.9
2000-08-13 | 0.047 | 0.044 | 0.045 | 0.041 | 0.043 | 0.047 | 2000-02-07 | 57.999 | 91.7487 | 2002-09-07 |  | 65 | 2003-03-13 06:38 | 6 | 63 | 2003-11-18 21:30 | 69.6
2000-08-14 | 0.047 | 0.046 | 0.047 | 0.049 | 0.045 | 0.05 | 2000-02-08 | 58.723 | 92.9394 | 2002-09-08 |  | 65 | 2003-03-13 12:18 | 8.3 | 65 | 2003-11-19 07:40 | 72
2000-08-15 | 0.051 | 0.051 | 0.05 | 0.031 | 0.036 | 0.041 | 2000-02-09 | 60.102 | 92.9394 | 2002-09-09 |  | 65 | 2003-03-14 06:58 | 6.3 | 64 | 2003-11-19 13:15 | 71.2
2000-08-16 | 0.05 | 0.053 | 0.045 | 0.036 | 0.036 | 0.039 | 2000-02-10 | 57.115 | 92.9394 | 2002-09-10 |  | 64 | 2003-03-14 12:58 | 7.1 | 66 | 2003-11-19 21:00 | 71.4
2000-08-17 | 0.04 | 0.042 | 0.044 | 0.035 | 0.049 | 0.041 | 2000-02-11 | 59.608 | 92.9394 | 2002-09-11 |  | 63 | 2003-03-15 06:38 | 6.5 | 65 | 2003-11-20 07:20 | 73.3
2000-08-18 | 0.047 | 0.045 | 0.047 | 0.044 | 0.046 | 0.052 | 2000-02-12 | 57.631 | 92.9394 | 2002-09-12 |  | 64 | 2003-03-15 12:30 | 8 | 66 | 2003-11-20 13:50 | 70.8
2000-08-19 | 0.052 | 0.053 | 0.05 | 0.039 | 0.044 | 0.05 | 2000-02-13 | 59.432 | 92.9394 | 2002-09-13 |  | 63 | 2003-03-16 06:36 | 7.1 | 64 | 2003-11-20 21:00 | 71.9
2000-08-20 | 0.049 | 0.051 | 0.054 | 0.048 | 0.049 | 0.047 | 2000-02-14 | 48.396 | 92.9394 | 2002-09-14 |  | 63 | 2003-03-16 12:28 | 7.4 | 66 | 2003-11-21 07:35 | 73.4
2000-08-21 | 0.054 | 0.056 | 0.049 | 0.046 | 0.034 | 0.042 | 2000-02-15 | 57.017 | 90.469 | 2002-09-15 |  | 65 | 2003-03-16 15:52 | 7 | 69 | 2003-11-21 13:30 | 72.8
2000-08-22 | 0.046 | 0.05 | 0.052 | 0.064 | 0.049 | 0.049 | 2000-02-16 | 59.557 | 90.469 | 2002-09-16 |  | 63 | 2003-03-17 06:38 | 6.4 | 66 | 2003-11-21 21:10 | 72.5
2000-08-23 | 0.055 | 0.058 | 0.057 | 0.053 | 0.069 | 0.06 | 2000-02-17 | 58.77 | 90.469 | 2002-09-17 |  | 61 | 2003-03-17 12:37 | 7 | 71 | 2003-11-22 06:36 | 73.6
2000-08-24 | 0.061 | 0.056 | 0.058 | 0.049 | 0.056 | 0.06 | 2000-02-18 | 56.558 | 90.469 | 2002-09-18 |  | 64 | 2003-03-18 07:02 | 6.7 | 66 | 2003-11-22 13:30 | 73.3
2000-08-25 | 0.073 | 0.056 | 0.049 | 0.042 | 0.045 | 0.047 | 2000-02-19 | 56.801 | 90.469 | 2002-09-19 |  | 61 | 2003-03-18 11:57 | 7.3 | 65 | 2003-11-22 21:10 | 71.7
2000-08-26 | 0.046 | 0.048 | 0.048 | 0.047 | 0.046 | 0.048 | 2000-02-20 | 57.813 | 90.469 | 2002-09-20 |  | 61 | 2003-03-18 15:30 | 6.8 | 64 | 2003-11-23 07:57 | 72.9
2000-08-27 | 0.051 | 0.053 | 0.053 | 0.046 | 0.044 | 0.054 | 2000-02-21 | 49.605 | 90.469 | 2002-09-21 |  | 61 | 2003-03-19 06:56 | 6.3 | 64 | 2003-11-23 13:30 | 73.5
2000-08-28 | 0.053 | 0.056 | 0.058 | 0.047 | 0.051 | 0.052 | 2000-02-22 | 57.108 | 88.8587 | 2002-09-22 |  | 61 | 2003-03-19 12:20 | 7.2 | 65 | 2003-11-23 21:00 | 70.6
2000-08-29 | 0.054 | 0.057 | 0.05 | 0.042 | 0.059 | 0.042 | 2000-02-23 | 53.605 | 88.8587 | 2002-09-23 |  | 63 | 2003-03-19 15:39 | 6.8 | 65 | 2003-11-24 07:50 | 74.2
2000-08-30 | 0.057 | 0.055 | 0.053 | 0.051 | 0.066 | 0.055 | 2000-02-24 | 58.588 | 88.8587 | 2002-09-24 |  | 57 | 2003-03-20 06:43 | 6.1 | 65 | 2003-11-24 14:00 | 74
2000-08-31 | 0.053 | 0.063 | 0.047 | 0.043 | 0.062 | 0.068 | 2000-02-25 | 58.512 | 88.8587 | 2002-09-25 |  | 57 | 2003-03-20 12:56 | 7.3 | 66 | 2003-11-24 20:50 | 72.7
2000-09-01 | 0.047 | 0.031 | 0.037 | 0.056 | 0.084 | 0.048 | 2000-02-26 | 56.896 | 88.8587 | 2002-09-26 |  | 60 | 2003-03-21 06:41 | 6.3 | 64 | 2003-11-25 07:40 | 73.2
2000-09-02 | 0.066 | 0.064 | 0.058 | 0.051 | 0.048 | 0.05 | 2000-02-27 | 61.608 | 88.8587 | 2002-09-27 |  | 56 | 2003-03-21 12:07 | 8.1 | 66 | 2003-11-25 13:30 | 72.8
2000-09-03 | 0.056 | 0.057 | 0.053 | 0.042 | 0.041 | 0.046 | 2000-02-28 | 52.217 | 88.8587 | 2002-09-28 |  | 59 | 2003-03-21 15:36 | 7.2 | 66 | 2003-11-25 21:00 | 69
2000-09-04 | 0.047 | 0.049 | 0.05 | 0.043 | 0.044 | 0.04 | 2000-02-29 | 61.347 | 88.8587 | 2002-09-29 |  | 62 | 2003-03-22 06:50 | 6.3 | 63 | 2003-11-26 07:45 | 71.6
2000-09-05 | 0.049 | 0.051 | 0.057 | 0.034 | 0.039 | 0.041 | 2000-03-01 | 59.209 | 88.8587 | 2002-09-30 |  | 56 | 2003-03-22 12:30 | 8.3 | 65 | 2003-11-26 13:30 | 72.8
2000-09-06 | 0.046 | 0.048 | 0.044 | 0.043 | 0.047 | 0.048 | 2000-03-02 | 59.796 | 88.8587 |  |  |  | 2003-03-22 | 7.4 | 65 | 2003-11-26 21:00 | 70.3
2000-09-07 | 0.05 | 0.057 | 0.044 | 0.036 | 0.037 | 0.037 | 2000-03-03 | 57.634 | 88.8587 | 2003-04-01 |  | 63 | 2003-03-23 07:05 | 6.7 | 63 | 2003-11-27 07:16 | 72.8
2000-09-08 | 0.035 | 0.037 | 0.048 | 0.032 | 0.044 | 0.046 | 2000-03-04 | 55.366 | 88.8587 | 2003-04-02 |  | 57 | 2003-03-23 16:17 | 7.3 | 66 | 2003-11-27 13:30 | 74.5
2000-09-09 | 0.045 | 0.051 | 0.043 | 0.045 | 0.046 | 0.048 | 2000-03-05 | 59.72 | 88.8587 | 2003-04-03 |  | 62 | 2003-03-24 06:50 | 6 | 65 | 2003-11-27 21:00 | 69.9
2000-09-10 | 0.047 | 0.051 | 0.044 | 0.037 | 0.035 | 0.042 | 2000-03-06 | 50.62 | 88.8587 | 2003-04-04 |  | 62 | 2003-03-24 12:15 | 9.5 | 63 | 2003-11-28 13:30 | 73.7
2000-09-11 | 0.048 | 0.047 | 0.031 | 0.043 | 0.053 | 0.043 | 2000-03-07 | 51.982 | 91.3692 | 2003-04-05 |  | 56 | 2003-03-25 06:45 | 7.7 | 62 | 2003-11-28 21:00 | 71.5
2000-09-12 | 0.045 | 0.05 | 0.048 | 0.065 | 0.042 | 0.043 | 2000-03-08 | 56.204 | 91.3692 | 2003-04-06 |  | 60 | 2003-03-25 11:15 | 8.2 | 64 | 2003-11-29 07:47 | 74.3
2000-09-13 | 0.044 | 0.047 | 0.051 | 0.046 | 0.044 | 0.045 | 2000-03-09 | 57.879 | 91.3692 | 2003-04-07 |  | 57 | 2003-03-26 06:40 | 7.2 | 62 | 2003-11-29 13:30 | 70.3
2000-09-14 | 0.044 | 0.046 | 0.038 | 0.031 | 0.031 | 0.032 | 2000-03-10 | 58.74 | 91.3692 | 2003-04-08 |  | 56 | 2003-03-26 12:36 | 7.4 | 63 | 2003-11-29 21:05 | 70.9
2000-09-15 | 0.037 | 0.037 | 0.046 | 0.036 | 0.037 | 0.033 | 2000-03-11 | 59.048 | 91.3692 | 2003-04-09 |  | 61 | 2003-03-26 15:50 | 6.8 | 64 | 2003-11-30 07:37 | 73.8
2000-09-16 | 0.038 | 0.04 | 0.039 | 0.031 | 0.03 | 0.03 | 2000-03-12 | 59.055 | 91.3692 | 2003-04-10 |  | 64 | 2003-03-27 06:43 | 6.4 | 63 | 2003-11-30 13:25 | 75.2
2000-09-17 | 0.038 | 0.04 | 0.04 | 0.031 | 0.03 | 0.036 | 2000-03-13 | 52.32 | 91.3692 | 2003-04-11 |  | 65 | 2003-03-27 13:38 | 7.5 | 63 | 2003-11-30 21:00 | 71
2000-09-18 | 0.042 | 0.044 | 0.038 | 0.028 | 0.028 | 0.034 | 2000-03-14 | 59.509 | 91.8967 | 2003-04-12 |  | 69 | 2003-03-27 15:24 | 6.6 | 63 | 2003-12-01 07:40 | 73.2
2000-09-19 | 0.038 | 0.042 | 0.036 | 0.025 | 0.032 | 0.036 | 2000-03-15 | 56.926 | 91.8967 | 2003-04-13 |  | 71 | 2003-03-28 06:49 | 6.6 | 63 | 2003-12-01 13:30 | 71.3
2000-09-20 | 0.04 | 0.042 | 0.04 | 0.027 | 0.028 | 0.036 | 2000-03-16 | 58.375 | 91.8967 | 2003-04-14 |  | 66 | 2003-03-28 12:48 | 7.5 | 66 | 2003-12-01 21:00 | 67.7
2000-09-21 | 0.038 | 0.042 | 0.042 | 0.03 | 0.029 | 0.032 | 2000-03-17 | 58.909 | 91.8967 | 2003-04-15 |  | 62 | 2003-03-28 15:56 | 6.2 | 63 | 2003-12-02 07:30 | 69.9
2000-09-22 | 0.038 | 0.04 | 0.04 | 0.05 | 0.047 | 0.045 | 2000-03-18 | 57.878 | 91.8967 | 2003-04-16 |  | 67 | 2003-03-29 06:47 | 6.7 | 64 | 2003-12-02 13:30 | 71.8
2000-09-23 | 0.053 | 0.052 | 0.046 | 0.041 | 0.042 | 0.043 | 2000-03-19 | 59.979 | 91.8967 | 2003-04-17 |  | 66 | 2003-03-29 12:48 | 8.6 | 64 | 2003-12-02 21:00 | 72.3
2000-09-24 | 0.044 | 0.047 | 0.028 | 0.03 | 0.03 | 0.048 | 2000-03-20 | 53.998 | 91.8967 | 2003-04-18 |  |  | 2003-03-29 | 7.9 | 64 | 2003-12-03 07:23 | 70.7
2000-09-25 | 0.049 | 0.048 | 0.043 | 0.045 | 0.03 | 0.043 | 2000-03-21 | 59.2 | 89.6603 | 2003-04-19 |  | 64 | 2003-03-30 07:20 | 7.2 | 65 | 2003-12-03 13:30 | 71.6
2000-09-26 | 0.048 | 0.047 | 0.039 | 0.033 | 0.036 | 0.045 | 2000-03-22 | 66.145 | 89.6603 | 2003-04-20 |  | 66 | 2003-03-30 11:50 | 7.2 | 66 | 2003-12-03 21:00 | 72.3
2000-09-27 | 0.053 | 0.055 | 0.049 | 0.038 | 0.036 | 0.055 | 2000-03-23 | 64.498 | 89.6603 | 2003-04-21 |  | 63 | 2003-03-31 06:50 | 6.9 | 64 | 2003-12-04 07:27 | 72.2
2000-09-28 | 0.061 | 0.05 | 0.053 | 0.058 | 0.048 | 0.06 | 2000-03-24 | 64.852 | 89.6603 | 2003-04-22 |  | 65 | 2003-03-31 11:30 | 8.5 | 67 | 2003-12-04 13:30 | 71.7
2000-09-29 | 0.052 | 0.06 | 0.055 | 0.043 | 0.036 | 0.045 | 2000-03-25 | 64.709 | 89.6603 | 2003-04-23 |  | 65 |  |  |  | 2003-12-04 21:00 | 69.1
2000-09-30 | 0.053 | 0.054 | 0.047 | 0.044 | 0.035 | 0.041 | 2000-03-26 | 63.608 | 89.6603 | 2003-04-24 |  | 66 |  |  |  | 2003-12-05 07:20 | 71.2
2000-10-01 | 0.046 | 0.043 | 0.051 | 0.034 | 0.033 | 0.05 | 2000-03-27 | 56.788 | 89.6603 | 2003-04-25 |  | 66 |  |  |  | 2003-12-05 13:30 | 71.4
2000-10-02 | 0.053 | 0.055 | 0.058 | 0.052 | 0.017 | 0.046 | 2000-03-28 | 61.752 | 88.5319 | 2003-04-26 |  | 61 |  |  |  | 2003-12-05 21:00 | 75.3
2000-10-03 | 0.05 | 0.053 | 0.076 | 0.05 | 0.042 | 0.046 | 2000-03-29 | 63.828 | 88.5319 | 2003-04-27 |  | 65 |  |  |  | 2003-12-06 06:48 | 70.9
2000-10-04 | 0.049 | 0.051 | 0.051 | 0.041 | 0.041 | 0.045 | 2000-03-30 | 62.71 | 88.5319 | 2003-04-28 |  | 67 |  |  |  | 2003-12-06 13:30 | 73
2000-10-05 | 0.051 | 0.052 | 0.05 | 0.046 | 0.052 | 0.046 | 2000-03-31 | 63.013 | 88.5319 | 2003-04-29 |  | 67 |  |  |  | 2003-12-06 21:00 | 69.1
2000-10-06 | 0.051 | 0.052 | 0.053 | 0.047 | 0.045 | 0.048 | 2000-04-01 | 61.201 | 88.5319 | 2003-04-30 |  | 63 |  |  |  | 2003-12-07 07:05 | 71.3
2000-10-07 | 0.048 | 0.051 | 0.045 | 0.034 | 0.04 | 0.049 | 2000-04-02 | 61.201 | 88.5319 | 2003-05-01 |  | 65 |  |  |  | 2003-12-07 13:30 | 71.3
2000-10-08 | 0.051 | 0.052 | 0.045 | 0.041 | 0.039 | 0.043 | 2000-04-03 | 52.448 | 88.5319 | 2003-05-02 |  | 67 |  |  |  | 2003-12-07 21:00 | 70.9
2000-10-09 | 0.052 | 0.053 | 0.024 | 0.046 | 0.044 | 0.049 | 2000-04-04 | 52.498 | 89.9912 | 2003-05-03 |  | 66 |  |  |  | 2003-12-08 07:20 | 71.4
2000-10-10 | 0.053 | 0.051 | 0.039 | 0.032 | 0.034 | 0.051 | 2000-04-05 | 61.582 | 89.9912 | 2003-05-04 |  | 67 |  |  |  | 2003-12-08 13:30 | 73
2000-10-11 | 0.051 | 0.05 | 0.035 | 0.036 | 0.047 | 0.045 | 2000-04-06 | 57.905 | 89.9912 | 2003-05-05 |  | 66 |  |  |  | 2003-12-08 13:30 | 74.4
2000-10-12 | 0.049 | 0.053 | 0.05 | 0.048 | 0.053 | 0.055 | 2000-04-07 | 59.86 | 89.9912 | 2003-05-06 | 350 | 60 |  |  |  | 2003-12-08 21:00 | 72
2000-10-13 | 0.055 | 0.052 | 0.053 | 0.045 | 0.046 | 0.051 | 2000-04-08 | 62.064 | 89.9912 | 2003-05-07 | 350 | 64 |  |  |  | 2003-12-09 07:18 | 73.4
2000-10-14 | 0.053 | 0.054 | 0.046 | 0.038 | 0.036 | 0.045 | 2000-04-09 | 61.412 | 89.9912 | 2003-05-08 | 340 | 64 |  |  |  | 2003-12-09 21:00 | 72
2000-10-15 | 0.05 | 0.05 | 0.055 | 0.046 | 0.045 | 0.047 | 2000-04-10 | 59.679 | 89.9912 | 2003-05-09 | 340 | 65 |  |  |  | 2003-12-10 07:32 | 73.5
2000-10-16 | 0.051 | 0.052 | 0.056 | 0.054 | 0.048 | 0.054 | 2000-04-11 | 54.211 | 91.5588 | 2003-05-10 |  | 63 |  |  |  | 2003-12-10 13:30 | 70.8
2000-10-17 | 0.055 | 0.055 | 0.056 | 0.05 | 0.044 | 0.06 | 2000-04-12 | 56.865 | 91.5588 | 2003-05-11 |  | 66 |  |  |  | 2003-12-10 21:00 | 67.9
2000-10-18 | 0.059 | 0.052 | 0.052 | 0.048 | 0.047 | 0.048 | 2000-04-13 | 61.514 | 91.5588 | 2003-05-12 |  | 64 |  |  |  | 2003-12-11 07:19 | 74.6
2000-10-19 | 0.052 | 0.052 | 0.04 | 0.038 | 0.04 | 0.039 | 2000-04-14 | 54.654 | 91.5588 | 2003-05-13 |  | 67 |  |  |  | 2003-12-11 13:30 | 71.9
2000-10-20 | 0.041 | 0.046 | 0.061 | 0.042 | 0.044 | 0.046 | 2000-04-15 | 62.034 | 91.5588 | 2003-05-14 |  | 68 |  |  |  | 2003-12-11 21:00 | 71.4
2000-10-21 | 0.047 | 0.049 | 0.049 | 0.04 | 0.039 | 0.036 | 2000-04-16 | 61.687 | 91.5588 | 2003-05-15 |  | 66 |  |  |  | 2003-12-12 07:32 | 72.9
2000-10-22 | 0.046 | 0.049 | 0.055 | 0.052 | 0.041 | 0.045 | 2000-04-17 | 55.126 | 91.5588 | 2003-05-16 |  | 63 |  |  |  | 2003-12-12 13:30 | 73
2000-10-23 | 0.05 | 0.053 | 0.04 | 0.04 | 0.036 | 0.042 | 2000-04-18 | 62.969 | 90.2818 | 2003-05-17 | 345 | 64 |  |  |  | 2003-12-12 21:10 | 70.9
2000-10-24 | 0.044 | 0.046 | 0.052 | 0.042 | 0.037 | 0.045 | 2000-04-19 | 60.611 | 90.2818 | 2003-05-18 |  | 66 |  |  |  | 2003-12-13 07:06 | 72.2
2000-10-25 | 0.049 | 0.052 | 0.031 | 0.028 | 0.028 | 0.05 | 2000-04-20 | 62.763 | 90.2818 | 2003-05-19 |  | 66 |  |  |  | 2003-12-13 13:30 | 71.9
2000-10-26 | 0.059 | 0.056 | 0.047 | 0.043 | 0.032 | 0.032 | 2000-04-21 | 59.999 | 90.2818 | 2003-05-20 | 345 | 62 |  |  |  | 2003-12-13 21:00 | 70.9
2000-10-27 | 0.031 | 0.032 | 0.041 | 0.041 | 0.033 | 0.032 | 2000-04-22 | 60.357 | 90.2818 | 2003-05-21 |  | 63 |  |  |  | 2003-12-14 07:57 | 74.4
2000-10-28 | 0.041 | 0.04 | 0.049 | 0.038 | 0.045 | 0.045 | 2000-04-23 | 60.876 | 90.2818 | 2003-05-22 | 345 | 63 |  |  |  | 2003-12-14 13:30 | 74.9
2000-10-29 | 0.047 | 0.047 | 0.044 | 0.046 | 0.043 | 0.03 | 2000-04-24 | 46.434 | 90.2818 | 2003-05-23 | 345 | 64 |  |  |  | 2003-12-14 21:00 | 70.4
2000-10-30 | 0.057 | 0.06 | 0.057 | 0.047 | 0.043 | 0.054 | 2000-04-25 | 45.038 | 91.1801 | 2003-05-24 |  | 65 |  |  |  | 2003-12-15 07:25 | 75
2000-10-31 | 0.058 | 0.057 | 0.042 | 0.04 | 0.042 | 0.041 | 2000-04-26 | 48.222 | 91.1801 | 2003-05-25 |  | 63 |  |  |  | 2003-12-15 21:00 | 74.1
2000-11-01 | 0.049 | 0.047 | 0.05 | 0.046 | 0.047 | 0.053 | 2000-04-27 | 46.284 | 91.1801 | 2003-05-26 |  | 61 |  |  |  | 2003-12-16 07:40 | 77.5
2000-11-02 | 0.057 | 0.057 | 0.053 | 0.045 | 0.046 | 0.034 | 2000-04-28 | 48.549 | 91.1801 | 2003-05-27 | 350 | 60 |  |  |  | 2003-12-16 13:30 | 77.9
2000-11-03 | 0.022 | 0.032 | 0.041 | 0.033 | 0.042 | 0.043 | 2000-04-29 | 47.305 | 91.1801 | 2003-05-28 |  | 61 |  |  |  | 2003-12-16 21:00 | 74.4
2000-11-04 | 0.045 | 0.048 | 0.045 | 0.046 | 0.054 | 0.041 | 2000-04-30 | 47.014 | 91.1801 | 2003-05-29 |  | 64 |  |  |  | 2003-12-17 07:26 | 78.2
2000-11-05 | 0.045 | 0.048 | 0.047 | 0.049 | 0.044 | 0.064 | 2000-05-01 | 42.92 | 91.1801 | 2003-05-30 |  | 62 |  |  |  | 2003-12-17 13:30 | 74
2000-11-06 | 0.059 | 0.057 | 0.052 | 0.057 | 0.053 | 0.045 | 2000-05-02 | 45.811 | 94.5366 | 2003-05-31 | 350 | 65 |  |  |  | 2003-12-17 21:00 | 73.9
2000-11-07 | 0.048 | 0.049 | 0.053 | 0.04 | 0.042 | 0.057 | 2000-05-03 | 50.475 | 94.5366 | 2003-06-01 | 360 | 65 |  |  |  | 2003-12-18 07:22 | 76.3
2000-11-08 | 0.061 | 0.057 | 0.039 | 0.035 | 0.038 | 0.04 | 2000-05-04 | 48.22 | 94.5366 | 2003-06-02 | 360 | 49 |  |  |  | 2003-12-18 13:30 | 75.1
2000-11-09 | 0.042 | 0.044 | 0.03 | 0.034 | 0.036 | 0.051 | 2000-05-05 | 48.352 | 94.5366 | 2003-06-03 | 450 | 64 |  |  |  | 2003-12-18 21:00 | 72.4
2000-11-10 | 0.05 | 0.048 | 0.046 | 0.045 | 0.047 | 0.052 | 2000-05-06 | 49.025 | 94.5366 | 2003-06-04 | 360 | 64 |  |  |  | 2003-12-19 07:20 | 72.8
2000-11-11 | 0.05 | 0.043 | 0.053 | 0.057 | 0.057 | 0.068 | 2000-05-07 | 49.896 | 94.5366 | 2003-06-05 | 372 | 66 |  |  |  | 2003-12-19 13:30 | 71.6
2000-11-12 | 0.062 | 0.06 | 0.068 | 0.055 | 0.044 | 0.04 | 2000-05-08 | 43.599 | 94.5366 | 2003-06-06 | 367 | 63 |  |  |  | 2003-12-19 21:00 | 69
2000-11-13 | 0.051 | 0.048 | 0.047 | 0.047 | 0.048 | 0.058 | 2000-05-09 | 47.787 | 91.6643 | 2003-06-07 | 367 | 65 |  |  |  | 2003-12-20 07:17 | 68.2
2000-11-14 | 0.059 | 0.06 | 0.062 | 0.053 | 0.047 | 0.05 | 2000-05-10 | 48.79 | 91.6643 | 2003-06-08 | 369 | 66 |  |  |  | 2003-12-20 13:30 | 69.6
2000-11-15 | 0.054 | 0.052 | 0.059 | 0.048 | 0.055 | 0.056 | 2000-05-11 | 47.997 | 91.6643 | 2003-06-09 | 360 | 65 |  |  |  | 2003-12-20 21:00 | 66.3
2000-11-16 | 0.059 | 0.059 | 0.058 | 0.074 | 0.058 | 0.058 | 2000-05-12 | 45.714 | 91.6643 | 2003-06-10 | 360 | 64 |  |  |  | 2003-12-21 07:00 | 69.5
2000-11-17 | 0.052 | 0.046 | 0.059 | 0.052 | 0.061 | 0.057 | 2000-05-13 | 46.613 | 91.6643 | 2003-06-11 | 360 | 64 |  |  |  | 2003-12-21 13:30 | 70
2000-11-18 | 0.058 | 0.06 | 0.072 | 0.054 | 0.057 | 0.051 | 2000-05-14 | 47.397 | 91.6643 | 2003-06-12 | 360 | 63 |  |  |  | 2003-12-21 21:00 | 68.1
2000-11-19 | 0.061 | 0.061 | 0.063 | 0.055 | 0.054 | 0.059 | 2000-05-15 | 41.763 | 91.6643 | 2003-06-13 | 360 | 53 |  |  |  | 2003-12-22 13:30 | 70.1
2000-11-20 | 0.059 | 0.06 | 0.058 | 0.061 | 0.048 | 0.06 | 2000-05-16 | 46.702 | 93.1751 | 2003-06-14 | 361 | 61 |  |  |  | 2003-12-22 21:00 | 75.6
2000-11-21 | 0.062 | 0.061 | 0.059 | 0.062 | 0.054 | 0.055 | 2000-05-17 | 45.202 | 93.1751 | 2003-06-15 | 356 | 60 |  |  |  | 2003-12-23 07:12 | 78.3
2000-11-22 | 0.054 | 0.055 | 0.052 | 0.048 | 0.062 | 0.062 | 2000-05-18 | 40.426 | 93.1751 | 2003-06-16 | 356 | 61 |  |  |  | 2003-12-23 13:30 | 79.2
2000-11-23 | 0.063 | 0.055 | 0.058 | 0.061 | 0.058 | 0.062 | 2000-05-19 | 43.66 | 93.1751 | 2003-06-17 | 370 | 55 |  |  |  | 2003-12-23 21:00 | 65.2
2000-11-24 | 0.067 | 0.062 | 0.06 | 0.063 | 0.048 | 0.057 | 2000-05-20 | 45.05 | 93.1751 | 2003-06-18 | 358 | 58 |  |  |  | 2003-12-24 08:05 | 70.6
2000-11-25 | 0.058 | 0.066 | 0.054 | 0.057 | 0.055 | 0.042 | 2000-05-21 | 45.421 | 93.1751 | 2003-06-19 | 358 | 60 |  |  |  | 2003-12-24 13:30 | 68.5
2000-11-26 | 0.061 | 0.065 | 0.06 | 0.054 | 0.051 | 0.057 | 2000-05-22 | 39.867 | 93.1751 | 2003-06-20 | 358 | 58 |  |  |  | 2003-12-24 21:00 | 71.6
2000-11-27 | 0.052 | 0.055 | 0.06 | 0.049 | 0.039 | 0.052 | 2000-05-23 | 46.209 | 91.5377 | 2003-06-21 | 358 | 61 |  |  |  | 2003-12-25 07:55 | 68
2000-11-28 | 0.056 | 0.055 | 0.049 | 0.06 | 0.061 | 0.05 | 2000-05-24 | 45.427 | 91.5377 | 2003-06-22 | 379 | 57 |  |  |  | 2003-12-25 13:30 | 74
2000-11-29 | 0.04 | 0.042 | 0.055 | 0.06 | 0.058 | 0.05 | 2000-05-25 | 46.415 | 91.5377 | 2003-06-23 | 369 | 59 |  |  |  | 2003-12-25 21:00 | 71.6
2000-11-30 | 0.042 | 0.046 | 0.053 | 0.062 | 0.061 | 0.057 | 2000-05-26 | 49.724 | 91.5377 | 2003-06-24 | 368 | 61 |  |  |  | 2003-12-26 07:24 | 71.9
2000-12-01 | 0.057 | 0.058 | 0.057 | 0.058 | 0.05 | 0.058 | 2000-05-27 | 50.067 | 91.5377 | 2003-06-25 | 373 | 62 |  |  |  | 2003-12-26 13:30 | 74
2000-12-02 | 0.057 | 0.06 | 0.054 | 0.048 | 0.044 | 0.049 | 2000-05-28 | 50.903 | 91.5377 | 2003-06-26 | 373 | 62 |  |  |  | 2003-12-26 21:00 | 69
2000-12-03 | 0.054 | 0.052 | 0.044 | 0.039 | 0.041 | 0.054 | 2000-05-29 | 43.253 | 91.5377 | 2003-06-27 | 366 | 62 |  |  |  | 2003-12-27 06:55 | 71.1
2000-12-04 | 0.056 | 0.056 | 0.029 | 0.046 | 0.047 | 0.058 | 2000-05-30 | 50.106 | 91.5377 | 2003-06-28 | 358 | 62 |  |  |  | 2003-12-27 13:30 | 74
2000-12-05 | 0.055 | 0.056 | 0.053 | 0.054 | 0.029 | 0.039 | 2000-05-31 | 52.602 | 91.5377 | 2003-06-29 | 358 | 63 |  |  |  | 2003-12-27 21:00 | 76.1
2000-12-06 | 0.052 | 0.052 | 0.057 | 0.052 | 0.05 | 0.048 | 2000-06-01 | 52.786 | 91.5377 | 2003-06-30 | 358 | 62 |  |  |  | 2003-12-28 08:03 | 78.6
2000-12-07 | 0.049 | 0.051 | 0.024 | 0.04 | 0.043 | 0.052 | 2000-06-02 | 47.355 | 91.5377 | 2003-07-01 | 370.5 | 62 |  |  |  | 2003-12-28 21:00 | 76.1
2000-12-08 | 0.052 | 0.049 | 0.054 | 0.052 | 0.056 | 0.043 | 2000-06-03 | 47.1 | 91.5377 | 2003-07-02 | 370.5 | 63 |  |  |  | 2003-12-29 07:18 | 74.5
2000-12-09 | 0.043 | 0.044 | 0.05 | 0.047 | 0.055 | 0.054 | 2000-06-04 | 48.659 | 91.5377 | 2003-07-03 | 370.5 | 63 |  |  |  | 2003-12-29 13:30 | 80.9
2000-12-10 | 0.056 | 0.054 | 0.05 | 0.048 | 0.051 | 0.037 | 2000-06-05 | 45.209 | 91.5377 | 2003-07-04 | 370.5 | 65 |  |  |  | 2003-12-29 21:00 | 74.7
2000-12-11 | 0.04 | 0.043 | 0.043 | 0.06 | 0.066 | 0.054 | 2000-06-06 | 50.106 | 91.5377 | 2003-07-05 | 370.6 | 65 |  |  |  | 2003-12-30 07:30 | 77.8
2000-12-12 | 0.053 | 0.054 | 0.054 | 0.049 | 0.048 | 0.042 | 2000-06-07 | 46.341 | 91.5377 | 2003-07-06 | 370.5 | 68 |  |  |  | 2003-12-30 13:30 | 76.6
2000-12-13 |  | 0.051 | 0.048 | 0.045 | 0.048 | 0.04 | 2000-06-08 | 48.239 | 91.5377 | 2003-07-07 | 402.7 | 65 |  |  |  | 2003-12-30 21:00 | 74.9
2000-12-14 | 0.041 | 0.047 | 0.045 | 0.045 | 0.047 | 0.049 | 2000-06-09 | 51.263 | 91.5377 | 2003-07-08 | 397.7 | 64 |  |  |  | 2003-12-31 07:30 | 70.6
2000-12-15 | 0.047 | 0.053 | 0.051 | 0.041 | 0.043 | 0.047 | 2000-06-10 | 49.943 | 91.5377 | 2003-07-09 | 397.3 | 61 |  |  |  | 2003-12-31 13:30 | 70.6
2000-12-16 | 0.049 | 0.05 | 0.049 | 0.047 | 0.046 | 0.047 | 2000-06-11 | 50.199 | 91.5377 | 2003-07-10 | 394.6 | 59 |  |  |  | 2003-12-31 21:00 | 67.4
2000-12-17 | 0.046 | 0.047 | 0.048 | 0.044 | 0.045 | 0.054 | 2000-06-12 | 46.104 | 91.5377 | 2003-07-11 | 396.1 | 63 |  |  |  | 2004-01-01 08:10 | 69.5
2000-12-18 | 0.05 | 0.05 | 0.053 |  |  |  | 2000-06-13 | 49.071 | 91.5377 | 2003-07-12 | 392.5 | 66 |  |  |  | 2004-01-01 13:30 | 71.2
2000-12-21 |  |  |  |  | 0.053 |  | 2000-06-14 | 48 | 91.5377 | 2003-07-13 | 400.4 | 62 |  |  |  | 2004-01-01 21:00 | 66
2000-12-22 |  |  | 0.043 | 0.036 | 0.036 | 0.042 | 2000-06-15 | 47.046 | 91.5377 | 2003-07-14 | 400.4 | 62 |  |  |  | 2004-01-02 07:30 | 71.9
2000-12-23 | 0.036 | 0.04 | 0.041 | 0.032 | 0.034 | 0.04 | 2000-06-16 | 47.432 | 91.5377 | 2003-07-15 | 405.4 | 64 |  |  |  | 2004-01-02 13:30 | 71.5
2000-12-24 | 0.034 | 0.032 | 0.032 | 0.031 | 0.051 | 0.032 | 2000-06-17 | 49.1 | 91.5377 | 2003-07-16 | 396.9 | 62 |  |  |  | 2004-01-02 21:00 | 67.7
2000-12-25 | 0.038 | 0.037 | 0.038 | 0.035 | 0.033 | 0.034 | 2000-06-18 | 49.504 | 91.5377 | 2003-07-17 | 396.9 | 67 |  |  |  | 2004-01-03 07:45 | 68.2
2000-12-26 | 0.035 | 0.034 | 0.035 | 0.034 | 0.044 | 0.04 | 2000-06-19 | 52.939 | 91.5377 | 2003-07-18 | 396.9 | 64 |  |  |  | 2004-01-03 13:30 | 71.5
2000-12-27 | 0.036 | 0.04 | 0.041 | 0.023 | 0.028 | 0.033 | 2000-06-20 | 50.1 | 91.5377 | 2003-07-19 | 396.5 | 66 |  |  |  | 2004-01-04 08:54 | 68.7
2000-12-28 | 0.032 | 0.033 | 0.032 | 0.028 | 0.039 | 0.032 | 2000-06-21 | 43.584 | 91.5377 | 2003-07-20 | 390.5 | 63 |  |  |  | 2004-01-04 13:30 | 69
2000-12-29 | 0.051 | 0.048 | 0.032 | 0.054 | 0.054 | 0.042 | 2000-06-22 | 48.144 | 91.5377 | 2003-07-21 | 390.5 | 62 |  |  |  | 2004-01-04 21:00 | 69.7
2000-12-30 | 0.043 | 0.049 | 0.042 | 0.055 | 0.037 | 0.065 | 2000-06-23 | 48.745 | 91.5377 | 2003-07-22 | 390.5 | 62 |  |  |  | 2004-01-05 07:10 | 71
2000-12-31 | 0.043 | 0.042 | 0.055 | 0.043 | 0.044 | 0.04 | 2000-06-24 | 48.721 | 91.5377 | 2003-07-23 | 390.5 | 64 |  |  |  | 2004-01-05 13:30 | 72.7
2001-01-01 | 0.044 | 0.042 | 0.031 | 0.036 | 0.039 | 0.029 | 2000-06-25 | 47.657 | 91.5377 | 2003-07-24 | 390.5 | 63 |  |  |  | 2004-01-05 21:00 | 72.5
2001-01-02 | 0.034 | 0.032 | 0.03 | 0.037 | 0.053 | 0.032 | 2000-06-26 | 44.23 | 91.5377 | 2003-07-25 | 401.6 | 63 |  |  |  | 2004-01-06 07:15 | 70.7
2001-01-03 | 0.031 | 0.044 | 0.043 | 0.065 | 0.062 | 0.059 | 2000-06-27 | 50.065 | 91.5377 | 2003-07-26 | 404.1 | 64 |  |  |  | 2004-01-06 13:30 | 70.5
2001-01-04 | 0.049 | 0.045 | 0.046 | 0.051 | 0.044 | 0.039 | 2000-06-28 | 46.953 | 91.5377 | 2003-07-27 | 398.6 | 62 |  |  |  | 2004-01-06 21:00 | 71.4
2001-01-05 | 0.02 | 0.032 | 0.036 | 0.05 | 0.044 | 0.037 | 2000-06-29 | 49.365 | 91.5377 | 2003-07-28 | 397.7 | 63 |  |  |  | 2004-01-07 07:15 | 71.6
2001-01-06 | 0.032 | 0.031 | 0.042 | 0.031 | 0.035 | 0.033 | 2000-06-30 | 46.694 | 91.5377 | 2003-07-29 | 405 | 67 |  |  |  | 2004-01-07 13:30 | 72.5
2001-01-07 | 0.027 | 0.028 | 0.03 | 0.029 | 0.032 | 0.048 | 2000-07-01 | 47.924 | 91.5377 | 2003-07-30 | 398.4 | 67 |  |  |  | 2004-01-08 07:20 | 69.1
2001-01-08 | 0.039 | 0.043 | 0.042 | 0.038 | 0.032 | 0.05 | 2000-07-02 | 49.395 | 91.5377 | 2003-07-31 | 400.4 | 67 |  |  |  | 2004-01-08 13:30 | 72
2001-01-09 | 0.041 | 0.042 | 0.032 | 0.039 | 0.045 | 0.043 | 2000-07-03 | 43.516 | 91.5377 | 2003-08-01 | 400.4 | 64 |  |  |  | 2004-01-08 21:00 | 70.6
2001-01-10 | 0.042 | 0.042 | 0.039 | 0.037 | 0.039 | 0.045 | 2000-07-04 | 50.525 | 91.5377 | 2003-08-02 | 403.8 | 65 |  |  |  | 2004-01-09 07:25 | 68.5
2001-01-11 | 0.048 | 0.047 | 0.042 | 0.044 | 0.043 | 0.034 | 2000-07-05 | 47.937 | 91.5377 | 2003-08-03 | 403.8 | 64 |  |  |  | 2004-01-09 13:30 | 68.9
2001-01-12 | 0.038 | 0.037 | 0.034 | 0.037 | 0.037 | 0.036 | 2000-07-06 | 48.077 | 91.5377 | 2003-08-04 | 399 | 65 |  |  |  | 2004-01-09 21:00 | 67.4
2001-01-13 | 0.041 | 0.039 | 0.042 | 0.02 | 0.025 | 0.036 | 2000-07-07 | 47.473 | 91.5377 | 2003-08-05 | 400.1 | 66 |  |  |  | 2004-01-10 07:38 | 68.8
2001-01-14 | 0.038 | 0.036 | 0.037 | 0.035 | 0.034 | 0.045 | 2000-07-08 | 49.277 | 91.5377 | 2003-08-06 | 388.5 | 62 |  |  |  | 2004-01-10 13:30 | 68.9
2001-01-15 | 0.04 | 0.053 | 0.036 | 0.034 | 0.025 | 0.039 | 2000-07-09 | 46.328 | 91.5377 | 2003-08-07 | 391.5 | 65 |  |  |  | 2004-01-10 21:00 | 66.5
2001-01-16 | 0.037 | 0.044 | 0.044 | 0.037 | 0.033 | 0.048 | 2000-07-10 | 43.786 | 91.5377 | 2003-08-08 | 397.3 | 66 |  |  |  | 2004-01-11 08:12 | 70.5
2001-01-17 | 0.041 | 0.042 | 0.026 | 0.029 | 0.035 | 0.028 | 2000-07-11 | 43.279 | 91.5377 | 2003-08-09 | 389.1 | 65 |  |  |  | 2004-01-11 13:30 | 73.5
2001-01-18 | 0.032 | 0.033 | 0.019 | 0.041 | 0.038 | 0.046 | 2000-07-12 | 47.262 | 91.5377 | 2003-08-10 | 389.1 | 64 |  |  |  | 2004-01-11 21:00 | 69.4
2001-01-19 | 0.047 | 0.04 | 0.038 | 0.042 | 0.041 | 0.039 | 2000-07-13 | 48.83 | 91.5377 | 2003-08-11 | 405.7 | 64 |  |  |  | 2004-01-12 08:00 | 70.5
2001-01-20 | 0.041 | 0.036 | 0.038 | 0.037 | 0.042 | 0.034 | 2000-07-14 | 47.622 | 91.5377 | 2003-08-12 | 402.5 | 62 |  |  |  | 2004-01-12 13:30 | 71.9
2001-01-21 | 0.037 | 0.036 | 0.036 | 0.033 | 0.039 | 0.032 | 2000-07-15 | 49.737 | 91.5377 | 2003-08-13 | 402.5 | 62 |  |  |  | 2004-01-12 21:00 | 69.3
2001-01-22 | 0.036 | 0.035 | 0.032 | 0.036 | 0.025 | 0.036 | 2000-07-16 | 47.841 | 91.5377 | 2003-08-14 | 400.1 | 64 |  |  |  | 2004-01-13 07:10 | 73.6
2001-01-23 | 0.032 | 0.036 | 0.042 | 0.032 | 0.033 | 0.047 | 2000-07-17 | 44.216 | 91.5377 | 2003-08-15 | 400.7 | 64 |  |  |  | 2004-01-13 13:30 | 73.1
2001-01-24 | 0.041 | 0.042 | 0.037 | 0.03 | 0.03 | 0.037 | 2000-07-18 | 51.725 | 91.5377 | 2003-08-16 | 400.2 | 64 |  |  |  | 2004-01-13 21:00 | 69.3
2001-01-25 | 0.049 | 0.034 | 0.041 | 0.039 | 0.032 | 0.035 | 2000-07-19 | 48.226 | 91.5377 | 2003-08-17 | 409.7 | 65 |  |  |  | 2004-01-14 07:50 | 71.8
2001-01-26 | 0.036 | 0.035 | 0.039 | 0.036 | 0.035 | 0.039 | 2000-07-20 | 48.059 | 91.5377 | 2003-08-18 | 397.7 | 64 |  |  |  | 2004-01-14 13:30 | 73.3
2001-01-27 | 0.034 | 0.034 | 0.04 | 0.043 | 0.041 | 0.039 | 2000-07-21 | 49.173 | 91.5377 | 2003-08-19 | 397.7 | 65 |  |  |  | 2004-01-14 21:00 | 72.8
2001-01-28 | 0.036 | 0.035 | 0.045 | 0.043 | 0.057 | 0.043 | 2000-07-22 | 48.978 | 91.5377 | 2003-08-20 | 397.7 | 68 |  |  |  | 2004-01-15 07:25 | 68.5
2001-01-29 | 0.045 | 0.046 | 0.035 | 0.036 | 0.044 | 0.056 | 2000-07-23 | 49.346 | 91.5377 | 2003-08-21 | 405.9 | 66 |  |  |  | 2004-01-15 13:30 | 73
2001-01-30 | 0.039 | 0.062 | 0.058 | 0.067 | 0.062 | 0.051 | 2000-07-24 | 42.148 | 91.5377 | 2003-08-22 | 405.9 | 64 |  |  |  | 2004-01-15 21:00 | 69.7
2001-01-31 | 0.065 | 0.051 |  |  | 0.045 | 0.038 | 2000-07-25 | 51.851 | 91.5377 | 2003-08-23 | 405.9 | 64 |  |  |  | 2004-01-16 07:15 | 74.5
2001-02-01 | 0.039 | 0.039 | 0.038 | 0.029 | 0.033 | 0.037 | 2000-07-26 | 49.883 | 91.5377 | 2003-08-24 | 405.9 | 63 |  |  |  | 2004-01-16 13:30 | 71
2001-02-02 | 0.033 | 0.034 | 0.042 | 0.037 | 0.033 | 0.037 | 2000-07-27 | 47.861 | 91.5377 | 2003-08-25 | 405.9 | 65 |  |  |  | 2004-01-16 21:00 | 71.5
2001-02-03 | 0.031 | 0.035 | 0.032 | 0.03 | 0.03 | 0.032 | 2000-07-28 | 49.921 | 91.5377 | 2003-08-26 | 390 | 63 |  |  |  | 2004-01-17 07:02 | 73.3
2001-02-04 | 0.036 | 0.03 | 0.04 | 0.039 | 0.035 | 0.038 | 2000-07-29 | 49.686 | 91.5377 | 2003-08-27 | 397.7 | 63 |  |  |  | 2004-01-17 13:30 | 72.8
2001-02-05 | 0.039 | 0.038 | 0.042 | 0.041 | 0.046 | 0.049 | 2000-07-30 | 48.279 | 91.5377 | 2003-08-28 | 399.8 | 66 |  |  |  | 2004-01-17 21:00 | 73.5
2001-02-06 | 0.041 | 0.039 | 0.041 | 0.038 | 0.039 | 0.03 | 2000-07-31 | 47.53 | 91.5377 | 2003-08-29 | 398.7 | 65 |  |  |  | 2004-01-18 07:20 | 72.2
2001-02-07 | 0.031 | 0.031 | 0.04 | 0.041 | 0.04 | 0.037 | 2000-08-01 | 49.601 | 91.5377 | 2003-08-30 | 398.7 | 66 |  |  |  | 2004-01-18 13:30 | 75.8
2001-02-08 | 0.04 | 0.038 | 0.037 | 0.044 | 0.03 | 0.035 | 2000-08-02 | 48.157 | 91.5377 | 2003-08-31 | 390 | 64 |  |  |  | 2004-01-18 21:00 | 69.5
2001-02-09 | 0.03 | 0.031 | 0.042 | 0.03 | 0.033 | 0.031 | 2000-08-03 | 48.748 | 91.5377 | 2003-09-01 | 408.2 | 64 |  |  |  | 2004-01-19 07:15 | 72.7
2001-02-10 | 0.03 | 0.03 | 0.038 | 0.027 | 0.031 | 0.032 | 2000-08-04 | 44.548 | 91.5377 | 2003-09-02 | 396.9 | 63 |  |  |  | 2004-01-19 13:30 | 71.9
2001-02-11 | 0.032 | 0.03 | 0.035 | 0.03 | 0.033 | 0.024 | 2000-08-05 | 52.77 | 91.5377 | 2003-09-03 | 400.1 | 65 |  |  |  | 2004-01-19 21:00 | 66.9
2001-02-12 | 0.025 | 0.033 | 0.041 | 0.041 | 0.039 | 0.042 | 2000-08-06 | 50.451 | 91.5377 | 2003-09-04 | 390.3 | 63 |  |  |  | 2004-01-20 07:15 | 74.7
2001-02-13 | 0.037 | 0.037 | 0.05 | 0.041 | 0.04 | 0.034 | 2000-08-07 | 44.445 | 91.5377 | 2003-09-05 | 399.8 | 66 |  |  |  | 2004-01-20 13:30 | 72.9
2001-02-14 | 0.037 | 0.04 | 0.041 | 0.041 | 0.04 | 0.043 | 2000-08-08 | 52.006 | 91.5377 | 2003-09-06 | 393.1 | 90 |  |  |  | 2004-01-20 21:00 | 72.3
2001-02-15 | 0.037 | 0.035 | 0.038 | 0.03 | 0.029 | 0.037 | 2000-08-09 | 53.058 | 91.5377 | 2003-09-07 | 400.2 | 63 |  |  |  | 2004-01-21 07:15 | 72.3
2001-02-16 | 0.038 | 0.039 | 0.04 | 0.037 | 0.039 | 0.043 | 2000-08-10 | 50.87 | 91.5377 | 2003-09-08 | 405 | 66 |  |  |  | 2004-01-21 13:30 | 71.7
2001-02-17 | 0.042 | 0.041 | 0.039 | 0.044 | 0.04 | 0.036 | 2000-08-11 | 50.736 | 91.5377 | 2003-09-09 | 389.4 | 65 |  |  |  | 2004-01-21 21:00 | 68.5
2001-02-18 | 0.034 | 0.035 | 0.05 | 0.036 | 0.044 | 0.038 | 2000-08-12 | 52.473 | 91.5377 | 2003-09-10 | 392.2 | 64 |  |  |  | 2004-01-22 07:20 | 68.9
2001-02-19 | 0.034 | 0.034 | 0.033 | 0.029 | 0.028 | 0.038 | 2000-08-13 | 50.058 | 91.5377 | 2003-09-11 | 392.2 | 63 |  |  |  | 2004-01-22 13:30 | 68.5
2001-02-20 | 0.039 | 0.04 | 0.036 | 0.034 | 0.046 | 0.027 | 2000-08-14 | 43.722 | 91.5377 | 2003-09-12 | 402.7 | 65 |  |  |  | 2004-01-22 21:00 | 65.7
2001-02-21 | 0.035 | 0.033 | 0.037 | 0.032 | 0.039 | 0.033 | 2000-08-15 | 50.241 | 91.5377 | 2003-09-13 | 396.9 | 65 |  |  |  | 2004-01-23 07:16 | 73.4
2001-02-22 | 0.033 | 0.031 | 0.037 | 0.039 | 0.036 | 0.032 | 2000-08-16 | 48.51 | 91.5377 | 2003-09-14 | 400.4 | 63 |  |  |  | 2004-01-23 13:30 | 68.5
2001-02-23 | 0.029 | 0.031 | 0.037 | 0.042 | 0.039 | 0.041 | 2000-08-17 | 48.77 | 91.5377 | 2003-09-15 | 400.4 | 66 |  |  |  | 2004-01-23 21:00 | 70.9
2001-02-24 | 0.035 | 0.034 | 0.042 | 0.037 | 0.04 | 0.033 | 2000-08-18 | 49.753 | 91.5377 | 2003-09-16 | 400.4 | 63 |  |  |  | 2004-01-24 07:04 | 72.9
2001-02-25 | 0.032 | 0.036 | 0.041 | 0.04 | 0.039 | 0.046 | 2000-08-19 | 49.127 | 91.5377 | 2003-09-17 | 396.9 | 63 |  |  |  | 2004-01-24 13:30 | 70.1
2001-02-26 | 0.037 | 0.038 | 0.069 | 0.049 | 0.046 | 0.044 | 2000-08-20 | 45.414 | 91.5377 | 2003-09-18 | 399.5 | 65 |  |  |  | 2004-01-24 21:00 | 67.3
2001-02-27 | 0.05 | 0.053 | 0.042 | 0.05 | 0.045 | 0.036 | 2000-08-21 | 47.518 | 91.5377 | 2003-09-19 | 399.5 | 61 |  |  |  | 2004-01-25 07:20 | 73.4
2001-02-28 | 0.031 | 0.032 | 0.034 | 0.037 | 0.044 | 0.033 | 2000-08-22 | 50.877 | 91.5377 | 2003-09-20 | 399.5 | 63 |  |  |  | 2004-01-25 13:30 | 71.7
2001-03-01 | 0.03 | 0.028 | 0.034 | 0.03 | 0.034 | 0.03 | 2000-08-23 | 50.027 | 91.5377 | 2003-09-21 | 399.5 | 66 |  |  |  | 2004-01-25 21:00 | 69.9
2001-03-02 | 0.028 | 0.028 | 0.028 | 0.032 | 0.03 | 0.036 | 2000-08-24 | 48.627 | 91.5377 | 2003-09-22 | 397.7 | 67 |  |  |  | 2004-01-26 07:30 | 71.6
2001-03-03 | 0.029 | 0.03 | 0.044 | 0.027 | 0.032 | 0.03 | 2000-08-25 | 49.425 | 91.5377 | 2003-09-23 | 402.2 | 69 |  |  |  | 2004-01-26 13:30 | 73.1
2001-03-04 | 0.03 | 0.031 | 0.03 | 0.033 | 0.032 | 0.034 | 2000-08-26 | 50.097 | 91.5377 | 2003-09-24 | 388.6 | 66 |  |  |  | 2004-01-26 21:00 | 73
2001-03-05 | 0.033 | 0.038 | 0.031 | 0.03 | 0.032 | 0.04 | 2000-08-27 | 50.492 | 91.5377 | 2003-09-25 | 398.6 | 66 |  |  |  | 2004-01-27 08:10 | 71.7
2001-03-06 | 0.041 | 0.041 | 0.045 | 0.04 | 0.034 | 0.042 | 2000-08-28 | 45.214 | 91.5377 | 2003-09-26 | 389.3 | 65 |  |  |  | 2004-01-27 13:30 | 70.1
2001-03-07 | 0.034 | 0.034 | 0.027 | 0.037 | 0.027 | 0.029 | 2000-08-29 | 48.476 | 91.5377 | 2003-09-27 | 389.3 | 66 |  |  |  | 2004-01-27 21:00 | 67.9
2001-03-08 | 0.029 | 0.03 | 0.039 | 0.032 | 0.035 | 0.026 | 2000-08-30 | 45.614 | 91.5377 | 2003-09-28 | 389.3 | 65 |  |  |  | 2004-01-28 07:28 | 71.4
2001-03-09 | 0.027 | 0.028 | 0.038 | 0.039 | 0.033 | 0.029 | 2000-08-31 | 50.284 | 91.5377 | 2003-09-29 | 389.3 | 66 |  |  |  | 2004-01-28 13:30 | 70.9
2001-03-10 | 0.029 | 0.027 | 0.039 | 0.035 | 0.033 | 0.033 | 2000-09-01 | 50.284 | 91.5377 | 2003-09-30 | 389.3 | 66 |  |  |  | 2004-01-28 21:00 | 68.4
2001-03-11 | 0.028 | 0.028 | 0.036 | 0.041 | 0.042 | 0.028 | 2000-09-02 | 49.949 | 91.5377 | 2003-10-01 | 389.3 | 66 |  |  |  | 2004-01-29 07:20 | 69.7
2001-03-12 | 0.037 | 0.034 | 0.039 | 0.05 | 0.039 | 0.034 | 2000-09-03 | 49.356 | 91.5377 | 2003-10-02 | 389.3 | 66 |  |  |  | 2004-01-30 07:30 | 67.43
2001-03-13 | 0.032 | 0.034 | 0.041 | 0.033 | 0.036 | 0.013 | 2000-09-04 | 49.814 | 91.5377 | 2003-10-03 | 389.3 | 64 |  |  |  | 2004-02-01 07:53 | 73
2001-03-14 | 0.027 | 0.033 | 0.034 | 0.036 | 0.032 | 0.032 | 2000-09-05 | 45.022 | 91.5377 | 2003-10-04 | 399.3 | 65 |  |  |  | 2004-02-01 13:30 | 74.8
2001-03-15 | 0.034 | 0.037 | 0.034 | 0.031 | 0.031 | 0.029 | 2000-09-06 | 50.169 | 91.5377 | 2003-10-05 | 399.3 | 86 |  |  |  | 2004-02-01 21:00 | 71.1
2001-03-16 | 0.033 | 0.031 | 0.032 | 0.027 | 0.029 | 0.027 | 2000-09-07 | 49.862 | 91.5377 | 2003-10-06 | 410.2 | 59 |  |  |  | 2004-02-02 07:20 | 72.4
2001-03-17 | 0.026 | 0.029 | 0.033 | 0.029 | 0.027 | 0.027 | 2000-09-08 | 49.862 | 91.5377 | 2003-10-07 | 406 | 65 |  |  |  | 2004-02-02 13:30 | 74.7
2001-03-18 | 0.027 | 0.027 | 0.03 | 0.034 | 0.034 | 0.013 | 2000-09-09 | 48.471 | 91.5377 | 2003-10-08 | 405.1 | 62 |  |  |  | 2004-02-02 21:00 | 71.4
2001-03-19 | 0.018 | 0.031 | 0.035 | 0.034 | 0.032 | 0.034 | 2000-09-10 | 49.781 | 91.5377 | 2003-10-09 | 405.1 | 66 |  |  |  | 2004-02-03 07:19 | 74.2
2001-03-20 | 0.032 | 0.034 | 0.035 | 0.034 | 0.036 | 0.037 | 2000-09-11 | 46.52 | 91.5377 | 2003-10-10 | 391.2 | 66 |  |  |  | 2004-02-03 13:30 | 76.2
2001-03-21 | 0.034 | 0.04 | 0.032 | 0.037 | 0.038 | 0.03 | 2000-09-12 | 49.872 | 92.555 | 2003-10-11 | 401 | 65 |  |  |  | 2004-02-03 21:00 | 73.8
2001-03-22 | 0.034 | 0.029 | 0.037 | 0.036 | 0.029 | 0.03 | 2000-09-13 | 49.872 | 92.555 | 2003-10-12 | 407.9 | 62 |  |  |  | 2004-02-04 07:20 | 74
2001-03-23 | 0.029 | 0.03 | 0.032 | 0.038 | 0.038 | 0.035 | 2000-09-14 | 49.265 | 92.555 | 2003-10-13 | 397.5 | 63 |  |  |  | 2004-02-04 13:30 | 74.5
2001-03-24 | 0.032 | 0.03 | 0.035 | 0.027 | 0.026 | 0.03 | 2000-09-15 | 49.367 | 92.555 | 2003-10-14 | 397.8 | 65 |  |  |  | 2004-02-04 21:00 | 73
2001-03-25 | 0.03 | 0.029 | 0.04 | 0.041 | 0.034 | 0.032 | 2000-09-16 | 49.447 | 92.555 | 2003-10-15 | 399.3 | 73.5 |  |  |  | 2004-02-05 07:17 | 73.7
2001-03-26 | 0.032 | 0.03 | 0.032 | 0.034 | 0.032 | 0.03 | 2000-09-17 | 47.8 | 92.555 | 2003-10-16 | 399.3 | 71.6 |  |  |  | 2004-02-05 13:30 | 78
2001-03-27 | 0.032 | 0.031 | 0.033 | 0.043 | 0.03 | 0.033 | 2000-09-18 | 45.115 | 92.555 | 2003-10-17 | 399.3 | 74 |  |  |  | 2004-02-05 21:00 | 76.1
2001-03-28 | 0.034 | 0.038 | 0.031 | 0.04 | 0.024 | 0.034 | 2000-09-19 | 45.115 | 88.2064 | 2003-10-18 | 399.3 | 74.2 |  |  |  | 2004-02-06 07:35 | 75.9
2001-03-29 | 0.034 | 0.036 | 0.053 | 0.038 | 0.03 | 0.032 | 2000-09-20 | 47.866 | 88.2064 | 2003-10-19 | 399.3 | 75.3 |  |  |  | 2004-02-06 13:15 | 74.3
2001-03-30 | 0.033 | 0.033 | 0.039 | 0.032 | 0.027 | 0.034 | 2000-09-21 | 50.064 | 88.2064 | 2003-10-20 | 399.3 |  |  |  |  | 2004-02-06 21:00 | 71.7
2001-03-31 | 0.032 | 0.034 | 0.03 | 0.032 | 0.031 | 0.028 | 2000-09-22 | 47.28 | 88.2064 | 2003-10-21 | 399.3 | 74.5 |  |  |  | 2004-02-07 07:35 | 75.9
2001-04-01 | 0.032 | 0.03 | 0.031 | 0.033 | 0.035 | 0.031 | 2000-09-23 | 47.131 | 88.2064 | 2003-10-22 | 410.3 | 71.6 |  |  |  | 2004-02-07 13:15 | 74.3
2001-04-02 | 0.032 | 0.031 | 0.036 | 0.036 | 0.024 | 0.028 | 2000-09-24 | 49.877 | 88.2064 | 2003-10-23 | 413.8 | 73.9 |  |  |  | 2004-02-07 21:00 | 71.7
2001-04-03 | 0.025 | 0.025 | 0.034 |  | 0.029 | 0.03 | 2000-09-25 | 44.608 | 88.2064 | 2003-10-24 | 396.9 | 74.3 |  |  |  | 2004-02-08 07:37 | 73.4
2001-04-04 | 0.032 | 0.039 | 0.036 | 0.027 | 0.025 | 0.032 | 2000-09-26 | 49.698 | 87.8213 | 2003-10-25 | 396.9 | 74.7 |  |  |  | 2004-02-08 13:50 | 75
2001-04-05 | 0.035 | 0.03 | 0.033 | 0.023 | 0.022 | 0.026 | 2000-09-27 | 48.77 | 87.8213 | 2003-10-26 | 396.9 | 75 |  |  |  | 2004-02-08 21:00 | 72.1
2001-04-06 | 0.032 | 0.034 | 0.028 | 0.028 | 0.033 | 0.032 | 2000-09-28 | 48.902 | 87.8213 | 2003-10-27 | 395.4 | 73.4 |  |  |  | 2004-02-09 14:30 | 72.5
2001-04-07 | 0.034 | 0.035 | 0.033 | 0.023 | 0.027 | 0.034 | 2000-09-29 | 50.416 | 87.8213 | 2003-10-28 | 395.4 | 75.1 |  |  |  | 2004-02-09 22:00 | 69.2
2001-04-08 | 0.033 | 0.034 | 0.031 | 0.028 | 0.025 | 0.03 | 2000-09-30 | 48.752 | 87.8213 | 2003-10-29 | 395.4 | 76 |  |  |  | 2004-02-10 07:11 | 73.1
2001-04-09 | 0.029 | 0.029 | 0.026 | 0.023 | 0.018 | 0.024 | 2000-10-01 | 49.399 | 87.8213 | 2003-10-30 | 390.2 | 74.1 |  |  |  | 2004-02-10 13:35 | 71.2
2001-04-10 | 0.029 | 0.029 | 0.031 | 0.018 | 0.017 | 0.023 | 2000-10-02 | 46 | 87.8213 | 2003-10-31 | 390.2 | 75.9 |  |  |  | 2004-02-10 21:00 | 68.9
2001-04-11 | 0.03 | 0.028 | 0.028 | 0.012 | 0.023 | 0.029 | 2000-10-03 | 49.504 | 83.1764 | [6 empty] | 2004-02-11 07:16 | 69.2
2001-04-12 | 0.027 | 0.027 | 0.032 | 0.028 | 0.024 | 0.028 | 2000-10-04 | 49.668 | 83.1764 | [6 empty] | 2004-02-11 13:30 | 73.7
2001-04-13 | 0.036 | 0.031 | 0.023 | 0.019 | 0.017 | 0.032 | 2000-10-05 | 49.765 | 83.1764 | [6 empty] | 2004-02-11 21:00 | 74.1
2001-04-14 | 0.025 | 0.028 | 0.021 | 0.013 | 0.012 | 0.048 | 2000-10-06 | 44.373 | 83.1764 | [6 empty] | 2004-02-12 07:20 | 73.9
2001-04-15 | 0.037 | 0.038 | 0.019 | 0.019 | 0.014 | 0.022 | 2000-10-07 | 49.809 | 83.1764 | [6 empty] | 2004-02-12 13:30 | 68.6
2001-04-16 | 0.018 | 0.02 | 0.02 | 0.011 | 0.012 | 0.016 | 2000-10-08 | 48.524 | 83.1764 | [6 empty] | 2004-02-12 21:00 | 69.4
2001-04-17 | 0.02 | 0.021 | 0.021 | 0.017 | 0.014 | 0.022 | 2000-10-09 | 46.947 | 83.1764 | [6 empty] | 2004-02-13 07:40 | 71.1
2001-04-18 | 0.024 | 0.02 | 0.014 | 0.001 | 0.009 | 0.021 | 2000-10-10 | 48.758 | 96.117 | [6 empty] | 2004-02-13 13:22 | 70
2001-04-19 | 0.033 | 0.023 | 0.016 | 0.013 | 0.013 | 0.023 | 2000-10-11 | 48.384 | 96.117 | [6 empty] | 2004-02-13 21:00 | 69.2
2001-04-20 | 0.018 | 0.023 | 0.022 | 0.019 | 0.017 | 0.026 | 2000-10-12 | 51.207 | 96.117 | [6 empty] | 2004-02-14 07:20 | 70.3
2001-04-21 | 0.022 | 0.024 | 0.024 | 0.015 | 0.017 | 0.023 | 2000-10-13 | 49.984 | 96.117 | [6 empty] | 2004-02-14 13:30 | 68.1
2001-04-22 | 0.021 | 0.023 | 0.027 | 0.014 | 0.013 | 0.018 | 2000-10-14 | 48.795 | 96.117 | [6 empty] | 2004-02-14 21:00 | 66.6
2001-04-23 | 0.02 | 0.025 | 0.02 | 0.012 | 0.017 | 0.021 | 2000-10-15 | 49.03 | 96.117 | [6 empty] | 2004-02-15 07:12 | 69.7
2001-04-24 | 0.025 | 0.029 | 0.02 | 0.009 | 0.012 | 0.015 | 2000-10-16 | 45.455 | 96.117 | [6 empty] | 2004-02-15 13:30 | 71.1
2001-04-25 | 0.019 | 0.016 | 0.018 | 0.018 | 0.012 | 0.021 | 2000-10-17 | 50.025 | 98.7416 | [6 empty] | 2004-02-15 21:00 | 68.6
2001-04-26 | 0.018 | 0.024 | 0.02 | 0.015 | 0.012 | 0.02 | 2000-10-18 | 49.32 | 98.7416 | [6 empty] | 2004-02-16 06:47 | 70.2
2001-04-27 | 0.013 | 0.022 | 0.023 | 0.014 | 0.015 | 0.024 | 2000-10-19 | 49.568 | 98.7416 | [6 empty] | 2004-02-16 13:30 | 69.7
2001-04-28 | 0.027 | 0.028 | 0.024 | 0.014 | 0.015 | 0.021 | 2000-10-20 | 48.835 | 98.7416 | [6 empty] | 2004-02-16 21:00 | 68.6
2001-04-29 | 0.024 | 0.028 | 0.021 | 0.014 | 0.016 | 0.018 | 2000-10-21 | 50.268 | 98.7416 | [6 empty] | 2004-02-17 00:07 | 68.3
2001-04-30 | 0.028 | 0.028 | 0.022 | 0.021 | 0.016 | 0.013 | 2000-10-22 | 49.612 | 98.7416 | [6 empty] | 2004-02-17 00:07 | 68.3
2001-05-01 | 0.018 | 0.022 | 0.022 | 0.019 | 0.022 | 0.021 | 2000-10-23 | 47.471 | 98.7416 | [6 empty] | 2004-02-17 00:21 | 68.7
2001-05-02 | 0.016 | 0.017 | 0.012 | 0.015 | 0.025 | 0.021 | 2000-10-24 | 50.279 | 93.6268 | [6 empty] | 2004-02-18 00:07 | 70.3
2001-05-03 | 0.03 | 0.033 | 0.023 | 0.039 | 0.027 | 0.028 | 2000-10-25 | 50.317 | 93.6268 | [6 empty] | 2004-02-18 00:14 | 66.4
2001-05-04 | 0.033 | 0.033 | 0.031 | 0.032 | 0.023 | 0.028 | 2000-10-26 | 47.719 | 93.6268 | [6 empty] | 2004-02-18 00:21 | 66.5
2001-05-05 | 0.032 | 0.029 | 0.03 | 0.024 | 0.025 | 0.026 | 2000-10-27 | 51.342 | 93.6268 | [6 empty] | 2004-02-19 00:07 | 68.1
2001-05-06 | 0.03 | 0.032 | 0.028 | 0.026 | 0.024 | 0.028 | 2000-10-28 | 50.151 | 93.6268 | [6 empty] | 2004-02-19 00:14 | 69
2001-05-07 | 0.031 | 0.03 | 0.034 | 0.022 | 0.024 | 0.022 | 2000-10-29 | 51.314 | 93.6268 | [6 empty] | 2004-02-19 00:21 | 66.6
2001-05-08 | 0.026 | 0.028 | 0.025 | 0.021 | 0.022 | 0.026 | 2000-10-30 | 46.913 | 93.6268 | [6 empty] | 2004-02-20 00:07 | 66.1
2001-05-09 | 0.029 | 0.034 | 0.029 | 0.022 | 0.017 | 0.02 | 2000-10-31 | 49.502 | 93.6268 | [6 empty] | 2004-02-20 00:13 | 67.4
2001-05-10 | 0.028 | 0.021 | 0.028 | 0.023 | 0.021 | 0.025 | 2000-11-01 | 51.079 | 93.6268 | [6 empty] | 2004-02-20 00:21 | 66.6
2001-05-11 | 0.026 | 0.028 | 0.031 | 0.024 | 0.025 | 0.03 | 2000-11-02 | 49.102 | 93.6268 | [6 empty] | 2004-02-21 00:07 | 67.3
2001-05-12 | 0.032 | 0.033 | 0.027 | 0.019 | 0.025 | 0.025 | 2000-11-03 | 50.796 | 93.6268 | [6 empty] | 2004-02-21 00:14 | 68.2
2001-05-13 | 0.028 | 0.028 | 0.029 | 0.026 | 0.019 | 0.026 | 2000-11-04 | 51.081 | 93.6268 | [6 empty] | 2004-02-21 00:21 | 65
2001-05-14 | 0.028 | 0.032 | 0.029 | 0.023 | 0.022 | 0.029 | 2000-11-05 | 51.101 | 93.6268 | [6 empty] | 2004-02-22 00:07 | 68.8
2001-05-15 | 0.031 | 0.03 | 0.03 | 0.024 | 0.022 | 0.026 | 2000-11-06 | 45.767 | 93.6268 | [6 empty] | 2004-02-22 00:14 | 69.5
2001-05-16 | 0.027 | 0.025 | 0.026 | 0.025 | 0.023 | 0.033 | 2000-11-07 | 52.425 | 93.6268 | [6 empty] | 2004-02-22 00:21 | 68.1
2001-05-17 | 0.035 | 0.034 | 0.031 | 0.029 | 0.028 | 0.029 | 2000-11-08 | 50.461 | 93.5837 | [6 empty] | 2004-02-23 00:07 | 69.7
2001-05-18 | 0.029 | 0.027 | 0.025 | 0.027 | 0.026 | 0.033 | 2000-11-09 | 51.972 | 93.5837 | [6 empty] | 2004-02-23 00:14 | 69.7
2001-05-19 | 0.034 | 0.031 | 0.03 | 0.019 | 0.019 | 0.028 | 2000-11-10 | 50.963 | 93.5837 | [6 empty] | 2004-02-23 00:21 | 67.2
2001-05-20 | 0.034 | 0.032 | 0.026 | 0.023 | 0.025 | 0.023 | 2000-11-11 | 49.719 | 93.5837 | [6 empty] | 2004-02-24 00:07 | 68.5
2001-05-21 | 0.029 | 0.029 | 0.029 | 0.017 | 0.021 | 0.027 | 2000-11-12 | 49.927 | 93.5837 | [6 empty] | 2004-02-24 00:14 | 68.3
2001-05-22 | 0.026 | 0.026 | 0.031 | 0.024 | 0.023 | 0.031 | 2000-11-13 | 48.691 | 93.5837 | [6 empty] | 2004-02-24 00:21 | 65.4
2001-05-23 | 0.032 | 0.03 | 0.027 | 0.026 | 0.029 | 0.032 | 2000-11-14 | 50.804 | 91.4745 | [6 empty] | 2004-02-25 00:21 | 65.3
2001-05-24 | 0.031 | 0.031 | 0.029 | 0.027 | 0.026 | 0.032 | 2000-11-15 | 49.877 | 91.4745 | [6 empty] | 2004-02-26 00:07 | 64.7
2001-05-25 | 0.033 | 0.034 | 0.029 | 0.026 | 0.026 | 0.03 | 2000-11-16 | 52.977 | 91.4745 | [6 empty] | 2004-02-26 00:07 | 64.7
2001-05-26 | 0.029 | 0.029 | 0.025 | 0.027 | 0.025 | 0.031 | 2000-11-17 | 48.929 | 91.4745 | [6 empty] | 2004-02-26 00:14 | 64
2001-05-27 | 0.03 | 0.029 | 0.029 | 0.027 | 0.019 | 0.032 | 2000-11-18 | 51.895 | 91.4745 | [6 empty] | 2004-02-27 00:07 | 65.8
2001-05-28 | 0.033 | 0.034 | 0.033 | 0.031 | 0.02 | 0.026 | 2000-11-19 | 50.199 | 91.4745 | [6 empty] | 2004-02-27 00:13 | 65.7
2001-05-29 | 0.026 | 0.027 | 0.038 | 0.032 | 0.026 | 0.027 | 2000-11-20 | 46.999 | 91.4745 | [6 empty] | 2004-02-27 00:21 | 65.8
2001-05-30 | 0.036 | 0.037 | 0.031 | 0.041 | 0.024 | 0.029 | 2000-11-21 | 51.888 | 93.1322 | [6 empty] | 2004-02-28 00:07 | 65.8
2001-05-31 | 0.035 | 0.036 | 0.04 | 0.025 | 0.019 | 0.03 | 2000-11-22 | 49.897 | 93.1322 | [6 empty] | 2004-02-28 00:14 | 67.2
2001-06-01 | 0.033 | 0.028 | 0.03 | 0.025 | 0.029 | 0.033 | 2000-11-23 | 51.459 | 93.1322 | [6 empty] | 2004-02-28 00:21 | 63.6
2001-06-02 | 0.036 | 0.036 | 0.032 | 0.029 | 0.033 | 0.029 | 2000-11-24 | 51.875 | 93.1322 | [6 empty] | 2004-02-29 00:07 | 70.4
2001-06-03 | 0.034 | 0.032 | 0.032 | 0.026 | 0.024 | 0.03 | 2000-11-25 | 51.407 | 93.1322 | [6 empty] | 2004-02-29 00:14 | 69.1
2001-06-04 | 0.033 | 0.029 | 0.024 | 0.025 | 0.021 | 0.033 | 2000-11-26 | 48.986 | 93.1322 | [6 empty] | 2004-02-29 00:21 | 65.4
2001-06-05 | 0.04 | 0.045 | 0.036 | 0.035 | 0.041 | 0.042 | 2000-11-27 | 46.122 | 93.1322 | [6 empty] | 2004-03-01 00:08 | 74.9
2001-06-06 | 0.038 | 0.042 | 0.034 | 0.031 | 0.032 | 0.037 | 2000-11-28 | 50.934 | 94.3192 | [6 empty] | 2004-03-01 00:14 | 68.5
2001-06-07 | 0.037 | 0.044 | 0.041 | 0.031 | 0.033 | 0.041 | 2000-11-29 | 51.345 | 94.3192 | [6 empty] | 2004-03-01 00:21 | 68.4
2001-06-08 | 0.043 | 0.046 | 0.035 | 0.033 | 0.031 | 0.04 | 2000-11-30 | 49.312 | 94.3192 | [6 empty] | 2004-03-02 00:07 | 69.2
2001-06-09 | 0.044 | 0.045 | 0.037 | 0.03 | 0.029 | 0.038 | 2000-12-01 | 51.777 | 94.3192 | [6 empty] | 2004-03-02 00:14 | 74.2
2001-06-10 | 0.039 | 0.041 | 0.038 | 0.03 | 0.028 | 0.038 | 2000-12-02 | 51.006 | 94.3192 | [6 empty] | 2004-03-02 00:21 | 65.7
2001-06-11 | 0.044 | 0.045 | 0.04 | 0.039 | 0.04 | 0.042 | 2000-12-03 | 50.268 | 94.3192 | [6 empty] | 2004-03-10 00:14 | 69.8
2001-06-12 | 0.042 | 0.044 | 0.036 | 0.026 | 0.027 | 0.034 | 2000-12-04 | 47.521 | 94.3192 | [6 empty] | 2004-03-10 00:21 | 69.2
2001-06-13 | 0.043 | 0.046 | 0.035 | 0.028 | 0.03 | 0.044 | 2000-12-05 | 51.673 | 93.994 | [6 empty] | 2004-03-11 00:13 | 69.5
2001-06-14 | 0.043 | 0.046 | 0.042 | 0.03 | 0.034 | 0.043 | 2000-12-06 | 52.287 | 93.994 | [6 empty] | 2004-03-11 00:21 | 70.3
2001-06-15 | 0.045 | 0.044 | 0.047 | 0.044 | 0.052 | 0.059 | 2000-12-07 | 50.443 | 93.994 | [6 empty] | 2004-03-12 00:08 | 68.1
2001-06-16 | 0.043 | 0.043 | 0.054 | 0.036 | 0.032 | 0.041 | 2000-12-08 | 50.668 | 93.994 | [6 empty] | 2004-03-12 00:15 | 68.4
2001-06-17 | 0.043 | 0.043 | 0.055 | 0.045 | 0.044 | 0.04 | 2000-12-09 | 51.556 | 93.994 | [6 empty] | 2004-03-12 00:21 | 71.4
2001-06-18 | 0.042 | 0.045 | 0.038 | 0.03 | 0.028 | 0.036 | 2000-12-10 | 49.967 | 93.994 | [6 empty] | 2004-03-13 00:07 | 68.9
2001-06-19 | 0.032 | 0.028 | 0.041 | 0.033 | 0.036 | 0.036 | 2000-12-11 | 47.506 | 93.994 | [6 empty] | 2004-03-13 00:14 | 67.9
2001-06-20 | 0.036 | 0.052 | 0.035 | 0.024 | 0.03 | 0.036 | 2000-12-12 | 50.288 | 94.1022 | [6 empty] | 2004-03-13 00:21 | 66.8
2001-06-21 | 0.036 | 0.041 | 0.04 | 0.037 | 0.037 | 0.038 | 2000-12-13 | 50.194 | 94.1022 | [6 empty] | 2004-03-14 00:07 | 69.6
2001-06-22 | 0.042 | 0.047 | 0.04 | 0.031 | 0.034 | 0.039 | 2000-12-14 | 49.727 | 94.1022 | [6 empty] | 2004-03-14 00:14 | 69.4
2001-06-23 | 0.041 | 0.045 | 0.04 | 0.038 | 0.04 | 0.039 | 2000-12-15 | 49.399 | 94.1022 | [6 empty] | 2004-03-15 00:07 | 68.7
2001-06-24 | 0.041 | 0.046 | 0.042 | 0.034 | 0.034 | 0.031 | 2000-12-16 | 48.656 | 94.1022 | [6 empty] | 2004-03-15 00:14 | 70.4
2001-06-25 | 0.031 | 0.032 | 0.034 | 0.018 | 0.023 | 0.025 | 2000-12-17 | 48.775 | 94.1022 | [6 empty] | 2004-03-15 00:21 | 67.5
2001-06-26 | 0.032 | 0.03 | 0.029 | 0.023 | 0.028 | 0.028 | 2000-12-18 | 45.746 | 94.1022 | [6 empty] | 2004-03-16 00:07 | 67
2001-06-27 | 0.025 | 0.034 | 0.03 | 0.025 | 0.03 | 0.03 | 2000-12-19 | 48.839 | 95.9401 | [6 empty] | 2004-03-16 00:13 | 69.3
2001-06-28 | 0.035 | 0.036 | 0.031 | 0.029 | 0.031 | 0.037 | 2000-12-20 | 41.884 | 95.9401 | [6 empty] | 2004-03-16 00:21 | 69.5
2001-06-29 | 0.04 | 0.039 | 0.037 | 0.03 | 0.031 | 0.041 | 2000-12-21 | 50.259 | 95.9401 | [6 empty] | 2004-03-17 00:07 | 69.9
2001-06-30 | 0.044 | 0.043 | 0.037 | 0.033 | 0.032 | 0.042 | 2000-12-22 | 46.302 | 95.9401 | [6 empty] | 2004-03-17 00:14 | 70.2
2001-07-01 | 0.045 | 0.045 | 0.037 | 0.038 | 0.037 | 0.041 | 2000-12-23 | 49.985 | 95.9401 | [6 empty] | 2004-03-17 00:21 | 68.6
2001-07-02 | 0.044 | 0.039 | 0.033 | 0.021 | 0.024 | 0.039 | 2000-12-24 | 49.174 | 95.9401 | [6 empty] | 2004-03-18 00:07 | 69.3
2001-07-03 | 0.043 | 0.042 | 0.04 | 0.027 | 0.031 | 0.029 | 2000-12-25 | 49.725 | 95.9401 | [6 empty] | 2004-03-18 00:14 | 70.1
2001-07-04 | 0.029 | 0.035 | 0.034 | 0.028 | 0.028 | 0.035 | 2000-12-26 | 50.219 | 93.0465 | [6 empty] | 2004-03-18 00:21 | 67.4
2001-07-05 | 0.035 | 0.046 | 0.038 | 0.032 | 0.032 | 0.04 | 2000-12-27 | 49.671 | 93.0465 | [6 empty] | 2004-03-19 00:07 | 69
2001-07-06 | 0.044 | 0.044 | 0.036 | 0.03 | 0.029 | 0.037 | 2000-12-28 | 48.431 | 93.0465 | [6 empty] | 2004-03-19 00:14 | 65.2
2001-07-07 | 0.044 | 0.045 | 0.038 | 0.031 | 0.031 | 0.033 | 2000-12-29 | 53.117 | 93.0465 | [6 empty] | 2004-03-19 00:21 | 65.4
2001-07-08 | 0.038 | 0.038 | 0.047 | 0.039 | 0.036 | 0.04 | 2000-12-30 | 38.928 | 93.0465 | [6 empty] | 2004-03-20 00:07 | 67.7
2001-07-09 | 0.04 | 0.04 | 0.039 | 0.024 | 0.022 | 0.036 | 2000-12-31 | 34.003 | 93.0465 | [6 empty] | 2004-03-20 00:14 | 67.3
2001-07-10 | 0.034 | 0.039 | 0.038 | 0.028 | 0.026 | 0.034 | 2001-01-01 | 35.255 | 93.0465 | [6 empty] | 2004-03-20 00:21 | 65.8
2001-07-11 | 0.048 | 0.054 | 0.042 | 0.022 | 0.03 | 0.035 | 2001-01-02 | 31.332 | 91.9602 | [6 empty] | 2004-03-21 00:07 | 68.3
2001-07-12 | 0.044 | 0.042 | 0.034 | 0.021 | 0.027 | 0.031 | 2001-01-03 | 20.454 | 91.9602 | [6 empty] | 2004-03-21 00:14 | 65
2001-07-13 | 0.04 | 0.039 | 0.034 | 0.024 | 0.031 | 0.033 | 2001-01-04 | 11.677 | 91.9602 | [6 empty] | 2004-03-21 00:21 | 66.5
2001-07-14 | 0.038 | 0.039 | 0.034 | 0.026 | 0.028 | 0.033 | 2001-01-05 | 24.266 | 91.9602 | [6 empty] | 2004-03-22 00:14 | 70.3
2001-07-15 | 0.038 | 0.038 | 0.03 | 0.026 | 0.022 | 0.029 | 2001-01-06 | 35.009 | 91.9602 | [6 empty] | 2004-03-22 00:21 | 66
2001-07-16 | 0.033 | 0.035 | 0.032 | 0.025 | 0.022 | 0.031 | 2001-01-07 | 34.849 | 91.9602 | [6 empty] | 2004-03-23 00:07 | 66.5
2001-07-17 | 0.036 | 0.037 | 0.034 | 0.032 | 0.034 | 0.031 | 2001-01-08 | 38.701 | 91.9602 | [6 empty] | 2004-03-23 00:14 | 68.5
2001-07-18 | 0.036 | 0.037 | 0.037 | 0.026 | 0.029 | 0.037 | 2001-01-09 | 41.024 | 94.7109 | [6 empty] | 2004-03-23 00:21 | 66.8
2001-07-19 | 0.04 | 0.044 | 0.036 | 0.031 | 0.03 | 0.036 | 2001-01-10 | 44.499 | 94.7109 | [6 empty] | 2004-03-24 00:07 | 65.9
2001-07-20 | 0.04 | 0.046 | 0.038 | 0.032 | 0.033 | 0.035 | 2001-01-11 | 40.897 | 94.7109 | [6 empty] | 2004-03-24 00:14 | 66.9
2001-07-21 | 0.042 | 0.04 | 0.037 | 0.032 | 0.031 | 0.04 | 2001-01-12 | 47.863 | 94.7109 | [6 empty] | 2004-03-24 00:21 | 65.2
2001-07-22 | 0.044 | 0.046 | 0.037 | 0.028 | 0.022 | 0.039 | 2001-01-13 | 49.692 | 94.7109 | [6 empty] | 2004-03-25 00:07 | 64.8
2001-07-23 | 0.04 | 0.038 | 0.04 | 0.035 | 0.036 | 0.043 | 2001-01-14 | 48.735 | 94.7109 | [6 empty] | 2004-03-25 00:13 | 66
2001-07-24 | 0.043 | 0.042 | 0.039 | 0.031 | 0.038 | 0.043 | 2001-01-15 | 45.758 | 94.7109 | [6 empty] | 2004-03-25 00:21 | 64.7
2001-07-25 | 0.041 | 0.042 | 0.038 | 0.032 | 0.033 | 0.043 | 2001-01-16 | 49.118 | 91.9814 | [6 empty] | 2004-03-26 00:08 | 64.9
2001-07-26 | 0.045 | 0.045 | 0.042 | 0.042 | 0.035 | 0.039 | 2001-01-17 | 44.676 | 91.9814 | [6 empty] | 2004-03-26 00:14 | 65.6
2001-07-27 | 0.048 | 0.046 | 0.045 | 0.029 | 0.032 | 0.035 | 2001-01-18 | 48.076 | 91.9814 | [6 empty] | 2004-03-26 00:21 | 63.9
2001-07-28 | 0.046 | 0.044 | 0.043 | 0.029 | 0.027 | 0.03 | 2001-01-19 | 42.259 | 91.9814 | [6 empty] | 2004-03-27 00:08 | 65.9
2001-07-29 | 0.036 | 0.04 | 0.042 | 0.033 | 0.031 | 0.032 | 2001-01-20 | 45.51 | 91.9814 | [6 empty] | 2004-03-27 00:14 | 65.9
2001-07-30 | 0.041 | 0.039 | 0.04 | 0.033 | 0.031 | 0.042 | 2001-01-21 | 48.661 | 91.9814 | [6 empty] | 2004-03-27 00:21 | 64.1
2001-07-31 | 0.042 | 0.044 | 0.038 | 0.026 | 0.025 | 0.042 | 2001-01-22 | 49.189 | 91.9814 | [6 empty] | 2004-03-28 | 64.2
2001-08-01 | 0.043 | 0.046 | 0.032 | 0.028 | 0.034 | 0.037 | 2001-01-23 | 45.214 | 97.3419 | [6 empty] | 2004-03-28 00:21 | 64.2
2001-08-02 | 0.04 | 0.039 | 0.042 | 0.03 | 0.031 | 0.034 | 2001-01-24 | 44.086 | 97.3419 | [6 empty] | 2004-03-29 00:07 | 65.8
2001-08-03 | 0.045 | 0.049 | 0.04 | 0.032 | 0.037 | 0.041 | 2001-01-25 | 44.763 | 97.3419 | [6 empty] | 2004-03-29 00:14 | 66
2001-08-04 | 0.043 | 0.042 | 0.039 | 0.033 | 0.035 | 0.038 | 2001-01-26 | 44.099 | 97.3419 | [6 empty] | 2004-03-29 00:21 | 63.6
2001-08-05 | 0.041 | 0.044 | 0.042 | 0.032 | 0.034 | 0.035 | 2001-01-27 | 44.099 | 97.3419 | [6 empty] | 2004-03-30 00:14 | 65.6
2001-08-06 | 0.041 | 0.042 | 0.029 | 0.021 | 0.029 | 0.039 | 2001-01-28 | 43.738 | 97.3419 | [6 empty] | 2004-03-30 00:21 | 64.3
2001-08-07 | 0.041 | 0.044 | 0.045 | 0.024 | 0.042 | 0.051 | 2001-01-29 | 37.506 | 97.3419 | [6 empty] | 2004-03-31 00:07 | 64.4
2001-08-08 | 0.05 | 0.049 | 0.04 | 0.033 | 0.031 | 0.036 | 2001-01-30 | 44.698 | 97.3419 | [6 empty] | 2004-03-31 00:13 | 66.2
2001-08-09 | 0.045 | 0.046 |  |  | 0.029 | 0.036 | 2001-01-31 | 43.161 | 97.3419 | [6 empty] | 2004-04-01 00:07 | 63.2
2001-08-10 | 0.043 | 0.044 |  | 0.037 | 0.043 | 0.042 | 2001-02-01 | 43.349 | 97.3419 | [6 empty] | 2004-04-01 00:14 | 66.6
2001-08-11 | 0.042 | 0.043 | 0.043 | 0.031 | 0.03 | 0.039 | 2001-02-02 | 43.413 | 97.3419 | [6 empty] | 2004-04-01 00:21 | 66.5
2001-08-12 | 0.043 | 0.045 | 0.049 | 0.042 | 0.04 | 0.042 | 2001-02-03 | 43.76 | 97.3419 | [6 empty] | 2004-04-02 00:07 | 63.3
2001-08-13 | 0.046 | 0.045 | 0.042 | 0.04 | 0.038 | 0.043 | 2001-02-04 | 42.389 | 97.3419 | [6 empty] | 2004-04-02 00:14 | 66.6
2001-08-14 | 0.044 | 0.051 | 0.045 | 0.028 | 0.033 | 0.051 | 2001-02-05 | 39.325 | 97.3419 | [6 empty] | 2004-04-02 00:21 | 65.7
2001-08-15 | 0.049 | 0.048 | 0.04 | 0.027 | 0.03 | 0.039 | 2001-02-06 | 42.399 | 97.3419 | [6 empty] | 2004-04-03 00:07 | 65.2
2001-08-16 | 0.041 | 0.04 | 0.043 | 0.032 | 0.039 | 0.04 | 2001-02-07 | 41.723 | 97.3419 | [6 empty] | 2004-04-03 00:14 | 66.2
2001-08-17 | 0.04 | 0.045 | 0.043 | 0.036 | 0.037 | 0.041 | 2001-02-08 | 37.876 | 97.3419 | [6 empty] | 2004-04-03 00:21 | 65.9
2001-08-18 | 0.042 | 0.044 | 0.044 | 0.031 | 0.03 | 0.032 | 2001-02-09 | 27.463 | 97.3419 | [6 empty] | 2004-04-04 00:07 | 69.3
2001-08-19 | 0.04 | 0.042 | 0.04 | 0.031 | 0.032 | 0.042 | 2001-02-10 | 19.047 | 97.3419 | [6 empty] | 2004-04-04 00:14 | 70.7
2001-08-20 | 0.046 | 0.045 | 0.04 | 0.028 | 0.025 | 0.032 | 2001-02-11 | 16.028 | 97.3419 | [6 empty] | 2004-04-04 00:21 | 68.6
2001-08-21 | 0.036 | 0.045 | 0.041 | 0.026 | 0.024 | 0.037 | 2001-02-12 | 0 | 97.3419 | [6 empty] | 2004-04-05 00:07 | 68
2001-08-22 | 0.041 | 0.036 | 0.037 | 0.026 | 0.033 | 0.041 | 2001-02-13 | 0 | 97.3419 | [6 empty] | 2004-04-05 00:14 | 69.4
2001-08-23 | 0.045 | 0.046 | 0.032 | 0.043 | 0.036 | 0.042 | 2001-02-14 | 0 | 97.3419 | [6 empty] | 2004-04-05 00:21 | 68.9
2001-08-24 | 0.049 | 0.044 | 0.049 | 0.031 | 0.038 | 0.035 | 2001-02-15 | 0 | 97.3419 | [6 empty] | 2004-04-06 00:08 | 71.5
2001-08-25 | 0.044 | 0.047 | 0.046 | 0.044 | 0.024 | 0.034 | 2001-02-16 | 19.531 | 97.3419 | [6 empty] | 2004-04-06 00:14 | 66.3
2001-08-26 | 0.045 | 0.043 | 0.049 | 0.042 | 0.048 | 0.042 | 2001-02-17 | 32.988 | 97.3419 | [6 empty] | 2004-04-06 00:21 | 64.4
2001-08-27 | 0.046 | 0.047 | 0.055 | 0.048 | 0.053 | 0.042 | 2001-02-18 | 33.498 | 97.3419 | [6 empty] | 2004-04-07 00:07 | 69.6
2001-08-28 | 0.043 | 0.045 | 0.045 | 0.035 | 0.037 | 0.038 | 2001-02-19 | 35.261 | 97.3419 | [6 empty] | 2004-04-07 00:14 | 69.4
2001-08-29 | 0.04 | 0.04 | 0.035 | 0.024 | 0.027 | 0.03 | 2001-02-20 | 35.208 | 92.0874 | [6 empty] | 2004-04-07 00:21 | 68.9
2001-08-30 | 0.043 | 0.045 | 0.04 | 0.029 | 0.029 | 0.039 | 2001-02-21 | 39.058 | 92.0874 | [6 empty] | 2004-04-08 00:07 | 71.1
2001-08-31 | 0.04 | 0.042 | 0.042 | 0.039 | 0.027 | 0.037 | 2001-02-22 | 36.194 | 92.0874 | [6 empty] | 2004-04-08 00:14 | 71.4
2001-09-01 | 0.041 | 0.046 | 0.043 | 0.04 | 0.04 | 0.033 | 2001-02-23 | 36.716 | 92.0874 | [6 empty] | 2004-04-08 00:21 | 69
2001-09-02 | 0.042 | 0.043 | 0.043 | 0.038 | 0.034 | 0.039 | 2001-02-24 | 37.243 | 92.0874 | [6 empty] | 2004-04-09 00:07 | 65.5
2001-09-03 | 0.039 | 0.045 | 0.043 | 0.04 | 0.03 | 0.031 | 2001-02-25 | 37.804 | 92.0874 | [6 empty] | 2004-04-09 00:14 | 68.9
2001-09-04 | 0.038 | 0.034 | 0.038 | 0.034 | 0.028 | 0.033 | 2001-02-26 | 36.352 | 92.0874 | [6 empty] | 2004-04-09 00:21 | 67
2001-09-05 | 0.043 | 0.041 | 0.038 | 0.028 | 0.028 | 0.031 | 2001-02-27 | 38.645 | 93.7778 | [6 empty] | 2004-04-10 00:08 | 67.6
2001-09-06 | 0.042 | 0.042 | 0.04 | 0.031 | 0.029 | 0.033 | 2001-02-28 | 40.089 | 93.7778 | [6 empty] | 2004-04-10 00:14 | 67.5
2001-09-07 | 0.048 | 0.043 | 0.041 | 0.028 | 0.029 | 0.035 | 2001-03-01 | 41.619 | 93.7778 | [6 empty] | 2004-04-10 00:21 | 66.2
2001-09-08 | 0.044 | 0.046 | 0.042 | 0.026 | 0.027 | 0.036 | 2001-03-02 | 38.129 | 93.7778 | [6 empty] | 2004-04-11 00:07 | 67.8
2001-09-09 | 0.046 | 0.047 | 0.04 | 0.032 | 0.032 | 0.042 | 2001-03-03 | 40.127 | 93.7778 | [6 empty] | 2004-04-11 00:14 | 69
2001-09-10 | 0.043 | 0.047 | 0.04 | 0.033 | 0.052 | 0.057 | 2001-03-04 | 39.324 | 93.7778 | [6 empty] | 2004-04-11 00:21 | 68.8
2001-09-11 | 0.054 | 0.064 | 0.053 | 0.039 | 0.041 | 0.04 | 2001-03-05 | 36.898 | 93.7778 | [6 empty] | 2004-04-12 00:14 | 69.7
2001-09-12 | 0.049 | 0.057 | 0.045 | 0.034 | 0.027 | 0.035 | 2001-03-06 | 42.277 | 94.3844 | [6 empty] | 2004-04-12 00:21 | 66.6
2001-09-13 | 0.04 | 0.043 | 0.037 | 0.027 | 0.031 | 0.036 | 2001-03-07 | 41.909 | 94.3844 | [6 empty] | 2004-04-13 00:07 | 67.2
2001-09-14 | 0.041 | 0.046 | 0.042 | 0.039 | 0.029 | 0.038 | 2001-03-08 | 42.298 | 94.3844 | [6 empty] | 2004-04-13 00:14 | 68.4
2001-09-15 | 0.041 | 0.041 | 0.039 | 0.029 | 0.026 | 0.035 | 2001-03-09 | 40.644 | 94.3844 | [6 empty] | 2004-04-13 00:21 | 65.7
2001-09-16 | 0.039 | 0.038 | 0.037 | 0.023 | 0.024 | 0.033 | 2001-03-10 | 41.222 | 94.3844 | [6 empty] | 2004-04-14 00:07 | 65.9
2001-09-17 | 0.036 | 0.037 | 0.039 | 0.031 | 0.022 | 0.021 | 2001-03-11 | 41.448 | 94.3844 | [6 empty] | 2004-04-14 00:14 | 67.8
2001-09-18 | 0.024 | 0.023 | 0.036 | 0.032 | 0.03 | 0.035 | 2001-03-12 | 44.422 | 94.3844 | [6 empty] | 2004-04-14 00:21 | 67.4
2001-09-19 | 0.04 | 0.044 | 0.042 | 0.031 | 0.028 | 0.03 | 2001-03-13 | 42.311 | 95.6093 | [6 empty] | 2004-04-15 00:07 | 66.5
2001-09-20 | 0.038 | 0.038 | 0.038 | 0.034 | 0.032 | 0.037 | 2001-03-14 | 41.941 | 95.6093 | [6 empty] | 2004-04-15 00:13 | 68.2
2001-09-21 | 0.036 | 0.039 | 0.035 | 0.025 | 0.022 | 0.032 | 2001-03-15 | 41.504 | 95.6093 | [6 empty] | 2004-04-15 00:21 | 65.6
2001-09-22 | 0.037 | 0.041 | 0.035 | 0.027 | 0.026 | 0.028 | 2001-03-16 | 41.45 | 95.6093 | [6 empty] | 2004-04-16 00:07 | 66.1
2001-09-23 | 0.035 | 0.044 | 0.034 | 0.023 | 0.022 | 0.028 | 2001-03-17 | 42.564 | 95.6093 | [6 empty] | 2004-04-16 00:14 | 67.2
2001-09-24 | 0.037 | 0.044 | 0.035 | 0.028 |  |  | 2001-03-18 | 40.797 | 95.6093 | [6 empty] | 2004-04-16 00:21 | 65.3
2001-09-25 | 0.038 | [5 empty] | 2001-03-19 | 38.22 | 95.6093 | [6 empty] | 2004-04-17 00:08 | 66.5
2001-09-26 | 0.042 |  |  | 0.025 |  |  | 2001-03-20 | 42.129 | 95.1262 | [6 empty] | 2004-04-17 00:14 | 66
2001-09-27 | 0.04 |  |  | 0.03 |  |  | 2001-03-21 | 43.152 | 95.1262 | [6 empty] | 2004-04-17 00:21 | 65.1
2001-09-28 | 0.036 |  |  | 0.029 |  |  | 2001-03-22 | 42.124 | 95.1262 | [6 empty] | 2004-04-18 00:07 | 67.3
2001-09-29 | 0.036 |  |  | 0.026 |  |  | 2001-03-23 | 41.109 | 95.1262 | [6 empty] | 2004-04-18 00:14 | 67.4
2001-09-30 | 0.037 |  |  | 0.028 |  |  | 2001-03-24 | 40.745 | 95.1262 | [6 empty] | 2004-04-18 00:21 | 65.8
2001-10-01 | 0.037 |  |  | 0.032 |  |  | 2001-03-25 | 39.732 | 95.1262 | [6 empty] | 2004-04-19 00:08 | 67
2001-10-02 | 0.036 |  |  | 0.033 |  |  | 2001-03-26 | 41.647 | 95.1262 | [6 empty] | 2004-04-19 00:14 | 67.5
2001-10-03 | 0.043 |  |  | 0.028 |  |  | 2001-03-27 | 42.747 | 98.4464 | [6 empty] | 2004-04-19 00:21 | 64
2001-10-04 | 0.037 |  |  | 0.03 |  |  | 2001-03-28 | 44.459 | 98.4464 | [6 empty] | 2004-04-20 00:07 | 66.1
2001-10-05 | 0.039 |  |  | 0.03 |  |  | 2001-03-29 | 44.299 | 98.4464 | [6 empty] | 2004-04-20 00:13 | 68
2001-10-06 | 0.042 |  |  | 0.035 |  |  | 2001-03-30 | 42.154 | 98.4464 | [6 empty] | 2004-04-20 00:21 | 66.6
2001-10-07 | 0.039 |  |  | 0.037 |  |  | 2001-03-31 | 43.006 | 98.4464 | [6 empty] | 2004-04-21 00:07 | 67.8
2001-10-08 | 0.041 |  |  | 0.03 |  |  | 2001-04-01 | 41.094 | 98.4464 | [6 empty] | 2004-04-21 00:14 | 68.3
2001-10-09 | 0.037 |  |  | 0.028 |  |  | 2001-04-02 | 44.075 | 98.4464 | [6 empty] | 2004-04-21 00:21 | 66.7
2001-10-10 | 0.04 |  |  | 0.039 |  |  | 2001-04-03 | 44.484 | 94.7109 | [6 empty] | 2004-04-22 00:07 | 67
2001-10-11 | 0.041 |  |  | 0.044 |  |  | 2001-04-04 | 44.325 | 94.7109 | [6 empty] | 2004-04-22 00:14 | 67.4
2001-10-12 | 0.043 |  |  | 0.035 |  |  | 2001-04-05 | 43.068 | 94.7109 | [6 empty] | 2004-04-22 00:21 | 66.7
2001-10-13 | 0.043 |  |  | 0.029 |  |  | 2001-04-06 | 43.549 | 94.7109 | [6 empty] | 2004-04-23 00:07 | 66.9
2001-10-14 | 0.038 |  |  | 0.035 |  |  | 2001-04-07 | 43.95 | 94.7109 | [6 empty] | 2004-04-23 00:14 | 67.6
2001-10-15 | 0.041 |  |  | 0.044 |  |  | 2001-04-08 | 44.028 | 94.7109 | [6 empty] | 2004-04-23 00:21 | 65.6
2001-10-16 | 0.042 |  |  | 0.04 |  |  | 2001-04-09 | 40.741 | 94.7109 | [6 empty] | 2004-04-24 00:08 | 67.3
2001-10-17 | 0.079 |  |  | 0.039 |  |  | 2001-04-10 | 42.958 | 93.6052 | [6 empty] | 2004-04-24 00:14 | 67.6
2001-10-18 | 0.059 |  |  | 0.046 |  |  | 2001-04-11 | 43.664 | 93.6052 | [6 empty] | 2004-04-24 00:21 | 66
2001-10-19 | 0.052 |  |  | 0.034 |  |  | 2001-04-12 | 43.914 | 93.6052 | [6 empty] | 2004-04-25 00:08 | 68.2
2001-10-20 | 0.042 |  |  | 0.032 |  |  | 2001-04-13 | 42.519 | 93.6052 | [6 empty] | 2004-04-25 00:14 | 69
2001-10-21 | 0.041 |  |  | 0.03 |  |  | 2001-04-14 | 43.117 | 93.6052 | [6 empty] | 2004-04-25 00:21 | 66.7
2001-10-22 | 0.05 |  |  | 0.032 |  |  | 2001-04-15 | 43.911 | 93.6052 | [6 empty] | 2004-04-26 00:07 | 68.6
2001-10-23 | 0.028 |  |  | 0.033 |  |  | 2001-04-16 | 40.829 | 93.6052 | [6 empty] | 2004-04-26 00:14 | 70.3
2001-10-24 | 0.046 |  |  | 0.027 |  |  | 2001-04-17 | 42.559 | 95.5652 | [6 empty] | 2004-04-26 00:21 | 63.4
2001-10-25 | 0.085 |  |  | 0.06 |  |  | 2001-04-18 | 38.84 | 95.5652 | [6 empty] | 2004-04-27 00:07 | 65.2
2001-10-26 | 0.037 |  |  | 0.02 |  |  | 2001-04-19 | 44.128 | 95.5652 | [6 empty] | 2004-04-27 00:14 | 66.8
2001-10-27 | 0.038 |  |  | 0.025 |  |  | 2001-04-20 | 40.217 | 95.5652 | [6 empty] | 2004-04-27 00:21 | 66
2001-10-28 | 0.039 |  |  | 0.021 |  |  | 2001-04-21 | 44.501 | 95.5652 | [6 empty] | 2004-04-28 00:07 | 67.4
2001-10-29 | 0.034 |  |  | 0.03 |  |  | 2001-04-22 | 43.296 | 95.5652 | [6 empty] | 2004-04-28 00:14 | 68.7
2001-10-30 | 0.046 |  |  | 0.02 |  |  | 2001-04-23 | 42.154 | 95.5652 | [6 empty] | 2004-04-28 00:21 | 67.3
2001-10-31 | 0.048 |  |  | 0.039 |  |  | 2001-04-24 | 42.758 | 94.8855 | [6 empty] | 2004-04-29 00:07 | 67.2
2001-11-01 | 0.04 |  |  | 0.031 |  |  | 2001-04-25 | 43.146 | 94.8855 | [6 empty] | 2004-04-29 00:14 | 67.8
2001-11-02 | 0.055 |  |  | 0.042 |  |  | 2001-04-26 | 42.933 | 94.8855 | [6 empty] | 2004-04-30 07:30 | 64.5
2001-11-03 | 0.05 |  |  | 0.035 |  |  | 2001-04-27 | 41.744 | 94.8855 | [6 empty] | 2004-04-30 13:30 | 65.7
2001-11-04 | 0.043 |  |  | 0.028 |  |  | 2001-04-28 | 43.294 | 94.8855 | [6 empty] | 2004-04-30 21:00 | 65.1
2001-11-05 | 0.04 |  |  | 0.035 |  |  | 2001-04-29 | 43.672 | 94.8855 | [6 empty] | 2004-05-01 07:40 | 67
2001-11-06 | 0.045 |  |  | 0.029 |  |  | 2001-04-30 | 43.567 | 94.8855 | [6 empty] | 2004-05-01 13:30 | 66.8
2001-11-07 | 0.036 |  |  | 0.03 |  |  | 2001-05-01 | 44.739 | 94.2323 | [6 empty] | 2004-05-01 21:00 | 64.6
2001-11-08 | 0.039 |  |  | 0.037 |  |  | 2001-05-02 | 42.752 | 94.2323 | [6 empty] | 2004-05-02 06:51 | 67.3
2001-11-09 | 0.04 |  |  | 0.038 |  |  | 2001-05-03 | 46.109 | 94.2323 | [6 empty] | 2004-05-02 13:30 | 67.6
2001-11-10 | 0.044 |  |  | 0.026 |  |  | 2001-05-04 | 52.77 | 94.2323 | [6 empty] | 2004-05-02 21:00 | 65.8
2001-11-11 | 0.042 |  |  | 0.044 |  |  | 2001-05-05 | 46.197 | 94.2323 | [6 empty] | 2004-05-03 07:48 | 67.3
2001-11-12 | 0.046 |  |  | 0.031 |  |  | 2001-05-06 | 42.191 | 94.2323 | [6 empty] | 2004-05-03 13:30 | 68.2
2001-11-13 | 0.04 |  |  | 0.026 |  |  | 2001-05-07 | 44.482 | 94.2323 | [6 empty] | 2004-05-03 21:00 | 65.1
2001-11-14 | 0.035 |  |  | 0.031 |  |  | 2001-05-08 | 45.2 | 95.0605 | [6 empty] | 2004-05-04 07:43 | 65.8
2001-11-15 | 0.04 |  |  | 0.032 |  |  | 2001-05-09 | 44.96 | 95.0605 | [6 empty] | 2004-05-04 14:20 | 67
2001-11-16 | 0.041 |  |  | 0.033 |  |  | 2001-05-10 | 49.241 | 95.0605 | [6 empty] | 2004-05-04 21:00 | 65.2
2001-11-17 | 0.044 |  |  | 0.036 |  |  | 2001-05-11 | 52.769 | 95.0605 | [6 empty] | 2004-05-05 07:22 | 66.6
2001-11-18 | 0.045 |  |  | 0.035 |  |  | 2001-05-12 | 55.238 | 95.0605 | [6 empty] | 2004-05-05 13:20 | 67.6
2001-11-19 | 0.046 |  |  | 0.045 |  |  | 2001-05-13 | 54.981 | 95.0605 | [6 empty] | 2004-05-05 21:00 | 64.8
2001-11-20 | 0.035 |  |  | 0.021 |  |  | 2001-05-14 | 52.251 | 95.0605 | [6 empty] | 2004-05-06 07:03 | 66.4
2001-11-21 | 0.037 |  |  | 0.018 |  |  | 2001-05-15 | 54.747 | 94.9948 | [6 empty] | 2004-05-06 14:00 | 67.2
2001-11-22 | 0.039 |  |  | 0.03 |  |  | 2001-05-16 | 55.5 | 94.9948 | [6 empty] | 2004-05-06 21:00 | 65.7
2001-11-23 | 0.031 |  |  | 0.02 |  |  | 2001-05-17 | 56.298 | 94.9948 | [6 empty] | 2004-05-07 07:13 | 67.4
2001-11-24 | 0.029 |  |  | 0.034 |  |  | 2001-05-18 | 47.385 | 94.9948 | [6 empty] | 2004-05-07 13:30 | 68.4
2001-11-25 | 0.034 |  |  | 0.031 |  |  | 2001-05-19 | 49.908 | 94.9948 | [6 empty] | 2004-05-07 21:00 | 67.4
2001-11-26 | 0.031 |  |  | 0.025 |  |  | 2001-05-20 | 54.578 | 94.9948 | [6 empty] | 2004-05-08 07:23 | 68.2
2001-11-27 | 0.027 |  |  | 0.024 |  |  | 2001-05-21 | 51.939 | 94.9948 | [6 empty] | 2004-05-08 12:30 | 68.4
2001-11-28 | 0.033 |  |  | 0.032 |  |  | 2001-05-22 | 53.988 | 94.5584 | [6 empty] | 2004-05-08 21:00 | 65.7
2001-11-29 | 0.028 |  |  | 0.031 |  |  | 2001-05-23 | 54.166 | 94.5584 | [6 empty] | 2004-05-09 07:49 | 68.2
2001-11-30 | 0.036 |  |  | 0.026 |  |  | 2001-05-24 | 53.049 | 94.5584 | [6 empty] | 2004-05-09 13:30 | 68.2
2001-12-01 | 0.038 |  |  | 0.033 |  |  | 2001-05-25 | 53.783 | 94.5584 | [6 empty] | 2004-05-09 21:00 | 66.7
2001-12-02 | 0.034 |  |  | 0.037 |  |  | 2001-05-26 | 48.489 | 94.5584 | [6 empty] | 2004-05-10 06:45 | 67
2001-12-03 | 0.042 |  |  | 0.032 |  |  | 2001-05-27 | 46.78 | 94.5584 | [6 empty] | 2004-05-10 14:45 | 67.9
2001-12-04 | 0.034 | [5 empty] | 2001-05-28 | 44.713 | 94.5584 | [6 empty] | 2004-05-10 21:00 | 66.3
2001-12-05 | 0.039 |  |  | 0.03 |  |  | 2001-05-29 | 45.37 | 94.5584 | [6 empty] | 2004-05-11 07:18 | 67
2001-12-06 | 0.036 |  |  | 0.025 |  |  | 2001-05-30 | 51.122 | 94.5584 | [6 empty] | 2004-05-11 13:30 | 67.4
2001-12-07 | 0.036 |  |  | 0.034 |  |  | 2001-05-31 | 50.68 | 94.5584 | [6 empty] | 2004-05-11 21:00 | 64.6
2001-12-08 | 0.037 |  |  | 0.026 |  |  | 2001-06-01 | 49.676 | 94.5584 | [6 empty] | 2004-05-12 07:45 | 66.9
2001-12-09 | 0.037 |  |  | 0.036 |  |  | 2001-06-02 | 51.395 | 94.5584 | [6 empty] | 2004-05-12 13:30 | 68.1
2001-12-10 | 0.043 |  |  | 0.039 |  |  | 2001-06-03 | 50.46 | 94.5584 | [6 empty] | 2004-05-12 21:00 | 67.4
2001-12-11 | 0.042 |  |  | 0.025 |  |  | 2001-06-04 | 49.124 | 94.5584 | [6 empty] | 2004-05-13 07:05 | 68.6
2001-12-12 | 0.029 |  |  | 0.034 |  |  | 2001-06-05 | 54.318 | 95.1919 | [6 empty] | 2004-05-13 13:05 | 68.8
2001-12-13 | 0.037 |  |  | 0.041 |  |  | 2001-06-06 | 55.917 | 95.1919 | [6 empty] | 2004-05-13 21:00 | 67.2
2001-12-14 | 0.039 |  |  | 0.043 |  |  | 2001-06-07 | 52.716 | 95.1919 | [6 empty] | 2004-05-14 07:18 | 67.8
2001-12-15 | 0.04 |  |  | 0.031 |  |  | 2001-06-08 | 49.876 | 95.1919 | [6 empty] | 2004-05-14 13:40 | 67.7
2001-12-16 | 0.039 |  |  | 0.036 |  |  | 2001-06-09 | 48.761 | 95.1919 | [6 empty] | 2004-05-14 21:00 | 66.8
2001-12-17 | 0.037 |  |  | 0.031 |  |  | 2001-06-10 | 53.449 | 95.1919 | [6 empty] | 2004-05-15 07:40 | 67.8
2001-12-18 | 0.032 |  |  | 0.037 |  |  | 2001-06-11 | 47.446 | 95.1919 | [6 empty] | 2004-05-15 13:30 | 67.3
2001-12-19 | 0.034 |  |  | 0.031 |  |  | 2001-06-12 | 50.111 | 89.5571 | [6 empty] | 2004-05-15 21:00 | 65.8
2001-12-20 | 0.037 |  |  | 0.035 |  |  | 2001-06-13 | 53.327 | 89.5571 | [6 empty] | 2004-05-16 08:02 | 68
2001-12-21 | 0.039 |  |  | 0.027 |  |  | 2001-06-14 | 52.118 | 89.5571 | [6 empty] | 2004-05-16 13:30 | 68.5
2001-12-22 | 0.037 |  |  | 0.025 |  |  | 2001-06-15 | 51.079 | 89.5571 | [6 empty] | 2004-05-16 21:00 | 66.7
2001-12-23 | 0.037 |  |  | 0.027 |  |  | 2001-06-16 | 51.623 | 89.5571 | [6 empty] | 2004-05-17 07:18 | 68.1
2001-12-24 | 0.036 |  |  | 0.029 |  |  | 2001-06-17 | 50.438 | 89.5571 | [6 empty] | 2004-05-17 13:30 | 69.4
2001-12-25 | 0.037 |  |  | 0.027 |  |  | 2001-06-18 | 48.166 | 89.5571 | [6 empty] | 2004-05-17 21:00 | 66.1
2001-12-26 | 0.038 |  |  | 0.022 |  |  | 2001-06-19 | 49.999 | 94.82 | [6 empty] | 2004-05-18 07:15 | 67.1
2001-12-27 | 0.017 |  |  | 0.028 |  |  | 2001-06-20 | 51.587 | 94.82 | [6 empty] | 2004-05-18 13:30 | 67.4
2001-12-28 | 0.038 |  |  | 0.024 |  |  | 2001-06-21 | 48.213 | 94.82 | [6 empty] | 2004-05-18 21:00 | 65.9
2001-12-29 | 0.038 |  |  | 0.037 |  |  | 2001-06-22 | 48.717 | 94.82 | [6 empty] | 2004-05-19 06:26 | 66.8
2001-12-30 | 0.036 |  |  | 0.018 |  |  | 2001-06-23 | 51.187 | 94.82 | [6 empty] | 2004-05-19 13:30 | 67.3
2001-12-31 | 0.025 |  |  | 0.022 |  |  | 2001-06-24 | 51.138 | 94.82 | [6 empty] | 2004-05-19 21:00 | 65.2
2002-01-01 | 0.029 |  |  | 0.025 |  |  | 2001-06-25 | 46.9 | 94.82 | [6 empty] | 2004-05-20 07:14 | 65.8
2002-01-02 | 0.033 |  |  | 0.032 |  |  | 2001-06-26 | 47.473 | 90.2818 | [6 empty] | 2004-05-20 14:00 | 66.3
2002-01-03 | 0.035 |  |  | 0.036 |  |  | 2001-06-27 | 49.085 | 90.2818 | [6 empty] | 2004-05-20 21:00 | 64.5
2002-01-04 | 0.035 |  |  | 0.034 |  |  | 2001-06-28 | 48.127 | 90.2818 | [6 empty] | 2004-05-21 07:11 | 65.8
2002-01-05 | 0.037 |  |  | 0.026 |  |  | 2001-06-29 | 47.51 | 90.2818 | [6 empty] | 2004-05-21 13:30 | 66.5
2002-01-06 | 0.036 |  |  | 0.031 |  |  | 2001-06-30 | 48.178 | 90.2818 | [6 empty] | 2004-05-21 21:00 | 62.5
2002-01-07 | 0.033 |  |  | 0.041 |  |  | 2001-07-01 | 44.635 | 90.2818 | [6 empty] | 2004-05-22 07:35 | 65.3
2002-01-08 | 0.04 |  |  | 0.036 |  |  | 2001-07-02 | 53.743 | 90.2818 | [6 empty] | 2004-05-22 14:15 | 65.8
2002-01-09 | 0.035 |  |  | 0.041 |  |  | 2001-07-03 | 52.605 | 90.3649 | [6 empty] | 2004-05-22 21:00 | 64.2
2002-01-10 | 0.035 |  |  | 0.031 |  |  | 2001-07-04 | 53.117 | 90.3649 | [6 empty] | 2004-05-23 07:16 | 67.2
2002-01-11 | 0.023 |  |  | 0.032 |  |  | 2001-07-05 | 54.654 | 90.3649 | [6 empty] | 2004-05-23 13:30 | 66.7
2002-01-12 | 0.03 |  |  | 0.029 |  |  | 2001-07-06 | 47.997 | 90.3649 | [6 empty] | 2004-05-23 21:00 | 64.6
2002-01-13 | 0.031 |  |  | 0.031 |  |  | 2001-07-07 | 49.453 | 90.3649 | [6 empty] | 2004-05-24 07:17 | 67.9
2002-01-14 | 0.033 |  |  | 0.035 |  |  | 2001-07-08 | 49.215 | 90.3649 | [6 empty] | 2004-05-24 14:25 | 66
2002-01-15 | 0.036 | [5 empty] | 2001-07-09 | 46.627 | 90.3649 | [6 empty] | 2004-05-24 21:00 | 62.9
2002-01-16 | 0.032 |  |  | 0.038 |  |  | 2001-07-10 | 51.394 | 95.1919 | [6 empty] | 2004-05-25 07:15 | 63.1
2002-01-17 | 0.035 |  |  | 0.042 |  |  | 2001-07-11 | 47.939 | 95.1919 | [6 empty] | 2004-05-25 13:25 | 67.3
2002-01-18 | 0.041 |  |  | 0.029 |  |  | 2001-07-12 | 50.716 | 95.1919 | [6 empty] | 2004-05-25 21:00 | 68.6
2002-01-19 | 0.029 |  |  | 0.029 |  |  | 2001-07-13 | 50.237 | 95.1919 | [6 empty] | 2004-05-26 07:13 | 69.5
2002-01-20 | 0.02 |  |  | 0.038 |  |  | 2001-07-14 | 47.781 | 95.1919 | [6 empty] | 2004-05-26 13:49 | 65.5
2002-01-21 | 0.04 |  |  | 0.038 |  |  | 2001-07-15 | 50.034 | 95.1919 | [6 empty] | 2004-05-26 21:00 | 69
2002-01-22 | 0.041 |  |  | 0.035 |  |  | 2001-07-16 | 44.39 | 95.1919 | [6 empty] | 2004-05-27 07:14 | 66.3
2002-01-23 | 0.038 |  |  | 0.036 |  |  | 2001-07-17 | 49.743 | 99.3802 | [6 empty] | 2004-05-28 07:13 | 65.2
2002-01-24 | 0.038 |  |  | 0.043 |  |  | 2001-07-18 | 49.253 | 99.3802 | [6 empty] | 2004-05-28 14:15 | 67.2
2002-01-25 | 0.036 |  |  | 0.042 |  |  | 2001-07-19 | 50.202 | 99.3802 | [6 empty] | 2004-05-28 21:00 | 63.2
2002-01-26 | 0.034 |  |  | 0.028 |  |  | 2001-07-20 | 48.354 | 99.3802 | [6 empty] | 2004-05-29 07:23 | 66.1
2002-01-27 | 0.037 |  |  | 0.035 |  |  | 2001-07-21 | 48.304 | 99.3802 | [6 empty] | 2004-05-29 13:30 | 69.5
2002-01-28 | 0.036 |  |  | 0.038 |  |  | 2001-07-22 | 48.138 | 99.3802 | [6 empty] | 2004-05-29 21:00 | 63.2
2002-01-29 | 0.033 |  |  | 0.04 |  |  | 2001-07-23 | 45.147 | 99.3802 | [6 empty] | 2004-05-30 07:39 | 71
2002-01-30 | 0.035 |  |  | 0.038 |  |  | 2001-07-24 | 50.041 | 92.6403 | [6 empty] | 2004-05-30 13:30 | 70.7
2002-01-31 | 0.039 |  |  | 0.038 |  |  | 2001-07-25 | 49.518 | 92.6403 | [6 empty] | 2004-05-30 21:00 | 70
2002-02-01 | 0.039 |  |  | 0.039 |  |  | 2001-07-26 | 48.656 | 92.6403 | [6 empty] | 2004-05-31 07:14 | 69.3
2002-02-02 | 0.034 |  |  | 0.027 |  |  | 2001-07-27 | 48.076 | 92.6403 | [6 empty] | 2004-05-31 13:40 | 69.5
2002-02-03 | 0.035 |  |  | 0.032 |  |  | 2001-07-28 | 51.597 | 92.6403 | [6 empty] | 2004-05-31 21:00 | 73.78
2002-02-04 | 0.035 |  |  | 0.038 |  |  | 2001-07-29 | 50.546 | 92.6403 | [6 empty] | 2004-06-01 07:27 | 74.6
2002-02-05 | 0.035 |  |  | 0.03 |  |  | 2001-07-30 | 45.072 | 92.6403 | [6 empty] | 2004-06-01 13:30 | 75.31
2002-02-06 | 0.033 | [5 empty] | 2001-07-31 | 49.179 | 92.6403 | [6 empty] | 2004-06-01 21:00 | 73.14
2002-02-07 | 0.036 |  |  | 0.038 |  |  | 2001-08-01 | 50.089 | 92.6403 | [6 empty] | 2004-06-02 07:25 | 73.39
2002-02-08 | 0.04 |  |  | 0.037 |  |  | 2001-08-02 | 49.046 | 92.6403 | [6 empty] | 2004-06-02 13:30 | 72.33
2002-02-09 | 0.043 |  |  | 0.036 |  |  | 2001-08-03 | 50.777 | 92.6403 | [6 empty] | 2004-06-02 21:00 | 72.68
2002-02-10 | 0.03 |  |  | 0.038 |  |  | 2001-08-04 | 51.718 | 92.6403 | [6 empty] | 2004-06-03 07:19 | 72.6
2002-02-11 | 0.035 |  |  | 0.035 |  |  | 2001-08-05 | 51.646 | 92.6403 | [6 empty] | 2004-06-03 13:40 | 73.83
2002-02-12 | 0.034 |  |  | 0.028 |  |  | 2001-08-06 | 52.226 | 92.6403 | [6 empty] | 2004-06-03 21:00 | 70.17
2002-02-13 | 0.03 |  |  | 0.044 |  |  | 2001-08-07 | 45.033 | 92.3422 | [6 empty] | 2004-06-04 07:48 | 71.38
2002-02-14 | 0.038 |  |  | 0.029 |  |  | 2001-08-08 | 55.684 | 92.3422 | [6 empty] | 2004-06-04 14:10 | 78.41
2002-02-15 | 0.035 |  |  | 0.035 |  |  | 2001-08-09 | 47.568 | 92.3422 | [6 empty] | 2004-06-04 21:00 | 77.42
2002-02-16 | 0.037 |  |  | 0.027 |  |  | 2001-08-10 | 52.287 | 92.3422 | [6 empty] | 2004-06-05 07:35 | 74.92
2002-02-17 | 0.042 |  |  | 0.041 |  |  | 2001-08-11 | 51.109 | 92.3422 | [6 empty] | 2004-06-05 13:30 | 73.92
2002-02-18 | 0.038 |  |  | 0.03 |  |  | 2001-08-12 | 51.354 | 92.3422 | [6 empty] | 2004-06-05 21:00 | 73.35
2002-02-19 | 0.034 |  |  | 0.036 |  |  | 2001-08-13 | 47.905 | 92.3422 | [6 empty] | 2004-06-06 07:25 | 74.88
2002-02-20 | 0.039 |  |  | 0.037 |  |  | 2001-08-14 | 53.278 | 91.7698 | [6 empty] | 2004-06-06 14:25 | 74.9
2002-02-21 | 0.033 |  |  | 0.036 |  |  | 2001-08-15 | 51.109 | 91.7698 | [6 empty] | 2004-06-06 21:00 | 74.43
2002-02-22 | 0.035 |  |  | 0.038 |  |  | 2001-08-16 | 52.895 | 91.7698 | [6 empty] | 2004-06-07 07:10 | 74.71
2002-02-23 | 0.037 |  |  | 0.043 |  |  | 2001-08-17 | 52.098 | 91.7698 | [6 empty] | 2004-06-07 13:10 | 77
2002-02-24 | 0.038 |  |  | 0.037 |  |  | 2001-08-18 | 53.194 | 91.7698 | [6 empty] | 2004-06-07 21:00 | 73.73
2002-02-25 | 0.035 |  |  | 0.037 |  |  | 2001-08-19 | 50.146 | 91.7698 | [6 empty] | 2004-06-08 06:45 | 74.08
2002-02-26 | 0.033 |  |  | 0.028 |  |  | 2001-08-20 | 49.811 | 91.7698 | [6 empty] | 2004-06-08 13:30 | 74.49
2002-02-27 | 0.04 | [5 empty] | 2001-08-21 | 51.935 | 91.9179 | [6 empty] | 2004-06-08 21:00 | 69.6
[7 empty] | 2001-08-22 | 50.13 | 91.9179 | [6 empty] | 2004-06-09 06:50 | 69.4
[7 empty] | 2001-08-23 | 50.494 | 91.9179 | [6 empty] | 2004-06-09 14:50 | 67.3
[7 empty] | 2001-08-24 | 40.732 | 91.9179 | [6 empty] | 2004-06-09 21:00 | 65.4
[7 empty] | 2001-08-25 | 48.301 | 91.9179 | [6 empty] | 2004-06-10 06:40 | 64.6
[7 empty] | 2001-08-26 | 48.552 | 91.9179 | [6 empty] | 2004-06-10 15:50 | 66.1
[7 empty] | 2001-08-27 | 47.854 | 91.9179 | [6 empty] | 2004-06-10 21:00 | 66.7
[7 empty] | 2001-08-28 | 48.555 | 93.519 | [6 empty] | 2004-06-11 07:05 | 65.6
[7 empty] | 2001-08-29 | 51.069 | 93.519 | [6 empty] | 2004-06-11 13:30 | 66.3
[7 empty] | 2001-08-30 | 47.831 | 93.519 | [6 empty] | 2004-06-11 21:00 | 65.3
[7 empty] | 2001-08-31 | 47.909 | 93.519 | [6 empty] | 2004-06-12 07:40 | 66.7
[7 empty] | 2001-09-01 | 46.876 | 93.519 | [6 empty] | 2004-06-12 14:00 | 67.2
[7 empty] | 2001-09-02 | 48.536 | 93.519 | [6 empty] | 2004-06-12 21:00 | 66.3
[7 empty] | 2001-09-03 | 46.269 | 93.519 | [6 empty] | 2004-06-13 07:00 | 67.6
[7 empty] | 2001-09-04 | 50.687 | 89.1661 | [6 empty] | 2004-06-13 13:53 | 69.2
[7 empty] | 2001-09-05 | 53.318 | 89.1661 | [6 empty] | 2004-06-13 21:00 | 67.8
[7 empty] | 2001-09-06 | 48.233 | 89.1661 | [6 empty] | 2004-06-14 06:40 | 68.9
[7 empty] | 2001-09-07 | 49.988 | 89.1661 | [6 empty] | 2004-06-14 14:45 | 68.6
[7 empty] | 2001-09-08 | 47.903 | 89.1661 | [6 empty] | 2004-06-14 21:00 | 65.1
[7 empty] | 2001-09-09 | 50.239 | 89.1661 | [6 empty] | 2004-06-15 06:45 | 67.4
[7 empty] | 2001-09-10 | 47.671 | 89.1661 | [6 empty] | 2004-06-15 13:30 | 68.4
[7 empty] | 2001-09-11 | 51.852 | 90.803 | [6 empty] | 2004-06-15 21:00 | 68.5
[7 empty] | 2001-09-12 | 52.051 | 90.803 | [6 empty] | 2004-06-16 06:35 | 67.4
[7 empty] | 2001-09-13 | 51.928 | 90.803 | [6 empty] | 2004-06-16 13:40 | 68
[7 empty] | 2001-09-14 | 54.137 | 90.803 | [6 empty] | 2004-06-16 21:00 | 67.4
[7 empty] | 2001-09-15 | 50.892 | 90.803 | [6 empty] | 2004-06-17 06:50 | 67.6
[7 empty] | 2001-09-16 | 48.099 | 90.803 | [6 empty] | 2004-06-17 14:00 | 68.6
[7 empty] | 2001-09-17 | 50.679 | 90.803
[7 empty] | 2001-09-18 | 50.258 | 93.8642
[7 empty] | 2001-09-19 | 41.791 | 93.8642
[7 empty] | 2001-09-20 | 48.207 | 93.8642
[7 empty] | 2001-09-21 | 46.619 | 93.8642
[7 empty] | 2001-09-22 | 48.284 | 93.8642
[7 empty] | 2001-09-23 | 49.756 | 93.8642
[7 empty] | 2001-09-24 | 45.812 | 93.8642
[7 empty] | 2001-09-25 | 33.73 | 93.2395
[7 empty] | 2001-09-26 | 33.447 | 93.2395
[7 empty] | 2001-09-27 | 35.828 | 93.2395
[7 empty] | 2001-09-28 | 35.058 | 93.2395
[7 empty] | 2001-09-29 | 34.884 | 93.2395
[7 empty] | 2001-09-30 | 31.488 | 93.2395
[7 empty] | 2001-10-01 | 35.168 | 93.2395
[7 empty] | 2001-10-02 | 36.958 | 94.2323
[7 empty] | 2001-10-03 | 34.155 | 94.2323
[7 empty] | 2001-10-04 | 46.417 | 94.2323
[7 empty] | 2001-10-05 | 49.303 | 94.2323
[7 empty] | 2001-10-06 | 52.765 | 94.2323
[7 empty] | 2001-10-07 | 52.632 | 94.2323
[7 empty] | 2001-10-08 | 49.965 | 94.2323
[7 empty] | 2001-10-09 | 48.811 | 93.261
[7 empty] | 2001-10-10 | 48.819 | 93.261
[7 empty] | 2001-10-11 | 49.413 | 93.261
[7 empty] | 2001-10-12 | 47.349 | 93.261
[7 empty] | 2001-10-13 | 49.242 | 93.261
[7 empty] | 2001-10-14 | 48.34 | 93.261
[7 empty] | 2001-10-15 | 44.268 | 93.261
[7 empty] | 2001-10-16 | 47.84 | 94.1456
[7 empty] | 2001-10-17 | 45.578 | 94.1456
[7 empty] | 2001-10-18 | 48.631 | 94.1456
[7 empty] | 2001-10-19 | 47.117 | 94.1456
[7 empty] | 2001-10-20 | 49.312 | 94.1456
[7 empty] | 2001-10-21 | 47.59 | 94.1456
[7 empty] | 2001-10-22 | 38.693 | 94.1456
[7 empty] | 2001-10-23 | 38.772 | 94.3626
[7 empty] | 2001-10-24 | 40.296 | 94.3626
[7 empty] | 2001-10-25 | 46.418 | 94.3626
[7 empty] | 2001-10-26 | 48.478 | 94.3626
[7 empty] | 2001-10-27 | 46.425 | 94.3626
[7 empty] | 2001-10-28 | 49.706 | 94.3626
[7 empty] | 2001-10-29 | 40.512 | 94.3626
[7 empty] | 2001-10-30 | 48.058 | 94.3626
[7 empty] | 2001-10-31 | 46.008 | 94.3626
[7 empty] | 2001-11-01 | 49.663 | 94.3626
[7 empty] | 2001-11-02 | 46.941 | 94.3626
[7 empty] | 2001-11-03 | 49.627 | 94.3626
[7 empty] | 2001-11-04 | 46.73 | 94.3626
[7 empty] | 2001-11-05 | 41.787 | 94.3626
[7 empty] | 2001-11-06 | 41.368 | 94.3626
[7 empty] | 2001-11-07 | 50.298 | 94.3626
[7 empty] | 2001-11-08 | 43.683 | 94.3626
[7 empty] | 2001-11-09 | 48.129 | 94.3626
[7 empty] | 2001-11-10 | 47.831 | 94.3626
[7 empty] | 2001-11-11 | 44.806 | 94.3626
[7 empty] | 2001-11-12 | 47.211 | 94.3626
[7 empty] | 2001-11-13 | 45.25 | 93.476
[7 empty] | 2001-11-14 | 45.369 | 93.476
[7 empty] | 2001-11-15 | 47.128 | 93.476
[7 empty] | 2001-11-16 | 44.75 | 93.476
[7 empty] | 2001-11-17 | 45.925 | 93.476
[7 empty] | 2001-11-18 | 46.522 | 93.476
[7 empty] | 2001-11-19 | 40.738 | 93.476
[7 empty] | 2001-11-20 | 48.544 | 94.7545
[7 empty] | 2001-11-21 | 44.459 | 94.7545
[7 empty] | 2001-11-22 | 46.237 | 94.7545
[7 empty] | 2001-11-23 | 44.941 | 94.7545
[7 empty] | 2001-11-24 | 48.311 | 94.7545
[7 empty] | 2001-11-25 | 45.15 | 94.7545
[7 empty] | 2001-11-26 | 40.548 | 94.7545
[7 empty] | 2001-11-27 | 42.634 | 93.5621
[7 empty] | 2001-11-28 | 32.25 | 93.5621
[7 empty] | 2001-11-29 | 47.468 | 93.5621
[7 empty] | 2001-11-30 | 47.072 | 93.5621
[7 empty] | 2001-12-01 | 36.599 | 93.5621
[7 empty] | 2001-12-02 | 35.083 | 93.5621
[7 empty] | 2001-12-03 | 37.462 | 93.5621
[7 empty] | 2001-12-04 | 42.965 | 99.4718
[7 empty] | 2001-12-05 | 44.102 | 99.4718
[7 empty] | 2001-12-06 | 42.324 | 99.4718
[7 empty] | 2001-12-07 | 43.629 | 99.4718
[7 empty] | 2001-12-08 | 41.232 | 99.4718
[7 empty] | 2001-12-09 | 43.398 | 99.4718
[7 empty] | 2001-12-10 | 43.876 | 99.4718
[7 empty] | 2001-12-11 | 42.917 | 94.9948
[7 empty] | 2001-12-12 | 45.008 | 94.9948
[7 empty] | 2001-12-13 | 43.045 | 94.9948
[7 empty] | 2001-12-14 | 42.847 | 94.9948
[7 empty] | 2001-12-15 | 42.461 | 94.9948
[7 empty] | 2001-12-16 | 43.609 | 94.9948
[7 empty] | 2001-12-17 | 42.813 | 94.9948
[7 empty] | 2001-12-18 | 41.448 | 92.2996
[7 empty] | 2001-12-19 | 41.657 | 92.2996
[7 empty] | 2001-12-20 | 43.934 | 92.2996
[7 empty] | 2001-12-21 | 41.06 | 92.2996
[7 empty] | 2001-12-22 | 43.441 | 92.2996
[7 empty] | 2001-12-23 | 43.301 | 92.2996
[7 empty] | 2001-12-24 | 39.328 | 92.2996
[7 empty] | 2001-12-25 | 34.857 | 92.2996
[7 empty] | 2001-12-26 | 38.638 | 92.2996
[7 empty] | 2001-12-27 | 43.743 | 92.2996
[7 empty] | 2001-12-28 | 42.941 | 92.2996
[7 empty] | 2001-12-29 | 44.447 | 92.2996
[7 empty] | 2001-12-30 | 42.315 | 92.2996
[7 empty] | 2001-12-31 | 39.642 | 92.2996
[7 empty] | 2002-01-01 | 43.424 | 92.2996
[7 empty] | 2002-01-02 | 41.206 | 92.2996
[7 empty] | 2002-01-03 | 45.58 | 92.2996
[7 empty] | 2002-01-04 | 47.748 | 92.2996
[7 empty] | 2002-01-05 | 45.843 | 92.2996
[7 empty] | 2002-01-06 | 43.774 | 92.2996
[7 empty] | 2002-01-07 | 44.427 | 92.2996
[7 empty] | 2002-01-08 | 45.28 | 92.7897
[7 empty] | 2002-01-09 | 41.71 | 92.7897
[7 empty] | 2002-01-10 | 34.374 | 92.7897
[7 empty] | 2002-01-11 | 38.78 | 92.7897
[7 empty] | 2002-01-12 | 47.34 | 92.7897
[7 empty] | 2002-01-13 | 43.966 | 92.7897
[7 empty] | 2002-01-14 | 43.344 | 92.7897
[7 empty] | 2002-01-15 | 49.487 | 94.3409
[7 empty] | 2002-01-16 | 40.977 | 94.3409
[7 empty] | 2002-01-17 | 32.696 | 94.3409
[7 empty] | 2002-01-18 | 39.728 | 94.3409
[7 empty] | 2002-01-19 | 44.374 | 94.3409
[7 empty] | 2002-01-20 | 44.592 | 94.3409
[7 empty] | 2002-01-21 | 44.773 | 94.3409
[7 empty] | 2002-01-22 | 45.402 | 94.3409
[7 empty] | 2002-01-23 | 45.377 | 94.3409
[7 empty] | 2002-01-24 | 44.535 | 94.3409
[7 empty] | 2002-01-25 | 51.311 | 94.3409
[7 empty] | 2002-01-26 | 48.424 | 94.3409
[7 empty] | 2002-01-27 | 52.627 | 94.3409
[7 empty] | 2002-01-28 | 38.173 | 94.3409
[7 empty] | 2002-01-29 | 34.79 | 94.1673
[7 empty] | 2002-01-30 | 36.992 | 94.1673
[7 empty] | 2002-01-31 | 45.236 | 94.1673
[7 empty] | 2002-02-01 | 42.112 | 94.1673
[7 empty] | 2002-02-02 | 43.994 | 94.1673
[7 empty] | 2002-02-03 | 42.887 | 94.1673
[7 empty] | 2002-02-04 | 35.989 | 94.1673
[7 empty] | 2002-02-05 | 34.529 | 92.3209
[7 empty] | 2002-02-06 | 43.836 | 92.3209
[7 empty] | 2002-02-07 | 45.552 | 92.3209
[7 empty] | 2002-02-08 | 43.698 | 92.3209
[7 empty] | 2002-02-09 | 45.39 | 92.3209
[7 empty] | 2002-02-10 | 44.562 | 92.3209
[7 empty] | 2002-02-11 | 39.731 | 92.3209
[7 empty] | 2002-02-12 | 34.182 | 94.3626
[7 empty] | 2002-02-13 | 42.578 | 94.3626
[7 empty] | 2002-02-14 | 44.325 | 94.3626
[7 empty] | 2002-02-15 | 44.645 | 94.3626
[7 empty] | 2002-02-16 | 44.764 | 94.3626
[7 empty] | 2002-02-17 | 45.217 | 94.3626
[7 empty] | 2002-02-18 | 40.546 | 94.3626
[7 empty] | 2002-02-19 | 45.12 | 95.3016
[7 empty] | 2002-02-20 | 45.204 | 95.3016
[7 empty] | 2002-02-21 | 44.8 | 95.3016
[7 empty] | 2002-02-22 | 45.025 | 95.3016
[7 empty] | 2002-02-23 | 43.214 | 95.3016
[7 empty] | 2002-02-24 | 44.167 | 95.3016
[7 empty] | 2002-02-25 | 43.77 | 95.3016
[7 empty] | 2002-02-26 | 44.496 | 96.6941
[7 empty] | 2002-02-27 | 45.16 | 96.6941
[7 empty] | 2002-02-28 | 43.036 | 96.6941
[7 empty] | 2002-03-01 | 45.755 | 96.6941
[7 empty] | 2002-03-02 | 44.322 | 96.6941
[7 empty] | 2002-03-03 | 45.044 | 96.6941
[7 empty] | 2002-03-04 | 41.455 | 96.6941
[7 empty] | 2002-03-05 | 46.347 | 94.4061
[7 empty] | 2002-03-06 | 41.371 | 94.4061
[7 empty] | 2002-03-07 | 36.403 | 94.4061
[7 empty] | 2002-03-08 | 38.244 | 94.4061
[7 empty] | 2002-03-09 | 38.314 | 94.4061
[7 empty] | 2002-03-10 | 37.022 | 94.4061
[7 empty] | 2002-03-11 | 37.083 | 94.4061
[7 empty] | 2002-03-12 | 39.253 | 94.9511
[7 empty] | 2002-03-13 | 36.576 | 94.9511
[7 empty] | 2002-03-14 | 36.326 | 94.9511
[7 empty] | 2002-03-15 | 39.039 | 94.9511
[7 empty] | 2002-03-16 | 36.092 | 94.9511
[7 empty] | 2002-03-17 | 37.52 | 94.9511
[7 empty] | 2002-03-18 | 38.163 | 94.9511
[7 empty] | 2002-03-19 | 37.721 | 93.3039
[7 empty] | 2002-03-20 | 37.903 | 93.3039
[7 empty] | 2002-03-21 | 38.43 | 93.3039
[7 empty] | 2002-03-22 | 33.255 | 93.3039
[7 empty] | 2002-03-23 | 35.27 | 93.3039
[7 empty] | 2002-03-24 | 37.521 | 93.3039
[7 empty] | 2002-03-25 | 38.549 | 93.3039
[7 empty] | 2002-03-26 | 34.977 | 95.1919
[7 empty] | 2002-03-27 | 36.894 | 95.1919
[7 empty] | 2002-03-28 | 32.48 | 95.1919
[7 empty] | 2002-03-29 | 30.091 | 95.1919
[7 empty] | 2002-03-30 | 25.108 | 95.1919
[7 empty] | 2002-03-31 | 29.059 | 95.1919
[7 empty] | 2002-04-01 | 30.995 | 95.1919
[7 empty] | 2002-04-02 | 28.427 | 95.2138
[7 empty] | 2002-04-03 | 29.692 | 95.2138
[7 empty] | 2002-04-04 | 28.547 | 95.2138
[7 empty] | 2002-04-05 | 27.298 | 95.2138
[7 empty] | 2002-04-06 | 25.888 | 95.2138
[7 empty] | 2002-04-07 | 24.7 | 95.2138
[7 empty] | 2002-04-08 | 22.812 | 95.2138
[7 empty] | 2002-04-09 | 20.495 | 94.9948
[7 empty] | 2002-04-10 | 18.461 | 94.9948
[7 empty] | 2002-04-11 | 19.314 | 94.9948
[7 empty] | 2002-04-12 | 17.697 | 94.9948
[7 empty] | 2002-04-13 | 20.649 | 94.9948
[7 empty] | 2002-04-14 | 18.901 | 94.9948
[7 empty] | 2002-04-15 | 20.554 | 94.9948
[7 empty] | 2002-04-16 | 19.042 | 95.4113
[7 empty] | 2002-04-17 | 19.826 | 95.4113
[7 empty] | 2002-04-18 | 18.27 | 95.4113
[7 empty] | 2002-04-19 | 19.59 | 95.4113
[7 empty] | 2002-04-20 | 18.05 | 95.4113
[7 empty] | 2002-04-21 | 16.167 | 95.4113
[7 empty] | 2002-04-22 | 0.18 | 95.4113
[7 empty] | 2002-04-23 | 0 | 95.4113
[7 empty] | 2002-04-24 | 0 | 95.4113
[7 empty] | 2002-04-25 | 0 | 95.4113
[7 empty] | 2002-04-26 | 19.441 | 95.4113
[7 empty] | 2002-04-27 | 18.197 | 95.4113
[7 empty] | 2002-04-28 | 18.723 | 95.4113
[7 empty] | 2002-04-29 | 19.281 | 95.4113
[7 empty] | 2002-04-30 | 18.896 | 95.4113
[7 empty] | 2002-05-01 | 18.878 | 95.4113
[7 empty] | 2002-05-02 | 18.788 | 95.4113
[7 empty] | 2002-05-03 | 17.486 | 95.4113
[7 empty] | 2002-05-04 | 19.825 | 95.4113
[7 empty] | 2002-05-05 | 15.73 | 95.4113
[7 empty] | 2002-05-06 | 22.198 | 95.4113
[7 empty] | 2002-05-07 | 17.332 | 95.918
[7 empty] | 2002-05-08 | 17.17 | 95.918
[7 empty] | 2002-05-09 | 18.431 | 95.918
[7 empty] | 2002-05-10 | 18.504 | 95.918
[7 empty] | 2002-05-11 | 17.234 | 95.918
[7 empty] | 2002-05-12 | 15.268 | 95.918
[7 empty] | 2002-05-13 | 17.845 | 95.918
[7 empty] | 2002-05-14 | 19.948 | 94.8418
[7 empty] | 2002-05-15 | 16.81 | 94.8418
[7 empty] | 2002-05-16 | 18.311 | 94.8418
[7 empty] | 2002-05-17 | 15.564 | 94.8418
[7 empty] | 2002-05-18 | 37.855 | 94.8418
[7 empty] | 2002-05-19 | 19.921 | 94.8418
[7 empty] | 2002-05-20 | 16.077 | 94.8418
[7 empty] | 2002-05-21 | 20.714 | 95.6093
[7 empty] | 2002-05-22 | 17.957 | 95.6093
[7 empty] | 2002-05-23 | 15.566 | 95.6093
[7 empty] | 2002-05-24 | 19.011 | 95.6093
[7 empty] | 2002-05-25 | 17.207 | 95.6093
[7 empty] | 2002-05-26 | 17.844 | 95.6093
[7 empty] | 2002-05-27 | 20.213 | 95.6093
[7 empty] | 2002-05-28 | 22.917 | 95.0167
[7 empty] | 2002-05-29 | 17.878 | 95.0167
[7 empty] | 2002-05-30 | 24.322 | 95.0167
[7 empty] | 2002-05-31 | 20.847 | 95.0167
[7 empty] | 2002-06-01 | 18.21 | 95.0167
[7 empty] | 2002-06-02 | 19.334 | 95.0167
[7 empty] | 2002-06-03 | 18.269 | 95.0167
[7 empty] | 2002-06-04 | 20.644 | 93.6268
[7 empty] | 2002-06-05 | 19.7 | 93.6268
[7 empty] | 2002-06-06 | 19.765 | 93.6268
[7 empty] | 2002-06-07 | 19.582 | 93.6268
[7 empty] | 2002-06-08 | 20.066 | 93.6268
[7 empty] | 2002-06-09 | 19.052 | 93.6268
[7 empty] | 2002-06-10 | 19.346 | 93.6268
[7 empty] | 2002-06-11 | 31.86 | 94.3626
[7 empty] | 2002-06-12 | 18.023 | 94.3626
[7 empty] | 2002-06-13 | 22.45 | 94.3626
[7 empty] | 2002-06-14 | 22.853 | 94.3626
[7 empty] | 2002-06-15 | 18.291 | 94.3626
[7 empty] | 2002-06-16 | 19.095 | 94.3626
[7 empty] | 2002-06-17 | 19.837 | 94.3626
[7 empty] | 2002-06-18 | 20.76 | 95.9622
[7 empty] | 2002-06-19 | 16.203 | 95.9622
[7 empty] | 2002-06-20 | 21.084 | 95.9622
[7 empty] | 2002-06-21 | 19.355 | 95.9622
[7 empty] | 2002-06-22 | 18.547 | 95.9622
[7 empty] | 2002-06-23 | 20.658 | 95.9622
[7 empty] | 2002-06-24 | 22.398 | 95.9622
[7 empty] | 2002-06-25 | 27.006 | 94.4278
[7 empty] | 2002-06-26 | 25.693 | 94.4278
[7 empty] | 2002-06-27 | 26.299 | 94.4278
[7 empty] | 2002-06-28 | 21.276 | 94.4278
[7 empty] | 2002-06-29 | 17.198 | 94.4278
[7 empty] | 2002-06-30 | 17.622 | 94.4278
[7 empty] | 2002-07-01 | 20.702 | 94.4278
[7 empty] | 2002-07-02 | 23.329 | 95.0824
[7 empty] | 2002-07-03 | 27.033 | 95.0824
[7 empty] | 2002-07-04 | 19.616 | 95.0824
[7 empty] | 2002-07-05 | 20.612 | 95.0824
[7 empty] | 2002-07-06 | 19.237 | 95.0824
[7 empty] | 2002-07-07 | 20.083 | 95.0824
[7 empty] | 2002-07-08 | 22.605 | 95.0824
[7 empty] | 2002-07-09 | 25.199 | 93.0679
[7 empty] | 2002-07-10 | 21.68 | 93.0679
[7 empty] | 2002-07-11 | 19.826 | 93.0679
[7 empty] | 2002-07-12 | 21.42 | 93.0679
[7 empty] | 2002-07-13 | 36.281 | 93.0679
[7 empty] | 2002-07-14 | 26.22 | 93.0679
[7 empty] | 2002-07-15 | 22.09 | 93.0679
[7 empty] | 2002-07-16 | 19.489 | 93.8426
[7 empty] | 2002-07-17 | 18.954 | 93.8426
[7 empty] | 2002-07-18 | 22.759 | 93.8426
[7 empty] | 2002-07-19 | 20.858 | 93.8426
[7 empty] | 2002-07-20 | 20.576 | 93.8426
[7 empty] | 2002-07-21 | 18.35 | 93.8426
[7 empty] | 2002-07-22 | 24.054 | 93.8426
[7 empty] | 2002-07-23 | 22.38 | 95.2138
[7 empty] | 2002-07-24 | 23.174 | 95.2138
[7 empty] | 2002-07-25 | 19.487 | 95.2138
[7 empty] | 2002-07-26 | 19.538 | 95.2138
[7 empty] | 2002-07-27 | 19.823 | 95.2138
[7 empty] | 2002-07-28 | 19.939 | 95.2138
[7 empty] | 2002-07-29 | 20.994 | 95.2138
[7 empty] | 2002-07-30 | 20.994 | 95.2138
[7 empty] | 2002-07-31 | 21.111 | 95.2138
[7 empty] | 2002-08-01 | 20.963 | 95.2138
[7 empty] | 2002-08-02 | 20.361 | 95.2138
[7 empty] | 2002-08-03 | 19.264 | 95.2138
[7 empty] | 2002-08-04 | 20.653 | 95.2138
[7 empty] | 2002-08-05 | 21.248 | 95.2138
[7 empty] | 2002-08-06 | 20.658 | 96.1834
[7 empty] | 2002-08-07 | 20.882 | 96.1834
[7 empty] | 2002-08-08 | 20.465 | 96.1834
[7 empty] | 2002-08-09 | 19.482 | 96.1834
[7 empty] | 2002-08-10 | 19.492 | 96.1834
[7 empty] | 2002-08-11 | 20.216 | 96.1834
[7 empty] | 2002-08-12 | 21.84 | 96.1834
[7 empty] | 2002-08-13 | 31.413 | 94.3626
[7 empty] | 2002-08-14 | 49.958 | 94.3626
[7 empty] | 2002-08-15 | 45.94 | 94.3626
[7 empty] | 2002-08-16 | 52.602 | 94.3626
[7 empty] | 2002-08-17 | 49.554 | 94.3626
[7 empty] | 2002-08-18 | 50.108 | 94.3626
[7 empty] | 2002-08-19 | 42.908 | 94.3626
[7 empty] | 2002-08-20 | 48.434 | 94.4496
[7 empty] | 2002-08-21 | 43.387 | 94.4496
[7 empty] | 2002-08-22 | 25.864 | 94.4496
[7 empty] | 2002-08-23 | 27.19 | 94.4496
[7 empty] | 2002-08-24 | 21.956 | 94.4496
[7 empty] | 2002-08-25 | 19.71 | 94.4496
[7 empty] | 2002-08-26 | 25.644 | 94.4496
[7 empty] | 2002-08-27 | 20.841 | 94.0156
[7 empty] | 2002-08-28 | 22.937 | 94.0156
[7 empty] | 2002-08-29 | 21.973 | 94.0156
[7 empty] | 2002-08-30 | 19.449 | 94.0156
[7 empty] | 2002-08-31 | 19.501 | 94.0156
[7 empty] | 2002-09-01 | 21.16 | 94.0156
[7 empty] | 2002-09-02 | 22.718 | 94.0156
[7 empty] | 2002-09-03 | 20.96 | 95.3894
[7 empty] | 2002-09-04 | 22.483 | 95.3894
[7 empty] | 2002-09-05 | 18.355 | 95.3894
[7 empty] | 2002-09-06 | 22.42 | 95.3894
[7 empty] | 2002-09-07 | 18.993 | 95.3894
[7 empty] | 2002-09-08 | 20.078 | 95.3894
[7 empty] | 2002-09-09 | 38.4 | 95.3894
[7 empty] | 2002-09-10 | 49.065 | 96.4717
[7 empty] | 2002-09-11 | 42.849 | 96.4717
[7 empty] | 2002-09-12 | 25.252 | 96.4717
[7 empty] | 2002-09-13 | 39.002 | 96.4717
[7 empty] | 2002-09-14 | 45.077 | 96.4717
[7 empty] | 2002-09-15 | 21.056 | 96.4717
[7 empty] | 2002-09-16 | 25.101 | 96.4717
[7 empty] | 2002-09-17 | 22.939 | 94.6891
[7 empty] | 2002-09-18 | 21.644 | 94.6891
[7 empty] | 2002-09-19 | 23.436 | 94.6891
[7 empty] | 2002-09-20 | 21.181 | 94.6891
[7 empty] | 2002-09-21 | 23.435 | 94.6891
[7 empty] | 2002-09-22 | 20.763 | 94.6891
[7 empty] | 2002-09-23 | 19.545 | 94.6891
[7 empty] | 2002-09-24 | 22.983 | 94.1673
[7 empty] | 2002-09-25 | 22.996 | 94.1673
[7 empty] | 2002-09-26 | 22.456 | 94.1673
[7 empty] | 2002-09-27 | 20.192 | 94.1673
[7 empty] | 2002-09-28 | 24.445 | 94.1673
[7 empty] | 2002-09-29 | 26.911 | 94.1673
[7 empty] | 2002-09-30 | 23.082 | 94.1673
[7 empty] | 2002-10-01 | 22.251 | 93.4975
[7 empty] | 2002-10-02 | 23.55 | 93.4975
[7 empty] | 2002-10-03 | 22.676 | 93.4975
[7 empty] | 2002-10-04 | 22.519 | 93.4975
[7 empty] | 2002-10-05 | 21.211 | 93.4975
[7 empty] | 2002-10-06 | 23.345 | 93.4975
[7 empty] | 2002-10-07 | 24.022 | 93.4975
[7 empty] | 2002-10-08 | 22.889 | 92.747
[7 empty] | 2002-10-09 | 22.869 | 92.747
[7 empty] | 2002-10-10 | 21.842 | 92.747
[7 empty] | 2002-10-11 | 21.959 | 92.747
[7 empty] | 2002-10-12 | 23.796 | 92.747
[7 empty] | 2002-10-13 | 21.79 | 92.747
[7 empty] | 2002-10-14 | 24.441 | 92.747
[7 empty] | 2002-10-15 | 22.56 | 95.0605
[7 empty] | 2002-10-16 | 21.655 | 95.0605
[7 empty] | 2002-10-17 | 23.314 | 95.0605
[7 empty] | 2002-10-18 | 19.791 | 95.0605
[7 empty] | 2002-10-19 | 23.514 | 95.0605
[7 empty] | 2002-10-20 | 20.449 | 95.0605
[7 empty] | 2002-10-21 | 23.541 | 95.0605
[7 empty] | 2002-10-22 | 23.779 | 94.5584
[7 empty] | 2002-10-23 | 21.614 | 94.5584
[7 empty] | 2002-10-24 | 22.97 | 94.5584
[7 empty] | 2002-10-25 | 21.162 | 94.5584
[7 empty] | 2002-10-26 | 22.816 | 94.5584
[7 empty] | 2002-10-27 | 23.089 | 94.5584
[7 empty] | 2002-10-28 | 24.313 | 94.5584
[7 empty] | 2002-10-29 | 22.699 | 94.5584
[7 empty] | 2002-10-30 | 22.025 | 94.5584
[7 empty] | 2002-10-31 | 22.627 | 94.5584
[7 empty] | 2002-11-01 | 21.933 | 94.5584
[7 empty] | 2002-11-02 | 20.101 | 94.5584
[7 empty] | 2002-11-03 | 22.12 | 94.5584
[7 empty] | 2002-11-04 | 21.258 | 94.5584
[7 empty] | 2002-11-05 | 21.466 | 94.5584
[7 empty] | 2002-11-06 | 20.618 | 94.6891
[7 empty] | 2002-11-07 | 21.313 | 94.6891
[7 empty] | 2002-11-08 | 19.342 | 94.6891
[7 empty] | 2002-11-09 | 20.957 | 94.6891
[7 empty] | 2002-11-10 | 19.223 | 94.6891
[7 empty] | 2002-11-11 | 21.984 | 94.6891
[7 empty] | 2002-11-12 | 19.747 | 95.5652
[7 empty] | 2002-11-13 | 21.531 | 95.5652
[7 empty] | 2002-11-14 | 19.138 | 95.5652
[7 empty] | 2002-11-15 | 22.082 | 95.5652
[7 empty] | 2002-11-16 | 19.67 | 95.5652
[7 empty] | 2002-11-17 | 44.493 | 95.5652
[7 empty] | 2002-11-18 | 32.174 | 95.5652
[7 empty] | 2002-11-19 | 19.589 | 93.7562
[7 empty] | 2002-11-20 | 19.528 | 93.7562
[7 empty] | 2002-11-21 | 20.53 | 93.7562
[7 empty] | 2002-11-22 | 20.981 | 93.7562
[7 empty] | 2002-11-23 | 19.197 | 93.7562
[7 empty] | 2002-11-24 | 18.945 | 93.7562
[7 empty] | 2002-11-25 | 19.991 | 93.7562
[7 empty] | 2002-11-26 | 19.744 | 93.3039
[7 empty] | 2002-11-27 | 18.364 | 93.3039
[7 empty] | 2002-11-28 | 16.781 | 93.3039
[7 empty] | 2002-11-29 | 17.474 | 93.3039
[7 empty] | 2002-11-30 | 17.787 | 93.3039
[7 empty] | 2002-12-01 | 18.717 | 93.3039
[7 empty] | 2002-12-02 | 20.369 | 93.3039
[7 empty] | 2002-12-03 | 18.452 | 92.8539
[7 empty] | 2002-12-04 | 25.369 | 92.8539
[7 empty] | 2002-12-05 | 44.559 | 92.8539
[7 empty] | 2002-12-06 | 39.151 | 92.8539
[7 empty] | 2002-12-07 | 42.383 | 92.8539
[7 empty] | 2002-12-08 | 39.241 | 92.8539
[7 empty] | 2002-12-09 | 35.988 | 92.8539
[7 empty] | 2002-12-10 | 40.283 | 97.4316
[7 empty] | 2002-12-11 | 38.535 | 97.4316
[7 empty] | 2002-12-12 | 44.072 | 97.4316
[7 empty] | 2002-12-13 | 44.273 | 97.4316
[7 empty] | 2002-12-14 | 32.799 | 97.4316
[7 empty] | 2002-12-15 | 48.809 | 97.4316
[7 empty] | 2002-12-16 | 40.227 | 97.4316
[7 empty] | 2002-12-17 | 37.715 | 92.8753
[7 empty] | 2002-12-18 | 37.228 | 92.8753
[7 empty] | 2002-12-19 | 32.741 | 92.8753
[7 empty] | 2002-12-20 | 36.448 | 92.8753
[7 empty] | 2002-12-21 | 39.528 | 92.8753
[7 empty] | 2002-12-22 | 36.204 | 92.8753
[7 empty] | 2002-12-23 | 36.872 | 92.8753
[7 empty] | 2002-12-24 | 34.949 | 92.8753
[7 empty] | 2002-12-25 | 35.658 | 92.8753
[7 empty] | 2002-12-26 | 36.355 | 92.8753
[7 empty] | 2002-12-27 | 36.428 | 92.8753
[7 empty] | 2002-12-28 | 36.627 | 92.8753
[7 empty] | 2002-12-29 | 34.559 | 92.8753
[7 empty] | 2002-12-30 | 43.301 | 92.8753
[7 empty] | 2002-12-31 | 45.691 | 92.8753
[7 empty] | 2003-01-01 | 37.085 | 92.8753
[7 empty] | 2003-01-02 | 46.822 | 92.8753
[7 empty] | 2003-01-03 | 42.386 | 92.8753
[7 empty] | 2003-01-04 | 44.375 | 92.8753
[7 empty] | 2003-01-05 | 31.857 | 92.8753
[7 empty] | 2003-01-06 | 39.96 | 92.8753
[7 empty] | 2003-01-07 | 41.355 | 94.3409
[7 empty] | 2003-01-08 | 44.656 | 94.3409
[7 empty] | 2003-01-09 | 46.512 | 94.3409
[7 empty] | 2003-01-10 | 42.868 | 94.3409
[7 empty] | 2003-01-11 | 44.41 | 94.3409
[7 empty] | 2003-01-12 | 42.68 | 94.3409
[7 empty] | 2003-01-13 | 42.933 | 94.3409
[7 empty] | 2003-01-14 | 42.563 | 92.619
[7 empty] | 2003-01-15 | 46.13 | 92.619
[7 empty] | 2003-01-16 | 46.164 | 92.619
[7 empty] | 2003-01-17 | 41.741 | 92.619
[7 empty] | 2003-01-18 | 43.76 | 92.619
[7 empty] | 2003-01-19 | 43.737 | 92.619
[7 empty] | 2003-01-20 | 43.182 | 92.619
[7 empty] | 2003-01-21 | 42.268 | 90.2818
[7 empty] | 2003-01-22 | 42.342 | 90.2818
[7 empty] | 2003-01-23 | 44.011 | 90.2818
[7 empty] | 2003-01-24 | 40.638 | 90.2818
[7 empty] | 2003-01-25 | 45.637 | 90.2818
[7 empty] | 2003-01-26 | 46.254 | 90.2818
[7 empty] | 2003-01-27 | 46.166 | 90.2818
[7 empty] | 2003-01-28 | 45.435 | 93.3684
[7 empty] | 2003-01-29 | 43.939 | 93.3684
[7 empty] | 2003-01-30 | 42.914 | 93.3684
[7 empty] | 2003-01-31 | 41.974 | 93.3684
[7 empty] | 2003-02-01 | 45.47 | 93.3684
[7 empty] | 2003-02-02 | 43.747 | 93.3684
[7 empty] | 2003-02-03 | 41.856 | 93.3684
[7 empty] | 2003-02-04 | 43.682 | 93.8426
[7 empty] | 2003-02-05 | 39.216 | 93.8426
[7 empty] | 2003-02-06 | 40.786 | 93.8426
[7 empty] | 2003-02-07 | 45.579 | 93.8426
[7 empty] | 2003-02-08 | 45.534 | 93.8426
[7 empty] | 2003-02-09 | 43.832 | 93.8426
[7 empty] | 2003-02-10 | 42.162 | 93.8426
[7 empty] | 2003-02-11 | 38.459 | 94.4278
[7 empty] | 2003-02-12 | 42.479 | 94.4278
[7 empty] | 2003-02-13 | 42.502 | 94.4278
[7 empty] | 2003-02-14 | 39.686 | 94.4278
[7 empty] | 2003-02-15 | 42.16 | 94.4278
[7 empty] | 2003-02-16 | 42.039 | 94.4278
[7 empty] | 2003-02-17 | 45.859 | 94.4278
[7 empty] | 2003-02-18 | 38.743 | 94.4278
[7 empty] | 2003-02-19 | 38.767 | 94.4278
[7 empty] | 2003-02-20 | 40.883 | 94.4278
[7 empty] | 2003-02-21 | 37.635 | 93.6052
[7 empty] | 2003-02-22 | 38.514 | 93.6052
[7 empty] | 2003-02-23 | 38.009 | 93.6052
[7 empty] | 2003-02-24 | 39.13 | 93.6052
[7 empty] | 2003-02-25 | 38.207 | 95.8076
[7 empty] | 2003-02-26 | 39.552 | 95.8076
[7 empty] | 2003-02-27 | 36.223 | 95.8076
[7 empty] | 2003-02-28 | 37.786 | 95.8076
[7 empty] | 2003-03-01 | 38.356 | 95.8076
[7 empty] | 2003-03-02 | 37.514 | 95.8076
[7 empty] | 2003-03-03 | 39.998 | 95.8076
[7 empty] | 2003-03-04 | 39.144 | 96.272
[7 empty] | 2003-03-05 | 40.417 | 96.272
[7 empty] | 2003-03-06 | 40.521 | 96.272
[7 empty] | 2003-03-07 | 45.901 | 96.272
[7 empty] | 2003-03-08 | 49.309 | 96.272
[7 empty] | 2003-03-09 | 47.785 | 96.272
[7 empty] | 2003-03-10 | 42.299 | 96.272
[7 empty] | 2003-03-11 | 47.911 | 91.5166
[7 empty] | 2003-03-12 | 46.706 | 91.5166
[7 empty] | 2003-03-13 | 47.3 | 91.5166
[7 empty] | 2003-03-14 | 47.574 | 91.5166
[7 empty] | 2003-03-15 | 46.68 | 91.5166
[7 empty] | 2003-03-16 | 45.724 | 91.5166
[7 empty] | 2003-03-17 | 45.194 | 91.5166
[7 empty] | 2003-03-18 | 49.273 | 84.4112
[7 empty] | 2003-03-19 | 41.279 | 84.4112
[7 empty] | 2003-03-20 | 47.898 | 84.4112
[7 empty] | 2003-03-21 | 39.371 | 84.4112
[7 empty] | 2003-03-22 | 46.425 | 84.4112
[7 empty] | 2003-03-23 | 44.426 | 84.4112
[7 empty] | 2003-03-24 | 43.712 | 84.4112
[7 empty] | 2003-03-25 | 47.752 | 93.3899
[7 empty] | 2003-03-26 | 35.735 | 93.3899
[7 empty] | 2003-03-27 | 48.173 | 93.3899
[7 empty] | 2003-03-28 | 44.061 | 93.3899
[7 empty] | 2003-03-29 | 43.44 | 93.3899
[7 empty] | 2003-03-30 | 37.648 | 93.3899
[7 empty] | 2003-03-31 | 40.125 | 93.3899
[7 empty] | 2003-04-01 | 40.46 | 89.4129
[7 empty] | 2003-04-02 | 43.347 | 89.4129
[7 empty] | 2003-04-03 | 42.543 | 89.4129
[7 empty] | 2003-04-04 | 42.657 | 89.4129
[7 empty] | 2003-04-05 | 41.977 | 89.4129
[7 empty] | 2003-04-06 | 40.273 | 89.4129
[7 empty] | 2003-04-07 | 42.057 | 89.4129
[7 empty] | 2003-04-08 | 43.934 | 85.428
[7 empty] | 2003-04-09 | 43.135 | 85.428
[7 empty] | 2003-04-10 | 45.936 | 85.428
[7 empty] | 2003-04-11 | 46.609 | 85.428
[7 empty] | 2003-04-12 | 47.026 | 85.428
[7 empty] | 2003-04-13 | 46.491 | 85.428
[7 empty] | 2003-04-14 | 45.328 | 85.428
[7 empty] | 2003-04-15 | 46.987 | 93.994
[7 empty] | 2003-04-16 | 48.59 | 93.994
[7 empty] | 2003-04-17 | 45.949 | 93.994
[7 empty] | 2003-04-18 | 47.721 | 93.994
[7 empty] | 2003-04-19 | 47.216 | 93.994
[7 empty] | 2003-04-20 | 45.168 | 93.994
[7 empty] | 2003-04-21 | 45.51 | 93.994
[7 empty] | 2003-04-22 | 48.399 | 92.8325
[7 empty] | 2003-04-23 | 39.069 | 92.8325
[7 empty] | 2003-04-24 | 44.016 | 92.8325
[7 empty] | 2003-04-25 | 37.008 | 92.8325
[7 empty] | 2003-04-26 | 40.867 | 92.8325
[7 empty] | 2003-04-27 | 48.406 | 92.8325
[7 empty] | 2003-04-28 | 43.928 | 92.8325
[7 empty] | 2003-04-29 | 48.046 | 92.8325
[7 empty] | 2003-04-30 | 46.439 | 92.8325
[7 empty] | 2003-05-01 | 36.809 | 92.8325
[7 empty] | 2003-05-02 | 36.305 | 92.8325
[7 empty] | 2003-05-03 | 40.379 | 92.8325
[7 empty] | 2003-05-04 | 41.808 | 92.8325
[7 empty] | 2003-05-05 | 35.858 | 92.8325
[7 empty] | 2003-05-06 | 45.795 | 94.0156
[7 empty] | 2003-05-07 | 45.144 | 94.0156
[7 empty] | 2003-05-08 | 41.968 | 94.0156
[7 empty] | 2003-05-09 | 44.86 | 94.0156
[7 empty] | 2003-05-10 | 44.248 | 94.0156
[7 empty] | 2003-05-11 | 40.619 | 94.0156
[7 empty] | 2003-05-12 | 44.453 | 94.0156
[7 empty] | 2003-05-13 | 44.487 | 95.7635
[7 empty] | 2003-05-14 | 42.385 | 95.7635
[7 empty] | 2003-05-15 | 34.344 | 95.7635
[7 empty] | 2003-05-16 | 41.159 | 95.7635
[7 empty] | 2003-05-17 | 39.8 | 95.7635
[7 empty] | 2003-05-18 | 40.193 | 95.7635
[7 empty] | 2003-05-19 | 40.519 | 95.7635
[7 empty] | 2003-05-20 | 41.504 | 94.6237
[7 empty] | 2003-05-21 | 44.821 | 94.6237
[7 empty] | 2003-05-22 | 42.865 | 94.6237
[7 empty] | 2003-05-23 | 42.004 | 94.6237
[7 empty] | 2003-05-24 | 43.332 | 94.6237
[7 empty] | 2003-05-25 | 41.395 | 94.6237
[7 empty] | 2003-05-26 | 43.72 | 94.6237
[7 empty] | 2003-05-27 | 46.148 | 89.2278
[7 empty] | 2003-05-28 | 43.445 | 89.2278
[7 empty] | 2003-05-29 | 44.582 | 89.2278
[7 empty] | 2003-05-30 | 46.333 | 89.2278
[7 empty] | 2003-05-31 | 49.494 | 89.2278
[7 empty] | 2003-06-01 | 46.992 | 89.2278
[7 empty] | 2003-06-02 | 42.173 | 89.2278
[7 empty] | 2003-06-03 | 50.056 | 90.2818
[7 empty] | 2003-06-04 | 48.591 | 90.2818
[7 empty] | 2003-06-05 | 48.266 | 90.2818
[7 empty] | 2003-06-06 | 45.695 | 90.2818
[7 empty] | 2003-06-07 | 50.432 | 90.2818
[7 empty] | 2003-06-08 | 48.167 | 90.2818
[7 empty] | 2003-06-09 | 42.988 | 90.2818
[7 empty] | 2003-06-10 | 39.409 | 90.1571
[7 empty] | 2003-06-11 | 49.059 | 90.1571
[7 empty] | 2003-06-12 | 50.177 | 90.1571
[7 empty] | 2003-06-13 | 43.454 | 90.1571
[7 empty] | 2003-06-14 | 50.001 | 90.1571
[7 empty] | 2003-06-15 | 47.491 | 90.1571
[7 empty] | 2003-06-16 | 50.781 | 90.1571
[7 empty] | 2003-06-17 | 47.82 | 89.5777
[7 empty] | 2003-06-18 | 45.193 | 89.5777
[7 empty] | 2003-06-19 | 40.962 | 89.5777
[7 empty] | 2003-06-20 | 48.466 | 89.5777
[7 empty] | 2003-06-21 | 48.246 | 89.5777
[7 empty] | 2003-06-22 | 47.562 | 89.5777
[7 empty] | 2003-06-23 | 50.008 | 89.5777
[7 empty] | 2003-06-24 | 49.186 | 87.7001
[7 empty] | 2003-06-25 | 45.346 | 87.7001
[7 empty] | 2003-06-26 | 45.461 | 87.7001
[7 empty] | 2003-06-27 | 45.945 | 87.7001
[7 empty] | 2003-06-28 | 45.688 | 87.7001
[7 empty] | 2003-06-29 | 46.51 | 87.7001
[7 empty] | 2003-06-30 | 46.74 | 87.7001
[7 empty] | 2003-07-01 | 49.584 | 88.247
[7 empty] | 2003-07-02 | 45.561 | 88.247
[7 empty] | 2003-07-03 | 47.159 | 88.247
[7 empty] | 2003-07-04 | 44.502 | 88.247
[7 empty] | 2003-07-05 | 45.649 | 88.247
[7 empty] | 2003-07-06 | 45.37 | 88.247
[7 empty] | 2003-07-07 | 49.301 | 88.247
[7 empty] | 2003-07-08 | 49.841 | 90.7194
[7 empty] | 2003-07-09 | 48.611 | 90.7194
[7 empty] | 2003-07-10 | 48.302 | 90.7194
[7 empty] | 2003-07-11 | 38.593 | 90.7194
[7 empty] | 2003-07-12 | 46.786 | 90.7194
[7 empty] | 2003-07-13 | 50.472 | 90.7194
[7 empty] | 2003-07-14 | 47.581 | 90.7194
[7 empty] | 2003-07-15 | 48.768 | 99.3574
[7 empty] | 2003-07-16 | 49.455 | 99.3574
[7 empty] | 2003-07-17 | 47.884 | 99.3574
[7 empty] | 2003-07-18 | 47.791 | 99.3574
[7 empty] | 2003-07-19 | 46.604 | 99.3574
[7 empty] | 2003-07-20 | 46.656 | 99.3574
[7 empty] | 2003-07-21 | 48.996 | 99.3574
[7 empty] | 2003-07-22 | 47.537 | 95.9622
[7 empty] | 2003-07-23 | 55.277 | 95.9622
[7 empty] | 2003-07-24 | 56.656 | 95.9622
[7 empty] | 2003-07-25 | 54.955 | 95.9622
[7 empty] | 2003-07-26 | 57.777 | 95.9622
[7 empty] | 2003-07-27 | 55.536 | 95.9622
[7 empty] | 2003-07-28 | 54.857 | 95.9622
[7 empty] | 2003-07-29 | 58.008 | 95.9622
[7 empty] | 2003-07-30 | 58.393 | 95.9622
[7 empty] | 2003-07-31 | 53.731 | 95.9622
[7 empty] | 2003-08-01 | 48.271 | 95.9622
[7 empty] | 2003-08-02 | 56.942 | 95.9622
[7 empty] | 2003-08-03 | 56.079 | 95.9622
[7 empty] | 2003-08-04 | 52.029 | 95.9622
[7 empty] | 2003-08-05 | 50.392 | 98.22
[7 empty] | 2003-08-06 | 45.014 | 98.22
[7 empty] | 2003-08-07 | 49.889 | 98.22
[7 empty] | 2003-08-08 | 55.206 | 98.22
[7 empty] | 2003-08-09 | 57.53 | 98.22
[7 empty] | 2003-08-10 | 57.334 | 98.22
[7 empty] | 2003-08-11 | 56.379 | 98.22
[7 empty] | 2003-08-12 | 59.55 | 89.9498
[7 empty] | 2003-08-13 | 56.154 | 89.9498
[7 empty] | 2003-08-14 | 59.888 | 89.9498
[7 empty] | 2003-08-15 | 56.718 | 89.9498
[7 empty] | 2003-08-16 | 53.599 | 89.9498
[7 empty] | 2003-08-17 | 45.313 | 89.9498
[7 empty] | 2003-08-18 | 30.424 | 89.9498
[7 empty] | 2003-08-19 | 26.974 | 88.4301
[7 empty] | 2003-08-20 | 29.395 | 88.4301
[7 empty] | 2003-08-21 | 28.995 | 88.4301
[7 empty] | 2003-08-22 | 26.547 | 88.4301
[7 empty] | 2003-08-23 | 43.12 | 88.4301
[7 empty] | 2003-08-24 | 39.294 | 88.4301
[7 empty] | 2003-08-25 | 40.17 | 88.4301
[7 empty] | 2003-08-26 | 40.788 | 96.2055
[7 empty] | 2003-08-27 | 52.443 | 96.2055
[7 empty] | 2003-08-28 | 50.927 | 96.2055
[7 empty] | 2003-08-29 | 44.805 | 96.2055
[7 empty] | 2003-08-30 | 36.418 | 96.2055
[7 empty] | 2003-08-31 | 41.464 | 96.2055
[7 empty] | 2003-09-01 | 33.453 | 96.2055
[7 empty] | 2003-09-02 | 11.772 | 91.1171
[7 empty] | 2003-09-03 | 32.181 | 91.1171
[7 empty] | 2003-09-04 | 32.281 | 91.1171
[7 empty] | 2003-09-05 | 31.844 | 91.1171
[7 empty] | 2003-09-06 | 36.756 | 91.1171
[7 empty] | 2003-09-07 | 38.433 | 91.1171
[7 empty] | 2003-09-08 | 32.173 | 91.1171
[7 empty] | 2003-09-09 | 37.623 | 96.8947
[7 empty] | 2003-09-10 | 31.278 | 96.8947
[7 empty] | 2003-09-11 | 39.229 | 96.8947
[7 empty] | 2003-09-12 | 37.481 | 96.8947
[7 empty] | 2003-09-13 | 38.852 | 96.8947
[7 empty] | 2003-09-14 | 38.781 | 96.8947
[7 empty] | 2003-09-15 | 27.902 | 96.8947
[7 empty] | 2003-09-16 | 16.355 | 97.0957
[7 empty] | 2003-09-17 | 16.758 | 97.0957
[7 empty] | 2003-09-18 | 22.909 | 97.0957
[7 empty] | 2003-09-19 | 29.92 | 97.0957
[7 empty] | 2003-09-20 | 46.492 | 97.0957
[7 empty] | 2003-09-21 | 40.914 | 97.0957
[7 empty] | 2003-09-22 | 46.895 | 97.0957
[7 empty] | 2003-09-23 | 43.912 | 94.9511
[7 empty] | 2003-09-24 | 34.397 | 94.9511
[7 empty] | 2003-09-25 | 17.994 | 94.9511
[7 empty] | 2003-09-26 | 18.342 | 94.9511
[7 empty] | 2003-09-27 | 14.067 | 94.9511
[7 empty] | 2003-09-28 | 12.17 | 94.9511
[7 empty] | 2003-09-29 | 11.582 | 94.9511
[7 empty] | 2003-09-30 | 9.021 | 96.3607
[7 empty] | 2003-10-01 | 11.386 | 96.3607
[7 empty] | 2003-10-02 | 11.527 | 96.3607
[7 empty] | 2003-10-03 | 11.406 | 96.3607
[7 empty] | 2003-10-04 | 15.317 | 96.3607
[7 empty] | 2003-10-05 | 13.855 | 96.3607
[7 empty] | 2003-10-06 | 15.447 | 96.3607
[7 empty] | 2003-10-07 | 12.868 | 93.2395
[7 empty] | 2003-10-08 | 12.906 | 93.2395
[7 empty] | 2003-10-09 | 14.792 | 93.2395
[7 empty] | 2003-10-10 | 13.8 | 93.2395
[7 empty] | 2003-10-11 | 11.491 | 93.2395
[7 empty] | 2003-10-12 | 13.713 | 93.2395
[7 empty] | 2003-10-13 | 12.509 | 93.2395
[7 empty] | 2003-10-14 | 12.38 | 91.939
[7 empty] | 2003-10-15 | 4.025 | 91.939
[7 empty] | 2003-10-16 | -0.358 | 91.939
[7 empty] | 2003-10-17 | 4.549 | 91.939
[7 empty] | 2003-10-18 | 21.057 | 91.939
[7 empty] | 2003-10-19 | 20.711 | 91.939
[7 empty] | 2003-10-20 | 23.004 | 91.939
[7 empty] | 2003-10-21 | 24.135 | 90.0326
[7 empty] | 2003-10-22 | 20.641 | 90.0326
[7 empty] | 2003-10-23 | 19.593 | 90.0326
[7 empty] | 2003-10-24 | 21.015 | 90.0326
[7 empty] | 2003-10-25 | 23.532 | 90.0326
[7 empty] | 2003-10-26 | 21.278 | 90.0326
[7 empty] | 2003-10-27 | 24.889 | 90.0326
[7 empty] | 2003-10-28 | 25.695 | 88.9201
[7 empty] | 2003-10-29 | 25.459 | 88.9201
[7 empty] | 2003-10-30 | 20.396 | 88.9201
[7 empty] | 2003-10-31 | 24.757 | 88.9201
[7 empty] | 2003-11-01 | 22.248 | 88.9201
[7 empty] | 2003-11-02 | 26.807 | 88.9201
[7 empty] | 2003-11-03 | 34.727 | 88.9201
[7 empty] | 2003-11-04 | 44.037 | 89.2894
[7 empty] | 2003-11-05 | 41.011 | 89.2894
[7 empty] | 2003-11-06 | 42.165 | 89.2894
[7 empty] | 2003-11-07 | 39.18 | 89.2894
[7 empty] | 2003-11-08 | 37.991 | 89.2894
[7 empty] | 2003-11-09 | 42.816 | 89.2894
[7 empty] | 2003-11-10 | 38.721 | 89.2894
[7 empty] | 2003-11-11 | 41.921 | 89.2894
[7 empty] | 2003-11-12 | 44.226 | 90.1986
[7 empty] | 2003-11-13 | 35.873 | 90.1986
[7 empty] | 2003-11-14 | 18.536 | 90.1986
[7 empty] | 2003-11-15 | 44.376 | 90.1986
[7 empty] | 2003-11-16 | 46.035 | 90.1986
[7 empty] | 2003-11-17 | 44.565 | 90.1986
[7 empty] | 2003-11-18 | 43.148 | 91.2851
[7 empty] | 2003-11-19 | 37.619 | 91.2851
[7 empty] | 2003-11-20 | 41.68 | 91.2851
[7 empty] | 2003-11-21 | 38.367 | 91.2851
[7 empty] | 2003-11-22 | 37.878 | 91.2851
[7 empty] | 2003-11-23 | 37.485 | 91.2851
[7 empty] | 2003-11-24 | 37.338 | 91.2851
[7 empty] | 2003-11-25 | 41.604 | 89.8876
[7 empty] | 2003-11-26 | 37.744 | 89.8876
[7 empty] | 2003-11-27 | 37.812 | 89.8876
[7 empty] | 2003-11-28 | 36.174 | 89.8876
[7 empty] | 2003-11-29 | 37.146 | 89.8876
[7 empty] | 2003-11-30 | 38.768 | 89.8876
[7 empty] | 2003-12-01 | 39.53 | 89.8876
[7 empty] | 2003-12-02 | 39.282 | 88.8587
[7 empty] | 2003-12-03 | 39.282 | 88.8587
[7 empty] | 2003-12-04 | 33.92 | 88.8587
[7 empty] | 2003-12-05 | 33.55 | 88.8587
[7 empty] | 2003-12-06 | 33.883 | 88.8587
[7 empty] | 2003-12-07 | 33.106 | 88.8587
[7 empty] | 2003-12-08 | 31.682 | 88.8587
[7 empty] | 2003-12-09 | 30.669 | 89.2689
[7 empty] | 2003-12-10 | 36.412 | 89.2689
[7 empty] | 2003-12-11 | 37.654 | 89.2689
[7 empty] | 2003-12-12 | 36.069 | 89.2689
[7 empty] | 2003-12-13 | 35.054 | 89.2689
[7 empty] | 2003-12-14 | 36.452 | 89.2689
[7 empty] | 2003-12-15 | 36.258 | 89.2689
[7 empty] | 2003-12-16 | 36.774 | 87.0362
[7 empty] | 2003-12-17 | 38.944 | 87.0362
[7 empty] | 2003-12-18 | 35.629 | 87.0362
[7 empty] | 2003-12-19 | 32.858 | 87.0362
[7 empty] | 2003-12-20 | 34.477 | 87.0362
[7 empty] | 2003-12-21 | 35.249 | 87.0362
[7 empty] | 2003-12-22 | 34.421 | 87.0362
[7 empty] | 2003-12-23 | 34.487 | 88.2877
[7 empty] | 2003-12-24 | 37.012 | 88.2877
[7 empty] | 2003-12-25 | 36.511 | 88.2877
[7 empty] | 2003-12-26 | 35.644 | 88.2877
[7 empty] | 2003-12-27 | 33.509 | 88.2877
[7 empty] | 2003-12-28 | 38.774 | 88.2877
[7 empty] | 2003-12-29 | 36.672 | 88.2877
[7 empty] | 2003-12-30 | 38.099 | 88.2877
[7 empty] | 2003-12-31 | 37.115 | 88.2877
[7 empty] | 2004-01-01 | 37.502 | 88.2877
[7 empty] | 2004-01-02 | 37.262 | 88.2877
[7 empty] | 2004-01-03 | 35.74 | 88.2877
[7 empty] | 2004-01-04 | 36.01 | 88.2877
[7 empty] | 2004-01-05 | 36.815 | 88.2877
[7 empty] | 2004-01-06 | 36.608 | 90.4899
[7 empty] | 2004-01-07 | 36.022 | 90.4899
[7 empty] | 2004-01-08 | 35.804 | 90.4899
[7 empty] | 2004-01-09 | 37.167 | 90.4899
[7 empty] | 2004-01-10 | 35.697 | 90.4899
[7 empty] | 2004-01-11 | 37.194 | 90.4899
[7 empty] | 2004-01-12 | 34.405 | 90.4899
[7 empty] | 2004-01-13 | 39.012 | 90.3233
[7 empty] | 2004-01-14 | 36.97 | 90.3233
[7 empty] | 2004-01-15 | 35.836 | 90.3233
[7 empty] | 2004-01-16 | 36.029 | 90.3233
[7 empty] | 2004-01-17 | 35.665 | 90.3233
[7 empty] | 2004-01-18 | 35.998 | 90.3233
[7 empty] | 2004-01-19 | 35.211 | 90.3233
[7 empty] | 2004-01-20 | 36.773 | 92.045
[7 empty] | 2004-01-21 | 36.079 | 92.045
[7 empty] | 2004-01-22 | 37.908 | 92.045
[7 empty] | 2004-01-23 | 43.751 | 92.045
[7 empty] | 2004-01-24 | 40.619 | 92.045
[7 empty] | 2004-01-25 | 40.831 | 92.045
[7 empty] | 2004-01-26 | 40.98 | 92.045
[7 empty] | 2004-01-27 | 50.861 | 91.0123
[7 empty] | 2004-01-28 | 48.709 | 91.0123
[7 empty] | 2004-01-29 | 41.473 | 91.0123
[7 empty] | 2004-01-30 | 41.329 | 91.0123
[7 empty] | 2004-01-31 | 42.718 | 91.0123
[7 empty] | 2004-02-01 | 40.277 | 91.0123
[7 empty] | 2004-02-02 | 40.277 | 91.0123
[7 empty] | 2004-02-03 | 40.5 | 90.3649
[7 empty] | 2004-02-04 | 39.886 | 90.3649
[7 empty] | 2004-02-05 | 37.293 | 90.3649
[7 empty] | 2004-02-06 | 23.653 | 90.3649
[7 empty] | 2004-02-07 | 39.897 | 90.3649
[7 empty] | 2004-02-08 | 36.914 | 90.3649
[7 empty] | 2004-02-09 | 44.063 | 90.3649
[7 empty] | 2004-02-10 | 47.912 | 91.3692
[7 empty] | 2004-02-11 | 44.538 | 91.3692
[7 empty] | 2004-02-12 | 47.41 | 91.3692
[7 empty] | 2004-02-13 | 46.57 | 91.3692
[7 empty] | 2004-02-14 | 48.082 | 91.3692
[7 empty] | 2004-02-15 | 47.442 | 91.3692
[7 empty] | 2004-02-16 | 44.419 | 91.3692
[7 empty] | 2004-02-17 | 37.144 | 91.3482
[7 empty] | 2004-02-18 | 38.251 | 91.3482
[7 empty] | 2004-02-19 | 37.051 | 91.3482
[7 empty] | 2004-02-20 | 38.858 | 91.3482
[7 empty] | 2004-02-21 | 37.685 | 91.3482
[7 empty] | 2004-02-22 | 36.809 | 91.3482
[7 empty] | 2004-02-23 | 37.474 | 91.3482
[7 empty] | 2004-02-24 | 37.823 | 91.3482
[7 empty] | 2004-02-25 | 39.004 | 91.3482
[7 empty] | 2004-02-26 | 36.662 | 91.3482
[7 empty] | 2004-02-27 | 36.152 | 91.3482
[7 empty] | 2004-02-28 | 35.005 | 91.3482
[7 empty] | 2004-02-29 | 36.344 | 91.3482
[7 empty] | 2004-03-01 | 37.235 | 91.3482
[7 empty] | 2004-03-02 | 44.158 | 91.3482
[7 empty] | 2004-03-03 | 42.252 | 91.3482
[7 empty] | 2004-03-04 | 41.738 | 91.3482
[7 empty] | 2004-03-05 | 38.876 | 91.3482
[7 empty] | 2004-03-06 | 39.319 | 91.3482
[7 empty] | 2004-03-07 | 41.53 | 91.3482
[7 empty] | 2004-03-08 | 40.569 | 91.3482
[7 empty] | 2004-03-09 | 41.402 | 93.3254
[7 empty] | 2004-03-10 | 42.781 | 93.3254
[7 empty] | 2004-03-11 | 36.427 | 93.3254
[7 empty] | 2004-03-12 | 41.727 | 93.3254
[7 empty] | 2004-03-13 | 43.957 | 93.3254
[7 empty] | 2004-03-14 | 43.073 | 93.3254
[7 empty] | 2004-03-15 | 54.214 | 93.3254
[7 empty] | 2004-03-16 | 44.706 | 93.3254
[7 empty] | 2004-03-17 | 43.01 | 93.3254
[7 empty] | 2004-03-18 | 44.274 | 93.3254
[7 empty] | 2004-03-19 | 39.89 | 93.3254
[7 empty] | 2004-03-20 | 46.06 | 93.3254
[7 empty] | 2004-03-21 | 42.511 | 93.3254
[7 empty] | 2004-03-22 | 42.683 | 93.3254
[7 empty] | 2004-03-23 | 40.81 | 89.1867
[7 empty] | 2004-03-24 | 30.717 | 89.1867
[7 empty] | 2004-03-25 | 42.407 | 89.1867
[7 empty] | 2004-03-26 | 40.565 | 89.1867
[7 empty] | 2004-03-27 | 39.739 | 89.1867
[7 empty] | 2004-03-28 | 40.457 | 89.1867
[7 empty] | 2004-03-29 | 41.929 | 89.1867
[7 empty] | 2004-03-30 | 47.46 | 89.1867
[7 empty] | 2004-03-31 | 39.895 | 89.1867
[7 empty] | 2004-04-01 | 39.536 | 89.1867
[7 empty] | 2004-04-02 | 39.504 | 89.1867
[7 empty] | 2004-04-03 | 39.844 | 89.1867
[7 empty] | 2004-04-04 | 37.374 | 89.1867
[7 empty] | 2004-04-05 | 42.238 | 89.1867
[7 empty] | 2004-04-06 | 42.682 | 90.8448
[7 empty] | 2004-04-07 | 42.457 | 90.8448
[7 empty] | 2004-04-08 | 41.715 | 90.8448
[7 empty] | 2004-04-09 | 42.187 | 90.8448
[7 empty] | 2004-04-10 | 42.634 | 90.8448
[7 empty] | 2004-04-11 | 45.006 | 90.8448
[7 empty] | 2004-04-12 | 41.907 | 90.8448
[7 empty] | 2004-04-13 | 42.109 | 85.8025
[7 empty] | 2004-04-14 | 40.722 | 85.8025
[7 empty] | 2004-04-15 | 38.91 | 85.8025
[7 empty] | 2004-04-16 | 39.332 | 85.8025
[7 empty] | 2004-04-17 | 40.222 | 85.8025
[7 empty] | 2004-04-18 | 40.192 | 85.8025
[7 empty] | 2004-04-19 | 39.775 | 85.8025
[7 empty] | 2004-04-20 | 41.292 | 85.8025
[7 empty] | 2004-04-21 | 40.214 | 85.8025
[7 empty] | 2004-04-22 | 41.619 | 85.8025
[7 empty] | 2004-04-23 | 44.697 | 85.8025
[7 empty] | 2004-04-24 | 44.597 | 85.8025
[7 empty] | 2004-04-25 | 46.333 | 85.8025
[7 empty] | 2004-04-26 | 39.1 | 85.8025
[7 empty] | 2004-04-27 | 35.566 | 85.8025
[7 empty] | 2004-04-28 | 35.656 | 85.8025
[7 empty] | 2004-04-29 | 38.584 | 85.8025
[7 empty] | 2004-04-30 | 38.537 | 85.8025
[7 empty] | 2004-05-01 | 37.985 | 85.8025
[7 empty] | 2004-05-02 | 37.625 | 85.8025
[7 empty] | 2004-05-03 | 34.357 | 85.8025
[7 empty] | 2004-05-04 | 32.516 | 85.8025
[7 empty] | 2004-05-05 | 31.052 | 85.8025
[7 empty] | 2004-05-06 | 31.663 | 85.8025
[7 empty] | 2004-05-07 | 30.658 | 85.8025
[7 empty] | 2004-05-08 | 31.651 | 85.8025
[7 empty] | 2004-05-09 | 30.794 | 85.8025
[7 empty] | 2004-05-10 | 31.647 | 85.8025
[7 empty] | 2004-05-11 | 33.133 | 85.8025
[7 empty] | 2004-05-12 | 37.015 | 85.8025
[7 empty] | 2004-05-13 | 27.151 | 85.8025
[7 empty] | 2004-05-14 | 28.417 | 85.8025
[7 empty] | 2004-05-15 | 26.274 | 85.8025
[7 empty] | 2004-05-16 | 29.087 | 85.8025
[7 empty] | 2004-05-17 | 28.627 | 85.8025
[7 empty] | 2004-05-18 | 30.132 | 96.8501
[7 empty] | 2004-05-19 | 32.847 | 96.8501
[7 empty] | 2004-05-20 | 32.625 | 96.8501
[7 empty] | 2004-05-21 | 37.148 | 96.8501
[7 empty] | 2004-05-22 | 42.622 | 96.8501
[7 empty] | 2004-05-23 | 42.521 | 96.8501
[7 empty] | 2004-05-24 | 42.881 | 96.8501
[7 empty] | 2004-05-25 | 43.037 | 96.8501
[7 empty] | 2004-05-26 | 42.215 | 96.8501
[7 empty] | 2004-05-27 | 43.972 | 96.8501
[7 empty] | 2004-05-28 | 42.645 | 96.8501
[7 empty] | 2004-05-29 | 42.097 | 96.8501
[7 empty] | 2004-05-30 | 44.951 | 96.8501
[7 empty] | 2004-05-31 | 44.123 | 96.8501
[7 empty] | 2004-06-01 | 44.023 | 96.8501
[7 empty] | 2004-06-02 | 39.13 | 96.8501
[7 empty] | 2004-06-03 | 44.998 | 96.8501
[7 empty] | 2004-06-04 | 44.969 | 96.8501
[7 empty] | 2004-06-05 | 44.353 | 96.8501
[7 empty] | 2004-06-06 | 44.208 | 96.8501
[7 empty] | 2004-06-07 | 42.697 | 96.8501
[7 empty] | 2004-06-08 | 43.542 | 96.8501
[7 empty] | 2004-06-09 | 45.328 | 96.8501
[7 empty] | 2004-06-10 | 43.812 | 96.8501
[7 empty] | 2004-06-11 | 45.193 | 96.8501
[7 empty] | 2004-06-12 | 44.903 | 96.8501
[7 empty] | 2004-06-13 | 44.567 | 96.8501
[7 empty] | 2004-06-14 | 44.453 | 96.8501
[7 empty] | 2004-06-15 | 42.621 | 96.8501
[7 empty] | 2004-06-16 | 44.468 | 96.8501
[7 empty] | 2004-06-17 | 44.315 | 96.8501
[7 empty] | 2004-06-18 | 43.047 | 96.8501
[7 empty] | 2004-06-19 | 42.883 | 96.8501
[7 empty] | 2004-06-20 | 43.836 | 96.8501
[7 empty] | 2004-06-21 | 44.928 | 96.8501
[7 empty] | 2004-06-22 | 44.977 | 96.8501
[7 empty] | 2004-06-23 | 44.591 | 96.8501
[7 empty] | 2004-06-24 | 43.988 | 96.8501
[7 empty] | 2004-06-25 | 45.511 | 96.8501
[7 empty] | 2004-06-26 | 43.815 | 96.8501
[7 empty] | 2004-06-27 | 40.914 | 96.8501
[7 empty] | 2004-06-28 | 43.394 | 96.8501
[7 empty] | 2004-06-29 | 41.918 | 96.8501
[7 empty] | 2004-06-30 | 42.601 | 96.8501
[7 empty] | 2004-07-01 | 41.479 | 96.8501
[7 empty] | 2004-07-02 | 41.097 | 96.8501
[7 empty] | 2004-07-03 | 42.091 | 96.8501
[7 empty] | 2004-07-04 | 35.631 | 96.8501
[7 empty] | 2004-07-05 | 43.464 | 96.8501
[7 empty] | 2004-07-06 | 42.103 | 91.6431
[7 empty] | 2004-07-07 | 45.519 | 91.6431
[7 empty] | 2004-07-08 | 41.495 | 91.6431
[7 empty] | 2004-07-09 | 43.767 | 91.6431
[7 empty] | 2004-07-10 | 40.334 | 91.6431
[7 empty] | 2004-07-11 | 43.74 | 91.6431
[7 empty] | 2004-07-12 | 42.564 | 91.6431
[7 empty] | 2004-07-13 | 45.076 | 92.406
[7 empty] | 2004-07-14 | 44.259 | 92.406
[7 empty] | 2004-07-15 | 42.491 | 92.406
[7 empty] | 2004-07-16 | 45.769 | 92.406
[7 empty] | 2004-07-17 | 42.485 | 92.406
[7 empty] | 2004-07-18 | 42.922 | 92.406
[7 empty] | 2004-07-19 | 44.393 | 92.406

## Pathogen DR
Cryptosporidium |  | Giardia |  | Adenovirus |  | Rotavirus |  | Cryptosporidium |  | Giardia |  | Adenovirus |  | Rotavirus |  | Cryptosporidium |  | Giardia |  | Adenovirus
USEPA UVDGM 2003 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2003
80% Credible limits |  | 80% Credible limits |  | 80% Credible limits |  | 80% Credible limits |  | 50% Prediction Interval |  | 50% Prediction Interval |  | 50% Prediction Interval |  | 50% Prediction Interval |  | Tier 1 REDs |  | Tier 1 REDs |  | Tier 1 REDs
UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log
mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.6 | 0.5 | 1.5 | 0.5 | 39 | 0.5 | 11.6 | 0.5 | 0.7 | 0.5 | 0.3 | 1 | 0 | 0.5 | 3.2 | 0.5 | 6.8 | 0.5 | 6.6 | 0.5 | 55 | 0.5
2.5 | 1 | 2.1 | 1 | 58 | 1 | 17 | 1 | 1.3 | 1 | 0.3 | 1.5 | 18 | 1 | 8.5 | 1 | 11 | 1 | 9.7 | 1 | 81 | 1
3.9 | 1.5 | 3 | 1.5 | 79 | 1.5 | 22.3 | 1.5 | 1.8 | 1.5 | 0.7 | 2 | 40 | 1.5 | 13.9 | 1.5 | 15 | 1.5 | 13 | 1.5 | 110 | 1.5
5.8 | 2 | 5.2 | 2 | 100 | 2 | 27.7 | 2 | 2.5 | 2 | 0.8 | 2.5 | 62.4 | 2 | 19.2 | 2 | 21 | 2 | 20 | 2 | 139 | 2
8.5 | 2.5 | 7.7 | 2.5 | 121 | 2.5 | 33.1 | 2.5 | 2.9 | 2.5 | 1.3 | 3 | 84.7 | 2.5 | 24.6 | 2.5 | 28 | 2.5 | 26 | 2.5 | 169 | 2.5
12 | 3 | 11 | 3 | 143 | 3 | 38.4 | 3 | 4.3 | 3 |  |  | 107 | 3 | 30 | 3 | 36 | 3 | 34 | 3 | 199 | 3
|  |  |  | 163 | 3.5 | 43.8 | 3.5 |  |  |  |  | 129.3 | 3.5 | 35.3 | 3.5 |  |  |  |  | 227 | 3.5
|  |  |  | 186 | 4 | 49.2 | 4 |  |  |  |  | 151.7 | 4 | 40.7 | 4 |  |  |  |  | 259 | 4
y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d)
Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data:
a = | -0.002479 | a = | -0.027557 | a = | -0.028948 | a = | -0.011498 | a = | 0.020396 | a = | 0.0012008 | a = | 0.27179 | a = | 0.048198 | a = | -0.0087794 | a = | -0.020093 | a = | -0.039529
b = | 11.7843 | b = | 8.2545 | b = | 3964.4212 | b = | 1054.6673 | b = | 5.1239 | b = | 1.5929 | b = | 5004.7743 | b = | 1725.009 | b = | 157.8254 | b = | 120.1141 | b = | 6045.8958
c = | 4.0713 | c = | 3.7692 | c = | 14.3494 | c = | 10.8126 | c = | 4.3845 | c = | 6.8477 | c = | 282.7328 | c = | 222.6385 | c = | 4.5861 | c = | 4.384 | c = | 17.1227
d = | 1.3924 | d = | 1.4118 | d = | 1.405 | d = | 1.649 | d = | 1.671 | d = | 0.86615 | d = | 0.83445 | d = | 0.92602 | d = | 1.5845 | d = | 1.5679 | d = | 1.3553
Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log
| Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation
0 | -0.002479 | 0 | -0.027557 | 0 | -0.028948 | 0 | -0.011498 | 0 | 0.020396 | 0 | 0.0012008 | 0 | 0.27179 | 0 | 0.048198 | 0 | -0.0087794 | 0 | -0.020093 | 0 | -0.039529
1 | 0.31618 | 1 | 0.3827 | 5 | 0.0057672 | 5 | 0.1324 | 1 | 0.73303 | 1 | 2.6416 | 5 | 0.48782 | 5 | 0.61949 | 1 | 0.020151 | 1 | 0.016271 | 5 | -0.014422
2 | 0.7397 | 2 | 0.89794 | 10 | 0.062619 | 10 | 0.42734 | 2 | 1.6931 | 2 | 3.6548 | 10 | 0.65677 | 10 | 1.1312 | 2 | 0.076908 | 2 | 0.085997 | 10 | 0.024561
3 | 1.1443 | 3 | 1.353 | 15 | 0.13213 | 15 | 0.81309 | 3 | 2.422 | 3 | 4.2403 | 15 | 0.81147 | 15 | 1.6212 | 3 | 0.15143 | 3 | 0.17605 | 20 | 0.12349
4 | 1.5008 | 4 | 1.7253 | 20 | 0.21102 | 20 | 1.2551 | 4 | 2.9196 | 4 | 4.629 | 20 | 0.95754 | 20 | 2.0969 | 4 | 0.23897 | 4 | 0.28023 | 30 | 0.24095
6 | 2.063 | 6 | 2.2627 | 25 | 0.29737 | 25 | 1.7279 | 6 | 3.4933 | 6 | 5.1203 | 25 | 1.0975 | 25 | 2.5618 | 6 | 0.44041 | 6 | 0.51465 | 40 | 0.37148
8 | 2.4644 | 8 | 2.6123 | 30 | 0.38987 | 30 | 2.2126 | 8 | 3.7869 | 8 | 5.4219 | 30 | 1.2327 | 30 | 3.018 | 8 | 0.66194 | 8 | 0.76511 | 50 | 0.51196
10 | 2.7549 | 10 | 2.8492 | 40 | 0.5895 | 40 | 3.1663 | 10 | 3.9546 | 10 | 5.6279 | 40 | 1.4923 | 40 | 3.9088 | 10 | 0.89074 | 10 | 1.0166 | 60 | 0.66024
12 | 2.9703 | 12 | 3.0166 | 50 | 0.80404 | 50 | 4.0495 | 12 | 4.0591 | 12 | 5.7782 | 50 | 1.7408 | 50 | 4.7761 | 12 | 1.1181 | 12 | 1.26 | 70 | 0.81474
14 | 3.134 | 14 | 3.1393 | 60 | 1.0293 | 60 | 4.836 | 14 | 4.1286 | 14 | 5.8933 | 60 | 1.9807 | 60 | 5.6239 | 14 | 1.3385 | 14 | 1.4899 | 80 | 0.9742
16 | 3.2614 | 16 | 3.2323 | 70 | 1.2623 | 70 | 5.5217 | 16 | 4.1774 | 16 | 5.9843 | 70 | 2.2137 | 70 | 6.4548 | 16 | 1.5484 | 16 | 1.704 | 90 | 1.1376
18 | 3.3626 | 18 | 3.3044 | 80 | 1.5004 | 80 | 6.1134 | 18 | 4.2129 | 18 | 6.0584 | 80 | 2.4408 | 80 | 7.2706 | 18 | 1.7459 | 18 | 1.9011 | 100 | 1.3042
20 | 3.4444 | 20 | 3.3618 | 90 | 1.7417 | 90 | 6.6218 | 20 | 4.2397 | 20 | 6.1199 | 90 | 2.6629 | 90 | 8.073 | 20 | 1.9302 | 20 | 2.0815 | 125 | 1.7297
25 | 3.5922 | 25 | 3.463 | 100 | 1.9847 | 100 | 7.0583 | 25 | 4.2837 | 25 | 6.2364 | 100 | 2.8806 | 100 | 8.8628 | 25 | 2.3334 | 25 | 2.4651 | 150 | 2.1621
30 | 3.6895 | 30 | 3.5281 | 110 | 2.2279 | 110 | 7.4339 | 30 | 4.3098 | 30 | 6.3188 | 110 | 3.0944 | 110 | 9.6411 | 30 | 2.6619 | 30 | 2.7671 | 175 | 2.5951
35 | 3.7576 | 35 | 3.5728 | 120 | 2.4704 | 120 | 7.7581 | 35 | 4.3265 | 35 | 6.3804 | 120 | 3.3047 | 120 | 10.4085 | 35 | 2.9285 | 35 | 3.0056 | 200 | 3.0244
40 | 3.8074 | 40 | 3.6051 | 130 | 2.7112 | 130 | 8.039 | 40 | 4.338 | 40 | 6.4283 | 130 | 3.5118 | 130 | 11.1658 | 40 | 3.1455 | 40 | 3.1957 | 225 | 3.447
50 | 3.8745 | 50 | 3.648 | 140 | 2.9495 | 140 | 8.2835 | 50 | 4.3524 | 50 | 6.4983 | 140 | 3.7159 | 140 | 11.9135 | 50 | 3.4703 | 50 | 3.474 | 250 | 3.8605
60 | 3.9169 | 60 | 3.6748 | 150 | 3.185 | 150 | 8.4973 | 60 | 4.3608 | 60 | 6.5471 | 150 | 3.9174 | 150 | 12.6519 | 60 | 3.6961 | 60 | 3.6633 | 275 | 4.2635
70 | 3.9458 | 70 | 3.6929 | 160 | 3.4169 | 160 | 8.6851 | 70 | 4.3661 | 70 | 6.5832 | 160 | 4.1164 | 160 | 13.3816 | 70 | 3.8584 | 70 | 3.7974 | 300 | 4.6547
80 | 3.9666 | 80 | 3.7058 | 170 | 3.645 | 170 | 8.8508 | 80 | 4.3698 | 80 | 6.6111 | 170 | 4.313 | 170 | 14.103 | 80 | 3.9788 | 80 | 3.896 | 325 | 5.0336
100 | 3.994 | 100 | 3.7227 | 180 | 3.8689 | 180 | 8.9977 | 100 | 4.3744 | 100 | 6.6515 | 180 | 4.5075 | 180 | 14.8162 | 100 | 4.1422 | 100 | 4.0284 | 350 | 5.3998
120 | 4.0111 | 120 | 3.7331 | 190 | 4.0884 | 190 | 9.1284 | 120 | 4.377 | 120 | 6.6794 | 190 | 4.6999 | 190 | 15.5218 | 120 | 4.2454 | 120 | 4.1114 | 375 | 5.753
This worksheet provides equations for the UV dose-response of various pathogens. The data has been fitted to a mathematical function y=(a*b+c*x^d)/(b+x^d). The results of that fit can be used to define the UV dose-response of the pathogen in the worksheet RISKMODEL.

## ADVANCED LCA
NYSERDA - Advanced Life Cycle Cost Analysis Tool
Starting Column | 5
Ending Column | 5
Save Directory | C:\Documents and Settings\HWright\Desktop\UVCAT TC Version\91184_multimedia
Save Name | Output Case 5
Lamp Aging Functions
Units: y = %, x = hrs
MMF: y=(a*b+c*x^d)/(b+x^d)
EXP: y=a*e^(b*x)
LIN: Y = ax+b
COMMENTS |  | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6
|  | LPHO | LPHO | LPHO | LPHO | LPHO | LPHO
|  | A | A | A | C | C | C
OUTPUTS | 0 | 1 | 2 | 3 | 4 | 5 | 6
Lamp Life |  | 12000 | 12000 | 12000 | 12000 | 12000 | 12000
Age Factor |  | 0.70211 | 0.70211 | 0.70211 | 0.70211 | 0.70211 | 0.70211
Average # Lamps |  | 243.0141 | 243.0141 | 243.0141 | 243.0141 | 243.0141 | 352.2139
Average Power Level | % | 0.90916 | 0.90916 | 0.90916 | 0.90916 | 0.90916 | 0.92147
Power | $/yr | 69675.4922 | 69675.4922 | 69675.4922 | 69675.4922 | 69675.4922 | 102351.8984
Consumables
Lamps | $/yr | 28384.041 | 28384.041 | 28384.041 | 28384.041 | 28384.041 | 41138.5859
Sleeves | $/yr | 2430.1406 | 2430.1406 | 2430.1406 | 2430.1406 | 2430.1406 | 3522.1392
Ballasts | $/yr | 7290.4214 | 7290.4214 | 7290.4214 | 7290.4214 | 7290.4214 | 10566.418
Sensors | $/yr | 1316.3262 | 1316.3262 | 1316.3262 | 1316.3262 | 1316.3262 | 1907.8254
Calibration | $/yr | 4657.7695 | 4657.7695 | 4657.7695 | 4657.7695 | 4657.7695 | 6750.7666
Total Consumables | $/yr | 44078.6992 | 44078.6992 | 44078.6992 | 44078.6992 | 44078.6992 | 63885.7344
Labor | $/yr | 16004.3174 | 16004.3174 | 16004.3174 | 16004.3174 | 16004.3174 | 16523.0156
Patent | $/yr | 326892.1875 | 326892.1875 | 326892.1875 | 326892.1875 | 326892.1875 | 326892.1875
Total O&M | $/yr | 456650.6875 | 456650.6875 | 456650.6875 | 456650.6875 | 456650.6875 | 509652.8438
Total Capital | $ | 1750000 | 1750000 | 1750000 | 1750000 | 1750000 | 1750000
Total Present Worth | $ | 6987747.5 | 6987747.5 | 6987747.5 | 6987747.5 | 6987747.5 | 7595678
Present Worth O&M | $ | 5237747.5 | 5237747.5 | 5237747.5 | 5237747.5 | 5237747.5 | 5845678
Design Power Setting | % | 91.3964 | 91.3964 | 91.3964 | 91.3964 | 91.3964 | 139.1022
UV SYSTEM SIZING CRITERIA
Design Flow | mgd | 126.6087 | 126.6087 | 126.6087 | 126.6087 | 126.6087 | 126.6087
Average Flow | mgd | 59.492 | 59.492 | 59.492 | 59.492 | 59.492 | 59.492
Average UVT | % | 89.6279 | 89.6279 | 89.6279 | 89.6279 | 89.6279 | 89.6279
Design UVT | % | 86.7 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7
Design UV Dose | mJ/cm^2 | 36 | 36 | 36 | 36 | 36 | 50
Minimum Number of Trains |  | 0 | 0 | 0 | 0 | 0 | 0
REACTOR DESIGN INPUTS
Configuration
Max. Flow per reactor | mgd | 30 | 30 | 30 | 30 | 30 | 30
Number of Trains |  | 7 | 7 | 7 | 7 | 7 | 7
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 1 | 1
Banks/Reactor |  | 11 | 11 | 11 | 11 | 11 | 11
Lamps/Bank |  | 12 | 12 | 12 | 12 | 12 | 12
Lamps/Ballast |  | 2 | 2 | 2 | 2 | 2 | 2
Sensors/bank |  | 1 | 1 | 1 | 1 | 1 | 1
Redundancy
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 1 | 1
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
Lamp Life | hrs | 12000 | 12000 | 12000 | 12000 | 12000 | 12000
Lamp Aging Factor | % | 70.2112 | 70.2112 | 70.2112 | 70.2112 | 70.2112 | 70.2112
Lamp Cost | $ | 160 | 160 | 160 | 160 | 160 | 160
Lamp Replacement Time | min | 5 | 5 | 5 | 5 | 5 | 5
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM
Coefficient A |  | 194.4896 | 194.4896 | 194.4896 | 194.4896 | 194.4896 | 194.4896
Coefficient B |  | -343.378 | -343.378 | -343.378 | -343.378 | -343.378 | -343.378
Coefficient C |  | -0.10815 | -0.10815 | -0.10815 | -0.10815 | -0.10815 | -0.10815
Coefficient D |  | 0 | 0 | 0 | 0 | 0 | 0
Coefficient E |  | 0 | 0 | 0 | 0 | 0 | 0
Coefficient F |  | 0 | 0 | 0 | 0 | 0 | 0
Lamp Power | kW | 0 | 0 | 0 | 0 | 0 | 0
Lamp Aging Equation | 9999 | 70.2112 | 70.2112 | 70.2112 | 70.2112 | 70.2112 | 70.2112
Sleeve Data
Sleeve Life | yrs | 10 | 10 | 10 | 10 | 10 | 10
Sleeve Cost | $ | 100 | 100 | 100 | 100 | 100 | 100
Sleeve Replacement Time | min | 5 | 5 | 5 | 5 | 5 | 5
Sleeve Cleaning Type (Rinse, Wiper) |  | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 4 | 4
Sleeve Cleaning Time/Reactor | min | 180 | 180 | 180 | 180 | 180 | 180
Fouling Factor | % | 85 | 85 | 85 | 85 | 85 | 85
Ballast Data
Ballast Life | yrs | 5 | 5 | 5 | 5 | 5 | 5
Ballast Costs | $ | 300 | 300 | 300 | 300 | 300 | 300
Ballast replacement | min | 1 | 1 | 1 | 1 | 1 | 1
Sensor Data
Sensor life | yrs | 10 | 10 | 10 | 10 | 10 | 10
Sensor cost | $ | 650 | 650 | 650 | 650 | 650 | 650
Sensor replacement | min | 10 | 10 | 10 | 10 | 10 | 10
Sensor cal period | months | 12 | 12 | 12 | 12 | 12 | 12
Sensor calibration cost | $ | 230 | 230 | 230 | 230 | 230 | 230
Sensor calibration | min | 5 | 5 | 5 | 5 | 5 | 5
Dose Model and Pacing | Enter if dose pacing responds to the following parameters.
Dose Model |  | 3 | 3 | 3 | 3 | 3 | 3
Dose Model |  | Drinking Water - LPHO - Full Pacing - Case 3 | Drinking Water - LPHO - Full Pacing - Case 3 | Drinking Water - LPHO - Full Pacing - Case 3 | Drinking Water - LPHO - Full Pacing - Case 3 | Drinking Water - LPHO - Full Pacing - Case 3 | Drinking Water - LPHO - Full Pacing - Case 3
Failure Data
Supply Voltage Lower Limit | % nom | 90 | 90 | 90 | 80 | 90 | 90
PQ Event Duration Lower Limit | s | 0.016667 | 0.016667 | 0.016667 | 0.16667 | 0.016667 | 0.016667
UPS (y/n) |  | y | n | n | n | y | n
Generator (y/n) |  | y | n | y | y | y | y
Generator Startup Time | s | 120 | 120 | 120 | 120 | 120 | 120
Automatic Flow Shutoff Valve (y/n) |  | n | n | n | n | n | n
Shut Off Valve Response Time | s | 30 | 30 | 30 | 30 | 30 | 30
Lamp Cool-down Time | min | 4 | 4 | 4 | 2 | 4 | 4
Lamp Warmup Time | min | 5 | 5 | 5 | 2.5 | 5 | 5
Lamp Failure Probability | per day | 0 | 0 | 0 | 0 | 0.1 | 0
Ballast Failure Probability | per day | 0 | 0 | 0 | 0 | 0 | 0
UV Sensor Failure Probability | per day | 0 | 0 | 0 | 0 | 0 | 0
UVT Monitor Failure Probability | per day | 0 | 0 | 0 | 0 | 0 | 0
WTP INPUTS
Labor rate | $/hr | 60 | 60 | 60 | 60 | 60 | 60
Electricity Cost | $/kWhr | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
Interest rate | % | 6 | 6 | 6 | 6 | 6 | 6
Period | yrs | 20 | 20 | 20 | 20 | 20 | 20
Supply Voltage | volts | 480 | 480 | 480 | 480 | 480 | 480
Population |  | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000
CAPITAL COSTS INPUTS
Reactor | Total $ | 1750000 | 1750000 | 1750000 | 1750000 | 1750000 | 1750000
Install Factor | Total $
Validation | Total $
Inlet/Oultet Piping
Valves | Total $
Flowmeters | Total $
Piping and Appurtences | Total $
Channels | Total $
Power
Switch gear | Total $
Transformer | Total $
Distribution Panels | Total $
Generator | Total $
UPS | Total $
Misc Electrical | Total $
Other
Yard piping | Total $
Chlorine contactor | Total $
Low lift pumps | Total $
UV Building
Demolition | Total $
Civil/sitework | Total $
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC
Misc Electrical
Civil/Site Work
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
Ballast Power Settings (%)
Setting 1 |  | 50 | 50 | 50 | 50 | 50 | 50
Setting 2 |  | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Setting 3 |  | 55 | 55 | 55 | 55 | 55 | 55
Setting 4 |  | 57.5 | 57.5 | 57.5 | 57.5 | 57.5 | 57.5
Setting 5 |  | 60 | 60 | 60 | 60 | 60 | 60
Setting 6 |  | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
Setting 7 |  | 65 | 65 | 65 | 65 | 65 | 65
Setting 8 |  | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5
Setting 9 |  | 70 | 70 | 70 | 70 | 70 | 70
Setting 10 |  | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5
Setting 11 |  | 75 | 75 | 75 | 75 | 75 | 75
Setting 12 |  | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
Setting 13 |  | 80 | 80 | 80 | 80 | 80 | 80
Setting 14 |  | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
Setting 15 |  | 85 | 85 | 85 | 85 | 85 | 85
Setting 16 |  | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5
Setting 17 |  | 90 | 90 | 90 | 90 | 90 | 90
Setting 18 |  | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5
Setting 19 |  | 95 | 95 | 95 | 95 | 95 | 95
Setting 20 |  | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
Setting 21 |  | 100 | 100 | 100 | 100 | 100 | 100
Setting 22 |  | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
Setting 23 |  | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
Setting 24 |  | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
Note on A44: Example. Enter 95% as "95" as opposed to "0.95"
Note on A45: Example. Enter 95% as "95" as opposed to "0.95"
Note on A163: Enter ballast power settings in ascending order. Enter "9999" to indicate last ballast setting. UVCAT uses the "9999" to indicate the end of the ballast settings list.
Note on B76: This cell contains a lamp aging equation for fit types MMF, EXP, and LIN that can be copied to other columns.
Advanced LCA
Clear

## WQ
Starting Row | 15
Ending Row | 445 |  |  |  | 604.8
[12 empty] | 116.207 |  | 1.0131
WATER QUALITY INPUTS | [5 empty] | OUTPUTS
[13 empty] | Ideal |  | Daily |  | Sum
Date_Time | Flow | UVT | Pathogens | Supply | PQ | Target | Trains | Reactors | Banks/ | Flow/ | Fouling | Total | Total |  | Power | Power | Power | Offspec | Offspec | Offspec | UV System | Risk | Annual | Accumulated
|  |  |  | Voltage | Event | RED |  | Per Train | Reactor | Reactor | Factor | Power | Power | Ratio | Costs | Costs | Costs | Flag | Time | Volume | Log Kill |  | Risk | Risk
|  |  | Microbes |  | Duration | mJ/cm2 |  |  |  | mgd |  | kW | kW |  | $ | $ | $ |  | % of month | % of month
| mgd | % | per L | V | s
2005-03-06 03:47 | 57.1697 | 90.4723 | 2.7865 | 480 | 0 | 50 | 2 | 1 | 9 | 28.5848 | 1 | 71.928 | 70.5924 | 1.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4898 |  |  | 0
2005-03-07 00:06 | 50.0881 | 90.7427 | 3.4115 | 480 | 0 | 50 | 2 | 1 | 8 | 25.0441 | 0.99546 | 62.208 | 62.0324 | 1.0028 | 149.2992 | 3037.3059 | 126.5544 | 0 | 0 | 0 | 3.4733 | 3.2674e-07 | 0.0001349 | 0.32674
2005-03-08 00:39 | 59.7317 | 89.5345 | 2.6561 | 480 | 0 | 50 | 2 | 1 | 10 | 29.8658 | 0.98998 | 83.808 | 82.3243 | 1.018 | 201.1392 | 4940.4824 | 332.4078 | 0 | 0 | 0 | 3.4726 | 3.0762e-07 | 0.0001052 | 0.63436
2005-03-09 01:01 | 52.4436 | 89.0576 | 3.5724 | 480 | 0 | 50 | 2 | 1 | 10 | 26.2218 | 0.98454 | 77.76 | 77.2922 | 1.0061 | 186.624 | 4548.96 | 521.9478 | 0 | 0 | 0 | 3.4747 | 4.0866e-07 | 0.00014082 | 1.043
2005-03-10 01:32 | 51.4963 | 90.0097 | 2.0357 | 480 | 0 | 50 | 2 | 1 | 9 | 25.7481 | 0.97907 | 71.928 | 70.4067 | 1.0216 | 172.6272 | 4223.9712 | 697.9466 | 0 | 0 | 0 | 3.4918 | 2.2471e-07 | 7.7138e-05 | 1.2677
2005-03-11 02:10 | 53.0004 | 91.9685 | 2.1414 | 480 | 0 | 50 | 2 | 1 | 8 | 26.5002 | 0.97357 | 60.48 | 59.0756 | 1.0238 | 145.152 | 3578.9036 | 847.0676 | 0 | 0 | 0 | 3.4948 | 2.3659e-07 | 8.0601e-05 | 1.5043
2005-03-12 02:42 | 50.0981 | 89.939 | 1.8978 | 480 | 0 | 50 | 2 | 1 | 9 | 25.049 | 0.96809 | 71.712 | 70.6199 | 1.0155 | 172.1088 | 4227.4219 | 1023.2101 | 0 | 0 | 0 | 3.4716 | 2.2034e-07 | 7.5349e-05 | 1.7247
2005-03-13 03:16 | 60.8423 | 90.2798 | 1.3428 | 480 | 0 | 50 | 3 | 1 | 7 | 20.2808 | 0.9626 | 87.696 | 86.7338 | 1.0111 | 210.4705 | 5169.6812 | 1238.6135 | 0 | 0 | 0 | 3.4819 | 1.5223e-07 | 5.206e-05 | 1.8769
2005-03-14 03:43 | 53.1385 | 90.0341 | 1.8383 | 480 | 0 | 50 | 2 | 1 | 9 | 26.5693 | 0.95714 | 75.816 | 75.6176 | 1.0026 | 181.9584 | 4452.2949 | 1424.1259 | 0 | 0 | 0 | 3.4707 | 2.1306e-07 | 7.3141e-05 | 2.09
2005-03-15 00:16 | 62.8603 | 91.7795 | 1.3456 | 480 | 0 | 50 | 3 | 1 | 7 | 20.9534 | 0.95256 | 76.356 | 75.8969 | 1.006 | 183.2544 | 3762.4426 | 1580.8943 | 0 | 0 | 0 | 3.4767 | 1.2905e-07 | 5.2799e-05 | 2.219
2005-03-16 03:54 | 58.364 | 89.4994 | 1.9958 | 480 | 0 | 50 | 2 | 1 | 11 | 29.182 | 0.94639 | 86.832 | 85.682 | 1.0134 | 208.3968 | 5763.4736 | 1821.0391 | 0 | 0 | 0 | 3.4717 | 2.6082e-07 | 7.9215e-05 | 2.4798
2005-03-17 00:12 | 55.086 | 91.737 | 1.145 | 480 | 0 | 50 | 2 | 1 | 8 | 27.543 | 0.94187 | 67.392 | 67.2177 | 1.0026 | 161.7408 | 3275.2517 | 1957.5079 | 0 | 0 | 0 | 3.4718 | 1.0954e-07 | 4.5438e-05 | 2.5894
2005-03-18 00:45 | 51.8075 | 91.827 | 1.103 | 480 | 0 | 50 | 2 | 1 | 8 | 25.9038 | 0.93638 | 63.936 | 63.141 | 1.0126 | 153.4464 | 3769.0266 | 2114.5508 | 0 | 0 | 0 | 3.4822 | 1.2497e-07 | 4.2737e-05 | 2.7143
2005-03-19 01:24 | 49.6107 | 90.4426 | 1.3014 | 480 | 0 | 50 | 2 | 1 | 9 | 24.8054 | 0.93088 | 71.712 | 70.5117 | 1.017 | 172.1088 | 4243.5571 | 2291.3657 | 0 | 0 | 0 | 3.4868 | 1.4645e-07 | 4.9891e-05 | 2.8608
2005-03-20 01:55 | 40.9747 | 90.737 | 1.0605 | 480 | 0 | 50 | 2 | 1 | 7 | 20.4873 | 0.92542 | 60.48 | 60.1152 | 1.0061 | 145.152 | 3551.6882 | 2439.3528 | 0 | 0 | 0 | 3.4767 | 1.2122e-07 | 4.1613e-05 | 2.982
2005-03-21 02:27 | 56.008 | 91.1744 | 1.4311 | 480 | 0 | 50 | 2 | 1 | 9 | 28.004 | 0.91994 | 75.384 | 74.1855 | 1.0162 | 180.9216 | 4443.8877 | 2624.5149 | 0 | 0 | 0 | 3.474 | 1.6521e-07 | 5.6498e-05 | 3.1472
2005-03-22 03:14 | 52.1987 | 90.8101 | 1.1905 | 480 | 0 | 50 | 2 | 1 | 9 | 26.0994 | 0.91441 | 73.656 | 73.0293 | 1.0086 | 176.7744 | 4375.167 | 2806.8135 | 0 | 0 | 0 | 3.4775 | 1.3737e-07 | 4.6623e-05 | 3.2846
2005-03-23 03:55 | 55.2872 | 90.117 | 0.88207 | 480 | 0 | 50 | 2 | 1 | 10 | 27.6436 | 0.90889 | 83.592 | 82.5549 | 1.0126 | 200.6208 | 4965.3657 | 3013.7036 | 0 | 0 | 0 | 3.4807 | 1.0105e-07 | 3.4295e-05 | 3.3856
2005-03-24 03:25 | 43.296 | 90.0973 | 1.1642 | 480 | 0 | 50 | 2 | 1 | 9 | 21.648 | 0.90366 | 67.824 | 67.2851 | 1.008 | 162.7776 | 3815.0994 | 3172.666 | 0 | 0 | 0 | 3.4761 | 1.2762e-07 | 4.5738e-05 | 3.5133
2005-03-25 03:54 | 48.3784 | 89.5831 | 1.2889 | 480 | 0 | 50 | 2 | 1 | 10 | 24.1892 | 0.89817 | 79.272 | 78.3773 | 1.0114 | 190.2528 | 4673.084 | 3367.3779 | 0 | 0 | 0 | 3.4794 | 1.4695e-07 | 5.0254e-05 | 3.6602
2005-03-26 00:20 | 52.3121 | 89.8124 | 1.8126 | 480 | 0 | 50 | 2 | 1 | 10 | 26.156 | 0.89361 | 83.592 | 83.1857 | 1.0049 | 200.6208 | 4100.1885 | 3538.219 | 0 | 0 | 0 | 3.4732 | 1.7444e-07 | 7.1692e-05 | 3.8346
2005-03-27 00:51 | 54.5584 | 90.7258 | 0.92558 | 480 | 0 | 50 | 2 | 1 | 10 | 27.2792 | 0.88815 | 79.272 | 78.5291 | 1.0095 | 190.2528 | 4655.2476 | 3732.1877 | 0 | 0 | 0 | 3.4764 | 1.0586e-07 | 3.6342e-05 | 3.9405
2005-03-28 01:25 | 53.3209 | 90.5691 | 0.35823 | 480 | 0 | 50 | 2 | 1 | 10 | 26.6604 | 0.88267 | 79.488 | 78.9836 | 1.0064 | 190.7712 | 4685.8169 | 3927.4302 | 0 | 0 | 0 | 3.4731 | 4.1444e-08 | 1.4173e-05 | 3.9819
2005-03-29 02:00 | 44.8258 | 89.5307 | 1.4574 | 480 | 0 | 50 | 2 | 1 | 10 | 22.4129 | 0.87718 | 77.112 | 75.8171 | 1.0171 | 185.0688 | 4545.7524 | 4116.8364 | 0 | 0 | 0 | 3.4828 | 1.649e-07 | 5.6391e-05 | 4.1468
2005-03-30 02:55 | 65.5065 | 91.0242 | 0.60788 | 480 | 0 | 50 | 3 | 1 | 8 | 21.8355 | 0.87162 | 97.416 | 95.943 | 1.0154 | 233.7984 | 5830.3477 | 4359.7676 | 0 | 0 | 0 | 3.4752 | 7.1051e-08 | 2.3933e-05 | 4.2179
2005-03-31 03:30 | 63.7547 | 90.9483 | 1.1413 | 480 | 0 | 50 | 3 | 1 | 8 | 21.2516 | 0.86613 | 95.904 | 95.2441 | 1.0069 | 230.1696 | 5653.5405 | 4595.3315 | 0 | 0 | 0 | 3.4762 | 1.3109e-07 | 4.4829e-05 | 4.349
2005-04-01 00:02 | 55.5897 | 91.0428 | 1.8779 | 395.4 | 0.11 | 50 | 2 | 1 | 10 | 27.7948 | 0.86155 | 81.432 | 80.4776 | 1.0119 | 195.4368 | 4012.562 | 4762.5215 | 0.0073059 | 0 | 0 | 2.1173 | 4.1207e-06 | 0.0016845 | 8.4697
2005-04-02 00:41 | 58.9983 | 91.0413 | 1.662 | 480 | 0 | 50 | 2 | 1 | 11 | 29.4991 | 0.85605 | 84.24 | 83.7817 | 1.0055 | 202.176 | 4984.9023 | 4970.2256 | 0 | 0 | 0 | 3.4724 | 1.9333e-07 | 6.5862e-05 | 8.663
2005-04-03 01:06 | 43.5649 | 91.4208 | 4.0321 | 480 | 0 | 50 | 2 | 1 | 8 | 21.7825 | 0.85059 | 65.664 | 64.7998 | 1.0133 | 157.5936 | 3856.1187 | 5130.897 | 0 | 0 | 0 | 3.4831 | 4.5415e-07 | 0.0001559 | 9.1172
2005-04-04 02:30 | 58.1476 | 91.7919 | 1.905 | 480 | 0 | 50 | 2 | 1 | 9 | 29.0738 | 0.99491 | 69.768 | 68.7826 | 1.0143 | 167.4432 | 4254.1045 | 5308.1514 | 0 | 0 | 0 | 3.4841 | 2.2227e-07 | 7.3486e-05 | 9.3394
2005-04-05 03:17 | 63.9246 | 91.778 | 3.1137 | 480 | 0 | 50 | 3 | 1 | 7 | 21.3082 | 0.98939 | 79.38 | 78.4484 | 1.0119 | 190.512 | 4715.1729 | 5504.6167 | 0 | 0 | 0 | 3.4828 | 3.5496e-07 | 0.00012046 | 9.6944
2005-04-06 03:49 | 50.4285 | 89.079 | 0.99966 | 480 | 0 | 50 | 2 | 1 | 10 | 25.2142 | 0.98391 | 83.16 | 81.7007 | 1.0179 | 199.584 | 4902.2822 | 5708.8784 | 0 | 0.020725 | 0.022917 | 3.4743 | 1.1533e-07 | 3.9441e-05 | 9.8097
2005-04-07 00:19 | 50.5646 | 90.5188 | 0.30813 | 480 | 0 | 50 | 2 | 1 | 9 | 25.2823 | 0.97935 | 73.224 | 71.6405 | 1.0221 | 175.7376 | 3591.6372 | 5858.5298 | 0 | 0.020156 | 0.022327 | 3.4729 | 2.9675e-08 | 1.2196e-05 | 9.8394
2005-04-08 01:12 | 55.7088 | 91.8491 | 2.4277 | 480 | 0 | 50 | 2 | 1 | 9 | 27.8544 | 0.97378 | 67.824 | 67.4525 | 1.0055 | 162.7776 | 4059.2656 | 6027.666 | 0 | 0.020828 | 0.02313 | 3.4749 | 2.84e-07 | 9.5659e-05 | 10.1234
2005-04-09 01:59 | 52.7838 | 90.666 | 2.8455 | 480 | 0 | 50 | 2 | 1 | 9 | 26.3919 | 0.96825 | 75.6 | 74.6707 | 1.0124 | 181.44 | 4490.6406 | 6214.7759 | 0 | 0.02082 | 0.023087 | 3.4818 | 3.2514e-07 | 0.00011035 | 10.4485
2005-04-10 02:26 | 55.5924 | 92.3017 | 2.1548 | 480 | 0 | 50 | 2 | 1 | 8 | 27.7962 | 0.96279 | 67.392 | 66.3599 | 1.0156 | 161.7408 | 3957.5959 | 6379.6758 | 0 | 0.020825 | 0.023065 | 3.4852 | 2.4153e-07 | 8.2914e-05 | 10.6901
2005-04-11 02:50 | 56.7547 | 91.0465 | 1.7172 | 480 | 0 | 50 | 2 | 1 | 10 | 28.3774 | 0.95735 | 76.896 | 75.625 | 1.0168 | 184.5504 | 4498.4165 | 6567.1099 | 0 | 0.020831 | 0.023004 | 3.4716 | 1.9782e-07 | 6.817e-05 | 10.8879
2005-04-12 03:12 | 59.8016 | 89.716 | 1.3521 | 480 | 0 | 50 | 2 | 1 | 11 | 29.9008 | 0.95191 | 92.88 | 91.4597 | 1.0155 | 222.912 | 5433.48 | 6793.5049 | 0 | 0.020149 | 0.022194 | 3.4723 | 1.5551e-07 | 5.3589e-05 | 11.0434
2005-04-13 03:35 | 47.8752 | 91.0582 | 1.9653 | 480 | 0 | 50 | 2 | 1 | 8 | 23.9376 | 0.94647 | 69.12 | 68.5227 | 1.0087 | 165.888 | 4043.5203 | 6961.9849 | 0 | 0.020154 | 0.022221 | 3.4782 | 2.2298e-07 | 7.684e-05 | 11.2664
2005-04-14 04:04 | 60.5543 | 90.4717 | 1.6199 | 480 | 0 | 50 | 3 | 1 | 8 | 20.1848 | 0.94101 | 92.124 | 90.5574 | 1.0173 | 221.0976 | 5409.9824 | 7187.4009 | 0 | 0.020725 | 0.015292 | 3.4734 | 1.8656e-07 | 6.4042e-05 | 11.4529
2005-04-15 01:32 | 53.0385 | 91.7964 | 1.2213 | 480 | 0 | 50 | 2 | 1 | 9 | 26.5192 | 0.93622 | 69.552 | 68.2505 | 1.0191 | 166.9248 | 3583.667 | 7336.7202 | 0 | 0.020128 | 0.022243 | 3.4716 | 1.2393e-07 | 4.849e-05 | 11.5769
2005-04-16 02:13 | 56.6496 | 90.7872 | 2.8981 | 480 | 0 | 50 | 2 | 1 | 10 | 28.3248 | 0.93069 | 81.432 | 80.9563 | 1.0059 | 195.4368 | 4837.061 | 7538.2646 | 0 | 0.020774 | 0.023085 | 3.4731 | 3.3784e-07 | 0.00011465 | 11.9147
2005-04-17 02:35 | 57.4163 | 89.9098 | 1.6266 | 480 | 0 | 50 | 2 | 1 | 11 | 28.7081 | 0.92525 | 90.504 | 89.1506 | 1.0152 | 217.2096 | 5294.4839 | 7758.8682 | 0 | 0.020779 | 0.023039 | 3.4704 | 1.8791e-07 | 6.4754e-05 | 12.1026
2005-04-18 02:57 | 51.3322 | 89.7987 | 1.4429 | 480 | 0 | 50 | 2 | 1 | 10 | 25.6661 | 0.91983 | 85.32 | 83.9176 | 1.0167 | 204.768 | 4972.0229 | 7966.0356 | 0 | 0.02079 | 0.022998 | 3.4719 | 1.6549e-07 | 5.7251e-05 | 12.2681
2005-04-19 03:30 | 49.5259 | 90.4503 | 1.4534 | 480 | 0 | 50 | 2 | 1 | 10 | 24.763 | 0.91435 | 77.112 | 75.5424 | 1.0208 | 185.0688 | 4545.7524 | 8155.4419 | 0 | 0.020787 | 0.022921 | 3.4896 | 1.6187e-07 | 5.5355e-05 | 12.43
2005-04-20 04:03 | 49.5703 | 91.5256 | 1.6548 | 480 | 0 | 50 | 2 | 1 | 9 | 24.7852 | 0.90887 | 69.768 | 68.6965 | 1.0156 | 167.4432 | 4112.8242 | 8326.8096 | 0 | 0.020787 | 0.022906 | 3.4854 | 1.861e-07 | 6.3642e-05 | 12.6161
2005-04-21 00:39 | 42.621 | 91.7341 | 1.7574 | 480 | 0 | 50 | 2 | 1 | 8 | 21.3105 | 0.90426 | 60.48 | 59.5692 | 1.0153 | 145.152 | 2993.7595 | 8451.5498 | 0 | 0.02021 | 0.022362 | 3.4851 | 1.6605e-07 | 6.7626e-05 | 12.7821
2005-04-21 04:45 | 46.8113 | 91.0676 | 1.4225 | 480 | 0 | 50 | 2 | 1 | 9 | 23.4057 | 0.90334 | 69.768 | 69.2407 | 1.0076 | 167.4432 | 690.7033 | 8480.3291 | 0 | 0.020787 | 0.023026 | 3.4772 | 2.7378e-08 | 5.575e-05 | 12.8095
2005-04-22 01:42 | 51.84 | 90.3845 | 1.9152 | 480 | 0 | 50 | 2 | 1 | 10 | 25.92 | 0.89867 | 83.16 | 81.5201 | 1.0201 | 199.584 | 4172.5532 | 8654.1855 | 0 | 0.020202 | 0.022431 | 3.4747 | 1.8791e-07 | 7.5499e-05 | 12.9974
2005-04-23 02:07 | 79.9608 | 88.95 | 2.9005 | 480 | 0 | 50 | 4 | 1 | 9 | 19.9902 | 0.89321 | 145.26 | 144.2269 | 1.0072 | 348.624 | 8530.3926 | 9009.6182 | 0 | 0.02021 | 0.011137 | 3.473 | 3.3439e-07 | 0.00011479 | 13.3318
2005-04-24 02:25 | 50.4851 | 90.2275 | 2.8887 | 480 | 0 | 50 | 2 | 1 | 10 | 25.2425 | 0.88779 | 83.376 | 82.1872 | 1.0145 | 200.1024 | 4858.7368 | 9212.0654 | 0 | 0.020187 | 0.022038 | 3.4748 | 3.2909e-07 | 0.00011384 | 13.6609
2005-04-25 02:48 | 52.2759 | 89.8757 | 1.9557 | 480 | 0 | 50 | 2 | 1 | 11 | 26.138 | 0.88235 | 88.128 | 86.7025 | 1.0164 | 211.5072 | 5155.4888 | 9426.8779 | 0 | 0.020763 | 0.022539 | 3.4706 | 2.2583e-07 | 7.7821e-05 | 13.8867
2005-04-26 02:24 | 50.1631 | 91.5671 | 2.521 | 480 | 0 | 50 | 2 | 1 | 9 | 25.0815 | 0.87708 | 73.656 | 72.4331 | 1.0169 | 176.7744 | 4176.2954 | 9600.8906 | 0 | 0.020787 | 0.022594 | 3.4869 | 2.7174e-07 | 9.6615e-05 | 14.1585
2005-04-27 03:00 | 59.6461 | 86.9788 | 3.0898 | 480 | 0 | 50 | 3 | 1 | 11 | 19.882 | 0.8716 | 135.324 | 133.8565 | 1.011 | 324.7776 | 7977.3496 | 9933.2803 | 0 | 0.020787 | 0.015054 | 3.4748 | 3.5609e-07 | 0.00012177 | 14.5146
2005-04-28 03:26 | 71.9197 | 91.4482 | 4.211 | 480 | 0 | 50 | 3 | 1 | 9 | 23.9732 | 0.86613 | 103.68 | 103.0365 | 1.0062 | 248.832 | 6088.6094 | 10186.9727 | 0 | 0.02079 | 0.014902 | 3.4748 | 4.8338e-07 | 0.00016593 | 14.998
2005-04-29 03:44 | 52.6055 | 91.7219 | 3.6225 | 480 | 0 | 50 | 2 | 1 | 9 | 26.3028 | 0.86071 | 77.544 | 76.2896 | 1.0164 | 186.1056 | 4518.877 | 10375.2588 | 0 | 0.020809 | 0.022277 | 3.4865 | 4.017e-07 | 0.00013896 | 15.3997
2005-04-30 00:14 | 41.1904 | 88.0499 | 6.0115 | 0 | 2723 | 50 | 2 | 1 | 11 | 20.5952 | 0.85615 | 88.56 | 87.3797 | 1.0135 | 212.5441 | 4343.8691 | 10556.2529 | 0.0073394 | 0.04047 | 0.038858 | 2.1151 | 1.3196e-05 | 0.0054092 | 28.596 | 13.1963
2005-05-01 00:30 | 58.496 | 91.4893 | 4.1455 | 480 | 0 | 50 | 2 | 1 | 11 | 29.248 | 0.85073 | 84.024 | 83.5492 | 1.0057 | 201.6576 | 4896.499 | 10760.2734 | 0 | 0.02082 | 0.017793 | 3.4704 | 4.7711e-07 | 0.00016504 | 29.0731
2005-05-02 00:53 | 58.9993 | 90.8344 | 7.5108 | 480 | 0 | 50 | 2 | 1 | 10 | 29.4997 | 0.99529 | 81.432 | 80.692 | 1.0092 | 195.4368 | 4763.7725 | 10958.7637 | 0 | 0.020828 | 0.017785 | 3.4757 | 8.5724e-07 | 0.00029538 | 29.9304
2005-05-03 01:25 | 73.503 | 89.0788 | 5.8944 | 480 | 0 | 50 | 3 | 1 | 10 | 24.501 | 0.98981 | 120.96 | 119.8323 | 1.0094 | 290.304 | 7130.5923 | 11255.8721 | 0 | 0.020825 | 0.011746 | 3.474 | 6.8059e-07 | 0.00023272 | 30.6109
2005-05-04 01:52 | 40.8309 | 90.6819 | 8.4196 | 480 | 0 | 50 | 2 | 1 | 8 | 20.4155 | 0.98435 | 62.208 | 61.0442 | 1.0191 | 149.2992 | 3653.165 | 11408.0869 | 0 | 0.020141 | 0.017022 | 3.4892 | 9.351e-07 | 0.00032096 | 31.546
2005-05-05 02:14 | 84.5628 | 91.1945 | 1.7357 | 480 | 0 | 50 | 3 | 1 | 10 | 28.1876 | 0.97891 | 110.808 | 108.7497 | 1.0189 | 265.9392 | 6482.2681 | 11678.1816 | 0 | 0.020169 | 0.011284 | 3.4717 | 1.999e-07 | 6.8887e-05 | 31.7459
2005-05-06 02:36 | 64.2739 | 89.2012 | 3.8136 | 480 | 0 | 50 | 3 | 1 | 9 | 21.4246 | 0.97347 | 109.512 | 108.6806 | 1.0076 | 262.8288 | 6406.4521 | 11945.1172 | 0 | 0.020179 | 0.011202 | 3.4767 | 4.3422e-07 | 0.00014963 | 32.1802
2005-05-07 02:50 | 65.6092 | 89.0672 | 7.4423 | 480 | 0 | 50 | 3 | 1 | 10 | 21.8697 | 0.96807 | 111.456 | 110.4258 | 1.0093 | 267.4944 | 6470.021 | 12214.7012 | 0 | 0.02076 | 0.011439 | 3.4744 | 8.4541e-07 | 0.00029356 | 33.0256
2005-05-08 03:13 | 72.7912 | 90.6982 | 0.97047 | 480 | 0 | 50 | 3 | 1 | 9 | 24.2637 | 0.96263 | 106.488 | 104.7898 | 1.0162 | 255.5712 | 6229.5474 | 12474.2656 | 0 | 0.020777 | 0.011339 | 3.4799 | 1.0969e-07 | 3.7799e-05 | 33.1353
2005-05-09 03:31 | 74.6475 | 89.8149 | 12.3176 | 480 | 0 | 50 | 3 | 1 | 10 | 24.8825 | 0.95718 | 117.936 | 117.0614 | 1.0075 | 283.0464 | 6899.2559 | 12761.7344 | 0 | 0.020787 | 0.011215 | 3.4725 | 1.416e-06 | 0.00048784 | 34.5512
2005-05-10 03:53 | 66.6144 | 90.6484 | 4.1405 | 480 | 0 | 50 | 3 | 1 | 9 | 22.2048 | 0.95176 | 98.928 | 98.0191 | 1.0093 | 237.4272 | 5765.0293 | 13001.9443 | 0 | 0.020793 | 0.011112 | 3.4723 | 4.7445e-07 | 0.00016412 | 35.0257
2005-05-11 00:15 | 76.8463 | 90.4892 | 1.082 | 480 | 0 | 50 | 3 | 1 | 10 | 25.6154 | 0.9472 | 114.696 | 112.8377 | 1.0165 | 275.2704 | 5625.8398 | 13236.3545 | 0 | 0.02022 | 0.010739 | 3.48 | 1.0251e-07 | 4.2132e-05 | 35.1282
2005-05-12 00:35 | 50.7196 | 90.2964 | 1.0392 | 480 | 0 | 50 | 2 | 1 | 10 | 25.3598 | 0.94178 | 81 | 79.3953 | 1.0202 | 194.4 | 4720.2754 | 13433.0322 | 0 | 0.020222 | 0.016042 | 3.4736 | 1.187e-07 | 4.1063e-05 | 35.2469
2005-05-13 00:56 | 60.9337 | 91.1046 | 0.96907 | 480 | 0 | 50 | 3 | 1 | 8 | 20.3112 | 0.93634 | 90.612 | 89.0132 | 1.018 | 217.4689 | 5300.8032 | 13653.8994 | 0 | 0.020222 | 0.01071 | 3.4829 | 1.0877e-07 | 3.7483e-05 | 35.3556
2005-05-14 01:16 | 42.1449 | 90.3461 | 1.2043 | 480 | 0 | 50 | 2 | 1 | 9 | 21.0725 | 0.9309 | 69.768 | 68.4416 | 1.0194 | 167.4432 | 4081.4285 | 13823.959 | 0 | 0.020222 | 0.016085 | 3.4856 | 1.3434e-07 | 4.6296e-05 | 35.49
2005-05-15 01:38 | 56.169 | 89.0352 | 1.3715 | 480 | 0 | 50 | 3 | 1 | 9 | 18.723 | 0.92548 | 104.544 | 103.5433 | 1.0097 | 250.9055 | 6092.3003 | 14077.8047 | 0 | 0.020831 | 0.011065 | 3.4722 | 1.5719e-07 | 5.4378e-05 | 35.6472
2005-05-16 02:00 | 70.5957 | 90.3362 | 1.1722 | 480 | 0 | 50 | 3 | 1 | 10 | 23.5319 | 0.92004 | 111.348 | 109.5229 | 1.0167 | 267.2352 | 6513.8589 | 14349.2158 | 0 | 0.020149 | 0.010676 | 3.4736 | 1.3443e-07 | 4.6326e-05 | 35.7816
2005-05-17 02:21 | 63.7549 | 90.689 | 0.43952 | 480 | 0 | 50 | 3 | 1 | 9 | 21.2516 | 0.9146 | 99.036 | 98.2763 | 1.0077 | 237.6864 | 5793.6064 | 14590.6162 | 0 | 0.020159 | 0.010609 | 3.4737 | 5.0387e-08 | 1.7364e-05 | 35.832
2005-05-18 02:42 | 81.2001 | 91.3287 | 1.3491 | 480 | 0 | 50 | 3 | 1 | 10 | 27.0667 | 0.90916 | 115.56 | 113.3341 | 1.0196 | 277.3439 | 6760.2583 | 14872.2939 | 0 | 0.020159 | 0.010519 | 3.4808 | 1.5216e-07 | 5.2437e-05 | 35.9842
2005-05-19 02:58 | 72.1502 | 89.6161 | 1.5666 | 480 | 0 | 50 | 3 | 1 | 11 | 24.0501 | 0.90374 | 122.364 | 121.0144 | 1.0112 | 293.6736 | 7130.7632 | 15169.4092 | 0 | 0.020159 | 0.010393 | 3.474 | 1.7878e-07 | 6.1846e-05 | 36.1629
2005-05-20 03:17 | 61.4438 | 89.7813 | 1.6972 | 480 | 0 | 50 | 3 | 1 | 9 | 20.4813 | 0.89832 | 109.62 | 108.0791 | 1.0143 | 263.088 | 6388.105 | 15435.5801 | 0 | 0.020166 | 0.010305 | 3.4807 | 1.9073e-07 | 6.5979e-05 | 36.3537
2005-05-21 03:43 | 75.6355 | 90.2234 | 1.6307 | 480 | 0 | 50 | 3 | 1 | 10 | 25.2118 | 0.89286 | 125.28 | 123.7174 | 1.0126 | 300.672 | 7357.0688 | 15742.125 | 0 | 0.020744 | 0.010418 | 3.4745 | 1.8731e-07 | 6.4301e-05 | 36.541
2005-05-22 00:03 | 51.7206 | 90.965 | 1.7988 | 480 | 0 | 50 | 2 | 1 | 10 | 25.8603 | 0.88832 | 81.432 | 80.1475 | 1.016 | 195.4368 | 3975.9177 | 15907.7881 | 0 | 0.020289 | 0.01525 | 3.4802 | 1.6956e-07 | 7.0011e-05 | 36.7105
2005-05-22 04:05 | 46.2548 | 89.8086 | 1.0124 | 480 | 0 | 50 | 2 | 1 | 10 | 23.1274 | 0.88742 | 83.592 | 82.4667 | 1.0136 | 200.6208 | 808.7527 | 15941.4863 | 0 | 0.020763 | 0.015531 | 3.4783 | 1.8996e-08 | 3.9582e-05 | 36.7295
2005-05-23 00:16 | 34.4339 | 90.1085 | 1.4779 | 480 | 0 | 50 | 2 | 1 | 8 | 17.217 | 0.88292 | 63.936 | 63.0502 | 1.014 | 153.4464 | 3092.9036 | 16070.3574 | 0 | 0.020199 | 0.015257 | 3.4842 | 1.3676e-07 | 5.6994e-05 | 36.8663
2005-05-24 00:42 | 49.319 | 88.6817 | 1.3045 | 480 | 0 | 50 | 3 | 1 | 9 | 16.4397 | 0.87748 | 102.06 | 101.2604 | 1.0079 | 244.9441 | 5970.5117 | 16319.1289 | 0 | 0.020202 | 0.010303 | 3.4754 | 1.4897e-07 | 5.1337e-05 | 37.0153
2005-05-25 01:01 | 75.9068 | 88.6753 | 1.0735 | 347 | 0.23667 | 50 | 4 | 1 | 10 | 18.9767 | 0.87204 | 149.04 | 147.2108 | 1.0124 | 357.696 | 8718.8408 | 16682.4141 | 0.0061538 | 0.040399 | 0.028398 | 2.1878 | 2.3772e-06 | 0.00081888 | 39.3925
2005-05-26 00:27 | 46.229 | 89.0576 | 1.4022 | 480 | 0 | 50 | 2 | 1 | 11 | 23.1145 | 0.8668 | 90.72 | 89.4932 | 1.0137 | 217.728 | 5103.0005 | 16895.0391 | 0 | 0.04045 | 0.035993 | 3.4708 | 1.556e-07 | 5.5765e-05 | 39.5481
2005-05-27 01:02 | 62.4973 | 89.6264 | 1.4521 | 480 | 0 | 50 | 3 | 1 | 10 | 20.8324 | 0.86132 | 115.668 | 114.5358 | 1.0099 | 277.6031 | 6818.6265 | 17179.1484 | 0 | 0.040399 | 0.030771 | 3.4729 | 1.6807e-07 | 5.7476e-05 | 39.7161
2005-05-28 01:40 | 51.5229 | 91.2629 | 1.449 | 480 | 0 | 50 | 2 | 1 | 10 | 25.7615 | 0.85582 | 81.432 | 80.4468 | 1.0122 | 195.4368 | 4818.7388 | 17379.9297 | 0 | 0.040394 | 0.03585 | 3.4764 | 1.6699e-07 | 5.6888e-05 | 39.8831
2005-05-29 02:02 | 41.4174 | 89.1471 | 1.2548 | 480 | 0 | 50 | 2 | 1 | 10 | 20.7087 | 0.85038 | 85.32 | 83.8842 | 1.0171 | 204.768 | 4991.2202 | 17587.8965 | 0 | 0.040399 | 0.036227 | 3.4705 | 1.4493e-07 | 4.9943e-05 | 40.028
2005-05-30 02:31 | 52.6256 | 89.2966 | 1.545 | 480 | 0 | 50 | 2 | 1 | 11 | 26.3128 | 0.99491 | 88.56 | 86.7918 | 1.0204 | 212.5441 | 5200.6875 | 17804.5918 | 0 | 0.020766 | 0.021334 | 3.4836 | 1.7379e-07 | 5.966e-05 | 40.2018
2005-05-31 03:00 | 74.4613 | 88.5299 | 1.7563 | 480 | 0 | 50 | 3 | 1 | 11 | 24.8204 | 0.98945 | 132.84 | 131.0754 | 1.0135 | 318.816 | 7801.0293 | 18129.6348 | 0 | 0.02076 | 0.021168 | 3.4741 | 2.0194e-07 | 6.9321e-05 | 40.4038
2005-06-01 03:38 | 68.9394 | 90.458 | 2.6502 | 480 | 0 | 50 | 3 | 1 | 9 | 22.9798 | 0.98395 | 104.652 | 103.6628 | 1.0095 | 251.1647 | 6192.7803 | 18387.668 | 0 | 0.020752 | 0.021009 | 3.4721 | 3.0852e-07 | 0.0001051 | 40.7123
2005-06-02 03:05 | 60.923 | 87.2808 | 4.7107 | 480 | 0 | 50 | 3 | 1 | 11 | 20.3077 | 0.97872 | 125.928 | 124.7019 | 1.0098 | 302.2271 | 7083.4487 | 18682.8125 | 0 | 0.020785 | 0.021059 | 3.4714 | 5.2207e-07 | 0.00018709 | 41.2344
2005-06-03 02:34 | 66.0167 | 88.1097 | 2.6154 | 480 | 0 | 50 | 3 | 1 | 11 | 22.0056 | 0.97349 | 125.928 | 124.3898 | 1.0124 | 302.2271 | 7083.4487 | 18977.957 | 0 | 0.020814 | 0.021017 | 3.4742 | 2.8802e-07 | 0.00010322 | 41.5224
2005-06-04 03:01 | 54.0591 | 87.237 | 3.4838 | 480 | 0 | 50 | 3 | 1 | 10 | 18.0197 | 0.96802 | 118.8 | 116.3054 | 1.0214 | 285.12 | 6976.5298 | 19268.6465 | 0 | 0.020812 | 0.021045 | 3.4814 | 3.9392e-07 | 0.00013522 | 41.9163
2005-06-05 03:31 | 46.7477 | 86.3959 | 3.5477 | 480 | 0 | 50 | 3 | 1 | 10 | 15.5826 | 0.96254 | 112.428 | 110.6993 | 1.0156 | 269.8273 | 6627.6323 | 19544.7969 | 0 | 0.020806 | 0.02132 | 3.4761 | 4.0758e-07 | 0.00013938 | 42.3239
2005-06-06 04:03 | 71.336 | 89.3617 | 4.1285 | 480 | 0 | 50 | 3 | 1 | 10 | 23.7787 | 0.95708 | 125.28 | 123.0007 | 1.0185 | 300.672 | 7357.0688 | 19851.3418 | 0 | 0.020798 | 0.021381 | 3.4793 | 4.6907e-07 | 0.00016101 | 42.7929
2005-06-07 00:37 | 25.8097 | 89.5259 | 4.1402 | 480 | 0 | 50 | 1 | 1 | 11 | 25.8097 | 0.95248 | 44.28 | 43.7151 | 1.0129 | 106.272 | 2191.8599 | 19942.6699 | 0 | 0.02022 | 0.020904 | 3.4755 | 3.9995e-07 | 0.00016287 | 43.1929
2005-06-08 01:06 | 64.9258 | 90.6834 | 4.4586 | 480 | 0 | 50 | 3 | 1 | 9 | 21.6419 | 0.94701 | 101.736 | 99.6068 | 1.0214 | 244.1665 | 5974.4482 | 20191.6055 | 0 | 0.020217 | 0.021176 | 3.4817 | 5.0379e-07 | 0.00017293 | 43.6967
2005-06-09 01:36 | 66.6386 | 90.6416 | 5.2007 | 480 | 0 | 50 | 3 | 1 | 9 | 22.2129 | 0.94155 | 104.76 | 103.5015 | 1.0122 | 251.4239 | 6152.0288 | 20447.9395 | 0 | 0.020215 | 0.021266 | 3.4765 | 5.9476e-07 | 0.00020416 | 44.2914
2005-06-10 02:09 | 51.9718 | 87.4195 | 2.8189 | 480 | 0 | 50 | 3 | 1 | 10 | 17.3239 | 0.93607 | 115.776 | 114.2367 | 1.0135 | 277.8623 | 6824.9927 | 20732.3145 | 0 | 0.020779 | 0.02213 | 3.4741 | 3.2539e-07 | 0.00011127 | 44.6168
2005-06-11 02:43 | 63.7623 | 88.9602 | 4.8449 | 480 | 0 | 50 | 3 | 1 | 10 | 21.2541 | 0.93059 | 121.608 | 119.0758 | 1.0213 | 291.8592 | 7168.792 | 21031.0137 | 0 | 0.020771 | 0.022197 | 3.4746 | 5.5861e-07 | 0.00019102 | 45.1755
2005-06-12 03:11 | 59.5056 | 89.1456 | 3.7262 | 480 | 0 | 50 | 3 | 1 | 9 | 19.8352 | 0.92513 | 113.724 | 112.6679 | 1.0094 | 272.9377 | 6678.4434 | 21309.2812 | 0 | 0.020768 | 0.02212 | 3.4776 | 4.2506e-07 | 0.00014591 | 45.6005
2005-06-13 03:37 | 70.6033 | 89.5403 | 6.0555 | 480 | 0 | 50 | 3 | 1 | 10 | 23.5344 | 0.91966 | 125.82 | 125.1469 | 1.0054 | 301.968 | 7388.7808 | 21617.1465 | 0 | 0.020766 | 0.021946 | 3.4724 | 6.9907e-07 | 0.00023996 | 46.2996
2005-06-14 00:01 | 40.7889 | 88.8613 | 3.4635 | 480 | 0 | 50 | 2 | 1 | 10 | 20.3944 | 0.91512 | 81.432 | 80.633 | 1.0099 | 195.4368 | 3975.9177 | 21782.8105 | 0 | 0.020197 | 0.02138 | 3.4715 | 3.331e-07 | 0.00013753 | 46.6327
2005-06-15 00:34 | 60.8822 | 87.8211 | 3.8544 | 480 | 0 | 50 | 3 | 1 | 11 | 20.2941 | 0.90964 | 129.924 | 128.5413 | 1.0108 | 311.8176 | 7659.0205 | 22101.9355 | 0 | 0.020189 | 0.021353 | 3.4774 | 4.4153e-07 | 0.00015099 | 47.0742
2005-06-16 01:03 | 70.6437 | 90.2576 | 0.69599 | 480 | 0 | 50 | 3 | 1 | 10 | 23.5479 | 0.90418 | 119.124 | 117.4221 | 1.0145 | 285.8976 | 6995.5566 | 22393.418 | 0 | 0.020187 | 0.021322 | 3.4778 | 7.9349e-08 | 2.724e-05 | 47.1536
2005-06-17 01:44 | 76.1967 | 91.4593 | 2.0857 | 480 | 0 | 50 | 3 | 1 | 9 | 25.3989 | 0.89867 | 113.724 | 113.1999 | 1.0046 | 272.9377 | 6729.6191 | 22673.8184 | 0 | 0.020179 | 0.021239 | 3.4727 | 2.4243e-07 | 8.259e-05 | 47.396
2005-06-18 02:19 | 62.9334 | 88.0777 | 3.6421 | 480 | 0 | 50 | 3 | 1 | 11 | 20.9778 | 0.89317 | 133.488 | 132.0937 | 1.0106 | 320.3712 | 7899.1528 | 23002.9492 | 0 | 0.020171 | 0.021264 | 3.4769 | 4.1926e-07 | 0.00014283 | 47.8153
2005-06-19 02:49 | 83.4992 | 90.1511 | 1.7253 | 480 | 0 | 50 | 4 | 1 | 9 | 20.8748 | 0.88771 | 144.18 | 141.4113 | 1.0196 | 346.032 | 8466.9697 | 23355.7402 | 0 | 0.020166 | 0.021298 | 3.4763 | 1.9738e-07 | 6.7756e-05 | 48.0126
2005-06-20 03:19 | 93.6398 | 91.6014 | 1.7198 | 480 | 0 | 50 | 4 | 1 | 9 | 23.41 | 0.88225 | 135 | 133.8841 | 1.0083 | 324 | 7927.874 | 23686.0684 | 0 | 0.020161 | 0.021037 | 3.4739 | 1.9784e-07 | 6.7916e-05 | 48.2105
2005-06-21 00:11 | 44.4814 | 89.1573 | 3.1942 | 480 | 0 | 50 | 2 | 1 | 11 | 22.2407 | 0.87758 | 88.02 | 86.4132 | 1.0186 | 211.248 | 4416.4043 | 23870.0859 | 0 | 0.020831 | 0.021783 | 3.4713 | 3.1582e-07 | 0.00012689 | 48.5263
2005-06-22 00:51 | 97.3139 | 89.7989 | 4.9064 | 480 | 0 | 50 | 4 | 1 | 11 | 24.3285 | 0.87208 | 167.6161 | 166.1302 | 1.0089 | 402.2787 | 9918.6836 | 24283.3652 | 0 | 0.020817 | 0.021417 | 3.4739 | 5.6876e-07 | 0.00019375 | 49.0951
2005-06-26 00:20 | 79.7484 | 89.3511 | 3.6565 | 480 | 0 | 50 | 4 | 1 | 10 | 19.9371 | 0.85075 | 154.656 | 152.7025 | 1.0128 | 371.1743 | 35458.75 | 25760.8125 | 0 | 0 | 0 | 3.4753 | 1.6368e-06 | 0.00014391 | 50.7319
2005-06-27 00:50 | 64.0562 | 89.6599 | 5.8774 | 480 | 0 | 50 | 3 | 1 | 9 | 21.3521 | 0.99529 | 109.512 | 108.0532 | 1.0135 | 262.8288 | 6431.0928 | 26028.7754 | 0 | 0 | 0 | 3.4719 | 6.7929e-07 | 0.00023317 | 51.4112
2005-06-28 00:20 | 76.2857 | 89.5751 | 2.7873 | 480 | 0 | 50 | 3 | 1 | 11 | 25.4286 | 0.99004 | 125.928 | 123.4108 | 1.0204 | 302.2271 | 7111.7822 | 26325.0996 | 0 | 0 | 0 | 3.4759 | 3.0693e-07 | 0.00010956 | 51.7181
2005-06-29 03:51 | 47.4279 | 90.0852 | 2.1488 | 480 | 0 | 50 | 2 | 1 | 10 | 23.7139 | 0.98391 | 77.328 | 76.7463 | 1.0076 | 185.5872 | 5097.8486 | 26537.5098 | 0 | 0 | 0 | 3.475 | 2.7682e-07 | 8.465e-05 | 51.9949
2005-06-30 00:26 | 77.352 | 89.8899 | 1.8916 | 480 | 0 | 50 | 3 | 1 | 11 | 25.784 | 0.9793 | 123.984 | 122.1781 | 1.0148 | 297.5616 | 6137.2075 | 26793.2266 | 0 | 0 | 0 | 3.4766 | 1.8228e-07 | 7.4233e-05 | 52.1772
2005-07-01 00:53 | 87.4548 | 89.5091 | 3.7393 | 480 | 0 | 50 | 4 | 1 | 10 | 21.8637 | 0.97386 | 146.124 | 144.3823 | 1.0121 | 350.6976 | 8548.2549 | 27149.4043 | 0 | 0 | 0 | 3.4764 | 4.2604e-07 | 0.00014681 | 52.6032
2005-07-02 03:22 | 49.333 | 90.3631 | 3.895 | 480 | 0 | 50 | 2 | 1 | 10 | 24.6665 | 0.96794 | 79.488 | 78.708 | 1.0099 | 190.7712 | 5061.3979 | 27360.2949 | 0 | 0 | 0 | 3.4774 | 4.8197e-07 | 0.00015258 | 53.0852
2005-07-03 03:51 | 84.9304 | 91.1316 | 2.2672 | 480 | 0 | 50 | 3 | 1 | 10 | 28.3101 | 0.96248 | 123.336 | 121.482 | 1.0153 | 296.0065 | 7242.9082 | 27662.082 | 0 | 0 | 0 | 3.4788 | 2.5789e-07 | 8.8527e-05 | 53.3431
2005-07-04 00:46 | 70.8949 | 91.3343 | 1.8257 | 480 | 0 | 50 | 3 | 1 | 9 | 23.6316 | 0.95781 | 103.032 | 102.197 | 1.0082 | 247.2767 | 5169.6294 | 27877.4824 | 0 | 0 | 0 | 3.4769 | 1.7821e-07 | 7.16e-05 | 53.5213
2005-07-05 02:39 | 93.9222 | 90.0453 | 1.9655 | 480 | 0 | 50 | 4 | 1 | 10 | 23.4805 | 0.95204 | 150.876 | 149.5659 | 1.0088 | 362.1024 | 9369.4004 | 28267.875 | 0 | 0 | 0 | 3.4761 | 2.3791e-07 | 7.7231e-05 | 53.7592
2005-07-06 01:24 | 89.4931 | 91.4252 | 1.8124 | 480 | 0 | 50 | 3 | 1 | 10 | 29.831 | 0.94695 | 126.684 | 125.8105 | 1.0069 | 304.0417 | 6926.4497 | 28556.4766 | 0 | 0 | 0 | 3.4715 | 1.952e-07 | 7.1972e-05 | 53.9544
2005-07-07 01:05 | 73.4612 | 91.6353 | 0.86757 | 480 | 0 | 50 | 3 | 1 | 9 | 24.4871 | 0.94166 | 105.732 | 104.0359 | 1.0163 | 253.7568 | 6018.793 | 28807.2598 | 0 | 0 | 0 | 3.4767 | 9.6115e-08 | 3.4039e-05 | 54.0505
2005-07-08 01:50 | 59.4831 | 89.8119 | 2.0219 | 480 | 0 | 50 | 3 | 1 | 9 | 19.8277 | 0.93613 | 107.676 | 105.9387 | 1.0164 | 258.4224 | 6395.9541 | 29073.7578 | 0 | 0 | 0 | 3.4788 | 2.3264e-07 | 7.8954e-05 | 54.2832
2005-07-09 02:20 | 63.6367 | 89.1711 | 1.3161 | 480 | 0 | 50 | 3 | 1 | 10 | 21.2122 | 0.93067 | 120.312 | 119.6064 | 1.0059 | 288.7488 | 7065.3232 | 29368.1465 | 0 | 0 | 0 | 3.4717 | 1.5218e-07 | 5.2241e-05 | 54.4353
2005-07-10 02:45 | 81.8249 | 88.0782 | 1.7707 | 480 | 0 | 50 | 4 | 1 | 11 | 20.4562 | 0.92523 | 166.3201 | 163.7856 | 1.0155 | 399.1682 | 9729.7256 | 29773.5508 | 0 | 0 | 0 | 3.4761 | 2.0191e-07 | 6.9578e-05 | 54.6372
2005-07-11 03:18 | 71.0468 | 88.9929 | 4.5382 | 480 | 0 | 50 | 3 | 1 | 11 | 23.6823 | 0.91975 | 136.296 | 133.9966 | 1.0172 | 327.1104 | 8034.6494 | 30108.3281 | 0 | 0 | 0 | 3.4725 | 5.2574e-07 | 0.00017978 | 55.163
2005-07-12 03:59 | 86.6647 | 85.4405 | 3.878 | 480 | 0 | 50 | 6 | 1 | 10 | 14.4441 | 0.91424 | 228.2041 | 225.8236 | 1.0105 | 547.6899 | 13503.9785 | 30670.9941 | 0 | 0 | 0 | 3.4766 | 4.4676e-07 | 0.00015219 | 55.6098
2005-07-13 00:29 | 101.6834 | 88.1788 | 2.6801 | 480 | 0 | 50 | 5 | 1 | 11 | 20.3367 | 0.90966 | 203.04 | 199.1552 | 1.0195 | 487.2961 | 10004.7969 | 31087.8613 | 0 | 0 | 0 | 3.4801 | 2.5506e-07 | 0.00010435 | 55.8648
2005-07-14 01:07 | 93.4718 | 87.9314 | 4.8789 | 145 | 6.832 | 50 | 5 | 1 | 10 | 18.6944 | 0.90416 | 197.8559 | 195.0847 | 1.0142 | 474.8543 | 11708.126 | 31575.6992 | 0.0060837 | 0.020801 | 0.026747 | 2.1929 | 1.0802e-05 | 0.0036734 | 66.667
2005-07-15 01:44 | 59.8943 | 90.5557 | 4.3592 | 480 | 0 | 50 | 3 | 1 | 9 | 19.9648 | 0.89867 | 103.032 | 102.3873 | 1.0063 | 247.2767 | 6073.7354 | 31828.7715 | 0 | 0.020801 | 0.026441 | 3.4751 | 5.02e-07 | 0.00017166 | 67.169
2005-07-16 02:15 | 44.7488 | 88.3604 | 3.4277 | 480 | 0 | 50 | 3 | 1 | 9 | 14.9163 | 0.89319 | 100.116 | 99.3667 | 1.0075 | 240.2785 | 5901.8398 | 32074.6816 | 0 | 0.020798 | 0.026596 | 3.4764 | 3.9358e-07 | 0.00013459 | 67.5626
2005-07-17 02:36 | 77.6205 | 86.1499 | 5.83 | 480 | 0 | 50 | 5 | 1 | 11 | 15.5241 | 0.88775 | 198.0721 | 194.5955 | 1.0179 | 475.373 | 11587.2178 | 32557.4824 | 0 | 0.020806 | 0.026751 | 3.4791 | 6.6017e-07 | 0.00022748 | 68.2227
2005-07-18 02:57 | 87.973 | 86.2974 | 6.0666 | 480 | 0 | 50 | 6 | 1 | 10 | 14.6622 | 0.88233 | 223.5601 | 219.8822 | 1.0167 | 536.5443 | 13027.9648 | 33100.3125 | 0 | 0.020817 | 0.022173 | 3.4771 | 6.874e-07 | 0.00023778 | 68.9101
2005-07-19 03:41 | 126.6087 | 87.6731 | 4.7264 | 480 | 0 | 50 | 7 | 1 | 11 | 18.087 | 0.87681 | 268.2722 | 263.9531 | 1.0164 | 643.8532 | 15935.3672 | 33764.2852 | 0 | 0.020809 | 0.018712 | 3.4792 | 5.4324e-07 | 0.00018435 | 69.4534
2005-07-20 00:13 | 22.0235 | 89.6873 | 2.5021 | 480 | 0 | 50 | 1 | 1 | 10 | 22.0235 | 0.87222 | 42.984 | 42.863 | 1.0028 | 103.1616 | 2118.0366 | 33852.5352 | 0 | 0.020233 | 0.0255 | 3.4715 | 2.4284e-07 | 9.9348e-05 | 69.6962
2005-07-21 00:48 | 99.5609 | 88.5708 | 2.9337 | 480 | 0 | 50 | 5 | 1 | 11 | 19.9122 | 0.86672 | 201.096 | 198.4742 | 1.0132 | 482.6304 | 11899.8564 | 34348.3633 | 0 | 0.020814 | 0.026474 | 3.4761 | 3.3839e-07 | 0.00011528 | 70.0346
2005-07-22 01:30 | 77.2406 | 88.2894 | 2.3755 | 480 | 0 | 50 | 4 | 1 | 11 | 19.3101 | 0.86122 | 167.5079 | 164.7877 | 1.0165 | 402.0191 | 9912.2832 | 34761.375 | 0 | 0.020814 | 0.026269 | 3.4778 | 2.7292e-07 | 9.2975e-05 | 70.3075
2005-07-23 02:09 | 31.6933 | 87.2664 | 3.8729 | 480 | 0 | 50 | 2 | 1 | 10 | 15.8467 | 0.85571 | 83.592 | 82.5385 | 1.0128 | 200.6208 | 4946.5576 | 34967.4805 | 0 | 0.020126 | 0.025651 | 3.4713 | 4.516e-07 | 0.00015384 | 70.7591
2005-07-24 02:30 | 81.6459 | 88.1834 | 2.3338 | 359.1 | 0.011667 | 50 | 5 | 1 | 10 | 16.3292 | 0.85027 | 182.4121 | 178.7762 | 1.0203 | 437.789 | 10671.1064 | 35412.1094 | 0 | 0.019488 | 0.025044 | 3.4802 | 2.636e-07 | 9.0837e-05 | 71.0227
2005-07-25 02:56 | 60.4118 | 89.0144 | 3.806 | 480 | 0 | 50 | 3 | 1 | 9 | 20.1373 | 0.99483 | 114.372 | 112.6899 | 1.0149 | 274.4929 | 6690.7637 | 35690.8906 | 0 | 0.01889 | 0.024324 | 3.4723 | 4.378e-07 | 0.00015086 | 71.4605
2005-07-26 03:22 | 83.0381 | 89.7934 | 4.0833 | 480 | 0 | 50 | 3 | 1 | 11 | 27.6794 | 0.98937 | 136.728 | 134.503 | 1.0165 | 328.1472 | 8029.353 | 36025.4453 | 0 | 0.020747 | 0.027373 | 3.4751 | 4.6848e-07 | 0.00016082 | 71.929
2005-07-27 02:50 | 62.4855 | 89.3606 | 2.8371 | 480 | 0 | 50 | 3 | 1 | 9 | 20.8285 | 0.98414 | 114.696 | 113.4344 | 1.0111 | 275.2705 | 6451.6519 | 36294.2656 | 0 | 0.020777 | 0.0274 | 3.4803 | 3.0808e-07 | 0.00011041 | 72.2371
2005-07-28 03:15 | 77.8566 | 88.5023 | 3.112 | 480 | 0 | 50 | 4 | 1 | 10 | 19.4642 | 0.97868 | 150.228 | 147.7054 | 1.0171 | 360.5473 | 8822.1406 | 36661.8555 | 0 | 0.02075 | 0.027367 | 3.476 | 3.5625e-07 | 0.00012229 | 72.5933
2005-07-29 03:48 | 86.2954 | 86.7454 | 3.0246 | 480 | 0 | 50 | 5 | 1 | 10 | 17.2591 | 0.97319 | 196.7759 | 193.6883 | 1.0159 | 472.2622 | 11599.9414 | 37145.1875 | 0 | 0.020068 | 0.026373 | 3.4795 | 3.448e-07 | 0.00011791 | 72.9381
2005-07-30 00:23 | 69.9777 | 88.6027 | 2.6638 | 480 | 0 | 50 | 3 | 1 | 11 | 23.3259 | 0.96861 | 134.568 | 133.1606 | 1.0106 | 322.9632 | 6630.8389 | 37421.4727 | 0 | 0.020256 | 0.026418 | 3.4753 | 2.5631e-07 | 0.00010486 | 73.1944
2005-07-31 00:51 | 68.2679 | 89.5124 | 5.2238 | 480 | 0 | 50 | 3 | 1 | 10 | 22.756 | 0.96315 | 123.336 | 121.5235 | 1.0149 | 296.0065 | 7242.9082 | 37723.2617 | 0 | 0.020151 | 0.026226 | 3.4727 | 6.0254e-07 | 0.00020683 | 73.797
2005-08-01 01:18 | 76.6405 | 89.1493 | 3.341 | 480 | 0 | 50 | 4 | 1 | 9 | 19.1601 | 0.95769 | 143.856 | 142.3083 | 1.0109 | 345.2545 | 8447.9453 | 38075.2578 | 0 | 0.020149 | 0.026338 | 3.4801 | 3.7886e-07 | 0.00013005 | 74.1758
2005-08-02 01:53 | 89.7538 | 89.3955 | 3.3799 | 480 | 0 | 50 | 4 | 1 | 10 | 22.4385 | 0.9522 | 160.38 | 158.9313 | 1.0091 | 384.912 | 9454.4014 | 38469.1914 | 0 | 0.020202 | 0.02623 | 3.4734 | 3.9077e-07 | 0.00013363 | 74.5666
2005-08-03 02:21 | 73.9845 | 87.9207 | 2.7971 | 480 | 0 | 50 | 4 | 1 | 10 | 18.4961 | 0.94674 | 158.652 | 155.7389 | 1.0187 | 380.7648 | 9316.8389 | 38857.3945 | 0 | 0.020787 | 0.02684 | 3.4761 | 3.2014e-07 | 0.0001099 | 74.8867
2005-08-04 02:52 | 78.3493 | 86.912 | 0.34729 | 480 | 0 | 50 | 5 | 1 | 10 | 15.6699 | 0.94126 | 183.708 | 179.7255 | 1.0222 | 440.8992 | 10829.5869 | 39308.6289 | 0 | 0.020825 | 0.026969 | 3.4804 | 3.951e-08 | 1.3512e-05 | 74.9263
2005-08-05 03:17 | 65.2671 | 86.3294 | 3.8078 | 480 | 0 | 50 | 4 | 1 | 11 | 16.3168 | 0.93582 | 161.8921 | 160.2869 | 1.01 | 388.541 | 9470.6855 | 39703.2422 | 0 | 0.020779 | 0.027138 | 3.4726 | 4.377e-07 | 0.00015083 | 75.364
2005-08-06 03:42 | 67.9079 | 85.2478 | 3.184 | 480 | 0 | 50 | 5 | 1 | 10 | 13.5816 | 0.93038 | 189.5401 | 187.5446 | 1.0106 | 454.8961 | 11088.0938 | 40165.2461 | 0 | 0.02076 | 0.027295 | 3.4782 | 3.6131e-07 | 0.0001245 | 75.7253
2005-08-07 04:04 | 108.2129 | 88.5765 | 3.4403 | 480 | 0 | 50 | 5 | 1 | 11 | 21.6426 | 0.92494 | 207.252 | 205.833 | 1.0069 | 497.4049 | 12124.2441 | 40670.4219 | 0 | 0.020771 | 0.027042 | 3.4734 | 3.9474e-07 | 0.00013603 | 76.12
2005-08-08 00:22 | 60.8337 | 88.7367 | 3.4891 | 480 | 0 | 50 | 3 | 1 | 10 | 20.2779 | 0.9204 | 126.576 | 124.6597 | 1.0154 | 303.7825 | 6180.0752 | 40927.9258 | 0 | 0.020202 | 0.026209 | 3.473 | 3.3439e-07 | 0.00013806 | 76.4544
2005-08-09 00:59 | 79.5245 | 91.0497 | 3.2012 | 480 | 0 | 50 | 3 | 1 | 10 | 26.5082 | 0.91491 | 126.792 | 124.9087 | 1.0151 | 304.3009 | 7474.3911 | 41239.3594 | 0 | 0.020199 | 0.026108 | 3.4791 | 3.6524e-07 | 0.0001249 | 76.8196
2005-08-10 00:23 | 85.3975 | 86.7704 | 2.4107 | 480 | 0 | 50 | 5 | 1 | 11 | 17.0795 | 0.90968 | 205.9561 | 201.4422 | 1.0224 | 494.2945 | 11585.0283 | 41722.0703 | 0 | 0.020225 | 0.026034 | 3.4781 | 2.6306e-07 | 9.4275e-05 | 77.0827
2005-08-11 00:01 | 80.0963 | 85.4869 | 2.2016 | 480 | 0 | 50 | 5 | 1 | 11 | 16.0193 | 0.90441 | 218.916 | 217.2802 | 1.0075 | 525.3983 | 12412.5352 | 42239.2578 | 0 | 0.020251 | 0.025998 | 3.475 | 2.439e-07 | 8.6715e-05 | 77.3266
2005-08-12 00:40 | 94.0847 | 88.6183 | 1.8802 | 480 | 0 | 50 | 5 | 1 | 10 | 18.8169 | 0.8989 | 192.4559 | 189.6646 | 1.0147 | 461.8943 | 11388.5801 | 42713.7812 | 0 | 0.020828 | 0.026822 | 3.4772 | 2.1632e-07 | 7.3695e-05 | 77.5429
2005-08-12 04:44 | 82.3435 | 88.5512 | 2.744 | 480 | 0 | 50 | 4 | 1 | 11 | 20.5859 | 0.89801 | 169.776 | 167.1612 | 1.0156 | 407.4624 | 1642.5826 | 42782.2227 | 0 | 0.020712 | 0.026648 | 3.4745 | 5.1935e-08 | 0.00010821 | 77.5948
2005-08-13 01:09 | 73.4394 | 86.9779 | 2.855 | 480 | 0 | 50 | 4 | 1 | 11 | 18.3599 | 0.89344 | 179.712 | 178.043 | 1.0094 | 431.3089 | 8814.875 | 43149.5078 | 0 | 0.020144 | 0.025898 | 3.4744 | 2.7401e-07 | 0.00011261 | 77.8689
2005-08-14 01:31 | 63.0181 | 87.7614 | 1.374 | 480 | 0 | 50 | 4 | 1 | 10 | 15.7545 | 0.888 | 147.42 | 145.6506 | 1.0121 | 353.808 | 8624.0713 | 43508.8438 | 0 | 0 | 0 | 3.4759 | 1.5672e-07 | 5.4005e-05 | 78.0256
2005-08-15 01:51 | 93.5074 | 89.7915 | 1.0525 | 480 | 0 | 50 | 4 | 1 | 11 | 23.3768 | 0.88256 | 170.1 | 168.121 | 1.0118 | 408.24 | 9950.8496 | 43923.4609 | 0 | 0 | 0 | 3.4735 | 1.2072e-07 | 4.16e-05 | 78.1463
2005-08-16 02:16 | 117.667 | 87.6285 | 1.6528 | 480 | 0 | 50 | 7 | 1 | 10 | 16.8096 | 0.87712 | 261.7921 | 259.2723 | 1.0097 | 628.301 | 15314.8359 | 44561.5781 | 0 | 0 | 0 | 3.4768 | 1.8817e-07 | 6.4844e-05 | 78.3344
2005-08-17 01:36 | 93.8157 | 86.5877 | 3.4738 | 480 | 0 | 50 | 6 | 1 | 11 | 15.6359 | 0.87191 | 235.116 | 231.4839 | 1.0157 | 564.2785 | 13172.376 | 45110.4258 | 0 | 0 | 0 | 3.4784 | 3.7728e-07 | 0.00013575 | 78.7117
2005-08-18 02:08 | 71.8627 | 88.2314 | 3.2565 | 480 | 0 | 50 | 4 | 1 | 10 | 17.9657 | 0.86643 | 164.592 | 162.3836 | 1.0136 | 395.0209 | 9702.7002 | 45514.7031 | 0 | 0 | 0 | 3.4785 | 3.7212e-07 | 0.00012725 | 79.0838
2005-08-19 02:44 | 64.9771 | 86.5757 | 1.0995 | 480 | 0 | 50 | 4 | 1 | 11 | 16.2443 | 0.86094 | 174.528 | 171.6867 | 1.0165 | 418.8672 | 10288.4248 | 45943.3867 | 0 | 0 | 0 | 3.4763 | 1.2628e-07 | 4.3186e-05 | 79.2101
2005-08-20 03:11 | 71.4766 | 86.6322 | 1.9781 | 480 | 0 | 50 | 5 | 1 | 10 | 14.2953 | 0.85548 | 192.5639 | 189.412 | 1.0166 | 462.1534 | 11308.3174 | 46414.5664 | 0 | 0 | 0 | 3.4789 | 2.2498e-07 | 7.7231e-05 | 79.4351
2005-08-21 03:32 | 70.1344 | 88.7069 | 0.67414 | 480 | 0 | 50 | 4 | 1 | 10 | 17.5336 | 0.85004 | 155.844 | 153.6688 | 1.0142 | 374.0255 | 9116.873 | 46794.4375 | 0 | 0 | 0 | 3.4772 | 7.6676e-08 | 2.6423e-05 | 79.5118
2005-08-22 03:55 | 66.3861 | 90.5686 | 2.353 | 480 | 0 | 50 | 3 | 1 | 9 | 22.1287 | 0.9946 | 106.812 | 105.4997 | 1.0124 | 256.3488 | 6248.5015 | 47054.793 | 0 | 0 | 0 | 3.4756 | 2.6861e-07 | 9.2564e-05 | 79.7804
2005-08-23 00:12 | 96.2502 | 88.8673 | 2.327 | 480 | 0 | 50 | 4 | 1 | 11 | 24.0626 | 0.99008 | 174.852 | 172.9616 | 1.0109 | 419.6447 | 8497.8057 | 47408.8672 | 0 | 0 | 0 | 3.4752 | 2.2087e-07 | 9.1618e-05 | 80.0013
2005-08-24 00:43 | 63.1293 | 86.257 | 4.2142 | 480 | 0 | 50 | 4 | 1 | 10 | 15.7823 | 0.9846 | 158.112 | 155.9209 | 1.0141 | 379.4688 | 9320.7031 | 47797.2305 | 0 | 0 | 0 | 3.4786 | 4.8136e-07 | 0.00016461 | 80.4826
2005-08-25 01:17 | 68.6812 | 89.433 | 2.2321 | 480 | 0 | 50 | 3 | 1 | 10 | 22.8937 | 0.97912 | 125.496 | 123.7814 | 1.0139 | 301.1905 | 7397.9912 | 48105.4805 | 0 | 0 | 0 | 3.4715 | 2.5918e-07 | 8.8632e-05 | 80.7418
2005-08-26 01:38 | 57.3765 | 87.6966 | 1.0466 | 480 | 0 | 50 | 3 | 1 | 10 | 19.1255 | 0.9737 | 127.872 | 126.4149 | 1.0115 | 306.8928 | 7451.7407 | 48415.9688 | 0 | 0 | 0 | 3.4744 | 1.1934e-07 | 4.1285e-05 | 80.8612
2005-08-27 02:15 | 54.554 | 89.9915 | 2.092 | 480 | 0 | 50 | 2 | 1 | 11 | 27.277 | 0.96819 | 93.312 | 91.7536 | 1.017 | 223.9488 | 5521.7373 | 48646.043 | 0 | 0 | 0 | 3.4749 | 2.4197e-07 | 8.2432e-05 | 81.1031
2005-08-28 02:38 | 60.8458 | 87.2109 | 2.4867 | 480 | 0 | 50 | 4 | 1 | 9 | 15.2114 | 0.96275 | 144.72 | 142.9786 | 1.0122 | 347.328 | 8466.1201 | 48998.7969 | 0 | 0 | 0 | 3.4784 | 2.8202e-07 | 9.7185e-05 | 81.3851
2005-08-29 03:05 | 79.4374 | 88.7166 | 2.1513 | 480 | 0 | 50 | 4 | 1 | 10 | 19.8594 | 0.95729 | 157.248 | 155.2832 | 1.0127 | 377.3952 | 9234.3877 | 49383.5625 | 0 | 0 | 0 | 3.4769 | 2.4578e-07 | 8.4371e-05 | 81.6309
2005-08-30 01:31 | 63.7988 | 88.2439 | 2.2705 | 480 | 0 | 50 | 3 | 1 | 11 | 21.2663 | 0.95229 | 134.136 | 131.6255 | 1.0191 | 321.9265 | 7213.1646 | 49684.1094 | 0 | 0 | 0 | 3.4745 | 2.3884e-07 | 8.9537e-05 | 81.8698
2005-08-31 02:54 | 69.6115 | 88.3192 | 1.4787 | 480 | 0 | 50 | 4 | 1 | 9 | 17.4029 | 0.94662 | 148.716 | 147.8056 | 1.0062 | 356.9185 | 9067.96 | 50061.9414 | 0 | 0 | 0 | 3.4755 | 1.7597e-07 | 5.8178e-05 | 82.0457
2005-09-01 02:23 | 68.8337 | 89.833 | 2.2553 | 480 | 0 | 50 | 3 | 1 | 10 | 22.9446 | 0.94139 | 124.848 | 123.7012 | 1.0093 | 299.6353 | 7022.7021 | 50354.5547 | 0 | 0 | 0 | 3.4717 | 2.4978e-07 | 8.9516e-05 | 82.2955
2005-09-02 02:42 | 68.7788 | 86.6965 | 2.3104 | 480 | 0 | 50 | 4 | 1 | 11 | 17.1947 | 0.93594 | 169.56 | 166.805 | 1.0165 | 406.944 | 9919.2588 | 50767.8555 | 0 | 0 | 0 | 3.4745 | 2.6441e-07 | 9.1117e-05 | 82.5599
2005-09-03 03:10 | 101.9073 | 88.5394 | 2.5955 | 480 | 0 | 50 | 5 | 1 | 11 | 20.3815 | 0.93048 | 201.744 | 198.2196 | 1.0178 | 484.1856 | 11847.417 | 51261.4961 | 0 | 0 | 0 | 3.4784 | 2.9548e-07 | 0.00010143 | 82.8554
2005-09-04 03:31 | 45.8364 | 88.1991 | 2.712 | 480 | 0 | 50 | 3 | 1 | 9 | 15.2788 | 0.92504 | 105.732 | 103.8806 | 1.0178 | 253.7568 | 6185.3208 | 51519.2188 | 0 | 0 | 0 | 3.4774 | 3.0827e-07 | 0.00010623 | 83.1637
2005-09-05 03:56 | 42.3499 | 87.3888 | 0.48785 | 480 | 0 | 50 | 3 | 1 | 9 | 14.1166 | 0.9196 | 106.812 | 105.5297 | 1.0122 | 256.3488 | 6248.5015 | 51779.5742 | 0 | 0 | 0 | 3.4751 | 5.5753e-08 | 1.9213e-05 | 83.2194
2005-09-06 00:12 | 22.3804 | 87.8992 | 1.3148 | 480 | 0 | 50 | 2 | 1 | 7 | 11.1902 | 0.91508 | 57.456 | 56.8441 | 1.0108 | 137.8944 | 2792.3618 | 51895.9219 | 0 | 0 | 0 | 3.4815 | 1.23e-07 | 5.1021e-05 | 83.3424
2005-09-07 00:43 | 69.7882 | 88.4699 | 1.4194 | 480 | 0 | 50 | 4 | 1 | 10 | 17.4471 | 0.9096 | 149.7959 | 148.4536 | 1.009 | 359.5103 | 8830.4717 | 52263.8594 | 0 | 0 | 0 | 3.4776 | 1.6251e-07 | 5.5575e-05 | 83.5049
2005-09-08 01:04 | 57.5268 | 87.9075 | 1.6932 | 480 | 0 | 50 | 3 | 1 | 11 | 19.1756 | 0.90418 | 132.3 | 130.43 | 1.0143 | 317.5201 | 7709.7837 | 52585.1016 | 0 | 0 | 0 | 3.4761 | 1.9232e-07 | 6.6529e-05 | 83.6972
2005-09-09 02:31 | 76.0939 | 90.0861 | 0.73299 | 480 | 0 | 50 | 3 | 1 | 11 | 25.3646 | 0.89849 | 137.916 | 135.5724 | 1.0173 | 330.9985 | 8440.4609 | 52936.7891 | 0 | 0 | 0 | 3.4772 | 8.7212e-08 | 2.8728e-05 | 83.7845
2005-09-10 02:55 | 79.5094 | 88.4062 | 0.93176 | 480 | 0 | 50 | 4 | 1 | 11 | 19.8774 | 0.89305 | 171.396 | 168.8577 | 1.015 | 411.3504 | 10026.665 | 53354.5664 | 0 | 0 | 0 | 3.4741 | 1.0672e-07 | 3.6776e-05 | 83.8912
2005-09-11 03:19 | 63.7526 | 89.071 | 1.0807 | 480 | 0 | 50 | 3 | 1 | 11 | 21.2509 | 0.8876 | 131.328 | 129.5951 | 1.0134 | 315.1873 | 7682.6895 | 53674.6797 | 0 | 0 | 0 | 3.4744 | 1.2371e-07 | 4.2632e-05 | 84.0149
2005-09-12 03:36 | 36.4135 | 88.9373 | 0.8577 | 480 | 0 | 50 | 2 | 1 | 10 | 18.2067 | 0.88218 | 79.704 | 79.0347 | 1.0085 | 191.2896 | 4644.7505 | 53868.2109 | 0 | 0 | 0 | 3.4763 | 9.7379e-08 | 3.3687e-05 | 84.1123
2005-09-13 01:58 | 52.0032 | 87.3128 | 0.77159 | 480 | 0 | 50 | 3 | 1 | 11 | 17.3344 | 0.87718 | 131.436 | 130.061 | 1.0106 | 315.4464 | 7067.9712 | 54162.7109 | 0 | 0 | 0 | 3.4746 | 8.1152e-08 | 3.0423e-05 | 84.1934
2005-09-14 01:22 | 51.7149 | 87.9657 | 0.88437 | 480 | 0 | 50 | 3 | 1 | 10 | 17.2383 | 0.87195 | 126.684 | 124.9897 | 1.0136 | 304.0417 | 7125.9771 | 54459.625 | 0 | 0 | 0 | 3.4748 | 9.7253e-08 | 3.4855e-05 | 84.2907
2005-09-15 01:44 | 84.9522 | 87.0796 | 1.0789 | 398.2 | 0.011667 | 50 | 5 | 1 | 11 | 16.9904 | 0.86653 | 212.5439 | 209.3762 | 1.0151 | 510.1054 | 12385.998 | 54975.707 | 0 | 0 | 0 | 3.48 | 1.2146e-07 | 4.2018e-05 | 84.4121
2005-09-16 02:04 | 68.9489 | 89.0811 | 1.0835 | 480 | 0 | 50 | 4 | 1 | 9 | 17.2372 | 0.86109 | 150.66 | 149.1548 | 1.0101 | 361.584 | 8813.6094 | 55342.9414 | 0 | 0 | 0 | 3.48 | 1.2242e-07 | 4.2187e-05 | 84.5346
2005-09-17 02:23 | 81.4957 | 89.7243 | 0.18821 | 480 | 0 | 50 | 4 | 1 | 10 | 20.3739 | 0.85567 | 162.648 | 160.6777 | 1.0123 | 390.3553 | 9478.3135 | 55737.8711 | 0 | 0 | 0 | 3.4772 | 2.1321e-08 | 7.3758e-06 | 84.5559
2005-09-18 02:45 | 61.4261 | 88.0834 | 0.88318 | 480 | 0 | 50 | 4 | 1 | 10 | 15.3565 | 0.85023 | 149.472 | 146.9597 | 1.0171 | 358.7327 | 8744.1094 | 56102.2109 | 0 | 0 | 0 | 3.4814 | 9.9482e-08 | 3.4283e-05 | 84.6554
2005-09-19 03:10 | 61.7142 | 87.9666 | 0.19595 | 480 | 0 | 50 | 3 | 1 | 11 | 20.5714 | 0.99477 | 129.06 | 127.2674 | 1.0141 | 309.744 | 7579.0483 | 56418.0039 | 0 | 0 | 0 | 3.4775 | 2.2354e-08 | 7.674e-06 | 84.6777
2005-09-20 03:30 | 63.0598 | 89.2948 | 2.0259 | 480 | 0 | 50 | 3 | 1 | 10 | 21.0199 | 0.98935 | 118.152 | 116.13 | 1.0174 | 283.5648 | 6885.3076 | 56704.8906 | 0 | 0 | 0 | 3.4801 | 2.28e-07 | 7.8874e-05 | 84.9057
2005-09-21 03:46 | 76.1456 | 87.1145 | 0.44394 | 480 | 0 | 50 | 4 | 1 | 11 | 19.0364 | 0.98393 | 172.8 | 170.1434 | 1.0156 | 414.72 | 10069.9189 | 57124.4688 | 0 | 0 | 0 | 3.4812 | 4.983e-08 | 1.7238e-05 | 84.9555
2005-09-22 03:18 | 70.8103 | 89.6764 | 0.9039 | 480 | 0 | 50 | 3 | 1 | 10 | 23.6034 | 0.97868 | 127.98 | 126.2726 | 1.0135 | 307.1519 | 7227.6694 | 57425.6211 | 0 | 0 | 0 | 3.4766 | 9.9369e-08 | 3.5471e-05 | 85.0549
2005-09-23 03:45 | 76.0808 | 87.915 | 2.8535 | 480 | 0 | 50 | 4 | 1 | 10 | 19.0202 | 0.97321 | 164.484 | 162.4933 | 1.0123 | 394.7617 | 9659.3242 | 57828.0938 | 0 | 0 | 0 | 3.4753 | 3.2721e-07 | 0.00011232 | 85.3821
2005-09-24 00:02 | 64.1137 | 88.6915 | 2.7744 | 480 | 0 | 50 | 3 | 1 | 11 | 21.3712 | 0.96869 | 127.548 | 125.6481 | 1.0151 | 306.1152 | 6198.832 | 58086.3789 | 0 | 0 | 0 | 3.4743 | 2.6391e-07 | 0.00010947 | 85.646
2005-09-25 00:30 | 68.6631 | 85.9086 | 2.4974 | 480 | 0 | 50 | 4 | 1 | 11 | 17.1658 | 0.96323 | 179.604 | 178.1718 | 1.008 | 431.0497 | 10547.2461 | 58525.8477 | 0 | 0 | 0 | 3.4717 | 2.8875e-07 | 9.9121e-05 | 85.9348
2005-09-26 00:57 | 67.4102 | 87.2667 | 1.4563 | 480 | 0 | 50 | 4 | 1 | 10 | 16.8526 | 0.95777 | 158.436 | 157.2393 | 1.0076 | 380.2464 | 9304.1553 | 58913.5195 | 0 | 0 | 0 | 3.4765 | 1.6655e-07 | 5.7175e-05 | 86.1013
2005-09-27 01:27 | 91.8084 | 87.6697 | 0.51052 | 480 | 0 | 50 | 5 | 1 | 10 | 18.3617 | 0.95231 | 202.7159 | 200.2341 | 1.0124 | 486.5183 | 11904.4941 | 59409.5391 | 0 | 0 | 0 | 3.4818 | 5.7671e-08 | 1.9798e-05 | 86.159
2005-09-28 03:55 | 53.6225 | 88.6034 | 1.2776 | 480 | 0 | 50 | 3 | 1 | 10 | 17.8742 | 0.94639 | 113.724 | 112.2141 | 1.0135 | 272.9376 | 7241.3745 | 59711.2617 | 0 | 0 | 0 | 3.4732 | 1.5963e-07 | 5.0538e-05 | 86.3186
2005-09-29 00:09 | 59.0519 | 88.1846 | 1.7643 | 480 | 0 | 50 | 3 | 1 | 11 | 19.684 | 0.94187 | 128.628 | 126.3272 | 1.0182 | 308.7072 | 6251.3203 | 59971.7344 | 0 | 0 | 0 | 3.476 | 1.6715e-07 | 6.9333e-05 | 86.4858
2005-09-30 00:31 | 74.3324 | 87.9003 | 1.0611 | 480 | 0 | 50 | 4 | 1 | 11 | 18.5831 | 0.93643 | 163.4039 | 161.278 | 1.0132 | 392.1694 | 9559.1299 | 60370.0312 | 0 | 0 | 0 | 3.482 | 1.1936e-07 | 4.1133e-05 | 86.6051
2005-10-01 00:59 | 58.4175 | 89.08 | 1.5148 | 480 | 0 | 50 | 3 | 1 | 10 | 19.4725 | 0.93098 | 119.988 | 117.9425 | 1.0173 | 287.9712 | 7019.2983 | 60662.5039 | 0 | 0 | 0 | 3.475 | 1.7315e-07 | 5.967e-05 | 86.7783
2005-10-02 01:22 | 77.229 | 85.4756 | 1.2789 | 480 | 0 | 50 | 5 | 1 | 11 | 15.4458 | 0.92552 | 215.46 | 212.6294 | 1.0133 | 517.1039 | 12652.8867 | 61189.707 | 0 | 0 | 0 | 3.4802 | 1.4501e-07 | 4.9779e-05 | 86.9233
2005-10-03 01:50 | 70.3899 | 87.049 | 1.3925 | 480 | 0 | 50 | 4 | 1 | 11 | 17.5975 | 0.92006 | 172.8 | 170.7475 | 1.012 | 414.72 | 10147.6797 | 61612.5273 | 0 | 0 | 0 | 3.4773 | 1.5894e-07 | 5.4563e-05 | 87.0823
2005-10-04 02:16 | 53.0275 | 88.24 | 1.127 | 480 | 0 | 50 | 3 | 1 | 10 | 17.6758 | 0.91462 | 121.716 | 119.9803 | 1.0145 | 292.1185 | 7120.3887 | 61909.2109 | 0 | 0 | 0 | 3.4834 | 1.2634e-07 | 4.3538e-05 | 87.2086
2005-10-05 02:46 | 76.9171 | 86.7034 | 1.4577 | 480 | 0 | 50 | 5 | 1 | 10 | 15.3834 | 0.90914 | 197.316 | 195.8404 | 1.0075 | 473.5583 | 11631.7764 | 62393.8672 | 0 | 0 | 0 | 3.4768 | 1.6723e-07 | 5.7187e-05 | 87.3758
2005-10-06 03:15 | 56.5888 | 89.8101 | 1.1475 | 480 | 0 | 50 | 3 | 1 | 9 | 18.8629 | 0.90368 | 112.752 | 111.3089 | 1.013 | 270.6049 | 6621.3643 | 62669.7578 | 0 | 0 | 0 | 3.4826 | 1.2937e-07 | 4.4411e-05 | 87.5052
2005-10-07 03:37 | 51.2749 | 88.5053 | 1.2626 | 480 | 0 | 50 | 3 | 1 | 10 | 17.0916 | 0.89824 | 116.748 | 114.8877 | 1.0162 | 280.1952 | 6829.7568 | 62954.332 | 0 | 0 | 0 | 3.4735 | 1.448e-07 | 4.9901e-05 | 87.65
2005-10-08 04:02 | 78.3052 | 85.2876 | 0.84336 | 480 | 0 | 50 | 6 | 1 | 10 | 13.0509 | 0.89279 | 229.716 | 228.1236 | 1.007 | 551.3185 | 13438.3877 | 63514.2656 | 0 | 0 | 0 | 3.4764 | 9.6083e-08 | 3.3111e-05 | 87.7461
2005-10-09 00:27 | 66.4124 | 88.7217 | 1.1919 | 480 | 0 | 50 | 4 | 1 | 9 | 16.6031 | 0.88823 | 149.472 | 147.2026 | 1.0154 | 358.7329 | 7331.603 | 63819.75 | 0 | 0 | 0 | 3.4784 | 1.1334e-07 | 4.6583e-05 | 87.8594
2005-10-10 00:50 | 51.924 | 87.609 | 0.72743 | 480 | 0 | 50 | 3 | 1 | 11 | 17.308 | 0.88279 | 129.06 | 126.9941 | 1.0163 | 309.744 | 7550.0098 | 64134.332 | 0 | 0 | 0 | 3.4802 | 8.2152e-08 | 2.831e-05 | 87.9416
2005-10-11 01:24 | 64.9568 | 89.6114 | 0.89928 | 480 | 0 | 50 | 3 | 1 | 11 | 21.6523 | 0.87731 | 129.168 | 127.7564 | 1.011 | 310.0032 | 7614.4536 | 64451.6016 | 0 | 0 | 0 | 3.4794 | 1.0254e-07 | 3.5066e-05 | 88.0441
2005-10-12 01:54 | 87.3289 | 86.7504 | 0.73337 | 480 | 0 | 50 | 6 | 1 | 10 | 14.5548 | 0.87185 | 228.204 | 224.7952 | 1.0152 | 547.6896 | 13401.2812 | 65009.9883 | 0 | 0 | 0 | 3.4783 | 8.3509e-08 | 2.8668e-05 | 88.1276
2005-10-13 02:23 | 47.8 | 86.4687 | 0.76123 | 480 | 0 | 50 | 3 | 1 | 11 | 15.9333 | 0.86639 | 136.188 | 134.6936 | 1.0111 | 326.8513 | 7997.6426 | 65343.2227 | 0 | 0 | 0 | 3.4763 | 8.7096e-08 | 2.9899e-05 | 88.2147
2005-10-14 02:55 | 67.651 | 89.0463 | 0.76255 | 480 | 0 | 50 | 4 | 1 | 9 | 16.9127 | 0.8609 | 150.66 | 149.5205 | 1.0076 | 361.584 | 8881.4062 | 65713.2812 | 0 | 0 | 0 | 3.4775 | 8.7323e-08 | 2.9863e-05 | 88.3021
2005-10-15 03:42 | 46.1064 | 88.9725 | 0.92846 | 480 | 0 | 50 | 3 | 1 | 9 | 15.3688 | 0.85538 | 106.92 | 106.0571 | 1.0081 | 256.608 | 6351.0479 | 65977.9062 | 0 | 0 | 0 | 3.4777 | 1.0709e-07 | 3.6345e-05 | 88.4091
2005-10-16 00:04 | 54.6574 | 87.7653 | 1.1163 | 480 | 0 | 50 | 3 | 1 | 11 | 18.2191 | 0.85082 | 138.996 | 136.8123 | 1.016 | 333.5904 | 6817.7529 | 66261.9766 | 0 | 0 | 0 | 3.4723 | 1.0765e-07 | 4.4245e-05 | 88.5168
2005-10-17 00:26 | 47.8942 | 87.7503 | 1.2079 | 480 | 0 | 50 | 3 | 1 | 9 | 15.9647 | 0.99538 | 109.836 | 108.5668 | 1.0117 | 263.6065 | 6425.4077 | 66529.7031 | 0 | 0 | 0 | 3.4814 | 1.3605e-07 | 4.6885e-05 | 88.6528
2005-10-18 00:59 | 78.0441 | 86.4986 | 1.1189 | 480 | 0 | 50 | 5 | 1 | 10 | 15.6088 | 0.98991 | 190.2961 | 187.7622 | 1.0135 | 456.7105 | 11175.1357 | 66995.3359 | 0 | 0 | 0 | 3.4747 | 1.2849e-07 | 4.4108e-05 | 88.7813
2005-10-19 00:25 | 51.8029 | 85.1 | 1.2574 | 0 | 30.189 | 50 | 4 | 1 | 10 | 12.9507 | 0.98468 | 149.7959 | 148.9317 | 1.0058 | 359.5103 | 8426.0225 | 67346.4219 | 0.0064 | 0.020225 | 0.020145 | 2.1718 | 2.778e-06 | 0.00099514 | 91.5593
2005-10-19 04:28 | 57.261 | 87.8261 | 0.65052 | 480 | 0 | 50 | 3 | 1 | 10 | 19.087 | 0.98376 | 128.196 | 127.0679 | 1.0089 | 307.6704 | 1269.1403 | 67399.3047 | 0 | 0.020795 | 0.020694 | 3.4776 | 1.251e-08 | 2.5474e-05 | 91.5718
2005-10-20 00:52 | 65.4461 | 88.3977 | 0.54238 | 480 | 0 | 50 | 3 | 1 | 11 | 21.8154 | 0.97922 | 134.46 | 133.0332 | 1.0107 | 322.7041 | 6565.0107 | 67672.8438 | 0 | 0.020225 | 0.020159 | 3.4713 | 5.2192e-08 | 2.155e-05 | 91.624
2005-10-21 01:21 | 57.1631 | 85.4668 | 0.56646 | 385.5 | 0.081667 | 50 | 4 | 1 | 10 | 14.2908 | 0.97376 | 162.756 | 160.3322 | 1.0151 | 390.6145 | 9557.8477 | 68071.0859 | 0.0061303 | 0.04044 | 0.039207 | 2.19 | 1.2528e-06 | 0.00042999 | 92.8768
2005-10-22 01:49 | 51.3993 | 90.3052 | 0.58143 | 480 | 0 | 50 | 2 | 1 | 11 | 25.6996 | 0.9683 | 86.832 | 85.7771 | 1.0123 | 208.3968 | 5099.2095 | 68283.5547 | 0 | 0.04043 | 0.039503 | 3.4806 | 6.5861e-08 | 2.2609e-05 | 92.9427
2005-10-23 02:19 | 60.287 | 87.3749 | 0.19177 | 480 | 0 | 50 | 4 | 1 | 9 | 15.0718 | 0.96281 | 146.664 | 143.9701 | 1.0187 | 351.9937 | 8645.8447 | 68643.7969 | 0 | 0.040373 | 0.0398 | 3.4838 | 2.1644e-08 | 7.402e-06 | 92.9643
2005-10-24 02:47 | 56.9101 | 86.4115 | 0.47032 | 480 | 0 | 50 | 4 | 1 | 10 | 14.2275 | 0.95735 | 149.7959 | 147.635 | 1.0146 | 359.5103 | 8796.7676 | 69010.3281 | 0 | 0.041505 | 0.041349 | 3.4838 | 5.289e-08 | 1.8157e-05 | 93.0172
2005-10-25 03:29 | 75.7838 | 88.0672 | 0.47899 | 480 | 0 | 50 | 4 | 1 | 10 | 18.9459 | 0.95185 | 167.076 | 165.7721 | 1.0079 | 400.9824 | 9886.7217 | 69422.2734 | 0 | 0.041494 | 0.041339 | 3.4768 | 5.5156e-08 | 1.879e-05 | 93.0724
2005-10-26 03:52 | 67.8115 | 90.0681 | 0.54419 | 480 | 0 | 50 | 3 | 1 | 10 | 22.6038 | 0.94641 | 123.444 | 121.6281 | 1.0149 | 296.2657 | 7221.4761 | 69723.1719 | 0 | 0.041499 | 0.041262 | 3.4752 | 6.218e-08 | 2.1428e-05 | 93.1346
2005-10-27 00:36 | 54.9107 | 87.0619 | 0.68569 | 480 | 0 | 50 | 3 | 1 | 11 | 18.3036 | 0.94178 | 136.188 | 134.6401 | 1.0115 | 326.8513 | 6771.9502 | 70005.3359 | 0 | 0.040343 | 0.04015 | 3.4776 | 6.6219e-08 | 2.6847e-05 | 93.2008
2005-10-28 01:07 | 58.0829 | 90.6004 | 0.35438 | 480 | 0 | 50 | 3 | 1 | 9 | 19.361 | 0.9363 | 103.572 | 101.4691 | 1.0207 | 248.5728 | 6105.5688 | 70259.7344 | 0 | 0.040338 | 0.040633 | 3.4718 | 4.1117e-08 | 1.4061e-05 | 93.2419
2005-10-29 01:47 | 51.6441 | 86.8079 | 0.4376 | 480 | 0 | 50 | 3 | 1 | 11 | 17.2147 | 0.9308 | 132.732 | 131.7471 | 1.0075 | 318.5569 | 7854.4175 | 70587 | 0 | 0.041575 | 0.042187 | 3.4754 | 5.055e-08 | 1.7221e-05 | 93.2924
2005-10-30 02:15 | 48.5214 | 88.4398 | 0.57969 | 402.6 | 0.043333 | 50 | 3 | 1 | 9 | 16.1738 | 0.92533 | 112.428 | 110.359 | 1.0187 | 269.8273 | 6602.3369 | 70862.0938 | 0.0061303 | 0.062354 | 0.059456 | 2.1897 | 1.2832e-06 | 0.00044041 | 94.5756
2005-10-31 02:44 | 37.5338 | 87.7937 | 0.26465 | 480 | 0 | 50 | 2 | 1 | 11 | 18.7669 | 0.91987 | 89.208 | 88.1791 | 1.0117 | 214.0992 | 5238.7407 | 71080.375 | 0 | 0.062346 | 0.060221 | 3.4796 | 3.0045e-08 | 1.0314e-05 | 94.6057
2005-11-01 03:24 | 58.7756 | 89.4706 | 0.35212 | 480 | 0 | 50 | 3 | 1 | 10 | 19.5919 | 0.91437 | 118.476 | 117.3485 | 1.0096 | 284.3424 | 7010.8174 | 71372.4922 | 0 | 0.06233 | 0.060875 | 3.4786 | 4.0377e-08 | 1.3756e-05 | 94.646
2005-11-02 03:50 | 47.5596 | 86.626 | 0.25248 | 480 | 0 | 50 | 3 | 1 | 11 | 15.8532 | 0.90891 | 129.06 | 126.8769 | 1.0172 | 309.744 | 7579.0483 | 71688.2891 | 0 | 0.06233 | 0.061592 | 3.4819 | 2.8515e-08 | 9.7889e-06 | 94.6745
2005-11-03 00:19 | 59.7648 | 87.0331 | 0.31056 | 480 | 0 | 50 | 4 | 1 | 10 | 14.9412 | 0.90435 | 156.816 | 154.4044 | 1.0156 | 376.3584 | 7691.8242 | 72008.7812 | 0 | 0.060614 | 0.055793 | 3.4744 | 2.9803e-08 | 1.2249e-05 | 94.7043
2005-11-04 00:45 | 49.606 | 89.3361 | 0.33328 | 480 | 0 | 50 | 3 | 1 | 9 | 16.5353 | 0.89888 | 106.92 | 105.1509 | 1.0168 | 256.608 | 6278.877 | 72270.3984 | 0 | 0.060606 | 0.060285 | 3.4867 | 3.7224e-08 | 1.2779e-05 | 94.7416
2005-11-05 01:17 | 42 | 87.6273 | 0.34711 | 480 | 0 | 50 | 3 | 1 | 9 | 14 | 0.8934 | 109.836 | 108.4728 | 1.0126 | 263.6065 | 6474.834 | 72540.1797 | 0 | 0.060606 | 0.060939 | 3.4824 | 3.9309e-08 | 1.3443e-05 | 94.7809
2005-11-06 01:44 | 51.2228 | 88.5622 | 0.45069 | 480 | 0 | 50 | 3 | 1 | 10 | 17.0743 | 0.88796 | 118.476 | 117.0661 | 1.012 | 284.3424 | 6930.8462 | 72828.9688 | 0 | 0.060614 | 0.061645 | 3.4811 | 5.08e-08 | 1.7506e-05 | 94.8317
2005-11-07 02:12 | 55.2177 | 89.9771 | 0.37541 | 480 | 0 | 50 | 3 | 1 | 9 | 18.4059 | 0.8825 | 112.752 | 110.7841 | 1.0178 | 270.6049 | 6621.3643 | 73104.8594 | 0 | 0.060606 | 0.061663 | 3.4877 | 4.1835e-08 | 1.4362e-05 | 94.8735
2005-11-08 03:17 | 84.5527 | 87.1615 | 0.57318 | 480 | 0 | 50 | 5 | 1 | 11 | 16.9105 | 0.87689 | 213.4079 | 209.8684 | 1.0169 | 512.1791 | 12868.499 | 73641.0469 | 0 | 0.062257 | 0.047262 | 3.4757 | 6.7428e-08 | 2.2543e-05 | 94.9409
2005-11-09 03:48 | 51.5889 | 90.332 | 0.70255 | 480 | 0 | 50 | 3 | 1 | 9 | 17.1963 | 0.87141 | 101.088 | 100.5829 | 1.005 | 242.6111 | 5959.1357 | 73889.3438 | 0 | 0.062241 | 0.063244 | 3.4746 | 8.1e-08 | 2.77e-05 | 95.0219
2005-11-10 00:16 | 55.2615 | 86.451 | 0.60844 | 480 | 0 | 50 | 4 | 1 | 10 | 13.8154 | 0.86685 | 161.892 | 158.8207 | 1.0193 | 388.5409 | 7940.8037 | 74220.2109 | 0 | 0.06053 | 0.057258 | 3.474 | 5.8441e-08 | 2.402e-05 | 95.0804
2005-11-11 00:46 | 78.4413 | 87.9769 | 0.53065 | 480 | 0 | 50 | 5 | 1 | 10 | 15.6883 | 0.86138 | 190.2961 | 187.0507 | 1.0174 | 456.7105 | 11175.1357 | 74685.8438 | 0 | 0.060537 | 0.045594 | 3.4784 | 6.0409e-08 | 2.0738e-05 | 95.1408
2005-11-12 01:24 | 55.1299 | 89.8514 | 0.4756 | 480 | 0 | 50 | 3 | 1 | 10 | 18.3766 | 0.85588 | 115.236 | 113.0525 | 1.0193 | 276.5664 | 6819.0898 | 74969.9688 | 0 | 0.060522 | 0.061658 | 3.4886 | 5.3296e-08 | 1.8157e-05 | 95.1941
2005-11-13 01:50 | 57.4715 | 90.5882 | 0.7228 | 480 | 0 | 50 | 3 | 1 | 9 | 19.1572 | 0.85042 | 112.752 | 111.529 | 1.011 | 270.6049 | 6621.3643 | 75245.8594 | 0 | 0.060522 | 0.062057 | 3.4808 | 8.1846e-08 | 2.8097e-05 | 95.2759
2005-11-14 02:17 | 51.6878 | 89.2358 | 0.58708 | 480 | 0 | 50 | 3 | 1 | 9 | 17.2293 | 0.99498 | 101.088 | 100.6027 | 1.0048 | 242.6111 | 5913.6465 | 75492.2578 | 0 | 0.060537 | 0.062185 | 3.4744 | 6.7199e-08 | 2.3157e-05 | 95.3431
2005-11-15 01:41 | 51.7273 | 89.1013 | 0.54321 | 480 | 0 | 50 | 3 | 1 | 9 | 17.2424 | 0.98975 | 104.004 | 102.8297 | 1.0114 | 249.6096 | 5850.2246 | 75736.0156 | 0 | 0.062362 | 0.06403 | 3.4812 | 5.8854e-08 | 2.1093e-05 | 95.402
2005-11-16 02:19 | 55.4455 | 87.7132 | 0.56331 | 480 | 0 | 50 | 3 | 1 | 10 | 18.4818 | 0.98424 | 128.088 | 126.1134 | 1.0157 | 307.4112 | 7579.6064 | 76051.8359 | 0 | 0.062338 | 0.063919 | 3.4812 | 6.4207e-08 | 2.1874e-05 | 95.4662
2005-11-17 01:46 | 58.8295 | 87.9985 | 0.52869 | 480 | 0 | 50 | 3 | 1 | 11 | 19.6098 | 0.97901 | 128.952 | 126.583 | 1.0187 | 309.4848 | 7253.5503 | 76354.0703 | 0 | 0.062427 | 0.064232 | 3.4801 | 5.7433e-08 | 2.0584e-05 | 95.5236
2005-11-18 02:24 | 55.2438 | 89.3387 | 0.62142 | 480 | 0 | 50 | 3 | 1 | 9 | 18.4146 | 0.97351 | 109.836 | 108.7986 | 1.0095 | 263.6065 | 6499.5474 | 76624.8828 | 0 | 0.041548 | 0.040694 | 3.4793 | 7.1143e-08 | 2.4237e-05 | 95.5948
2005-11-19 03:00 | 33.6422 | 90.6371 | 0.81066 | 480 | 0 | 50 | 2 | 1 | 8 | 16.8211 | 0.96802 | 60.48 | 59.279 | 1.0203 | 145.152 | 3565.2954 | 76773.4375 | 0 | 0.041542 | 0.041075 | 3.4909 | 9.0012e-08 | 3.0782e-05 | 95.6848
2005-11-20 03:26 | 48.7624 | 90.0016 | 0.71394 | 480 | 0 | 50 | 2 | 1 | 11 | 24.3812 | 0.96256 | 86.832 | 85.8857 | 1.011 | 208.3968 | 5099.2095 | 76985.9062 | 0 | 0.020771 | 0.018695 | 3.4789 | 8.1187e-08 | 2.7871e-05 | 95.766
2005-11-21 03:50 | 43.3728 | 89.6788 | 0.46162 | 480 | 0 | 50 | 2 | 1 | 10 | 21.6864 | 0.95712 | 83.7 | 82.3026 | 1.017 | 200.88 | 4896.4507 | 77189.9219 | 0 | 0.020774 | 0.018791 | 3.4733 | 5.2978e-08 | 1.8257e-05 | 95.8189
2005-11-22 00:32 | 64.5752 | 89.2088 | 0.61434 | 480 | 0 | 50 | 3 | 1 | 11 | 21.5251 | 0.9525 | 125.604 | 124.8874 | 1.0057 | 301.4496 | 6245.6587 | 77450.1562 | 0 | 0.020194 | 0.018279 | 3.4738 | 5.9849e-08 | 2.4264e-05 | 95.8788
2005-11-23 00:58 | 34.2703 | 89.9523 | 0.60117 | 409.5 | 0.07 | 50 | 2 | 1 | 8 | 17.1352 | 0.94706 | 67.392 | 67.101 | 1.0043 | 161.7408 | 3942.4326 | 77614.4219 | 0.0061538 | 0.040399 | 0.036466 | 2.188 | 1.3308e-06 | 0.00045852 | 97.2096
2005-11-24 01:36 | 51.2656 | 88.9907 | 0.29835 | 480 | 0 | 50 | 3 | 1 | 9 | 17.0885 | 0.94155 | 109.836 | 108.8434 | 1.0091 | 263.6065 | 6499.5474 | 77885.2344 | 0 | 0.040389 | 0.030713 | 3.4788 | 3.4194e-08 | 1.1649e-05 | 97.2438
2005-11-25 01:57 | 59.3456 | 89.9128 | 0.43574 | 480 | 0 | 50 | 3 | 1 | 9 | 19.7819 | 0.93611 | 115.668 | 113.9433 | 1.0151 | 277.6032 | 6766.5776 | 78167.1719 | 0 | 0.040404 | 0.030933 | 3.485 | 4.8672e-08 | 1.6773e-05 | 97.2925
2005-11-26 02:25 | 47.4703 | 89.2848 | 0.40468 | 480 | 0 | 50 | 3 | 1 | 8 | 15.8234 | 0.93065 | 102.816 | 101.2591 | 1.0154 | 246.7584 | 6037.8691 | 78418.75 | 0 | 0.041558 | 0.032309 | 3.486 | 4.5273e-08 | 1.5542e-05 | 97.3378
2005-11-27 02:47 | 45.9288 | 89.905 | 0.56903 | 480 | 0 | 50 | 2 | 1 | 11 | 22.9644 | 0.92521 | 86.724 | 85.3444 | 1.0162 | 208.1376 | 5073.354 | 78630.1406 | 0 | 0.041569 | 0.038971 | 3.4777 | 6.4638e-08 | 2.2275e-05 | 97.4024
2005-11-28 03:21 | 61.6221 | 92.7077 | 0.34661 | 480 | 0 | 50 | 3 | 1 | 8 | 20.5407 | 0.91973 | 88.776 | 87.2171 | 1.0179 | 213.0624 | 5233.3462 | 78848.1953 | 0 | 0.041575 | 0.032546 | 3.4721 | 4.0193e-08 | 1.3745e-05 | 97.4426
2005-11-29 04:01 | 38.3617 | 89.1766 | 0.41856 | 480 | 0 | 50 | 2 | 1 | 10 | 19.1809 | 0.91422 | 81.864 | 81.0029 | 1.0106 | 196.4736 | 4844.3032 | 79050.0391 | 0 | 0.020782 | 0.019369 | 3.4788 | 4.7979e-08 | 1.6346e-05 | 97.4906
2005-11-30 00:33 | 42.5849 | 90.7976 | 0.51345 | 480 | 0 | 50 | 2 | 1 | 9 | 21.2924 | 0.90964 | 77.76 | 76.6209 | 1.0149 | 186.624 | 3831.6243 | 79209.6875 | 0 | 0.020207 | 0.018957 | 3.4845 | 4.8372e-08 | 1.979e-05 | 97.5389
2005-12-01 04:20 | 58.6819 | 89.4662 | 0.16789 | 480 | 0 | 50 | 3 | 1 | 10 | 19.5606 | 0.90345 | 121.716 | 120.0601 | 1.0138 | 292.1185 | 8106.2886 | 79547.4531 | 0 | 0.020806 | 0.012914 | 3.4824 | 2.1479e-08 | 6.5017e-06 | 97.5604
2005-12-02 00:48 | 48.74 | 90.5476 | 0.61623 | 480 | 0 | 50 | 2 | 1 | 11 | 24.37 | 0.89886 | 86.832 | 86.4926 | 1.0039 | 208.3968 | 4278.647 | 79725.7266 | 0 | 0.02023 | 0.018828 | 3.4713 | 5.9842e-08 | 2.4483e-05 | 97.6203
2005-12-03 01:15 | 50.6544 | 89.3489 | 0.767 | 480 | 0 | 50 | 3 | 1 | 9 | 16.8848 | 0.89342 | 109.836 | 109.1202 | 1.0066 | 263.6065 | 6425.4077 | 79993.4531 | 0 | 0.020806 | 0.012942 | 3.4761 | 8.7449e-08 | 3.0136e-05 | 97.7077
2005-12-04 01:42 | 57.4677 | 90.2164 | 0.82292 | 480 | 0 | 50 | 3 | 1 | 9 | 19.1559 | 0.88796 | 114.372 | 112.5547 | 1.0161 | 274.4929 | 6716.4971 | 80273.3047 | 0 | 0.020806 | 0.012947 | 3.4749 | 9.4448e-08 | 3.2423e-05 | 97.8022
2005-12-05 02:11 | 39.1435 | 90.3574 | 0.45636 | 480 | 0 | 50 | 2 | 1 | 9 | 19.5718 | 0.8825 | 77.76 | 76.7186 | 1.0136 | 186.624 | 4566.4561 | 80463.5703 | 0 | 0.020809 | 0.019392 | 3.4832 | 5.1392e-08 | 1.7642e-05 | 97.8536
2005-12-06 02:45 | 40.7717 | 90.0265 | 0.1609 | 204.5 | 0.12833 | 50 | 2 | 1 | 10 | 20.3858 | 0.87702 | 81.864 | 81.4921 | 1.0046 | 196.4736 | 4825.8838 | 80664.6484 | 0.0061069 | 0.041607 | 0.035213 | 2.191 | 3.5642e-07 | 0.00012188 | 98.21
2005-12-07 03:13 | 47.5753 | 88.2859 | 1.3412 | 480 | 0 | 50 | 3 | 1 | 10 | 15.8584 | 0.87155 | 117.72 | 115.5673 | 1.0186 | 282.528 | 6913.1064 | 80952.6953 | 0 | 0.041607 | 0.023613 | 3.4719 | 1.55e-07 | 5.3211e-05 | 98.365
2005-12-08 03:37 | 48.8618 | 89.7168 | 0.50397 | 480 | 0 | 50 | 3 | 1 | 9 | 16.2873 | 0.86609 | 105.732 | 104.2275 | 1.0144 | 253.7568 | 6209.1108 | 81211.4062 | 0 | 0.041645 | 0.023977 | 3.4732 | 5.8075e-08 | 1.9937e-05 | 98.4231
2005-12-09 00:16 | 51.4559 | 90.3375 | 1.4148 | 480 | 0 | 50 | 3 | 1 | 9 | 17.152 | 0.86149 | 104.004 | 102.5629 | 1.0141 | 249.6096 | 5148.1973 | 81425.9141 | 0 | 0.040486 | 0.02333 | 3.4839 | 1.3408e-07 | 5.4606e-05 | 98.5571
2005-12-10 00:45 | 42.6236 | 89.2073 | 0.93389 | 480 | 0 | 50 | 2 | 1 | 11 | 21.3118 | 0.85603 | 93.96 | 93.2619 | 1.0075 | 225.504 | 5517.8008 | 81655.8203 | 0 | 0.04164 | 0.036533 | 3.4738 | 1.0747e-07 | 3.6892e-05 | 98.6646
2005-12-11 01:08 | 56.5445 | 87.9577 | 0.57567 | 480 | 0 | 50 | 4 | 1 | 9 | 14.1361 | 0.85059 | 148.392 | 146.0097 | 1.0163 | 356.1408 | 8680.9326 | 82017.5234 | 0 | 0.041645 | 0.018482 | 3.478 | 6.5347e-08 | 2.2519e-05 | 98.73
2005-12-12 01:40 | 44.0542 | 89.9211 | 0.28823 | 480 | 0 | 50 | 2 | 1 | 10 | 22.0271 | 0.9951 | 79.704 | 78.7492 | 1.0121 | 191.2896 | 4698.5508 | 82213.2969 | 0 | 0.04165 | 0.037387 | 3.4803 | 3.28e-08 | 1.1217e-05 | 98.7628
2005-12-13 02:15 | 49.1863 | 88.6555 | 1.5843 | 480 | 0 | 50 | 3 | 1 | 9 | 16.3954 | 0.98962 | 105.624 | 103.8848 | 1.0167 | 253.4975 | 6226.5332 | 82472.7344 | 0 | 0.041645 | 0.025087 | 3.4742 | 1.8284e-07 | 6.2525e-05 | 98.9456
2005-12-14 02:52 | 62.9192 | 91.1962 | 1.0148 | 480 | 0 | 50 | 3 | 1 | 8 | 20.9731 | 0.98412 | 102.816 | 101.6321 | 1.0116 | 246.7584 | 6084.1362 | 82726.2422 | 0 | 0.041629 | 0.025051 | 3.4822 | 1.1541e-07 | 3.9316e-05 | 99.061
2005-12-15 03:25 | 61.5606 | 90.3584 | 0.77456 | 480 | 0 | 50 | 3 | 1 | 9 | 20.5202 | 0.97866 | 109.836 | 107.9755 | 1.0172 | 263.6065 | 6450.1211 | 82995 | 0 | 0.041569 | 0.024835 | 3.4871 | 8.6442e-08 | 2.9675e-05 | 99.1474
2005-12-16 03:55 | 49.3634 | 90.3159 | 0.52638 | 480 | 0 | 50 | 2 | 1 | 11 | 24.6817 | 0.97317 | 84.456 | 83.5998 | 1.0102 | 202.6944 | 4978.6816 | 83202.4453 | 0 | 0.041575 | 0.037209 | 3.4777 | 6.0251e-08 | 2.0605e-05 | 99.2077
2005-12-17 00:26 | 44.0598 | 89.7996 | 0.425 | 480 | 0 | 50 | 2 | 1 | 10 | 22.0299 | 0.96859 | 83.592 | 82.2206 | 1.0167 | 200.6208 | 4118.9966 | 83374.0703 | 0 | 0.040424 | 0.036245 | 3.4722 | 4.1182e-08 | 1.6849e-05 | 99.2489
2005-12-18 00:54 | 54.1492 | 89.1213 | 0.30754 | 480 | 0 | 50 | 3 | 1 | 9 | 18.0497 | 0.96313 | 112.752 | 111.6552 | 1.0098 | 270.6049 | 6621.3643 | 83649.9609 | 0 | 0.040368 | 0.024253 | 3.4795 | 3.4926e-08 | 1.199e-05 | 99.2838
2005-12-19 01:24 | 62.9377 | 88.823 | 0.27362 | 480 | 0 | 50 | 3 | 1 | 11 | 20.9792 | 0.95767 | 129.06 | 127.5981 | 1.0115 | 309.744 | 7579.0483 | 83965.7578 | 0 | 0.040379 | 0.024236 | 3.4787 | 3.1131e-08 | 1.0687e-05 | 99.3149
2005-12-20 01:48 | 41.7568 | 90.1514 | 0.24103 | 480 | 0 | 50 | 2 | 1 | 10 | 20.8784 | 0.95223 | 77.328 | 76.1171 | 1.0159 | 185.5872 | 4523.688 | 84154.2422 | 0 | 0.040389 | 0.036173 | 3.4729 | 2.7687e-08 | 9.5412e-06 | 99.3426
2005-12-21 02:16 | 49.8363 | 89.89 | 0.40204 | 480 | 0 | 50 | 2 | 1 | 11 | 24.9181 | 0.94676 | 93.312 | 91.4259 | 1.0206 | 223.9488 | 5479.7471 | 84382.5625 | 0 | 0.040389 | 0.036064 | 3.4771 | 4.5913e-08 | 1.5762e-05 | 99.3885
2005-12-22 02:41 | 41.5217 | 89.4574 | 0.35685 | 480 | 0 | 50 | 2 | 1 | 10 | 20.7609 | 0.9413 | 84.024 | 83.1316 | 1.0107 | 201.6576 | 4934.3096 | 84588.1562 | 0 | 0.041542 | 0.037188 | 3.4786 | 4.0606e-08 | 1.394e-05 | 99.4291
2005-12-23 03:11 | 19.0616 | 90.2055 | 0.22361 | 480 | 0 | 50 | 1 | 1 | 9 | 19.0616 | 0.93584 | 36.828 | 36.1278 | 1.0194 | 88.3872 | 2162.7244 | 84678.2734 | 0 | 0.020768 | 0.016841 | 3.4734 | 2.5753e-08 | 8.8407e-06 | 99.4549
2005-12-24 03:37 | 43.6429 | 90.0374 | 0.46273 | 480 | 0 | 50 | 2 | 1 | 10 | 21.8215 | 0.93038 | 83.808 | 82.6422 | 1.0141 | 201.1392 | 4921.6255 | 84883.3438 | 0 | 0.020774 | 0.016978 | 3.475 | 5.31e-08 | 1.8229e-05 | 99.508
2005-12-25 04:01 | 50.3696 | 88.3948 | 0.20567 | 480 | 0 | 50 | 3 | 1 | 10 | 16.7899 | 0.92494 | 115.236 | 114.5489 | 1.006 | 276.5664 | 6741.3052 | 85164.2344 | 0 | 0.020774 | 0.011384 | 3.4743 | 2.3547e-08 | 8.1145e-06 | 99.5315
2005-12-26 00:22 | 59.9746 | 89.2442 | 0.15754 | 480 | 0 | 50 | 3 | 1 | 10 | 19.9915 | 0.9204 | 126.684 | 124.5552 | 1.0171 | 304.0417 | 6185.3481 | 85421.9609 | 0 | 0.020205 | 0.011031 | 3.4772 | 1.4952e-08 | 6.1738e-06 | 99.5465
2005-12-27 00:52 | 51.1181 | 89.6369 | 0.19897 | 480 | 0 | 50 | 3 | 1 | 9 | 17.0394 | 0.91493 | 106.812 | 104.8239 | 1.019 | 256.3488 | 6272.5342 | 85683.3203 | 0 | 0.020205 | 0.011016 | 3.4819 | 2.2472e-08 | 7.7146e-06 | 99.569
2005-12-28 01:24 | 33.7145 | 89.7307 | 0.24391 | 480 | 0 | 50 | 2 | 1 | 9 | 16.8572 | 0.90945 | 69.984 | 69.6325 | 1.005 | 167.9616 | 4125.5571 | 85855.2188 | 0 | 0.020199 | 0.016567 | 3.4744 | 2.8134e-08 | 9.6214e-06 | 99.5971
2005-12-29 01:14 | 55.5247 | 88.6518 | 0.35036 | 480 | 0 | 50 | 3 | 1 | 10 | 18.5082 | 0.90414 | 127.656 | 125.6876 | 1.0157 | 306.3744 | 7295.54 | 86159.2031 | 0 | 0.02022 | 0.011124 | 3.4744 | 3.9174e-08 | 1.3819e-05 | 99.6363
2005-12-30 00:40 | 39.5605 | 88.8325 | 0.34806 | 480 | 0 | 50 | 2 | 1 | 11 | 19.7803 | 0.8989 | 88.344 | 86.6103 | 1.02 | 212.0257 | 4969.3511 | 86366.2578 | 0 | 0.020831 | 0.017139 | 3.4713 | 3.8585e-08 | 1.3829e-05 | 99.6749
2005-12-31 00:31 | 52.4846 | 88.9224 | 0.3263 | 480 | 0 | 50 | 3 | 1 | 10 | 17.4949 | 0.89357 | 118.368 | 116.6673 | 1.0146 | 284.0832 | 6791.3638 | 86649.2344 | 0 | 0.020161 | 0.011078 | 3.4778 | 3.6343e-08 | 1.277e-05 | 99.7112
2006-01-01 01:02 | 55.5032 | 89.1489 | 0.3128 | 480 | 0 | 50 | 3 | 1 | 10 | 18.5011 | 0.88811 | 122.472 | 121.0234 | 1.012 | 293.9329 | 7192.1704 | 86948.9062 | 0 | 0.020828 | 0.011455 | 3.4745 | 3.5931e-08 | 1.2335e-05 | 99.7471
2006-01-02 01:43 | 51.6093 | 87.7041 | 0.38777 | 480 | 0 | 50 | 3 | 1 | 11 | 17.2031 | 0.8826 | 130.788 | 129.0711 | 1.0133 | 313.8913 | 7739.3813 | 87271.3828 | 0 | 0.02082 | 0.011419 | 3.4732 | 4.5019e-08 | 1.5337e-05 | 99.7922
2006-01-03 02:11 | 60.6973 | 88.2854 | 0.26189 | 480 | 0 | 50 | 4 | 1 | 9 | 15.1743 | 0.87714 | 149.58 | 147.486 | 1.0142 | 358.9919 | 8784.084 | 87637.3828 | 0 | 0.02082 | 0.0085517 | 3.4794 | 2.9745e-08 | 1.0211e-05 | 99.8219
2006-01-04 02:41 | 57.0611 | 90.6266 | 0.81832 | 480 | 0 | 50 | 3 | 1 | 9 | 19.0204 | 0.87166 | 111.348 | 109.493 | 1.0169 | 267.2353 | 6563.9668 | 87910.8828 | 0 | 0.020817 | 0.011317 | 3.4739 | 9.4502e-08 | 3.2318e-05 | 99.9164
2006-01-05 01:02 | 55.8144 | 89.294 | 0.81773 | 480 | 0 | 50 | 3 | 1 | 10 | 18.6048 | 0.86668 | 124.632 | 122.8368 | 1.0146 | 299.1169 | 6674.0454 | 88188.9688 | 0 | 0.020192 | 0.010927 | 3.4742 | 8.573e-08 | 3.2274e-05 | 100.0021
2006-01-06 01:19 | 62.4004 | 89.6279 | 0.61714 | 480 | 0 | 50 | 3 | 1 | 11 | 20.8001 | 0.86126 | 130.788 | 128.9943 | 1.0139 | 313.8913 | 7621.6724 | 88506.5391 | 0 | 0 | 0 | 3.4737 | 7.0478e-08 | 2.4381e-05 | 100.0726
2006-01-07 01:48 | 52.9128 | 89.5694 | 0.63374 | 480 | 0 | 50 | 3 | 1 | 10 | 17.6376 | 0.8558 | 115.236 | 114.3255 | 1.008 | 276.5664 | 6767.2334 | 88788.5078 | 0 | 0 | 0 | 3.4764 | 7.2485e-08 | 2.4883e-05 | 100.1451
2006-01-08 01:20 | 52.3689 | 89.7088 | 0.99689 | 480 | 0 | 50 | 3 | 1 | 9 | 17.4563 | 0.85054 | 115.668 | 115.0567 | 1.0053 | 277.6032 | 6532.3496 | 89060.6875 | 0 | 0 | 0 | 3.4749 | 1.1003e-07 | 3.9278e-05 | 100.2551
2006-01-09 01:44 | 59.6161 | 90.3034 | 1.3898 | 411.6 | 0.018333 | 50 | 3 | 1 | 9 | 19.872 | 0.9951 | 105.732 | 104.3852 | 1.0129 | 253.7568 | 6185.3208 | 89318.4062 | 0.0061538 | 0.020806 | 0.022955 | 2.1878 | 3.0778e-06 | 0.0010601 | 103.333
2006-01-10 02:18 | 61.0037 | 90.7615 | 0.86661 | 480 | 0 | 50 | 3 | 1 | 9 | 20.3346 | 0.9896 | 103.788 | 101.6633 | 1.0209 | 249.0912 | 6141.6543 | 89574.3047 | 0 | 0.020798 | 0.022781 | 3.4777 | 9.9589e-08 | 3.3928e-05 | 103.4325
2006-01-11 02:44 | 68.6655 | 91.1134 | 1.3537 | 480 | 0 | 50 | 3 | 1 | 9 | 22.8885 | 0.98416 | 111.564 | 110.2352 | 1.0121 | 267.7537 | 6526.4956 | 89846.2422 | 0 | 0.020804 | 0.02257 | 3.4713 | 1.5606e-07 | 5.3781e-05 | 103.5886
2006-01-12 03:11 | 56.8975 | 88.5664 | 1.6192 | 480 | 0 | 50 | 3 | 1 | 10 | 18.9658 | 0.9787 | 121.716 | 120.7552 | 1.008 | 292.1185 | 7147.7744 | 90144.0625 | 0 | 0.020806 | 0.022335 | 3.4761 | 1.8532e-07 | 6.3617e-05 | 103.7739
2006-01-13 03:43 | 62.9767 | 88.4006 | 1.3115 | 480 | 0 | 50 | 3 | 1 | 11 | 20.9922 | 0.97321 | 134.46 | 132.8306 | 1.0123 | 322.7041 | 7926.4189 | 90474.3281 | 0 | 0.020809 | 0.022282 | 3.4741 | 1.5139e-07 | 5.1773e-05 | 103.9253
2006-01-14 00:04 | 43.0583 | 88.5263 | 1.5213 | 480 | 0 | 50 | 2 | 1 | 11 | 21.5291 | 0.96867 | 91.584 | 90.9993 | 1.0064 | 219.8016 | 4471.5889 | 90660.6406 | 0 | 0.020238 | 0.021662 | 3.4727 | 1.4592e-07 | 6.0251e-05 | 104.0713
2006-01-15 00:34 | 57.175 | 90.4986 | 0.5674 | 480 | 0 | 50 | 3 | 1 | 9 | 19.0583 | 0.96321 | 102.816 | 101.2388 | 1.0156 | 246.7583 | 6037.8682 | 90912.2188 | 0 | 0.020238 | 0.021829 | 3.4735 | 6.5339e-08 | 2.243e-05 | 104.1366
2006-01-16 01:02 | 60.9481 | 88.1851 | 0.80498 | 480 | 0 | 50 | 3 | 1 | 11 | 20.316 | 0.95775 | 135.648 | 133.9209 | 1.0129 | 325.5553 | 7965.9307 | 91244.1328 | 0 | 0.020817 | 0.022338 | 3.4735 | 9.2686e-08 | 3.1818e-05 | 104.2293
2006-01-17 01:29 | 52.9733 | 90.8791 | 0.18527 | 480 | 0 | 50 | 2 | 1 | 11 | 26.4866 | 0.95229 | 87.588 | 86.5644 | 1.0118 | 210.2112 | 5143.6055 | 91458.4531 | 0 | 0.020817 | 0.022224 | 3.4709 | 2.1462e-08 | 7.3678e-06 | 104.2507
2006-01-18 01:55 | 52.8688 | 90.2511 | 0.42666 | 480 | 0 | 50 | 3 | 1 | 8 | 17.6229 | 0.94685 | 101.952 | 100.771 | 1.0117 | 244.6849 | 5964.1934 | 91706.9609 | 0 | 0.02082 | 0.022308 | 3.482 | 4.7988e-08 | 1.6537e-05 | 104.2987
2006-01-19 02:22 | 66.7312 | 90.3496 | 0.48775 | 480 | 0 | 50 | 3 | 1 | 10 | 22.2437 | 0.94139 | 121.608 | 120.0185 | 1.0132 | 291.8593 | 7141.4316 | 92004.5234 | 0 | 0.020817 | 0.022198 | 3.4775 | 5.5649e-08 | 1.9104e-05 | 104.3544
2006-01-20 03:12 | 61.2649 | 88.8571 | 0.38125 | 480 | 0 | 50 | 3 | 1 | 11 | 20.4216 | 0.93584 | 129.06 | 127.968 | 1.0085 | 309.744 | 7695.2021 | 92325.1562 | 0 | 0.020806 | 0.021926 | 3.4762 | 4.4298e-08 | 1.4978e-05 | 104.3987
2006-01-21 02:36 | 62.3328 | 87.8182 | 0.5568 | 480 | 0 | 50 | 4 | 1 | 10 | 15.5832 | 0.93061 | 149.688 | 147.2121 | 1.0168 | 359.2511 | 8419.9473 | 92675.9844 | 0 | 0.020151 | 0.015845 | 3.4823 | 6.0174e-08 | 2.1566e-05 | 104.4588
2006-01-22 03:02 | 50.8975 | 90.7446 | 0.57672 | 480 | 0 | 50 | 2 | 1 | 11 | 25.4487 | 0.92517 | 88.56 | 87.1777 | 1.0159 | 212.5441 | 5180.7612 | 92891.8516 | 0 | 0.020154 | 0.020989 | 3.4713 | 6.6495e-08 | 2.2915e-05 | 104.5253
2006-01-23 03:33 | 49.1023 | 91.3271 | 0.38436 | 480 | 0 | 50 | 2 | 1 | 10 | 24.5511 | 0.91968 | 81.864 | 81.2252 | 1.0079 | 196.4736 | 4825.8838 | 93092.9297 | 0 | 0.020151 | 0.020736 | 3.4758 | 4.419e-08 | 1.5112e-05 | 104.5695
2006-01-24 03:54 | 72.5545 | 88.9628 | 0.51578 | 480 | 0 | 50 | 4 | 1 | 10 | 18.1386 | 0.91424 | 155.736 | 153.6915 | 1.0133 | 373.7664 | 9110.5547 | 93472.5391 | 0 | 0.020154 | 0.015282 | 3.4716 | 5.9422e-08 | 2.0477e-05 | 104.629
2006-01-25 00:16 | 51.1939 | 90.2751 | 0.5333 | 480 | 0 | 50 | 3 | 1 | 8 | 17.0646 | 0.9097 | 102.816 | 101.4975 | 1.013 | 246.7584 | 5019.9907 | 93681.7031 | 0 | 0.020263 | 0.020321 | 3.4836 | 4.9878e-08 | 2.0594e-05 | 104.6788
2006-01-26 00:56 | 51.4047 | 90.5463 | 0.58381 | 480 | 0 | 50 | 2 | 1 | 11 | 25.7024 | 0.9042 | 93.528 | 92.3973 | 1.0122 | 224.4672 | 5534.5195 | 93912.3047 | 0 | 0.020831 | 0.020937 | 3.475 | 6.7501e-08 | 2.2996e-05 | 104.7463
2006-01-27 01:42 | 64.9091 | 88.4438 | 0.56947 | 480 | 0 | 50 | 4 | 1 | 10 | 16.2273 | 0.89867 | 149.688 | 148.4296 | 1.0085 | 359.2511 | 8891.4648 | 94282.7812 | 0 | 0.020825 | 0.015549 | 3.4737 | 6.6299e-08 | 2.2501e-05 | 104.8126
2006-01-28 02:09 | 71.1624 | 88.5097 | 0.82445 | 480 | 0 | 50 | 4 | 1 | 10 | 17.7906 | 0.89321 | 165.348 | 162.6138 | 1.0168 | 396.8351 | 9710.0596 | 94687.3672 | 0 | 0.020806 | 0.015321 | 3.475 | 9.461e-08 | 3.2479e-05 | 104.9072
2006-01-29 02:44 | 55.1855 | 88.9102 | 0.63621 | 408.7 | 0.01 | 50 | 3 | 1 | 10 | 18.3952 | 0.88773 | 126.684 | 124.9009 | 1.0143 | 304.0417 | 7468.0239 | 94998.5312 | 0 | 0.020774 | 0.020213 | 3.4742 | 7.3421e-08 | 2.5109e-05 | 104.9807
2006-01-30 03:10 | 52.7585 | 89.8866 | 0.86563 | 480 | 0 | 50 | 3 | 1 | 9 | 17.5862 | 0.88227 | 111.564 | 110.2416 | 1.012 | 267.7537 | 6551.5977 | 95271.5156 | 0 | 0.020758 | 0.020106 | 3.4714 | 1.0017e-07 | 3.4386e-05 | 105.0808
2006-01-31 03:33 | 56.3353 | 88.5601 | 0.91055 | 480 | 0 | 50 | 3 | 1 | 11 | 18.7784 | 0.87683 | 132.3 | 130.3169 | 1.0152 | 317.5201 | 7739.5518 | 95594 | 0 | 0.02076 | 0.020102 | 3.4724 | 1.0471e-07 | 3.6084e-05 | 105.1855
2006-02-01 04:00 | 52.0141 | 89.8401 | 1.0108 | 480 | 0 | 50 | 3 | 1 | 9 | 17.338 | 0.87137 | 112.644 | 110.7312 | 1.0173 | 270.3457 | 6615.0215 | 95869.625 | 0 | 0.020766 | 0.0201 | 3.4808 | 1.1446e-07 | 3.9291e-05 | 105.3
2006-02-02 00:21 | 55.2234 | 87.1469 | 0.51685 | 480 | 0 | 50 | 4 | 1 | 10 | 13.8058 | 0.86682 | 152.9279 | 151.1284 | 1.0119 | 367.0271 | 7466.707 | 96180.7344 | 0 | 0.020197 | 0.014691 | 3.4767 | 4.9114e-08 | 2.0279e-05 | 105.3491
2006-02-03 01:00 | 60.0874 | 91.2623 | 0.28942 | 480 | 0 | 50 | 3 | 1 | 9 | 20.0291 | 0.86132 | 109.836 | 109.0233 | 1.0075 | 263.6065 | 6499.5474 | 96451.5469 | 0 | 0.020192 | 0.019567 | 3.4771 | 3.3302e-08 | 1.1346e-05 | 105.3824
2006-02-04 01:27 | 54.6438 | 90.0997 | 0.42192 | 480 | 0 | 50 | 3 | 1 | 9 | 18.2146 | 0.85588 | 115.668 | 114.9734 | 1.006 | 277.6032 | 6766.5776 | 96733.4844 | 0 | 0.020822 | 0.020181 | 3.4756 | 4.8156e-08 | 1.6595e-05 | 105.4306
2006-02-05 02:04 | 55.9378 | 89.4685 | 0.72615 | 480 | 0 | 50 | 3 | 1 | 10 | 18.646 | 0.85038 | 125.712 | 124.2655 | 1.0116 | 301.7089 | 7439.0098 | 97043.4453 | 0 | 0.020812 | 0.020216 | 3.4741 | 8.4131e-08 | 2.8662e-05 | 105.5147
2006-02-06 02:39 | 56.1849 | 90.2204 | 0.65058 | 480 | 0 | 50 | 3 | 1 | 9 | 18.7283 | 0.99489 | 101.088 | 100.3191 | 1.0077 | 242.6111 | 5959.1357 | 97291.7422 | 0 | 0.020809 | 0.020233 | 3.4773 | 7.4538e-08 | 2.549e-05 | 105.5892
2006-02-07 03:10 | 51.0724 | 89.2165 | 0.78269 | 480 | 0 | 50 | 3 | 1 | 9 | 17.0241 | 0.98941 | 104.004 | 103.1641 | 1.0081 | 249.6096 | 6131.0352 | 97547.2031 | 0 | 0.020779 | 0.020194 | 3.4778 | 8.9569e-08 | 3.0631e-05 | 105.6788
2006-02-08 03:35 | 59.8027 | 91.5329 | 0.77443 | 480 | 0 | 50 | 2 | 1 | 11 | 29.9013 | 0.98397 | 88.884 | 87.7931 | 1.0124 | 213.3217 | 5199.7158 | 97763.8594 | 0 | 0 | 0 | 3.4717 | 8.9197e-08 | 3.0738e-05 | 105.768
2006-02-09 00:05 | 55.622 | 91.3378 | 0.73346 | 480 | 0 | 50 | 2 | 1 | 11 | 27.811 | 0.97939 | 84.456 | 84.0989 | 1.0042 | 202.6944 | 4161.5698 | 97937.2578 | 0 | 0 | 0 | 3.4714 | 7.1203e-08 | 2.9131e-05 | 105.8392
2006-02-10 00:39 | 47.0172 | 90.9572 | 0.74994 | 480 | 0 | 50 | 2 | 1 | 10 | 23.5086 | 0.9739 | 78.3 | 77.3237 | 1.0126 | 187.92 | 4615.7852 | 98129.5859 | 0 | 0 | 0 | 3.4716 | 8.707e-08 | 2.9776e-05 | 105.9263
2006-02-11 01:13 | 53.4956 | 89.9632 | 0.8071 | 480 | 0 | 50 | 3 | 1 | 9 | 17.8319 | 0.96842 | 102.816 | 101.3047 | 1.0149 | 246.7583 | 6061.002 | 98382.125 | 0 | 0 | 0 | 3.4728 | 9.3443e-08 | 3.1956e-05 | 106.0197
2006-02-12 01:35 | 61.3386 | 91.4044 | 1.2051 | 480 | 0 | 50 | 3 | 1 | 8 | 20.4462 | 0.96298 | 101.952 | 100.6276 | 1.0132 | 244.6849 | 5964.1934 | 98630.6328 | 0 | 0 | 0 | 3.4835 | 1.3508e-07 | 4.6549e-05 | 106.1548
2006-02-13 02:10 | 56.6066 | 90.5836 | 0.75365 | 480 | 0 | 50 | 3 | 1 | 9 | 18.8689 | 0.9575 | 101.088 | 100.7308 | 1.0035 | 242.6111 | 5959.1357 | 98878.9297 | 0 | 0 | 0 | 3.473 | 8.7205e-08 | 2.9822e-05 | 106.242
2006-02-14 02:35 | 45.8145 | 91.0598 | 0.75334 | 480 | 0 | 50 | 2 | 1 | 10 | 22.9072 | 0.95204 | 77.328 | 76.1946 | 1.0149 | 185.5872 | 4541.0869 | 99068.1406 | 0 | 0 | 0 | 3.4728 | 8.6872e-08 | 2.9822e-05 | 106.3289
2006-02-15 03:03 | 44.6204 | 91.5635 | 0.89583 | 480 | 0 | 50 | 2 | 1 | 9 | 22.3102 | 0.94658 | 73.656 | 72.0057 | 1.0229 | 176.7744 | 4325.4487 | 99248.3672 | 0 | 0 | 0 | 3.4768 | 1.0237e-07 | 3.5144e-05 | 106.4313
2006-02-16 03:30 | 62.5463 | 90.2361 | 0.66185 | 480 | 0 | 50 | 3 | 1 | 10 | 20.8488 | 0.94113 | 116.964 | 115.0491 | 1.0166 | 280.7135 | 6842.3921 | 99533.4688 | 0 | 0 | 0 | 3.4753 | 7.5595e-08 | 2.6051e-05 | 106.5068
2006-02-17 00:09 | 59.8127 | 91.6402 | 0.80902 | 480 | 0 | 50 | 2 | 1 | 11 | 29.9064 | 0.93651 | 93.096 | 91.2505 | 1.0202 | 223.4304 | 4629.1982 | 99726.3516 | 0 | 0 | 0 | 3.4712 | 7.9289e-08 | 3.2146e-05 | 106.5861
2006-02-18 00:31 | 54.9763 | 92.1149 | 1.0324 | 480 | 0 | 50 | 2 | 1 | 10 | 27.4881 | 0.93107 | 83.592 | 81.916 | 1.0205 | 200.6208 | 4890.1328 | 99930.1094 | 0 | 0 | 0 | 3.4755 | 1.1787e-07 | 4.0621e-05 | 106.704
2006-02-19 01:03 | 64.99 | 91.2202 | 0.52555 | 480 | 0 | 50 | 3 | 1 | 9 | 21.6633 | 0.92561 | 112.644 | 110.8058 | 1.0166 | 270.3457 | 6615.0215 | 100205.7344 | 0 | 0 | 0 | 3.4802 | 5.959e-08 | 2.0457e-05 | 106.7636
2006-02-20 01:31 | 48.8817 | 89.4834 | 1.0716 | 480 | 0 | 50 | 3 | 1 | 9 | 16.2939 | 0.92015 | 104.004 | 103.3069 | 1.0067 | 249.6096 | 6107.6343 | 100460.2188 | 0 | 0 | 0 | 3.4764 | 1.2258e-07 | 4.2079e-05 | 106.8862
2006-02-21 01:55 | 46.8211 | 89.825 | 0.82689 | 480 | 0 | 50 | 2 | 1 | 11 | 23.4106 | 0.9147 | 93.204 | 91.3592 | 1.0202 | 223.6896 | 5452.4336 | 100687.4062 | 0 | 0 | 0 | 3.4734 | 9.4873e-08 | 3.2694e-05 | 106.981
2006-02-22 02:17 | 52.0678 | 92.7948 | 0.8154 | 480 | 0 | 50 | 2 | 1 | 9 | 26.0339 | 0.90926 | 75.816 | 74.7043 | 1.0149 | 181.9584 | 4435.2363 | 100872.2109 | 0 | 0 | 0 | 3.4846 | 9.1164e-08 | 3.1416e-05 | 107.0722
2006-02-23 01:36 | 56.3605 | 91.364 | 1.1897 | 480 | 0 | 50 | 2 | 1 | 11 | 28.1803 | 0.90405 | 93.528 | 92.3883 | 1.0123 | 224.4672 | 5239.9062 | 101090.5391 | 0 | 0 | 0 | 3.4765 | 1.2978e-07 | 4.6699e-05 | 107.202
2006-02-24 02:12 | 58.5591 | 90.6325 | 0.91686 | 480 | 0 | 50 | 3 | 1 | 9 | 19.5197 | 0.89857 | 112.644 | 110.6894 | 1.0177 | 270.3457 | 6640.3662 | 101367.2188 | 0 | 0 | 0 | 3.4813 | 1.0409e-07 | 3.5598e-05 | 107.3061
2006-02-25 02:55 | 51.3851 | 92.3847 | 1.2179 | 480 | 0 | 50 | 2 | 1 | 10 | 25.6926 | 0.89305 | 77.544 | 77.2276 | 1.0041 | 186.1056 | 4606.1138 | 101559.1406 | 0 | 0 | 0 | 3.4719 | 1.4237e-07 | 4.8318e-05 | 107.4485
2006-02-26 03:24 | 47.3428 | 90.2999 | 1.1174 | 480 | 0 | 50 | 2 | 1 | 11 | 23.6714 | 0.88758 | 91.152 | 90.1241 | 1.0114 | 218.7648 | 5352.9014 | 101782.1797 | 0 | 0 | 0 | 3.4746 | 1.2834e-07 | 4.4056e-05 | 107.5768
2006-02-27 03:44 | 58.367 | 91.4352 | 1.025 | 480 | 0 | 50 | 3 | 1 | 9 | 19.4557 | 0.88214 | 103.896 | 101.8564 | 1.02 | 249.3504 | 6077.9155 | 102035.4297 | 0 | 0 | 0 | 3.4829 | 1.1505e-07 | 3.9646e-05 | 107.6918
2006-02-28 00:05 | 53.694 | 91.8405 | 0.71716 | 480 | 0 | 50 | 2 | 1 | 11 | 26.847 | 0.8776 | 86.616 | 85.4947 | 1.0131 | 207.8784 | 4229.0264 | 102211.6406 | 0 | 0 | 0 | 3.4718 | 6.8927e-08 | 2.846e-05 | 107.7608
2006-02-28 04:13 | 63.6871 | 91.7766 | 1.0734 | 480 | 0 | 50 | 3 | 1 | 9 | 21.229 | 0.87668 | 108.648 | 107.1409 | 1.0141 | 260.7552 | 1075.6152 | 102256.4609 | 0 | 0 | 0 | 3.4728 | 2.0867e-08 | 4.2492e-05 | 107.7816
2006-03-01 00:31 | 52.8632 | 91.7728 | 0.61294 | 480 | 0 | 50 | 2 | 1 | 11 | 26.4316 | 0.87214 | 86.616 | 85.4566 | 1.0136 | 207.8784 | 4229.0264 | 102432.6719 | 0 | 0 | 0 | 3.4725 | 5.8821e-08 | 2.4287e-05 | 107.8405
2006-03-01 04:35 | 55.922 | 91.152 | 0.48111 | 480 | 0 | 50 | 3 | 1 | 9 | 18.6407 | 0.87124 | 104.004 | 102.4307 | 1.0154 | 249.6096 | 1006.2386 | 102474.6016 | 0 | 0 | 0 | 3.4853 | 8.8827e-09 | 1.8509e-05 | 107.8493
2006-03-02 01:08 | 50.9499 | 90.3924 | 0.58077 | 480 | 0 | 50 | 3 | 1 | 9 | 16.9833 | 0.86666 | 104.004 | 102.9616 | 1.0101 | 249.6096 | 5124.7964 | 102688.1328 | 0 | 0 | 0 | 3.4799 | 5.529e-08 | 2.2621e-05 | 107.9046
2006-03-03 01:54 | 58.4886 | 90.7107 | 0.3676 | 480 | 0 | 50 | 3 | 1 | 9 | 19.4962 | 0.86113 | 115.668 | 114.5007 | 1.0102 | 277.6032 | 6870.6787 | 102974.4141 | 0 | 0 | 0 | 3.48 | 4.2179e-08 | 1.4315e-05 | 107.9468
2006-03-04 02:22 | 45.2373 | 91.761 | 0.4167 | 480 | 0 | 50 | 2 | 1 | 10 | 22.6187 | 0.85567 | 77.544 | 77.0603 | 1.0063 | 186.1056 | 4553.7715 | 103164.1562 | 0 | 0 | 0 | 3.4741 | 4.7916e-08 | 1.6449e-05 | 107.9947
2006-03-05 02:50 | 65.5489 | 91.2398 | 0.34857 | 480 | 0 | 50 | 3 | 1 | 10 | 21.8496 | 0.85021 | 120.204 | 118.6108 | 1.0134 | 288.4896 | 7058.9805 | 103458.2812 | 0 | 0 | 0 | 3.472 | 4.0277e-08 | 1.3827e-05 | 108.035
2006-03-06 03:23 | 47.7092 | 91.4838 | 0.52018 | 480 | 0 | 50 | 2 | 1 | 9 | 23.8546 | 0.99473 | 75.816 | 74.4219 | 1.0187 | 181.9584 | 4469.3535 | 103644.5078 | 0 | 0 | 0 | 3.4886 | 5.8074e-08 | 1.986e-05 | 108.0931
2006-03-07 03:47 | 48.2151 | 90.0443 | 0.59462 | 480 | 0 | 50 | 2 | 1 | 11 | 24.1075 | 0.98929 | 86.4 | 85.1003 | 1.0153 | 207.36 | 5054.3999 | 103855.1094 | 0 | 0 | 0 | 3.4728 | 6.8313e-08 | 2.3541e-05 | 108.1614
2006-03-08 00:06 | 46.4452 | 91.0055 | 0.32737 | 480 | 0 | 50 | 2 | 1 | 10 | 23.2226 | 0.98474 | 77.112 | 75.6591 | 1.0192 | 185.0688 | 3764.9934 | 104011.9844 | 0 | 0 | 0 | 3.4721 | 3.1444e-08 | 1.2983e-05 | 108.1928
2006-03-09 00:39 | 51.5582 | 90.9896 | 0.46857 | 480 | 0 | 50 | 2 | 1 | 10 | 25.7791 | 0.97926 | 85.968 | 84.6494 | 1.0156 | 206.3232 | 5067.814 | 104223.1406 | 0 | 0 | 0 | 3.4804 | 5.331e-08 | 1.8231e-05 | 108.2461
2006-03-10 01:01 | 58.2941 | 90.4482 | 0.74952 | 480 | 0 | 50 | 3 | 1 | 9 | 19.4314 | 0.97382 | 105.732 | 104.3427 | 1.0133 | 253.7568 | 6185.3208 | 104480.8594 | 0 | 0 | 0 | 3.4715 | 8.6373e-08 | 2.9765e-05 | 108.3325
2006-03-11 01:32 | 51.8982 | 91.4247 | 1.2676 | 480 | 0 | 50 | 2 | 1 | 10 | 25.9491 | 0.96836 | 83.376 | 81.6772 | 1.0208 | 200.1024 | 4896.2559 | 104684.8672 | 0 | 0 | 0 | 3.4714 | 1.4667e-07 | 5.035e-05 | 108.4792
2006-03-12 02:10 | 65.5019 | 90.7929 | 1.1491 | 480 | 0 | 50 | 3 | 1 | 9 | 21.834 | 0.96286 | 115.56 | 113.784 | 1.0156 | 277.344 | 6838.2622 | 104969.7969 | 0 | 0 | 0 | 3.4794 | 1.3152e-07 | 4.4806e-05 | 108.6107
2006-03-13 02:42 | 64.2745 | 90.8361 | 1.3054 | 480 | 0 | 50 | 3 | 1 | 9 | 21.4248 | 0.95737 | 112.752 | 111.7358 | 1.0091 | 270.6049 | 6646.7334 | 105246.7422 | 0 | 0 | 0 | 3.4789 | 1.4903e-07 | 5.0966e-05 | 108.7597
2006-03-14 03:16 | 57.1202 | 90.4937 | 1.2402 | 480 | 0 | 50 | 3 | 1 | 9 | 19.0401 | 0.95189 | 105.732 | 104.1479 | 1.0152 | 253.7568 | 6232.9004 | 105506.4453 | 0 | 0 | 0 | 3.4734 | 1.4338e-07 | 4.9032e-05 | 108.9031
2006-03-15 03:43 | 52.8273 | 90.6842 | 1.4968 | 480 | 0 | 50 | 2 | 1 | 11 | 26.4136 | 0.94643 | 91.152 | 90.4473 | 1.0078 | 218.7648 | 5352.9014 | 105729.4844 | 0 | 0 | 0 | 3.4723 | 1.7284e-07 | 5.9333e-05 | 109.076
2006-03-16 00:16 | 55.6394 | 92.1151 | 1.9339 | 480 | 0 | 50 | 2 | 1 | 10 | 27.8197 | 0.94185 | 83.808 | 82.559 | 1.0151 | 201.1392 | 4129.6396 | 105901.5547 | 0 | 0 | 0 | 3.4793 | 1.8436e-07 | 7.5426e-05 | 109.2603
2006-03-17 03:54 | 60.3751 | 92.3827 | 1.37 | 480 | 0 | 50 | 3 | 1 | 8 | 20.125 | 0.93567 | 92.448 | 90.7024 | 1.0192 | 221.8752 | 6136.2358 | 106157.2344 | 0 | 0 | 0 | 3.49 | 1.7163e-07 | 5.2129e-05 | 109.4319
2006-03-18 00:12 | 45.4084 | 90.5153 | 1.3731 | 480 | 0 | 50 | 2 | 1 | 10 | 22.7042 | 0.93115 | 83.916 | 83.2771 | 1.0077 | 201.3984 | 4078.3181 | 106327.1641 | 0 | 0 | 0 | 3.4735 | 1.3086e-07 | 5.4281e-05 | 109.5628
2006-03-19 00:45 | 51.5744 | 90.7688 | 0.91668 | 480 | 0 | 50 | 2 | 1 | 11 | 25.7872 | 0.92567 | 90.936 | 89.452 | 1.0166 | 218.2464 | 5360.6777 | 106550.5234 | 0 | 0 | 0 | 3.4711 | 1.0653e-07 | 3.6432e-05 | 109.6693
2006-03-20 01:24 | 47.487 | 90.6333 | 1.1461 | 480 | 0 | 50 | 2 | 1 | 11 | 23.7435 | 0.92017 | 86.076 | 84.2624 | 1.0215 | 206.5824 | 5093.5474 | 106762.7578 | 0 | 0 | 0 | 3.4738 | 1.3289e-07 | 4.5273e-05 | 109.8022
2006-03-21 01:55 | 47.7721 | 89.2514 | 0.8657 | 480 | 0 | 50 | 3 | 1 | 9 | 15.924 | 0.9147 | 106.812 | 105.0834 | 1.0164 | 256.3488 | 6272.5342 | 107024.1172 | 0 | 0 | 0 | 3.4796 | 9.8279e-08 | 3.3738e-05 | 109.9005
2006-03-22 02:27 | 55.9444 | 89.7317 | 1.1085 | 480 | 0 | 50 | 3 | 1 | 10 | 18.6481 | 0.90922 | 115.128 | 114.0149 | 1.0098 | 276.3072 | 6786.7954 | 107306.8984 | 0 | 0 | 0 | 3.4752 | 1.2763e-07 | 4.3648e-05 | 110.0281
2006-03-23 03:14 | 59.4373 | 90.2165 | 1.0277 | 480 | 0 | 50 | 3 | 1 | 10 | 19.8124 | 0.9037 | 116.964 | 115.1269 | 1.016 | 280.7135 | 6947.6597 | 107596.3828 | 0 | 0 | 0 | 3.4741 | 1.1953e-07 | 4.0568e-05 | 110.1477
2006-03-24 03:55 | 53.0473 | 90.4457 | 1.0718 | 480 | 0 | 50 | 3 | 1 | 9 | 17.6824 | 0.89817 | 104.004 | 103.3596 | 1.0062 | 249.6096 | 6177.8369 | 107853.7891 | 0 | 0 | 0 | 3.4759 | 1.2414e-07 | 4.213e-05 | 110.2718
2006-03-25 03:25 | 55.8079 | 91.3523 | 1.0118 | 480 | 0 | 50 | 3 | 1 | 8 | 18.6026 | 0.89294 | 101.952 | 100.4503 | 1.015 | 244.6849 | 5734.8013 | 108092.7422 | 0 | 0 | 0 | 3.4854 | 1.0857e-07 | 3.8909e-05 | 110.3804
2006-03-26 03:54 | 51.5696 | 90.3673 | 0.98701 | 385.2 | 0.26333 | 50 | 3 | 1 | 9 | 17.1899 | 0.88746 | 104.004 | 102.7173 | 1.0125 | 249.6096 | 6131.0352 | 108348.2031 | 0.0061069 | 0.020782 | 0.020615 | 2.1915 | 2.1838e-06 | 0.00074655 | 112.5642
2006-03-27 00:20 | 52.5915 | 90.6764 | 2.5463 | 480 | 0 | 50 | 3 | 1 | 9 | 17.5305 | 0.8829 | 102.924 | 101.4612 | 1.0144 | 247.0175 | 5048.4209 | 108558.5547 | 0 | 0.02021 | 0.020069 | 3.478 | 2.4235e-07 | 9.9601e-05 | 112.8065
2006-03-28 00:51 | 49.8961 | 91.3241 | 1.584 | 480 | 0 | 50 | 2 | 1 | 11 | 24.9481 | 0.87743 | 86.508 | 85.4481 | 1.0124 | 207.6192 | 5080.1821 | 108770.2266 | 0 | 0.020217 | 0.020122 | 3.4723 | 1.8288e-07 | 6.2779e-05 | 112.9894
2006-03-29 01:25 | 48.5459 | 90.0095 | 1.6596 | 480 | 0 | 50 | 3 | 1 | 9 | 16.182 | 0.87195 | 104.004 | 102.782 | 1.0119 | 249.6096 | 6131.0352 | 109025.6875 | 0 | 0.020215 | 0.020122 | 3.4817 | 1.8823e-07 | 6.4369e-05 | 113.1776
2006-03-30 02:00 | 55.9251 | 90.1152 | 1.6306 | 480 | 0 | 50 | 3 | 1 | 10 | 18.6417 | 0.86647 | 115.884 | 114.564 | 1.0115 | 278.1216 | 6831.3613 | 109310.3281 | 0 | 0.020779 | 0.020714 | 3.471 | 1.8955e-07 | 6.4821e-05 | 113.3672
2006-03-31 02:55 | 54.7624 | 90.5197 | 1.8561 | 0 | 15.924 | 50 | 3 | 1 | 9 | 18.2541 | 0.8609 | 111.78 | 110.552 | 1.0111 | 268.2721 | 6690.0347 | 109589.0781 | 0.006015 | 0.041531 | 0.042118 | 2.1977 | 4.1108e-06 | 0.0013837 | 117.478
2006-04-01 03:30 | 53.9628 | 89.9544 | 2.0506 | 480 | 0 | 50 | 3 | 1 | 10 | 17.9876 | 0.85542 | 115.128 | 114.1977 | 1.0081 | 276.3072 | 6786.7954 | 109871.8594 | 0 | 0.041531 | 0.042098 | 3.4739 | 2.3678e-07 | 8.0972e-05 | 117.7147
2006-04-02 00:02 | 62.9275 | 91.1609 | 1.2711 | 480 | 0 | 50 | 3 | 1 | 10 | 20.9758 | 0.85084 | 117.936 | 115.729 | 1.0191 | 283.0464 | 5811.2959 | 110114 | 0 | 0.040384 | 0.040837 | 3.4768 | 1.2188e-07 | 4.9863e-05 | 117.8366
2006-04-03 00:41 | 41.6245 | 89.5251 | 1.0845 | 480 | 0 | 50 | 2 | 1 | 10 | 20.8122 | 0.99533 | 81.648 | 80.6478 | 1.0124 | 195.9552 | 4831.521 | 110315.3125 | 0 | 0.040389 | 0.040903 | 3.4757 | 1.2518e-07 | 4.2646e-05 | 117.9618
2006-04-04 01:06 | 51.1176 | 91.35 | 1.7688 | 480 | 0 | 50 | 2 | 1 | 10 | 25.5588 | 0.98987 | 81.432 | 79.9559 | 1.0185 | 195.4368 | 4782.0947 | 110514.5703 | 0 | 0.040389 | 0.041041 | 3.4723 | 2.0423e-07 | 7.0108e-05 | 118.166
2006-04-05 02:30 | 54.3464 | 90.9267 | 0.79265 | 480 | 0 | 50 | 2 | 1 | 11 | 27.1732 | 0.9842 | 88.776 | 87.3449 | 1.0164 | 213.0625 | 5413.1182 | 110740.1172 | 0 | 0.040338 | 0.041057 | 3.4801 | 9.3336e-08 | 3.0859e-05 | 118.2594
2006-04-06 03:17 | 55.0598 | 89.0216 | 1.1358 | 480 | 0 | 50 | 3 | 1 | 10 | 18.3533 | 0.97868 | 115.128 | 113.6178 | 1.0133 | 276.3072 | 6838.603 | 111025.0625 | 0 | 0.040328 | 0.041096 | 3.4792 | 1.3057e-07 | 4.4312e-05 | 118.3899
2006-04-07 03:49 | 48.6013 | 90.6126 | 1.029 | 480 | 0 | 50 | 2 | 1 | 10 | 24.3006 | 0.97319 | 85.968 | 84.7468 | 1.0144 | 206.3232 | 5067.814 | 111236.2188 | 0 | 0.041451 | 0.042002 | 3.4799 | 1.1721e-07 | 4.0084e-05 | 118.5071
2006-04-08 00:19 | 48.4775 | 91.9964 | 0.764 | 480 | 0 | 50 | 2 | 1 | 9 | 24.2388 | 0.96863 | 73.872 | 73.4154 | 1.0062 | 177.2928 | 3623.4224 | 111387.1953 | 0 | 0.040312 | 0.040959 | 3.4758 | 7.3095e-08 | 3.0042e-05 | 118.5802
2006-04-09 01:12 | 53.1228 | 88.7246 | 0.50506 | 480 | 0 | 50 | 3 | 1 | 10 | 17.7076 | 0.96307 | 116.964 | 115.2867 | 1.0145 | 280.7135 | 7000.2935 | 111678.875 | 0 | 0.041656 | 0.04231 | 3.4725 | 5.94e-08 | 2.0008e-05 | 118.6396
2006-04-10 01:59 | 55.0265 | 89.9298 | 0.59453 | 480 | 0 | 50 | 3 | 1 | 9 | 18.3422 | 0.95754 | 108.864 | 107.4193 | 1.0134 | 261.2737 | 6466.5229 | 111948.3125 | 0 | 0.04164 | 0.042321 | 3.4831 | 6.7736e-08 | 2.2989e-05 | 118.7074
2006-04-11 02:26 | 43.0337 | 88.7991 | 0.92868 | 480 | 0 | 50 | 2 | 1 | 11 | 21.5168 | 0.95208 | 93.528 | 91.9953 | 1.0167 | 224.4672 | 5492.4321 | 112177.1641 | 0 | 0.04165 | 0.042594 | 3.4823 | 1.0478e-07 | 3.5971e-05 | 118.8122
2006-04-12 02:50 | 48.6681 | 91.4709 | 0.91376 | 480 | 0 | 50 | 2 | 1 | 10 | 24.3341 | 0.94664 | 79.488 | 78.574 | 1.0116 | 190.7712 | 4650.0474 | 112370.9141 | 0 | 0.041661 | 0.043129 | 3.4731 | 1.0491e-07 | 3.6152e-05 | 118.9171
2006-04-13 03:12 | 54.4902 | 90.0957 | 0.92076 | 480 | 0 | 50 | 3 | 1 | 9 | 18.1634 | 0.9412 | 106.92 | 106.1862 | 1.0069 | 256.608 | 6254.8198 | 112631.5312 | 0 | 0.040297 | 0.041745 | 3.4766 | 1.0486e-07 | 3.6135e-05 | 119.0219
2006-04-14 03:35 | 47.5187 | 89.031 | 0.77988 | 480 | 0 | 50 | 3 | 1 | 9 | 15.8396 | 0.93576 | 106.92 | 105.4519 | 1.0139 | 256.608 | 6254.8198 | 112892.1484 | 0 | 0.040307 | 0.04201 | 3.4838 | 8.735e-08 | 3.0102e-05 | 119.1093
2006-04-15 04:04 | 59.2985 | 89.0773 | 0.79776 | 480 | 0 | 50 | 3 | 1 | 11 | 19.7662 | 0.93029 | 125.388 | 124.2195 | 1.0094 | 300.9312 | 7363.4097 | 113198.9609 | 0 | 0.041451 | 0.043291 | 3.4741 | 9.1736e-08 | 3.1492e-05 | 119.201
2006-04-16 01:32 | 59.779 | 87.9795 | 0.68982 | 480 | 0 | 50 | 4 | 1 | 9 | 14.9448 | 0.9255 | 147.744 | 145.9253 | 1.0125 | 354.5856 | 7612.5098 | 113516.1484 | 0 | 0.040257 | 0.031406 | 3.4823 | 6.8288e-08 | 2.6719e-05 | 119.2693
2006-04-17 02:13 | 53.3178 | 90.782 | 1.1285 | 480 | 0 | 50 | 3 | 1 | 8 | 17.7726 | 0.91998 | 101.952 | 100.5469 | 1.014 | 244.6849 | 6055.9502 | 113768.4766 | 0 | 0.041548 | 0.043288 | 3.4845 | 1.2815e-07 | 4.3494e-05 | 119.3974
2006-04-18 02:35 | 52.7251 | 89.6814 | 1.5178 | 480 | 0 | 50 | 3 | 1 | 9 | 17.575 | 0.91454 | 112.644 | 111.1906 | 1.0131 | 270.3457 | 6589.6768 | 114043.0469 | 0 | 0.041558 | 0.043172 | 3.4768 | 1.7278e-07 | 5.9539e-05 | 119.5702
2006-04-19 02:57 | 52.9585 | 88.0534 | 0.93385 | 480 | 0 | 50 | 3 | 1 | 11 | 17.6528 | 0.90912 | 128.844 | 127.4581 | 1.0109 | 309.2256 | 7508.3843 | 114355.8984 | 0 | 0.04158 | 0.043102 | 3.4749 | 1.0636e-07 | 3.6794e-05 | 119.6766
2006-04-20 03:30 | 48.9101 | 89.4866 | 1.0515 | 480 | 0 | 50 | 3 | 1 | 9 | 16.3034 | 0.90363 | 108.648 | 106.8485 | 1.0168 | 260.7552 | 6404.8003 | 114622.7656 | 0 | 0.041575 | 0.043005 | 3.4756 | 1.2095e-07 | 4.1363e-05 | 119.7975
2006-04-21 04:03 | 65.5805 | 87.7332 | 0.89942 | 480 | 0 | 50 | 4 | 1 | 11 | 16.3951 | 0.89815 | 162.0001 | 160.284 | 1.0107 | 388.8001 | 9549.9033 | 115020.6797 | 0 | 0.041575 | 0.032142 | 3.4764 | 1.0327e-07 | 3.5315e-05 | 119.9008
2006-04-22 00:39 | 52.7486 | 89.0315 | 0.81707 | 480 | 0 | 50 | 3 | 1 | 10 | 17.5829 | 0.89355 | 121.284 | 119.5745 | 1.0143 | 291.0817 | 6003.5596 | 115270.8281 | 0 | 0.040419 | 0.041528 | 3.474 | 7.9211e-08 | 3.226e-05 | 119.98
2006-04-23 01:42 | 50.7799 | 88.6812 | 0.7744 | 480 | 0 | 50 | 3 | 1 | 10 | 16.9266 | 0.88796 | 121.608 | 120.5627 | 1.0087 | 291.8593 | 7305.6025 | 115575.2266 | 0 | 0.040404 | 0.041668 | 3.4757 | 9.0757e-08 | 3.0456e-05 | 120.0708
2006-04-24 02:07 | 59.6403 | 88.3996 | 1.2354 | 480 | 0 | 50 | 4 | 1 | 9 | 14.9101 | 0.8825 | 147.744 | 146.0854 | 1.0114 | 354.5856 | 8676.2666 | 115936.7344 | 0 | 0.040419 | 0.031284 | 3.4812 | 1.3976e-07 | 4.7978e-05 | 120.2105
2006-04-25 02:25 | 65.4635 | 88.8655 | 0.91096 | 480 | 0 | 50 | 4 | 1 | 10 | 16.3659 | 0.87708 | 151.632 | 149.1917 | 1.0164 | 363.9167 | 8836.3525 | 116304.9141 | 0 | 0.040373 | 0.031091 | 3.4789 | 1.0281e-07 | 3.5565e-05 | 120.3133
2006-04-26 02:48 | 61.7311 | 87.2701 | 0.95337 | 480 | 0 | 50 | 4 | 1 | 11 | 15.4328 | 0.87164 | 165.996 | 163.7167 | 1.0139 | 398.3903 | 9710.7637 | 116709.5312 | 0 | 0.020763 | 0.016122 | 3.4741 | 1.092e-07 | 3.7633e-05 | 120.4225
2006-04-27 02:24 | 25.9087 | 91.4232 | 0.71616 | 480 | 0 | 50 | 1 | 1 | 11 | 25.9087 | 0.86636 | 45.576 | 44.7445 | 1.0186 | 109.3824 | 2584.1592 | 116817.2031 | 0 | 0.020787 | 0.021618 | 3.4839 | 7.7738e-08 | 2.764e-05 | 120.5003
2006-04-28 03:00 | 35.206 | 89.6302 | 0.65452 | 480 | 0 | 50 | 2 | 1 | 10 | 17.603 | 0.86088 | 79.488 | 78.4042 | 1.0138 | 190.7712 | 4685.8169 | 117012.4453 | 0 | 0.020787 | 0.021879 | 3.476 | 7.5221e-08 | 2.5724e-05 | 120.5755
2006-04-29 03:26 | 50.6361 | 88.5529 | 0.56235 | 480 | 0 | 50 | 3 | 1 | 10 | 16.8787 | 0.85542 | 127.98 | 126.7893 | 1.0094 | 307.152 | 7515.625 | 117325.5938 | 0 | 0.02079 | 0.022014 | 3.4767 | 6.4279e-08 | 2.2066e-05 | 120.6398
2006-04-30 03:44 | 55.0596 | 90.607 | 1.725 | 480 | 0 | 50 | 2 | 1 | 11 | 27.5298 | 1 | 92.34 | 91.1277 | 1.0133 | 221.616 | 5381.1133 | 117549.8047 | 0 | 0 | 0 | 3.4711 | 1.9819e-07 | 6.856e-05 | 120.838
2006-05-01 00:14 | 67.911 | 90.7556 | 0.89034 | 480 | 0 | 50 | 3 | 1 | 10 | 22.637 | 0.99544 | 114.804 | 113.028 | 1.0157 | 275.5296 | 5631.1362 | 117784.4375 | 0 | 0 | 0 | 3.4726 | 8.5803e-08 | 3.5265e-05 | 120.9238
2006-05-02 00:30 | 58.273 | 87.7038 | 0.43704 | 480 | 0 | 50 | 3 | 1 | 11 | 19.4243 | 0.99002 | 135.648 | 134.2644 | 1.0103 | 325.5553 | 7904.8887 | 118113.8047 | 0 | 0 | 0 | 3.476 | 4.9651e-08 | 1.7177e-05 | 120.9734 |  |  | 240
2006-05-03 00:53 | 59.2137 | 88.6441 | 0.99644 | 480 | 0 | 50 | 3 | 1 | 11 | 19.7379 | 0.98458 | 125.28 | 123.6937 | 1.0128 | 300.672 | 7328.8799 | 118419.1719 | 0 | 0 | 0 | 3.4756 | 1.1375e-07 | 3.92e-05 | 121.0872 |  |  | -114.6018
2006-05-04 01:25 | 54.8142 | 88.8448 | 0.88074 | 480 | 0 | 50 | 3 | 1 | 10 | 18.2714 | 0.97909 | 118.044 | 116.1967 | 1.0159 | 283.3056 | 6958.6934 | 118709.1172 | 0 | 0 | 0 | 3.4738 | 1.0174e-07 | 3.4793e-05 | 121.1889 |  |  | -0.47751
2006-05-05 01:52 | 51.7564 | 88.1582 | 1.7625 | 89.8 | 0.67667 | 50 | 3 | 1 | 10 | 17.2521 | 0.97363 | 121.284 | 119.1675 | 1.0178 | 291.0817 | 7122.4043 | 119005.8828 | 0.0061303 | 0.020141 | 0.020195 | 2.1896 | 3.9014e-06 | 0.0013384 | 125.0903
2006-05-06 02:14 | 61.7397 | 88.3429 | 1.5541 | 480 | 0 | 50 | 3 | 1 | 11 | 20.5799 | 0.96819 | 137.7 | 135.7675 | 1.0142 | 330.4801 | 8055.4517 | 119341.5234 | 0 | 0.020169 | 0.020172 | 3.4723 | 1.7874e-07 | 6.1594e-05 | 125.2691
2006-05-07 02:36 | 76.2663 | 89.0308 | 1.1233 | 480 | 0 | 50 | 4 | 1 | 10 | 19.0666 | 0.96275 | 157.14 | 155.8542 | 1.0082 | 377.136 | 9192.6904 | 119724.5547 | 0 | 0.020179 | 0.015005 | 3.4726 | 1.2912e-07 | 4.4496e-05 | 125.3982 |  | 426.9507 | 1.072
Note on C14: Example. Enter 95% as "95" as opposed to "0.95"

## REDMODEL
UV SYSTEM SENSOR AND DOSE MODEL
Product ID | Model ID | Location | Drinking Water - MP - Case 1 |  |  | Drinking Water - MP - Case 2 |  |  | Drinking Water - LPHO - Full Pacing - Case 3 |  |  | Drinking Water - LPHO - Flow and UVT Pacing - Case 3 |  |  | Drinking Water - LPHO - Flow Pacing - Case 3 |  |  | Drinking Water - LPHO - No Dose Pacing - Case 3 |  |  | Drinking Water - LPHO - Full Dose Pacing - Case 4 |  |  | Wastewater - Ideal |  |  | Wastewater - Flow pacing |  |  | Wastewater - Flow & lamp pacing |  |  | Wright et al, 2005
Drinking Water - MP - Case 1 | 1 | G | [6 empty] | 10 bank reactor of 12 lamps per bank |  |  | 10 bank reactor of 12 lamps per bank |  |  | 10 bank reactor of 12 lamps per bank |  |  | 10 bank reactor of 12 lamps per bank |  |  | One bank reactor of 10 x 12 lamps
Drinking Water - MP - Case 2 | 2 | K | Target RED/Reactor | mJ/cm2 | 36 | Target RED/Reactor | mJ/cm2 | 36 | Target RED/Reactor | mJ/cm2 | 50 | Target RED/Reactor | mJ/cm2 | 36 | Target RED/Reactor | mJ/cm2 | 36 | Target RED/Reactor | mJ/cm2 | 36 | Target RED/Reactor | mJ/cm2 | 36 | Target RED/Reactor | mJ/cm2 | 4.1 | Target RED/Reactor | mJ/cm2 | 11 | Target RED/Reactor | mJ/cm2 | 11 | Target RED/Reactor | mJ/cm2 | 23.6
Drinking Water - LPHO - Full Pacing - Case 3 | 3 | O | Flow/Reactor | mgd | 22.1965 | Flow/Reactor | mgd | 22.1965 | Flow/Reactor | mgd | 12.7111 | Flow/Reactor | mgd | 22.1965 | Flow/Reactor | mgd | 21.0545 | Flow/Reactor | mgd | 14.7977 | Flow/Reactor | mgd | 22.1965 | Flow/Reactor | mgd | 17.494 | Flow/Reactor | mgd | 8.8786 | Flow/Reactor | mgd | 8.8786 | Flow/Reactor | mgd | 10
Drinking Water - LPHO - Flow and UVT Pacing - Case 3 | 4 | S | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 89.0308 | UVT | % | 85.8 | UVT | % | 85.8025 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 93.4236 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 75
Drinking Water - LPHO - Flow Pacing - Case 3 | 5 | W | Lamp Aging Factor | % | 86.8352 | Lamp Aging Factor | % | 82.0289 | Lamp Aging Factor | % | 88.2798 | Lamp Aging Factor | % | 80 | Lamp Aging Factor | % | 80.202 | Lamp Aging Factor | % | 79.4332 | Lamp Aging Factor | % | 71.436 | Lamp Aging Factor | % | 100 | Lamp Aging Factor | % | 71.9859 | Lamp Aging Factor | % | 84.3487 | Lamp Aging Factor | % | 100
Drinking Water - LPHO - No Dose Pacing - Case 3 | 6 | AA | Fouling Factor | % | 95.1786 | Fouling Factor | % | 98.3929 | Fouling Factor | % | 96.2751 | Fouling Factor | % | 87.1 | Fouling Factor | % | 87.1429 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 100 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 100
Drinking Water - LPHO - Full Dose Pacing - Case 4 | 7 | AE | Number Operating Banks/Reactor |  | 2 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 11 | Number Operating Banks/Reactor |  | 10 | Number Operating Banks/Reactor |  | 9 | Number Operating Banks/Reactor |  | 10 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 2
Wastewater - Ideal | 8 | AI | Actual Power 1 | kW | 20 | Actual Power 1 | kW | 12 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 100 | Actual Power 1 | kW | 80 | Actual Power 1 | kW | 80 | Actual Power 1 | kW | 15
Wastewater - Flow pacing | 9 | AM | Actual Power 2 | kW | 20 | Actual Power 2 | kW | 12 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW |  | Actual Power 2 | kW |  | Actual Power 2 | kW |  | Actual Power 2 | kW
Wastewater - Flow & lamp pacing | 10 | AQ | # Type 1 Lamps / Bank |  | 3 | # Type 1 Lamps / Bank |  | 8 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 120 | # Type 1 Lamps / Bank |  | 64 | # Type 1 Lamps / Bank |  | 64 | # Type 1 Lamps / Bank |  | 64 | # Type 1 Lamps / Bank |  | 3
Wright et al, 2005 | 11 | AU | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0
Not used | 12 | AY | Model Calc |  | G17:G34 | Model Calc |  | K17:K34 | Model Calc |  | O17:O34 | Model Calc |  | S17:S34 | Model Calc |  | W17:W38 | Model Calc |  | AA17:AA38 | Model Calc |  | AE17:AE34 | Model Calc |  | AI17:AI27 | Model Calc |  | AM17:AM27 | Model Calc |  | AQ17:AQ27 | Model Calc |  | AU17:AU34
Not used | 13 | BC
Not used | 14 | BG | Target Lamp Power 1 | kW | 14.6823 | Target Lamp Power 1 | kW | 4.7717 | Target Lamp Power 1 | kW | 0.16417 | Target Lamp Power 1 | kW | 0.4264 | Target Lamp Power 1 | kW | 0.35589 | Target Lamp Power 1 | kW | 0.32798 | Target Lamp Power 1 | kW | 0.17507 | Target Lamp Power 1 | kW | 0.016139 | Target Lamp Power 1 | kW | 0.0559 | Target Lamp Power 1 | kW | 0.046391 | Target Lamp Power 1 | kW | 15.7487
Not used | 15 | BK | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW | 0 | Target Lamp Power 2 | kW | 0 | Target Lamp Power 2 | kW | 0 | Target Lamp Power 2 | kW
Not used | 16 | BO | Target Sensor | W/m2 | 270.3462 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 2.5059 | Target Sensor | W/m2 | 3.8048 | Target Sensor | W/m2 | 3.641 | Target Sensor | W/m2 | 3.3554 | Target Sensor | W/m2 | 2.589 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 27.9765
Not used | 17 | BS | Sensor | W/m2 | 471.5664 | Sensor | W/m2 | 1 | Sensor | W/m2 | 5.4951 | Sensor | W/m2 | 3.7506 | Sensor | W/m2 | 3.7625 | Sensor | W/m2 | 5.9197 | Sensor | W/m2 | 5.3237 | Sensor | W/m2 | 1 | Sensor | W/m2 | 1 | Sensor | W/m2 | 1 | Sensor | W/m2 | 26.6465
Not used | 18 | BW | Credited dose | mJ/cm2 | 53.0448 | Credited dose | mJ/cm2 | 66.9954 | Credited dose | mJ/cm2 | 92.4034 | Credited dose | mJ/cm2 | 35.5986 | Credited dose | mJ/cm2 | 33.6571 | Credited dose | mJ/cm2 | 94.3969 | Credited dose | mJ/cm2 | 63.2679 | Credited dose | mJ/cm2 |  | Credited dose | mJ/cm2 |  | Credited dose | mJ/cm2 |  | Credited dose | mJ/cm2 | 23.0582
Not used | 19 | CA | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0
Not used | 20 | CE | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.05046 | UVA | cm-1 | 0.066513 | UVA | cm-1 | 0.0665 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.029543 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.12494
|  |  | Output factor | % | 82.6485 | Output factor | % | 80.7106 | Output factor | % | 84.9915 | Output factor | % | 69.68 | Output factor | % | 69.8903 | Output factor | % | 75.6034 | Output factor | % | 67.9918 | Output factor | % | 100 | Output factor | % | 68.5151 | Output factor | % | 80.2819 | Output factor | % | 100
|  |  | Min banks |  | 1 | Min banks |  | 1 | Min banks |  | 2 | Min banks |  | 2 | Min banks |  | 2 | Min banks |  | 10 | Min banks |  | 1 | Residence Time | s | 0.68606 | Residence Time | s | 1.3518 | Residence Time | s | 1.3518 | Min banks |  | 1
|  |  | Min UVT | % | 75 | Min UVT | % | 75 | Min UVT | % | 85 | Min UVT | % | 85 | Min UVT | % | 85 | Min UVT | % | 85 | Min UVT | % | 85 | Iavg | mW/cm2 | 24.9947 | Iavg | mW/cm2 | 16.5143 | Iavg | mW/cm2 | 16.5143 | Min UVT | % | 75
|  |  | Max UVT | % | 95 | Max UVT | % | 95 | Max UVT | % | 96 | Max UVT | % | 96 | Max UVT | % | 96 | Max UVT | % | 96 | Max UVT | % | 96 | [9 empty] | Max UVT | % | 98
|  |  | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | [9 empty] | Min Flow | mgd | 5
|  |  | Max Flow | mgd | 35 | Max Flow | mgd | 36 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | RED Model |  |  | RED Model |  |  | RED Model |  |  | Max Flow | mgd | 40
|  |  | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 89.0308 | Dose calc UVT | % | 85.8 | Dose calc UVT | % | 85.8025 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Lamps x-direction |  | 8 | Lamps x-direction |  | 8 | Lamps x-direction |  | 8 | Dose calc UVT | % | 75
|  |  | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.05046 | Dose calc UVA | cm-1 | 0.066513 | Dose calc UVA | cm-1 | 0.0665 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Lamps y-direction |  | 8 | Lamps y-direction |  | 8 | Lamps y-direction |  | 8 | Dose calc UVA | cm-1 | 0.12494
|  |  | Dose calc flow | mgd | 22.1965 | Dose calc flow | mgd | 22.1965 | Dose calc flow | mgd | 12.7111 | Dose calc flow | mgd | 22.1965 | Dose calc flow | mgd | 21.0545 | Dose calc flow | mgd | 14.7977 | Dose calc flow | mgd | 22.1965 | Lamp spacing | cm | 7.62 | Lamp spacing | cm | 7.62 | Lamp spacing | cm | 7.62 | Dose calc flow | mgd | 10
|  |  | S Nominal | W/m2 | 570.5686 | Fraction of Peak Power |  | 0.32094 | S Nominal | W/m2 | 6.4654 | S Nominal | W/m2 | 5.3827 | S Nominal | W/m2 | 5.3834 | S Nominal | W/m2 | 7.8299 | S Nominal | W/m2 | 7.8299 | Lamp length | cm | 147 | Lamp length | cm | 147 | Lamp length | cm | 147 | S Nominal | W/m2 | 26.6465
|  |  | S Nominal *Q | W/m2/mgd | 12664.6254 |  |  |  | S Nominal *Q | W/m2/mgd | 82.1826 | S Nominal *Q | W/m2/mgd | 119.4761 | S Nominal *Q | W/m2/mgd | 113.3453 | S Nominal *Q | W/m2/mgd | 115.8644 | S Nominal *Q | W/m2/mgd | 173.7967 | Sleeve diameter | cm | 2.54 | Sleeve diameter | cm | 2.54 | Sleeve diameter | cm | 2.54 | S Nominal *Q | W/m2/mgd | 266.465
[24 empty] | 100% Lamp Power | kW | 0.0675 | 100% Lamp Power | kW | 0.0675 | 100% Lamp Power | kW | 0.0675
|  |  | Sensor Model Coefficients |  |  | Model Coefficients |  |  | Sensor Model Coefficients |  |  | Sensor Model Coefficients |  |  | S Nominal Default | W/m2 | 6.1714 | S Nominal Default | W/m2 | 6.1714 | Sensor Model Coefficients | [11 empty] | Sensor Model Coefficients
|  |  | A |  | -4 | A |  | 2.3676 | A |  | -1.383 | A |  | -1.383 | S Nominal Default*Q | W/m2/mgd | 129.9365 | S Nominal *Q Default | W/m2/mgd | 136.0698 | A |  | -1.383 | Logistic Model: y=a/(1+b*exp(-cx)) |  |  | Logistic Model: y=a/(1+b*exp(-cx)) |  |  | Logistic Model: y=a/(1+b*exp(-cx)) |  |  | A |  | 1.3577
|  |  | B |  | 0.11 | B |  | 8.2746 | B |  | 0.056732 | B |  | 0.056732 | Default UVA | cm-1 | 0.05448 | Default UVA | cm-1 | 0.05448 | B |  | 0.056732 | Coefficient Data: |  |  | Coefficient Data: |  |  | Coefficient Data: |  |  | B |  | 0.08262
|  |  | C |  | 1.8 | C |  | 0.67349 | [6 empty] | Sensor Model Coefficients |  |  | Sensor Model Coefficients | [5 empty] | a = |  | -9.7123 | a = |  | -9.7123 | a = |  | -9.7123 | C |  | -1.8933
[6 empty] | D |  | 0.93411 | RED Model Coefficients |  |  | RED Model Coefficients |  |  | A |  | -1.383 | A |  | -1.383 | RED Model Coefficients |  |  | b = |  | -6.156 | b = |  | -6.156 | b = |  | -6.156
|  |  | RED Model Coefficients | [5 empty] | A |  | 2.4987 | A |  | 2.4987 | B |  | 0.056732 | B |  | 0.056732 | A |  | 2.4987 | c = |  | 0.01594 | c = |  | 0.01594 | c = |  | 0.01594 | RED Model Coefficients
|  |  | A |  | 2.1514 | Lamp Power (100%) | kW | 12 | B |  | 9.2 | B |  | 9.2 | [6 empty] | B |  | 9.2 | [9 empty] | A |  | 3.0794
|  |  | B |  | 10.2072 |  |  |  | C |  | 0.78215 | C |  | 0.78215 | RED Model Coefficients |  |  | RED Model Coefficients |  |  | C |  | 0.78215 |  |  |  | Default UVT | % | 85 | Default UVT | % | 85 | B |  | -22.8474
|  |  | C |  | 0.69671 | Validated Range |  |  | D |  | 0.94868 | D |  | 0.94868 | A |  | 2.4987 | A |  | 2.4987 | D |  | 0.94868 |  |  |  | Default Lamp aging | % | 70 | Default Lamp aging | % | 70 | C |  | 0.80207
|  |  | D |  | 1.0956 | Min Banks |  | 1 | [6 empty] | B |  | 9.2 | B |  | 9.2 | [6 empty] | Default Fouling | % | 85 | Default Fouling | % | 85 | D |  | 1.9267
|  |  | Nominal Power |  | 20 | Max Banks |  | 3 | Nominal Power |  | 0.36 | Nominal Power |  | 0.36 | C |  | 0.78215 | C |  | 0.78215 | Nominal Power |  | 0.36 | [9 empty] | E |  | -36.2535
[6 empty] | Min UVT (%) |  |  | Default Flow |  | 13.229 | Default Flow |  | 13.229 | D |  | 0.94868 | D |  | 0.94868 | Default Flow |  | 16.5362 | [9 empty] | Nominal Power |  | 15
[6 empty] | 1 bank |  | 75 | Default UVT |  | 88.2104 | Default UVT |  | 88.2104 | [6 empty] | Default UVT |  | 88.2104
|  |  | Validated Range |  |  | 2 banks |  | 75 | Default Output Factor |  | 59.5 | Default Output Factor |  | 59.6785 | Nominal Power |  | 0.36 | Nominal Power |  | 0.36 | Default Output Factor |  | 59.5
|  |  | Min Banks |  | 1 | 3 banks |  | 75 | Default Trains |  | 3 | Default Trains |  | 3 | Default Flow |  | 22.0483 | Default Flow |  | 22.0483 | Default Trains |  | 3 | [9 empty] | Validated Range
|  |  | Max Banks |  | 3 | Max UVT (%) |  |  | Default Reactors |  | 1 | Default Reactors |  | 1 | Default UVT |  | 88.2104 | Default UVT |  | 88.2104 | Default Reactors |  | 1 | [9 empty] | Min Banks |  | 1
|  |  | Min UVT (%) |  |  | 1 bank |  | 95 | Default Banks |  | 10 | Default Banks |  | 10 | Default Output Factor |  | 59.6785 | Default Output Factor |  | 59.6785 | Default Banks |  | 10 | [9 empty] | Max Banks |  | 1
|  |  | 1 bank |  | 75 | 2 banks |  | 95 | [6 empty] | Default Trains |  | 3 | Default Trains |  | 3 | [12 empty] | Min UVT (%)
|  |  | 2 banks |  | 75 | 3 banks |  | 95 | Validated Range |  |  | Validated Range |  |  | Default Reactors |  | 1 | Default Reactors |  | 1 | Validated Range |  |  | UVDIS Data | UVT | Iavg | [6 empty] | 1 bank |  | 75
|  |  | 3 banks |  | 75 | Min Flow (mgd) |  |  | Min Banks |  | 2 | Min Banks |  | 2 | Default Banks |  | 10 | Default Banks |  | 10 | Min Banks |  | 1 |  | % | mW/cm2 | [6 empty] | 2 banks |  | 75
|  |  | Max UVT (%) |  |  | 1 bank |  | 5 | Max Banks |  | 11 | Max Banks |  | 11 | [6 empty] | Max Banks |  | 11 |  | 95 | 27.4 | [6 empty] | 3 banks |  | 75
|  |  | 1 bank |  | 95 | 2 banks |  | 5 | Min UVT (%) |  |  | Min UVT (%) |  |  | Validated Range |  |  | Validated Range |  |  | Min UVT (%) |  |  |  | 90 | 20.92 | [6 empty] | Max UVT (%)
|  |  | 2 banks |  | 95 | 3 banks |  | 5 | 1 bank |  | 85 | 1 bank |  | 85 | Min Banks |  | 2 | Min Banks |  | 8 | 1 bank |  | 85 |  | 85 | 16.48 | [6 empty] | 1 bank |  | 98
|  |  | 3 banks |  | 95 | Max Flow (mgd) |  |  | 2 banks |  | 85 | 2 banks |  | 85 | Max Banks |  | 11 | Max Banks |  | 8 | Max UVT (%) |  |  |  | 80 | 13.45 | [6 empty] | 2 banks |  | 98
|  |  | Min Flow (mgd) |  |  | 1 bank |  | 36 | 3 banks |  | 85 | 3 banks |  | 85 | Min UVT (%) |  |  | Min UVT (%) |  |  | Min UVT (%) |  |  |  | 75 | 11.2 | [6 empty] | 3 banks |  | 98
|  |  | 1 bank |  | 5 | 2 banks |  | 36 | 4 banks |  | 85 | 4 banks |  | 85 | 1 bank |  | 85 | 1 bank |  | 85 | 1 bank |  | 96 |  | 70 | 9.51 | [6 empty] | Min Flow (mgd)
|  |  | 2 banks |  | 5 | 3 banks |  | 36 | 5 banks |  | 85 | 5 banks |  | 85 | 2 banks |  | 85 | 2 banks |  | 85 | Min Flow (mgd) |  |  |  | 65 | 8.191 | [6 empty] | 1 bank |  | 5
|  |  | 3 banks |  | 5 |  |  |  | 6 banks |  | 85 | 6 banks |  | 85 | 3 banks |  | 85 | 3 banks |  | 85 | 1 bank |  | 5 |  | 60 | 7.131 | [6 empty] | 2 banks |  | 5
|  |  | Max Flow (mgd) | [5 empty] | 7 banks |  | 85 | 7 banks |  | 85 | 4 banks |  | 85 | 4 banks |  | 85 | Max Flow (mgd) |  |  |  | 55 | 6.259 | [6 empty] | 3 banks |  | 5
|  |  | 1 bank |  | 35 |  |  |  | 8 banks |  | 85 | 8 banks |  | 85 | 5 banks |  | 85 | 5 banks |  | 85 | 1 bank |  | 30 |  | 50 | 5.531 | [6 empty] | Max Flow (mgd)
|  |  | 2 banks |  | 35 |  |  |  | 9 banks |  | 85 | 9 banks |  | 85 | 6 banks |  | 85 | 6 banks |  | 85 |  |  |  |  | 45 | 4.904 | [6 empty] | 1 bank |  | 40
|  |  | 3 banks |  | 35 |  |  |  | 10 banks |  | 85 | 10 banks |  | 85 | 7 banks |  | 85 | 7 banks |  | 85 |  |  |  |  | 40 | 4.367 | [6 empty] | 2 banks |  | 40
[9 empty] | 11 banks |  | 85 | 11 banks |  | 85 | 8 banks |  | 85 | 8 banks |  | 85 |  |  |  |  | 35 | 3.894 | [6 empty] | 3 banks |  | 40
[9 empty] | 12 banks |  | 85 | Max UVT (%) |  |  | 9 banks |  | 85 | 9 banks |  | 85 |  |  |  |  | 30 | 3.469
[9 empty] | Max UVT (%) |  |  | Min UVT (%) |  |  | 10 banks |  | 85 | 10 banks |  | 85 |  |  |  |  | 25 | 3.087
[9 empty] | Min UVT (%) |  |  | 1 bank |  | 96 | 11 banks |  | 85 | 11 banks |  | 85 |  |  |  |  | 20 | 2.735
[9 empty] | 1 bank |  | 96 | 2 banks |  | 96 | Max UVT (%) |  |  | Max UVT (%) | [6 empty] | 15 | 2.391
[9 empty] | 2 banks |  | 96 | 3 banks |  | 96 | Min UVT (%) |  |  | Min UVT (%)
[9 empty] | 3 banks |  | 96 | 4 banks |  | 96 | 1 bank |  | 96 | 1 bank |  | 96
[9 empty] | 4 banks |  | 96 | 5 banks |  | 96 | 2 banks |  | 96 | 2 banks |  | 96
[9 empty] | 5 banks |  | 96 | 6 banks |  | 96 | 3 banks |  | 96 | 3 banks |  | 96
[9 empty] | 6 banks |  | 96 | 7 banks |  | 96 | 4 banks |  | 96 | 4 banks |  | 96
[9 empty] | 7 banks |  | 96 | 8 banks |  | 96 | 5 banks |  | 96 | 5 banks |  | 96
[9 empty] | 8 banks |  | 96 | 9 banks |  | 96 | 6 banks |  | 96 | 6 banks |  | 96
[9 empty] | 9 banks |  | 96 | 10 banks |  | 96 | 7 banks |  | 96 | 7 banks |  | 96
[9 empty] | 10 banks |  | 96 | 11 banks |  | 96 | 8 banks |  | 96 | 8 banks |  | 96
[9 empty] | 11 banks |  | 96 | Min Flow (mgd) |  |  | 9 banks |  | 96 | 9 banks |  | 96
[9 empty] | 12 banks |  | 96 | 1 bank |  | 5 | 10 banks |  | 96 | 10 banks |  | 96
[9 empty] | Min Flow (mgd) |  |  | 2 banks |  | 5 | 11 banks |  | 96 | 11 banks |  | 96
[9 empty] | 1 bank |  | 5 | 3 banks |  | 5 | Min Flow (mgd) |  |  | Min Flow (mgd)
[9 empty] | 2 banks |  | 5 | 4 banks |  | 5 | 1 bank |  | 5 | 1 bank |  | 5
[9 empty] | 3 banks |  | 5 | 5 banks |  | 5 | 2 banks |  | 5 | 2 banks |  | 5
[9 empty] | 4 banks |  | 5 | 6 banks |  | 5 | 3 banks |  | 5 | 3 banks |  | 5
[9 empty] | 5 banks |  | 5 | 7 banks |  | 5 | 4 banks |  | 5 | 4 banks |  | 5
[9 empty] | 6 banks |  | 5 | 8 banks |  | 5 | 5 banks |  | 5 | 5 banks |  | 5
[9 empty] | 7 banks |  | 5 | 9 banks |  | 5 | 6 banks |  | 5 | 6 banks |  | 5
[9 empty] | 8 banks |  | 5 | 10 banks |  | 5 | 7 banks |  | 5 | 7 banks |  | 5
[9 empty] | 9 banks |  | 5 | 11 banks |  | 5 | 8 banks |  | 5 | 8 banks |  | 5
[9 empty] | 10 banks |  | 5 | Max Flow (mgd) |  |  | 9 banks |  | 5 | 9 banks |  | 5
[9 empty] | 11 banks |  | 5 | 1 bank |  | 30 | 10 banks |  | 5 | 10 banks |  | 5
[9 empty] | 12 banks |  | 5 | 2 banks |  | 30 | 11 banks |  | 5 | 11 banks |  | 5
[9 empty] | Max Flow (mgd) |  |  | 3 banks |  | 30 | Max Flow (mgd) |  |  | Max Flow (mgd)
[9 empty] | 1 bank |  | 30 | 4 banks |  | 30 | 1 bank |  | 30 | 1 bank |  | 30
[9 empty] | 2 banks |  | 30 | 5 banks |  | 30 | 2 banks |  | 30 | 2 banks |  | 30
[9 empty] | 3 banks |  | 30 | 6 banks |  | 30 | 3 banks |  | 30 | 3 banks |  | 30
[9 empty] | 4 banks |  | 30 | 7 banks |  | 30 | 4 banks |  | 30 | 4 banks |  | 30
[9 empty] | 5 banks |  | 30 | 8 banks |  | 30 | 5 banks |  | 30 | 5 banks |  | 30
[9 empty] | 6 banks |  | 30 | 9 banks |  | 30 | 6 banks |  | 30 | 6 banks |  | 30
[9 empty] | 7 banks |  | 30 | 10 banks |  | 30 | 7 banks |  | 30 | 7 banks |  | 30
[9 empty] | 8 banks |  | 30 | 11 banks |  | 30 | 8 banks |  | 30 | 8 banks |  | 30
[9 empty] | 9 banks |  | 30 |  |  |  | 9 banks |  | 30 | 9 banks |  | 30
[9 empty] | 10 banks |  | 30 |  |  |  | 10 banks |  | 30 | 10 banks |  | 30
[9 empty] | 11 banks |  | 30 |  |  |  | 11 banks |  | 30 | 11 banks |  | 30
[9 empty] | 12 banks |  | 30

## RISKMODEL
Pathogen UV Dose-response |  |  | Risk Model
UV Dose | mJ/cm2 | 50.0519 | Pathogen concentration | #/L | 1.1233
log Inactivation |  | 3.4717 | Filter log Removal |  | 2
Max Credit |  | 6 | UV Log Inactivation |  | 3.4726
Credit |  | 3.4717 | Chemical log Inactivation |  | 0
|  |  | Water consumption | L/day | 1.2
MMF Model: y=(a*b+c*x^d)/(b+x^d) |  |  | Infections per dose |  | 0.028
Coefficient Data: |  |  | Delta Time | days | 1.0156
a = |  | -0.0087794 | Risk |  | 1.2912e-07
b = |  | 157.8254 | Annual risk |  | 4.4496e-05
c = |  | 4.5861 | Population |  | 1000000
d = |  | 1.5845 | Infectons |  | 0.12912

## REACTORDOSE
Reactor | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Bank | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Train 1 | Train 2 | Train 3 | Train 4 | Train 5 | Train 6 | Train 7 | Train 8
Date/Time | Train 1: Reactor Dose (mJ/cm2)
2005-03-06 03:45 | Train 1: 50.7384; Train 2: 50.7384
2005-03-07 00:06 | Train 1: 50.1107; Train 2: 50.1107
2005-03-08 00:39 | Train 1: 50.0854; Train 2: 50.0854
2005-03-09 01:02 | Train 1: 50.1623; Train 2: 50.1623
2005-03-10 01:30 | Train 1: 50.815; Train 2: 50.815
2005-03-11 02:09 | Train 1: 50.9273; Train 2: 50.9273
2005-03-12 02:43 | Train 1: 50.0458; Train 2: 50.0458
2005-03-13 03:17 | Train 1: 50.2142; Train 2: 50.2142; Train 3: 50.8902
2005-03-14 03:45 | Train 1: 50.0115; Train 2: 50.0115
2005-03-15 00:17 | Train 1: 50.0447; Train 2: 50.0447; Train 3: 50.6367
2005-03-16 03:56 | Train 1: 50.051; Train 2: 50.051
2005-03-17 00:11 | Train 1: 50.0539; Train 2: 50.0539
2005-03-18 00:45 | Train 1: 50.4458; Train 2: 50.4458
2005-03-19 01:24 | Train 1: 50.6207; Train 2: 50.6207
2005-03-20 01:52 | Train 1: 50.2372; Train 2: 50.2372
2005-03-21 02:26 | Train 1: 50.1384; Train 2: 50.1384
2005-03-22 03:11 | Train 1: 50.2697; Train 2: 50.2697
2005-03-23 03:56 | Train 1: 50.3885; Train 2: 50.3885
2005-03-24 03:22 | Train 1: 50.2172; Train 2: 50.2172
2005-03-25 03:56 | Train 1: 50.342; Train 2: 50.342
2005-03-26 00:22 | Train 1: 50.1078; Train 2: 50.1078
2005-03-27 00:51 | Train 1: 50.2275; Train 2: 50.2275
2005-03-28 01:24 | Train 1: 50.1036; Train 2: 50.1036
2005-03-29 01:58 | Train 1: 50.4676; Train 2: 50.4676
2005-03-30 02:54 | Train 1: 50.1905; Train 2: 50.1905; Train 3: 50.1684
2005-03-31 03:28 | Train 1: 50.154; Train 2: 50.154; Train 3: 50.3576
2005-04-01 | Train 1: 50.402; Train 2: 50.402
2005-04-02 00:39 | Train 1: 50.0768; Train 2: 50.0768
2005-04-03 01:08 | Train 1: 50.4793; Train 2: 50.4793
2005-04-04 02:32 | Train 1: 50.5182; Train 2: 50.5182
2005-04-05 03:17 | Train 1: 50.3609; Train 2: 50.3609; Train 3: 50.6901
2005-04-06 03:51 | Train 1: 50.1484; Train 2: 50.1484
2005-04-07 00:17 | Train 1: 50.0958; Train 2: 50.0958
2005-04-08 01:13 | Train 1: 50.1693; Train 2: 50.1693
2005-04-09 01:58 | Train 1: 50.431; Train 2: 50.431
2005-04-10 02:26 | Train 1: 50.5592; Train 2: 50.5592
2005-04-11 02:49 | Train 1: 50.0473; Train 2: 50.0473
2005-04-12 03:11 | Train 1: 50.0747; Train 2: 50.0747
2005-04-13 03:34 | Train 1: 50.2961; Train 2: 50.2961
2005-04-14 04:02 | Train 1: 50.0861; Train 2: 50.0861; Train 3: 50.1745
2005-04-15 01:30 | Train 1: 50.0453; Train 2: 50.0453
2005-04-16 02:15 | Train 1: 50.1039; Train 2: 50.1039
2005-04-17 02:38 | Train 1: 50.0028; Train 2: 50.0028
2005-04-18 02:54 | Train 1: 50.0568; Train 2: 50.0568
2005-04-19 03:28 | Train 1: 50.7294; Train 2: 50.7294
2005-04-20 04:02 | Train 1: 50.5682; Train 2: 50.5682
2005-04-21 00:39 | Train 1: 50.5583; Train 2: 50.5583
2005-04-21 04:47 | Train 1: 50.2581; Train 2: 50.2581
2005-04-22 01:41 | Train 1: 50.1622; Train 2: 50.1622
2005-04-23 02:09 | Train 1: 50.1677; Train 2: 50.1677; Train 3: 50.0289; Train 4: 50.0289
2005-04-24 02:26 | Train 1: 50.1665; Train 2: 50.1665
2005-04-25 02:49 | Train 1: 50.0092; Train 2: 50.0092
2005-04-26 02:26 | Train 1: 50.626; Train 2: 50.626
2005-04-27 03:00 | Train 1: 50.2189; Train 2: 50.2189; Train 3: 50.0604
2005-04-28 03:28 | Train 1: 50.0846; Train 2: 50.0846; Train 3: 50.3376
2005-04-29 03:45 | Train 1: 50.6106; Train 2: 50.6106
2005-04-30 00:11 | Train 1: 50.1672; Train 2: 50.1672
2005-05-01 00:28 | Train 1: 50.0005; Train 2: 50.0005
2005-05-02 00:51 | Train 1: 50.1992; Train 2: 50.1992
2005-05-03 01:24 | Train 1: 50.1001; Train 2: 50.1001; Train 3: 50.2063
2005-05-04 01:52 | Train 1: 50.7124; Train 2: 50.7124
2005-05-05 02:15 | Train 1: 50.0111; Train 2: 50.0111; Train 3: 50.1348
2005-05-06 02:38 | Train 1: 50.0998; Train 2: 50.0998; Train 3: 50.5223
2005-05-07 02:49 | Train 1: 50.1903; Train 2: 50.1903; Train 3: 50.071
2005-05-08 03:11 | Train 1: 50.5284; Train 2: 50.5284; Train 3: 50.0289
2005-05-09 03:34 | Train 1: 50.1198; Train 2: 50.1198; Train 3: 50.0083
2005-05-10 03:51 | Train 1: 50.0939; Train 2: 50.0939; Train 3: 50.0283
2005-05-11 00:17 | Train 1: 50.5203; Train 2: 50.5203; Train 3: 50.059
2005-05-12 00:34 | Train 1: 50.1231; Train 2: 50.1231
2005-05-13 00:56 | Train 1: 50.4945; Train 2: 50.4945; Train 3: 50.4331
2005-05-14 01:19 | Train 1: 50.5757; Train 2: 50.5757
2005-05-15 01:36 | Train 1: 50.0093; Train 2: 50.0093; Train 3: 50.1875
2005-05-16 01:58 | Train 1: 50.0889; Train 2: 50.0889; Train 3: 50.1872
2005-05-17 02:21 | Train 1: 50.0893; Train 2: 50.0893; Train 3: 50.2021
2005-05-18 02:43 | Train 1: 50.4125; Train 2: 50.4125; Train 3: 50.3549
2005-05-19 03:00 | Train 1: 50.0785; Train 2: 50.0785; Train 3: 50.2589
2005-05-20 03:17 | Train 1: 50.5223; Train 2: 50.5223; Train 3: 50.1317
2005-05-21 03:45 | Train 1: 50.1539; Train 2: 50.1539; Train 3: 50.1645
2005-05-22 00:06 | Train 1: 50.371; Train 2: 50.371
2005-05-22 04:08 | Train 1: 50.297; Train 2: 50.297
2005-05-23 00:17 | Train 1: 50.5234; Train 2: 50.5234
2005-05-24 00:39 | Train 1: 50.1049; Train 2: 50.1049; Train 3: 50.363
2005-05-25 01:02 | Train 1: 50.0359; Train 2: 50.0359; Train 3: 50.1725; Train 4: 50.0135
2005-05-26 00:28 | Train 1: 50.0183; Train 2: 50.0183
2005-05-27 01:02 | Train 1: 50.0545; Train 2: 50.0545; Train 3: 50.1797
2005-05-28 01:41 | Train 1: 50.229; Train 2: 50.229
2005-05-29 02:04 | Train 1: 50.0059; Train 2: 50.0059
2005-05-30 02:32 | Train 1: 50.5008; Train 2: 50.5008
2005-05-31 03:00 | Train 1: 50.1529; Train 2: 50.1529; Train 3: 50.1193
2005-06-01 03:39 | Train 1: 50.016; Train 2: 50.016; Train 3: 50.1605
2005-06-02 03:06 | Train 1: 50.0132; Train 2: 50.0132; Train 3: 50.0926
2005-06-03 02:32 | Train 1: 50.1363; Train 2: 50.1363; Train 3: 50.1558
2005-06-04 03:00 | Train 1: 50.5299; Train 2: 50.5299; Train 3: 50.1902
2005-06-05 03:34 | Train 1: 50.3013; Train 2: 50.3013; Train 3: 50.0516
2005-06-06 04:02 | Train 1: 50.424; Train 2: 50.424; Train 3: 50.1641
2005-06-07 00:39 | Train 1: 50.195
2005-06-08 01:08 | Train 1: 50.4982; Train 2: 50.5475; Train 3: 50.2388
2005-06-09 01:36 | Train 1: 50.1079; Train 2: 50.1543; Train 3: 50.429
2005-06-10 02:09 | Train 1: 50.1675; Train 2: 50.2154; Train 3: 50.0369
2005-06-11 02:43 | Train 1: 50.1152; Train 2: 50.1567; Train 3: 50.2035
2005-06-12 03:11 | Train 1: 50.222; Train 2: 50.2601; Train 3: 50.3305
2005-06-13 03:39 | Train 1: 50.0411; Train 2: 50.0802; Train 3: 50.1061
2005-06-14 | Train 1: 50.0201; Train 2: 50.0659
2005-06-15 00:34 | Train 1: 50.2846; Train 2: 50.3233; Train 3: 50.1868
2005-06-16 01:02 | Train 1: 50.1914; Train 2: 50.2364; Train 3: 50.4136
2005-06-17 01:41 | Train 1: 50.0797; Train 2: 50.1176; Train 3: 50.07
2005-06-18 02:21 | Train 1: 50.2779; Train 2: 50.3155; Train 3: 50.1472
2005-06-19 02:49 | Train 1: 50.1045; Train 2: 50.143; Train 3: 50.0216; Train 4: 50.6355
2005-06-20 03:17 | Train 1: 50.0891; Train 2: 50.1259; Train 3: 50.232; Train 4: 50.088
2005-06-21 00:11 | Train 1: 50.015; Train 2: 50.0587
2005-06-22 00:51 | Train 1: 50.0428; Train 2: 50.0776; Train 3: 50.2732; Train 4: 50.1382
2005-06-26 00:22 | Train 1: 50.165; Train 2: 50.2002; Train 3: 50.2325; Train 4: 50.1516
2005-06-27 00:51 | Train 1: 50.1326; Train 2: 50.0235; Train 3: 50.0154
2005-06-28 00:22 | Train 1: 50.0775; Train 2: 50.1118; Train 3: 50.4418
2005-06-29 03:51 | Train 1: 50.1443; Train 2: 50.2018
2005-06-30 00:28 | Train 1: 50.2612; Train 2: 50.3159; Train 3: 50.1296
2005-07-01 00:51 | Train 1: 50.1744; Train 2: 50.2306; Train 3: 50.0304; Train 4: 50.4814
2005-07-02 03:22 | Train 1: 50.2372; Train 2: 50.2905
2005-07-03 03:51 | Train 1: 50.3845; Train 2: 50.4166; Train 3: 50.1538
2005-07-04 00:45 | Train 1: 50.0882; Train 2: 50.1199; Train 3: 50.5369
2005-07-05 02:38 | Train 1: 50.0035; Train 2: 50.0362; Train 3: 50.484; Train 4: 50.3451
2005-07-06 01:24 | Train 1: 50.0311; Train 2: 50.0636; Train 3: 50.0328
2005-07-07 01:08 | Train 1: 50.4936; Train 2: 50.0294; Train 3: 50.2015
2005-07-08 01:52 | Train 1: 50.362; Train 2: 50.3974; Train 3: 50.1915
2005-07-09 02:21 | Train 1: 50.0247; Train 2: 50.0565; Train 3: 50.0701
2005-07-10 02:43 | Train 1: 50.4252; Train 2: 50.024; Train 3: 50.2119; Train 4: 50.2005
2005-07-11 03:17 | Train 1: 50.064; Train 2: 50.0147; Train 3: 50.1651
2005-07-12 03:56 | 50.179 | 50.2146 | 50.0398 | 50.2421 | 50.3672 | 50.3672
2005-07-13 00:28 | 50.3244 | 50.3584 | 50.0539 | 50.0475 | 51.0754
2005-07-14 01:08 | 50.2655 | 50.2951 | 50.0242 | 50.1149 | 50.795
2005-07-15 01:41 | Train 1: 50.1114; Train 2: 50.1419; Train 3: 50.2826
2005-07-16 02:15 | Train 1: 50.1897; Train 2: 50.2188; Train 3: 50.2706
2005-07-17 02:38 | 50.2617 | 50.2946 | 50.0166 | 50.7324 | 50.3502
2005-07-18 02:54 | 50.0057 | 50.0364 | 50.1074 | 50.3265 | 50.794 | 50.2786
2005-07-19 03:39 | 50.0318 | 50.0641 | 50.1578 | 50.2786 | 50.4079 | 50.4516 | 50.9799
2005-07-20 00:11 | Train 1: 50.0445
2005-07-21 00:51 | 50.0169 | 50.1098 | 50.341 | 50.0924 | 50.5201
2005-07-22 01:30 | Train 1: 50.3955; Train 2: 50.0586; Train 3: 50.0159; Train 4: 50.6602
2005-07-23 02:09 | Train 1: 50.0054; Train 2: 50.0695
2005-07-24 02:32 | 50.3375 | 50.0058 | 50.065 | 50.362 | 51.1178
2005-07-25 02:54 | Train 1: 50.0255; Train 2: 50.0899; Train 3: 50.1003
2005-07-26 03:22 | Train 1: 50.3814; Train 2: 50.0541; Train 3: 50.0973
2005-07-27 02:49 | Train 1: 50.2705; Train 2: 50.3261; Train 3: 50.5239
2005-07-28 03:17 | Train 1: 50.232; Train 2: 50.294; Train 3: 50.071; Train 4: 50.2574
2005-07-29 03:51 | 50.3701 | 50.0483 | 50.0396 | 50.7888 | 50.4915
2005-07-30 00:22 | Train 1: 50.1619; Train 2: 50.2581; Train 3: 50.1355
2005-07-31 00:51 | Train 1: 50.0239; Train 2: 50.0844; Train 3: 50.1616
2005-08-01 01:19 | Train 1: 50.3993; Train 2: 50.4544; Train 3: 50.5086; Train 4: 50.1144
2005-08-02 01:52 | Train 1: 50.0758; Train 2: 50.0465; Train 3: 50.1671; Train 4: 50.1657
2005-08-03 02:21 | Train 1: 50.3536; Train 2: 50.0435; Train 3: 50.035; Train 4: 50.4384
2005-08-04 02:54 | 50.2236 | 50.2839 | 50.0978 | 50.336 | 50.9704
2005-08-05 03:17 | Train 1: 50.0543; Train 2: 50.1077; Train 3: 50.0533; Train 4: 50.1188
2005-08-06 03:39 | 50.0341 | 50.1156 | 50.2316 | 50.5856 | 50.5139
2005-08-07 04:02 | 50.0822 | 50.134 | 50.0321 | 50.1407 | 50.1758
2005-08-08 00:22 | Train 1: 50.0737; Train 2: 50.1311; Train 3: 50.0963
2005-08-09 00:56 | Train 1: 50.3743; Train 2: 50.0572; Train 3: 50.5661
2005-08-10 00:22 | 50.016 | 50.0681 | 50.0466 | 50.3764 | 50.9889
2005-08-11 | 50.02 | 50.0967 | 50.0457 | 50.3436 | 50.3765
2005-08-12 00:39 | 50.0829 | 50.0289 | 50.1375 | 50.071 | 50.9911
2005-08-12 04:41 | Train 1: 50.0536; Train 2: 50.1094; Train 3: 50.0848; Train 4: 50.3774
2005-08-13 01:08 | Train 1: 50.0798; Train 2: 50.0733; Train 3: 50.1804; Train 4: 50.2745
2005-08-14 01:30 | Train 1: 50.1241; Train 2: 50.2001; Train 3: 50.308; Train 4: 50.208
2005-08-15 01:52 | Train 1: 50.0311; Train 2: 50.1114; Train 3: 50.3226; Train 4: 50.012
2005-08-16 02:15 | 50.0807 | 50.1298 | 50.0771 | 50.0622 | 50.14 | 51.0132 | 50.2137
2005-08-17 01:36 | 50.1337 | 50.2029 | 50.535 | 50.3996 | 50.2553 | 50.303
2005-08-18 02:09 | Train 1: 50.2489; Train 2: 50.0191; Train 3: 50.4253; Train 4: 50.5338
2005-08-19 02:43 | Train 1: 50.1733; Train 2: 50.2269; Train 3: 50.1614; Train 4: 50.3276
2005-08-20 03:11 | 50.1795 | 50.2276 | 50.0614 | 50.094 | 51.0696
2005-08-21 03:34 | Train 1: 50.1099; Train 2: 50.1628; Train 3: 50.4822; Train 4: 50.2724
2005-08-22 03:56 | Train 1: 50.201; Train 2: 50.2486; Train 3: 50.1376
2005-08-23 00:11 | Train 1: 50.1587; Train 2: 50.2301; Train 3: 50.2994; Train 4: 50.0433
2005-08-24 00:45 | Train 1: 50.19; Train 2: 50.2371; Train 3: 50.0182; Train 4: 50.8197
2005-08-25 01:19 | Train 1: 50.0899; Train 2: 50.0398; Train 3: 50.0023
2005-08-26 01:36 | Train 1: 50.1651; Train 2: 50.2116; Train 3: 50.0766
2005-08-27 02:15 | Train 1: 50.1435; Train 2: 50.1945
2005-08-28 02:38 | Train 1: 50.6019; Train 2: 50.0413; Train 3: 50.3558; Train 4: 50.2221
2005-08-29 03:06 | Train 1: 50.367; Train 2: 50.413; Train 3: 50.0544; Train 4: 50.1546
2005-08-30 01:30 | Train 1: 50.0139; Train 2: 50.0604; Train 3: 50.3974
2005-08-31 02:54 | Train 1: 50.3176; Train 2: 50.363; Train 3: 50.0905; Train 4: 50.01
2005-09-01 02:21 | Train 1: 50.036; Train 2: 50.0819; Train 3: 50.033
2005-09-02 02:43 | Train 1: 50.014; Train 2: 50.0598; Train 3: 50.2074; Train 4: 50.3406
2005-09-03 03:11 | 50.1128 | 50.1836 | 50.4043 | 50.4229 | 50.4002
2005-09-04 03:34 | Train 1: 50.1702; Train 2: 50.2189; Train 3: 50.4115
2005-09-05 03:56 | Train 1: 50.237; Train 2: 50.2812; Train 3: 50.0173
2005-09-06 00:11 | Train 1: 50.3984; Train 2: 50.4426
2005-09-07 00:45 | Train 1: 50.0416; Train 2: 50.0853; Train 3: 50.6814; Train 4: 50.2953
2005-09-08 01:02 | Train 1: 50.2975; Train 2: 50.3411; Train 3: 50.0102
2005-09-09 02:32 | Train 1: 50.2155; Train 2: 50.2642; Train 3: 50.291
2005-09-10 02:54 | Train 1: 50.0679; Train 2: 50.1318; Train 3: 50.1043; Train 4: 50.266
2005-09-11 03:17 | Train 1: 50.117; Train 2: 50.1805; Train 3: 50.1531
2005-09-12 03:34 | Train 1: 50.2009; Train 2: 50.2436
2005-09-13 01:58 | Train 1: 50.4377; Train 2: 50.0211; Train 3: 50.0236
2005-09-14 01:24 | Train 1: 50.0576; Train 2: 50.1039; Train 3: 50.3384
2005-09-15 01:41 | 50.1209 | 50.167 | 50.3676 | 50.2699 | 50.9023
2005-09-16 02:04 | Train 1: 50.0053; Train 2: 50.047; Train 3: 50.6921; Train 4: 50.7381
2005-09-17 02:21 | Train 1: 50.1148; Train 2: 50.1572; Train 3: 50.7666; Train 4: 50.0141
2005-09-18 02:43 | Train 1: 50.4909; Train 2: 50.5326; Train 3: 50.002; Train 4: 50.647
2005-09-19 03:11 | Train 1: 50.2657; Train 2: 50.307; Train 3: 50.2372
2005-09-20 03:28 | Train 1: 50.5037; Train 2: 50.545; Train 3: 50.056
2005-09-21 03:45 | Train 1: 50.273; Train 2: 50.3139; Train 3: 50.3709; Train 4: 50.687
2005-09-22 03:17 | Train 1: 50.2845; Train 2: 50.326; Train 3: 50.0996
2005-09-23 03:45 | Train 1: 50.0894; Train 2: 50.1336; Train 3: 50.3015; Train 4: 50.2183
2005-09-24 | Train 1: 50.0927; Train 2: 50.1367; Train 3: 50.2125
2005-09-25 00:28 | Train 1: 50.0312; Train 2: 50.0916; Train 3: 50.0805; Train 4: 50.0013
2005-09-26 00:56 | Train 1: 50.0023; Train 2: 50.0421; Train 3: 50.5419; Train 4: 50.3394
2005-09-27 01:24 | 50.1084 | 50.1481 | 50.6935 | 50.6371 | 50.5847
2005-09-28 03:56 | Train 1: 50.0715; Train 2: 50.1146; Train 3: 50.13
2005-09-29 00:11 | Train 1: 50.6014; Train 2: 50.0041; Train 3: 50.0437
2005-09-30 00:34 | Train 1: 50.3091; Train 2: 50.3484; Train 3: 50.7575; Train 4: 50.3428
2005-10-01 00:56 | Train 1: 50.04; Train 2: 50.0799; Train 3: 50.4064
2005-10-02 01:24 | 50.2223 | 50.2611 | 50.3217 | 50.6129 | 50.4374
2005-10-03 01:52 | Train 1: 50.2196; Train 2: 50.2583; Train 3: 50.1144; Train 4: 50.4537
2005-10-04 02:15 | Train 1: 50.3248; Train 2: 50.3634; Train 3: 50.7993
2005-10-05 02:49 | 50.0408 | 50.079 | 50.5315 | 50.3732 | 50.1901
2005-10-06 03:17 | Train 1: 50.291; Train 2: 50.33; Train 3: 50.7758
2005-10-07 03:39 | Train 1: 50.0116; Train 2: 50.0503; Train 3: 50.3005
2005-10-08 04:02 | 50.0299 | 50.0676 | 50.4965 | 50.3641 | 50.1119 | 50.3101
2005-10-09 00:28 | Train 1: 50.0097; Train 2: 50.0505; Train 3: 50.1153; Train 4: 51.0727
2005-10-10 00:51 | Train 1: 50.4288; Train 2: 50.4665; Train 3: 50.2239
2005-10-11 01:24 | Train 1: 50.2; Train 2: 50.2374; Train 3: 50.5895
2005-10-12 01:52 | 50.0487 | 50.0043 | 50.0253 | 50.247 | 50.6955 | 50.8096
2005-10-13 02:21 | Train 1: 50.1989; Train 2: 50.2367; Train 3: 50.2298
2005-10-14 02:54 | Train 1: 50.0505; Train 2: 50.0873; Train 3: 50.4984; Train 4: 50.4525
2005-10-15 03:39 | Train 1: 50.1463; Train 2: 50.183; Train 3: 50.5052
2005-10-16 00:06 | Train 1: 50.0431; Train 2: 50.0972; Train 3: 50.0791
2005-10-17 00:28 | Train 1: 50.2799; Train 2: 50.3164; Train 3: 50.6552
2005-10-18 00:56 | 50.0077 | 50.0469 | 50.0066 | 50.2206 | 50.5366
2005-10-19 00:22 | Train 1: 50.1043; Train 2: 50.1404; Train 3: 50.405; Train 4: 50.0004
2005-10-19 04:30 | Train 1: 50.1232; Train 2: 50.1593; Train 3: 50.5355
2005-10-20 00:51 | Train 1: 50.0156; Train 2: 50.0544; Train 3: 50.0322
2005-10-21 01:19 | Train 1: 50.3497; Train 2: 50.3863; Train 3: 50.7248; Train 4: 50.6503
2005-10-22 01:47 | Train 1: 50.3684; Train 2: 50.4042
2005-10-23 02:21 | Train 1: 50.5549; Train 2: 50.5914; Train 3: 50.0628; Train 4: 50.8413
2005-10-24 02:49 | Train 1: 50.4565; Train 2: 50.492; Train 3: 50.7498; Train 4: 50.3291
2005-10-25 03:28 | Train 1: 50.0532; Train 2: 50.0883; Train 3: 50.4496; Train 4: 50.3826
2005-10-26 03:51 | Train 1: 50.1655; Train 2: 50.2034; Train 3: 50.1737
2005-10-27 00:34 | Train 1: 50.2355; Train 2: 50.2705; Train 3: 50.3157
2005-10-28 01:08 | Train 1: 50.0494; Train 2: 50.0869; Train 3: 50.0328
2005-10-29 01:47 | Train 1: 50.0737; Train 2: 50.1083; Train 3: 50.3913
2005-10-30 02:15 | Train 1: 50.6829; Train 2: 50.0202; Train 3: 50.046
2005-10-31 02:43 | Train 1: 50.3325; Train 2: 50.367
2005-11-01 03:22 | Train 1: 50.2018; Train 2: 50.2367; Train 3: 50.4958
2005-11-02 03:51 | Train 1: 50.5097; Train 2: 50.544; Train 3: 50.2544
2005-11-03 00:17 | Train 1: 50.0862; Train 2: 50.1227; Train 3: 50.0501; Train 4: 50.3573
2005-11-04 00:45 | Train 1: 50.516; Train 2: 50.5501; Train 3: 50.7927
2005-11-05 01:19 | Train 1: 50.3429; Train 2: 50.3774; Train 3: 50.6421
2005-11-06 01:41 | Train 1: 50.3061; Train 2: 50.3398; Train 3: 50.5691
2005-11-07 02:09 | Train 1: 50.5408; Train 2: 50.5745; Train 3: 50.8555
2005-11-08 03:17 | 50.0461 | 50.0819 | 50.014 | 50.4788 | 50.3883
2005-11-09 03:51 | Train 1: 50.0883; Train 2: 50.1214; Train 3: 50.2691
2005-11-10 00:17 | Train 1: 50.0218; Train 2: 50.0572; Train 3: 50.0509; Train 4: 50.4308
2005-11-11 00:45 | 50.1163 | 50.1517 | 50.042 | 50.3652 | 50.8681
2005-11-12 01:24 | Train 1: 50.6136; Train 2: 50.6467; Train 3: 50.8125
2005-11-13 01:52 | Train 1: 50.2892; Train 2: 50.322; Train 3: 50.567
2005-11-14 02:15 | Train 1: 50.0909; Train 2: 50.1234; Train 3: 50.2434
2005-11-15 01:41 | Train 1: 50.3393; Train 2: 50.3718; Train 3: 50.5191
2005-11-16 02:21 | Train 1: 50.4603; Train 2: 50.0318; Train 3: 50.7487
2005-11-17 01:47 | Train 1: 50.6125; Train 2: 50.0083; Train 3: 50.4874
2005-11-18 02:26 | Train 1: 50.2524; Train 2: 50.2845; Train 3: 50.4752
2005-11-19 03:00 | Train 1: 50.764; Train 2: 50.7963
2005-11-20 03:28 | Train 1: 50.3061; Train 2: 50.338
2005-11-21 03:51 | Train 1: 50.1874; Train 2: 50.0317
2005-11-22 00:34 | Train 1: 50.0537; Train 2: 50.0853; Train 3: 50.2556
2005-11-23 00:56 | Train 1: 50.1436; Train 2: 50.175
2005-11-24 01:36 | Train 1: 50.2185; Train 2: 50.2499; Train 3: 50.4908
2005-11-25 01:58 | Train 1: 50.4374; Train 2: 50.4688; Train 3: 50.7579
2005-11-26 02:26 | Train 1: 50.4771; Train 2: 50.5084; Train 3: 50.793
2005-11-27 02:49 | Train 1: 50.5492; Train 2: 50.0121
2005-11-28 03:22 | Train 1: 50.0337; Train 2: 50.0652; Train 3: 50.0981
2005-11-29 04:02 | Train 1: 50.3009; Train 2: 50.3318
2005-11-30 00:34 | Train 1: 50.5166; Train 2: 50.5476
2005-12-01 04:19 | Train 1: 50.3457; Train 2: 50.377; Train 3: 50.6422
2005-12-02 00:51 | Train 1: 50.0197; Train 2: 50.0501
2005-12-03 01:13 | Train 1: 50.1057; Train 2: 50.1361; Train 3: 50.4103
2005-12-04 01:41 | Train 1: 50.257; Train 2: 50.0201; Train 3: 50.237
2005-12-05 02:09 | Train 1: 50.4676; Train 2: 50.498
2005-12-06 02:43 | Train 1: 50.0618; Train 2: 50.0918
2005-12-07 03:11 | Train 1: 50.0521; Train 2: 50.0845; Train 3: 50.0387
2005-12-08 03:39 | Train 1: 50.1217; Train 2: 50.1547; Train 3: 50.0395
2005-12-09 00:17 | Train 1: 50.4144; Train 2: 50.4449; Train 3: 50.6703
2005-12-10 00:45 | Train 1: 50.1131; Train 2: 50.1427
2005-12-11 01:08 | Train 1: 50.2522; Train 2: 50.0212; Train 3: 50.2637; Train 4: 50.6257
2005-12-12 01:41 | Train 1: 50.3583; Train 2: 50.3879
2005-12-13 02:15 | Train 1: 50.2418; Train 2: 50.0119; Train 3: 50.1781
2005-12-14 02:54 | Train 1: 50.3121; Train 2: 50.3414; Train 3: 50.6925
2005-12-15 03:22 | Train 1: 50.5154; Train 2: 50.5454; Train 3: 50.8387
2005-12-16 03:56 | Train 1: 50.2629; Train 2: 50.292
2005-12-17 00:28 | Train 1: 50.0548; Train 2: 50.0862
2005-12-18 00:56 | Train 1: 50.2125; Train 2: 50.2414; Train 3: 50.5817
2005-12-19 01:24 | Train 1: 50.2265; Train 2: 50.2553; Train 3: 50.4605
2005-12-20 01:47 | Train 1: 50.0735; Train 2: 50.1163
2005-12-21 02:15 | Train 1: 50.2368; Train 2: 50.2679
2005-12-22 02:43 | Train 1: 50.2975; Train 2: 50.326
2005-12-23 03:11 | Train 1: 50.1147
2005-12-24 03:39 | Train 1: 50.1525; Train 2: 50.1948
2005-12-25 04:02 | Train 1: 50.0217; Train 2: 50.0636; Train 3: 50.3635
2005-12-26 00:22 | Train 1: 50.2143; Train 2: 50.2604; Train 3: 50.3014
2005-12-27 00:51 | Train 1: 50.6065; Train 2: 50.6487; Train 3: 50.0582
2005-12-28 01:24 | Train 1: 50.131; Train 2: 50.1732
2005-12-29 01:13 | Train 1: 50.2064; Train 2: 50.2481; Train 3: 50.0082
2005-12-30 00:39 | Train 1: 50.0141; Train 2: 50.0562
2005-12-31 00:34 | Train 1: 50.3769; Train 2: 50.4189; Train 3: 50.052
2006-01-01 01:02 | Train 1: 50.0589; Train 2: 50.0288; Train 3: 50.3881
2006-01-02 01:41 | Train 1: 50.0807; Train 2: 50.1249; Train 3: 50.1189
2006-01-03 02:09 | Train 1: 50.4321; Train 2: 50.4732; Train 3: 50.047; Train 4: 50.4216
2006-01-04 02:43 | Train 1: 50.0151; Train 2: 50.0564; Train 3: 50.3288
2006-01-05 01:02 | Train 1: 50.0609; Train 2: 50.1015; Train 3: 50.2667
2006-01-06 01:19 | Train 1: 50.105; Train 2: 50.1493; Train 3: 50.1261
2006-01-07 01:47 | Train 1: 50.1111; Train 2: 50.152; Train 3: 50.4214
2006-01-08 01:19 | Train 1: 50.0198; Train 2: 50.0605; Train 3: 50.4367
2006-01-09 01:41 | Train 1: 50.0278; Train 2: 50.0709; Train 3: 50.0062
2006-01-10 02:21 | Train 1: 50.7486; Train 2: 50.0037; Train 3: 50.0886
2006-01-11 02:43 | Train 1: 50.0114; Train 2: 50.0543; Train 3: 50.0403
2006-01-12 03:11 | Train 1: 50.0902; Train 2: 50.1299; Train 3: 50.4328
2006-01-13 03:45 | Train 1: 50.3605; Train 2: 50.0419; Train 3: 50.02
2006-01-14 00:06 | Train 1: 50.067; Train 2: 50.1064
2006-01-15 00:34 | Train 1: 50.122; Train 2: 50.165; Train 3: 50.0623
2006-01-16 01:02 | Train 1: 50.0407; Train 2: 50.0814; Train 3: 50.2346
2006-01-17 01:30 | Train 1: 50.0337; Train 2: 50.0056
2006-01-18 01:52 | Train 1: 50.6378; Train 2: 50.6772; Train 3: 50.0183
2006-01-19 02:21 | Train 1: 50.329; Train 2: 50.3686; Train 3: 50.1073
2006-01-20 03:11 | Train 1: 50.103; Train 2: 50.1417; Train 3: 50.4135
2006-01-21 02:38 | Train 1: 50.3393; Train 2: 50.3786; Train 3: 50.6165; Train 4: 50.4736
2006-01-22 03:00 | Train 1: 50.013; Train 2: 50.055
2006-01-23 03:34 | Train 1: 50.1854; Train 2: 50.2244
2006-01-24 03:56 | Train 1: 50.0419; Train 2: 50.0837; Train 3: 50.0482; Train 4: 50.0133
2006-01-25 00:17 | Train 1: 50.3536; Train 2: 50.3925; Train 3: 50.7608
2006-01-26 00:56 | Train 1: 50.156; Train 2: 50.1942
2006-01-27 01:41 | Train 1: 50.0127; Train 2: 50.0511; Train 3: 50.3121; Train 4: 50.1244
2006-01-28 02:09 | Train 1: 50.2506; Train 2: 50.2886; Train 3: 50.0174; Train 4: 50.139
2006-01-29 02:43 | Train 1: 50.1143; Train 2: 50.1557; Train 3: 50.1613
2006-01-30 03:11 | Train 1: 50.019; Train 2: 50.0596; Train 3: 50.035
2006-01-31 03:34 | Train 1: 50.0021; Train 2: 50.0395; Train 3: 50.1884
2006-02-01 04:02 | Train 1: 50.5413; Train 2: 50.579; Train 3: 50.0649
2006-02-02 00:22 | Train 1: 50.3928; Train 2: 50.4308; Train 3: 50.0526; Train 4: 50.0862
2006-02-03 01:02 | Train 1: 50.1338; Train 2: 50.171; Train 3: 50.4599
2006-02-04 01:24 | Train 1: 50.063; Train 2: 50.1005; Train 3: 50.437
2006-02-05 02:04 | Train 1: 50.0586; Train 2: 50.0316; Train 3: 50.3377
2006-02-06 02:38 | Train 1: 50.1766; Train 2: 50.214; Train 3: 50.3972
2006-02-07 03:11 | Train 1: 50.1866; Train 2: 50.2234; Train 3: 50.4349
2006-02-08 03:34 | Train 1: 50.0623; Train 2: 50.0398
2006-02-09 00:06 | Train 1: 50.0219; Train 2: 50.0584
2006-02-10 00:39 | Train 1: 50.0586; Train 2: 50.0325
2006-02-11 01:13 | Train 1: 50.1015; Train 2: 50.1412; Train 3: 50.0311
2006-02-12 01:36 | Train 1: 50.701; Train 2: 50.7382; Train 3: 50.0642
2006-02-13 02:09 | Train 1: 50.0106; Train 2: 50.0467; Train 3: 50.2463
2006-02-14 02:38 | Train 1: 50.0755; Train 2: 50.1121
2006-02-15 03:06 | Train 1: 50.2215; Train 2: 50.261
2006-02-16 03:28 | Train 1: 50.1867; Train 2: 50.2254; Train 3: 50.1498
2006-02-17 00:11 | Train 1: 50.0152; Train 2: 50.0519
2006-02-18 00:34 | Train 1: 50.1736; Train 2: 50.2121
2006-02-19 01:02 | Train 1: 50.505; Train 2: 50.5408; Train 3: 50.07
2006-02-20 01:30 | Train 1: 50.1141; Train 2: 50.1501; Train 3: 50.418
2006-02-21 01:52 | Train 1: 50.2254; Train 2: 50.0031
2006-02-22 02:15 | Train 1: 50.5207; Train 2: 50.5562
2006-02-23 01:36 | Train 1: 50.2143; Train 2: 50.2502
2006-02-24 02:09 | Train 1: 50.5389; Train 2: 50.5743; Train 3: 50.1271
2006-02-25 02:54 | Train 1: 50.0403; Train 2: 50.0753
2006-02-26 03:22 | Train 1: 50.1421; Train 2: 50.1776
2006-02-27 03:45 | Train 1: 50.6564; Train 2: 50.692; Train 3: 50.0842
2006-02-28 00:06 | Train 1: 50.0361; Train 2: 50.0714
2006-02-28 04:13 | Train 1: 50.0592; Train 2: 50.097; Train 3: 50.1251
2006-03-01 00:34 | Train 1: 50.0612; Train 2: 50.0965
2006-03-01 04:36 | Train 1: 50.4357; Train 2: 50.471; Train 3: 50.7865
2006-03-02 01:08 | Train 1: 50.234; Train 2: 50.2686; Train 3: 50.5788
2006-03-03 01:52 | Train 1: 50.2016; Train 2: 50.236; Train 3: 50.6549
2006-03-04 02:21 | Train 1: 50.1224; Train 2: 50.1572
2006-03-05 02:49 | Train 1: 50.0265; Train 2: 50.0638; Train 3: 50.093
2006-03-06 03:22 | Train 1: 50.6722; Train 2: 50.7072
2006-03-07 03:45 | Train 1: 50.0725; Train 2: 50.1118
2006-03-08 00:06 | Train 1: 50.0454; Train 2: 50.0824
2006-03-09 00:39 | Train 1: 50.3593; Train 2: 50.3942
2006-03-10 01:02 | Train 1: 50.004; Train 2: 50.0407; Train 3: 50.0833
2006-03-11 01:30 | Train 1: 50.0211; Train 2: 50.0556
2006-03-12 02:09 | Train 1: 50.4328; Train 2: 50.4666; Train 3: 50.1265
2006-03-13 02:43 | Train 1: 50.1528; Train 2: 50.1868; Train 3: 50.6277
2006-03-14 03:17 | Train 1: 50.0755; Train 2: 50.1119; Train 3: 50.155
2006-03-15 03:45 | Train 1: 50.0551; Train 2: 50.0895
2006-03-16 00:17 | Train 1: 50.32; Train 2: 50.3545
2006-03-17 03:56 | Train 1: 50.6014; Train 2: 50.6349; Train 3: 51.0055
2006-03-18 00:11 | Train 1: 50.2184; Train 2: 50.0162
2006-03-19 00:45 | Train 1: 50.0116; Train 2: 50.0471
2006-03-20 01:24 | Train 1: 50.2369; Train 2: 50.0208
2006-03-21 01:52 | Train 1: 50.4831; Train 2: 50.5162; Train 3: 50.0563
2006-03-22 02:26 | Train 1: 50.1642; Train 2: 50.1974; Train 3: 50.183
2006-03-23 03:11 | Train 1: 50.0904; Train 2: 50.1259; Train 3: 50.2044
2006-03-24 03:56 | Train 1: 50.0612; Train 2: 50.0938; Train 3: 50.4756
2006-03-25 03:22 | Train 1: 50.7282; Train 2: 50.7616; Train 3: 50.2274
2006-03-26 03:56 | Train 1: 50.3076; Train 2: 50.3402; Train 3: 50.7148
2006-03-27 00:22 | Train 1: 50.7952; Train 2: 50.0345; Train 3: 50.0551
2006-03-28 00:51 | Train 1: 50.1206; Train 2: 50.029
2006-03-29 01:24 | Train 1: 50.2822; Train 2: 50.315; Train 3: 50.6918
2006-03-30 01:58 | Train 1: 50.0342; Train 2: 50.0107; Train 3: 50.0321
2006-03-31 02:54 | Train 1: 50.5683; Train 2: 50.6006; Train 3: 50.0045
2006-04-01 03:28 | Train 1: 50.1067; Train 2: 50.1391; Train 3: 50.1573
2006-04-02 | Train 1: 50.3369; Train 2: 50.3701; Train 3: 50.023
2006-04-03 00:39 | Train 1: 50.1858; Train 2: 50.2188
2006-04-04 01:08 | Train 1: 50.056; Train 2: 50.0906
2006-04-05 02:32 | Train 1: 50.3504; Train 2: 50.3833
2006-04-06 03:17 | Train 1: 50.3016; Train 2: 50.3337; Train 3: 50.3602
2006-04-07 03:51 | Train 1: 50.3412; Train 2: 50.3739
2006-04-08 00:17 | Train 1: 50.1872; Train 2: 50.2191
2006-04-09 01:13 | Train 1: 50.0284; Train 2: 50.062; Train 3: 50.1569
2006-04-10 01:58 | Train 1: 50.6695; Train 2: 50.7011; Train 3: 50.0784
2006-04-11 02:26 | Train 1: 50.4347; Train 2: 50.4671
2006-04-12 02:49 | Train 1: 50.0872; Train 2: 50.1193
2006-04-13 03:11 | Train 1: 50.0688; Train 2: 50.0998; Train 3: 50.5437
2006-04-14 03:34 | Train 1: 50.3426; Train 2: 50.3741; Train 3: 50.816
2006-04-15 04:02 | Train 1: 50.0952; Train 2: 50.126; Train 3: 50.1981
2006-04-16 01:30 | Train 1: 50.6203; Train 2: 50.6518; Train 3: 50.1417; Train 4: 50.3993
2006-04-17 02:15 | Train 1: 50.6859; Train 2: 50.717; Train 3: 50.2017
2006-04-18 02:38 | Train 1: 50.3338; Train 2: 50.365; Train 3: 50.0321
2006-04-19 02:54 | Train 1: 50.1617; Train 2: 50.1923; Train 3: 50.1576
2006-04-20 03:28 | Train 1: 50.1398; Train 2: 50.173; Train 3: 50.2773
2006-04-21 04:02 | Train 1: 50.1164; Train 2: 50.1468; Train 3: 50.2355; Train 4: 50.4135
2006-04-22 00:39 | Train 1: 50.1694; Train 2: 50.2012; Train 3: 50.0406
2006-04-23 01:41 | Train 1: 50.0972; Train 2: 50.1279; Train 3: 50.3793
2006-04-24 02:09 | Train 1: 50.586; Train 2: 50.6166; Train 3: 50.0728; Train 4: 50.3634
2006-04-25 02:26 | Train 1: 50.3765; Train 2: 50.4081; Train 3: 50.0022; Train 4: 50.5023
2006-04-26 02:49 | Train 1: 50.0113; Train 2: 50.0459; Train 3: 50.3504; Train 4: 50.1576
2006-04-27 02:26 | Train 1: 50.5104
2006-04-28 03:00 | Train 1: 50.1884; Train 2: 50.2349
2006-04-29 03:28 | Train 1: 50.1314; Train 2: 50.0155; Train 3: 50.5749
2006-04-30 03:45 | Train 1: 50.0343; Train 2: 50.0228
2006-05-01 00:11 | Train 1: 50.1024; Train 2: 50.1483; Train 3: 50.0047
2006-05-02 00:28 | Train 1: 50.097; Train 2: 50.0085; Train 3: 50.5374
2006-05-03 00:51 | Train 1: 50.2743; Train 2: 50.3143; Train 3: 50.0014
2006-05-04 01:24 | Train 1: 50.1448; Train 2: 50.1909; Train 3: 50.0487
2006-05-05 01:52 | Train 1: 50.2566; Train 2: 50.3027; Train 3: 50.16
2006-05-06 02:15 | Train 1: 50.0612; Train 2: 50.1035; Train 3: 50.06
2006-05-07 02:38 | Train 1: 50.0156; Train 2: 50.055; Train 3: 50.2105; Train 4: 50.0519

## TARGET POWER 1
Train | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Reactor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Bank | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Train 1, Bank 1 | Train 1, Bank 2 | Train 1, Bank 3 | Train 1, Bank 4 | Train 1, Bank 5 | Train 1, Bank 6 | Train 1, Bank 7 | Train 1, Bank 8 | Train 1, Bank 9 | Train 1, Bank 10 | Train 1, Bank 11 | Train 2, Bank 1 | Train 2, Bank 2 | Train 2, Bank 3 | Train 2, Bank 4 | Train 2, Bank 5 | Train 2, Bank 6 | Train 2, Bank 7 | Train 2, Bank 8 | Train 2, Bank 9 | Train 2, Bank 10 | Train 2, Bank 11 | Train 3, Bank 1 | Train 3, Bank 2 | Train 3, Bank 3 | Train 3, Bank 4 | Train 3, Bank 5 | Train 3, Bank 6 | Train 3, Bank 7 | Train 3, Bank 8 | Train 3, Bank 9 | Train 3, Bank 10 | Train 3, Bank 11 | Train 4, Bank 1 | Train 4, Bank 2 | Train 4, Bank 3 | Train 4, Bank 4 | Train 4, Bank 5 | Train 4, Bank 6 | Train 4, Bank 7 | Train 4, Bank 8 | Train 4, Bank 9 | Train 4, Bank 10 | Train 4, Bank 11 | Train 5, Bank 1 | Train 5, Bank 2 | Train 5, Bank 3 | Train 5, Bank 4 | Train 5, Bank 5 | Train 5, Bank 6 | Train 5, Bank 7 | Train 5, Bank 8 | Train 5, Bank 9 | Train 5, Bank 10 | Train 5, Bank 11 | Train 6, Bank 1 | Train 6, Bank 2 | Train 6, Bank 3 | Train 6, Bank 4 | Train 6, Bank 5 | Train 6, Bank 6 | Train 6, Bank 7 | Train 6, Bank 8 | Train 6, Bank 9 | Train 6, Bank 10 | Train 6, Bank 11 | Train 7, Bank 1 | Train 7, Bank 2 | Train 7, Bank 3 | Train 7, Bank 4 | Train 7, Bank 5 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 12
Date/Time | Target Power 1 (kW)
2005-03-06 03:45 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 |  |  | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682 | 0.32682
2005-03-07 00:06 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 |  |  |  | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309 | 0.32309
2005-03-08 00:39 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34125 | 0.33917 |  | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34372 | 0.34125 | 0.33917
2005-03-09 01:02 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32057 | 0.31865 |  | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32266 | 0.32057 | 0.31865
2005-03-10 01:30 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32412 |  |  | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32619 | 0.32412
2005-03-11 02:09 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 |  |  |  | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769
2005-03-12 02:43 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32362 |  |  | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32362
2005-03-13 03:17 | 0.34909 | 0.34909 | 0.34909 | 0.34909 | 0.34909 | 0.34909 | 0.34909 |  |  |  |  | 0.34909 | 0.34909 | 0.34909 | 0.34909 | 0.34909 | 0.34909 | 0.34909 |  |  |  |  | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437
2005-03-14 03:45 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.34916 | 0.3453 |  |  | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.3509 | 0.34916 | 0.3453
2005-03-15 00:17 | 0.30565 | 0.30565 | 0.30565 | 0.30565 | 0.30565 | 0.30565 | 0.30565 |  |  |  |  | 0.30565 | 0.30565 | 0.30565 | 0.30565 | 0.30565 | 0.30565 | 0.30565 |  |  |  |  | 0.29223 | 0.29223 | 0.29223 | 0.29223 | 0.29223 | 0.29223 | 0.29223
2005-03-16 03:56 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32508 | 0.32169 | 0.31459 | 0.31008 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32508 | 0.32169 | 0.31459 | 0.31008
2005-03-17 00:11 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.34712 |  |  |  | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.35052 | 0.34712
2005-03-18 00:45 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32618 |  |  |  | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32618
2005-03-19 01:24 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32486 | 0.3186 |  |  | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32779 | 0.32486 | 0.3186
2005-03-20 01:52 | 0.35783 | 0.35783 | 0.35783 | 0.35783 | 0.35783 | 0.35783 | 0.35783 |  |  |  |  | 0.35783 | 0.35783 | 0.35783 | 0.35783 | 0.35783 | 0.35783 | 0.35783
2005-03-21 02:26 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.34079 | 0.33457 |  |  | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.3451 | 0.34079 | 0.33457
2005-03-22 03:11 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33562 | 0.32968 |  |  | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | 0.33562 | 0.32968
2005-03-23 03:56 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34356 | 0.33772 | 0.32571 |  | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34754 | 0.34356 | 0.33772 | 0.32571
2005-03-24 03:22 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.30933 | 0.30431 |  |  | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.31284 | 0.30933 | 0.30431
2005-03-25 03:56 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32634 | 0.32119 | 0.30898 |  | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32634 | 0.32119 | 0.30898
2005-03-26 00:22 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.34631 | 0.34106 | 0.32852 |  | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.35003 | 0.34631 | 0.34106 | 0.32852
2005-03-27 00:51 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.32692 | 0.32212 | 0.31077 |  | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.33032 | 0.32692 | 0.32212 | 0.31077
2005-03-28 01:24 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.32881 | 0.32414 | 0.3132 |  | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.33212 | 0.32881 | 0.32414 | 0.3132
2005-03-29 01:58 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.31565 | 0.31127 | 0.30122 |  | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.3187 | 0.31565 | 0.31127 | 0.30122
2005-03-30 02:54 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34034 |  |  |  | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34358 | 0.34034 |  |  |  | 0.31365 | 0.31365 | 0.31365 | 0.31365 | 0.31365 | 0.31365 | 0.31365 | 0.3089
2005-03-31 03:28 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.33754 |  |  |  | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.34066 | 0.33754 |  |  |  | 0.31214 | 0.31214 | 0.31214 | 0.31214 | 0.31214 | 0.31214 | 0.31214 | 0.30772
2005-04-01 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33552 | 0.32916 | 0.31894 |  | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33852 | 0.33552 | 0.32916 | 0.31894
2005-04-02 00:39 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32024 | 0.31438 | 0.30493 | 0.28993 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32024 | 0.31438 | 0.30493 | 0.28993
2005-04-03 01:08 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33501 |  |  |  | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33785 | 0.33501
2005-04-04 02:32 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.3171 | 0.31054 |  |  | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.3171 | 0.31054
2005-04-05 03:17 | 0.32103 | 0.32103 | 0.32103 | 0.32103 | 0.32103 | 0.32103 | 0.32103 |  |  |  |  | 0.32103 | 0.32103 | 0.32103 | 0.32103 | 0.32103 | 0.32103 | 0.32103 |  |  |  |  | 0.29184 | 0.29184 | 0.29184 | 0.29184 | 0.29184 | 0.29184 | 0.29184
2005-04-06 03:51 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34034 | 0.33349 | 0.32278 |  | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34394 | 0.34034 | 0.33349 | 0.32278
2005-04-07 00:17 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.3297 | 0.32321 |  |  | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.3297 | 0.32321
2005-04-08 01:13 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31049 | 0.30454 |  |  | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31364 | 0.31049 | 0.30454
2005-04-09 01:58 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34376 | 0.33734 |  |  | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34717 | 0.34376 | 0.33734
2005-04-10 02:26 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34268 |  |  |  | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34268
2005-04-11 02:49 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31554 | 0.30906 | 0.29664 |  | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31854 | 0.31554 | 0.30906 | 0.29664
2005-04-12 03:11 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35033 | 0.3433 | 0.32992 | 0.31213 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35359 | 0.35033 | 0.3433 | 0.32992 | 0.31213
2005-04-13 03:34 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35407 |  |  |  | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35729 | 0.35407
2005-04-14 04:02 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32329 |  |  |  | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32618 | 0.32329 |  |  |  | 0.29238 | 0.29238 | 0.29238 | 0.29238 | 0.29238 | 0.29238 | 0.29238 | 0.28672
2005-04-15 01:30 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31464 | 0.30716 |  |  | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31742 | 0.31464 | 0.30716
2005-04-16 02:15 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.33818 | 0.33033 | 0.31701 |  | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.34109 | 0.33818 | 0.33033 | 0.31701
2005-04-17 02:38 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34198 | 0.33418 | 0.32108 | 0.30334 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34486 | 0.34198 | 0.33418 | 0.32108 | 0.30334
2005-04-18 02:54 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.35049 | 0.3427 | 0.3296 |  | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.35049 | 0.3427 | 0.3296
2005-04-19 03:28 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31546 | 0.30859 | 0.29715 |  | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31806 | 0.31546 | 0.30859 | 0.29715
2005-04-20 04:02 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31682 | 0.31006 |  |  | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31682 | 0.31006
2005-04-21 00:39 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.30813 |  |  |  | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.31056 | 0.30813
2005-04-21 04:47 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.31937 | 0.31254 |  |  | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.32187 | 0.31937 | 0.31254
2005-04-22 01:41 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34059 | 0.33343 | 0.32011 |  | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34322 | 0.34059 | 0.33343 | 0.32011
2005-04-23 02:09 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35576 | 0.34845 |  |  | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35846 | 0.35576 | 0.34845 |  |  | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31173 | 0.30577 |  |  | 0.30577 | 0.30577 | 0.30577 | 0.30577 | 0.30577 | 0.30577 | 0.30577 | 0.30577 | 0.30577
2005-04-24 02:26 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.3434 | 0.33648 | 0.32263 |  | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.34599 | 0.3434 | 0.33648 | 0.32263
2005-04-25 02:49 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33292 | 0.32634 | 0.31319 | 0.29256 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33537 | 0.33292 | 0.32634 | 0.31319 | 0.29256
2005-04-26 02:26 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.33416 | 0.32767 |  |  | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.3366 | 0.33416 | 0.32767
2005-04-27 03:00 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35546 | 0.34868 | 0.33426 | 0.31308 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35799 | 0.35546 | 0.34868 | 0.33426 | 0.31308 | 0.31665 | 0.31665 | 0.31665 | 0.31665 | 0.31665 | 0.31665 | 0.31665 | 0.31111 | 0.30553 | 0.3033 | 0.3033
2005-04-28 03:28 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.32948 | 0.3233 |  |  | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.33181 | 0.32948 | 0.3233 |  |  | 0.29446 | 0.29446 | 0.29446 | 0.29446 | 0.29446 | 0.29446 | 0.29446 | 0.28955 | 0.28472
2005-04-29 03:45 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35203 | 0.34551 |  |  | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35446 | 0.35203 | 0.34551
2005-04-30 00:11 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33557 | 0.32948 | 0.31501 | 0.29574 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33786 | 0.33557 | 0.32948 | 0.31501 | 0.29574
2005-05-01 00:28 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.32073 | 0.315 | 0.30146 | 0.28372 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.3229 | 0.32073 | 0.315 | 0.30146 | 0.28372
2005-05-02 00:51 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33724 | 0.33131 | 0.31735 |  | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33947 | 0.33724 | 0.33131 | 0.31735
2005-05-03 01:24 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34713 | 0.34113 | 0.32709 |  | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34941 | 0.34713 | 0.34113 | 0.32709 |  | 0.30918 | 0.30918 | 0.30918 | 0.30918 | 0.30918 | 0.30918 | 0.30918 | 0.30434 | 0.29947 | 0.29544
2005-05-04 01:52 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31616 |  |  |  | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31819 | 0.31616
2005-05-05 02:15 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.31491 | 0.30907 | 0.29659 |  | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.3169 | 0.31491 | 0.30907 | 0.29659 |  | 0.28092 | 0.28092 | 0.28092 | 0.28092 | 0.28092 | 0.28092 | 0.28092 | 0.27666 | 0.27252 | 0.26907
2005-05-06 02:38 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.3475 | 0.34113 |  |  | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.34966 | 0.3475 | 0.34113 |  |  | 0.31084 | 0.31084 | 0.31084 | 0.31084 | 0.31084 | 0.31084 | 0.31084 | 0.30632 | 0.30196
2005-05-07 02:49 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.31923 | 0.31347 | 0.30056 |  | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.31923 | 0.31347 | 0.30056 |  | 0.28632 | 0.28632 | 0.28632 | 0.28632 | 0.28632 | 0.28632 | 0.28632 | 0.28239 | 0.27849 | 0.27367
2005-05-08 03:11 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33448 | 0.32855 |  |  | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33651 | 0.33448 | 0.32855 |  |  | 0.30081 | 0.30081 | 0.30081 | 0.30081 | 0.30081 | 0.30081 | 0.30081 | 0.29678 | 0.29287
2005-05-09 03:34 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.3379 | 0.33198 | 0.31799 |  | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.33992 | 0.3379 | 0.33198 | 0.31799 |  | 0.3046 | 0.3046 | 0.3046 | 0.3046 | 0.3046 | 0.3046 | 0.3046 | 0.30067 | 0.29694 | 0.29063
2005-05-10 03:51 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.3124 | 0.30701 |  |  | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.31425 | 0.3124 | 0.30701 |  |  | 0.28226 | 0.28226 | 0.28226 | 0.28226 | 0.28226 | 0.28226 | 0.28226 | 0.2788 | 0.27542
2005-05-11 00:17 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32527 | 0.31974 | 0.30607 |  | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32719 | 0.32527 | 0.31974 | 0.30607 |  | 0.29447 | 0.29447 | 0.29447 | 0.29447 | 0.29447 | 0.29447 | 0.29447 | 0.29092 | 0.28757 | 0.28062
2005-05-12 00:34 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33196 | 0.32638 | 0.31271 |  | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33387 | 0.33196 | 0.32638 | 0.31271
2005-05-13 00:56 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31814 |  |  |  | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31995 | 0.31814 |  |  |  | 0.2882 | 0.2882 | 0.2882 | 0.2882 | 0.2882 | 0.2882 | 0.2882 | 0.28484
2005-05-14 01:19 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31609 | 0.31042 |  |  | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31789 | 0.31609 | 0.31042
2005-05-15 01:36 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.32975 | 0.32392 |  |  | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.33159 | 0.32975 | 0.32392 |  |  | 0.2989 | 0.2989 | 0.2989 | 0.2989 | 0.2989 | 0.2989 | 0.2989 | 0.29558 | 0.29115
2005-05-16 01:58 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31555 | 0.31004 | 0.29633 |  | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31728 | 0.31555 | 0.31004 | 0.29633 |  | 0.28663 | 0.28663 | 0.28663 | 0.28663 | 0.28663 | 0.28663 | 0.28663 | 0.2835 | 0.27941 | 0.27181
2005-05-17 02:21 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31257 | 0.30719 |  |  | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31428 | 0.31257 | 0.30719 |  |  | 0.28445 | 0.28445 | 0.28445 | 0.28445 | 0.28445 | 0.28445 | 0.28445 | 0.28149 | 0.27756
2005-05-18 02:43 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.32615 | 0.32061 | 0.30618 |  | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.3279 | 0.32615 | 0.32061 | 0.30618 |  | 0.29737 | 0.29737 | 0.29737 | 0.29737 | 0.29737 | 0.29737 | 0.29737 | 0.29433 | 0.29036 | 0.28171
2005-05-19 03:00 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.31973 | 0.31437 | 0.30049 | 0.27688 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.32142 | 0.31973 | 0.31437 | 0.30049 | 0.27688 | 0.29202 | 0.29202 | 0.29202 | 0.29202 | 0.29202 | 0.29202 | 0.29202 | 0.28911 | 0.28534 | 0.27716 | 0.26594
2005-05-20 03:17 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34317 | 0.33749 |  |  | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34498 | 0.34317 | 0.33749 |  |  | 0.31394 | 0.31394 | 0.31394 | 0.31394 | 0.31394 | 0.31394 | 0.31394 | 0.31091 | 0.30702
2005-05-21 03:45 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35543 | 0.34962 | 0.33393 |  | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35727 | 0.35543 | 0.34962 | 0.33393 |  | 0.3257 | 0.3257 | 0.3257 | 0.3257 | 0.3257 | 0.3257 | 0.3257 | 0.32264 | 0.31869 | 0.30877
2005-05-22 00:06 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33529 | 0.32987 | 0.31526 |  | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33701 | 0.33529 | 0.32987 | 0.31526
2005-05-22 04:08 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34499 | 0.33942 | 0.32443 |  | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34675 | 0.34499 | 0.33942 | 0.32443
2005-05-23 00:17 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.32692 |  |  |  | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.3286 | 0.32692
2005-05-24 00:39 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32152 | 0.31598 |  |  | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32313 | 0.32152 | 0.31598 |  |  | 0.29427 | 0.29427 | 0.29427 | 0.29427 | 0.29427 | 0.29427 | 0.29427 | 0.29156 | 0.28808
2005-05-25 01:02 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.32929 | 0.3237 | 0.30914 |  | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.33092 | 0.32929 | 0.3237 | 0.30914 |  | 0.30183 | 0.30183 | 0.30183 | 0.30183 | 0.30183 | 0.30183 | 0.30183 | 0.29917 | 0.29569 | 0.28583 |  | 0.27189 | 0.27189 | 0.27189 | 0.27189 | 0.27189 | 0.27189 | 0.27189 | 0.27189 | 0.27189 | 0.26991
2005-05-26 00:28 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34462 | 0.33884 | 0.32385 | 0.29732 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34632 | 0.34462 | 0.33884 | 0.32385 | 0.29732
2005-05-27 01:02 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.329 | 0.32355 | 0.30944 |  | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.3306 | 0.329 | 0.32355 | 0.30944 |  | 0.30165 | 0.30165 | 0.30165 | 0.30165 | 0.30165 | 0.30165 | 0.30165 | 0.29902 | 0.29564 | 0.2861
2005-05-28 01:41 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.33659 | 0.33106 | 0.31687 |  | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.3382 | 0.33659 | 0.33106 | 0.31687
2005-05-29 02:04 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35095 | 0.34527 | 0.33067 |  | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35261 | 0.35095 | 0.34527 | 0.33067
2005-05-30 02:32 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33415 | 0.32878 | 0.31511 | 0.28827 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33572 | 0.33415 | 0.32878 | 0.31511 | 0.28827
2005-05-31 03:00 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34614 | 0.34067 | 0.32669 | 0.29959 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34614 | 0.34067 | 0.32669 | 0.29959 | 0.3167 | 0.3167 | 0.3167 | 0.3167 | 0.3167 | 0.3167 | 0.3167 | 0.31404 | 0.31059 | 0.3009 | 0.28581
2005-06-01 03:39 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.32903 | 0.32387 |  |  | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.33054 | 0.32903 | 0.32387 |  |  | 0.30149 | 0.30149 | 0.30149 | 0.30149 | 0.30149 | 0.30149 | 0.30149 | 0.29898 | 0.29579
2005-06-02 03:06 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.32898 | 0.32389 | 0.31041 | 0.28535 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.33048 | 0.32898 | 0.32389 | 0.31041 | 0.28535 | 0.30184 | 0.30184 | 0.30184 | 0.30184 | 0.30184 | 0.30184 | 0.30184 | 0.29942 | 0.2963 | 0.2865 | 0.27278
2005-06-03 02:32 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32791 | 0.32287 | 0.30962 | 0.28526 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32939 | 0.32791 | 0.32287 | 0.30962 | 0.28526 | 0.30125 | 0.30125 | 0.30125 | 0.30125 | 0.30125 | 0.30125 | 0.30125 | 0.29886 | 0.29582 | 0.28637 | 0.27325
2005-06-04 03:00 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33359 | 0.32854 | 0.31525 |  | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33508 | 0.33359 | 0.32854 | 0.31525 |  | 0.30686 | 0.30686 | 0.30686 | 0.30686 | 0.30686 | 0.30686 | 0.30686 | 0.30452 | 0.3015 | 0.29211
2005-06-05 03:34 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31736 | 0.31259 | 0.30011 |  | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31876 | 0.31736 | 0.31259 | 0.30011 |  | 0.29231 | 0.29231 | 0.29231 | 0.29231 | 0.29231 | 0.29231 | 0.29231 | 0.29009 | 0.28728 | 0.27863
2005-06-06 04:02 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.35245 | 0.34723 | 0.33356 |  | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.35245 | 0.34723 | 0.33356 |  | 0.32502 | 0.32502 | 0.32502 | 0.32502 | 0.32502 | 0.32502 | 0.32502 | 0.32265 | 0.3196 | 0.3102
2005-06-07 00:39 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.3363 | 0.33135 | 0.31847 | 0.29247
2005-06-08 01:08 | 0.31698 | 0.31698 | 0.31698 | 0.31698 | 0.31698 | 0.31698 | 0.31698 | 0.31562 | 0.31103 |  |  | 0.31666 | 0.31666 | 0.31666 | 0.31666 | 0.31666 | 0.31666 | 0.31666 | 0.31529 | 0.31064 |  |  | 0.29105 | 0.29105 | 0.29105 | 0.29105 | 0.29105 | 0.29105 | 0.29105 | 0.28893 | 0.28625
2005-06-09 01:36 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | 0.32784 | 0.32311 |  |  | 0.3289 | 0.3289 | 0.3289 | 0.3289 | 0.3289 | 0.3289 | 0.3289 | 0.32749 | 0.32273 |  |  | 0.30268 | 0.30268 | 0.30268 | 0.30268 | 0.30268 | 0.30268 | 0.30268 | 0.30052 | 0.2978
2005-06-10 02:09 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32728 | 0.32262 | 0.30948 |  | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32694 | 0.32222 | 0.30895 |  | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30038 | 0.29772 | 0.28773
2005-06-11 02:43 | 0.34242 | 0.34242 | 0.34242 | 0.34242 | 0.34242 | 0.34242 | 0.34242 | 0.341 | 0.33617 | 0.32268 |  | 0.34207 | 0.34207 | 0.34207 | 0.34207 | 0.34207 | 0.34207 | 0.34207 | 0.34063 | 0.33578 | 0.32211 |  | 0.31552 | 0.31552 | 0.31552 | 0.31552 | 0.31552 | 0.31552 | 0.31552 | 0.31337 | 0.31065 | 0.30046
2005-06-12 03:11 | 0.35797 | 0.35797 | 0.35797 | 0.35797 | 0.35797 | 0.35797 | 0.35797 | 0.35649 | 0.35152 |  |  | 0.35762 | 0.35762 | 0.35762 | 0.35762 | 0.35762 | 0.35762 | 0.35762 | 0.35613 | 0.3511 |  |  | 0.33021 | 0.33021 | 0.33021 | 0.33021 | 0.33021 | 0.33021 | 0.33021 | 0.32799 | 0.32521
2005-06-13 03:39 | 0.35962 | 0.35962 | 0.35962 | 0.35962 | 0.35962 | 0.35962 | 0.35962 | 0.35815 | 0.35319 | 0.33879 |  | 0.35926 | 0.35926 | 0.35926 | 0.35926 | 0.35926 | 0.35926 | 0.35926 | 0.35778 | 0.35279 | 0.33823 |  | 0.3321 | 0.3321 | 0.3321 | 0.3321 | 0.3321 | 0.3321 | 0.3321 | 0.32992 | 0.32718 | 0.31599
2005-06-14 | 0.33883 | 0.33883 | 0.33883 | 0.33883 | 0.33883 | 0.33883 | 0.33883 | 0.33745 | 0.33283 | 0.31939 |  | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.33712 | 0.33244 | 0.31886
2005-06-15 00:34 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33816 | 0.33356 | 0.32028 | 0.29281 | 0.33919 | 0.33919 | 0.33919 | 0.33919 | 0.33919 | 0.33919 | 0.33919 | 0.33782 | 0.33319 | 0.31976 | 0.29171 | 0.3135 | 0.3135 | 0.3135 | 0.3135 | 0.3135 | 0.3135 | 0.3135 | 0.31147 | 0.30893 | 0.29858 | 0.27995
2005-06-16 01:02 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33589 | 0.33138 | 0.31832 |  | 0.33692 | 0.33692 | 0.33692 | 0.33692 | 0.33692 | 0.33692 | 0.33692 | 0.33557 | 0.331 | 0.31782 |  | 0.3117 | 0.3117 | 0.3117 | 0.3117 | 0.3117 | 0.3117 | 0.3117 | 0.30975 | 0.30727 | 0.29722
2005-06-17 01:41 | 0.35927 | 0.35927 | 0.35927 | 0.35927 | 0.35927 | 0.35927 | 0.35927 | 0.35785 | 0.35307 |  |  | 0.35892 | 0.35892 | 0.35892 | 0.35892 | 0.35892 | 0.35892 | 0.35892 | 0.35749 | 0.35269 |  |  | 0.3324 | 0.3324 | 0.3324 | 0.3324 | 0.3324 | 0.3324 | 0.3324 | 0.33033 | 0.32774
2005-06-18 02:21 | 0.34852 | 0.34852 | 0.34852 | 0.34852 | 0.34852 | 0.34852 | 0.34852 | 0.34714 | 0.34257 | 0.32889 | 0.30085 | 0.34819 | 0.34819 | 0.34819 | 0.34819 | 0.34819 | 0.34819 | 0.34819 | 0.34681 | 0.34218 | 0.32837 | 0.29971 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32081 | 0.31834 | 0.30749 | 0.28818
2005-06-19 02:49 | 0.35143 | 0.35143 | 0.35143 | 0.35143 | 0.35143 | 0.35143 | 0.35143 | 0.35006 | 0.34548 |  |  | 0.35111 | 0.35111 | 0.35111 | 0.35111 | 0.35111 | 0.35111 | 0.35111 | 0.34972 | 0.34511 |  |  | 0.32578 | 0.32578 | 0.32578 | 0.32578 | 0.32578 | 0.32578 | 0.32578 | 0.32382 | 0.3214 |  |  | 0.28339 | 0.28339 | 0.28339 | 0.28339 | 0.28339 | 0.28339 | 0.28339 | 0.28339 | 0.28339
2005-06-20 03:17 | 0.33224 | 0.33224 | 0.33224 | 0.33224 | 0.33224 | 0.33224 | 0.33224 | 0.33095 | 0.32667 |  |  | 0.33193 | 0.33193 | 0.33193 | 0.33193 | 0.33193 | 0.33193 | 0.33193 | 0.33064 | 0.32631 |  |  | 0.30829 | 0.30829 | 0.30829 | 0.30829 | 0.30829 | 0.30829 | 0.30829 | 0.30647 | 0.30419 |  |  | 0.26939 | 0.26939 | 0.26939 | 0.26939 | 0.26939 | 0.26939 | 0.26939 | 0.26939 | 0.26939
2005-06-21 00:11 | 0.33401 | 0.33401 | 0.33401 | 0.33401 | 0.33401 | 0.33401 | 0.33401 | 0.33273 | 0.32846 | 0.31488 | 0.28858 | 0.33371 | 0.33371 | 0.33371 | 0.33371 | 0.33371 | 0.33371 | 0.33371 | 0.33242 | 0.3281 | 0.31437 | 0.28757
2005-06-22 00:51 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34033 | 0.33599 | 0.32226 | 0.29593 | 0.34132 | 0.34132 | 0.34132 | 0.34132 | 0.34132 | 0.34132 | 0.34132 | 0.34001 | 0.33564 | 0.32176 | 0.29493 | 0.31696 | 0.31696 | 0.31696 | 0.31696 | 0.31696 | 0.31696 | 0.31696 | 0.31511 | 0.31281 | 0.30124 | 0.28295 | 0.27802 | 0.27802 | 0.27802 | 0.27802 | 0.27802 | 0.27802 | 0.27802 | 0.27802 | 0.27802 | 0.27281 | 0.2709
2005-06-26 00:22 | 0.34056 | 0.34056 | 0.34056 | 0.34056 | 0.34056 | 0.34056 | 0.34056 | 0.3393 | 0.33514 | 0.32203 |  | 0.34026 | 0.34026 | 0.34026 | 0.34026 | 0.34026 | 0.34026 | 0.34026 | 0.339 | 0.33479 | 0.32155 |  | 0.31702 | 0.31702 | 0.31702 | 0.31702 | 0.31702 | 0.31702 | 0.31702 | 0.31529 | 0.31314 | 0.30247 |  | 0.28219 | 0.28219 | 0.28219 | 0.28219 | 0.28219 | 0.28219 | 0.28219 | 0.28219 | 0.28219 | 0.27792
2005-06-27 00:51 | 0.34209 | 0.34209 | 0.34209 | 0.34209 | 0.34209 | 0.34209 | 0.34209 | 0.34084 | 0.33668 |  |  | 0.34179 | 0.34179 | 0.34179 | 0.34179 | 0.34179 | 0.34179 | 0.34179 | 0.34053 | 0.33635 |  |  | 0.31871 | 0.31871 | 0.31871 | 0.31871 | 0.31871 | 0.31871 | 0.31871 | 0.317 | 0.31488
2005-06-28 00:22 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32336 | 0.31945 | 0.3068 | 0.28322 | 0.32425 | 0.32425 | 0.32425 | 0.32425 | 0.32425 | 0.32425 | 0.32425 | 0.32308 | 0.31913 | 0.30636 | 0.28233 | 0.30258 | 0.30258 | 0.30258 | 0.30258 | 0.30258 | 0.30258 | 0.30258 | 0.30098 | 0.29899 | 0.28851 | 0.27241
2005-06-29 03:51 | 0.32228 | 0.32228 | 0.32228 | 0.32228 | 0.32228 | 0.32228 | 0.32228 | 0.32113 | 0.31728 | 0.30487 |  | 0.32201 | 0.32201 | 0.32201 | 0.32201 | 0.32201 | 0.32201 | 0.32201 | 0.32084 | 0.31697 | 0.30443
2005-06-30 00:28 | 0.32118 | 0.32118 | 0.32118 | 0.32118 | 0.32118 | 0.32118 | 0.32118 | 0.32003 | 0.31623 | 0.30397 | 0.28075 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.31976 | 0.31593 | 0.30355 | 0.27993 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29795 | 0.29602 | 0.28584 | 0.27041
2005-07-01 00:51 | 0.3217 | 0.3217 | 0.3217 | 0.3217 | 0.3217 | 0.3217 | 0.3217 | 0.32057 | 0.31678 | 0.30464 |  | 0.32143 | 0.32143 | 0.32143 | 0.32143 | 0.32143 | 0.32143 | 0.32143 | 0.32028 | 0.31648 | 0.30421 |  | 0.30021 | 0.30021 | 0.30021 | 0.30021 | 0.30021 | 0.30021 | 0.30021 | 0.29867 | 0.29677 | 0.28679 |  | 0.26671 | 0.26671 | 0.26671 | 0.26671 | 0.26671 | 0.26671 | 0.26671 | 0.26671 | 0.26671 | 0.26286
2005-07-02 03:22 | 0.33045 | 0.33045 | 0.33045 | 0.33045 | 0.33045 | 0.33045 | 0.33045 | 0.32929 | 0.32545 | 0.3131 |  | 0.33017 | 0.33017 | 0.33017 | 0.33017 | 0.33017 | 0.33017 | 0.33017 | 0.32901 | 0.32514 | 0.31268
2005-07-03 03:51 | 0.34758 | 0.34758 | 0.34758 | 0.34758 | 0.34758 | 0.34758 | 0.34758 | 0.34638 | 0.34236 | 0.32952 |  | 0.3473 | 0.3473 | 0.3473 | 0.3473 | 0.3473 | 0.3473 | 0.3473 | 0.34607 | 0.34204 | 0.32906 |  | 0.32434 | 0.32434 | 0.32434 | 0.32434 | 0.32434 | 0.32434 | 0.32434 | 0.32273 | 0.32071 | 0.31011
2005-07-04 00:45 | 0.32327 | 0.32327 | 0.32327 | 0.32327 | 0.32327 | 0.32327 | 0.32327 | 0.32216 | 0.31845 |  |  | 0.32301 | 0.32301 | 0.32301 | 0.32301 | 0.32301 | 0.32301 | 0.32301 | 0.32188 | 0.31815 |  |  | 0.30185 | 0.30185 | 0.30185 | 0.30185 | 0.30185 | 0.30185 | 0.30185 | 0.30037 | 0.29851
2005-07-05 02:38 | 0.33297 | 0.33297 | 0.33297 | 0.33297 | 0.33297 | 0.33297 | 0.33297 | 0.33183 | 0.32804 | 0.31554 |  | 0.33269 | 0.33269 | 0.33269 | 0.33269 | 0.33269 | 0.33269 | 0.33269 | 0.33155 | 0.32774 | 0.3151 |  | 0.31114 | 0.31114 | 0.31114 | 0.31114 | 0.31114 | 0.31114 | 0.31114 | 0.30964 | 0.30776 | 0.29721 |  | 0.27656 | 0.27656 | 0.27656 | 0.27656 | 0.27656 | 0.27656 | 0.27656 | 0.27656 | 0.27656 | 0.27276
2005-07-06 01:24 | 0.35971 | 0.35971 | 0.35971 | 0.35971 | 0.35971 | 0.35971 | 0.35971 | 0.35848 | 0.35443 | 0.34103 |  | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35819 | 0.35411 | 0.34058 |  | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33473 | 0.33272 | 0.32153
2005-07-07 01:08 | 0.32884 | 0.32884 | 0.32884 | 0.32884 | 0.32884 | 0.32884 | 0.32884 | 0.32774 | 0.32406 |  |  | 0.32858 | 0.32858 | 0.32858 | 0.32858 | 0.32858 | 0.32858 | 0.32858 | 0.32747 | 0.32376 |  |  | 0.30771 | 0.30771 | 0.30771 | 0.30771 | 0.30771 | 0.30771 | 0.30771 | 0.30624 | 0.30443
2005-07-08 01:52 | 0.33478 | 0.33478 | 0.33478 | 0.33478 | 0.33478 | 0.33478 | 0.33478 | 0.33367 | 0.32994 |  |  | 0.33452 | 0.33452 | 0.33452 | 0.33452 | 0.33452 | 0.33452 | 0.33452 | 0.33338 | 0.32965 |  |  | 0.31346 | 0.31346 | 0.31346 | 0.31346 | 0.31346 | 0.31346 | 0.31346 | 0.31201 | 0.31019
2005-07-09 02:21 | 0.34178 | 0.34178 | 0.34178 | 0.34178 | 0.34178 | 0.34178 | 0.34178 | 0.34064 | 0.33688 | 0.32367 |  | 0.34151 | 0.34151 | 0.34151 | 0.34151 | 0.34151 | 0.34151 | 0.34151 | 0.34037 | 0.33657 | 0.32326 |  | 0.32024 | 0.32024 | 0.32024 | 0.32024 | 0.32024 | 0.32024 | 0.32024 | 0.31875 | 0.31692 | 0.30545
2005-07-10 02:43 | 0.33417 | 0.33417 | 0.33417 | 0.33417 | 0.33417 | 0.33417 | 0.33417 | 0.33307 | 0.32941 | 0.31662 | 0.29058 | 0.3339 | 0.3339 | 0.3339 | 0.3339 | 0.3339 | 0.3339 | 0.3339 | 0.3328 | 0.32912 | 0.31622 | 0.28975 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.31189 | 0.31012 | 0.29907 | 0.28025 | 0.27758 | 0.27758 | 0.27758 | 0.27758 | 0.27758 | 0.27758 | 0.27758 | 0.27758 | 0.27758 | 0.27397 | 0.26812
2005-07-11 03:17 | 0.35159 | 0.35159 | 0.35159 | 0.35159 | 0.35159 | 0.35159 | 0.35159 | 0.35043 | 0.34662 | 0.3333 | 0.30636 | 0.3513 | 0.3513 | 0.3513 | 0.3513 | 0.3513 | 0.3513 | 0.3513 | 0.35015 | 0.3463 | 0.33287 | 0.30551 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32835 | 0.32652 | 0.3151 | 0.29575
2005-07-12 03:56 | 0.35436 | 0.35436 | 0.35436 | 0.35436 | 0.35436 | 0.35436 | 0.35436 | 0.35321 | 0.3494 | 0.3361 |  | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35292 | 0.34908 | 0.33566 |  | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33118 | 0.32936 | 0.318 |  | 0.29517 | 0.29517 | 0.29517 | 0.29517 | 0.29517 | 0.29517 | 0.29517 | 0.29517 | 0.29517 | 0.29144 |  | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 |  | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764 | 0.2764
2005-07-13 00:28 | 0.33492 | 0.33492 | 0.33492 | 0.33492 | 0.33492 | 0.33492 | 0.33492 | 0.33383 | 0.33026 | 0.31779 | 0.29224 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33357 | 0.32997 | 0.31739 | 0.29142 | 0.31457 | 0.31457 | 0.31457 | 0.31457 | 0.31457 | 0.31457 | 0.31457 | 0.31318 | 0.31147 | 0.3009 | 0.28243 | 0.27979 | 0.27979 | 0.27979 | 0.27979 | 0.27979 | 0.27979 | 0.27979 | 0.27979 | 0.27979 | 0.27637 | 0.26967 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26275 | 0.26107
2005-07-14 01:08 | 0.35757 | 0.35757 | 0.35757 | 0.35757 | 0.35757 | 0.35757 | 0.35757 | 0.35643 | 0.35264 | 0.33945 |  | 0.3573 | 0.3573 | 0.3573 | 0.3573 | 0.3573 | 0.3573 | 0.3573 | 0.35615 | 0.35233 | 0.33902 |  | 0.33605 | 0.33605 | 0.33605 | 0.33605 | 0.33605 | 0.33605 | 0.33605 | 0.33459 | 0.33279 | 0.32166 |  | 0.29965 | 0.29965 | 0.29965 | 0.29965 | 0.29965 | 0.29965 | 0.29965 | 0.29965 | 0.29965 | 0.29613 |  | 0.28225 | 0.28225 | 0.28225 | 0.28225 | 0.28225 | 0.28225 | 0.28225 | 0.28225 | 0.28225 | 0.28225
2005-07-15 01:41 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32205 | 0.31865 |  |  | 0.32283 | 0.32283 | 0.32283 | 0.32283 | 0.32283 | 0.32283 | 0.32283 | 0.3218 | 0.31838 |  |  | 0.3038 | 0.3038 | 0.3038 | 0.3038 | 0.3038 | 0.3038 | 0.3038 | 0.30252 | 0.30091
2005-07-16 02:15 | 0.31348 | 0.31348 | 0.31348 | 0.31348 | 0.31348 | 0.31348 | 0.31348 | 0.31249 | 0.30922 |  |  | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31225 | 0.30895 |  |  | 0.29496 | 0.29496 | 0.29496 | 0.29496 | 0.29496 | 0.29496 | 0.29496 | 0.29371 | 0.29217
2005-07-17 02:38 | 0.32626 | 0.32626 | 0.32626 | 0.32626 | 0.32626 | 0.32626 | 0.32626 | 0.32523 | 0.32184 | 0.30939 | 0.28456 | 0.326 | 0.326 | 0.326 | 0.326 | 0.326 | 0.326 | 0.326 | 0.32498 | 0.32158 | 0.30901 | 0.28382 | 0.30714 | 0.30714 | 0.30714 | 0.30714 | 0.30714 | 0.30714 | 0.30714 | 0.30587 | 0.30429 | 0.29342 | 0.27531 | 0.27386 | 0.27386 | 0.27386 | 0.27386 | 0.27386 | 0.27386 | 0.27386 | 0.27386 | 0.27386 | 0.27076 | 0.26339 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25868 | 0.25548
2005-07-18 02:54 | 0.34302 | 0.34302 | 0.34302 | 0.34302 | 0.34302 | 0.34302 | 0.34302 | 0.34195 | 0.33842 | 0.32545 |  | 0.34277 | 0.34277 | 0.34277 | 0.34277 | 0.34277 | 0.34277 | 0.34277 | 0.34168 | 0.33813 | 0.32504 |  | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32178 | 0.32013 | 0.30887 |  | 0.28877 | 0.28877 | 0.28877 | 0.28877 | 0.28877 | 0.28877 | 0.28877 | 0.28877 | 0.28877 | 0.28561 |  | 0.27344 | 0.27344 | 0.27344 | 0.27344 | 0.27344 | 0.27344 | 0.27344 | 0.27344 | 0.27344 | 0.27344 |  | 0.26809 | 0.26809 | 0.26809 | 0.26809 | 0.26809 | 0.26809 | 0.26809 | 0.26809 | 0.26809 | 0.26809
2005-07-19 03:39 | 0.32811 | 0.32811 | 0.32811 | 0.32811 | 0.32811 | 0.32811 | 0.32811 | 0.3271 | 0.32374 | 0.31143 | 0.28652 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32684 | 0.32347 | 0.31107 | 0.28576 | 0.30922 | 0.30922 | 0.30922 | 0.30922 | 0.30922 | 0.30922 | 0.30922 | 0.30798 | 0.30643 | 0.29581 | 0.27742 | 0.27703 | 0.27703 | 0.27703 | 0.27703 | 0.27703 | 0.27703 | 0.27703 | 0.27703 | 0.27703 | 0.2741 | 0.26587 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.26293 | 0.2583 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.25802 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546 | 0.2546
2005-07-20 00:11 | 0.35959 | 0.35959 | 0.35959 | 0.35959 | 0.35959 | 0.35959 | 0.35959 | 0.35849 | 0.35484 | 0.34146
2005-07-21 00:51 | 0.33143 | 0.33143 | 0.33143 | 0.33143 | 0.33143 | 0.33143 | 0.33143 | 0.33042 | 0.32707 | 0.31486 | 0.28964 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.32992 | 0.32653 | 0.31412 | 0.28891 | 0.31227 | 0.31227 | 0.31227 | 0.31227 | 0.31227 | 0.31227 | 0.31227 | 0.31101 | 0.30946 | 0.29889 | 0.28064 | 0.28025 | 0.28025 | 0.28025 | 0.28025 | 0.28025 | 0.28025 | 0.28025 | 0.28025 | 0.28025 | 0.27742 | 0.26936 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26645 | 0.26197
2005-07-22 01:30 | 0.33402 | 0.33402 | 0.33402 | 0.33402 | 0.33402 | 0.33402 | 0.33402 | 0.333 | 0.32966 | 0.31745 | 0.29243 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.3325 | 0.32912 | 0.31671 | 0.29169 | 0.31487 | 0.31487 | 0.31487 | 0.31487 | 0.31487 | 0.31487 | 0.31487 | 0.31363 | 0.31209 | 0.30156 | 0.28359 | 0.28321 | 0.28321 | 0.28321 | 0.28321 | 0.28321 | 0.28321 | 0.28321 | 0.28321 | 0.28321 | 0.2804 | 0.27256
2005-07-23 02:09 | 0.34643 | 0.34643 | 0.34643 | 0.34643 | 0.34643 | 0.34643 | 0.34643 | 0.34539 | 0.34195 | 0.3294 |  | 0.34593 | 0.34593 | 0.34593 | 0.34593 | 0.34593 | 0.34593 | 0.34593 | 0.34488 | 0.34139 | 0.32864
2005-07-24 02:32 | 0.32541 | 0.32541 | 0.32541 | 0.32541 | 0.32541 | 0.32541 | 0.32541 | 0.32444 | 0.32123 | 0.30954 |  | 0.32495 | 0.32495 | 0.32495 | 0.32495 | 0.32495 | 0.32495 | 0.32495 | 0.32395 | 0.3207 | 0.30883 |  | 0.3067 | 0.3067 | 0.3067 | 0.3067 | 0.3067 | 0.3067 | 0.3067 | 0.30549 | 0.30401 | 0.29392 |  | 0.27644 | 0.27644 | 0.27644 | 0.27644 | 0.27644 | 0.27644 | 0.27644 | 0.27644 | 0.27644 | 0.27378 |  | 0.26247 | 0.26247 | 0.26247 | 0.26247 | 0.26247 | 0.26247 | 0.26247 | 0.26247 | 0.26247 | 0.26247
2005-07-25 02:54 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.35425 | 0.35077 |  |  | 0.35479 | 0.35479 | 0.35479 | 0.35479 | 0.35479 | 0.35479 | 0.35479 | 0.35373 | 0.35019 |  |  | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33375 | 0.33215
2005-07-26 03:22 | 0.35208 | 0.35208 | 0.35208 | 0.35208 | 0.35208 | 0.35208 | 0.35208 | 0.35103 | 0.34761 | 0.33481 | 0.3081 | 0.35157 | 0.35157 | 0.35157 | 0.35157 | 0.35157 | 0.35157 | 0.35157 | 0.35051 | 0.34705 | 0.33405 | 0.30736 | 0.33217 | 0.33217 | 0.33217 | 0.33217 | 0.33217 | 0.33217 | 0.33217 | 0.33089 | 0.32932 | 0.31811 | 0.29905
2005-07-27 02:49 | 0.35753 | 0.35753 | 0.35753 | 0.35753 | 0.35753 | 0.35753 | 0.35753 | 0.35648 | 0.35302 |  |  | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35596 | 0.35245 |  |  | 0.33747 | 0.33747 | 0.33747 | 0.33747 | 0.33747 | 0.33747 | 0.33747 | 0.3362 | 0.33462
2005-07-28 03:17 | 0.32617 | 0.32617 | 0.32617 | 0.32617 | 0.32617 | 0.32617 | 0.32617 | 0.32522 | 0.32209 | 0.31008 |  | 0.32571 | 0.32571 | 0.32571 | 0.32571 | 0.32571 | 0.32571 | 0.32571 | 0.32475 | 0.32158 | 0.30938 |  | 0.30803 | 0.30803 | 0.30803 | 0.30803 | 0.30803 | 0.30803 | 0.30803 | 0.30687 | 0.30545 | 0.29482 |  | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27459
2005-07-29 03:51 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35107 | 0.34771 | 0.33486 |  | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.35057 | 0.34716 | 0.33412 |  | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33144 | 0.32992 | 0.31858 |  | 0.29994 | 0.29994 | 0.29994 | 0.29994 | 0.29994 | 0.29994 | 0.29994 | 0.29994 | 0.29994 | 0.29722 |  | 0.28442 | 0.28442 | 0.28442 | 0.28442 | 0.28442 | 0.28442 | 0.28442 | 0.28442 | 0.28442 | 0.28442
2005-07-30 00:22 | 0.34834 | 0.34834 | 0.34834 | 0.34834 | 0.34834 | 0.34834 | 0.34834 | 0.34733 | 0.34403 | 0.3314 | 0.30474 | 0.34786 | 0.34786 | 0.34786 | 0.34786 | 0.34786 | 0.34786 | 0.34786 | 0.34683 | 0.3435 | 0.33067 | 0.30399 | 0.32926 | 0.32926 | 0.32926 | 0.32926 | 0.32926 | 0.32926 | 0.32926 | 0.32804 | 0.32655 | 0.31547 | 0.29597
2005-07-31 00:51 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34604 | 0.34506 | 0.34179 | 0.32936 |  | 0.34557 | 0.34557 | 0.34557 | 0.34557 | 0.34557 | 0.34557 | 0.34557 | 0.34457 | 0.34126 | 0.32864 |  | 0.32724 | 0.32724 | 0.32724 | 0.32724 | 0.32724 | 0.32724 | 0.32724 | 0.32605 | 0.32459 | 0.3137
2005-08-01 01:19 | 0.34745 | 0.34745 | 0.34745 | 0.34745 | 0.34745 | 0.34745 | 0.34745 | 0.34645 | 0.34321 |  |  | 0.34696 | 0.34696 | 0.34696 | 0.34696 | 0.34696 | 0.34696 | 0.34696 | 0.34597 | 0.34268 |  |  | 0.32872 | 0.32872 | 0.32872 | 0.32872 | 0.32872 | 0.32872 | 0.32872 | 0.32753 | 0.32607 |  |  | 0.29613 | 0.29613 | 0.29613 | 0.29613 | 0.29613 | 0.29613 | 0.29613 | 0.29613 | 0.29613
2005-08-02 01:52 | 0.35032 | 0.35032 | 0.35032 | 0.35032 | 0.35032 | 0.35032 | 0.35032 | 0.34933 | 0.34607 | 0.33332 |  | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34884 | 0.34554 | 0.3326 |  | 0.33158 | 0.33158 | 0.33158 | 0.33158 | 0.33158 | 0.33158 | 0.33158 | 0.33041 | 0.32896 | 0.31769 |  | 0.29928 | 0.29928 | 0.29928 | 0.29928 | 0.29928 | 0.29928 | 0.29928 | 0.29928 | 0.29928 | 0.29575
2005-08-03 02:21 | 0.34307 | 0.34307 | 0.34307 | 0.34307 | 0.34307 | 0.34307 | 0.34307 | 0.34209 | 0.33893 | 0.32655 |  | 0.34259 | 0.34259 | 0.34259 | 0.34259 | 0.34259 | 0.34259 | 0.34259 | 0.34162 | 0.33842 | 0.32585 |  | 0.32486 | 0.32486 | 0.32486 | 0.32486 | 0.32486 | 0.32486 | 0.32486 | 0.32371 | 0.3223 | 0.3114 |  | 0.2937 | 0.2937 | 0.2937 | 0.2937 | 0.2937 | 0.2937 | 0.2937 | 0.2937 | 0.2937 | 0.29037
2005-08-04 02:54 | 0.32605 | 0.32605 | 0.32605 | 0.32605 | 0.32605 | 0.32605 | 0.32605 | 0.32514 | 0.32216 | 0.31047 |  | 0.32561 | 0.32561 | 0.32561 | 0.32561 | 0.32561 | 0.32561 | 0.32561 | 0.32469 | 0.32166 | 0.30982 |  | 0.30888 | 0.30888 | 0.30888 | 0.30888 | 0.30888 | 0.30888 | 0.30888 | 0.30781 | 0.30649 | 0.29626 |  | 0.27975 | 0.27975 | 0.27975 | 0.27975 | 0.27975 | 0.27975 | 0.27975 | 0.27975 | 0.27975 | 0.27662 |  | 0.26345 | 0.26345 | 0.26345 | 0.26345 | 0.26345 | 0.26345 | 0.26345 | 0.26345 | 0.26345 | 0.26345
2005-08-05 03:17 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32265 | 0.3197 | 0.30821 | 0.28255 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.32311 | 0.3222 | 0.31923 | 0.30755 | 0.2819 | 0.30665 | 0.30665 | 0.30665 | 0.30665 | 0.30665 | 0.30665 | 0.30665 | 0.30558 | 0.30428 | 0.29425 | 0.27465 | 0.27815 | 0.27815 | 0.27815 | 0.27815 | 0.27815 | 0.27815 | 0.27815 | 0.27815 | 0.27815 | 0.27516 | 0.26275
2005-08-06 03:39 | 0.3397 | 0.3397 | 0.3397 | 0.3397 | 0.3397 | 0.3397 | 0.3397 | 0.33877 | 0.33569 | 0.32372 |  | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33831 | 0.33519 | 0.32304 |  | 0.32209 | 0.32209 | 0.32209 | 0.32209 | 0.32209 | 0.32209 | 0.32209 | 0.321 | 0.31965 | 0.30922 |  | 0.29261 | 0.29261 | 0.29261 | 0.29261 | 0.29261 | 0.29261 | 0.29261 | 0.29261 | 0.29261 | 0.28954 |  | 0.27538 | 0.27538 | 0.27538 | 0.27538 | 0.27538 | 0.27538 | 0.27538 | 0.27538 | 0.27538 | 0.27538
2005-08-07 04:02 | 0.34128 | 0.34128 | 0.34128 | 0.34128 | 0.34128 | 0.34128 | 0.34128 | 0.34035 | 0.33728 | 0.32534 | 0.29835 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.33989 | 0.33679 | 0.32467 | 0.29765 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32263 | 0.32129 | 0.31095 | 0.29018 | 0.29456 | 0.29456 | 0.29456 | 0.29456 | 0.29456 | 0.29456 | 0.29456 | 0.29456 | 0.29456 | 0.29154 | 0.278 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.27775 | 0.26835
2005-08-08 00:22 | 0.35448 | 0.35448 | 0.35448 | 0.35448 | 0.35448 | 0.35448 | 0.35448 | 0.35351 | 0.35034 | 0.33803 |  | 0.35402 | 0.35402 | 0.35402 | 0.35402 | 0.35402 | 0.35402 | 0.35402 | 0.35303 | 0.34983 | 0.33734 |  | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33636 | 0.33522 | 0.33384 | 0.3232
2005-08-09 00:56 | 0.35512 | 0.35512 | 0.35512 | 0.35512 | 0.35512 | 0.35512 | 0.35512 | 0.35416 | 0.35101 | 0.33875 |  | 0.35466 | 0.35466 | 0.35466 | 0.35466 | 0.35466 | 0.35466 | 0.35466 | 0.35369 | 0.35049 | 0.33807 |  | 0.33711 | 0.33711 | 0.33711 | 0.33711 | 0.33711 | 0.33711 | 0.33711 | 0.33598 | 0.33461 | 0.32408
2005-08-10 00:22 | 0.33377 | 0.33377 | 0.33377 | 0.33377 | 0.33377 | 0.33377 | 0.33377 | 0.33286 | 0.32992 | 0.3185 | 0.29179 | 0.33334 | 0.33334 | 0.33334 | 0.33334 | 0.33334 | 0.33334 | 0.33334 | 0.33242 | 0.32944 | 0.31786 | 0.29114 | 0.31695 | 0.31695 | 0.31695 | 0.31695 | 0.31695 | 0.31695 | 0.31695 | 0.3159 | 0.31462 | 0.30484 | 0.28394 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28525 | 0.27238 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.2721 | 0.26323
2005-08-11 | 0.35958 | 0.35958 | 0.35958 | 0.35958 | 0.35958 | 0.35958 | 0.35958 | 0.35861 | 0.35546 | 0.34324 | 0.31484 | 0.35911 | 0.35911 | 0.35911 | 0.35911 | 0.35911 | 0.35911 | 0.35911 | 0.35814 | 0.35494 | 0.34255 | 0.31413 | 0.3416 | 0.3416 | 0.3416 | 0.3416 | 0.3416 | 0.3416 | 0.3416 | 0.34048 | 0.33911 | 0.32868 | 0.30656 | 0.31099 | 0.31099 | 0.31099 | 0.31099 | 0.31099 | 0.31099 | 0.31099 | 0.31099 | 0.31099 | 0.30794 | 0.29441 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.29417 | 0.28498
2005-08-12 00:39 | 0.34219 | 0.34219 | 0.34219 | 0.34219 | 0.34219 | 0.34219 | 0.34219 | 0.34128 | 0.33829 | 0.32675 |  | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34083 | 0.3378 | 0.32611 |  | 0.32519 | 0.32519 | 0.32519 | 0.32519 | 0.32519 | 0.32519 | 0.32519 | 0.32415 | 0.32286 | 0.31303 |  | 0.29646 | 0.29646 | 0.29646 | 0.29646 | 0.29646 | 0.29646 | 0.29646 | 0.29646 | 0.29646 | 0.29362 |  | 0.28086 | 0.28086 | 0.28086 | 0.28086 | 0.28086 | 0.28086 | 0.28086 | 0.28086 | 0.28086 | 0.28086
2005-08-12 04:41 | 0.33637 | 0.33637 | 0.33637 | 0.33637 | 0.33637 | 0.33637 | 0.33637 | 0.33548 | 0.33254 | 0.32122 | 0.29493 | 0.33594 | 0.33594 | 0.33594 | 0.33594 | 0.33594 | 0.33594 | 0.33594 | 0.33504 | 0.33207 | 0.32059 | 0.2943 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31867 | 0.3174 | 0.30776 | 0.28738 | 0.29151 | 0.29151 | 0.29151 | 0.29151 | 0.29151 | 0.29151 | 0.29151 | 0.29151 | 0.29151 | 0.28873 | 0.27633
2005-08-13 01:08 | 0.35807 | 0.35807 | 0.35807 | 0.35807 | 0.35807 | 0.35807 | 0.35807 | 0.35712 | 0.35402 | 0.34203 | 0.31436 | 0.35761 | 0.35761 | 0.35761 | 0.35761 | 0.35761 | 0.35761 | 0.35761 | 0.35666 | 0.35352 | 0.34136 | 0.31368 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | 0.33933 | 0.338 | 0.32784 | 0.30643 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.30787 | 0.29493
2005-08-14 01:30 | 0.31923 | 0.31923 | 0.31923 | 0.31923 | 0.31923 | 0.31923 | 0.31923 | 0.31838 | 0.31563 | 0.30503 |  | 0.31882 | 0.31882 | 0.31882 | 0.31882 | 0.31882 | 0.31882 | 0.31882 | 0.31797 | 0.31519 | 0.30444 |  | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30264 | 0.30146 | 0.2925 |  | 0.27752 | 0.27752 | 0.27752 | 0.27752 | 0.27752 | 0.27752 | 0.27752 | 0.27752 | 0.27752 | 0.27498
2005-08-15 01:52 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33688 | 0.33398 | 0.32284 | 0.29676 | 0.33733 | 0.33733 | 0.33733 | 0.33733 | 0.33733 | 0.33733 | 0.33733 | 0.33644 | 0.33351 | 0.32222 | 0.29616 | 0.32135 | 0.32135 | 0.32135 | 0.32135 | 0.32135 | 0.32135 | 0.32135 | 0.32034 | 0.31911 | 0.30973 | 0.28943 | 0.29413 | 0.29413 | 0.29413 | 0.29413 | 0.29413 | 0.29413 | 0.29413 | 0.29413 | 0.29413 | 0.29147 | 0.27891
2005-08-16 02:15 | 0.35028 | 0.35028 | 0.35028 | 0.35028 | 0.35028 | 0.35028 | 0.35028 | 0.34937 | 0.34639 | 0.33493 |  | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34984 | 0.34892 | 0.34591 | 0.33428 |  | 0.33339 | 0.33339 | 0.33339 | 0.33339 | 0.33339 | 0.33339 | 0.33339 | 0.33234 | 0.33107 | 0.32145 |  | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30283 |  | 0.28697 | 0.28697 | 0.28697 | 0.28697 | 0.28697 | 0.28697 | 0.28697 | 0.28697 | 0.28697 | 0.28697 |  | 0.27193 | 0.27193 | 0.27193 | 0.27193 | 0.27193 | 0.27193 | 0.27193 | 0.27193 | 0.27193 | 0.27193 |  | 0.26853 | 0.26853 | 0.26853 | 0.26853 | 0.26853 | 0.26853 | 0.26853 | 0.26853 | 0.26853 | 0.26853
2005-08-17 01:36 | 0.32638 | 0.32638 | 0.32638 | 0.32638 | 0.32638 | 0.32638 | 0.32638 | 0.32554 | 0.32277 | 0.31216 | 0.28702 | 0.32598 | 0.32598 | 0.32598 | 0.32598 | 0.32598 | 0.32598 | 0.32598 | 0.32512 | 0.32233 | 0.31157 | 0.28642 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.30978 | 0.30862 | 0.29972 | 0.28008 | 0.28508 | 0.28508 | 0.28508 | 0.28508 | 0.28508 | 0.28508 | 0.28508 | 0.28508 | 0.28508 | 0.28263 | 0.27015 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.26825 | 0.25912 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25473 | 0.25006
2005-08-18 02:09 | 0.35521 | 0.35521 | 0.35521 | 0.35521 | 0.35521 | 0.35521 | 0.35521 | 0.35429 | 0.35131 | 0.33984 |  | 0.35477 | 0.35477 | 0.35477 | 0.35477 | 0.35477 | 0.35477 | 0.35477 | 0.35385 | 0.35083 | 0.3392 |  | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33728 | 0.33601 | 0.32645 |  | 0.31075 | 0.31075 | 0.31075 | 0.31075 | 0.31075 | 0.31075 | 0.31075 | 0.31075 | 0.31075 | 0.30813
2005-08-19 02:43 | 0.34425 | 0.34425 | 0.34425 | 0.34425 | 0.34425 | 0.34425 | 0.34425 | 0.34337 | 0.34049 | 0.32946 | 0.30296 | 0.34383 | 0.34383 | 0.34383 | 0.34383 | 0.34383 | 0.34383 | 0.34383 | 0.34294 | 0.34003 | 0.32885 | 0.30236 | 0.32799 | 0.32799 | 0.32799 | 0.32799 | 0.32799 | 0.32799 | 0.32799 | 0.327 | 0.32578 | 0.31661 | 0.29578 | 0.3016 | 0.3016 | 0.3016 | 0.3016 | 0.3016 | 0.3016 | 0.3016 | 0.3016 | 0.3016 | 0.29911 | 0.28561
2005-08-20 03:11 | 0.34044 | 0.34044 | 0.34044 | 0.34044 | 0.34044 | 0.34044 | 0.34044 | 0.33957 | 0.33675 | 0.32592 |  | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.33915 | 0.33629 | 0.32531 |  | 0.32447 | 0.32447 | 0.32447 | 0.32447 | 0.32447 | 0.32447 | 0.32447 | 0.32349 | 0.3223 | 0.31332 |  | 0.29871 | 0.29871 | 0.29871 | 0.29871 | 0.29871 | 0.29871 | 0.29871 | 0.29871 | 0.29871 | 0.29629 |  | 0.28031 | 0.28031 | 0.28031 | 0.28031 | 0.28031 | 0.28031 | 0.28031 | 0.28031 | 0.28031 | 0.28031
2005-08-21 03:34 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.33485 | 0.33207 | 0.32146 |  | 0.33528 | 0.33528 | 0.33528 | 0.33528 | 0.33528 | 0.33528 | 0.33528 | 0.33442 | 0.33162 | 0.32088 |  | 0.32005 | 0.32005 | 0.32005 | 0.32005 | 0.32005 | 0.32005 | 0.32005 | 0.31909 | 0.31794 | 0.30916 |  | 0.29494 | 0.29494 | 0.29494 | 0.29494 | 0.29494 | 0.29494 | 0.29494 | 0.29494 | 0.29494 | 0.2926
2005-08-22 03:56 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.33046 | 0.32775 |  |  | 0.33089 | 0.33089 | 0.33089 | 0.33089 | 0.33089 | 0.33089 | 0.33089 | 0.33006 | 0.3273 |  |  | 0.31597 | 0.31597 | 0.31597 | 0.31597 | 0.31597 | 0.31597 | 0.31597 | 0.31503 | 0.3139
2005-08-23 00:11 | 0.3464 | 0.3464 | 0.3464 | 0.3464 | 0.3464 | 0.3464 | 0.3464 | 0.34554 | 0.34271 | 0.33165 | 0.30476 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34511 | 0.34225 | 0.33105 | 0.30415 | 0.33047 | 0.33047 | 0.33047 | 0.33047 | 0.33047 | 0.33047 | 0.33047 | 0.32949 | 0.32831 | 0.31909 | 0.29769 | 0.30464 | 0.30464 | 0.30464 | 0.30464 | 0.30464 | 0.30464 | 0.30464 | 0.30464 | 0.30464 | 0.30224 | 0.28768
2005-08-24 00:45 | 0.34035 | 0.34035 | 0.34035 | 0.34035 | 0.34035 | 0.34035 | 0.34035 | 0.3395 | 0.33673 | 0.32595 |  | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33908 | 0.33628 | 0.32537 |  | 0.32479 | 0.32479 | 0.32479 | 0.32479 | 0.32479 | 0.32479 | 0.32479 | 0.32385 | 0.3227 | 0.31372 |  | 0.2997 | 0.2997 | 0.2997 | 0.2997 | 0.2997 | 0.2997 | 0.2997 | 0.2997 | 0.2997 | 0.29741
2005-08-25 01:19 | 0.35107 | 0.35107 | 0.35107 | 0.35107 | 0.35107 | 0.35107 | 0.35107 | 0.35019 | 0.34736 | 0.33631 |  | 0.35064 | 0.35064 | 0.35064 | 0.35064 | 0.35064 | 0.35064 | 0.35064 | 0.34977 | 0.3469 | 0.33571 |  | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33416 | 0.33298 | 0.32382
2005-08-26 01:36 | 0.35849 | 0.35849 | 0.35849 | 0.35849 | 0.35849 | 0.35849 | 0.35849 | 0.35761 | 0.35472 | 0.34352 |  | 0.35806 | 0.35806 | 0.35806 | 0.35806 | 0.35806 | 0.35806 | 0.35806 | 0.35716 | 0.35426 | 0.34292 |  | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34133 | 0.34015 | 0.33087
2005-08-27 02:15 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.3534 | 0.35254 | 0.34972 | 0.33874 | 0.31077 | 0.35298 | 0.35298 | 0.35298 | 0.35298 | 0.35298 | 0.35298 | 0.35298 | 0.35211 | 0.34926 | 0.33815 | 0.31018
2005-08-28 02:38 | 0.34567 | 0.34567 | 0.34567 | 0.34567 | 0.34567 | 0.34567 | 0.34567 | 0.34483 | 0.34208 |  |  | 0.34527 | 0.34527 | 0.34527 | 0.34527 | 0.34527 | 0.34527 | 0.34527 | 0.34441 | 0.34164 |  |  | 0.32999 | 0.32999 | 0.32999 | 0.32999 | 0.32999 | 0.32999 | 0.32999 | 0.32905 | 0.32791 |  |  | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427
2005-08-29 03:06 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.338 | 0.33533 | 0.32467 |  | 0.33842 | 0.33842 | 0.33842 | 0.33842 | 0.33842 | 0.33842 | 0.33842 | 0.3376 | 0.3349 | 0.32411 |  | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32355 | 0.32265 | 0.32154 | 0.31257 |  | 0.29862 | 0.29862 | 0.29862 | 0.29862 | 0.29862 | 0.29862 | 0.29862 | 0.29862 | 0.29862 | 0.29583
2005-08-30 01:30 | 0.34271 | 0.34271 | 0.34271 | 0.34271 | 0.34271 | 0.34271 | 0.34271 | 0.34188 | 0.33919 | 0.32848 | 0.30145 | 0.34231 | 0.34231 | 0.34231 | 0.34231 | 0.34231 | 0.34231 | 0.34231 | 0.34147 | 0.33876 | 0.32791 | 0.30086 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32736 | 0.32644 | 0.32533 | 0.31633 | 0.29401
2005-08-31 02:54 | 0.3571 | 0.3571 | 0.3571 | 0.3571 | 0.3571 | 0.3571 | 0.3571 | 0.35624 | 0.35346 |  |  | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35582 | 0.353 |  |  | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34026 | 0.33911 |  |  | 0.31492 | 0.31492 | 0.31492 | 0.31492 | 0.31492 | 0.31492 | 0.31492 | 0.31492 | 0.31492
2005-09-01 02:21 | 0.35068 | 0.35068 | 0.35068 | 0.35068 | 0.35068 | 0.35068 | 0.35068 | 0.34984 | 0.34711 | 0.33602 |  | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.34942 | 0.34668 | 0.33545 |  | 0.33517 | 0.33517 | 0.33517 | 0.33517 | 0.33517 | 0.33517 | 0.33517 | 0.33425 | 0.33313 | 0.32373
2005-09-02 02:43 | 0.33367 | 0.33367 | 0.33367 | 0.33367 | 0.33367 | 0.33367 | 0.33367 | 0.33288 | 0.3303 | 0.31982 | 0.29355 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33249 | 0.32988 | 0.31928 | 0.29299 | 0.31901 | 0.31901 | 0.31901 | 0.31901 | 0.31901 | 0.31901 | 0.31901 | 0.31814 | 0.31708 | 0.30821 | 0.28648 | 0.29443 | 0.29443 | 0.29443 | 0.29443 | 0.29443 | 0.29443 | 0.29443 | 0.29443 | 0.29443 | 0.29121 | 0.27643
2005-09-03 03:11 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32524 | 0.32274 | 0.31256 | 0.28717 | 0.32564 | 0.32564 | 0.32564 | 0.32564 | 0.32564 | 0.32564 | 0.32564 | 0.32486 | 0.32234 | 0.31203 | 0.28665 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31094 | 0.30991 | 0.30132 | 0.28038 | 0.28804 | 0.28804 | 0.28804 | 0.28804 | 0.28804 | 0.28804 | 0.28804 | 0.28804 | 0.28804 | 0.28492 | 0.27078 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.26726 | 0.25757
2005-09-04 03:34 | 0.32585 | 0.32585 | 0.32585 | 0.32585 | 0.32585 | 0.32585 | 0.32585 | 0.32509 | 0.3226 |  |  | 0.32549 | 0.32549 | 0.32549 | 0.32549 | 0.32549 | 0.32549 | 0.32549 | 0.32471 | 0.3222 |  |  | 0.31172 | 0.31172 | 0.31172 | 0.31172 | 0.31172 | 0.31172 | 0.31172 | 0.31088 | 0.30986
2005-09-05 03:56 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33022 | 0.32771 |  |  | 0.33062 | 0.33062 | 0.33062 | 0.33062 | 0.33062 | 0.33062 | 0.33062 | 0.32984 | 0.3273 |  |  | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31587 | 0.31486
2005-09-06 00:11 | 0.33855 | 0.33855 | 0.33855 | 0.33855 | 0.33855 | 0.33855 | 0.33855 |  |  |  |  | 0.33817 | 0.33817 | 0.33817 | 0.33817 | 0.33817 | 0.33817 | 0.33817
2005-09-07 00:45 | 0.32366 | 0.32366 | 0.32366 | 0.32366 | 0.32366 | 0.32366 | 0.32366 | 0.32272 | 0.32028 | 0.3099 |  | 0.32329 | 0.32329 | 0.32329 | 0.32329 | 0.32329 | 0.32329 | 0.32329 | 0.32235 | 0.31988 | 0.30938 |  | 0.3096 | 0.3096 | 0.3096 | 0.3096 | 0.3096 | 0.3096 | 0.3096 | 0.30878 | 0.30779 | 0.29886 |  | 0.28584 | 0.28584 | 0.28584 | 0.28584 | 0.28584 | 0.28584 | 0.28584 | 0.28584 | 0.28584 | 0.28281
2005-09-08 01:02 | 0.33942 | 0.33942 | 0.33942 | 0.33942 | 0.33942 | 0.33942 | 0.33942 | 0.33844 | 0.33589 | 0.32508 | 0.29873 | 0.33904 | 0.33904 | 0.33904 | 0.33904 | 0.33904 | 0.33904 | 0.33904 | 0.33806 | 0.33548 | 0.32454 | 0.29818 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32392 | 0.32288 | 0.31359 | 0.2918
2005-09-09 02:32 | 0.35272 | 0.35272 | 0.35272 | 0.35272 | 0.35272 | 0.35272 | 0.35272 | 0.35171 | 0.34908 | 0.33791 | 0.31082 | 0.35233 | 0.35233 | 0.35233 | 0.35233 | 0.35233 | 0.35233 | 0.35233 | 0.35131 | 0.34864 | 0.33735 | 0.31028 | 0.33759 | 0.33759 | 0.33759 | 0.33759 | 0.33759 | 0.33759 | 0.33759 | 0.3367 | 0.33565 | 0.32609 | 0.30374
2005-09-10 02:54 | 0.33752 | 0.33752 | 0.33752 | 0.33752 | 0.33752 | 0.33752 | 0.33752 | 0.33656 | 0.33405 | 0.32344 | 0.2978 | 0.33715 | 0.33715 | 0.33715 | 0.33715 | 0.33715 | 0.33715 | 0.33715 | 0.33618 | 0.33365 | 0.32291 | 0.29727 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.3223 | 0.32129 | 0.31221 | 0.29111 | 0.2981 | 0.2981 | 0.2981 | 0.2981 | 0.2981 | 0.2981 | 0.2981 | 0.2981 | 0.2981 | 0.29499 | 0.28016
2005-09-11 03:17 | 0.33702 | 0.33702 | 0.33702 | 0.33702 | 0.33702 | 0.33702 | 0.33702 | 0.33607 | 0.33357 | 0.32303 | 0.2977 | 0.33664 | 0.33664 | 0.33664 | 0.33664 | 0.33664 | 0.33664 | 0.33664 | 0.33569 | 0.33317 | 0.32251 | 0.29719 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.3219 | 0.3209 | 0.31192 | 0.29115
2005-09-12 03:34 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.33037 | 0.32793 | 0.31764 |  | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33094 | 0.33 | 0.32753 | 0.31712
2005-09-13 01:58 | 0.33821 | 0.33821 | 0.33821 | 0.33821 | 0.33821 | 0.33821 | 0.33821 | 0.33726 | 0.33479 | 0.32434 | 0.29894 | 0.33784 | 0.33784 | 0.33784 | 0.33784 | 0.33784 | 0.33784 | 0.33784 | 0.33689 | 0.33439 | 0.32383 | 0.29845 | 0.3238 | 0.3238 | 0.3238 | 0.3238 | 0.3238 | 0.3238 | 0.3238 | 0.32299 | 0.32199 | 0.31306 | 0.29248
2005-09-14 01:24 | 0.35406 | 0.35406 | 0.35406 | 0.35406 | 0.35406 | 0.35406 | 0.35406 | 0.35307 | 0.35048 | 0.33961 |  | 0.35368 | 0.35368 | 0.35368 | 0.35368 | 0.35368 | 0.35368 | 0.35368 | 0.35268 | 0.35007 | 0.33907 |  | 0.33906 | 0.33906 | 0.33906 | 0.33906 | 0.33906 | 0.33906 | 0.33906 | 0.3382 | 0.33716 | 0.32789
2005-09-15 01:41 | 0.3444 | 0.3444 | 0.3444 | 0.3444 | 0.3444 | 0.3444 | 0.3444 | 0.34344 | 0.34095 | 0.33044 | 0.30459 | 0.34403 | 0.34403 | 0.34403 | 0.34403 | 0.34403 | 0.34403 | 0.34403 | 0.34306 | 0.34055 | 0.32992 | 0.30407 | 0.3299 | 0.3299 | 0.3299 | 0.3299 | 0.3299 | 0.3299 | 0.3299 | 0.32907 | 0.32806 | 0.31911 | 0.29811 | 0.3039 | 0.3039 | 0.3039 | 0.3039 | 0.3039 | 0.3039 | 0.3039 | 0.3039 | 0.3039 | 0.30077 | 0.28597 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.28149 | 0.2717
2005-09-16 02:04 | 0.35995 | 0.35995 | 0.35995 | 0.35995 | 0.35995 | 0.35995 | 0.35995 | 0.35896 | 0.35636 |  |  | 0.35957 | 0.35957 | 0.35957 | 0.35957 | 0.35957 | 0.35957 | 0.35957 | 0.35857 | 0.35595 |  |  | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34403 | 0.34299 |  |  | 0.31799 | 0.31799 | 0.31799 | 0.31799 | 0.31799 | 0.31799 | 0.31799 | 0.31799 | 0.31799
2005-09-17 02:21 | 0.34997 | 0.34997 | 0.34997 | 0.34997 | 0.34997 | 0.34997 | 0.34997 | 0.34901 | 0.34649 | 0.33569 |  | 0.34959 | 0.34959 | 0.34959 | 0.34959 | 0.34959 | 0.34959 | 0.34959 | 0.34863 | 0.34609 | 0.33516 |  | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33458 | 0.33357 | 0.32429 |  | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30589
2005-09-18 02:43 | 0.31998 | 0.31998 | 0.31998 | 0.31998 | 0.31998 | 0.31998 | 0.31998 | 0.3191 | 0.31682 | 0.30699 |  | 0.31964 | 0.31964 | 0.31964 | 0.31964 | 0.31964 | 0.31964 | 0.31964 | 0.31876 | 0.31646 | 0.30652 |  | 0.30674 | 0.30674 | 0.30674 | 0.30674 | 0.30674 | 0.30674 | 0.30674 | 0.30598 | 0.30507 | 0.29665 |  | 0.2833 | 0.2833 | 0.2833 | 0.2833 | 0.2833 | 0.2833 | 0.2833 | 0.2833 | 0.2833 | 0.28003
2005-09-19 03:11 | 0.33075 | 0.33075 | 0.33075 | 0.33075 | 0.33075 | 0.33075 | 0.33075 | 0.32986 | 0.3275 | 0.31741 | 0.29238 | 0.3304 | 0.3304 | 0.3304 | 0.3304 | 0.3304 | 0.3304 | 0.3304 | 0.3295 | 0.32713 | 0.31692 | 0.29191 | 0.31714 | 0.31714 | 0.31714 | 0.31714 | 0.31714 | 0.31714 | 0.31714 | 0.31638 | 0.31544 | 0.30681 | 0.28626
2005-09-20 03:28 | 0.32876 | 0.32876 | 0.32876 | 0.32876 | 0.32876 | 0.32876 | 0.32876 | 0.32787 | 0.32555 | 0.31557 |  | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32752 | 0.32517 | 0.31509 |  | 0.31532 | 0.31532 | 0.31532 | 0.31532 | 0.31532 | 0.31532 | 0.31532 | 0.31455 | 0.31362 | 0.30512
2005-09-21 03:45 | 0.33963 | 0.33963 | 0.33963 | 0.33963 | 0.33963 | 0.33963 | 0.33963 | 0.33871 | 0.33633 | 0.32608 | 0.30039 | 0.33927 | 0.33927 | 0.33927 | 0.33927 | 0.33927 | 0.33927 | 0.33927 | 0.33835 | 0.33594 | 0.32558 | 0.29992 | 0.32582 | 0.32582 | 0.32582 | 0.32582 | 0.32582 | 0.32582 | 0.32582 | 0.32503 | 0.32408 | 0.31536 | 0.29421 | 0.30071 | 0.30071 | 0.30071 | 0.30071 | 0.30071 | 0.30071 | 0.30071 | 0.30071 | 0.30071 | 0.2973 | 0.28193
2005-09-22 03:17 | 0.3574 | 0.3574 | 0.3574 | 0.3574 | 0.3574 | 0.3574 | 0.3574 | 0.35644 | 0.35393 | 0.34322 |  | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35702 | 0.35606 | 0.35353 | 0.3427 |  | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34212 | 0.34113 | 0.33203
2005-09-23 03:45 | 0.3536 | 0.3536 | 0.3536 | 0.3536 | 0.3536 | 0.3536 | 0.3536 | 0.35266 | 0.3502 | 0.33965 |  | 0.35324 | 0.35324 | 0.35324 | 0.35324 | 0.35324 | 0.35324 | 0.35324 | 0.35229 | 0.3498 | 0.33914 |  | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33857 | 0.3376 | 0.32866 |  | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.31325 | 0.30974
2005-09-24 | 0.32636 | 0.32636 | 0.32636 | 0.32636 | 0.32636 | 0.32636 | 0.32636 | 0.3255 | 0.32323 | 0.31355 | 0.2887 | 0.32603 | 0.32603 | 0.32603 | 0.32603 | 0.32603 | 0.32603 | 0.32603 | 0.32515 | 0.32287 | 0.31309 | 0.28823 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.3133 | 0.31257 | 0.31167 | 0.30346 | 0.28285
2005-09-25 00:28 | 0.35545 | 0.35545 | 0.35545 | 0.35545 | 0.35545 | 0.35545 | 0.35545 | 0.35451 | 0.35205 | 0.34156 | 0.31475 | 0.35508 | 0.35508 | 0.35508 | 0.35508 | 0.35508 | 0.35508 | 0.35508 | 0.35413 | 0.35165 | 0.34106 | 0.31426 | 0.3413 | 0.3413 | 0.3413 | 0.3413 | 0.3413 | 0.3413 | 0.3413 | 0.3405 | 0.33953 | 0.33067 | 0.30847 | 0.31499 | 0.31499 | 0.31499 | 0.31499 | 0.31499 | 0.31499 | 0.31499 | 0.31499 | 0.31499 | 0.31152 | 0.29532
2005-09-26 00:56 | 0.34198 | 0.34198 | 0.34198 | 0.34198 | 0.34198 | 0.34198 | 0.34198 | 0.34108 | 0.33873 | 0.32871 |  | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34163 | 0.34072 | 0.33836 | 0.32821 |  | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32768 | 0.32676 | 0.31829 |  | 0.30336 | 0.30336 | 0.30336 | 0.30336 | 0.30336 | 0.30336 | 0.30336 | 0.30336 | 0.30336 | 0.30007
2005-09-27 01:24 | 0.359 | 0.359 | 0.359 | 0.359 | 0.359 | 0.359 | 0.359 | 0.35806 | 0.35561 | 0.34514 |  | 0.35864 | 0.35864 | 0.35864 | 0.35864 | 0.35864 | 0.35864 | 0.35864 | 0.35769 | 0.35521 | 0.34464 |  | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34407 | 0.34311 | 0.3343 |  | 0.3188 | 0.3188 | 0.3188 | 0.3188 | 0.3188 | 0.3188 | 0.3188 | 0.3188 | 0.3188 | 0.31537 |  | 0.29262 | 0.29262 | 0.29262 | 0.29262 | 0.29262 | 0.29262 | 0.29262 | 0.29262 | 0.29262 | 0.29262
2005-09-28 03:56 | 0.31741 | 0.31741 | 0.31741 | 0.31741 | 0.31741 | 0.31741 | 0.31741 | 0.31658 | 0.31442 | 0.30523 |  | 0.31709 | 0.31709 | 0.31709 | 0.31709 | 0.31709 | 0.31709 | 0.31709 | 0.31625 | 0.31408 | 0.30479 |  | 0.30499 | 0.30499 | 0.30499 | 0.30499 | 0.30499 | 0.30499 | 0.30499 | 0.30429 | 0.30345 | 0.29571
2005-09-29 00:11 | 0.32795 | 0.32795 | 0.32795 | 0.32795 | 0.32795 | 0.32795 | 0.32795 | 0.3271 | 0.32488 | 0.31542 | 0.29029 | 0.32762 | 0.32762 | 0.32762 | 0.32762 | 0.32762 | 0.32762 | 0.32762 | 0.32677 | 0.32452 | 0.31497 | 0.28983 | 0.31517 | 0.31517 | 0.31517 | 0.31517 | 0.31517 | 0.31517 | 0.31517 | 0.31446 | 0.31359 | 0.30566 | 0.28459
2005-09-30 00:34 | 0.32146 | 0.32146 | 0.32146 | 0.32146 | 0.32146 | 0.32146 | 0.32146 | 0.32063 | 0.31846 | 0.30924 | 0.28483 | 0.32114 | 0.32114 | 0.32114 | 0.32114 | 0.32114 | 0.32114 | 0.32114 | 0.3203 | 0.31811 | 0.30879 | 0.2844 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.3083 | 0.30745 | 0.29974 | 0.27932 | 0.2855 | 0.2855 | 0.2855 | 0.2855 | 0.2855 | 0.2855 | 0.2855 | 0.2855 | 0.2855 | 0.28249 | 0.26715
2005-10-01 00:56 | 0.33352 | 0.33352 | 0.33352 | 0.33352 | 0.33352 | 0.33352 | 0.33352 | 0.33266 | 0.33043 | 0.32091 |  | 0.33319 | 0.33319 | 0.33319 | 0.33319 | 0.33319 | 0.33319 | 0.33319 | 0.33232 | 0.33007 | 0.32045 |  | 0.32066 | 0.32066 | 0.32066 | 0.32066 | 0.32066 | 0.32066 | 0.32066 | 0.31994 | 0.31908 | 0.31112
2005-10-02 01:24 | 0.34902 | 0.34902 | 0.34902 | 0.34902 | 0.34902 | 0.34902 | 0.34902 | 0.34812 | 0.34579 | 0.33589 | 0.30942 | 0.34867 | 0.34867 | 0.34867 | 0.34867 | 0.34867 | 0.34867 | 0.34867 | 0.34777 | 0.34541 | 0.33542 | 0.30894 | 0.33564 | 0.33564 | 0.33564 | 0.33564 | 0.33564 | 0.33564 | 0.33564 | 0.33489 | 0.33398 | 0.32572 | 0.3035 | 0.31013 | 0.31013 | 0.31013 | 0.31013 | 0.31013 | 0.31013 | 0.31013 | 0.31013 | 0.31013 | 0.30689 | 0.29057 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.28481 | 0.27426
2005-10-03 01:52 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.33922 | 0.33697 | 0.32738 | 0.3018 | 0.33975 | 0.33975 | 0.33975 | 0.33975 | 0.33975 | 0.33975 | 0.33975 | 0.33888 | 0.3366 | 0.32691 | 0.30136 | 0.32712 | 0.32712 | 0.32712 | 0.32712 | 0.32712 | 0.32712 | 0.32712 | 0.32639 | 0.32552 | 0.31753 | 0.29613 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.30249 | 0.29939 | 0.28374
2005-10-04 02:15 | 0.33918 | 0.33918 | 0.33918 | 0.33918 | 0.33918 | 0.33918 | 0.33918 | 0.33833 | 0.33608 | 0.32657 |  | 0.33885 | 0.33885 | 0.33885 | 0.33885 | 0.33885 | 0.33885 | 0.33885 | 0.33799 | 0.33572 | 0.32611 |  | 0.32632 | 0.32632 | 0.32632 | 0.32632 | 0.32632 | 0.32632 | 0.32632 | 0.3256 | 0.32473 | 0.31683
2005-10-05 02:49 | 0.35063 | 0.35063 | 0.35063 | 0.35063 | 0.35063 | 0.35063 | 0.35063 | 0.34975 | 0.34744 | 0.33766 |  | 0.35029 | 0.35029 | 0.35029 | 0.35029 | 0.35029 | 0.35029 | 0.35029 | 0.3494 | 0.34708 | 0.33719 |  | 0.33741 | 0.33741 | 0.33741 | 0.33741 | 0.33741 | 0.33741 | 0.33741 | 0.33667 | 0.33577 | 0.32765 |  | 0.31202 | 0.31202 | 0.31202 | 0.31202 | 0.31202 | 0.31202 | 0.31202 | 0.31202 | 0.31202 | 0.30885 |  | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661
2005-10-06 03:17 | 0.34841 | 0.34841 | 0.34841 | 0.34841 | 0.34841 | 0.34841 | 0.34841 | 0.34753 | 0.34524 |  |  | 0.34806 | 0.34806 | 0.34806 | 0.34806 | 0.34806 | 0.34806 | 0.34806 | 0.34718 | 0.34488 |  |  | 0.33533 | 0.33533 | 0.33533 | 0.33533 | 0.33533 | 0.33533 | 0.33533 | 0.3346 | 0.33372
2005-10-07 03:39 | 0.32472 | 0.32472 | 0.32472 | 0.32472 | 0.32472 | 0.32472 | 0.32472 | 0.3239 | 0.32179 | 0.31261 |  | 0.3244 | 0.3244 | 0.3244 | 0.3244 | 0.3244 | 0.3244 | 0.3244 | 0.32358 | 0.32145 | 0.31218 |  | 0.3126 | 0.3126 | 0.3126 | 0.3126 | 0.3126 | 0.3126 | 0.3126 | 0.31192 | 0.3111 | 0.30342
2005-10-08 04:02 | 0.35073 | 0.35073 | 0.35073 | 0.35073 | 0.35073 | 0.35073 | 0.35073 | 0.34986 | 0.34758 | 0.33773 |  | 0.35039 | 0.35039 | 0.35039 | 0.35039 | 0.35039 | 0.35039 | 0.35039 | 0.34951 | 0.34722 | 0.33726 |  | 0.33771 | 0.33771 | 0.33771 | 0.33771 | 0.33771 | 0.33771 | 0.33771 | 0.33699 | 0.33611 | 0.32787 |  | 0.31209 | 0.31209 | 0.31209 | 0.31209 | 0.31209 | 0.31209 | 0.31209 | 0.31209 | 0.31209 | 0.30898 |  | 0.28718 | 0.28718 | 0.28718 | 0.28718 | 0.28718 | 0.28718 | 0.28718 | 0.28718 | 0.28718 | 0.28718 |  | 0.26787 | 0.26787 | 0.26787 | 0.26787 | 0.26787 | 0.26787 | 0.26787 | 0.26787 | 0.26787 | 0.26787
2005-10-09 00:28 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35321 | 0.35091 |  |  | 0.35375 | 0.35375 | 0.35375 | 0.35375 | 0.35375 | 0.35375 | 0.35375 | 0.35286 | 0.35055 |  |  | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34026 | 0.33938 |  |  | 0.31533 | 0.31533 | 0.31533 | 0.31533 | 0.31533 | 0.31533 | 0.31533 | 0.31533 | 0.31533
2005-10-10 00:51 | 0.32938 | 0.32938 | 0.32938 | 0.32938 | 0.32938 | 0.32938 | 0.32938 | 0.32857 | 0.32645 | 0.31708 | 0.29176 | 0.32907 | 0.32907 | 0.32907 | 0.32907 | 0.32907 | 0.32907 | 0.32907 | 0.32825 | 0.32611 | 0.31664 | 0.29134 | 0.31727 | 0.31727 | 0.31727 | 0.31727 | 0.31727 | 0.31727 | 0.31727 | 0.31659 | 0.31578 | 0.30786 | 0.28636
2005-10-11 01:24 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.3313 | 0.33049 | 0.32836 | 0.31898 | 0.29375 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33099 | 0.33017 | 0.32802 | 0.31855 | 0.29334 | 0.31918 | 0.31918 | 0.31918 | 0.31918 | 0.31918 | 0.31918 | 0.31918 | 0.3185 | 0.31769 | 0.30979 | 0.2884
2005-10-12 01:52 | 0.34536 | 0.34536 | 0.34536 | 0.34536 | 0.34536 | 0.34536 | 0.34536 | 0.34451 | 0.34231 | 0.33259 |  | 0.34503 | 0.34503 | 0.34503 | 0.34503 | 0.34503 | 0.34503 | 0.34503 | 0.34418 | 0.34196 | 0.33214 |  | 0.33279 | 0.33279 | 0.33279 | 0.33279 | 0.33279 | 0.33279 | 0.33279 | 0.33208 | 0.33124 | 0.32307 |  | 0.30754 | 0.30754 | 0.30754 | 0.30754 | 0.30754 | 0.30754 | 0.30754 | 0.30754 | 0.30754 | 0.30408 |  | 0.28296 | 0.28296 | 0.28296 | 0.28296 | 0.28296 | 0.28296 | 0.28296 | 0.28296 | 0.28296 | 0.28296 |  | 0.26451 | 0.26451 | 0.26451 | 0.26451 | 0.26451 | 0.26451 | 0.26451 | 0.26451 | 0.26451 | 0.26451
2005-10-13 02:21 | 0.34922 | 0.34922 | 0.34922 | 0.34922 | 0.34922 | 0.34922 | 0.34922 | 0.34837 | 0.34615 | 0.33636 | 0.30978 | 0.34889 | 0.34889 | 0.34889 | 0.34889 | 0.34889 | 0.34889 | 0.34889 | 0.34804 | 0.3458 | 0.33592 | 0.30935 | 0.33657 | 0.33657 | 0.33657 | 0.33657 | 0.33657 | 0.33657 | 0.33657 | 0.33587 | 0.33502 | 0.32681 | 0.30421
2005-10-14 02:54 | 0.35954 | 0.35954 | 0.35954 | 0.35954 | 0.35954 | 0.35954 | 0.35954 | 0.35866 | 0.35639 |  |  | 0.3592 | 0.3592 | 0.3592 | 0.3592 | 0.3592 | 0.3592 | 0.3592 | 0.35832 | 0.35603 |  |  | 0.34658 | 0.34658 | 0.34658 | 0.34658 | 0.34658 | 0.34658 | 0.34658 | 0.34586 | 0.345 |  |  | 0.32029 | 0.32029 | 0.32029 | 0.32029 | 0.32029 | 0.32029 | 0.32029 | 0.32029 | 0.32029
2005-10-15 03:39 | 0.33176 | 0.33176 | 0.33176 | 0.33176 | 0.33176 | 0.33176 | 0.33176 | 0.33096 | 0.32887 |  |  | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.33064 | 0.32854 |  |  | 0.31986 | 0.31986 | 0.31986 | 0.31986 | 0.31986 | 0.31986 | 0.31986 | 0.3192 | 0.3184
2005-10-16 00:06 | 0.35467 | 0.35467 | 0.35467 | 0.35467 | 0.35467 | 0.35467 | 0.35467 | 0.35382 | 0.35159 | 0.34139 | 0.31465 | 0.35434 | 0.35434 | 0.35434 | 0.35434 | 0.35434 | 0.35434 | 0.35434 | 0.35348 | 0.35124 | 0.34094 | 0.31422 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.34131 | 0.34046 | 0.33176 | 0.30908
2005-10-17 00:28 | 0.33957 | 0.33957 | 0.33957 | 0.33957 | 0.33957 | 0.33957 | 0.33957 | 0.33875 | 0.33663 |  |  | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33925 | 0.33843 | 0.33629 |  |  | 0.3275 | 0.3275 | 0.3275 | 0.3275 | 0.3275 | 0.3275 | 0.3275 | 0.32683 | 0.32603
2005-10-18 00:56 | 0.33582 | 0.33582 | 0.33582 | 0.33582 | 0.33582 | 0.33582 | 0.33582 | 0.33502 | 0.33293 | 0.32316 |  | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.3347 | 0.3326 | 0.32273 |  | 0.32395 | 0.32395 | 0.32395 | 0.32395 | 0.32395 | 0.32395 | 0.32395 | 0.32329 | 0.3225 | 0.3141 |  | 0.29904 | 0.29904 | 0.29904 | 0.29904 | 0.29904 | 0.29904 | 0.29904 | 0.29904 | 0.29904 | 0.29533 |  | 0.27522 | 0.27522 | 0.27522 | 0.27522 | 0.27522 | 0.27522 | 0.27522 | 0.27522 | 0.27522 | 0.27522
2005-10-19 00:22 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32314 | 0.32237 | 0.32037 | 0.31101 |  | 0.32284 | 0.32284 | 0.32284 | 0.32284 | 0.32284 | 0.32284 | 0.32284 | 0.32207 | 0.32005 | 0.31061 |  | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31177 | 0.31114 | 0.31038 | 0.30234 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.28445
2005-10-19 04:30 | 0.35887 | 0.35887 | 0.35887 | 0.35887 | 0.35887 | 0.35887 | 0.35887 | 0.35802 | 0.3558 | 0.34542 |  | 0.35854 | 0.35854 | 0.35854 | 0.35854 | 0.35854 | 0.35854 | 0.35854 | 0.35768 | 0.35544 | 0.34496 |  | 0.34625 | 0.34625 | 0.34625 | 0.34625 | 0.34625 | 0.34625 | 0.34625 | 0.34555 | 0.34471 | 0.3358
2005-10-20 00:51 | 0.3448 | 0.3448 | 0.3448 | 0.3448 | 0.3448 | 0.3448 | 0.3448 | 0.34398 | 0.34186 | 0.33193 | 0.30576 | 0.34448 | 0.34448 | 0.34448 | 0.34448 | 0.34448 | 0.34448 | 0.34448 | 0.34366 | 0.34152 | 0.33149 | 0.30534 | 0.33273 | 0.33273 | 0.33273 | 0.33273 | 0.33273 | 0.33273 | 0.33273 | 0.33206 | 0.33125 | 0.32275 | 0.30041
2005-10-21 01:19 | 0.34789 | 0.34789 | 0.34789 | 0.34789 | 0.34789 | 0.34789 | 0.34789 | 0.34707 | 0.34493 | 0.33496 |  | 0.34756 | 0.34756 | 0.34756 | 0.34756 | 0.34756 | 0.34756 | 0.34756 | 0.34674 | 0.34459 | 0.33452 |  | 0.33576 | 0.33576 | 0.33576 | 0.33576 | 0.33576 | 0.33576 | 0.33576 | 0.33509 | 0.33429 | 0.32575 |  | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30603
2005-10-22 01:47 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32989 | 0.32911 | 0.3271 | 0.31769 | 0.29268 | 0.32959 | 0.32959 | 0.32959 | 0.32959 | 0.32959 | 0.32959 | 0.32959 | 0.32881 | 0.32678 | 0.31728 | 0.29227
2005-10-23 02:21 | 0.34608 | 0.34608 | 0.34608 | 0.34608 | 0.34608 | 0.34608 | 0.34608 | 0.34527 | 0.34317 |  |  | 0.34576 | 0.34576 | 0.34576 | 0.34576 | 0.34576 | 0.34576 | 0.34576 | 0.34495 | 0.34283 |  |  | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.33326 | 0.33247 |  |  | 0.30835 | 0.30835 | 0.30835 | 0.30835 | 0.30835 | 0.30835 | 0.30835 | 0.30835 | 0.30835
2005-10-24 02:49 | 0.32026 | 0.32026 | 0.32026 | 0.32026 | 0.32026 | 0.32026 | 0.32026 | 0.31951 | 0.31758 | 0.30834 |  | 0.31997 | 0.31997 | 0.31997 | 0.31997 | 0.31997 | 0.31997 | 0.31997 | 0.31922 | 0.31727 | 0.30795 |  | 0.30906 | 0.30906 | 0.30906 | 0.30906 | 0.30906 | 0.30906 | 0.30906 | 0.30846 | 0.30773 | 0.29973 |  | 0.28559 | 0.28559 | 0.28559 | 0.28559 | 0.28559 | 0.28559 | 0.28559 | 0.28559 | 0.28559 | 0.28177
2005-10-25 03:28 | 0.35951 | 0.35951 | 0.35951 | 0.35951 | 0.35951 | 0.35951 | 0.35951 | 0.35868 | 0.35651 | 0.34619 |  | 0.35919 | 0.35919 | 0.35919 | 0.35919 | 0.35919 | 0.35919 | 0.35919 | 0.35835 | 0.35616 | 0.34575 |  | 0.34701 | 0.34701 | 0.34701 | 0.34701 | 0.34701 | 0.34701 | 0.34701 | 0.34632 | 0.34551 | 0.33659 |  | 0.32086 | 0.32086 | 0.32086 | 0.32086 | 0.32086 | 0.32086 | 0.32086 | 0.32086 | 0.32086 | 0.31662
2005-10-26 03:51 | 0.34341 | 0.34341 | 0.34341 | 0.34341 | 0.34341 | 0.34341 | 0.34341 | 0.34262 | 0.34056 | 0.33075 |  | 0.3431 | 0.3431 | 0.3431 | 0.3431 | 0.3431 | 0.3431 | 0.3431 | 0.3423 | 0.34023 | 0.33033 |  | 0.33153 | 0.33153 | 0.33153 | 0.33153 | 0.33153 | 0.33153 | 0.33153 | 0.33088 | 0.3301 | 0.32164
2005-10-27 00:34 | 0.3489 | 0.3489 | 0.3489 | 0.3489 | 0.3489 | 0.3489 | 0.3489 | 0.34809 | 0.34601 | 0.33608 | 0.30929 | 0.34859 | 0.34859 | 0.34859 | 0.34859 | 0.34859 | 0.34859 | 0.34859 | 0.34778 | 0.34567 | 0.33566 | 0.30887 | 0.33687 | 0.33687 | 0.33687 | 0.33687 | 0.33687 | 0.33687 | 0.33687 | 0.33622 | 0.33544 | 0.32688 | 0.30355
2005-10-28 01:08 | 0.31721 | 0.31721 | 0.31721 | 0.31721 | 0.31721 | 0.31721 | 0.31721 | 0.31649 | 0.3146 |  |  | 0.31693 | 0.31693 | 0.31693 | 0.31693 | 0.31693 | 0.31693 | 0.31693 | 0.3162 | 0.3143 |  |  | 0.30634 | 0.30634 | 0.30634 | 0.30634 | 0.30634 | 0.30634 | 0.30634 | 0.30574 | 0.30503
2005-10-29 01:47 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34058 | 0.33856 | 0.32874 | 0.30275 | 0.34106 | 0.34106 | 0.34106 | 0.34106 | 0.34106 | 0.34106 | 0.34106 | 0.34027 | 0.33823 | 0.32833 | 0.30235 | 0.3297 | 0.3297 | 0.3297 | 0.3297 | 0.3297 | 0.3297 | 0.3297 | 0.32907 | 0.32831 | 0.31979 | 0.29719
2005-10-30 02:15 | 0.34496 | 0.34496 | 0.34496 | 0.34496 | 0.34496 | 0.34496 | 0.34496 | 0.34419 | 0.34215 |  |  | 0.34466 | 0.34466 | 0.34466 | 0.34466 | 0.34466 | 0.34466 | 0.34466 | 0.34388 | 0.34182 |  |  | 0.33324 | 0.33324 | 0.33324 | 0.33324 | 0.33324 | 0.33324 | 0.33324 | 0.33261 | 0.33184
2005-10-31 02:43 | 0.33911 | 0.33911 | 0.33911 | 0.33911 | 0.33911 | 0.33911 | 0.33911 | 0.33835 | 0.33636 | 0.32649 | 0.30089 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33882 | 0.33804 | 0.33604 | 0.32609 | 0.3005
2005-11-01 03:22 | 0.33129 | 0.33129 | 0.33129 | 0.33129 | 0.33129 | 0.33129 | 0.33129 | 0.33054 | 0.3286 | 0.31902 |  | 0.331 | 0.331 | 0.331 | 0.331 | 0.331 | 0.331 | 0.331 | 0.33025 | 0.32829 | 0.31862 |  | 0.31994 | 0.31994 | 0.31994 | 0.31994 | 0.31994 | 0.31994 | 0.31994 | 0.31934 | 0.31861 | 0.3102
2005-11-02 03:51 | 0.32871 | 0.32871 | 0.32871 | 0.32871 | 0.32871 | 0.32871 | 0.32871 | 0.32797 | 0.32606 | 0.3166 | 0.29179 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32842 | 0.32768 | 0.32575 | 0.3162 | 0.29142 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31691 | 0.31619 | 0.30789 | 0.28614
2005-11-03 00:17 | 0.33497 | 0.33497 | 0.33497 | 0.33497 | 0.33497 | 0.33497 | 0.33497 | 0.33422 | 0.33227 | 0.32267 |  | 0.33467 | 0.33467 | 0.33467 | 0.33467 | 0.33467 | 0.33467 | 0.33467 | 0.33392 | 0.33196 | 0.32227 |  | 0.32359 | 0.32359 | 0.32359 | 0.32359 | 0.32359 | 0.32359 | 0.32359 | 0.32299 | 0.32225 | 0.31384 |  | 0.2982 | 0.2982 | 0.2982 | 0.2982 | 0.2982 | 0.2982 | 0.2982 | 0.2982 | 0.2982 | 0.29431
2005-11-04 00:45 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32793 | 0.32603 |  |  | 0.32837 | 0.32837 | 0.32837 | 0.32837 | 0.32837 | 0.32837 | 0.32837 | 0.32764 | 0.32572 |  |  | 0.31755 | 0.31755 | 0.31755 | 0.31755 | 0.31755 | 0.31755 | 0.31755 | 0.31696 | 0.31624
2005-11-05 01:19 | 0.33902 | 0.33902 | 0.33902 | 0.33902 | 0.33902 | 0.33902 | 0.33902 | 0.33827 | 0.33632 |  |  | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33798 | 0.33601 |  |  | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32701 | 0.32628
2005-11-06 01:41 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.32968 | 0.32779 | 0.31806 |  | 0.33013 | 0.33013 | 0.33013 | 0.33013 | 0.33013 | 0.33013 | 0.33013 | 0.32939 | 0.32749 | 0.31767 |  | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31935 | 0.31876 | 0.31805 | 0.30943
2005-11-07 02:09 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34545 | 0.34347 |  |  | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34514 | 0.34315 |  |  | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33466 | 0.33405 | 0.33332
2005-11-08 03:17 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34356 | 0.3416 | 0.33136 | 0.30521 | 0.34402 | 0.34402 | 0.34402 | 0.34402 | 0.34402 | 0.34402 | 0.34402 | 0.34326 | 0.34129 | 0.33096 | 0.30481 | 0.33288 | 0.33288 | 0.33288 | 0.33288 | 0.33288 | 0.33288 | 0.33288 | 0.33228 | 0.33155 | 0.32241 | 0.29935 | 0.30624 | 0.30624 | 0.30624 | 0.30624 | 0.30624 | 0.30624 | 0.30624 | 0.30624 | 0.30624 | 0.30229 | 0.2834 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.28037 | 0.26734
2005-11-09 03:51 | 0.31429 | 0.31429 | 0.31429 | 0.31429 | 0.31429 | 0.31429 | 0.31429 | 0.3136 | 0.31183 |  |  | 0.31402 | 0.31402 | 0.31402 | 0.31402 | 0.31402 | 0.31402 | 0.31402 | 0.31333 | 0.31154 |  |  | 0.30391 | 0.30391 | 0.30391 | 0.30391 | 0.30391 | 0.30391 | 0.30391 | 0.30335 | 0.30269
2005-11-10 00:17 | 0.34451 | 0.34451 | 0.34451 | 0.34451 | 0.34451 | 0.34451 | 0.34451 | 0.34376 | 0.34181 | 0.33149 |  | 0.34421 | 0.34421 | 0.34421 | 0.34421 | 0.34421 | 0.34421 | 0.34421 | 0.34346 | 0.3415 | 0.33109 |  | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33316 | 0.33257 | 0.33184 | 0.3226 |  | 0.30657 | 0.30657 | 0.30657 | 0.30657 | 0.30657 | 0.30657 | 0.30657 | 0.30657 | 0.30657 | 0.30266
2005-11-11 00:45 | 0.33462 | 0.33462 | 0.33462 | 0.33462 | 0.33462 | 0.33462 | 0.33462 | 0.33389 | 0.33201 | 0.32203 |  | 0.33434 | 0.33434 | 0.33434 | 0.33434 | 0.33434 | 0.33434 | 0.33434 | 0.33361 | 0.33171 | 0.32165 |  | 0.32365 | 0.32365 | 0.32365 | 0.32365 | 0.32365 | 0.32365 | 0.32365 | 0.32307 | 0.32237 | 0.31344 |  | 0.298 | 0.298 | 0.298 | 0.298 | 0.298 | 0.298 | 0.298 | 0.298 | 0.298 | 0.29425 |  | 0.27293 | 0.27293 | 0.27293 | 0.27293 | 0.27293 | 0.27293 | 0.27293 | 0.27293 | 0.27293 | 0.27293
2005-11-12 01:24 | 0.31899 | 0.31899 | 0.31899 | 0.31899 | 0.31899 | 0.31899 | 0.31899 | 0.3183 | 0.31651 | 0.30705 |  | 0.31872 | 0.31872 | 0.31872 | 0.31872 | 0.31872 | 0.31872 | 0.31872 | 0.31803 | 0.31622 | 0.30667 |  | 0.30857 | 0.30857 | 0.30857 | 0.30857 | 0.30857 | 0.30857 | 0.30857 | 0.30803 | 0.30736 | 0.29891
2005-11-13 01:52 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34767 | 0.34573 |  |  | 0.34813 | 0.34813 | 0.34813 | 0.34813 | 0.34813 | 0.34813 | 0.34813 | 0.34738 | 0.34542 |  |  | 0.3371 | 0.3371 | 0.3371 | 0.3371 | 0.3371 | 0.3371 | 0.3371 | 0.3365 | 0.33578
2005-11-14 02:15 | 0.31427 | 0.31427 | 0.31427 | 0.31427 | 0.31427 | 0.31427 | 0.31427 | 0.3136 | 0.31185 |  |  | 0.31401 | 0.31401 | 0.31401 | 0.31401 | 0.31401 | 0.31401 | 0.31401 | 0.31334 | 0.31157 |  |  | 0.30411 | 0.30411 | 0.30411 | 0.30411 | 0.30411 | 0.30411 | 0.30411 | 0.30357 | 0.30293
2005-11-15 01:41 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32052 | 0.31875 |  |  | 0.32095 | 0.32095 | 0.32095 | 0.32095 | 0.32095 | 0.32095 | 0.32095 | 0.32025 | 0.31847 |  |  | 0.31087 | 0.31087 | 0.31087 | 0.31087 | 0.31087 | 0.31087 | 0.31087 | 0.31032 | 0.30966
2005-11-16 02:21 | 0.35581 | 0.35581 | 0.35581 | 0.35581 | 0.35581 | 0.35581 | 0.35581 | 0.35505 | 0.35308 | 0.34213 |  | 0.35551 | 0.35551 | 0.35551 | 0.35551 | 0.35551 | 0.35551 | 0.35551 | 0.35475 | 0.35277 | 0.34172 |  | 0.34439 | 0.34439 | 0.34439 | 0.34439 | 0.34439 | 0.34439 | 0.34439 | 0.3438 | 0.34307 | 0.33312
2005-11-17 01:47 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32786 | 0.32716 | 0.32536 | 0.31531 | 0.28994 | 0.32759 | 0.32759 | 0.32759 | 0.32759 | 0.32759 | 0.32759 | 0.32759 | 0.32689 | 0.32508 | 0.31493 | 0.28957 | 0.31739 | 0.31739 | 0.31739 | 0.31739 | 0.31739 | 0.31739 | 0.31739 | 0.31684 | 0.31617 | 0.30705 | 0.28445
2005-11-18 02:26 | 0.33981 | 0.33981 | 0.33981 | 0.33981 | 0.33981 | 0.33981 | 0.33981 | 0.33909 | 0.33723 |  |  | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33953 | 0.33881 | 0.33693 |  |  | 0.329 | 0.329 | 0.329 | 0.329 | 0.329 | 0.329 | 0.329 | 0.32843 | 0.32775
2005-11-19 03:00 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.3083 |  |  |  | 0.3087 | 0.3087 | 0.3087 | 0.3087 | 0.3087 | 0.3087 | 0.3087 | 0.30805
2005-11-20 03:28 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.33041 | 0.32972 | 0.32778 | 0.31756 | 0.29221 | 0.33014 | 0.33014 | 0.33014 | 0.33014 | 0.33014 | 0.33014 | 0.33014 | 0.32945 | 0.3275 | 0.31719 | 0.29184
2005-11-21 03:51 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34403 | 0.34202 | 0.33141 |  | 0.34447 | 0.34447 | 0.34447 | 0.34447 | 0.34447 | 0.34447 | 0.34447 | 0.34375 | 0.34172 | 0.33102
2005-11-22 00:34 | 0.32356 | 0.32356 | 0.32356 | 0.32356 | 0.32356 | 0.32356 | 0.32356 | 0.32288 | 0.321 | 0.31107 | 0.28629 | 0.3233 | 0.3233 | 0.3233 | 0.3233 | 0.3233 | 0.3233 | 0.3233 | 0.32262 | 0.32072 | 0.31071 | 0.28594 | 0.31295 | 0.31295 | 0.31295 | 0.31295 | 0.31295 | 0.31295 | 0.31295 | 0.31241 | 0.31176 | 0.30266 | 0.28058
2005-11-23 00:56 | 0.34972 | 0.34972 | 0.34972 | 0.34972 | 0.34972 | 0.34972 | 0.34972 | 0.34899 |  |  |  | 0.34944 | 0.34944 | 0.34944 | 0.34944 | 0.34944 | 0.34944 | 0.34944 | 0.34871
2005-11-24 01:36 | 0.3401 | 0.3401 | 0.3401 | 0.3401 | 0.3401 | 0.3401 | 0.3401 | 0.3394 | 0.33728 |  |  | 0.33983 | 0.33983 | 0.33983 | 0.33983 | 0.33983 | 0.33983 | 0.33983 | 0.33912 | 0.33699 |  |  | 0.32887 | 0.32887 | 0.32887 | 0.32887 | 0.32887 | 0.32887 | 0.32887 | 0.32831 | 0.32763
2005-11-25 01:58 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35528 | 0.35309 |  |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35499 | 0.35278 |  |  | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34431 | 0.34372 | 0.34302
2005-11-26 02:26 | 0.35566 | 0.35566 | 0.35566 | 0.35566 | 0.35566 | 0.35566 | 0.35566 | 0.35493 |  |  |  | 0.35537 | 0.35537 | 0.35537 | 0.35537 | 0.35537 | 0.35537 | 0.35537 | 0.35464 |  |  |  | 0.34401 | 0.34401 | 0.34401 | 0.34401 | 0.34401 | 0.34401 | 0.34401 | 0.34343
2005-11-27 02:49 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32838 | 0.32771 | 0.32556 | 0.31527 | 0.29035 | 0.32812 | 0.32812 | 0.32812 | 0.32812 | 0.32812 | 0.32812 | 0.32812 | 0.32745 | 0.32528 | 0.3149 | 0.28999
2005-11-28 03:22 | 0.30636 | 0.30636 | 0.30636 | 0.30636 | 0.30636 | 0.30636 | 0.30636 | 0.30574 |  |  |  | 0.30611 | 0.30611 | 0.30611 | 0.30611 | 0.30611 | 0.30611 | 0.30611 | 0.30549 |  |  |  | 0.29626 | 0.29626 | 0.29626 | 0.29626 | 0.29626 | 0.29626 | 0.29626 | 0.29575
2005-11-29 04:02 | 0.33939 | 0.33939 | 0.33939 | 0.33939 | 0.33939 | 0.33939 | 0.33939 | 0.3387 | 0.33635 | 0.32577 |  | 0.33912 | 0.33912 | 0.33912 | 0.33912 | 0.33912 | 0.33912 | 0.33912 | 0.33843 | 0.33606 | 0.32539
2005-11-30 00:34 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.35458 | 0.35213 |  |  | 0.35502 | 0.35502 | 0.35502 | 0.35502 | 0.35502 | 0.35502 | 0.35502 | 0.3543 | 0.35183
2005-12-01 04:19 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.33832 | 0.33599 | 0.3253 |  | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33873 | 0.33805 | 0.3357 | 0.32493 |  | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32761 | 0.32707 | 0.32604 | 0.31622
2005-12-02 00:51 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33216 | 0.32989 | 0.31943 | 0.29409 | 0.33257 | 0.33257 | 0.33257 | 0.33257 | 0.33257 | 0.33257 | 0.33257 | 0.3319 | 0.32961 | 0.31907 | 0.29373
2005-12-03 01:13 | 0.34108 | 0.34108 | 0.34108 | 0.34108 | 0.34108 | 0.34108 | 0.34108 | 0.3404 | 0.33807 |  |  | 0.34081 | 0.34081 | 0.34081 | 0.34081 | 0.34081 | 0.34081 | 0.34081 | 0.34013 | 0.33779 |  |  | 0.32954 | 0.32954 | 0.32954 | 0.32954 | 0.32954 | 0.32954 | 0.32954 | 0.32899 | 0.32796
2005-12-04 01:41 | 0.3518 | 0.3518 | 0.3518 | 0.3518 | 0.3518 | 0.3518 | 0.3518 | 0.3511 | 0.34871 |  |  | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35082 | 0.34841 |  |  | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33994 | 0.33938 | 0.33833
2005-12-05 02:09 | 0.35574 | 0.35574 | 0.35574 | 0.35574 | 0.35574 | 0.35574 | 0.35574 | 0.35504 | 0.35263 |  |  | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35476 | 0.35233
2005-12-06 02:43 | 0.34146 | 0.34146 | 0.34146 | 0.34146 | 0.34146 | 0.34146 | 0.34146 | 0.34078 | 0.33848 | 0.32739 |  | 0.3412 | 0.3412 | 0.3412 | 0.3412 | 0.3412 | 0.3412 | 0.3412 | 0.34052 | 0.3382 | 0.32702
2005-12-07 03:11 | 0.3264 | 0.3264 | 0.3264 | 0.3264 | 0.3264 | 0.3264 | 0.3264 | 0.32577 | 0.32357 | 0.31301 |  | 0.32616 | 0.32616 | 0.32616 | 0.32616 | 0.32616 | 0.32616 | 0.32616 | 0.32551 | 0.3233 | 0.31266 |  | 0.31521 | 0.31521 | 0.31521 | 0.31521 | 0.31521 | 0.31521 | 0.31521 | 0.31469 | 0.31372 | 0.30398
2005-12-08 03:39 | 0.32581 | 0.32581 | 0.32581 | 0.32581 | 0.32581 | 0.32581 | 0.32581 | 0.32517 | 0.32299 |  |  | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32492 | 0.32272 |  |  | 0.31468 | 0.31468 | 0.31468 | 0.31468 | 0.31468 | 0.31468 | 0.31468 | 0.31417 | 0.3132
2005-12-09 00:17 | 0.3206 | 0.3206 | 0.3206 | 0.3206 | 0.3206 | 0.3206 | 0.3206 | 0.31997 | 0.31783 |  |  | 0.32035 | 0.32035 | 0.32035 | 0.32035 | 0.32035 | 0.32035 | 0.32035 | 0.31972 | 0.31757 |  |  | 0.30968 | 0.30968 | 0.30968 | 0.30968 | 0.30968 | 0.30968 | 0.30968 | 0.30917 | 0.30823
2005-12-10 00:45 | 0.35896 | 0.35896 | 0.35896 | 0.35896 | 0.35896 | 0.35896 | 0.35896 | 0.35826 | 0.35588 | 0.34406 | 0.3166 | 0.35869 | 0.35869 | 0.35869 | 0.35869 | 0.35869 | 0.35869 | 0.35869 | 0.35799 | 0.35558 | 0.34367 | 0.31623
2005-12-11 01:08 | 0.35176 | 0.35176 | 0.35176 | 0.35176 | 0.35176 | 0.35176 | 0.35176 | 0.35108 | 0.34875 |  |  | 0.3515 | 0.3515 | 0.3515 | 0.3515 | 0.3515 | 0.3515 | 0.3515 | 0.35081 | 0.34847 |  |  | 0.33971 | 0.33971 | 0.33971 | 0.33971 | 0.33971 | 0.33971 | 0.33971 | 0.33916 | 0.33813 |  |  | 0.31003 | 0.31003 | 0.31003 | 0.31003 | 0.31003 | 0.31003 | 0.31003 | 0.31003 | 0.31003
2005-12-12 01:41 | 0.32997 | 0.32997 | 0.32997 | 0.32997 | 0.32997 | 0.32997 | 0.32997 | 0.32933 | 0.32716 | 0.31621 |  | 0.32973 | 0.32973 | 0.32973 | 0.32973 | 0.32973 | 0.32973 | 0.32973 | 0.32908 | 0.32689 | 0.31586
2005-12-13 02:15 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32477 | 0.32415 | 0.32201 |  |  | 0.32453 | 0.32453 | 0.32453 | 0.32453 | 0.32453 | 0.32453 | 0.32453 | 0.3239 | 0.32175 |  |  | 0.31357 | 0.31357 | 0.31357 | 0.31357 | 0.31357 | 0.31357 | 0.31357 | 0.31306 | 0.31211
2005-12-14 02:54 | 0.35715 | 0.35715 | 0.35715 | 0.35715 | 0.35715 | 0.35715 | 0.35715 | 0.35646 |  |  |  | 0.35688 | 0.35688 | 0.35688 | 0.35688 | 0.35688 | 0.35688 | 0.35688 | 0.35619 |  |  |  | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34432
2005-12-15 03:22 | 0.33754 | 0.33754 | 0.33754 | 0.33754 | 0.33754 | 0.33754 | 0.33754 | 0.3369 | 0.33456 |  |  | 0.33729 | 0.33729 | 0.33729 | 0.33729 | 0.33729 | 0.33729 | 0.33729 | 0.33664 | 0.33429 |  |  | 0.32599 | 0.32599 | 0.32599 | 0.32599 | 0.32599 | 0.32599 | 0.32599 | 0.32547 | 0.32432
2005-12-16 03:56 | 0.32183 | 0.32183 | 0.32183 | 0.32183 | 0.32183 | 0.32183 | 0.32183 | 0.32122 | 0.319 | 0.30813 | 0.28357 | 0.3216 | 0.3216 | 0.3216 | 0.3216 | 0.3216 | 0.3216 | 0.3216 | 0.32098 | 0.31874 | 0.30778 | 0.28322
2005-12-17 00:28 | 0.34455 | 0.34455 | 0.34455 | 0.34455 | 0.34455 | 0.34455 | 0.34455 | 0.34389 | 0.34152 | 0.32992 |  | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.34364 | 0.34125 | 0.32956
2005-12-18 00:56 | 0.3491 | 0.3491 | 0.3491 | 0.3491 | 0.3491 | 0.3491 | 0.3491 | 0.34844 | 0.34604 |  |  | 0.34885 | 0.34885 | 0.34885 | 0.34885 | 0.34885 | 0.34885 | 0.34885 | 0.34818 | 0.34577 |  |  | 0.33698 | 0.33698 | 0.33698 | 0.33698 | 0.33698 | 0.33698 | 0.33698 | 0.33644 | 0.33525
2005-12-19 01:24 | 0.33108 | 0.33108 | 0.33108 | 0.33108 | 0.33108 | 0.33108 | 0.33108 | 0.33045 | 0.32819 | 0.31696 | 0.29169 | 0.33084 | 0.33084 | 0.33084 | 0.33084 | 0.33084 | 0.33084 | 0.33084 | 0.33021 | 0.32793 | 0.31661 | 0.29135 | 0.31962 | 0.31962 | 0.31962 | 0.31962 | 0.31962 | 0.31962 | 0.31962 | 0.31911 | 0.318 | 0.30721 | 0.28464
2005-12-20 01:47 | 0.31897 | 0.31897 | 0.31897 | 0.31897 | 0.31897 | 0.31897 | 0.31897 | 0.31837 | 0.31619 | 0.30543 |  | 0.31874 | 0.31874 | 0.31874 | 0.31874 | 0.31874 | 0.31874 | 0.31874 | 0.31813 | 0.31594 | 0.30509
2005-12-21 02:15 | 0.35193 | 0.35193 | 0.35193 | 0.35193 | 0.35193 | 0.35193 | 0.35193 | 0.35128 | 0.34889 | 0.33705 | 0.31021 | 0.35168 | 0.35168 | 0.35168 | 0.35168 | 0.35168 | 0.35168 | 0.35168 | 0.35102 | 0.34861 | 0.33668 | 0.30984
2005-12-22 02:43 | 0.34835 | 0.34835 | 0.34835 | 0.34835 | 0.34835 | 0.34835 | 0.34835 | 0.3477 | 0.34534 | 0.33368 |  | 0.3481 | 0.3481 | 0.3481 | 0.3481 | 0.3481 | 0.3481 | 0.3481 | 0.34744 | 0.34507 | 0.33331
2005-12-23 03:11 | 0.33491 | 0.33491 | 0.33491 | 0.33491 | 0.33491 | 0.33491 | 0.33491 | 0.33428 | 0.33203
2005-12-24 03:39 | 0.34636 | 0.34636 | 0.34636 | 0.34636 | 0.34636 | 0.34636 | 0.34636 | 0.34571 | 0.34339 | 0.33171 |  | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34598 | 0.34533 | 0.34298 | 0.33135
2005-12-25 04:02 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32322 | 0.32105 | 0.31018 |  | 0.32347 | 0.32347 | 0.32347 | 0.32347 | 0.32347 | 0.32347 | 0.32347 | 0.32287 | 0.32068 | 0.30985 |  | 0.3121 | 0.3121 | 0.3121 | 0.3121 | 0.3121 | 0.3121 | 0.3121 | 0.31161 | 0.31052 | 0.30004
2005-12-26 00:22 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35209 | 0.35144 | 0.34909 | 0.3373 |  | 0.35171 | 0.35171 | 0.35171 | 0.35171 | 0.35171 | 0.35171 | 0.35171 | 0.35105 | 0.34868 | 0.33694 |  | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33938 | 0.33884 | 0.33767 | 0.32634
2005-12-27 00:51 | 0.32791 | 0.32791 | 0.32791 | 0.32791 | 0.32791 | 0.32791 | 0.32791 | 0.3273 | 0.32512 |  |  | 0.32756 | 0.32756 | 0.32756 | 0.32756 | 0.32756 | 0.32756 | 0.32756 | 0.32695 | 0.32474 |  |  | 0.31612 | 0.31612 | 0.31612 | 0.31612 | 0.31612 | 0.31612 | 0.31612 | 0.31562 | 0.31453
2005-12-28 01:24 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32232 | 0.32018 |  |  | 0.32257 | 0.32257 | 0.32257 | 0.32257 | 0.32257 | 0.32257 | 0.32257 | 0.32197 | 0.31981
2005-12-29 01:13 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.3553 | 0.35466 | 0.35231 | 0.3402 |  | 0.35493 | 0.35493 | 0.35493 | 0.35493 | 0.35493 | 0.35493 | 0.35493 | 0.35427 | 0.3519 | 0.33984 |  | 0.34247 | 0.34247 | 0.34247 | 0.34247 | 0.34247 | 0.34247 | 0.34247 | 0.34193 | 0.34076 | 0.3292
2005-12-30 00:39 | 0.33349 | 0.33349 | 0.33349 | 0.33349 | 0.33349 | 0.33349 | 0.33349 | 0.33288 | 0.33068 | 0.31937 | 0.29336 | 0.33313 | 0.33313 | 0.33313 | 0.33313 | 0.33313 | 0.33313 | 0.33313 | 0.33252 | 0.3303 | 0.31903 | 0.29303
2005-12-31 00:34 | 0.32982 | 0.32982 | 0.32982 | 0.32982 | 0.32982 | 0.32982 | 0.32982 | 0.32922 | 0.32705 | 0.31591 |  | 0.32947 | 0.32947 | 0.32947 | 0.32947 | 0.32947 | 0.32947 | 0.32947 | 0.32886 | 0.32667 | 0.31558 |  | 0.31783 | 0.31783 | 0.31783 | 0.31783 | 0.31783 | 0.31783 | 0.31783 | 0.31734 | 0.31625 | 0.30559
2006-01-01 01:02 | 0.34211 | 0.34211 | 0.34211 | 0.34211 | 0.34211 | 0.34211 | 0.34211 | 0.34149 | 0.33925 | 0.32773 |  | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34175 | 0.34112 | 0.33886 | 0.32739 |  | 0.32972 | 0.32972 | 0.32972 | 0.32972 | 0.32972 | 0.32972 | 0.32972 | 0.32921 | 0.32809 | 0.31709
2006-01-02 01:41 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.3345 | 0.33231 | 0.32108 | 0.29481 | 0.33475 | 0.33475 | 0.33475 | 0.33475 | 0.33475 | 0.33475 | 0.33475 | 0.33414 | 0.33194 | 0.32075 | 0.29448 | 0.32302 | 0.32302 | 0.32302 | 0.32302 | 0.32302 | 0.32302 | 0.32302 | 0.32252 | 0.32143 | 0.31071 | 0.28711
2006-01-03 02:09 | 0.35606 | 0.35606 | 0.35606 | 0.35606 | 0.35606 | 0.35606 | 0.35606 | 0.35542 | 0.35311 |  |  | 0.35569 | 0.35569 | 0.35569 | 0.35569 | 0.35569 | 0.35569 | 0.35569 | 0.35504 | 0.35271 |  |  | 0.34327 | 0.34327 | 0.34327 | 0.34327 | 0.34327 | 0.34327 | 0.34327 | 0.34274 | 0.34159 |  |  | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164
2006-01-04 02:43 | 0.34248 | 0.34248 | 0.34248 | 0.34248 | 0.34248 | 0.34248 | 0.34248 | 0.34187 | 0.33965 |  |  | 0.34212 | 0.34212 | 0.34212 | 0.34212 | 0.34212 | 0.34212 | 0.34212 | 0.34151 | 0.33927 |  |  | 0.33022 | 0.33022 | 0.33022 | 0.33022 | 0.33022 | 0.33022 | 0.33022 | 0.32972 | 0.32861
2006-01-05 01:02 | 0.34718 | 0.34718 | 0.34718 | 0.34718 | 0.34718 | 0.34718 | 0.34718 | 0.34656 | 0.34431 | 0.33248 |  | 0.34682 | 0.34682 | 0.34682 | 0.34682 | 0.34682 | 0.34682 | 0.34682 | 0.34619 | 0.34393 | 0.33214 |  | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.33428 | 0.33317 | 0.3218
2006-01-06 01:19 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33426 | 0.33211 | 0.32074 | 0.29454 | 0.33451 | 0.33451 | 0.33451 | 0.33451 | 0.33451 | 0.33451 | 0.33451 | 0.33391 | 0.33173 | 0.32041 | 0.2942 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32247 | 0.3214 | 0.31049 | 0.28693
2006-01-07 01:47 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32308 | 0.32251 | 0.32043 | 0.30951 |  | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32274 | 0.32217 | 0.32008 | 0.30919 |  | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31164 | 0.31117 | 0.31014 | 0.29968
2006-01-08 01:19 | 0.35982 | 0.35982 | 0.35982 | 0.35982 | 0.35982 | 0.35982 | 0.35982 | 0.35918 | 0.35688 |  |  | 0.35944 | 0.35944 | 0.35944 | 0.35944 | 0.35944 | 0.35944 | 0.35944 | 0.3588 | 0.35648 |  |  | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.3466 | 0.34546
2006-01-09 01:41 | 0.32643 | 0.32643 | 0.32643 | 0.32643 | 0.32643 | 0.32643 | 0.32643 | 0.32585 | 0.32377 |  |  | 0.32609 | 0.32609 | 0.32609 | 0.32609 | 0.32609 | 0.32609 | 0.32609 | 0.32551 | 0.32341 |  |  | 0.31495 | 0.31495 | 0.31495 | 0.31495 | 0.31495 | 0.31495 | 0.31495 | 0.31448 | 0.31345
2006-01-10 02:21 | 0.3179 | 0.3179 | 0.3179 | 0.3179 | 0.3179 | 0.3179 | 0.3179 | 0.31734 | 0.31532 |  |  | 0.31757 | 0.31757 | 0.31757 | 0.31757 | 0.31757 | 0.31757 | 0.31757 | 0.31701 | 0.31497 |  |  | 0.30677 | 0.30677 | 0.30677 | 0.30677 | 0.30677 | 0.30677 | 0.30677 | 0.30631 | 0.30531
2006-01-11 02:43 | 0.34469 | 0.34469 | 0.34469 | 0.34469 | 0.34469 | 0.34469 | 0.34469 | 0.34408 | 0.3419 |  |  | 0.34433 | 0.34433 | 0.34433 | 0.34433 | 0.34433 | 0.34433 | 0.34433 | 0.34373 | 0.34153 |  |  | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33266 | 0.33217 | 0.33108
2006-01-12 03:11 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | 0.34062 | 0.33847 | 0.32649 |  | 0.34087 | 0.34087 | 0.34087 | 0.34087 | 0.34087 | 0.34087 | 0.34087 | 0.34026 | 0.33809 | 0.32616 |  | 0.32935 | 0.32935 | 0.32935 | 0.32935 | 0.32935 | 0.32935 | 0.32935 | 0.32886 | 0.3278 | 0.31617
2006-01-13 03:45 | 0.34478 | 0.34478 | 0.34478 | 0.34478 | 0.34478 | 0.34478 | 0.34478 | 0.34418 | 0.34201 | 0.32996 | 0.30288 | 0.34443 | 0.34443 | 0.34443 | 0.34443 | 0.34443 | 0.34443 | 0.34443 | 0.34382 | 0.34163 | 0.32962 | 0.30254 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33283 | 0.33234 | 0.33127 | 0.31958 | 0.29515
2006-01-14 00:06 | 0.3504 | 0.3504 | 0.3504 | 0.3504 | 0.3504 | 0.3504 | 0.3504 | 0.34979 | 0.3476 | 0.33539 | 0.30801 | 0.35005 | 0.35005 | 0.35005 | 0.35005 | 0.35005 | 0.35005 | 0.35005 | 0.34943 | 0.34721 | 0.33504 | 0.30767
2006-01-15 00:34 | 0.31655 | 0.31655 | 0.31655 | 0.31655 | 0.31655 | 0.31655 | 0.31655 | 0.316 | 0.31402 |  |  | 0.31623 | 0.31623 | 0.31623 | 0.31623 | 0.31623 | 0.31623 | 0.31623 | 0.31567 | 0.31368 |  |  | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30551 | 0.30506 | 0.30409
2006-01-16 01:02 | 0.34759 | 0.34759 | 0.34759 | 0.34759 | 0.34759 | 0.34759 | 0.34759 | 0.34699 | 0.34482 | 0.33264 | 0.30568 | 0.34725 | 0.34725 | 0.34725 | 0.34725 | 0.34725 | 0.34725 | 0.34725 | 0.34664 | 0.34445 | 0.33231 | 0.30534 | 0.33552 | 0.33552 | 0.33552 | 0.33552 | 0.33552 | 0.33552 | 0.33552 | 0.33503 | 0.33396 | 0.32207 | 0.29762
2006-01-17 01:30 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33329 | 0.33271 | 0.33064 | 0.31901 | 0.29331 | 0.33295 | 0.33295 | 0.33295 | 0.33295 | 0.33295 | 0.33295 | 0.33295 | 0.33237 | 0.33028 | 0.31868 | 0.293
2006-01-18 01:52 | 0.35421 | 0.35421 | 0.35421 | 0.35421 | 0.35421 | 0.35421 | 0.35421 | 0.3536 |  |  |  | 0.35386 | 0.35386 | 0.35386 | 0.35386 | 0.35386 | 0.35386 | 0.35386 | 0.35325 |  |  |  | 0.34184 | 0.34184 | 0.34184 | 0.34184 | 0.34184 | 0.34184 | 0.34184 | 0.34134
2006-01-19 02:21 | 0.33914 | 0.33914 | 0.33914 | 0.33914 | 0.33914 | 0.33914 | 0.33914 | 0.33856 | 0.33635 | 0.32456 |  | 0.3388 | 0.3388 | 0.3388 | 0.3388 | 0.3388 | 0.3388 | 0.3388 | 0.33822 | 0.33599 | 0.32423 |  | 0.32733 | 0.32733 | 0.32733 | 0.32733 | 0.32733 | 0.32733 | 0.32733 | 0.32686 | 0.32567 | 0.31414
2006-01-20 03:11 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33156 | 0.3294 | 0.3179 | 0.29232 | 0.3318 | 0.3318 | 0.3318 | 0.3318 | 0.3318 | 0.3318 | 0.3318 | 0.33122 | 0.32905 | 0.31758 | 0.292 | 0.32061 | 0.32061 | 0.32061 | 0.32061 | 0.32061 | 0.32061 | 0.32061 | 0.32014 | 0.31898 | 0.30775 | 0.2844
2006-01-21 02:38 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32121 | 0.32066 | 0.31858 | 0.30749 |  | 0.32089 | 0.32089 | 0.32089 | 0.32089 | 0.32089 | 0.32089 | 0.32089 | 0.32034 | 0.31824 | 0.30719 |  | 0.3101 | 0.3101 | 0.3101 | 0.3101 | 0.3101 | 0.3101 | 0.3101 | 0.30966 | 0.30854 | 0.29772 |  | 0.2798 | 0.2798 | 0.2798 | 0.2798 | 0.2798 | 0.2798 | 0.2798 | 0.2798 | 0.2798 | 0.27566
2006-01-22 03:00 | 0.33563 | 0.33563 | 0.33563 | 0.33563 | 0.33563 | 0.33563 | 0.33563 | 0.33506 | 0.33289 | 0.32135 | 0.29551 | 0.3353 | 0.3353 | 0.3353 | 0.3353 | 0.3353 | 0.3353 | 0.3353 | 0.33472 | 0.33253 | 0.32103 | 0.2952
2006-01-23 03:34 | 0.34039 | 0.34039 | 0.34039 | 0.34039 | 0.34039 | 0.34039 | 0.34039 | 0.33981 | 0.33761 | 0.32595 |  | 0.34005 | 0.34005 | 0.34005 | 0.34005 | 0.34005 | 0.34005 | 0.34005 | 0.33947 | 0.33725 | 0.32563
2006-01-24 03:56 | 0.33536 | 0.33536 | 0.33536 | 0.33536 | 0.33536 | 0.33536 | 0.33536 | 0.3348 | 0.33264 | 0.3212 |  | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33504 | 0.33447 | 0.33229 | 0.32088 |  | 0.3236 | 0.3236 | 0.3236 | 0.3236 | 0.3236 | 0.3236 | 0.3236 | 0.32314 | 0.32197 | 0.31075 |  | 0.29217 | 0.29217 | 0.29217 | 0.29217 | 0.29217 | 0.29217 | 0.29217 | 0.29217 | 0.29217 | 0.2879
2006-01-25 00:17 | 0.35677 | 0.35677 | 0.35677 | 0.35677 | 0.35677 | 0.35677 | 0.35677 | 0.35617 |  |  |  | 0.35642 | 0.35642 | 0.35642 | 0.35642 | 0.35642 | 0.35642 | 0.35642 | 0.35581 |  |  |  | 0.34429 | 0.34429 | 0.34429 | 0.34429 | 0.34429 | 0.34429 | 0.34429 | 0.3438
2006-01-26 00:56 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35513 | 0.35274 | 0.34064 | 0.31316 | 0.35539 | 0.35539 | 0.35539 | 0.35539 | 0.35539 | 0.35539 | 0.35539 | 0.35478 | 0.35237 | 0.34031 | 0.31282
2006-01-27 01:41 | 0.32389 | 0.32389 | 0.32389 | 0.32389 | 0.32389 | 0.32389 | 0.32389 | 0.32335 | 0.32118 | 0.31021 |  | 0.32358 | 0.32358 | 0.32358 | 0.32358 | 0.32358 | 0.32358 | 0.32358 | 0.32303 | 0.32084 | 0.3099 |  | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.31206 | 0.3108 | 0.3 |  | 0.2822 | 0.2822 | 0.2822 | 0.2822 | 0.2822 | 0.2822 | 0.2822 | 0.2822 | 0.2822 | 0.27812
2006-01-28 02:09 | 0.35476 | 0.35476 | 0.35476 | 0.35476 | 0.35476 | 0.35476 | 0.35476 | 0.35417 | 0.35179 | 0.33982 |  | 0.35442 | 0.35442 | 0.35442 | 0.35442 | 0.35442 | 0.35442 | 0.35442 | 0.35382 | 0.35143 | 0.33949 |  | 0.34233 | 0.34233 | 0.34233 | 0.34233 | 0.34233 | 0.34233 | 0.34233 | 0.34185 | 0.34047 | 0.3287 |  | 0.30935 | 0.30935 | 0.30935 | 0.30935 | 0.30935 | 0.30935 | 0.30935 | 0.30935 | 0.30935 | 0.30492
2006-01-29 02:43 | 0.35292 | 0.35292 | 0.35292 | 0.35292 | 0.35292 | 0.35292 | 0.35292 | 0.35233 | 0.34998 | 0.33811 |  | 0.35258 | 0.35258 | 0.35258 | 0.35258 | 0.35258 | 0.35258 | 0.35258 | 0.35199 | 0.34961 | 0.33779 |  | 0.34059 | 0.34059 | 0.34059 | 0.34059 | 0.34059 | 0.34059 | 0.34059 | 0.34011 | 0.33875 | 0.3271
2006-01-30 03:11 | 0.3447 | 0.3447 | 0.3447 | 0.3447 | 0.3447 | 0.3447 | 0.3447 | 0.34413 | 0.34183 |  |  | 0.34437 | 0.34437 | 0.34437 | 0.34437 | 0.34437 | 0.34437 | 0.34437 | 0.34379 | 0.34148 |  |  | 0.3327 | 0.3327 | 0.3327 | 0.3327 | 0.3327 | 0.3327 | 0.3327 | 0.33224 | 0.33091
2006-01-31 03:34 | 0.33823 | 0.33823 | 0.33823 | 0.33823 | 0.33823 | 0.33823 | 0.33823 | 0.33767 | 0.33543 | 0.32398 | 0.29758 | 0.3379 | 0.3379 | 0.3379 | 0.3379 | 0.3379 | 0.3379 | 0.3379 | 0.33734 | 0.33508 | 0.32367 | 0.29727 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.32604 | 0.32474 | 0.31349 | 0.28899
2006-02-01 04:02 | 0.3462 | 0.3462 | 0.3462 | 0.3462 | 0.3462 | 0.3462 | 0.3462 | 0.34563 | 0.34334 |  |  | 0.34587 | 0.34587 | 0.34587 | 0.34587 | 0.34587 | 0.34587 | 0.34587 | 0.3453 | 0.34299 |  |  | 0.33423 | 0.33423 | 0.33423 | 0.33423 | 0.33423 | 0.33423 | 0.33423 | 0.33377 | 0.33245
2006-02-02 00:22 | 0.32969 | 0.32969 | 0.32969 | 0.32969 | 0.32969 | 0.32969 | 0.32969 | 0.32914 | 0.32697 | 0.31576 |  | 0.32937 | 0.32937 | 0.32937 | 0.32937 | 0.32937 | 0.32937 | 0.32937 | 0.32882 | 0.32663 | 0.31546 |  | 0.31832 | 0.31832 | 0.31832 | 0.31832 | 0.31832 | 0.31832 | 0.31832 | 0.31788 | 0.31662 | 0.30559 |  | 0.28737 | 0.28737 | 0.28737 | 0.28737 | 0.28737 | 0.28737 | 0.28737 | 0.28737 | 0.28737 | 0.2833
2006-02-03 01:02 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34083 | 0.34027 | 0.33803 |  |  | 0.34051 | 0.34051 | 0.34051 | 0.34051 | 0.34051 | 0.34051 | 0.34051 | 0.33995 | 0.33769 |  |  | 0.32912 | 0.32912 | 0.32912 | 0.32912 | 0.32912 | 0.32912 | 0.32912 | 0.32867 | 0.32738
2006-02-04 01:24 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35942 | 0.35883 | 0.35648 |  |  | 0.35908 | 0.35908 | 0.35908 | 0.35908 | 0.35908 | 0.35908 | 0.35908 | 0.35848 | 0.35611 |  |  | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34712 | 0.34664 | 0.34528
2006-02-05 02:04 | 0.35105 | 0.35105 | 0.35105 | 0.35105 | 0.35105 | 0.35105 | 0.35105 | 0.35048 | 0.34818 | 0.33606 |  | 0.35072 | 0.35072 | 0.35072 | 0.35072 | 0.35072 | 0.35072 | 0.35072 | 0.35014 | 0.34783 | 0.33574 |  | 0.33907 | 0.33907 | 0.33907 | 0.33907 | 0.33907 | 0.33907 | 0.33907 | 0.33861 | 0.33729 | 0.3253
2006-02-06 02:38 | 0.31358 | 0.31358 | 0.31358 | 0.31358 | 0.31358 | 0.31358 | 0.31358 | 0.31307 | 0.31103 |  |  | 0.31328 | 0.31328 | 0.31328 | 0.31328 | 0.31328 | 0.31328 | 0.31328 | 0.31277 | 0.31071 |  |  | 0.30292 | 0.30292 | 0.30292 | 0.30292 | 0.30292 | 0.30292 | 0.30292 | 0.30251 | 0.30133
2006-02-07 03:11 | 0.32246 | 0.32246 | 0.32246 | 0.32246 | 0.32246 | 0.32246 | 0.32246 | 0.32194 | 0.31984 |  |  | 0.32216 | 0.32216 | 0.32216 | 0.32216 | 0.32216 | 0.32216 | 0.32216 | 0.32163 | 0.31952 |  |  | 0.31153 | 0.31153 | 0.31153 | 0.31153 | 0.31153 | 0.31153 | 0.31153 | 0.31111 | 0.30991
2006-02-08 03:34 | 0.33807 | 0.33807 | 0.33807 | 0.33807 | 0.33807 | 0.33807 | 0.33807 | 0.33752 | 0.33533 | 0.32348 | 0.29701 | 0.33775 | 0.33775 | 0.33775 | 0.33775 | 0.33775 | 0.33775 | 0.33775 | 0.33719 | 0.33499 | 0.32318 | 0.2967
2006-02-09 00:06 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.32382 | 0.3233 | 0.3212 | 0.30989 | 0.28466 | 0.32352 | 0.32352 | 0.32352 | 0.32352 | 0.32352 | 0.32352 | 0.32352 | 0.32299 | 0.32088 | 0.3096 | 0.28437
2006-02-10 00:39 | 0.32404 | 0.32404 | 0.32404 | 0.32404 | 0.32404 | 0.32404 | 0.32404 | 0.32352 | 0.32143 | 0.31015 |  | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32373 | 0.32321 | 0.3211 | 0.30986
2006-02-11 01:13 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31672 | 0.31622 | 0.31418 |  |  | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31592 | 0.31387 |  |  | 0.30576 | 0.30576 | 0.30576 | 0.30576 | 0.30576 | 0.30576 | 0.30576 | 0.30534 | 0.30416
2006-02-12 01:36 | 0.35365 | 0.35365 | 0.35365 | 0.35365 | 0.35365 | 0.35365 | 0.35365 | 0.35308 |  |  |  | 0.35332 | 0.35332 | 0.35332 | 0.35332 | 0.35332 | 0.35332 | 0.35332 | 0.35275 |  |  |  | 0.34144 | 0.34144 | 0.34144 | 0.34144 | 0.34144 | 0.34144 | 0.34144 | 0.34098
2006-02-13 02:09 | 0.31491 | 0.31491 | 0.31491 | 0.31491 | 0.31491 | 0.31491 | 0.31491 | 0.31442 | 0.3123 |  |  | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31412 | 0.31198 |  |  | 0.30408 | 0.30408 | 0.30408 | 0.30408 | 0.30408 | 0.30408 | 0.30408 | 0.30367 | 0.30238
2006-02-14 02:38 | 0.31933 | 0.31933 | 0.31933 | 0.31933 | 0.31933 | 0.31933 | 0.31933 | 0.31883 | 0.31669 | 0.30541 |  | 0.31904 | 0.31904 | 0.31904 | 0.31904 | 0.31904 | 0.31904 | 0.31904 | 0.31853 | 0.31637 | 0.30513
2006-02-15 03:06 | 0.33388 | 0.33388 | 0.33388 | 0.33388 | 0.33388 | 0.33388 | 0.33388 | 0.33335 | 0.33112 |  |  | 0.33357 | 0.33357 | 0.33357 | 0.33357 | 0.33357 | 0.33357 | 0.33357 | 0.33304 | 0.33079
2006-02-16 03:28 | 0.32514 | 0.32514 | 0.32514 | 0.32514 | 0.32514 | 0.32514 | 0.32514 | 0.32463 | 0.32246 | 0.31092 |  | 0.32484 | 0.32484 | 0.32484 | 0.32484 | 0.32484 | 0.32484 | 0.32484 | 0.32432 | 0.32214 | 0.31063 |  | 0.3138 | 0.3138 | 0.3138 | 0.3138 | 0.3138 | 0.3138 | 0.3138 | 0.31338 | 0.31205 | 0.30046
2006-02-17 00:11 | 0.35141 | 0.35141 | 0.35141 | 0.35141 | 0.35141 | 0.35141 | 0.35141 | 0.35086 | 0.34853 | 0.33609 | 0.3085 | 0.35109 | 0.35109 | 0.35109 | 0.35109 | 0.35109 | 0.35109 | 0.35109 | 0.35053 | 0.34818 | 0.33578 | 0.30819
2006-02-18 00:34 | 0.3433 | 0.3433 | 0.3433 | 0.3433 | 0.3433 | 0.3433 | 0.3433 | 0.34276 | 0.34049 | 0.32838 |  | 0.34299 | 0.34299 | 0.34299 | 0.34299 | 0.34299 | 0.34299 | 0.34299 | 0.34244 | 0.34015 | 0.32808
2006-02-19 01:02 | 0.34652 | 0.34652 | 0.34652 | 0.34652 | 0.34652 | 0.34652 | 0.34652 | 0.34598 | 0.34369 |  |  | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34621 | 0.34566 | 0.34335 |  |  | 0.33426 | 0.33426 | 0.33426 | 0.33426 | 0.33426 | 0.33426 | 0.33426 | 0.33382 | 0.33241
2006-02-20 01:30 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32306 | 0.32255 | 0.32042 |  |  | 0.32276 | 0.32276 | 0.32276 | 0.32276 | 0.32276 | 0.32276 | 0.32276 | 0.32225 | 0.32011 |  |  | 0.31166 | 0.31166 | 0.31166 | 0.31166 | 0.31166 | 0.31166 | 0.31166 | 0.31126 | 0.30994
2006-02-21 01:52 | 0.35184 | 0.35184 | 0.35184 | 0.35184 | 0.35184 | 0.35184 | 0.35184 | 0.35129 | 0.34899 | 0.3364 | 0.30881 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35153 | 0.35097 | 0.34864 | 0.33609 | 0.3085
2006-02-22 02:15 | 0.34638 | 0.34638 | 0.34638 | 0.34638 | 0.34638 | 0.34638 | 0.34638 | 0.34585 | 0.34358 |  |  | 0.34607 | 0.34607 | 0.34607 | 0.34607 | 0.34607 | 0.34607 | 0.34607 | 0.34553 | 0.34324
2006-02-23 01:36 | 0.3558 | 0.3558 | 0.3558 | 0.3558 | 0.3558 | 0.3558 | 0.3558 | 0.35524 | 0.35292 | 0.34014 | 0.31241 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35492 | 0.35258 | 0.33982 | 0.31209
2006-02-24 02:09 | 0.34622 | 0.34622 | 0.34622 | 0.34622 | 0.34622 | 0.34622 | 0.34622 | 0.34569 | 0.34344 |  |  | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34591 | 0.34537 | 0.3431 |  |  | 0.33376 | 0.33376 | 0.33376 | 0.33376 | 0.33376 | 0.33376 | 0.33376 | 0.33332 | 0.33192
2006-02-25 02:54 | 0.32367 | 0.32367 | 0.32367 | 0.32367 | 0.32367 | 0.32367 | 0.32367 | 0.32317 | 0.32107 | 0.30937 |  | 0.32338 | 0.32338 | 0.32338 | 0.32338 | 0.32338 | 0.32338 | 0.32338 | 0.32287 | 0.32076 | 0.30909
2006-02-26 03:22 | 0.34707 | 0.34707 | 0.34707 | 0.34707 | 0.34707 | 0.34707 | 0.34707 | 0.34654 | 0.34429 | 0.33179 | 0.30477 | 0.34676 | 0.34676 | 0.34676 | 0.34676 | 0.34676 | 0.34676 | 0.34676 | 0.34622 | 0.34396 | 0.33149 | 0.30447
2006-02-27 03:45 | 0.31864 | 0.31864 | 0.31864 | 0.31864 | 0.31864 | 0.31864 | 0.31864 | 0.31815 | 0.3161 |  |  | 0.31836 | 0.31836 | 0.31836 | 0.31836 | 0.31836 | 0.31836 | 0.31836 | 0.31787 | 0.31579 |  |  | 0.30703 | 0.30703 | 0.30703 | 0.30703 | 0.30703 | 0.30703 | 0.30703 | 0.30662 | 0.30534
2006-02-28 00:06 | 0.32923 | 0.32923 | 0.32923 | 0.32923 | 0.32923 | 0.32923 | 0.32923 | 0.32873 | 0.32661 | 0.31471 | 0.28924 | 0.32894 | 0.32894 | 0.32894 | 0.32894 | 0.32894 | 0.32894 | 0.32894 | 0.32843 | 0.32629 | 0.31443 | 0.28895
2006-02-28 04:13 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.33466 | 0.3325 |  |  | 0.33487 | 0.33487 | 0.33487 | 0.33487 | 0.33487 | 0.33487 | 0.33487 | 0.33435 | 0.33218 |  |  | 0.32297 | 0.32297 | 0.32297 | 0.32297 | 0.32297 | 0.32297 | 0.32297 | 0.32254 | 0.3212
2006-03-01 00:34 | 0.32909 | 0.32909 | 0.32909 | 0.32909 | 0.32909 | 0.32909 | 0.32909 | 0.32859 | 0.32648 | 0.31451 | 0.28908 | 0.3288 | 0.3288 | 0.3288 | 0.3288 | 0.3288 | 0.3288 | 0.3288 | 0.32829 | 0.32617 | 0.31422 | 0.28879
2006-03-01 04:36 | 0.32043 | 0.32043 | 0.32043 | 0.32043 | 0.32043 | 0.32043 | 0.32043 | 0.31994 | 0.31788 |  |  | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.31965 | 0.31758 |  |  | 0.30878 | 0.30878 | 0.30878 | 0.30878 | 0.30878 | 0.30878 | 0.30878 | 0.30837 | 0.30709
2006-03-02 01:08 | 0.32207 | 0.32207 | 0.32207 | 0.32207 | 0.32207 | 0.32207 | 0.32207 | 0.32159 | 0.31952 |  |  | 0.32179 | 0.32179 | 0.32179 | 0.32179 | 0.32179 | 0.32179 | 0.32179 | 0.32129 | 0.31922 |  |  | 0.3104 | 0.3104 | 0.3104 | 0.3104 | 0.3104 | 0.3104 | 0.3104 | 0.30999 | 0.30871
2006-03-03 01:52 | 0.35815 | 0.35815 | 0.35815 | 0.35815 | 0.35815 | 0.35815 | 0.35815 | 0.35761 | 0.35533 |  |  | 0.35784 | 0.35784 | 0.35784 | 0.35784 | 0.35784 | 0.35784 | 0.35784 | 0.35729 | 0.35499 |  |  | 0.34521 | 0.34521 | 0.34521 | 0.34521 | 0.34521 | 0.34521 | 0.34521 | 0.34476 | 0.34334
2006-03-04 02:21 | 0.32299 | 0.32299 | 0.32299 | 0.32299 | 0.32299 | 0.32299 | 0.32299 | 0.3225 | 0.32044 | 0.30842 |  | 0.3227 | 0.3227 | 0.3227 | 0.3227 | 0.3227 | 0.3227 | 0.3227 | 0.32221 | 0.32014 | 0.30814
2006-03-05 02:49 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.33541 | 0.3349 | 0.33277 | 0.32033 |  | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.33511 | 0.3346 | 0.33246 | 0.32005 |  | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32281 | 0.32149 | 0.30858
2006-03-06 03:22 | 0.34506 | 0.34506 | 0.34506 | 0.34506 | 0.34506 | 0.34506 | 0.34506 | 0.34454 | 0.34235 |  |  | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34423 | 0.34203
2006-03-07 03:45 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32729 | 0.32522 | 0.313 | 0.28747 | 0.32749 | 0.32749 | 0.32749 | 0.32749 | 0.32749 | 0.32749 | 0.32749 | 0.327 | 0.32491 | 0.31273 | 0.28718
2006-03-08 00:06 | 0.3171 | 0.3171 | 0.3171 | 0.3171 | 0.3171 | 0.3171 | 0.3171 | 0.31663 | 0.31463 | 0.30285 |  | 0.31683 | 0.31683 | 0.31683 | 0.31683 | 0.31683 | 0.31683 | 0.31683 | 0.31635 | 0.31434 | 0.30258
2006-03-09 00:39 | 0.35478 | 0.35478 | 0.35478 | 0.35478 | 0.35478 | 0.35478 | 0.35478 | 0.35425 | 0.35202 | 0.33888 |  | 0.35447 | 0.35447 | 0.35447 | 0.35447 | 0.35447 | 0.35447 | 0.35447 | 0.35394 | 0.35169 | 0.33858
2006-03-10 01:02 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.3265 | 0.32601 | 0.32397 |  |  | 0.32621 | 0.32621 | 0.32621 | 0.32621 | 0.32621 | 0.32621 | 0.32621 | 0.32572 | 0.32366 |  |  | 0.31433 | 0.31433 | 0.31433 | 0.31433 | 0.31433 | 0.31433 | 0.31433 | 0.31393 | 0.31264
2006-03-11 01:30 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34232 | 0.34182 | 0.33968 | 0.32694 |  | 0.34203 | 0.34203 | 0.34203 | 0.34203 | 0.34203 | 0.34203 | 0.34203 | 0.34151 | 0.33936 | 0.32666
2006-03-12 02:09 | 0.35605 | 0.35605 | 0.35605 | 0.35605 | 0.35605 | 0.35605 | 0.35605 | 0.35553 | 0.35331 |  |  | 0.35575 | 0.35575 | 0.35575 | 0.35575 | 0.35575 | 0.35575 | 0.35575 | 0.35522 | 0.35298 |  |  | 0.34273 | 0.34273 | 0.34273 | 0.34273 | 0.34273 | 0.34273 | 0.34273 | 0.34229 | 0.3409
2006-03-13 02:43 | 0.34963 | 0.34963 | 0.34963 | 0.34963 | 0.34963 | 0.34963 | 0.34963 | 0.34912 | 0.34694 |  |  | 0.34933 | 0.34933 | 0.34933 | 0.34933 | 0.34933 | 0.34933 | 0.34933 | 0.34881 | 0.34662 |  |  | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33616 | 0.3348
2006-03-14 03:17 | 0.32588 | 0.32588 | 0.32588 | 0.32588 | 0.32588 | 0.32588 | 0.32588 | 0.3254 | 0.32338 |  |  | 0.32559 | 0.32559 | 0.32559 | 0.32559 | 0.32559 | 0.32559 | 0.32559 | 0.32511 | 0.32308 |  |  | 0.31376 | 0.31376 | 0.31376 | 0.31376 | 0.31376 | 0.31376 | 0.31376 | 0.31335 | 0.31209
2006-03-15 03:45 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34842 | 0.34791 | 0.34576 | 0.33253 | 0.30513 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34761 | 0.34544 | 0.33224 | 0.30484
2006-03-16 00:17 | 0.34603 | 0.34603 | 0.34603 | 0.34603 | 0.34603 | 0.34603 | 0.34603 | 0.34553 | 0.34339 | 0.3303 |  | 0.34574 | 0.34574 | 0.34574 | 0.34574 | 0.34574 | 0.34574 | 0.34574 | 0.34523 | 0.34308 | 0.33001
2006-03-17 03:56 | 0.31908 | 0.31908 | 0.31908 | 0.31908 | 0.31908 | 0.31908 | 0.31908 | 0.31862 |  |  |  | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 0.31834 |  |  |  | 0.30708 | 0.30708 | 0.30708 | 0.30708 | 0.30708 | 0.30708 | 0.30708 | 0.3067
2006-03-18 00:11 | 0.34905 | 0.34905 | 0.34905 | 0.34905 | 0.34905 | 0.34905 | 0.34905 | 0.34854 | 0.34632 | 0.33316 |  | 0.34876 | 0.34876 | 0.34876 | 0.34876 | 0.34876 | 0.34876 | 0.34876 | 0.34824 | 0.346 | 0.33286
2006-03-19 00:45 | 0.34459 | 0.34459 | 0.34459 | 0.34459 | 0.34459 | 0.34459 | 0.34459 | 0.34409 | 0.3419 | 0.32895 | 0.3017 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3443 | 0.3438 | 0.34159 | 0.32866 | 0.3014
2006-03-20 01:24 | 0.32458 | 0.32458 | 0.32458 | 0.32458 | 0.32458 | 0.32458 | 0.32458 | 0.32411 | 0.32205 | 0.30989 | 0.28436 | 0.3243 | 0.3243 | 0.3243 | 0.3243 | 0.3243 | 0.3243 | 0.3243 | 0.32383 | 0.32175 | 0.30962 | 0.28409
2006-03-21 01:52 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32845 | 0.32637 |  |  | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32866 | 0.32818 | 0.32608 |  |  | 0.31633 | 0.31633 | 0.31633 | 0.31633 | 0.31633 | 0.31633 | 0.31633 | 0.31592 | 0.31455
2006-03-22 02:26 | 0.32264 | 0.32264 | 0.32264 | 0.32264 | 0.32264 | 0.32264 | 0.32264 | 0.32218 | 0.32014 | 0.308 |  | 0.32237 | 0.32237 | 0.32237 | 0.32237 | 0.32237 | 0.32237 | 0.32237 | 0.3219 | 0.31985 | 0.30774 |  | 0.31031 | 0.31031 | 0.31031 | 0.31031 | 0.31031 | 0.31031 | 0.31031 | 0.30993 | 0.30858 | 0.29562
2006-03-23 03:11 | 0.32577 | 0.32577 | 0.32577 | 0.32577 | 0.32577 | 0.32577 | 0.32577 | 0.3253 | 0.32325 | 0.31104 |  | 0.3255 | 0.3255 | 0.3255 | 0.3255 | 0.3255 | 0.3255 | 0.3255 | 0.32503 | 0.32296 | 0.31077 |  | 0.31336 | 0.31336 | 0.31336 | 0.31336 | 0.31336 | 0.31336 | 0.31336 | 0.31297 | 0.31161 | 0.29859
2006-03-24 03:56 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32303 | 0.321 |  |  | 0.32322 | 0.32322 | 0.32322 | 0.32322 | 0.32322 | 0.32322 | 0.32322 | 0.32276 | 0.32071 |  |  | 0.31121 | 0.31121 | 0.31121 | 0.31121 | 0.31121 | 0.31121 | 0.31121 | 0.31082 | 0.30948
2006-03-25 03:22 | 0.35341 | 0.35341 | 0.35341 | 0.35341 | 0.35341 | 0.35341 | 0.35341 | 0.3529 |  |  |  | 0.35311 | 0.35311 | 0.35311 | 0.35311 | 0.35311 | 0.35311 | 0.35311 | 0.3526 |  |  |  | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.34002 | 0.3396
2006-03-26 03:56 | 0.32147 | 0.32147 | 0.32147 | 0.32147 | 0.32147 | 0.32147 | 0.32147 | 0.32101 | 0.31891 |  |  | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.3212 | 0.32074 | 0.31862 |  |  | 0.30933 | 0.30933 | 0.30933 | 0.30933 | 0.30933 | 0.30933 | 0.30933 | 0.30895 | 0.3075
2006-03-27 00:22 | 0.31753 | 0.31753 | 0.31753 | 0.31753 | 0.31753 | 0.31753 | 0.31753 | 0.31708 | 0.315 |  |  | 0.31726 | 0.31726 | 0.31726 | 0.31726 | 0.31726 | 0.31726 | 0.31726 | 0.31681 | 0.31472 |  |  | 0.30557 | 0.30557 | 0.30557 | 0.30557 | 0.30557 | 0.30557 | 0.30557 | 0.30519 | 0.30376
2006-03-28 00:51 | 0.3292 | 0.3292 | 0.3292 | 0.3292 | 0.3292 | 0.3292 | 0.3292 | 0.32873 | 0.32659 | 0.31403 | 0.28807 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32893 | 0.32846 | 0.3263 | 0.31376 | 0.28779
2006-03-29 01:24 | 0.32168 | 0.32168 | 0.32168 | 0.32168 | 0.32168 | 0.32168 | 0.32168 | 0.32122 | 0.31913 |  |  | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32095 | 0.31885 |  |  | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30951 | 0.30913 | 0.30769
2006-03-30 01:58 | 0.32418 | 0.32418 | 0.32418 | 0.32418 | 0.32418 | 0.32418 | 0.32418 | 0.32372 | 0.32162 | 0.3092 |  | 0.32391 | 0.32391 | 0.32391 | 0.32391 | 0.32391 | 0.32391 | 0.32391 | 0.32345 | 0.32133 | 0.30893 |  | 0.31196 | 0.31196 | 0.31196 | 0.31196 | 0.31196 | 0.31196 | 0.31196 | 0.31158 | 0.31013 | 0.29676
2006-03-31 02:54 | 0.34596 | 0.34596 | 0.34596 | 0.34596 | 0.34596 | 0.34596 | 0.34596 | 0.34548 | 0.34324 |  |  | 0.34568 | 0.34568 | 0.34568 | 0.34568 | 0.34568 | 0.34568 | 0.34568 | 0.34519 | 0.34294 |  |  | 0.33296 | 0.33296 | 0.33296 | 0.33296 | 0.33296 | 0.33296 | 0.33296 | 0.33255 | 0.33102
2006-04-01 03:28 | 0.32312 | 0.32312 | 0.32312 | 0.32312 | 0.32312 | 0.32312 | 0.32312 | 0.32266 | 0.32058 | 0.30815 |  | 0.32285 | 0.32285 | 0.32285 | 0.32285 | 0.32285 | 0.32285 | 0.32285 | 0.32239 | 0.3203 | 0.30789 |  | 0.31101 | 0.31101 | 0.31101 | 0.31101 | 0.31101 | 0.31101 | 0.31101 | 0.31063 | 0.3092 | 0.29581
2006-04-02 | 0.32743 | 0.32743 | 0.32743 | 0.32743 | 0.32743 | 0.32743 | 0.32743 | 0.32697 | 0.32487 | 0.31231 |  | 0.32717 | 0.32717 | 0.32717 | 0.32717 | 0.32717 | 0.32717 | 0.32717 | 0.3267 | 0.32458 | 0.31204 |  | 0.31519 | 0.31519 | 0.31519 | 0.31519 | 0.31519 | 0.31519 | 0.31519 | 0.31481 | 0.31337 | 0.29984
2006-04-03 00:39 | 0.33804 | 0.33804 | 0.33804 | 0.33804 | 0.33804 | 0.33804 | 0.33804 | 0.33757 | 0.3354 | 0.32247 |  | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33776 | 0.33729 | 0.33511 | 0.3222
2006-04-04 01:08 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33513 | 0.33467 | 0.33252 | 0.31975 |  | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.33439 | 0.33223 | 0.31948
2006-04-05 02:32 | 0.33653 | 0.33653 | 0.33653 | 0.33653 | 0.33653 | 0.33653 | 0.33653 | 0.33606 | 0.33391 | 0.32112 | 0.29411 | 0.33625 | 0.33625 | 0.33625 | 0.33625 | 0.33625 | 0.33625 | 0.33625 | 0.33578 | 0.33362 | 0.32085 | 0.29384
2006-04-06 03:17 | 0.32152 | 0.32152 | 0.32152 | 0.32152 | 0.32152 | 0.32152 | 0.32152 | 0.32107 | 0.31903 | 0.30684 |  | 0.32126 | 0.32126 | 0.32126 | 0.32126 | 0.32126 | 0.32126 | 0.32126 | 0.32081 | 0.31875 | 0.30659 |  | 0.30928 | 0.30928 | 0.30928 | 0.30928 | 0.30928 | 0.30928 | 0.30928 | 0.3089 | 0.30749 | 0.29429
2006-04-07 03:51 | 0.3552 | 0.3552 | 0.3552 | 0.3552 | 0.3552 | 0.3552 | 0.3552 | 0.3547 | 0.35245 | 0.33904 |  | 0.35491 | 0.35491 | 0.35491 | 0.35491 | 0.35491 | 0.35491 | 0.35491 | 0.35441 | 0.35214 | 0.33876
2006-04-08 00:17 | 0.34037 | 0.34037 | 0.34037 | 0.34037 | 0.34037 | 0.34037 | 0.34037 | 0.3399 | 0.33774 |  |  | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.34009 | 0.33962 | 0.33745
2006-04-09 01:13 | 0.32627 | 0.32627 | 0.32627 | 0.32627 | 0.32627 | 0.32627 | 0.32627 | 0.32583 | 0.32377 | 0.31138 |  | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32601 | 0.32556 | 0.32349 | 0.31113 |  | 0.31374 | 0.31374 | 0.31374 | 0.31374 | 0.31374 | 0.31374 | 0.31374 | 0.31336 | 0.31193 | 0.2986
2006-04-10 01:58 | 0.33623 | 0.33623 | 0.33623 | 0.33623 | 0.33623 | 0.33623 | 0.33623 | 0.33577 | 0.33366 |  |  | 0.33597 | 0.33597 | 0.33597 | 0.33597 | 0.33597 | 0.33597 | 0.33597 | 0.3355 | 0.33337 |  |  | 0.32335 | 0.32335 | 0.32335 | 0.32335 | 0.32335 | 0.32335 | 0.32335 | 0.32297 | 0.3215
2006-04-11 02:26 | 0.35445 | 0.35445 | 0.35445 | 0.35445 | 0.35445 | 0.35445 | 0.35445 | 0.35397 | 0.35174 | 0.33824 | 0.30959 | 0.35417 | 0.35417 | 0.35417 | 0.35417 | 0.35417 | 0.35417 | 0.35417 | 0.35368 | 0.35144 | 0.33796 | 0.3093
2006-04-12 02:49 | 0.32932 | 0.32932 | 0.32932 | 0.32932 | 0.32932 | 0.32932 | 0.32932 | 0.32887 | 0.32681 | 0.3143 |  | 0.32906 | 0.32906 | 0.32906 | 0.32906 | 0.32906 | 0.32906 | 0.32906 | 0.32861 | 0.32653 | 0.31404
2006-04-13 03:11 | 0.33241 | 0.33241 | 0.33241 | 0.33241 | 0.33241 | 0.33241 | 0.33241 | 0.33196 | 0.32988 |  |  | 0.33215 | 0.33215 | 0.33215 | 0.33215 | 0.33215 | 0.33215 | 0.33215 | 0.33169 | 0.3296 |  |  | 0.31955 | 0.31955 | 0.31955 | 0.31955 | 0.31955 | 0.31955 | 0.31955 | 0.31917 | 0.31772
2006-04-14 03:34 | 0.33011 | 0.33011 | 0.33011 | 0.33011 | 0.33011 | 0.33011 | 0.33011 | 0.32965 | 0.3276 |  |  | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32984 | 0.32939 | 0.32732 |  |  | 0.31736 | 0.31736 | 0.31736 | 0.31736 | 0.31736 | 0.31736 | 0.31736 | 0.31698 | 0.31555
2006-04-15 04:02 | 0.32321 | 0.32321 | 0.32321 | 0.32321 | 0.32321 | 0.32321 | 0.32321 | 0.32277 | 0.32077 | 0.30835 | 0.28227 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32296 | 0.32252 | 0.32049 | 0.3081 | 0.282 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31078 | 0.31041 | 0.30901 | 0.2955 | 0.27079
2006-04-16 01:30 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35389 | 0.35169 |  |  | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.35409 | 0.3536 | 0.35139 |  |  | 0.34076 | 0.34076 | 0.34076 | 0.34076 | 0.34076 | 0.34076 | 0.34076 | 0.34036 | 0.33883 |  |  | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029
2006-04-17 02:15 | 0.35378 | 0.35378 | 0.35378 | 0.35378 | 0.35378 | 0.35378 | 0.35378 | 0.35331 |  |  |  | 0.35351 | 0.35351 | 0.35351 | 0.35351 | 0.35351 | 0.35351 | 0.35351 | 0.35302 |  |  |  | 0.34024 | 0.34024 | 0.34024 | 0.34024 | 0.34024 | 0.34024 | 0.34024 | 0.33984
2006-04-18 02:38 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 0.34756 | 0.34531 |  |  | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.34728 | 0.34502 |  |  | 0.33474 | 0.33474 | 0.33474 | 0.33474 | 0.33474 | 0.33474 | 0.33474 | 0.33435 | 0.33273
2006-04-19 02:54 | 0.33163 | 0.33163 | 0.33163 | 0.33163 | 0.33163 | 0.33163 | 0.33163 | 0.33118 | 0.32905 | 0.31617 | 0.28955 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.33092 | 0.32877 | 0.31591 | 0.28929 | 0.319 | 0.319 | 0.319 | 0.319 | 0.319 | 0.319 | 0.319 | 0.31863 | 0.31709 | 0.30305 | 0.27788
2006-04-20 03:28 | 0.33441 | 0.33441 | 0.33441 | 0.33441 | 0.33441 | 0.33441 | 0.33441 | 0.33396 | 0.33181 |  |  | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.33369 | 0.33153 |  |  | 0.32172 | 0.32172 | 0.32172 | 0.32172 | 0.32172 | 0.32172 | 0.32172 | 0.32134 | 0.31979
2006-04-21 04:02 | 0.32304 | 0.32304 | 0.32304 | 0.32304 | 0.32304 | 0.32304 | 0.32304 | 0.3226 | 0.32054 | 0.30795 | 0.28217 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32235 | 0.32027 | 0.30769 | 0.28191 | 0.31082 | 0.31082 | 0.31082 | 0.31082 | 0.31082 | 0.31082 | 0.31082 | 0.31045 | 0.30896 | 0.29522 | 0.27091 | 0.27608 | 0.27608 | 0.27608 | 0.27608 | 0.27608 | 0.27608 | 0.27608 | 0.27608 | 0.27608 | 0.2719 | 0.25289
2006-04-22 00:39 | 0.33837 | 0.33837 | 0.33837 | 0.33837 | 0.33837 | 0.33837 | 0.33837 | 0.33792 | 0.33576 | 0.3226 |  | 0.33811 | 0.33811 | 0.33811 | 0.33811 | 0.33811 | 0.33811 | 0.33811 | 0.33766 | 0.33548 | 0.32234 |  | 0.3256 | 0.3256 | 0.3256 | 0.3256 | 0.3256 | 0.3256 | 0.3256 | 0.32522 | 0.32366 | 0.30933
2006-04-23 01:41 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | 0.3407 | 0.33852 | 0.3253 |  | 0.34088 | 0.34088 | 0.34088 | 0.34088 | 0.34088 | 0.34088 | 0.34088 | 0.34043 | 0.33824 | 0.32504 |  | 0.32831 | 0.32831 | 0.32831 | 0.32831 | 0.32831 | 0.32831 | 0.32831 | 0.32793 | 0.32636 | 0.31197
2006-04-24 02:09 | 0.35468 | 0.35468 | 0.35468 | 0.35468 | 0.35468 | 0.35468 | 0.35468 | 0.35421 | 0.35195 |  |  | 0.3544 | 0.3544 | 0.3544 | 0.3544 | 0.3544 | 0.3544 | 0.3544 | 0.35393 | 0.35166 |  |  | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34136 | 0.34097 | 0.33935 |  |  | 0.30318 | 0.30318 | 0.30318 | 0.30318 | 0.30318 | 0.30318 | 0.30318 | 0.30318 | 0.30318
2006-04-25 02:26 | 0.32723 | 0.32723 | 0.32723 | 0.32723 | 0.32723 | 0.32723 | 0.32723 | 0.3268 | 0.32472 | 0.31199 |  | 0.32698 | 0.32698 | 0.32698 | 0.32698 | 0.32698 | 0.32698 | 0.32698 | 0.32654 | 0.32445 | 0.31174 |  | 0.31498 | 0.31498 | 0.31498 | 0.31498 | 0.31498 | 0.31498 | 0.31498 | 0.31462 | 0.31313 | 0.29926 |  | 0.27995 | 0.27995 | 0.27995 | 0.27995 | 0.27995 | 0.27995 | 0.27995 | 0.27995 | 0.27995 | 0.27546
2006-04-26 02:49 | 0.32979 | 0.32979 | 0.32979 | 0.32979 | 0.32979 | 0.32979 | 0.32979 | 0.32935 | 0.32727 | 0.31447 | 0.28792 | 0.32953 | 0.32953 | 0.32953 | 0.32953 | 0.32953 | 0.32953 | 0.32953 | 0.3291 | 0.327 | 0.31422 | 0.28766 | 0.31748 | 0.31748 | 0.31748 | 0.31748 | 0.31748 | 0.31748 | 0.31748 | 0.31711 | 0.31562 | 0.3017 | 0.27652 | 0.28236 | 0.28236 | 0.28236 | 0.28236 | 0.28236 | 0.28236 | 0.28236 | 0.28236 | 0.28236 | 0.27788 | 0.2584
2006-04-27 02:26 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.34421 | 0.34203 | 0.3287 | 0.30109
2006-04-28 03:00 | 0.32867 | 0.32867 | 0.32867 | 0.32867 | 0.32867 | 0.32867 | 0.32867 | 0.32823 | 0.32617 | 0.31349 |  | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32833 | 0.32789 | 0.3258 | 0.31312
2006-04-29 03:28 | 0.35879 | 0.35879 | 0.35879 | 0.35879 | 0.35879 | 0.35879 | 0.35879 | 0.35832 | 0.35607 | 0.34227 |  | 0.35843 | 0.35843 | 0.35843 | 0.35843 | 0.35843 | 0.35843 | 0.35843 | 0.35795 | 0.35568 | 0.34186 |  | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.34486 | 0.34324 | 0.32817
2006-04-30 03:45 | 0.35115 | 0.35115 | 0.35115 | 0.35115 | 0.35115 | 0.35115 | 0.35115 | 0.35069 | 0.34849 | 0.33503 | 0.3068 | 0.3508 | 0.3508 | 0.3508 | 0.3508 | 0.3508 | 0.3508 | 0.3508 | 0.35033 | 0.34811 | 0.33463 | 0.30625
2006-05-01 00:11 | 0.31985 | 0.31985 | 0.31985 | 0.31985 | 0.31985 | 0.31985 | 0.31985 | 0.31944 | 0.31744 | 0.3052 |  | 0.31953 | 0.31953 | 0.31953 | 0.31953 | 0.31953 | 0.31953 | 0.31953 | 0.3191 | 0.31709 | 0.30484 |  | 0.30775 | 0.30775 | 0.30775 | 0.30775 | 0.30775 | 0.30775 | 0.30775 | 0.30741 | 0.30596 | 0.29259
2006-05-02 00:28 | 0.34927 | 0.34927 | 0.34927 | 0.34927 | 0.34927 | 0.34927 | 0.34927 | 0.34882 | 0.34664 | 0.33332 | 0.30524 | 0.34892 | 0.34892 | 0.34892 | 0.34892 | 0.34892 | 0.34892 | 0.34892 | 0.34846 | 0.34626 | 0.33293 | 0.3047 | 0.3361 | 0.3361 | 0.3361 | 0.3361 | 0.3361 | 0.3361 | 0.3361 | 0.33572 | 0.33415 | 0.3196 | 0.2928
2006-05-03 00:51 | 0.32174 | 0.32174 | 0.32174 | 0.32174 | 0.32174 | 0.32174 | 0.32174 | 0.32132 | 0.31932 | 0.30709 | 0.28135 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32141 | 0.32099 | 0.31897 | 0.30672 | 0.28086 | 0.30964 | 0.30964 | 0.30964 | 0.30964 | 0.30964 | 0.30964 | 0.30964 | 0.30929 | 0.30785 | 0.2945 | 0.26999
2006-05-04 01:24 | 0.32877 | 0.32877 | 0.32877 | 0.32877 | 0.32877 | 0.32877 | 0.32877 | 0.32834 | 0.3263 | 0.31384 |  | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.32844 | 0.328 | 0.32595 | 0.31347 |  | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31643 | 0.31608 | 0.31461 | 0.30103
2006-05-05 01:52 | 0.33716 | 0.33716 | 0.33716 | 0.33716 | 0.33716 | 0.33716 | 0.33716 | 0.33672 | 0.33463 | 0.32189 |  | 0.33681 | 0.33681 | 0.33681 | 0.33681 | 0.33681 | 0.33681 | 0.33681 | 0.33637 | 0.33427 | 0.32151 |  | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32454 | 0.32418 | 0.32268 | 0.3088
2006-05-06 02:15 | 0.35309 | 0.35309 | 0.35309 | 0.35309 | 0.35309 | 0.35309 | 0.35309 | 0.35263 | 0.35045 | 0.33715 | 0.3088 | 0.35273 | 0.35273 | 0.35273 | 0.35273 | 0.35273 | 0.35273 | 0.35273 | 0.35227 | 0.35007 | 0.33675 | 0.30827 | 0.33991 | 0.33991 | 0.33991 | 0.33991 | 0.33991 | 0.33991 | 0.33991 | 0.33953 | 0.33797 | 0.3235 | 0.29646
2006-05-07 02:38 | 0.34186 | 0.34186 | 0.34186 | 0.34186 | 0.34186 | 0.34186 | 0.34186 | 0.34142 | 0.33931 | 0.32647 |  | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34107 | 0.33895 | 0.32609 |  | 0.32914 | 0.32914 | 0.32914 | 0.32914 | 0.32914 | 0.32914 | 0.32914 | 0.32877 | 0.32727 | 0.31331 |  | 0.29221 | 0.29221 | 0.29221 | 0.29221 | 0.29221 | 0.29221 | 0.29221 | 0.29221 | 0.29221 | 0.28762

## TARGET POWER 2
Train | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Reactor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Bank | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Train 1, Bank 1 | Train 1, Bank 2 | Train 1, Bank 3 | Train 1, Bank 4 | Train 1, Bank 5 | Train 1, Bank 6 | Train 1, Bank 7 | Train 1, Bank 8 | Train 1, Bank 9 | Train 1, Bank 10 | Train 1, Bank 11 | Train 2, Bank 1 | Train 2, Bank 2 | Train 2, Bank 3 | Train 2, Bank 4 | Train 2, Bank 5 | Train 2, Bank 6 | Train 2, Bank 7 | Train 2, Bank 8 | Train 2, Bank 9 | Train 2, Bank 10 | Train 2, Bank 11 | Train 3, Bank 1 | Train 3, Bank 2 | Train 3, Bank 3 | Train 3, Bank 4 | Train 3, Bank 5 | Train 3, Bank 6 | Train 3, Bank 7 | Train 3, Bank 8 | Train 3, Bank 9 | Train 3, Bank 10 | Train 3, Bank 11 | Train 4, Bank 1 | Train 4, Bank 2 | Train 4, Bank 3 | Train 4, Bank 4 | Train 4, Bank 5 | Train 4, Bank 6 | Train 4, Bank 7 | Train 4, Bank 8 | Train 4, Bank 9 | Train 4, Bank 10 | Train 4, Bank 11 | Train 5, Bank 1 | Train 5, Bank 2 | Train 5, Bank 3 | Train 5, Bank 4 | Train 5, Bank 5 | Train 5, Bank 6 | Train 5, Bank 7 | Train 5, Bank 8 | Train 5, Bank 9 | Train 5, Bank 10 | Train 5, Bank 11 | Train 6, Bank 1 | Train 6, Bank 2 | Train 6, Bank 3 | Train 6, Bank 4 | Train 6, Bank 5 | Train 6, Bank 6 | Train 6, Bank 7 | Train 6, Bank 8 | Train 6, Bank 9 | Train 6, Bank 10 | Train 6, Bank 11 | Train 7, Bank 1 | Train 7, Bank 2 | Train 7, Bank 3 | Train 7, Bank 4 | Train 7, Bank 5 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 12
Date/Time | Target Power 2 (kW)
2005-03-06 03:45
2005-03-07 00:06
2005-03-08 00:39
2005-03-09 01:02
2005-03-10 01:30
2005-03-11 02:09
2005-03-12 02:43
2005-03-13 03:17
2005-03-14 03:45
2005-03-15 00:17
2005-03-16 03:56
2005-03-17 00:11
2005-03-18 00:45
2005-03-19 01:24
2005-03-20 01:52
2005-03-21 02:26
2005-03-22 03:11
2005-03-23 03:56
2005-03-24 03:22
2005-03-25 03:56
2005-03-26 00:22
2005-03-27 00:51
2005-03-28 01:24
2005-03-29 01:58
2005-03-30 02:54
2005-03-31 03:28
2005-04-01
2005-04-02 00:39
2005-04-03 01:08
2005-04-04 02:32
2005-04-05 03:17
2005-04-06 03:51
2005-04-07 00:17
2005-04-08 01:13
2005-04-09 01:58
2005-04-10 02:26
2005-04-11 02:49
2005-04-12 03:11
2005-04-13 03:34
2005-04-14 04:02
2005-04-15 01:30
2005-04-16 02:15
2005-04-17 02:38
2005-04-18 02:54
2005-04-19 03:28
2005-04-20 04:02
2005-04-21 00:39
2005-04-21 04:47
2005-04-22 01:41
2005-04-23 02:09
2005-04-24 02:26
2005-04-25 02:49
2005-04-26 02:26
2005-04-27 03:00
2005-04-28 03:28
2005-04-29 03:45
2005-04-30 00:11
2005-05-01 00:28
2005-05-02 00:51
2005-05-03 01:24
2005-05-04 01:52
2005-05-05 02:15
2005-05-06 02:38
2005-05-07 02:49
2005-05-08 03:11
2005-05-09 03:34
2005-05-10 03:51
2005-05-11 00:17
2005-05-12 00:34
2005-05-13 00:56
2005-05-14 01:19
2005-05-15 01:36
2005-05-16 01:58
2005-05-17 02:21
2005-05-18 02:43
2005-05-19 03:00
2005-05-20 03:17
2005-05-21 03:45
2005-05-22 00:06
2005-05-22 04:08
2005-05-23 00:17
2005-05-24 00:39
2005-05-25 01:02
2005-05-26 00:28
2005-05-27 01:02
2005-05-28 01:41
2005-05-29 02:04
2005-05-30 02:32
2005-05-31 03:00
2005-06-01 03:39
2005-06-02 03:06
2005-06-03 02:32
2005-06-04 03:00
2005-06-05 03:34
2005-06-06 04:02
2005-06-07 00:39
2005-06-08 01:08
2005-06-09 01:36
2005-06-10 02:09
2005-06-11 02:43
2005-06-12 03:11
2005-06-13 03:39
2005-06-14
2005-06-15 00:34
2005-06-16 01:02
2005-06-17 01:41
2005-06-18 02:21
2005-06-19 02:49
2005-06-20 03:17
2005-06-21 00:11
2005-06-22 00:51
2005-06-26 00:22
2005-06-27 00:51
2005-06-28 00:22
2005-06-29 03:51
2005-06-30 00:28
2005-07-01 00:51
2005-07-02 03:22
2005-07-03 03:51
2005-07-04 00:45
2005-07-05 02:38
2005-07-06 01:24
2005-07-07 01:08
2005-07-08 01:52
2005-07-09 02:21
2005-07-10 02:43
2005-07-11 03:17
2005-07-12 03:56
2005-07-13 00:28
2005-07-14 01:08
2005-07-15 01:41
2005-07-16 02:15
2005-07-17 02:38
2005-07-18 02:54
2005-07-19 03:39
2005-07-20 00:11
2005-07-21 00:51
2005-07-22 01:30
2005-07-23 02:09
2005-07-24 02:32
2005-07-25 02:54
2005-07-26 03:22
2005-07-27 02:49
2005-07-28 03:17
2005-07-29 03:51
2005-07-30 00:22
2005-07-31 00:51
2005-08-01 01:19
2005-08-02 01:52
2005-08-03 02:21
2005-08-04 02:54
2005-08-05 03:17
2005-08-06 03:39
2005-08-07 04:02
2005-08-08 00:22
2005-08-09 00:56
2005-08-10 00:22
2005-08-11
2005-08-12 00:39
2005-08-12 04:41
2005-08-13 01:08
2005-08-14 01:30
2005-08-15 01:52
2005-08-16 02:15
2005-08-17 01:36
2005-08-18 02:09
2005-08-19 02:43
2005-08-20 03:11
2005-08-21 03:34
2005-08-22 03:56
2005-08-23 00:11
2005-08-24 00:45
2005-08-25 01:19
2005-08-26 01:36
2005-08-27 02:15
2005-08-28 02:38
2005-08-29 03:06
2005-08-30 01:30
2005-08-31 02:54
2005-09-01 02:21
2005-09-02 02:43
2005-09-03 03:11
2005-09-04 03:34
2005-09-05 03:56
2005-09-06 00:11
2005-09-07 00:45
2005-09-08 01:02
2005-09-09 02:32
2005-09-10 02:54
2005-09-11 03:17
2005-09-12 03:34
2005-09-13 01:58
2005-09-14 01:24
2005-09-15 01:41
2005-09-16 02:04
2005-09-17 02:21
2005-09-18 02:43
2005-09-19 03:11
2005-09-20 03:28
2005-09-21 03:45
2005-09-22 03:17
2005-09-23 03:45
2005-09-24
2005-09-25 00:28
2005-09-26 00:56
2005-09-27 01:24
2005-09-28 03:56
2005-09-29 00:11
2005-09-30 00:34
2005-10-01 00:56
2005-10-02 01:24
2005-10-03 01:52
2005-10-04 02:15
2005-10-05 02:49
2005-10-06 03:17
2005-10-07 03:39
2005-10-08 04:02
2005-10-09 00:28
2005-10-10 00:51
2005-10-11 01:24
2005-10-12 01:52
2005-10-13 02:21
2005-10-14 02:54
2005-10-15 03:39
2005-10-16 00:06
2005-10-17 00:28
2005-10-18 00:56
2005-10-19 00:22
2005-10-19 04:30
2005-10-20 00:51
2005-10-21 01:19
2005-10-22 01:47
2005-10-23 02:21
2005-10-24 02:49
2005-10-25 03:28
2005-10-26 03:51
2005-10-27 00:34
2005-10-28 01:08
2005-10-29 01:47
2005-10-30 02:15
2005-10-31 02:43
2005-11-01 03:22
2005-11-02 03:51
2005-11-03 00:17
2005-11-04 00:45
2005-11-05 01:19
2005-11-06 01:41
2005-11-07 02:09
2005-11-08 03:17
2005-11-09 03:51
2005-11-10 00:17
2005-11-11 00:45
2005-11-12 01:24
2005-11-13 01:52
2005-11-14 02:15
2005-11-15 01:41
2005-11-16 02:21
2005-11-17 01:47
2005-11-18 02:26
2005-11-19 03:00
2005-11-20 03:28
2005-11-21 03:51
2005-11-22 00:34
2005-11-23 00:56
2005-11-24 01:36
2005-11-25 01:58
2005-11-26 02:26
2005-11-27 02:49
2005-11-28 03:22
2005-11-29 04:02
2005-11-30 00:34
2005-12-01 04:19
2005-12-02 00:51
2005-12-03 01:13
2005-12-04 01:41
2005-12-05 02:09
2005-12-06 02:43
2005-12-07 03:11
2005-12-08 03:39
2005-12-09 00:17
2005-12-10 00:45
2005-12-11 01:08
2005-12-12 01:41
2005-12-13 02:15
2005-12-14 02:54
2005-12-15 03:22
2005-12-16 03:56
2005-12-17 00:28
2005-12-18 00:56
2005-12-19 01:24
2005-12-20 01:47
2005-12-21 02:15
2005-12-22 02:43
2005-12-23 03:11
2005-12-24 03:39
2005-12-25 04:02
2005-12-26 00:22
2005-12-27 00:51
2005-12-28 01:24
2005-12-29 01:13
2005-12-30 00:39
2005-12-31 00:34
2006-01-01 01:02
2006-01-02 01:41
2006-01-03 02:09
2006-01-04 02:43
2006-01-05 01:02
2006-01-06 01:19
2006-01-07 01:47
2006-01-08 01:19
2006-01-09 01:41
2006-01-10 02:21
2006-01-11 02:43
2006-01-12 03:11
2006-01-13 03:45
2006-01-14 00:06
2006-01-15 00:34
2006-01-16 01:02
2006-01-17 01:30
2006-01-18 01:52
2006-01-19 02:21
2006-01-20 03:11
2006-01-21 02:38
2006-01-22 03:00
2006-01-23 03:34
2006-01-24 03:56
2006-01-25 00:17
2006-01-26 00:56
2006-01-27 01:41
2006-01-28 02:09
2006-01-29 02:43
2006-01-30 03:11
2006-01-31 03:34
2006-02-01 04:02
2006-02-02 00:22
2006-02-03 01:02
2006-02-04 01:24
2006-02-05 02:04
2006-02-06 02:38
2006-02-07 03:11
2006-02-08 03:34
2006-02-09 00:06
2006-02-10 00:39
2006-02-11 01:13
2006-02-12 01:36
2006-02-13 02:09
2006-02-14 02:38
2006-02-15 03:06
2006-02-16 03:28
2006-02-17 00:11
2006-02-18 00:34
2006-02-19 01:02
2006-02-20 01:30
2006-02-21 01:52
2006-02-22 02:15
2006-02-23 01:36
2006-02-24 02:09
2006-02-25 02:54
2006-02-26 03:22
2006-02-27 03:45
2006-02-28 00:06
2006-02-28 04:13
2006-03-01 00:34
2006-03-01 04:36
2006-03-02 01:08
2006-03-03 01:52
2006-03-04 02:21
2006-03-05 02:49
2006-03-06 03:22
2006-03-07 03:45
2006-03-08 00:06
2006-03-09 00:39
2006-03-10 01:02
2006-03-11 01:30
2006-03-12 02:09
2006-03-13 02:43
2006-03-14 03:17
2006-03-15 03:45
2006-03-16 00:17
2006-03-17 03:56
2006-03-18 00:11
2006-03-19 00:45
2006-03-20 01:24
2006-03-21 01:52
2006-03-22 02:26
2006-03-23 03:11
2006-03-24 03:56
2006-03-25 03:22
2006-03-26 03:56
2006-03-27 00:22
2006-03-28 00:51
2006-03-29 01:24
2006-03-30 01:58
2006-03-31 02:54
2006-04-01 03:28
2006-04-02
2006-04-03 00:39
2006-04-04 01:08
2006-04-05 02:32
2006-04-06 03:17
2006-04-07 03:51
2006-04-08 00:17
2006-04-09 01:13
2006-04-10 01:58
2006-04-11 02:26
2006-04-12 02:49
2006-04-13 03:11
2006-04-14 03:34
2006-04-15 04:02
2006-04-16 01:30
2006-04-17 02:15
2006-04-18 02:38
2006-04-19 02:54
2006-04-20 03:28
2006-04-21 04:02
2006-04-22 00:39
2006-04-23 01:41
2006-04-24 02:09
2006-04-25 02:26
2006-04-26 02:49
2006-04-27 02:26
2006-04-28 03:00
2006-04-29 03:28
2006-04-30 03:45
2006-05-01 00:11
2006-05-02 00:28
2006-05-03 00:51
2006-05-04 01:24
2006-05-05 01:52
2006-05-06 02:15
2006-05-07 02:38

## POWER 1
Train | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Reactor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Bank | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Train 1, Bank 1 | Train 1, Bank 2 | Train 1, Bank 3 | Train 1, Bank 4 | Train 1, Bank 5 | Train 1, Bank 6 | Train 1, Bank 7 | Train 1, Bank 8 | Train 1, Bank 9 | Train 1, Bank 10 | Train 1, Bank 11 | Train 2, Bank 1 | Train 2, Bank 2 | Train 2, Bank 3 | Train 2, Bank 4 | Train 2, Bank 5 | Train 2, Bank 6 | Train 2, Bank 7 | Train 2, Bank 8 | Train 2, Bank 9 | Train 2, Bank 10 | Train 2, Bank 11 | Train 3, Bank 1 | Train 3, Bank 2 | Train 3, Bank 3 | Train 3, Bank 4 | Train 3, Bank 5 | Train 3, Bank 6 | Train 3, Bank 7 | Train 3, Bank 8 | Train 3, Bank 9 | Train 3, Bank 10 | Train 3, Bank 11 | Train 4, Bank 1 | Train 4, Bank 2 | Train 4, Bank 3 | Train 4, Bank 4 | Train 4, Bank 5 | Train 4, Bank 6 | Train 4, Bank 7 | Train 4, Bank 8 | Train 4, Bank 9 | Train 4, Bank 10 | Train 4, Bank 11 | Train 5, Bank 1 | Train 5, Bank 2 | Train 5, Bank 3 | Train 5, Bank 4 | Train 5, Bank 5 | Train 5, Bank 6 | Train 5, Bank 7 | Train 5, Bank 8 | Train 5, Bank 9 | Train 5, Bank 10 | Train 5, Bank 11 | Train 6, Bank 1 | Train 6, Bank 2 | Train 6, Bank 3 | Train 6, Bank 4 | Train 6, Bank 5 | Train 6, Bank 6 | Train 6, Bank 7 | Train 6, Bank 8 | Train 6, Bank 9 | Train 6, Bank 10 | Train 6, Bank 11 | Train 7, Bank 1 | Train 7, Bank 2 | Train 7, Bank 3 | Train 7, Bank 4 | Train 7, Bank 5 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 12
Date/Time | Power 1 (kW)
2005-03-06 03:45 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-03-07 00:06 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-03-08 00:39 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342
2005-03-09 01:02 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-03-10 01:30 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-03-11 02:09 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-03-12 02:43 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-03-13 03:17 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-03-14 03:45 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-03-15 00:17 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 |  |  |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 |  |  |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-03-16 03:56 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.315 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.315
2005-03-17 00:11 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-03-18 00:45 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-03-19 01:24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-03-20 01:52 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
2005-03-21 02:26 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342
2005-03-22 03:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-03-23 03:56 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-03-24 03:22 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-03-25 03:56 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315
2005-03-26 00:22 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-03-27 00:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315
2005-03-28 01:24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2005-03-29 01:58 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306
2005-03-30 02:54 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-03-31 03:28 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-04-01 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-04-02 00:39 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.297
2005-04-03 01:08 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-04-04 02:32 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-04-05 03:17 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-04-06 03:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324
2005-04-07 00:17 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-04-08 01:13 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-04-09 01:58 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342
2005-04-10 02:26 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-04-11 02:49 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297
2005-04-12 03:11 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333 | 0.315
2005-04-13 03:34 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
2005-04-14 04:02 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288
2005-04-15 01:30 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315
2005-04-16 02:15 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-04-17 02:38 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324 | 0.306
2005-04-18 02:54 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333
2005-04-19 03:28 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306
2005-04-20 04:02 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-04-21 00:39 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-04-21 04:47 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-04-22 01:41 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324
2005-04-23 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-04-24 02:26 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.324 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.324
2005-04-25 02:49 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.315 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.315 | 0.297
2005-04-26 02:26 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-04-27 03:00 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.306 | 0.306
2005-04-28 03:28 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288
2005-04-29 03:45 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351
2005-04-30 00:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297
2005-05-01 00:28 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.288
2005-05-02 00:51 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-05-03 01:24 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306 | 0.297
2005-05-04 01:52 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-05-05 02:15 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.297 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.279 | 0.27
2005-05-06 02:38 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-05-07 02:49 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.279
2005-05-08 03:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.297
2005-05-09 03:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.297
2005-05-10 03:51 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.279
2005-05-11 00:17 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288 | 0.288
2005-05-12 00:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.315 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.315
2005-05-13 00:56 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288
2005-05-14 01:19 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-05-15 01:36 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.297
2005-05-16 01:58 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2005-05-17 02:21 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2005-05-18 02:43 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.297 | 0.288
2005-05-19 03:00 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.279 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.279 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288 | 0.279 | 0.27
2005-05-20 03:17 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-05-21 03:45 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315
2005-05-22 00:06 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-05-22 04:08 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-05-23 00:17 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-05-24 00:39 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-05-25 01:02 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27
2005-05-26 00:28 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.324 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.324 | 0.306
2005-05-27 01:02 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288
2005-05-28 01:41 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-05-29 02:04 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333
2005-05-30 02:32 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297
2005-05-31 03:00 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.306 | 0.288
2005-06-01 03:39 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297
2005-06-02 03:06 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288 | 0.279
2005-06-03 02:32 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288 | 0.279
2005-06-04 03:00 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306 | 0.297
2005-06-05 03:34 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288 | 0.279
2005-06-06 04:02 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315
2005-06-07 00:39 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297
2005-06-08 01:08 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288
2005-06-09 01:36 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-06-10 02:09 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.288
2005-06-11 02:43 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.306
2005-06-12 03:11 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-06-13 03:39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-06-14 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-06-15 00:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288
2005-06-16 01:02 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-06-17 01:41 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-06-18 02:21 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297
2005-06-19 02:49 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 |  |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-06-20 03:17 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-06-21 00:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.315 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.315 | 0.288
2005-06-22 00:51 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.288 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-06-26 00:22 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2005-06-27 00:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-06-28 00:22 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 | 0.288 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.279
2005-06-29 03:51 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306
2005-06-30 00:28 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 | 0.288 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288 | 0.279
2005-07-01 00:51 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-07-02 03:22 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2005-07-03 03:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315
2005-07-04 00:45 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-07-05 02:38 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-07-06 01:24 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-07-07 01:08 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-07-08 01:52 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-07-09 02:21 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306
2005-07-10 02:43 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27
2005-07-11 03:17 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2005-07-12 03:56 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-07-13 00:28 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-07-14 01:08 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-07-15 01:41 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-07-16 02:15 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-07-17 02:38 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306 | 0.297 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261
2005-07-18 02:54 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-07-19 03:39 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261
2005-07-20 00:11 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342
2005-07-21 00:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-07-22 01:30 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2005-07-23 02:09 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-07-24 02:32 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-07-25 02:54 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-07-26 03:22 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 | 0.315 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.306
2005-07-27 02:49 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-07-28 03:17 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-07-29 03:51 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-07-30 00:22 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2005-07-31 00:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2005-08-01 01:19 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-08-02 01:52 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297
2005-08-03 02:21 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-08-04 02:54 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-08-05 03:17 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306 | 0.297 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27
2005-08-06 03:39 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-08-07 04:02 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27
2005-08-08 00:22 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324
2005-08-09 00:56 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-08-10 00:22 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 | 0.288 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.27
2005-08-11 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288
2005-08-12 00:39 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-08-12 04:41 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.279
2005-08-13 01:08 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297
2005-08-14 01:30 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-08-15 01:52 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.279
2005-08-16 02:15 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-08-17 01:36 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.261 | 0.252
2005-08-18 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-08-19 02:43 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.288
2005-08-20 03:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-08-21 03:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-08-22 03:56 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-08-23 00:11 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.288
2005-08-24 00:45 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-08-25 01:19 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2005-08-26 01:36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333
2005-08-27 02:15 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315
2005-08-28 02:38 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-08-29 03:06 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297
2005-08-30 01:30 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2005-08-31 02:54 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-09-01 02:21 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324
2005-09-02 02:43 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.279
2005-09-03 03:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288 | 0.279 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.261
2005-09-04 03:34 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-09-05 03:56 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-09-06 00:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-09-07 00:45 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-09-08 01:02 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 | 0.297
2005-09-09 02:32 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306
2005-09-10 02:54 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 | 0.288
2005-09-11 03:17 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297
2005-09-12 03:34 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-09-13 01:58 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297
2005-09-14 01:24 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-09-15 01:41 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2005-09-16 02:04 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-09-17 02:21 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-09-18 02:43 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306 | 0.297 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-09-19 03:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2005-09-20 03:28 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.306
2005-09-21 03:45 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.288
2005-09-22 03:17 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-09-23 03:45 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-09-24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.297 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288
2005-09-25 00:28 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297
2005-09-26 00:56 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-09-27 01:24 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-09-28 03:56 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297
2005-09-29 00:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.306 | 0.288
2005-09-30 00:34 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.27
2005-10-01 00:56 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-10-02 01:24 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2005-10-03 01:52 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.288
2005-10-04 02:15 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-10-05 02:49 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-10-06 03:17 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-10-07 03:39 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-10-08 04:02 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-10-09 00:28 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-10-10 00:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2005-10-11 01:24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.297
2005-10-12 01:52 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
2005-10-13 02:21 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306
2005-10-14 02:54 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-10-15 03:39 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-10-16 00:06 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 | 0.315
2005-10-17 00:28 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-10-18 00:56 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-10-19 00:22 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-10-19 04:30 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342
2005-10-20 00:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.306
2005-10-21 01:19 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-10-22 01:47 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2005-10-23 02:21 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-10-24 02:49 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2005-10-25 03:28 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-10-26 03:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-10-27 00:34 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306
2005-10-28 01:08 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.306
2005-10-29 01:47 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.306
2005-10-30 02:15 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333
2005-10-31 02:43 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.306
2005-11-01 03:22 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-11-02 03:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2005-11-03 00:17 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297
2005-11-04 00:45 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-11-05 01:19 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-11-06 01:41 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-11-07 02:09 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-11-08 03:17 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.306 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.27
2005-11-09 03:51 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-11-10 00:17 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-11-11 00:45 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.297 |  | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279
2005-11-12 01:24 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-11-13 01:52 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-11-14 02:15 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2005-11-15 01:41 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-11-16 02:21 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342
2005-11-17 01:47 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2005-11-18 02:26 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-11-19 03:00 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-11-20 03:28 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2005-11-21 03:51 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-11-22 00:34 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.288
2005-11-23 00:56 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-11-24 01:36 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-11-25 01:58 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-11-26 02:26 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-11-27 02:49 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297
2005-11-28 03:22 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  |  |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297
2005-11-29 04:02 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-11-30 00:34 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
2005-12-01 04:19 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-12-02 00:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2005-12-03 01:13 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-12-04 01:41 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-12-05 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
2005-12-06 02:43 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-12-07 03:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.306
2005-12-08 03:39 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-12-09 00:17 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-12-10 00:45 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.324 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.324
2005-12-11 01:08 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-12-12 01:41 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2005-12-13 02:15 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2005-12-14 02:54 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2005-12-15 03:22 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2005-12-16 03:56 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2005-12-17 00:28 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2005-12-18 00:56 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2005-12-19 01:24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2005-12-20 01:47 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306
2005-12-21 02:15 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315
2005-12-22 02:43 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342
2005-12-23 03:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-12-24 03:39 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333
2005-12-25 04:02 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2005-12-26 00:22 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2005-12-27 00:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2005-12-28 01:24 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2005-12-29 01:13 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333
2005-12-30 00:39 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297
2005-12-31 00:34 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306
2006-01-01 01:02 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2006-01-02 01:41 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2006-01-03 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-01-04 02:43 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2006-01-05 01:02 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324
2006-01-06 01:19 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2006-01-07 01:47 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-01-08 01:19 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2006-01-09 01:41 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-01-10 02:21 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-01-11 02:43 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2006-01-12 03:11 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324
2006-01-13 03:45 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2006-01-14 00:06 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315
2006-01-15 00:34 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-01-16 01:02 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306
2006-01-17 01:30 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297
2006-01-18 01:52 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2006-01-19 02:21 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2006-01-20 03:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2006-01-21 02:38 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2006-01-22 03:00 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 | 0.297
2006-01-23 03:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-01-24 03:56 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288
2006-01-25 00:17 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2006-01-26 00:56 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315
2006-01-27 01:41 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2006-01-28 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-01-29 02:43 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-01-30 03:11 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2006-01-31 03:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297
2006-02-01 04:02 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-02-02 00:22 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
2006-02-03 01:02 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2006-02-04 01:24 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2006-02-05 02:04 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-02-06 02:38 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-02-07 03:11 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-02-08 03:34 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297
2006-02-09 00:06 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288
2006-02-10 00:39 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2006-02-11 01:13 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-02-12 01:36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2006-02-13 02:09 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-02-14 02:38 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306
2006-02-15 03:06 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-02-16 03:28 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-02-17 00:11 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 | 0.315
2006-02-18 00:34 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333
2006-02-19 01:02 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-02-20 01:30 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-02-21 01:52 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 | 0.315
2006-02-22 02:15 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2006-02-23 01:36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315
2006-02-24 02:09 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-02-25 02:54 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2006-02-26 03:22 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306
2006-02-27 03:45 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-02-28 00:06 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297
2006-02-28 04:13 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2006-03-01 00:34 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297
2006-03-01 04:36 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-02 01:08 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-03 01:52 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2006-03-04 02:21 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2006-03-05 02:49 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2006-03-06 03:22 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351
2006-03-07 03:45 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.288
2006-03-08 00:06 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306
2006-03-09 00:39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342
2006-03-10 01:02 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-11 01:30 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.342 | 0.333
2006-03-12 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342
2006-03-13 02:43 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2006-03-14 03:17 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-15 03:45 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306
2006-03-16 00:17 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333
2006-03-17 03:56 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-18 00:11 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333
2006-03-19 00:45 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.333 | 0.306
2006-03-20 01:24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 | 0.288
2006-03-21 01:52 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315
2006-03-22 02:26 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297
2006-03-23 03:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-03-24 03:56 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-25 03:22 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2006-03-26 03:56 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-27 00:22 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-03-28 00:51 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.288
2006-03-29 01:24 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
2006-03-30 01:58 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297
2006-03-31 02:54 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333
2006-04-01 03:28 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297
2006-04-02 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.315 | 0.306
2006-04-03 00:39 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324
2006-04-04 01:08 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 | 0.324
2006-04-05 02:32 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297
2006-04-06 03:17 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297
2006-04-07 03:51 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342
2006-04-08 00:17 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2006-04-09 01:13 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306
2006-04-10 01:58 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2006-04-11 02:26 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 | 0.315
2006-04-12 02:49 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2006-04-13 03:11 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2006-04-14 03:34 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2006-04-15 04:02 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 | 0.279
2006-04-16 01:30 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-04-17 02:15 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342
2006-04-18 02:38 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333
2006-04-19 02:54 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.297 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 | 0.279
2006-04-20 03:28 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324
2006-04-21 04:02 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.279 | 0.261
2006-04-22 00:39 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315
2006-04-23 01:41 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2006-04-24 02:09 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 |  |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 |  |  | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306 | 0.306
2006-04-25 02:26 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 |  | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279
2006-04-26 02:49 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.288 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 | 0.279 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.279 | 0.261
2006-04-27 02:26 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306
2006-04-28 03:00 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315
2006-04-29 03:28 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.342 |  | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333
2006-04-30 03:45 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.351 | 0.342 | 0.315 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.315
2006-05-01 00:11 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.306 |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.306 | 0.297
2006-05-02 00:28 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.342 | 0.306 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.351 | 0.333 | 0.306 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297
2006-05-03 00:51 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.288 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.297 | 0.27
2006-05-04 01:24 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.324 | 0.315 | 0.306
2006-05-05 01:52 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.324 | 0.315
2006-05-06 02:15 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.351 | 0.342 | 0.315 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.324 | 0.297
2006-05-07 02:38 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.333 |  | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.333 | 0.315 |  | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.288

## POWER 2
Train | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Reactor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Bank | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Train 1, Bank 1 | Train 1, Bank 2 | Train 1, Bank 3 | Train 1, Bank 4 | Train 1, Bank 5 | Train 1, Bank 6 | Train 1, Bank 7 | Train 1, Bank 8 | Train 1, Bank 9 | Train 1, Bank 10 | Train 1, Bank 11 | Train 2, Bank 1 | Train 2, Bank 2 | Train 2, Bank 3 | Train 2, Bank 4 | Train 2, Bank 5 | Train 2, Bank 6 | Train 2, Bank 7 | Train 2, Bank 8 | Train 2, Bank 9 | Train 2, Bank 10 | Train 2, Bank 11 | Train 3, Bank 1 | Train 3, Bank 2 | Train 3, Bank 3 | Train 3, Bank 4 | Train 3, Bank 5 | Train 3, Bank 6 | Train 3, Bank 7 | Train 3, Bank 8 | Train 3, Bank 9 | Train 3, Bank 10 | Train 3, Bank 11 | Train 4, Bank 1 | Train 4, Bank 2 | Train 4, Bank 3 | Train 4, Bank 4 | Train 4, Bank 5 | Train 4, Bank 6 | Train 4, Bank 7 | Train 4, Bank 8 | Train 4, Bank 9 | Train 4, Bank 10 | Train 4, Bank 11 | Train 5, Bank 1 | Train 5, Bank 2 | Train 5, Bank 3 | Train 5, Bank 4 | Train 5, Bank 5 | Train 5, Bank 6 | Train 5, Bank 7 | Train 5, Bank 8 | Train 5, Bank 9 | Train 5, Bank 10 | Train 5, Bank 11 | Train 6, Bank 1 | Train 6, Bank 2 | Train 6, Bank 3 | Train 6, Bank 4 | Train 6, Bank 5 | Train 6, Bank 6 | Train 6, Bank 7 | Train 6, Bank 8 | Train 6, Bank 9 | Train 6, Bank 10 | Train 6, Bank 11 | Train 7, Bank 1 | Train 7, Bank 2 | Train 7, Bank 3 | Train 7, Bank 4 | Train 7, Bank 5 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 12
Date/Time | Power 1 (kW)
2005-03-06 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-07 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-08 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-09 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-10 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-11 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-12 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-13 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-14 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-15 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-16 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-17 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-18 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-19 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-20 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-21 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-22 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-23 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-24 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-25 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-26 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-27 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-28 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-29 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-30 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-03-31 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-01 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-02 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-03 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-04 02:32 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-05 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-06 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-07 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-08 01:13 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-09 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-10 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-11 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-12 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-13 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-14 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-15 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-16 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-17 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-18 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-19 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-20 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-21 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-21 04:47 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-22 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-23 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-24 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-25 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-26 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-27 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-28 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-29 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-04-30 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-01 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-02 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-03 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-04 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-05 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-06 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-07 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-08 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-09 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-10 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-11 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-12 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-13 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-14 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-15 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-16 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-17 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-18 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-19 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-20 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-21 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-22 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-22 04:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-23 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-24 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-25 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-26 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-27 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-28 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-29 02:04 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-30 02:32 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-05-31 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-01 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-02 03:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-03 02:32 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-04 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-05 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-06 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-07 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-08 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-09 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-10 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-11 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-12 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-13 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-14 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-15 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-16 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-17 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-18 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-19 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-20 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-21 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-22 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-26 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-27 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-28 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-29 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-06-30 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-01 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-02 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-03 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-04 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-05 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-06 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-07 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-08 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-09 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-10 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-11 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-12 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-13 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-14 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-15 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-16 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-17 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-18 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-19 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-20 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-21 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-22 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-23 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-24 02:32 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-25 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-26 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-27 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-28 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-29 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-30 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-07-31 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-01 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-02 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-03 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-04 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-05 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-06 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-07 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-08 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-09 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-10 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-12 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-12 04:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-13 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-14 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-15 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-16 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-17 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-18 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-19 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-20 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-21 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-22 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-23 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-24 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-25 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-26 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-27 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-28 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-29 03:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-30 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-08-31 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-01 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-02 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-03 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-04 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-05 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-06 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-07 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-08 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-09 02:32 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-10 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-11 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-12 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-13 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-14 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-15 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-16 02:04 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-17 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-18 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-19 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-20 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-21 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-22 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-23 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-25 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-26 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-27 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-28 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-29 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-09-30 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-01 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-02 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-03 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-04 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-05 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-06 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-07 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-08 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-09 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-10 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-11 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-12 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-13 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-14 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-15 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-16 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-17 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-18 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-19 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-19 04:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-20 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-21 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-22 01:47 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-23 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-24 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-25 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-26 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-27 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-28 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-29 01:47 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-30 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-10-31 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-01 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-02 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-03 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-04 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-05 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-06 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-07 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-08 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-09 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-10 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-11 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-12 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-13 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-14 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-15 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-16 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-17 01:47 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-18 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-19 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-20 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-21 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-22 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-23 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-24 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-25 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-26 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-27 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-28 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-29 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-11-30 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-01 04:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-02 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-03 01:13 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-04 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-05 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-06 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-07 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-08 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-09 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-10 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-11 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-12 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-13 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-14 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-15 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-16 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-17 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-18 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-19 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-20 01:47 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-21 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-22 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-23 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-24 03:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-25 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-26 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-27 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-28 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-29 01:13 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-30 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2005-12-31 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-01 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-02 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-03 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-04 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-05 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-06 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-07 01:47 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-08 01:19 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-09 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-10 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-11 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-12 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-13 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-14 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-15 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-16 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-17 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-18 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-19 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-20 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-21 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-22 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-23 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-24 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-25 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-26 00:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-27 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-28 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-29 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-30 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-01-31 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-01 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-02 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-03 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-04 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-05 02:04 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-06 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-07 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-08 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-09 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-10 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-11 01:13 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-12 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-13 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-14 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-15 03:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-16 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-17 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-18 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-19 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-20 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-21 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-22 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-23 01:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-24 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-25 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-26 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-27 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-28 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-02-28 04:13 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-01 00:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-01 04:36 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-02 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-03 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-04 02:21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-05 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-06 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-07 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-08 00:06 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-09 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-10 01:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-11 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-12 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-13 02:43 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-14 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-15 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-16 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-17 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-18 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-19 00:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-20 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-21 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-22 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-23 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-24 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-25 03:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-26 03:56 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-27 00:22 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-28 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-29 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-30 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-03-31 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-01 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-03 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-04 01:08 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-05 02:32 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-06 03:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-07 03:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-08 00:17 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-09 01:13 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-10 01:58 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-11 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-12 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-13 03:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-14 03:34 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-15 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-16 01:30 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-17 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-18 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-19 02:54 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-20 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-21 04:02 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-22 00:39 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-23 01:41 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-24 02:09 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-25 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-26 02:49 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-27 02:26 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-28 03:00 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-29 03:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-04-30 03:45 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-01 00:11 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-02 00:28 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-03 00:51 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-04 01:24 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-05 01:52 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-06 02:15 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
2006-05-07 02:38 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18

## LAMP HOURS
Train | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Reactor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Bank | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Train 1, Bank 1 | Train 1, Bank 2 | Train 1, Bank 3 | Train 1, Bank 4 | Train 1, Bank 5 | Train 1, Bank 6 | Train 1, Bank 7 | Train 1, Bank 8 | Train 1, Bank 9 | Train 1, Bank 10 | Train 1, Bank 11 | Train 2, Bank 1 | Train 2, Bank 2 | Train 2, Bank 3 | Train 2, Bank 4 | Train 2, Bank 5 | Train 2, Bank 6 | Train 2, Bank 7 | Train 2, Bank 8 | Train 2, Bank 9 | Train 2, Bank 10 | Train 2, Bank 11 | Train 3, Bank 1 | Train 3, Bank 2 | Train 3, Bank 3 | Train 3, Bank 4 | Train 3, Bank 5 | Train 3, Bank 6 | Train 3, Bank 7 | Train 3, Bank 8 | Train 3, Bank 9 | Train 3, Bank 10 | Train 3, Bank 11 | Train 4, Bank 1 | Train 4, Bank 2 | Train 4, Bank 3 | Train 4, Bank 4 | Train 4, Bank 5 | Train 4, Bank 6 | Train 4, Bank 7 | Train 4, Bank 8 | Train 4, Bank 9 | Train 4, Bank 10 | Train 4, Bank 11 | Train 5, Bank 1 | Train 5, Bank 2 | Train 5, Bank 3 | Train 5, Bank 4 | Train 5, Bank 5 | Train 5, Bank 6 | Train 5, Bank 7 | Train 5, Bank 8 | Train 5, Bank 9 | Train 5, Bank 10 | Train 5, Bank 11 | Train 6, Bank 1 | Train 6, Bank 2 | Train 6, Bank 3 | Train 6, Bank 4 | Train 6, Bank 5 | Train 6, Bank 6 | Train 6, Bank 7 | Train 6, Bank 8 | Train 6, Bank 9 | Train 6, Bank 10 | Train 6, Bank 11 | Train 7, Bank 1 | Train 7, Bank 2 | Train 7, Bank 3 | Train 7, Bank 4 | Train 7, Bank 5 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 12
Date/Time | Lamp Hours (hrs)
2005-03-06 03:45
2005-03-07 00:06 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 |  |  | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438 | 20.3438
2005-03-08 00:39 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 20.3438 |  |  | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 44.9062 | 20.3438
2005-03-09 01:02 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 44.7188 | 24.375 |  | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 69.2812 | 44.7188 | 24.375
2005-03-10 01:30 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 69.1875 | 48.8438 |  | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 93.75 | 69.1875 | 48.8438
2005-03-11 02:09 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 93.8438 | 48.8438 |  | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 118.4062 | 93.8438 | 48.8438
2005-03-12 02:43 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 93.8438 | 48.8438 |  | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 142.9688 | 93.8438 | 48.8438
2005-03-13 03:17 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 118.4062 | 48.8438 |  | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 118.4062 | 48.8438
2005-03-14 03:45 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 167.5312 | 118.4062 | 48.8438 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 167.5312 | 118.4062 | 48.8438 |  | 24.4688 | 24.4688 | 24.4688 | 24.4688 | 24.4688 | 24.4688 | 24.4688
2005-03-15 00:17 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 188.0625 | 138.9375 | 48.8438 |  | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 212.5312 | 188.0625 | 138.9375 | 48.8438 |  | 24.4688 | 24.4688 | 24.4688 | 24.4688 | 24.4688 | 24.4688 | 24.4688
2005-03-16 03:56 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 188.0625 | 138.9375 | 48.8438 |  | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 240.1875 | 188.0625 | 138.9375 | 48.8438 |  | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-17 00:11 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 208.3125 | 159.1875 | 69.0938 | 20.25 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 260.4375 | 208.3125 | 159.1875 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-18 00:45 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 232.875 | 159.1875 | 69.0938 | 20.25 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 232.875 | 159.1875 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-19 01:24 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 257.5312 | 159.1875 | 69.0938 | 20.25 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 309.6562 | 257.5312 | 159.1875 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-20 01:52 | 334.125 | 334.125 | 334.125 | 334.125 | 334.125 | 334.125 | 334.125 | 282 | 183.6562 | 69.0938 | 20.25 | 334.125 | 334.125 | 334.125 | 334.125 | 334.125 | 334.125 | 334.125 | 282 | 183.6562 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-21 02:26 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 282 | 183.6562 | 69.0938 | 20.25 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 358.6875 | 282 | 183.6562 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-22 03:11 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 306.75 | 208.4062 | 69.0938 | 20.25 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 383.4375 | 306.75 | 208.4062 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-23 03:56 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 331.5 | 233.1562 | 69.0938 | 20.25 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 408.1875 | 331.5 | 233.1562 | 69.0938 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-24 03:22 | 431.625 | 431.625 | 431.625 | 431.625 | 431.625 | 431.625 | 431.625 | 354.9375 | 256.5938 | 92.5312 | 20.25 | 431.625 | 431.625 | 431.625 | 431.625 | 431.625 | 431.625 | 431.625 | 354.9375 | 256.5938 | 92.5312 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-25 03:56 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 379.5 | 281.1562 | 92.5312 | 20.25 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 456.1875 | 379.5 | 281.1562 | 92.5312 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-26 00:22 | 476.625 | 476.625 | 476.625 | 476.625 | 476.625 | 476.625 | 476.625 | 399.9375 | 301.5938 | 112.9688 | 20.25 | 476.625 | 476.625 | 476.625 | 476.625 | 476.625 | 476.625 | 476.625 | 399.9375 | 301.5938 | 112.9688 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-27 00:51 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 424.4062 | 326.0625 | 137.4375 | 20.25 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 501.0938 | 424.4062 | 326.0625 | 137.4375 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-28 01:24 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 448.9688 | 350.625 | 162 | 20.25 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 525.6562 | 448.9688 | 350.625 | 162 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-29 01:58 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 473.5312 | 375.1875 | 186.5625 | 20.25 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 550.2188 | 473.5312 | 375.1875 | 186.5625 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-30 02:54 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 498.4688 | 400.125 | 211.5 | 20.25 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 575.1562 | 498.4688 | 400.125 | 211.5 | 20.25 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125 | 52.125
2005-03-31 03:28 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 523.0312 | 400.125 | 211.5 | 20.25 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 599.7188 | 523.0312 | 400.125 | 211.5 | 20.25 | 76.6875 | 76.6875 | 76.6875 | 76.6875 | 76.6875 | 76.6875 | 76.6875 | 24.5625
2005-04-01 | 620.25 | 620.25 | 620.25 | 620.25 | 620.25 | 620.25 | 620.25 | 543.5625 | 400.125 | 211.5 | 20.25 | 620.25 | 620.25 | 620.25 | 620.25 | 620.25 | 620.25 | 620.25 | 543.5625 | 400.125 | 211.5 | 20.25 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 45.0938
2005-04-02 00:39 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 568.2188 | 424.7812 | 236.1562 | 20.25 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 644.9062 | 568.2188 | 424.7812 | 236.1562 | 20.25 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 45.0938
2005-04-03 01:08 | 669.375 | 669.375 | 669.375 | 669.375 | 669.375 | 669.375 | 669.375 | 592.6875 | 449.25 | 260.625 | 44.7188 | 669.375 | 669.375 | 669.375 | 669.375 | 669.375 | 669.375 | 669.375 | 592.6875 | 449.25 | 260.625 | 44.7188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 45.0938
2005-04-04 02:32 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 618.0938 | 449.25 | 260.625 | 44.7188 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 694.7812 | 618.0938 | 449.25 | 260.625 | 44.7188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 45.0938
2005-04-05 03:17 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 642.8438 | 474 | 260.625 | 44.7188 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 719.5312 | 642.8438 | 474 | 260.625 | 44.7188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 97.2188 | 45.0938
2005-04-06 03:51 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 642.8438 | 474 | 260.625 | 44.7188 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 744.0938 | 642.8438 | 474 | 260.625 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-07 00:17 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 663.2812 | 494.4375 | 281.0625 | 44.7188 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 764.5312 | 663.2812 | 494.4375 | 281.0625 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-08 01:13 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 688.2188 | 519.375 | 281.0625 | 44.7188 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 789.4688 | 688.2188 | 519.375 | 281.0625 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-09 01:58 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 712.9688 | 544.125 | 281.0625 | 44.7188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 814.2188 | 712.9688 | 544.125 | 281.0625 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-10 02:26 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 737.4375 | 568.5938 | 281.0625 | 44.7188 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 838.6875 | 737.4375 | 568.5938 | 281.0625 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-11 02:49 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 761.8125 | 568.5938 | 281.0625 | 44.7188 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 863.0625 | 761.8125 | 568.5938 | 281.0625 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-12 03:11 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 786.1875 | 592.9688 | 305.4375 | 44.7188 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 887.4375 | 786.1875 | 592.9688 | 305.4375 | 44.7188 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-13 03:34 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 810.5625 | 617.3438 | 329.8125 | 69.0938 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 911.8125 | 810.5625 | 617.3438 | 329.8125 | 69.0938 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-14 04:02 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 835.0312 | 617.3438 | 329.8125 | 69.0938 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 936.2812 | 835.0312 | 617.3438 | 329.8125 | 69.0938 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 121.7812 | 45.0938
2005-04-15 01:30 | 957.75 | 957.75 | 957.75 | 957.75 | 957.75 | 957.75 | 957.75 | 856.5 | 617.3438 | 329.8125 | 69.0938 | 957.75 | 957.75 | 957.75 | 957.75 | 957.75 | 957.75 | 957.75 | 856.5 | 617.3438 | 329.8125 | 69.0938 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-16 02:15 | 982.5 | 982.5 | 982.5 | 982.5 | 982.5 | 982.5 | 982.5 | 881.25 | 642.0938 | 329.8125 | 69.0938 | 982.5 | 982.5 | 982.5 | 982.5 | 982.5 | 982.5 | 982.5 | 881.25 | 642.0938 | 329.8125 | 69.0938 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-17 02:38 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 905.625 | 666.4688 | 354.1875 | 69.0938 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 1006.875 | 905.625 | 666.4688 | 354.1875 | 69.0938 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-18 02:54 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 929.9062 | 690.75 | 378.4688 | 93.375 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 1031.1562 | 929.9062 | 690.75 | 378.4688 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-19 03:28 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 954.4688 | 715.3125 | 403.0312 | 93.375 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 1055.7188 | 954.4688 | 715.3125 | 403.0312 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-20 04:02 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 979.0312 | 739.875 | 427.5938 | 93.375 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 1080.2812 | 979.0312 | 739.875 | 427.5938 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-21 00:39 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 999.6562 | 760.5 | 427.5938 | 93.375 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 1100.9062 | 999.6562 | 760.5 | 427.5938 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-21 04:47 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1003.7812 | 760.5 | 427.5938 | 93.375 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1105.0312 | 1003.7812 | 760.5 | 427.5938 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-22 01:41 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1024.6875 | 781.4062 | 427.5938 | 93.375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1125.9375 | 1024.6875 | 781.4062 | 427.5938 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-23 02:09 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1049.1562 | 805.875 | 452.0625 | 93.375 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1150.4062 | 1049.1562 | 805.875 | 452.0625 | 93.375 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 143.25 | 66.5625
2005-04-24 02:26 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1073.4375 | 830.1562 | 452.0625 | 93.375 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1174.6875 | 1073.4375 | 830.1562 | 452.0625 | 93.375 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 90.8438 | 24.2812 |  |  | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-04-25 02:49 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1097.8125 | 854.5312 | 476.4375 | 93.375 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1199.0625 | 1097.8125 | 854.5312 | 476.4375 | 93.375 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 90.8438 | 24.2812 |  |  | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-04-26 02:26 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1121.4375 | 878.1562 | 500.0625 | 117 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1222.6875 | 1121.4375 | 878.1562 | 500.0625 | 117 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 90.8438 | 24.2812 |  |  | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-04-27 03:00 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1146 | 902.7188 | 500.0625 | 117 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1247.25 | 1146 | 902.7188 | 500.0625 | 117 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 167.5312 | 90.8438 | 24.2812 |  |  | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-04-28 03:28 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1170.4688 | 927.1875 | 524.5312 | 141.4688 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1271.7188 | 1170.4688 | 927.1875 | 524.5312 | 141.4688 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 115.3125 | 48.75 | 24.4688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-04-29 03:45 | 1296 | 1296 | 1296 | 1296 | 1296 | 1296 | 1296 | 1194.75 | 951.4688 | 524.5312 | 141.4688 | 1296 | 1296 | 1296 | 1296 | 1296 | 1296 | 1296 | 1194.75 | 951.4688 | 524.5312 | 141.4688 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 139.5938 | 73.0312 | 24.4688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-04-30 00:11 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1215.1875 | 971.9062 | 524.5312 | 141.4688 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1316.4375 | 1215.1875 | 971.9062 | 524.5312 | 141.4688 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 139.5938 | 73.0312 | 24.4688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-01 00:28 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1239.4688 | 996.1875 | 548.8125 | 165.75 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1340.7188 | 1239.4688 | 996.1875 | 548.8125 | 165.75 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 139.5938 | 73.0312 | 24.4688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-02 00:51 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1263.8438 | 1020.5625 | 573.1875 | 190.125 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1365.0938 | 1263.8438 | 1020.5625 | 573.1875 | 190.125 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 139.5938 | 73.0312 | 24.4688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-03 01:24 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1288.4062 | 1045.125 | 597.75 | 190.125 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1389.6562 | 1288.4062 | 1045.125 | 597.75 | 190.125 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 216.2812 | 139.5938 | 73.0312 | 24.4688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-04 01:52 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1312.875 | 1069.5938 | 622.2188 | 190.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1414.125 | 1312.875 | 1069.5938 | 622.2188 | 190.125 | 240.75 | 240.75 | 240.75 | 240.75 | 240.75 | 240.75 | 240.75 | 164.0625 | 97.5 | 48.9375 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-05 02:15 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1337.25 | 1069.5938 | 622.2188 | 190.125 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1438.5 | 1337.25 | 1069.5938 | 622.2188 | 190.125 | 240.75 | 240.75 | 240.75 | 240.75 | 240.75 | 240.75 | 240.75 | 164.0625 | 97.5 | 48.9375 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-06 02:38 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1361.625 | 1093.9688 | 646.5938 | 190.125 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1462.875 | 1361.625 | 1093.9688 | 646.5938 | 190.125 | 265.125 | 265.125 | 265.125 | 265.125 | 265.125 | 265.125 | 265.125 | 188.4375 | 121.875 | 73.3125 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-07 02:49 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1385.8125 | 1118.1562 | 646.5938 | 190.125 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1487.0625 | 1385.8125 | 1118.1562 | 646.5938 | 190.125 | 289.3125 | 289.3125 | 289.3125 | 289.3125 | 289.3125 | 289.3125 | 289.3125 | 212.625 | 146.0625 | 73.3125 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-08 03:11 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1410.1875 | 1142.5312 | 670.9688 | 190.125 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1511.4375 | 1410.1875 | 1142.5312 | 670.9688 | 190.125 | 313.6875 | 313.6875 | 313.6875 | 313.6875 | 313.6875 | 313.6875 | 313.6875 | 237 | 170.4375 | 97.6875 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-09 03:34 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1434.5625 | 1166.9062 | 670.9688 | 190.125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1535.8125 | 1434.5625 | 1166.9062 | 670.9688 | 190.125 | 338.0625 | 338.0625 | 338.0625 | 338.0625 | 338.0625 | 338.0625 | 338.0625 | 261.375 | 194.8125 | 97.6875 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-10 03:51 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1458.8438 | 1191.1875 | 695.25 | 190.125 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1560.0938 | 1458.8438 | 1191.1875 | 695.25 | 190.125 | 362.3438 | 362.3438 | 362.3438 | 362.3438 | 362.3438 | 362.3438 | 362.3438 | 285.6562 | 219.0938 | 121.9688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-11 00:17 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1479.2812 | 1211.625 | 695.25 | 190.125 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1580.5312 | 1479.2812 | 1211.625 | 695.25 | 190.125 | 382.7812 | 382.7812 | 382.7812 | 382.7812 | 382.7812 | 382.7812 | 382.7812 | 306.0938 | 239.5312 | 121.9688 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-12 00:34 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1503.5625 | 1235.9062 | 719.5312 | 190.125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1604.8125 | 1503.5625 | 1235.9062 | 719.5312 | 190.125 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 330.375 | 263.8125 | 146.25 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-13 00:56 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1527.9375 | 1260.2812 | 743.9062 | 190.125 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1629.1875 | 1527.9375 | 1260.2812 | 743.9062 | 190.125 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 407.0625 | 330.375 | 263.8125 | 146.25 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-14 01:19 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1552.3125 | 1260.2812 | 743.9062 | 190.125 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1653.5625 | 1552.3125 | 1260.2812 | 743.9062 | 190.125 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 354.75 | 263.8125 | 146.25 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-15 01:36 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1576.5938 | 1284.5625 | 743.9062 | 190.125 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1677.8438 | 1576.5938 | 1284.5625 | 743.9062 | 190.125 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 431.4375 | 354.75 | 263.8125 | 146.25 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-16 01:58 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1600.9688 | 1308.9375 | 743.9062 | 190.125 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1702.2188 | 1600.9688 | 1308.9375 | 743.9062 | 190.125 | 455.8125 | 455.8125 | 455.8125 | 455.8125 | 455.8125 | 455.8125 | 455.8125 | 379.125 | 288.1875 | 146.25 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-17 02:21 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1625.3438 | 1333.3125 | 768.2812 | 190.125 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1726.5938 | 1625.3438 | 1333.3125 | 768.2812 | 190.125 | 480.1875 | 480.1875 | 480.1875 | 480.1875 | 480.1875 | 480.1875 | 480.1875 | 403.5 | 312.5625 | 170.625 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-18 02:43 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1649.7188 | 1357.6875 | 768.2812 | 190.125 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1750.9688 | 1649.7188 | 1357.6875 | 768.2812 | 190.125 | 504.5625 | 504.5625 | 504.5625 | 504.5625 | 504.5625 | 504.5625 | 504.5625 | 427.875 | 336.9375 | 170.625 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-19 03:00 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1674 | 1381.9688 | 792.5625 | 190.125 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1775.25 | 1674 | 1381.9688 | 792.5625 | 190.125 | 528.8438 | 528.8438 | 528.8438 | 528.8438 | 528.8438 | 528.8438 | 528.8438 | 452.1562 | 361.2188 | 194.9062 | 24.4688 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-20 03:17 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1698.2812 | 1406.25 | 816.8438 | 214.4062 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1799.5312 | 1698.2812 | 1406.25 | 816.8438 | 214.4062 | 553.125 | 553.125 | 553.125 | 553.125 | 553.125 | 553.125 | 553.125 | 476.4375 | 385.5 | 219.1875 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-21 03:45 | 1824 | 1824 | 1824 | 1824 | 1824 | 1824 | 1824 | 1722.75 | 1430.7188 | 816.8438 | 214.4062 | 1824 | 1824 | 1824 | 1824 | 1824 | 1824 | 1824 | 1722.75 | 1430.7188 | 816.8438 | 214.4062 | 577.5938 | 577.5938 | 577.5938 | 577.5938 | 577.5938 | 577.5938 | 577.5938 | 500.9062 | 409.9688 | 219.1875 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-22 00:06 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1743.0938 | 1451.0625 | 837.1875 | 214.4062 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1844.3438 | 1743.0938 | 1451.0625 | 837.1875 | 214.4062 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 521.25 | 430.3125 | 239.5312 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-22 04:08 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1747.125 | 1455.0938 | 841.2188 | 214.4062 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1848.375 | 1747.125 | 1455.0938 | 841.2188 | 214.4062 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 521.25 | 430.3125 | 239.5312 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-23 00:17 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1767.2812 | 1475.25 | 861.375 | 214.4062 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1868.5312 | 1767.2812 | 1475.25 | 861.375 | 214.4062 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 521.25 | 430.3125 | 239.5312 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-24 00:39 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1791.6562 | 1475.25 | 861.375 | 214.4062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1892.9062 | 1791.6562 | 1475.25 | 861.375 | 214.4062 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 597.9375 | 521.25 | 430.3125 | 239.5312 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-25 01:02 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1816.0312 | 1499.625 | 861.375 | 214.4062 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1917.2812 | 1816.0312 | 1499.625 | 861.375 | 214.4062 | 622.3125 | 622.3125 | 622.3125 | 622.3125 | 622.3125 | 622.3125 | 622.3125 | 545.625 | 454.6875 | 239.5312 | 48.75 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812 | 24.2812
2005-05-26 00:28 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1839.4688 | 1523.0625 | 884.8125 | 214.4062 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1940.7188 | 1839.4688 | 1523.0625 | 884.8125 | 214.4062 | 645.75 | 645.75 | 645.75 | 645.75 | 645.75 | 645.75 | 645.75 | 569.0625 | 478.125 | 262.9688 | 48.75 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-05-27 01:02 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1864.0312 | 1547.625 | 909.375 | 238.9688 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1965.2812 | 1864.0312 | 1547.625 | 909.375 | 238.9688 | 645.75 | 645.75 | 645.75 | 645.75 | 645.75 | 645.75 | 645.75 | 569.0625 | 478.125 | 262.9688 | 48.75 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-05-28 01:41 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1888.6875 | 1572.2812 | 934.0312 | 238.9688 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1989.9375 | 1888.6875 | 1572.2812 | 934.0312 | 238.9688 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 593.7188 | 502.7812 | 287.625 | 48.75 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-05-29 02:04 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 1913.0625 | 1596.6562 | 958.4062 | 238.9688 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 2014.3125 | 1913.0625 | 1596.6562 | 958.4062 | 238.9688 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 593.7188 | 502.7812 | 287.625 | 48.75 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-05-30 02:32 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 1937.5312 | 1621.125 | 982.875 | 238.9688 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 2038.7812 | 1937.5312 | 1621.125 | 982.875 | 238.9688 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 593.7188 | 502.7812 | 287.625 | 48.75 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-05-31 03:00 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 1962 | 1645.5938 | 1007.3438 | 263.4375 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 2063.25 | 1962 | 1645.5938 | 1007.3438 | 263.4375 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 670.4062 | 593.7188 | 502.7812 | 287.625 | 48.75 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-01 03:39 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 1986.6562 | 1670.25 | 1032 | 288.0938 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 2087.9062 | 1986.6562 | 1670.25 | 1032 | 288.0938 | 695.0625 | 695.0625 | 695.0625 | 695.0625 | 695.0625 | 695.0625 | 695.0625 | 618.375 | 527.4375 | 312.2812 | 73.4062 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-02 03:06 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2010.0938 | 1693.6875 | 1032 | 288.0938 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2111.3438 | 2010.0938 | 1693.6875 | 1032 | 288.0938 | 718.5 | 718.5 | 718.5 | 718.5 | 718.5 | 718.5 | 718.5 | 641.8125 | 550.875 | 312.2812 | 73.4062 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-03 02:32 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2033.5312 | 1717.125 | 1055.4375 | 311.5312 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2134.7812 | 2033.5312 | 1717.125 | 1055.4375 | 311.5312 | 741.9375 | 741.9375 | 741.9375 | 741.9375 | 741.9375 | 741.9375 | 741.9375 | 665.25 | 574.3125 | 335.7188 | 96.8438 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-04 03:00 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2058 | 1741.5938 | 1079.9062 | 336 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2159.25 | 2058 | 1741.5938 | 1079.9062 | 336 | 766.4062 | 766.4062 | 766.4062 | 766.4062 | 766.4062 | 766.4062 | 766.4062 | 689.7188 | 598.7812 | 360.1875 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-05 03:34 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2082.5625 | 1766.1562 | 1104.4688 | 336 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2183.8125 | 2082.5625 | 1766.1562 | 1104.4688 | 336 | 790.9688 | 790.9688 | 790.9688 | 790.9688 | 790.9688 | 790.9688 | 790.9688 | 714.2812 | 623.3438 | 384.75 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-06 04:02 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2107.0312 | 1790.625 | 1128.9375 | 336 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2208.2812 | 2107.0312 | 1790.625 | 1128.9375 | 336 | 815.4375 | 815.4375 | 815.4375 | 815.4375 | 815.4375 | 815.4375 | 815.4375 | 738.75 | 647.8125 | 409.2188 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-07 00:39 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2127.6562 | 1811.25 | 1149.5625 | 336 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2127.6562 | 1811.25 | 1149.5625 | 336 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 759.375 | 668.4375 | 429.8438 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-08 01:08 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2152.125 | 1835.7188 | 1174.0312 | 360.4688 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2228.9062 | 2127.6562 | 1811.25 | 1149.5625 | 336 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 836.0625 | 759.375 | 668.4375 | 429.8438 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-09 01:36 | 2277.8438 | 2277.8438 | 2277.8438 | 2277.8438 | 2277.8438 | 2277.8438 | 2277.8438 | 2176.5938 | 1860.1875 | 1174.0312 | 360.4688 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2253.375 | 2152.125 | 1835.7188 | 1149.5625 | 336 | 860.5312 | 860.5312 | 860.5312 | 860.5312 | 860.5312 | 860.5312 | 860.5312 | 783.8438 | 692.9062 | 429.8438 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-10 02:09 | 2302.4062 | 2302.4062 | 2302.4062 | 2302.4062 | 2302.4062 | 2302.4062 | 2302.4062 | 2201.1562 | 1884.75 | 1174.0312 | 360.4688 | 2277.9375 | 2277.9375 | 2277.9375 | 2277.9375 | 2277.9375 | 2277.9375 | 2277.9375 | 2176.6875 | 1860.2812 | 1149.5625 | 336 | 885.0938 | 885.0938 | 885.0938 | 885.0938 | 885.0938 | 885.0938 | 885.0938 | 808.4062 | 717.4688 | 429.8438 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-11 02:43 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2225.7188 | 1909.3125 | 1198.5938 | 360.4688 | 2302.5 | 2302.5 | 2302.5 | 2302.5 | 2302.5 | 2302.5 | 2302.5 | 2201.25 | 1884.8438 | 1174.125 | 336 | 909.6562 | 909.6562 | 909.6562 | 909.6562 | 909.6562 | 909.6562 | 909.6562 | 832.9688 | 742.0312 | 454.4062 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-12 03:11 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2250.1875 | 1933.7812 | 1223.0625 | 360.4688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2326.9688 | 2225.7188 | 1909.3125 | 1198.5938 | 336 | 934.125 | 934.125 | 934.125 | 934.125 | 934.125 | 934.125 | 934.125 | 857.4375 | 766.5 | 478.875 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-13 03:39 | 2375.9062 | 2375.9062 | 2375.9062 | 2375.9062 | 2375.9062 | 2375.9062 | 2375.9062 | 2274.6562 | 1958.25 | 1223.0625 | 360.4688 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2351.4375 | 2250.1875 | 1933.7812 | 1198.5938 | 336 | 958.5938 | 958.5938 | 958.5938 | 958.5938 | 958.5938 | 958.5938 | 958.5938 | 881.9062 | 790.9688 | 478.875 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-14 | 2396.25 | 2396.25 | 2396.25 | 2396.25 | 2396.25 | 2396.25 | 2396.25 | 2295 | 1978.5938 | 1243.4062 | 360.4688 | 2371.7812 | 2371.7812 | 2371.7812 | 2371.7812 | 2371.7812 | 2371.7812 | 2371.7812 | 2270.5312 | 1954.125 | 1218.9375 | 336 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 902.25 | 811.3125 | 499.2188 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-15 00:34 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2319.5625 | 2003.1562 | 1267.9688 | 360.4688 | 2396.3438 | 2396.3438 | 2396.3438 | 2396.3438 | 2396.3438 | 2396.3438 | 2396.3438 | 2295.0938 | 1978.6875 | 1243.5 | 336 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 978.9375 | 902.25 | 811.3125 | 499.2188 | 121.3125 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-16 01:02 | 2445.2812 | 2445.2812 | 2445.2812 | 2445.2812 | 2445.2812 | 2445.2812 | 2445.2812 | 2344.0312 | 2027.625 | 1292.4375 | 384.9375 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2420.8125 | 2319.5625 | 2003.1562 | 1267.9688 | 360.4688 | 1003.4062 | 1003.4062 | 1003.4062 | 1003.4062 | 1003.4062 | 1003.4062 | 1003.4062 | 926.7188 | 835.7812 | 523.6875 | 145.7812 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-17 01:41 | 2469.9375 | 2469.9375 | 2469.9375 | 2469.9375 | 2469.9375 | 2469.9375 | 2469.9375 | 2368.6875 | 2052.2812 | 1317.0938 | 384.9375 | 2445.4688 | 2445.4688 | 2445.4688 | 2445.4688 | 2445.4688 | 2445.4688 | 2445.4688 | 2344.2188 | 2027.8125 | 1292.625 | 360.4688 | 1028.0625 | 1028.0625 | 1028.0625 | 1028.0625 | 1028.0625 | 1028.0625 | 1028.0625 | 951.375 | 860.4375 | 548.3438 | 145.7812 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-18 02:21 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2393.3438 | 2076.9375 | 1317.0938 | 384.9375 | 2470.125 | 2470.125 | 2470.125 | 2470.125 | 2470.125 | 2470.125 | 2470.125 | 2368.875 | 2052.4688 | 1292.625 | 360.4688 | 1052.7188 | 1052.7188 | 1052.7188 | 1052.7188 | 1052.7188 | 1052.7188 | 1052.7188 | 976.0312 | 885.0938 | 548.3438 | 145.7812 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-19 02:49 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2417.8125 | 2101.4062 | 1341.5625 | 409.4062 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2494.5938 | 2393.3438 | 2076.9375 | 1317.0938 | 384.9375 | 1077.1875 | 1077.1875 | 1077.1875 | 1077.1875 | 1077.1875 | 1077.1875 | 1077.1875 | 1000.5 | 909.5625 | 572.8125 | 170.25 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 47.7188 | 23.4375
2005-06-20 03:17 | 2543.5312 | 2543.5312 | 2543.5312 | 2543.5312 | 2543.5312 | 2543.5312 | 2543.5312 | 2442.2812 | 2125.875 | 1341.5625 | 409.4062 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2519.0625 | 2417.8125 | 2101.4062 | 1317.0938 | 384.9375 | 1101.6562 | 1101.6562 | 1101.6562 | 1101.6562 | 1101.6562 | 1101.6562 | 1101.6562 | 1024.9688 | 934.0312 | 572.8125 | 170.25 | 72.1875 | 72.1875 | 72.1875 | 72.1875 | 72.1875 | 72.1875 | 72.1875 | 72.1875 | 72.1875 | 23.4375
2005-06-21 00:11 | 2564.4375 | 2564.4375 | 2564.4375 | 2564.4375 | 2564.4375 | 2564.4375 | 2564.4375 | 2463.1875 | 2146.7812 | 1341.5625 | 409.4062 | 2539.9688 | 2539.9688 | 2539.9688 | 2539.9688 | 2539.9688 | 2539.9688 | 2539.9688 | 2438.7188 | 2122.3125 | 1317.0938 | 384.9375 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1045.875 | 954.9375 | 572.8125 | 170.25 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 23.4375
2005-06-22 00:51 | 2589.0938 | 2589.0938 | 2589.0938 | 2589.0938 | 2589.0938 | 2589.0938 | 2589.0938 | 2487.8438 | 2171.4375 | 1366.2188 | 434.0625 | 2564.625 | 2564.625 | 2564.625 | 2564.625 | 2564.625 | 2564.625 | 2564.625 | 2463.375 | 2146.9688 | 1341.75 | 409.5938 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1122.5625 | 1045.875 | 954.9375 | 572.8125 | 170.25 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 93.0938 | 23.4375
2005-06-26 00:22 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2583.375 | 2266.9688 | 1461.75 | 529.5938 | 2660.1562 | 2660.1562 | 2660.1562 | 2660.1562 | 2660.1562 | 2660.1562 | 2660.1562 | 2558.9062 | 2242.5 | 1437.2812 | 505.125 | 1218.0938 | 1218.0938 | 1218.0938 | 1218.0938 | 1218.0938 | 1218.0938 | 1218.0938 | 1141.4062 | 1050.4688 | 668.3438 | 265.7812 | 188.625 | 188.625 | 188.625 | 188.625 | 188.625 | 188.625 | 188.625 | 188.625 | 188.625 | 118.9688 | 95.5312
2005-06-27 00:51 | 2709.0938 | 2709.0938 | 2709.0938 | 2709.0938 | 2709.0938 | 2709.0938 | 2709.0938 | 2607.8438 | 2291.4375 | 1486.2188 | 529.5938 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2684.625 | 2583.375 | 2266.9688 | 1461.75 | 505.125 | 1242.5625 | 1242.5625 | 1242.5625 | 1242.5625 | 1242.5625 | 1242.5625 | 1242.5625 | 1165.875 | 1074.9375 | 692.8125 | 265.7812 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 143.4375 | 95.5312
2005-06-28 00:22 | 2732.625 | 2732.625 | 2732.625 | 2732.625 | 2732.625 | 2732.625 | 2732.625 | 2631.375 | 2314.9688 | 1486.2188 | 529.5938 | 2708.1562 | 2708.1562 | 2708.1562 | 2708.1562 | 2708.1562 | 2708.1562 | 2708.1562 | 2606.9062 | 2290.5 | 1461.75 | 505.125 | 1266.0938 | 1266.0938 | 1266.0938 | 1266.0938 | 1266.0938 | 1266.0938 | 1266.0938 | 1189.4062 | 1098.4688 | 692.8125 | 265.7812 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 143.4375 | 95.5312
2005-06-29 03:51 | 2760.0938 | 2760.0938 | 2760.0938 | 2760.0938 | 2760.0938 | 2760.0938 | 2760.0938 | 2658.8438 | 2342.4375 | 1513.6875 | 557.0625 | 2735.625 | 2735.625 | 2735.625 | 2735.625 | 2735.625 | 2735.625 | 2735.625 | 2634.375 | 2317.9688 | 1489.2188 | 532.5938 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1216.875 | 1125.9375 | 720.2812 | 293.25 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 143.4375 | 95.5312
2005-06-30 00:28 | 2780.7188 | 2780.7188 | 2780.7188 | 2780.7188 | 2780.7188 | 2780.7188 | 2780.7188 | 2679.4688 | 2363.0625 | 1534.3125 | 557.0625 | 2756.25 | 2756.25 | 2756.25 | 2756.25 | 2756.25 | 2756.25 | 2756.25 | 2655 | 2338.5938 | 1509.8438 | 532.5938 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1293.5625 | 1216.875 | 1125.9375 | 720.2812 | 293.25 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 143.4375 | 95.5312
2005-07-01 00:51 | 2805.0938 | 2805.0938 | 2805.0938 | 2805.0938 | 2805.0938 | 2805.0938 | 2805.0938 | 2703.8438 | 2387.4375 | 1558.6875 | 581.4375 | 2780.625 | 2780.625 | 2780.625 | 2780.625 | 2780.625 | 2780.625 | 2780.625 | 2679.375 | 2362.9688 | 1534.2188 | 556.9688 | 1317.9375 | 1317.9375 | 1317.9375 | 1317.9375 | 1317.9375 | 1317.9375 | 1317.9375 | 1241.25 | 1150.3125 | 744.6562 | 317.625 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 213.0938 | 143.4375 | 95.5312
2005-07-02 03:22 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2730.375 | 2413.9688 | 1585.2188 | 581.4375 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2705.9062 | 2389.5 | 1560.75 | 556.9688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1267.7812 | 1176.8438 | 771.1875 | 317.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 169.9688 | 95.5312
2005-07-03 03:51 | 2856.0938 | 2856.0938 | 2856.0938 | 2856.0938 | 2856.0938 | 2856.0938 | 2856.0938 | 2754.8438 | 2438.4375 | 1609.6875 | 581.4375 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2831.625 | 2730.375 | 2413.9688 | 1585.2188 | 556.9688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1344.4688 | 1267.7812 | 1176.8438 | 771.1875 | 317.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 169.9688 | 95.5312
2005-07-04 00:45 | 2877 | 2877 | 2877 | 2877 | 2877 | 2877 | 2877 | 2775.75 | 2459.3438 | 1630.5938 | 581.4375 | 2852.5312 | 2852.5312 | 2852.5312 | 2852.5312 | 2852.5312 | 2852.5312 | 2852.5312 | 2751.2812 | 2434.875 | 1606.125 | 556.9688 | 1365.375 | 1365.375 | 1365.375 | 1365.375 | 1365.375 | 1365.375 | 1365.375 | 1288.6875 | 1197.75 | 792.0938 | 317.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 169.9688 | 95.5312
2005-07-05 02:38 | 2902.875 | 2902.875 | 2902.875 | 2902.875 | 2902.875 | 2902.875 | 2902.875 | 2801.625 | 2485.2188 | 1630.5938 | 581.4375 | 2878.4062 | 2878.4062 | 2878.4062 | 2878.4062 | 2878.4062 | 2878.4062 | 2878.4062 | 2777.1562 | 2460.75 | 1606.125 | 556.9688 | 1391.25 | 1391.25 | 1391.25 | 1391.25 | 1391.25 | 1391.25 | 1391.25 | 1314.5625 | 1223.625 | 792.0938 | 317.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 239.625 | 169.9688 | 95.5312
2005-07-06 01:24 | 2925.6562 | 2925.6562 | 2925.6562 | 2925.6562 | 2925.6562 | 2925.6562 | 2925.6562 | 2824.4062 | 2508 | 1653.375 | 581.4375 | 2901.1875 | 2901.1875 | 2901.1875 | 2901.1875 | 2901.1875 | 2901.1875 | 2901.1875 | 2799.9375 | 2483.5312 | 1628.9062 | 556.9688 | 1414.0312 | 1414.0312 | 1414.0312 | 1414.0312 | 1414.0312 | 1414.0312 | 1414.0312 | 1337.3438 | 1246.4062 | 814.875 | 317.625 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 192.75 | 95.5312
2005-07-07 01:08 | 2949.375 | 2949.375 | 2949.375 | 2949.375 | 2949.375 | 2949.375 | 2949.375 | 2848.125 | 2531.7188 | 1677.0938 | 581.4375 | 2924.9062 | 2924.9062 | 2924.9062 | 2924.9062 | 2924.9062 | 2924.9062 | 2924.9062 | 2823.6562 | 2507.25 | 1652.625 | 556.9688 | 1437.75 | 1437.75 | 1437.75 | 1437.75 | 1437.75 | 1437.75 | 1437.75 | 1361.0625 | 1270.125 | 838.5938 | 317.625 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 192.75 | 95.5312
2005-07-08 01:52 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2872.875 | 2556.4688 | 1677.0938 | 581.4375 | 2949.6562 | 2949.6562 | 2949.6562 | 2949.6562 | 2949.6562 | 2949.6562 | 2949.6562 | 2848.4062 | 2532 | 1652.625 | 556.9688 | 1462.5 | 1462.5 | 1462.5 | 1462.5 | 1462.5 | 1462.5 | 1462.5 | 1385.8125 | 1294.875 | 838.5938 | 317.625 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 192.75 | 95.5312
2005-07-09 02:21 | 2998.5938 | 2998.5938 | 2998.5938 | 2998.5938 | 2998.5938 | 2998.5938 | 2998.5938 | 2897.3438 | 2580.9375 | 1677.0938 | 581.4375 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2974.125 | 2872.875 | 2556.4688 | 1652.625 | 556.9688 | 1486.9688 | 1486.9688 | 1486.9688 | 1486.9688 | 1486.9688 | 1486.9688 | 1486.9688 | 1410.2812 | 1319.3438 | 838.5938 | 317.625 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 192.75 | 95.5312
2005-07-10 02:43 | 3022.9688 | 3022.9688 | 3022.9688 | 3022.9688 | 3022.9688 | 3022.9688 | 3022.9688 | 2921.7188 | 2605.3125 | 1701.4688 | 581.4375 | 2998.5 | 2998.5 | 2998.5 | 2998.5 | 2998.5 | 2998.5 | 2998.5 | 2897.25 | 2580.8438 | 1677 | 556.9688 | 1511.3438 | 1511.3438 | 1511.3438 | 1511.3438 | 1511.3438 | 1511.3438 | 1511.3438 | 1434.6562 | 1343.7188 | 862.9688 | 317.625 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 262.4062 | 192.75 | 95.5312
2005-07-11 03:17 | 3047.5312 | 3047.5312 | 3047.5312 | 3047.5312 | 3047.5312 | 3047.5312 | 3047.5312 | 2946.2812 | 2629.875 | 1726.0312 | 606 | 3023.0625 | 3023.0625 | 3023.0625 | 3023.0625 | 3023.0625 | 3023.0625 | 3023.0625 | 2921.8125 | 2605.4062 | 1701.5625 | 581.5312 | 1535.9062 | 1535.9062 | 1535.9062 | 1535.9062 | 1535.9062 | 1535.9062 | 1535.9062 | 1459.2188 | 1368.2812 | 887.5312 | 342.1875 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 217.3125 | 120.0938
2005-07-12 03:56 | 3072.1875 | 3072.1875 | 3072.1875 | 3072.1875 | 3072.1875 | 3072.1875 | 3072.1875 | 2970.9375 | 2654.5312 | 1750.6875 | 630.6562 | 3047.7188 | 3047.7188 | 3047.7188 | 3047.7188 | 3047.7188 | 3047.7188 | 3047.7188 | 2946.4688 | 2630.0625 | 1726.2188 | 606.1875 | 1560.5625 | 1560.5625 | 1560.5625 | 1560.5625 | 1560.5625 | 1560.5625 | 1560.5625 | 1483.875 | 1392.9375 | 912.1875 | 366.8438 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 286.9688 | 217.3125 | 120.0938
2005-07-13 00:28 | 3092.7188 | 3092.7188 | 3092.7188 | 3092.7188 | 3092.7188 | 3092.7188 | 3092.7188 | 2991.4688 | 2675.0625 | 1771.2188 | 630.6562 | 3068.25 | 3068.25 | 3068.25 | 3068.25 | 3068.25 | 3068.25 | 3068.25 | 2967 | 2650.5938 | 1746.75 | 606.1875 | 1581.0938 | 1581.0938 | 1581.0938 | 1581.0938 | 1581.0938 | 1581.0938 | 1581.0938 | 1504.4062 | 1413.4688 | 932.7188 | 366.8438 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 237.8438 | 120.0938 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 |  | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-14 01:08 | 3117.375 | 3117.375 | 3117.375 | 3117.375 | 3117.375 | 3117.375 | 3117.375 | 3016.125 | 2699.7188 | 1795.875 | 655.3125 | 3092.9062 | 3092.9062 | 3092.9062 | 3092.9062 | 3092.9062 | 3092.9062 | 3092.9062 | 2991.6562 | 2675.25 | 1771.4062 | 630.8438 | 1605.75 | 1605.75 | 1605.75 | 1605.75 | 1605.75 | 1605.75 | 1605.75 | 1529.0625 | 1438.125 | 957.375 | 391.5 | 332.1562 | 332.1562 | 332.1562 | 332.1562 | 332.1562 | 332.1562 | 332.1562 | 332.1562 | 332.1562 | 262.5 | 144.75 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 45.1875 | 24.6562 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-15 01:41 | 3141.9375 | 3141.9375 | 3141.9375 | 3141.9375 | 3141.9375 | 3141.9375 | 3141.9375 | 3040.6875 | 2724.2812 | 1820.4375 | 655.3125 | 3117.4688 | 3117.4688 | 3117.4688 | 3117.4688 | 3117.4688 | 3117.4688 | 3117.4688 | 3016.2188 | 2699.8125 | 1795.9688 | 630.8438 | 1630.3125 | 1630.3125 | 1630.3125 | 1630.3125 | 1630.3125 | 1630.3125 | 1630.3125 | 1553.625 | 1462.6875 | 981.9375 | 391.5 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 287.0625 | 144.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 24.6562 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-16 02:15 | 3166.5 | 3166.5 | 3166.5 | 3166.5 | 3166.5 | 3166.5 | 3166.5 | 3065.25 | 2748.8438 | 1820.4375 | 655.3125 | 3142.0312 | 3142.0312 | 3142.0312 | 3142.0312 | 3142.0312 | 3142.0312 | 3142.0312 | 3040.7812 | 2724.375 | 1795.9688 | 630.8438 | 1654.875 | 1654.875 | 1654.875 | 1654.875 | 1654.875 | 1654.875 | 1654.875 | 1578.1875 | 1487.25 | 981.9375 | 391.5 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 287.0625 | 144.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 24.6562 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-17 02:38 | 3190.875 | 3190.875 | 3190.875 | 3190.875 | 3190.875 | 3190.875 | 3190.875 | 3089.625 | 2773.2188 | 1820.4375 | 655.3125 | 3166.4062 | 3166.4062 | 3166.4062 | 3166.4062 | 3166.4062 | 3166.4062 | 3166.4062 | 3065.1562 | 2748.75 | 1795.9688 | 630.8438 | 1679.25 | 1679.25 | 1679.25 | 1679.25 | 1679.25 | 1679.25 | 1679.25 | 1602.5625 | 1511.625 | 981.9375 | 391.5 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 356.7188 | 287.0625 | 144.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 24.6562 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-18 02:54 | 3215.1562 | 3215.1562 | 3215.1562 | 3215.1562 | 3215.1562 | 3215.1562 | 3215.1562 | 3113.9062 | 2797.5 | 1844.7188 | 679.5938 | 3190.6875 | 3190.6875 | 3190.6875 | 3190.6875 | 3190.6875 | 3190.6875 | 3190.6875 | 3089.4375 | 2773.0312 | 1820.25 | 655.125 | 1703.5312 | 1703.5312 | 1703.5312 | 1703.5312 | 1703.5312 | 1703.5312 | 1703.5312 | 1626.8438 | 1535.9062 | 1006.2188 | 415.7812 | 381 | 381 | 381 | 381 | 381 | 381 | 381 | 381 | 381 | 311.3438 | 169.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 94.0312 | 48.9375 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-19 03:39 | 3239.9062 | 3239.9062 | 3239.9062 | 3239.9062 | 3239.9062 | 3239.9062 | 3239.9062 | 3138.6562 | 2822.25 | 1869.4688 | 679.5938 | 3215.4375 | 3215.4375 | 3215.4375 | 3215.4375 | 3215.4375 | 3215.4375 | 3215.4375 | 3114.1875 | 2797.7812 | 1845 | 655.125 | 1728.2812 | 1728.2812 | 1728.2812 | 1728.2812 | 1728.2812 | 1728.2812 | 1728.2812 | 1651.5938 | 1560.6562 | 1030.9688 | 415.7812 | 405.75 | 405.75 | 405.75 | 405.75 | 405.75 | 405.75 | 405.75 | 405.75 | 405.75 | 336.0938 | 169.0312 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 118.7812 | 48.9375 | 45.2812 | 45.2812 | 45.2812 | 45.2812 | 45.2812 | 45.2812 | 45.2812 | 45.2812 | 45.2812 | 45.2812
2005-07-20 00:11 | 3260.4375 | 3260.4375 | 3260.4375 | 3260.4375 | 3260.4375 | 3260.4375 | 3260.4375 | 3159.1875 | 2842.7812 | 1890 | 700.125 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3134.7188 | 2818.3125 | 1865.5312 | 675.6562 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1672.125 | 1581.1875 | 1051.5 | 436.3125 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 356.625 | 189.5625 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 69.4688 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-21 00:51 | 3285.0938 | 3285.0938 | 3285.0938 | 3285.0938 | 3285.0938 | 3285.0938 | 3285.0938 | 3183.8438 | 2867.4375 | 1914.6562 | 700.125 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3235.9688 | 3134.7188 | 2818.3125 | 1865.5312 | 675.6562 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1748.8125 | 1672.125 | 1581.1875 | 1051.5 | 436.3125 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 426.2812 | 356.625 | 189.5625 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 139.3125 | 69.4688 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-22 01:30 | 3309.75 | 3309.75 | 3309.75 | 3309.75 | 3309.75 | 3309.75 | 3309.75 | 3208.5 | 2892.0938 | 1939.3125 | 724.7812 | 3260.625 | 3260.625 | 3260.625 | 3260.625 | 3260.625 | 3260.625 | 3260.625 | 3159.375 | 2842.9688 | 1890.1875 | 700.3125 | 1773.4688 | 1773.4688 | 1773.4688 | 1773.4688 | 1773.4688 | 1773.4688 | 1773.4688 | 1696.7812 | 1605.8438 | 1076.1562 | 460.9688 | 450.9375 | 450.9375 | 450.9375 | 450.9375 | 450.9375 | 450.9375 | 450.9375 | 450.9375 | 450.9375 | 381.2812 | 214.2188 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-23 02:09 | 3334.4062 | 3334.4062 | 3334.4062 | 3334.4062 | 3334.4062 | 3334.4062 | 3334.4062 | 3233.1562 | 2916.75 | 1963.9688 | 749.4375 | 3285.2812 | 3285.2812 | 3285.2812 | 3285.2812 | 3285.2812 | 3285.2812 | 3285.2812 | 3184.0312 | 2867.625 | 1914.8438 | 724.9688 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1721.4375 | 1630.5 | 1100.8125 | 485.625 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 405.9375 | 238.875 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-24 02:32 | 3358.7812 | 3358.7812 | 3358.7812 | 3358.7812 | 3358.7812 | 3358.7812 | 3358.7812 | 3257.5312 | 2941.125 | 1988.3438 | 749.4375 | 3309.6562 | 3309.6562 | 3309.6562 | 3309.6562 | 3309.6562 | 3309.6562 | 3309.6562 | 3208.4062 | 2892 | 1939.2188 | 724.9688 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1798.125 | 1721.4375 | 1630.5 | 1100.8125 | 485.625 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 475.5938 | 405.9375 | 238.875 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 163.9688 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-25 02:54 | 3383.1562 | 3383.1562 | 3383.1562 | 3383.1562 | 3383.1562 | 3383.1562 | 3383.1562 | 3281.9062 | 2965.5 | 2012.7188 | 749.4375 | 3334.0312 | 3334.0312 | 3334.0312 | 3334.0312 | 3334.0312 | 3334.0312 | 3334.0312 | 3232.7812 | 2916.375 | 1963.5938 | 724.9688 | 1822.5 | 1822.5 | 1822.5 | 1822.5 | 1822.5 | 1822.5 | 1822.5 | 1745.8125 | 1654.875 | 1125.1875 | 485.625 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 430.3125 | 238.875 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-26 03:22 | 3407.625 | 3407.625 | 3407.625 | 3407.625 | 3407.625 | 3407.625 | 3407.625 | 3306.375 | 2989.9688 | 2012.7188 | 749.4375 | 3358.5 | 3358.5 | 3358.5 | 3358.5 | 3358.5 | 3358.5 | 3358.5 | 3257.25 | 2940.8438 | 1963.5938 | 724.9688 | 1846.9688 | 1846.9688 | 1846.9688 | 1846.9688 | 1846.9688 | 1846.9688 | 1846.9688 | 1770.2812 | 1679.3438 | 1125.1875 | 485.625 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 430.3125 | 238.875 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-27 02:49 | 3431.0625 | 3431.0625 | 3431.0625 | 3431.0625 | 3431.0625 | 3431.0625 | 3431.0625 | 3329.8125 | 3013.4062 | 2036.1562 | 772.875 | 3381.9375 | 3381.9375 | 3381.9375 | 3381.9375 | 3381.9375 | 3381.9375 | 3381.9375 | 3280.6875 | 2964.2812 | 1987.0312 | 748.4062 | 1870.4062 | 1870.4062 | 1870.4062 | 1870.4062 | 1870.4062 | 1870.4062 | 1870.4062 | 1793.7188 | 1702.7812 | 1148.625 | 509.0625 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 430.3125 | 238.875 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-28 03:17 | 3455.5312 | 3455.5312 | 3455.5312 | 3455.5312 | 3455.5312 | 3455.5312 | 3455.5312 | 3354.2812 | 3037.875 | 2036.1562 | 772.875 | 3406.4062 | 3406.4062 | 3406.4062 | 3406.4062 | 3406.4062 | 3406.4062 | 3406.4062 | 3305.1562 | 2988.75 | 1987.0312 | 748.4062 | 1894.875 | 1894.875 | 1894.875 | 1894.875 | 1894.875 | 1894.875 | 1894.875 | 1818.1875 | 1727.25 | 1148.625 | 509.0625 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 499.9688 | 430.3125 | 238.875 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-29 03:51 | 3480.0938 | 3480.0938 | 3480.0938 | 3480.0938 | 3480.0938 | 3480.0938 | 3480.0938 | 3378.8438 | 3062.4375 | 2060.7188 | 772.875 | 3430.9688 | 3430.9688 | 3430.9688 | 3430.9688 | 3430.9688 | 3430.9688 | 3430.9688 | 3329.7188 | 3013.3125 | 2011.5938 | 748.4062 | 1919.4375 | 1919.4375 | 1919.4375 | 1919.4375 | 1919.4375 | 1919.4375 | 1919.4375 | 1842.75 | 1751.8125 | 1173.1875 | 509.0625 | 524.5312 | 524.5312 | 524.5312 | 524.5312 | 524.5312 | 524.5312 | 524.5312 | 524.5312 | 524.5312 | 454.875 | 238.875 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 188.3438 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-30 00:22 | 3500.625 | 3500.625 | 3500.625 | 3500.625 | 3500.625 | 3500.625 | 3500.625 | 3399.375 | 3082.9688 | 2081.25 | 772.875 | 3451.5 | 3451.5 | 3451.5 | 3451.5 | 3451.5 | 3451.5 | 3451.5 | 3350.25 | 3033.8438 | 2032.125 | 748.4062 | 1939.9688 | 1939.9688 | 1939.9688 | 1939.9688 | 1939.9688 | 1939.9688 | 1939.9688 | 1863.2812 | 1772.3438 | 1193.7188 | 509.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 475.4062 | 238.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-07-31 00:51 | 3525.0938 | 3525.0938 | 3525.0938 | 3525.0938 | 3525.0938 | 3525.0938 | 3525.0938 | 3423.8438 | 3107.4375 | 2105.7188 | 797.3438 | 3475.9688 | 3475.9688 | 3475.9688 | 3475.9688 | 3475.9688 | 3475.9688 | 3475.9688 | 3374.7188 | 3058.3125 | 2056.5938 | 772.875 | 1964.4375 | 1964.4375 | 1964.4375 | 1964.4375 | 1964.4375 | 1964.4375 | 1964.4375 | 1887.75 | 1796.8125 | 1218.1875 | 533.5312 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 475.4062 | 238.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-01 01:19 | 3549.5625 | 3549.5625 | 3549.5625 | 3549.5625 | 3549.5625 | 3549.5625 | 3549.5625 | 3448.3125 | 3131.9062 | 2130.1875 | 797.3438 | 3500.4375 | 3500.4375 | 3500.4375 | 3500.4375 | 3500.4375 | 3500.4375 | 3500.4375 | 3399.1875 | 3082.7812 | 2081.0625 | 772.875 | 1988.9062 | 1988.9062 | 1988.9062 | 1988.9062 | 1988.9062 | 1988.9062 | 1988.9062 | 1912.2188 | 1821.2812 | 1242.6562 | 533.5312 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 545.0625 | 475.4062 | 238.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-02 01:52 | 3574.125 | 3574.125 | 3574.125 | 3574.125 | 3574.125 | 3574.125 | 3574.125 | 3472.875 | 3156.4688 | 2130.1875 | 797.3438 | 3525 | 3525 | 3525 | 3525 | 3525 | 3525 | 3525 | 3423.75 | 3107.3438 | 2081.0625 | 772.875 | 2013.4688 | 2013.4688 | 2013.4688 | 2013.4688 | 2013.4688 | 2013.4688 | 2013.4688 | 1936.7812 | 1845.8438 | 1242.6562 | 533.5312 | 569.625 | 569.625 | 569.625 | 569.625 | 569.625 | 569.625 | 569.625 | 569.625 | 569.625 | 475.4062 | 238.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-03 02:21 | 3598.5938 | 3598.5938 | 3598.5938 | 3598.5938 | 3598.5938 | 3598.5938 | 3598.5938 | 3497.3438 | 3180.9375 | 2154.6562 | 797.3438 | 3549.4688 | 3549.4688 | 3549.4688 | 3549.4688 | 3549.4688 | 3549.4688 | 3549.4688 | 3448.2188 | 3131.8125 | 2105.5312 | 772.875 | 2037.9375 | 2037.9375 | 2037.9375 | 2037.9375 | 2037.9375 | 2037.9375 | 2037.9375 | 1961.25 | 1870.3125 | 1267.125 | 533.5312 | 594.0938 | 594.0938 | 594.0938 | 594.0938 | 594.0938 | 594.0938 | 594.0938 | 594.0938 | 594.0938 | 499.875 | 238.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-04 02:54 | 3623.1562 | 3623.1562 | 3623.1562 | 3623.1562 | 3623.1562 | 3623.1562 | 3623.1562 | 3521.9062 | 3205.5 | 2179.2188 | 797.3438 | 3574.0312 | 3574.0312 | 3574.0312 | 3574.0312 | 3574.0312 | 3574.0312 | 3574.0312 | 3472.7812 | 3156.375 | 2130.0938 | 772.875 | 2062.5 | 2062.5 | 2062.5 | 2062.5 | 2062.5 | 2062.5 | 2062.5 | 1985.8125 | 1894.875 | 1291.6875 | 533.5312 | 618.6562 | 618.6562 | 618.6562 | 618.6562 | 618.6562 | 618.6562 | 618.6562 | 618.6562 | 618.6562 | 524.4375 | 238.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 208.875 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-05 03:17 | 3647.5312 | 3647.5312 | 3647.5312 | 3647.5312 | 3647.5312 | 3647.5312 | 3647.5312 | 3546.2812 | 3229.875 | 2203.5938 | 797.3438 | 3598.4062 | 3598.4062 | 3598.4062 | 3598.4062 | 3598.4062 | 3598.4062 | 3598.4062 | 3497.1562 | 3180.75 | 2154.4688 | 772.875 | 2086.875 | 2086.875 | 2086.875 | 2086.875 | 2086.875 | 2086.875 | 2086.875 | 2010.1875 | 1919.25 | 1316.0625 | 533.5312 | 643.0312 | 643.0312 | 643.0312 | 643.0312 | 643.0312 | 643.0312 | 643.0312 | 643.0312 | 643.0312 | 548.8125 | 238.875 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-06 03:39 | 3671.9062 | 3671.9062 | 3671.9062 | 3671.9062 | 3671.9062 | 3671.9062 | 3671.9062 | 3570.6562 | 3254.25 | 2227.9688 | 821.7188 | 3622.7812 | 3622.7812 | 3622.7812 | 3622.7812 | 3622.7812 | 3622.7812 | 3622.7812 | 3521.5312 | 3205.125 | 2178.8438 | 797.25 | 2111.25 | 2111.25 | 2111.25 | 2111.25 | 2111.25 | 2111.25 | 2111.25 | 2034.5625 | 1943.625 | 1340.4375 | 557.9062 | 667.4062 | 667.4062 | 667.4062 | 667.4062 | 667.4062 | 667.4062 | 667.4062 | 667.4062 | 667.4062 | 573.1875 | 263.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 233.25 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-07 04:02 | 3696.2812 | 3696.2812 | 3696.2812 | 3696.2812 | 3696.2812 | 3696.2812 | 3696.2812 | 3595.0312 | 3278.625 | 2252.3438 | 821.7188 | 3647.1562 | 3647.1562 | 3647.1562 | 3647.1562 | 3647.1562 | 3647.1562 | 3647.1562 | 3545.9062 | 3229.5 | 2203.2188 | 797.25 | 2135.625 | 2135.625 | 2135.625 | 2135.625 | 2135.625 | 2135.625 | 2135.625 | 2058.9375 | 1968 | 1364.8125 | 557.9062 | 691.7812 | 691.7812 | 691.7812 | 691.7812 | 691.7812 | 691.7812 | 691.7812 | 691.7812 | 691.7812 | 597.5625 | 263.25 | 257.625 | 257.625 | 257.625 | 257.625 | 257.625 | 257.625 | 257.625 | 257.625 | 257.625 | 257.625 | 94.125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-08 00:22 | 3716.625 | 3716.625 | 3716.625 | 3716.625 | 3716.625 | 3716.625 | 3716.625 | 3615.375 | 3298.9688 | 2272.6875 | 842.0625 | 3667.5 | 3667.5 | 3667.5 | 3667.5 | 3667.5 | 3667.5 | 3667.5 | 3566.25 | 3249.8438 | 2223.5625 | 817.5938 | 2155.9688 | 2155.9688 | 2155.9688 | 2155.9688 | 2155.9688 | 2155.9688 | 2155.9688 | 2079.2812 | 1988.3438 | 1385.1562 | 578.25 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 617.9062 | 283.5938 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 114.4688 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-09 00:56 | 3741.1875 | 3741.1875 | 3741.1875 | 3741.1875 | 3741.1875 | 3741.1875 | 3741.1875 | 3639.9375 | 3323.5312 | 2297.25 | 842.0625 | 3692.0625 | 3692.0625 | 3692.0625 | 3692.0625 | 3692.0625 | 3692.0625 | 3692.0625 | 3590.8125 | 3274.4062 | 2248.125 | 817.5938 | 2180.5312 | 2180.5312 | 2180.5312 | 2180.5312 | 2180.5312 | 2180.5312 | 2180.5312 | 2103.8438 | 2012.9062 | 1409.7188 | 578.25 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 617.9062 | 283.5938 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 114.4688 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-10 00:22 | 3764.625 | 3764.625 | 3764.625 | 3764.625 | 3764.625 | 3764.625 | 3764.625 | 3663.375 | 3346.9688 | 2320.6875 | 842.0625 | 3715.5 | 3715.5 | 3715.5 | 3715.5 | 3715.5 | 3715.5 | 3715.5 | 3614.25 | 3297.8438 | 2271.5625 | 817.5938 | 2203.9688 | 2203.9688 | 2203.9688 | 2203.9688 | 2203.9688 | 2203.9688 | 2203.9688 | 2127.2812 | 2036.3438 | 1433.1562 | 578.25 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 712.125 | 617.9062 | 283.5938 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 277.9688 | 114.4688 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-11 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3687 | 3370.5938 | 2344.3125 | 865.6875 | 3739.125 | 3739.125 | 3739.125 | 3739.125 | 3739.125 | 3739.125 | 3739.125 | 3637.875 | 3321.4688 | 2295.1875 | 841.2188 | 2227.5938 | 2227.5938 | 2227.5938 | 2227.5938 | 2227.5938 | 2227.5938 | 2227.5938 | 2150.9062 | 2059.9688 | 1456.7812 | 601.875 | 735.75 | 735.75 | 735.75 | 735.75 | 735.75 | 735.75 | 735.75 | 735.75 | 735.75 | 641.5312 | 307.2188 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 301.5938 | 138.0938 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-12 00:39 | 3812.9062 | 3812.9062 | 3812.9062 | 3812.9062 | 3812.9062 | 3812.9062 | 3812.9062 | 3711.6562 | 3395.25 | 2368.9688 | 890.3438 | 3763.7812 | 3763.7812 | 3763.7812 | 3763.7812 | 3763.7812 | 3763.7812 | 3763.7812 | 3662.5312 | 3346.125 | 2319.8438 | 865.875 | 2252.25 | 2252.25 | 2252.25 | 2252.25 | 2252.25 | 2252.25 | 2252.25 | 2175.5625 | 2084.625 | 1481.4375 | 626.5312 | 760.4062 | 760.4062 | 760.4062 | 760.4062 | 760.4062 | 760.4062 | 760.4062 | 760.4062 | 760.4062 | 666.1875 | 331.875 | 326.25 | 326.25 | 326.25 | 326.25 | 326.25 | 326.25 | 326.25 | 326.25 | 326.25 | 326.25 | 162.75 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-12 04:41 | 3816.9375 | 3816.9375 | 3816.9375 | 3816.9375 | 3816.9375 | 3816.9375 | 3816.9375 | 3715.6875 | 3399.2812 | 2373 | 890.3438 | 3767.8125 | 3767.8125 | 3767.8125 | 3767.8125 | 3767.8125 | 3767.8125 | 3767.8125 | 3666.5625 | 3350.1562 | 2323.875 | 865.875 | 2256.2812 | 2256.2812 | 2256.2812 | 2256.2812 | 2256.2812 | 2256.2812 | 2256.2812 | 2179.5938 | 2088.6562 | 1485.4688 | 626.5312 | 764.4375 | 764.4375 | 764.4375 | 764.4375 | 764.4375 | 764.4375 | 764.4375 | 764.4375 | 764.4375 | 670.2188 | 331.875 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 162.75 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-13 01:08 | 3837.375 | 3837.375 | 3837.375 | 3837.375 | 3837.375 | 3837.375 | 3837.375 | 3736.125 | 3419.7188 | 2393.4375 | 910.7812 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3788.25 | 3687 | 3370.5938 | 2344.3125 | 886.3125 | 2276.7188 | 2276.7188 | 2276.7188 | 2276.7188 | 2276.7188 | 2276.7188 | 2276.7188 | 2200.0312 | 2109.0938 | 1505.9062 | 646.9688 | 784.875 | 784.875 | 784.875 | 784.875 | 784.875 | 784.875 | 784.875 | 784.875 | 784.875 | 690.6562 | 352.3125 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 162.75 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-14 01:30 | 3861.75 | 3861.75 | 3861.75 | 3861.75 | 3861.75 | 3861.75 | 3861.75 | 3760.5 | 3444.0938 | 2417.8125 | 935.1562 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3711.375 | 3394.9688 | 2368.6875 | 910.6875 | 2301.0938 | 2301.0938 | 2301.0938 | 2301.0938 | 2301.0938 | 2301.0938 | 2301.0938 | 2224.4062 | 2133.4688 | 1530.2812 | 671.3438 | 809.25 | 809.25 | 809.25 | 809.25 | 809.25 | 809.25 | 809.25 | 809.25 | 809.25 | 715.0312 | 376.6875 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 162.75 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-15 01:52 | 3886.125 | 3886.125 | 3886.125 | 3886.125 | 3886.125 | 3886.125 | 3886.125 | 3784.875 | 3468.4688 | 2442.1875 | 935.1562 | 3837 | 3837 | 3837 | 3837 | 3837 | 3837 | 3837 | 3735.75 | 3419.3438 | 2393.0625 | 910.6875 | 2325.4688 | 2325.4688 | 2325.4688 | 2325.4688 | 2325.4688 | 2325.4688 | 2325.4688 | 2248.7812 | 2157.8438 | 1554.6562 | 671.3438 | 833.625 | 833.625 | 833.625 | 833.625 | 833.625 | 833.625 | 833.625 | 833.625 | 833.625 | 739.4062 | 376.6875 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 162.75 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-16 02:15 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3809.25 | 3492.8438 | 2466.5625 | 959.5312 | 3861.375 | 3861.375 | 3861.375 | 3861.375 | 3861.375 | 3861.375 | 3861.375 | 3760.125 | 3443.7188 | 2417.4375 | 935.0625 | 2349.8438 | 2349.8438 | 2349.8438 | 2349.8438 | 2349.8438 | 2349.8438 | 2349.8438 | 2273.1562 | 2182.2188 | 1579.0312 | 695.7188 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 763.7812 | 401.0625 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 330.2812 | 162.75 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 65.8125 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312 | 20.5312
2005-08-17 01:36 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3832.5938 | 3516.1875 | 2489.9062 | 959.5312 | 3884.7188 | 3884.7188 | 3884.7188 | 3884.7188 | 3884.7188 | 3884.7188 | 3884.7188 | 3783.4688 | 3467.0625 | 2440.7812 | 935.0625 | 2373.1875 | 2373.1875 | 2373.1875 | 2373.1875 | 2373.1875 | 2373.1875 | 2373.1875 | 2296.5 | 2205.5625 | 1602.375 | 695.7188 | 881.3438 | 881.3438 | 881.3438 | 881.3438 | 881.3438 | 881.3438 | 881.3438 | 881.3438 | 881.3438 | 787.125 | 401.0625 | 353.625 | 353.625 | 353.625 | 353.625 | 353.625 | 353.625 | 353.625 | 353.625 | 353.625 | 353.625 | 162.75 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 89.1562 | 20.5312 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-18 02:09 | 3958.4062 | 3958.4062 | 3958.4062 | 3958.4062 | 3958.4062 | 3958.4062 | 3958.4062 | 3857.1562 | 3540.75 | 2514.4688 | 984.0938 | 3909.2812 | 3909.2812 | 3909.2812 | 3909.2812 | 3909.2812 | 3909.2812 | 3909.2812 | 3808.0312 | 3491.625 | 2465.3438 | 959.625 | 2397.75 | 2397.75 | 2397.75 | 2397.75 | 2397.75 | 2397.75 | 2397.75 | 2321.0625 | 2230.125 | 1626.9375 | 720.2812 | 905.9062 | 905.9062 | 905.9062 | 905.9062 | 905.9062 | 905.9062 | 905.9062 | 905.9062 | 905.9062 | 811.6875 | 425.625 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-19 02:43 | 3982.9688 | 3982.9688 | 3982.9688 | 3982.9688 | 3982.9688 | 3982.9688 | 3982.9688 | 3881.7188 | 3565.3125 | 2539.0312 | 984.0938 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3933.8438 | 3832.5938 | 3516.1875 | 2489.9062 | 959.625 | 2422.3125 | 2422.3125 | 2422.3125 | 2422.3125 | 2422.3125 | 2422.3125 | 2422.3125 | 2345.625 | 2254.6875 | 1651.5 | 720.2812 | 930.4688 | 930.4688 | 930.4688 | 930.4688 | 930.4688 | 930.4688 | 930.4688 | 930.4688 | 930.4688 | 836.25 | 425.625 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-20 03:11 | 4007.4375 | 4007.4375 | 4007.4375 | 4007.4375 | 4007.4375 | 4007.4375 | 4007.4375 | 3906.1875 | 3589.7812 | 2563.5 | 1008.5625 | 3958.3125 | 3958.3125 | 3958.3125 | 3958.3125 | 3958.3125 | 3958.3125 | 3958.3125 | 3857.0625 | 3540.6562 | 2514.375 | 984.0938 | 2446.7812 | 2446.7812 | 2446.7812 | 2446.7812 | 2446.7812 | 2446.7812 | 2446.7812 | 2370.0938 | 2279.1562 | 1675.9688 | 744.75 | 954.9375 | 954.9375 | 954.9375 | 954.9375 | 954.9375 | 954.9375 | 954.9375 | 954.9375 | 954.9375 | 860.7188 | 450.0938 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 378.1875 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-21 03:34 | 4031.8125 | 4031.8125 | 4031.8125 | 4031.8125 | 4031.8125 | 4031.8125 | 4031.8125 | 3930.5625 | 3614.1562 | 2587.875 | 1008.5625 | 3982.6875 | 3982.6875 | 3982.6875 | 3982.6875 | 3982.6875 | 3982.6875 | 3982.6875 | 3881.4375 | 3565.0312 | 2538.75 | 984.0938 | 2471.1562 | 2471.1562 | 2471.1562 | 2471.1562 | 2471.1562 | 2471.1562 | 2471.1562 | 2394.4688 | 2303.5312 | 1700.3438 | 744.75 | 979.3125 | 979.3125 | 979.3125 | 979.3125 | 979.3125 | 979.3125 | 979.3125 | 979.3125 | 979.3125 | 885.0938 | 450.0938 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-22 03:56 | 4056.1875 | 4056.1875 | 4056.1875 | 4056.1875 | 4056.1875 | 4056.1875 | 4056.1875 | 3954.9375 | 3638.5312 | 2612.25 | 1008.5625 | 4007.0625 | 4007.0625 | 4007.0625 | 4007.0625 | 4007.0625 | 4007.0625 | 4007.0625 | 3905.8125 | 3589.4062 | 2563.125 | 984.0938 | 2495.5312 | 2495.5312 | 2495.5312 | 2495.5312 | 2495.5312 | 2495.5312 | 2495.5312 | 2418.8438 | 2327.9062 | 1724.7188 | 744.75 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 909.4688 | 450.0938 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-23 00:11 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 3975.1875 | 3658.7812 | 2612.25 | 1008.5625 | 4027.3125 | 4027.3125 | 4027.3125 | 4027.3125 | 4027.3125 | 4027.3125 | 4027.3125 | 3926.0625 | 3609.6562 | 2563.125 | 984.0938 | 2515.7812 | 2515.7812 | 2515.7812 | 2515.7812 | 2515.7812 | 2515.7812 | 2515.7812 | 2439.0938 | 2348.1562 | 1724.7188 | 744.75 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 1003.6875 | 909.4688 | 450.0938 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-24 00:45 | 4101 | 4101 | 4101 | 4101 | 4101 | 4101 | 4101 | 3999.75 | 3683.3438 | 2636.8125 | 1033.125 | 4051.875 | 4051.875 | 4051.875 | 4051.875 | 4051.875 | 4051.875 | 4051.875 | 3950.625 | 3634.2188 | 2587.6875 | 1008.6562 | 2540.3438 | 2540.3438 | 2540.3438 | 2540.3438 | 2540.3438 | 2540.3438 | 2540.3438 | 2463.6562 | 2372.7188 | 1749.2812 | 769.3125 | 1028.25 | 1028.25 | 1028.25 | 1028.25 | 1028.25 | 1028.25 | 1028.25 | 1028.25 | 1028.25 | 934.0312 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-25 01:19 | 4125.5625 | 4125.5625 | 4125.5625 | 4125.5625 | 4125.5625 | 4125.5625 | 4125.5625 | 4024.3125 | 3707.9062 | 2661.375 | 1033.125 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 4076.4375 | 3975.1875 | 3658.7812 | 2612.25 | 1008.6562 | 2564.9062 | 2564.9062 | 2564.9062 | 2564.9062 | 2564.9062 | 2564.9062 | 2564.9062 | 2488.2188 | 2397.2812 | 1773.8438 | 769.3125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 958.5938 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-26 01:36 | 4149.8438 | 4149.8438 | 4149.8438 | 4149.8438 | 4149.8438 | 4149.8438 | 4149.8438 | 4048.5938 | 3732.1875 | 2685.6562 | 1033.125 | 4100.7188 | 4100.7188 | 4100.7188 | 4100.7188 | 4100.7188 | 4100.7188 | 4100.7188 | 3999.4688 | 3683.0625 | 2636.5312 | 1008.6562 | 2589.1875 | 2589.1875 | 2589.1875 | 2589.1875 | 2589.1875 | 2589.1875 | 2589.1875 | 2512.5 | 2421.5625 | 1798.125 | 769.3125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 958.5938 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-27 02:15 | 4174.5 | 4174.5 | 4174.5 | 4174.5 | 4174.5 | 4174.5 | 4174.5 | 4073.25 | 3756.8438 | 2710.3125 | 1033.125 | 4125.375 | 4125.375 | 4125.375 | 4125.375 | 4125.375 | 4125.375 | 4125.375 | 4024.125 | 3707.7188 | 2661.1875 | 1008.6562 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2537.1562 | 2446.2188 | 1822.7812 | 769.3125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 958.5938 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-28 02:38 | 4198.875 | 4198.875 | 4198.875 | 4198.875 | 4198.875 | 4198.875 | 4198.875 | 4097.625 | 3781.2188 | 2734.6875 | 1057.5 | 4149.75 | 4149.75 | 4149.75 | 4149.75 | 4149.75 | 4149.75 | 4149.75 | 4048.5 | 3732.0938 | 2685.5625 | 1033.0312 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2613.8438 | 2537.1562 | 2446.2188 | 1822.7812 | 769.3125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 1052.8125 | 958.5938 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-29 03:06 | 4223.3438 | 4223.3438 | 4223.3438 | 4223.3438 | 4223.3438 | 4223.3438 | 4223.3438 | 4122.0938 | 3805.6875 | 2734.6875 | 1057.5 | 4174.2188 | 4174.2188 | 4174.2188 | 4174.2188 | 4174.2188 | 4174.2188 | 4174.2188 | 4072.9688 | 3756.5625 | 2685.5625 | 1033.0312 | 2638.3125 | 2638.3125 | 2638.3125 | 2638.3125 | 2638.3125 | 2638.3125 | 2638.3125 | 2561.625 | 2470.6875 | 1822.7812 | 769.3125 | 1077.2812 | 1077.2812 | 1077.2812 | 1077.2812 | 1077.2812 | 1077.2812 | 1077.2812 | 1077.2812 | 1077.2812 | 958.5938 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-30 01:30 | 4245.75 | 4245.75 | 4245.75 | 4245.75 | 4245.75 | 4245.75 | 4245.75 | 4144.5 | 3828.0938 | 2757.0938 | 1057.5 | 4196.625 | 4196.625 | 4196.625 | 4196.625 | 4196.625 | 4196.625 | 4196.625 | 4095.375 | 3778.9688 | 2707.9688 | 1033.0312 | 2660.7188 | 2660.7188 | 2660.7188 | 2660.7188 | 2660.7188 | 2660.7188 | 2660.7188 | 2584.0312 | 2493.0938 | 1845.1875 | 769.3125 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 981 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-08-31 02:54 | 4271.1562 | 4271.1562 | 4271.1562 | 4271.1562 | 4271.1562 | 4271.1562 | 4271.1562 | 4169.9062 | 3853.5 | 2782.5 | 1082.9062 | 4222.0312 | 4222.0312 | 4222.0312 | 4222.0312 | 4222.0312 | 4222.0312 | 4222.0312 | 4120.7812 | 3804.375 | 2733.375 | 1058.4375 | 2686.125 | 2686.125 | 2686.125 | 2686.125 | 2686.125 | 2686.125 | 2686.125 | 2609.4375 | 2518.5 | 1870.5938 | 794.7188 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 1099.6875 | 981 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-01 02:21 | 4294.5938 | 4294.5938 | 4294.5938 | 4294.5938 | 4294.5938 | 4294.5938 | 4294.5938 | 4193.3438 | 3876.9375 | 2782.5 | 1082.9062 | 4245.4688 | 4245.4688 | 4245.4688 | 4245.4688 | 4245.4688 | 4245.4688 | 4245.4688 | 4144.2188 | 3827.8125 | 2733.375 | 1058.4375 | 2709.5625 | 2709.5625 | 2709.5625 | 2709.5625 | 2709.5625 | 2709.5625 | 2709.5625 | 2632.875 | 2541.9375 | 1870.5938 | 794.7188 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 981 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-02 02:43 | 4318.9688 | 4318.9688 | 4318.9688 | 4318.9688 | 4318.9688 | 4318.9688 | 4318.9688 | 4217.7188 | 3901.3125 | 2806.875 | 1082.9062 | 4269.8438 | 4269.8438 | 4269.8438 | 4269.8438 | 4269.8438 | 4269.8438 | 4269.8438 | 4168.5938 | 3852.1875 | 2757.75 | 1058.4375 | 2733.9375 | 2733.9375 | 2733.9375 | 2733.9375 | 2733.9375 | 2733.9375 | 2733.9375 | 2657.25 | 2566.3125 | 1894.9688 | 794.7188 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 1123.125 | 981 | 474.6562 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-03 03:11 | 4343.4375 | 4343.4375 | 4343.4375 | 4343.4375 | 4343.4375 | 4343.4375 | 4343.4375 | 4242.1875 | 3925.7812 | 2831.3438 | 1107.375 | 4294.3125 | 4294.3125 | 4294.3125 | 4294.3125 | 4294.3125 | 4294.3125 | 4294.3125 | 4193.0625 | 3876.6562 | 2782.2188 | 1082.9062 | 2758.4062 | 2758.4062 | 2758.4062 | 2758.4062 | 2758.4062 | 2758.4062 | 2758.4062 | 2681.7188 | 2590.7812 | 1919.4375 | 819.1875 | 1147.5938 | 1147.5938 | 1147.5938 | 1147.5938 | 1147.5938 | 1147.5938 | 1147.5938 | 1147.5938 | 1147.5938 | 1005.4688 | 499.125 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 402.5625 | 187.3125 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-04 03:34 | 4367.8125 | 4367.8125 | 4367.8125 | 4367.8125 | 4367.8125 | 4367.8125 | 4367.8125 | 4266.5625 | 3950.1562 | 2855.7188 | 1131.75 | 4318.6875 | 4318.6875 | 4318.6875 | 4318.6875 | 4318.6875 | 4318.6875 | 4318.6875 | 4217.4375 | 3901.0312 | 2806.5938 | 1107.2812 | 2782.7812 | 2782.7812 | 2782.7812 | 2782.7812 | 2782.7812 | 2782.7812 | 2782.7812 | 2706.0938 | 2615.1562 | 1943.8125 | 843.5625 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1029.8438 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-05 03:56 | 4392.1875 | 4392.1875 | 4392.1875 | 4392.1875 | 4392.1875 | 4392.1875 | 4392.1875 | 4290.9375 | 3974.5312 | 2855.7188 | 1131.75 | 4343.0625 | 4343.0625 | 4343.0625 | 4343.0625 | 4343.0625 | 4343.0625 | 4343.0625 | 4241.8125 | 3925.4062 | 2806.5938 | 1107.2812 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2807.1562 | 2730.4688 | 2639.5312 | 1943.8125 | 843.5625 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1029.8438 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-06 00:11 | 4412.4375 | 4412.4375 | 4412.4375 | 4412.4375 | 4412.4375 | 4412.4375 | 4412.4375 | 4311.1875 | 3994.7812 | 2855.7188 | 1131.75 | 4363.3125 | 4363.3125 | 4363.3125 | 4363.3125 | 4363.3125 | 4363.3125 | 4363.3125 | 4262.0625 | 3945.6562 | 2806.5938 | 1107.2812 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2750.7188 | 2659.7812 | 1943.8125 | 843.5625 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1029.8438 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-07 00:45 | 4437 | 4437 | 4437 | 4437 | 4437 | 4437 | 4437 | 4311.1875 | 3994.7812 | 2855.7188 | 1131.75 | 4387.875 | 4387.875 | 4387.875 | 4387.875 | 4387.875 | 4387.875 | 4387.875 | 4262.0625 | 3945.6562 | 2806.5938 | 1107.2812 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2827.4062 | 2750.7188 | 2659.7812 | 1943.8125 | 843.5625 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1171.9688 | 1029.8438 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-08 01:02 | 4461.2812 | 4461.2812 | 4461.2812 | 4461.2812 | 4461.2812 | 4461.2812 | 4461.2812 | 4335.4688 | 4019.0625 | 2880 | 1131.75 | 4412.1562 | 4412.1562 | 4412.1562 | 4412.1562 | 4412.1562 | 4412.1562 | 4412.1562 | 4286.3438 | 3969.9375 | 2830.875 | 1107.2812 | 2851.6875 | 2851.6875 | 2851.6875 | 2851.6875 | 2851.6875 | 2851.6875 | 2851.6875 | 2775 | 2684.0625 | 1968.0938 | 843.5625 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1054.125 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-09 02:32 | 4486.7812 | 4486.7812 | 4486.7812 | 4486.7812 | 4486.7812 | 4486.7812 | 4486.7812 | 4360.9688 | 4044.5625 | 2905.5 | 1157.25 | 4437.6562 | 4437.6562 | 4437.6562 | 4437.6562 | 4437.6562 | 4437.6562 | 4437.6562 | 4311.8438 | 3995.4375 | 2856.375 | 1132.7812 | 2877.1875 | 2877.1875 | 2877.1875 | 2877.1875 | 2877.1875 | 2877.1875 | 2877.1875 | 2800.5 | 2709.5625 | 1993.5938 | 869.0625 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1054.125 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-10 02:54 | 4511.1562 | 4511.1562 | 4511.1562 | 4511.1562 | 4511.1562 | 4511.1562 | 4511.1562 | 4385.3438 | 4068.9375 | 2929.875 | 1181.625 | 4462.0312 | 4462.0312 | 4462.0312 | 4462.0312 | 4462.0312 | 4462.0312 | 4462.0312 | 4336.2188 | 4019.8125 | 2880.75 | 1157.1562 | 2901.5625 | 2901.5625 | 2901.5625 | 2901.5625 | 2901.5625 | 2901.5625 | 2901.5625 | 2824.875 | 2733.9375 | 2017.9688 | 893.4375 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1196.25 | 1054.125 | 523.5 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-11 03:17 | 4535.5312 | 4535.5312 | 4535.5312 | 4535.5312 | 4535.5312 | 4535.5312 | 4535.5312 | 4409.7188 | 4093.3125 | 2954.25 | 1206 | 4486.4062 | 4486.4062 | 4486.4062 | 4486.4062 | 4486.4062 | 4486.4062 | 4486.4062 | 4360.5938 | 4044.1875 | 2905.125 | 1181.5312 | 2925.9375 | 2925.9375 | 2925.9375 | 2925.9375 | 2925.9375 | 2925.9375 | 2925.9375 | 2849.25 | 2758.3125 | 2042.3438 | 917.8125 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1078.5 | 547.875 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-12 03:34 | 4559.8125 | 4559.8125 | 4559.8125 | 4559.8125 | 4559.8125 | 4559.8125 | 4559.8125 | 4434 | 4117.5938 | 2978.5312 | 1230.2812 | 4510.6875 | 4510.6875 | 4510.6875 | 4510.6875 | 4510.6875 | 4510.6875 | 4510.6875 | 4384.875 | 4068.4688 | 2929.4062 | 1205.8125 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2873.5312 | 2782.5938 | 2066.625 | 942.0938 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1078.5 | 547.875 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-13 01:58 | 4582.2188 | 4582.2188 | 4582.2188 | 4582.2188 | 4582.2188 | 4582.2188 | 4582.2188 | 4456.4062 | 4140 | 3000.9375 | 1230.2812 | 4533.0938 | 4533.0938 | 4533.0938 | 4533.0938 | 4533.0938 | 4533.0938 | 4533.0938 | 4407.2812 | 4090.875 | 2951.8125 | 1205.8125 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2950.2188 | 2873.5312 | 2782.5938 | 2066.625 | 942.0938 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1078.5 | 547.875 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-14 01:24 | 4605.6562 | 4605.6562 | 4605.6562 | 4605.6562 | 4605.6562 | 4605.6562 | 4605.6562 | 4479.8438 | 4163.4375 | 3024.375 | 1253.7188 | 4556.5312 | 4556.5312 | 4556.5312 | 4556.5312 | 4556.5312 | 4556.5312 | 4556.5312 | 4430.7188 | 4114.3125 | 2975.25 | 1229.25 | 2973.6562 | 2973.6562 | 2973.6562 | 2973.6562 | 2973.6562 | 2973.6562 | 2973.6562 | 2896.9688 | 2806.0312 | 2090.0625 | 965.5312 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1078.5 | 547.875 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-15 01:41 | 4629.9375 | 4629.9375 | 4629.9375 | 4629.9375 | 4629.9375 | 4629.9375 | 4629.9375 | 4504.125 | 4187.7188 | 3048.6562 | 1253.7188 | 4580.8125 | 4580.8125 | 4580.8125 | 4580.8125 | 4580.8125 | 4580.8125 | 4580.8125 | 4455 | 4138.5938 | 2999.5312 | 1229.25 | 2997.9375 | 2997.9375 | 2997.9375 | 2997.9375 | 2997.9375 | 2997.9375 | 2997.9375 | 2921.25 | 2830.3125 | 2114.3438 | 965.5312 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1220.625 | 1078.5 | 547.875 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 426.9375 | 211.6875 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-16 02:04 | 4654.3125 | 4654.3125 | 4654.3125 | 4654.3125 | 4654.3125 | 4654.3125 | 4654.3125 | 4528.5 | 4212.0938 | 3073.0312 | 1278.0938 | 4605.1875 | 4605.1875 | 4605.1875 | 4605.1875 | 4605.1875 | 4605.1875 | 4605.1875 | 4479.375 | 4162.9688 | 3023.9062 | 1253.625 | 3022.3125 | 3022.3125 | 3022.3125 | 3022.3125 | 3022.3125 | 3022.3125 | 3022.3125 | 2945.625 | 2854.6875 | 2138.7188 | 989.9062 | 1245 | 1245 | 1245 | 1245 | 1245 | 1245 | 1245 | 1245 | 1245 | 1102.875 | 572.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-17 02:21 | 4678.5938 | 4678.5938 | 4678.5938 | 4678.5938 | 4678.5938 | 4678.5938 | 4678.5938 | 4552.7812 | 4236.375 | 3073.0312 | 1278.0938 | 4629.4688 | 4629.4688 | 4629.4688 | 4629.4688 | 4629.4688 | 4629.4688 | 4629.4688 | 4503.6562 | 4187.25 | 3023.9062 | 1253.625 | 3046.5938 | 3046.5938 | 3046.5938 | 3046.5938 | 3046.5938 | 3046.5938 | 3046.5938 | 2969.9062 | 2878.9688 | 2138.7188 | 989.9062 | 1269.2812 | 1269.2812 | 1269.2812 | 1269.2812 | 1269.2812 | 1269.2812 | 1269.2812 | 1269.2812 | 1269.2812 | 1102.875 | 572.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-18 02:43 | 4702.9688 | 4702.9688 | 4702.9688 | 4702.9688 | 4702.9688 | 4702.9688 | 4702.9688 | 4577.1562 | 4260.75 | 3097.4062 | 1278.0938 | 4653.8438 | 4653.8438 | 4653.8438 | 4653.8438 | 4653.8438 | 4653.8438 | 4653.8438 | 4528.0312 | 4211.625 | 3048.2812 | 1253.625 | 3070.9688 | 3070.9688 | 3070.9688 | 3070.9688 | 3070.9688 | 3070.9688 | 3070.9688 | 2994.2812 | 2903.3438 | 2163.0938 | 989.9062 | 1293.6562 | 1293.6562 | 1293.6562 | 1293.6562 | 1293.6562 | 1293.6562 | 1293.6562 | 1293.6562 | 1293.6562 | 1127.25 | 572.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-19 03:11 | 4727.4375 | 4727.4375 | 4727.4375 | 4727.4375 | 4727.4375 | 4727.4375 | 4727.4375 | 4601.625 | 4285.2188 | 3121.875 | 1278.0938 | 4678.3125 | 4678.3125 | 4678.3125 | 4678.3125 | 4678.3125 | 4678.3125 | 4678.3125 | 4552.5 | 4236.0938 | 3072.75 | 1253.625 | 3095.4375 | 3095.4375 | 3095.4375 | 3095.4375 | 3095.4375 | 3095.4375 | 3095.4375 | 3018.75 | 2927.8125 | 2187.5625 | 989.9062 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1151.7188 | 572.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-20 03:28 | 4751.7188 | 4751.7188 | 4751.7188 | 4751.7188 | 4751.7188 | 4751.7188 | 4751.7188 | 4625.9062 | 4309.5 | 3146.1562 | 1302.375 | 4702.5938 | 4702.5938 | 4702.5938 | 4702.5938 | 4702.5938 | 4702.5938 | 4702.5938 | 4576.7812 | 4260.375 | 3097.0312 | 1277.9062 | 3119.7188 | 3119.7188 | 3119.7188 | 3119.7188 | 3119.7188 | 3119.7188 | 3119.7188 | 3043.0312 | 2952.0938 | 2211.8438 | 1014.1875 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1151.7188 | 572.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-21 03:45 | 4776 | 4776 | 4776 | 4776 | 4776 | 4776 | 4776 | 4650.1875 | 4333.7812 | 3170.4375 | 1302.375 | 4726.875 | 4726.875 | 4726.875 | 4726.875 | 4726.875 | 4726.875 | 4726.875 | 4601.0625 | 4284.6562 | 3121.3125 | 1277.9062 | 3144 | 3144 | 3144 | 3144 | 3144 | 3144 | 3144 | 3067.3125 | 2976.375 | 2236.125 | 1014.1875 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1318.125 | 1151.7188 | 572.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-22 03:17 | 4799.5312 | 4799.5312 | 4799.5312 | 4799.5312 | 4799.5312 | 4799.5312 | 4799.5312 | 4673.7188 | 4357.3125 | 3193.9688 | 1325.9062 | 4750.4062 | 4750.4062 | 4750.4062 | 4750.4062 | 4750.4062 | 4750.4062 | 4750.4062 | 4624.5938 | 4308.1875 | 3144.8438 | 1301.4375 | 3167.5312 | 3167.5312 | 3167.5312 | 3167.5312 | 3167.5312 | 3167.5312 | 3167.5312 | 3090.8438 | 2999.9062 | 2259.6562 | 1037.7188 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1175.25 | 595.7812 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-23 03:45 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4698.1875 | 4381.7812 | 3218.4375 | 1325.9062 | 4774.875 | 4774.875 | 4774.875 | 4774.875 | 4774.875 | 4774.875 | 4774.875 | 4649.0625 | 4332.6562 | 3169.3125 | 1301.4375 | 3192 | 3192 | 3192 | 3192 | 3192 | 3192 | 3192 | 3115.3125 | 3024.375 | 2284.125 | 1037.7188 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1341.6562 | 1175.25 | 595.7812 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-24 | 4844.25 | 4844.25 | 4844.25 | 4844.25 | 4844.25 | 4844.25 | 4844.25 | 4718.4375 | 4402.0312 | 3238.6875 | 1325.9062 | 4795.125 | 4795.125 | 4795.125 | 4795.125 | 4795.125 | 4795.125 | 4795.125 | 4669.3125 | 4352.9062 | 3189.5625 | 1301.4375 | 3212.25 | 3212.25 | 3212.25 | 3212.25 | 3212.25 | 3212.25 | 3212.25 | 3135.5625 | 3044.625 | 2304.375 | 1037.7188 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1195.5 | 595.7812 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-25 00:28 | 4868.7188 | 4868.7188 | 4868.7188 | 4868.7188 | 4868.7188 | 4868.7188 | 4868.7188 | 4742.9062 | 4426.5 | 3263.1562 | 1350.375 | 4819.5938 | 4819.5938 | 4819.5938 | 4819.5938 | 4819.5938 | 4819.5938 | 4819.5938 | 4693.7812 | 4377.375 | 3214.0312 | 1325.9062 | 3236.7188 | 3236.7188 | 3236.7188 | 3236.7188 | 3236.7188 | 3236.7188 | 3236.7188 | 3160.0312 | 3069.0938 | 2328.8438 | 1062.1875 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1361.9062 | 1195.5 | 595.7812 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-26 00:56 | 4893.1875 | 4893.1875 | 4893.1875 | 4893.1875 | 4893.1875 | 4893.1875 | 4893.1875 | 4767.375 | 4450.9688 | 3287.625 | 1374.8438 | 4844.0625 | 4844.0625 | 4844.0625 | 4844.0625 | 4844.0625 | 4844.0625 | 4844.0625 | 4718.25 | 4401.8438 | 3238.5 | 1350.375 | 3261.1875 | 3261.1875 | 3261.1875 | 3261.1875 | 3261.1875 | 3261.1875 | 3261.1875 | 3184.5 | 3093.5625 | 2353.3125 | 1086.6562 | 1386.375 | 1386.375 | 1386.375 | 1386.375 | 1386.375 | 1386.375 | 1386.375 | 1386.375 | 1386.375 | 1219.9688 | 620.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-27 01:24 | 4917.6562 | 4917.6562 | 4917.6562 | 4917.6562 | 4917.6562 | 4917.6562 | 4917.6562 | 4791.8438 | 4475.4375 | 3312.0938 | 1374.8438 | 4868.5312 | 4868.5312 | 4868.5312 | 4868.5312 | 4868.5312 | 4868.5312 | 4868.5312 | 4742.7188 | 4426.3125 | 3262.9688 | 1350.375 | 3285.6562 | 3285.6562 | 3285.6562 | 3285.6562 | 3285.6562 | 3285.6562 | 3285.6562 | 3208.9688 | 3118.0312 | 2377.7812 | 1086.6562 | 1410.8438 | 1410.8438 | 1410.8438 | 1410.8438 | 1410.8438 | 1410.8438 | 1410.8438 | 1410.8438 | 1410.8438 | 1244.4375 | 620.25 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 451.3125 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-28 03:56 | 4944.1875 | 4944.1875 | 4944.1875 | 4944.1875 | 4944.1875 | 4944.1875 | 4944.1875 | 4818.375 | 4501.9688 | 3338.625 | 1374.8438 | 4895.0625 | 4895.0625 | 4895.0625 | 4895.0625 | 4895.0625 | 4895.0625 | 4895.0625 | 4769.25 | 4452.8438 | 3289.5 | 1350.375 | 3312.1875 | 3312.1875 | 3312.1875 | 3312.1875 | 3312.1875 | 3312.1875 | 3312.1875 | 3235.5 | 3144.5625 | 2404.3125 | 1086.6562 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1270.9688 | 620.25 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-29 00:11 | 4964.4375 | 4964.4375 | 4964.4375 | 4964.4375 | 4964.4375 | 4964.4375 | 4964.4375 | 4838.625 | 4522.2188 | 3358.875 | 1374.8438 | 4915.3125 | 4915.3125 | 4915.3125 | 4915.3125 | 4915.3125 | 4915.3125 | 4915.3125 | 4789.5 | 4473.0938 | 3309.75 | 1350.375 | 3332.4375 | 3332.4375 | 3332.4375 | 3332.4375 | 3332.4375 | 3332.4375 | 3332.4375 | 3255.75 | 3164.8125 | 2424.5625 | 1086.6562 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1270.9688 | 620.25 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-09-30 00:34 | 4988.8125 | 4988.8125 | 4988.8125 | 4988.8125 | 4988.8125 | 4988.8125 | 4988.8125 | 4863 | 4546.5938 | 3383.25 | 1399.2188 | 4939.6875 | 4939.6875 | 4939.6875 | 4939.6875 | 4939.6875 | 4939.6875 | 4939.6875 | 4813.875 | 4497.4688 | 3334.125 | 1374.75 | 3356.8125 | 3356.8125 | 3356.8125 | 3356.8125 | 3356.8125 | 3356.8125 | 3356.8125 | 3280.125 | 3189.1875 | 2448.9375 | 1111.0312 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1437.375 | 1270.9688 | 620.25 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-01 00:56 | 5013.1875 | 5013.1875 | 5013.1875 | 5013.1875 | 5013.1875 | 5013.1875 | 5013.1875 | 4887.375 | 4570.9688 | 3407.625 | 1423.5938 | 4964.0625 | 4964.0625 | 4964.0625 | 4964.0625 | 4964.0625 | 4964.0625 | 4964.0625 | 4838.25 | 4521.8438 | 3358.5 | 1399.125 | 3381.1875 | 3381.1875 | 3381.1875 | 3381.1875 | 3381.1875 | 3381.1875 | 3381.1875 | 3304.5 | 3213.5625 | 2473.3125 | 1135.4062 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1295.3438 | 644.625 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-02 01:24 | 5037.6562 | 5037.6562 | 5037.6562 | 5037.6562 | 5037.6562 | 5037.6562 | 5037.6562 | 4911.8438 | 4595.4375 | 3432.0938 | 1423.5938 | 4988.5312 | 4988.5312 | 4988.5312 | 4988.5312 | 4988.5312 | 4988.5312 | 4988.5312 | 4862.7188 | 4546.3125 | 3382.9688 | 1399.125 | 3405.6562 | 3405.6562 | 3405.6562 | 3405.6562 | 3405.6562 | 3405.6562 | 3405.6562 | 3328.9688 | 3238.0312 | 2497.7812 | 1135.4062 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1461.75 | 1295.3438 | 644.625 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 477.8438 | 236.0625 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-03 01:52 | 5062.125 | 5062.125 | 5062.125 | 5062.125 | 5062.125 | 5062.125 | 5062.125 | 4936.3125 | 4619.9062 | 3456.5625 | 1448.0625 | 5013 | 5013 | 5013 | 5013 | 5013 | 5013 | 5013 | 4887.1875 | 4570.7812 | 3407.4375 | 1423.5938 | 3430.125 | 3430.125 | 3430.125 | 3430.125 | 3430.125 | 3430.125 | 3430.125 | 3353.4375 | 3262.5 | 2522.25 | 1159.875 | 1486.2188 | 1486.2188 | 1486.2188 | 1486.2188 | 1486.2188 | 1486.2188 | 1486.2188 | 1486.2188 | 1486.2188 | 1319.8125 | 669.0938 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 260.5312 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-04 02:15 | 5086.5 | 5086.5 | 5086.5 | 5086.5 | 5086.5 | 5086.5 | 5086.5 | 4960.6875 | 4644.2812 | 3480.9375 | 1472.4375 | 5037.375 | 5037.375 | 5037.375 | 5037.375 | 5037.375 | 5037.375 | 5037.375 | 4911.5625 | 4595.1562 | 3431.8125 | 1447.9688 | 3454.5 | 3454.5 | 3454.5 | 3454.5 | 3454.5 | 3454.5 | 3454.5 | 3377.8125 | 3286.875 | 2546.625 | 1184.25 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1344.1875 | 693.4688 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 260.5312 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-05 02:49 | 5111.0625 | 5111.0625 | 5111.0625 | 5111.0625 | 5111.0625 | 5111.0625 | 5111.0625 | 4985.25 | 4668.8438 | 3505.5 | 1472.4375 | 5061.9375 | 5061.9375 | 5061.9375 | 5061.9375 | 5061.9375 | 5061.9375 | 5061.9375 | 4936.125 | 4619.7188 | 3456.375 | 1447.9688 | 3479.0625 | 3479.0625 | 3479.0625 | 3479.0625 | 3479.0625 | 3479.0625 | 3479.0625 | 3402.375 | 3311.4375 | 2571.1875 | 1184.25 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1510.5938 | 1344.1875 | 693.4688 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 502.3125 | 260.5312 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-06 03:17 | 5135.5312 | 5135.5312 | 5135.5312 | 5135.5312 | 5135.5312 | 5135.5312 | 5135.5312 | 5009.7188 | 4693.3125 | 3529.9688 | 1472.4375 | 5086.4062 | 5086.4062 | 5086.4062 | 5086.4062 | 5086.4062 | 5086.4062 | 5086.4062 | 4960.5938 | 4644.1875 | 3480.8438 | 1447.9688 | 3503.5312 | 3503.5312 | 3503.5312 | 3503.5312 | 3503.5312 | 3503.5312 | 3503.5312 | 3426.8438 | 3335.9062 | 2595.6562 | 1184.25 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1368.6562 | 693.4688 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 260.5312 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-07 03:39 | 5159.9062 | 5159.9062 | 5159.9062 | 5159.9062 | 5159.9062 | 5159.9062 | 5159.9062 | 5034.0938 | 4717.6875 | 3529.9688 | 1472.4375 | 5110.7812 | 5110.7812 | 5110.7812 | 5110.7812 | 5110.7812 | 5110.7812 | 5110.7812 | 4984.9688 | 4668.5625 | 3480.8438 | 1447.9688 | 3527.9062 | 3527.9062 | 3527.9062 | 3527.9062 | 3527.9062 | 3527.9062 | 3527.9062 | 3451.2188 | 3360.2812 | 2595.6562 | 1184.25 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1368.6562 | 693.4688 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 260.5312 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-08 04:02 | 5184.2812 | 5184.2812 | 5184.2812 | 5184.2812 | 5184.2812 | 5184.2812 | 5184.2812 | 5058.4688 | 4742.0625 | 3554.3438 | 1472.4375 | 5135.1562 | 5135.1562 | 5135.1562 | 5135.1562 | 5135.1562 | 5135.1562 | 5135.1562 | 5009.3438 | 4692.9375 | 3505.2188 | 1447.9688 | 3552.2812 | 3552.2812 | 3552.2812 | 3552.2812 | 3552.2812 | 3552.2812 | 3552.2812 | 3475.5938 | 3384.6562 | 2620.0312 | 1184.25 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1535.0625 | 1368.6562 | 693.4688 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 526.7812 | 260.5312 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 113.7188 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-09 00:28 | 5204.7188 | 5204.7188 | 5204.7188 | 5204.7188 | 5204.7188 | 5204.7188 | 5204.7188 | 5078.9062 | 4762.5 | 3574.7812 | 1472.4375 | 5155.5938 | 5155.5938 | 5155.5938 | 5155.5938 | 5155.5938 | 5155.5938 | 5155.5938 | 5029.7812 | 4713.375 | 3525.6562 | 1447.9688 | 3572.7188 | 3572.7188 | 3572.7188 | 3572.7188 | 3572.7188 | 3572.7188 | 3572.7188 | 3496.0312 | 3405.0938 | 2640.4688 | 1184.25 | 1555.5 | 1555.5 | 1555.5 | 1555.5 | 1555.5 | 1555.5 | 1555.5 | 1555.5 | 1555.5 | 1389.0938 | 693.4688 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 260.5312 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-10 00:51 | 5229.0938 | 5229.0938 | 5229.0938 | 5229.0938 | 5229.0938 | 5229.0938 | 5229.0938 | 5103.2812 | 4786.875 | 3574.7812 | 1472.4375 | 5179.9688 | 5179.9688 | 5179.9688 | 5179.9688 | 5179.9688 | 5179.9688 | 5179.9688 | 5054.1562 | 4737.75 | 3525.6562 | 1447.9688 | 3597.0938 | 3597.0938 | 3597.0938 | 3597.0938 | 3597.0938 | 3597.0938 | 3597.0938 | 3520.4062 | 3429.4688 | 2640.4688 | 1184.25 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1389.0938 | 693.4688 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 260.5312 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-11 01:24 | 5253.6562 | 5253.6562 | 5253.6562 | 5253.6562 | 5253.6562 | 5253.6562 | 5253.6562 | 5127.8438 | 4811.4375 | 3599.3438 | 1497 | 5204.5312 | 5204.5312 | 5204.5312 | 5204.5312 | 5204.5312 | 5204.5312 | 5204.5312 | 5078.7188 | 4762.3125 | 3550.2188 | 1472.5312 | 3621.6562 | 3621.6562 | 3621.6562 | 3621.6562 | 3621.6562 | 3621.6562 | 3621.6562 | 3544.9688 | 3454.0312 | 2665.0312 | 1208.8125 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1389.0938 | 693.4688 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 260.5312 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-12 01:52 | 5278.125 | 5278.125 | 5278.125 | 5278.125 | 5278.125 | 5278.125 | 5278.125 | 5152.3125 | 4835.9062 | 3623.8125 | 1521.4688 | 5229 | 5229 | 5229 | 5229 | 5229 | 5229 | 5229 | 5103.1875 | 4786.7812 | 3574.6875 | 1497 | 3646.125 | 3646.125 | 3646.125 | 3646.125 | 3646.125 | 3646.125 | 3646.125 | 3569.4375 | 3478.5 | 2689.5 | 1233.2812 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1579.875 | 1389.0938 | 693.4688 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 547.2188 | 260.5312 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 134.1562 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-13 02:21 | 5302.5938 | 5302.5938 | 5302.5938 | 5302.5938 | 5302.5938 | 5302.5938 | 5302.5938 | 5176.7812 | 4860.375 | 3648.2812 | 1521.4688 | 5253.4688 | 5253.4688 | 5253.4688 | 5253.4688 | 5253.4688 | 5253.4688 | 5253.4688 | 5127.6562 | 4811.25 | 3599.1562 | 1497 | 3670.5938 | 3670.5938 | 3670.5938 | 3670.5938 | 3670.5938 | 3670.5938 | 3670.5938 | 3593.9062 | 3502.9688 | 2713.9688 | 1233.2812 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1413.5625 | 693.4688 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-14 02:54 | 5327.1562 | 5327.1562 | 5327.1562 | 5327.1562 | 5327.1562 | 5327.1562 | 5327.1562 | 5201.3438 | 4884.9375 | 3672.8438 | 1546.0312 | 5278.0312 | 5278.0312 | 5278.0312 | 5278.0312 | 5278.0312 | 5278.0312 | 5278.0312 | 5152.2188 | 4835.8125 | 3623.7188 | 1521.5625 | 3695.1562 | 3695.1562 | 3695.1562 | 3695.1562 | 3695.1562 | 3695.1562 | 3695.1562 | 3618.4688 | 3527.5312 | 2738.5312 | 1257.8438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1604.3438 | 1413.5625 | 693.4688 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-15 03:39 | 5351.9062 | 5351.9062 | 5351.9062 | 5351.9062 | 5351.9062 | 5351.9062 | 5351.9062 | 5226.0938 | 4909.6875 | 3672.8438 | 1546.0312 | 5302.7812 | 5302.7812 | 5302.7812 | 5302.7812 | 5302.7812 | 5302.7812 | 5302.7812 | 5176.9688 | 4860.5625 | 3623.7188 | 1521.5625 | 3719.9062 | 3719.9062 | 3719.9062 | 3719.9062 | 3719.9062 | 3719.9062 | 3719.9062 | 3643.2188 | 3552.2812 | 2738.5312 | 1257.8438 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1413.5625 | 693.4688 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-16 00:06 | 5372.3438 | 5372.3438 | 5372.3438 | 5372.3438 | 5372.3438 | 5372.3438 | 5372.3438 | 5246.5312 | 4930.125 | 3672.8438 | 1546.0312 | 5323.2188 | 5323.2188 | 5323.2188 | 5323.2188 | 5323.2188 | 5323.2188 | 5323.2188 | 5197.4062 | 4881 | 3623.7188 | 1521.5625 | 3740.3438 | 3740.3438 | 3740.3438 | 3740.3438 | 3740.3438 | 3740.3438 | 3740.3438 | 3663.6562 | 3572.7188 | 2738.5312 | 1257.8438 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1413.5625 | 693.4688 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-17 00:28 | 5396.7188 | 5396.7188 | 5396.7188 | 5396.7188 | 5396.7188 | 5396.7188 | 5396.7188 | 5270.9062 | 4954.5 | 3697.2188 | 1570.4062 | 5347.5938 | 5347.5938 | 5347.5938 | 5347.5938 | 5347.5938 | 5347.5938 | 5347.5938 | 5221.7812 | 4905.375 | 3648.0938 | 1545.9375 | 3764.7188 | 3764.7188 | 3764.7188 | 3764.7188 | 3764.7188 | 3764.7188 | 3764.7188 | 3688.0312 | 3597.0938 | 2762.9062 | 1282.2188 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1413.5625 | 693.4688 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-18 00:56 | 5421.1875 | 5421.1875 | 5421.1875 | 5421.1875 | 5421.1875 | 5421.1875 | 5421.1875 | 5295.375 | 4978.9688 | 3697.2188 | 1570.4062 | 5372.0625 | 5372.0625 | 5372.0625 | 5372.0625 | 5372.0625 | 5372.0625 | 5372.0625 | 5246.25 | 4929.8438 | 3648.0938 | 1545.9375 | 3789.1875 | 3789.1875 | 3789.1875 | 3789.1875 | 3789.1875 | 3789.1875 | 3789.1875 | 3712.5 | 3621.5625 | 2762.9062 | 1282.2188 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1629.0938 | 1413.5625 | 693.4688 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 571.6875 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-19 00:22 | 5444.625 | 5444.625 | 5444.625 | 5444.625 | 5444.625 | 5444.625 | 5444.625 | 5318.8125 | 5002.4062 | 3720.6562 | 1570.4062 | 5395.5 | 5395.5 | 5395.5 | 5395.5 | 5395.5 | 5395.5 | 5395.5 | 5269.6875 | 4953.2812 | 3671.5312 | 1545.9375 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3812.625 | 3735.9375 | 3645 | 2786.3438 | 1282.2188 | 1652.5312 | 1652.5312 | 1652.5312 | 1652.5312 | 1652.5312 | 1652.5312 | 1652.5312 | 1652.5312 | 1652.5312 | 1437 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-19 04:30 | 5448.75 | 5448.75 | 5448.75 | 5448.75 | 5448.75 | 5448.75 | 5448.75 | 5322.9375 | 5006.5312 | 3724.7812 | 1570.4062 | 5399.625 | 5399.625 | 5399.625 | 5399.625 | 5399.625 | 5399.625 | 5399.625 | 5273.8125 | 4957.4062 | 3675.6562 | 1545.9375 | 3816.75 | 3816.75 | 3816.75 | 3816.75 | 3816.75 | 3816.75 | 3816.75 | 3740.0625 | 3649.125 | 2790.4688 | 1282.2188 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1441.125 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-20 00:51 | 5469.0938 | 5469.0938 | 5469.0938 | 5469.0938 | 5469.0938 | 5469.0938 | 5469.0938 | 5343.2812 | 5026.875 | 3745.125 | 1570.4062 | 5419.9688 | 5419.9688 | 5419.9688 | 5419.9688 | 5419.9688 | 5419.9688 | 5419.9688 | 5294.1562 | 4977.75 | 3696 | 1545.9375 | 3837.0938 | 3837.0938 | 3837.0938 | 3837.0938 | 3837.0938 | 3837.0938 | 3837.0938 | 3760.4062 | 3669.4688 | 2810.8125 | 1282.2188 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1441.125 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-21 01:19 | 5493.5625 | 5493.5625 | 5493.5625 | 5493.5625 | 5493.5625 | 5493.5625 | 5493.5625 | 5367.75 | 5051.3438 | 3769.5938 | 1594.875 | 5444.4375 | 5444.4375 | 5444.4375 | 5444.4375 | 5444.4375 | 5444.4375 | 5444.4375 | 5318.625 | 5002.2188 | 3720.4688 | 1570.4062 | 3861.5625 | 3861.5625 | 3861.5625 | 3861.5625 | 3861.5625 | 3861.5625 | 3861.5625 | 3784.875 | 3693.9375 | 2835.2812 | 1306.6875 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1656.6562 | 1441.125 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-22 01:47 | 5518.0312 | 5518.0312 | 5518.0312 | 5518.0312 | 5518.0312 | 5518.0312 | 5518.0312 | 5392.2188 | 5075.8125 | 3794.0625 | 1594.875 | 5468.9062 | 5468.9062 | 5468.9062 | 5468.9062 | 5468.9062 | 5468.9062 | 5468.9062 | 5343.0938 | 5026.6875 | 3744.9375 | 1570.4062 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3809.3438 | 3718.4062 | 2859.75 | 1306.6875 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1465.5938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-23 02:21 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5416.7812 | 5100.375 | 3818.625 | 1619.4375 | 5493.4688 | 5493.4688 | 5493.4688 | 5493.4688 | 5493.4688 | 5493.4688 | 5493.4688 | 5367.6562 | 5051.25 | 3769.5 | 1594.9688 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3886.0312 | 3809.3438 | 3718.4062 | 2859.75 | 1306.6875 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1681.125 | 1465.5938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-24 02:49 | 5567.0625 | 5567.0625 | 5567.0625 | 5567.0625 | 5567.0625 | 5567.0625 | 5567.0625 | 5441.25 | 5124.8438 | 3818.625 | 1619.4375 | 5517.9375 | 5517.9375 | 5517.9375 | 5517.9375 | 5517.9375 | 5517.9375 | 5517.9375 | 5392.125 | 5075.7188 | 3769.5 | 1594.9688 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3910.5 | 3833.8125 | 3742.875 | 2859.75 | 1306.6875 | 1705.5938 | 1705.5938 | 1705.5938 | 1705.5938 | 1705.5938 | 1705.5938 | 1705.5938 | 1705.5938 | 1705.5938 | 1465.5938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-25 03:28 | 5591.7188 | 5591.7188 | 5591.7188 | 5591.7188 | 5591.7188 | 5591.7188 | 5591.7188 | 5465.9062 | 5149.5 | 3843.2812 | 1619.4375 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5542.5938 | 5416.7812 | 5100.375 | 3794.1562 | 1594.9688 | 3935.1562 | 3935.1562 | 3935.1562 | 3935.1562 | 3935.1562 | 3935.1562 | 3935.1562 | 3858.4688 | 3767.5312 | 2884.4062 | 1306.6875 | 1730.25 | 1730.25 | 1730.25 | 1730.25 | 1730.25 | 1730.25 | 1730.25 | 1730.25 | 1730.25 | 1490.25 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-26 03:51 | 5616.0938 | 5616.0938 | 5616.0938 | 5616.0938 | 5616.0938 | 5616.0938 | 5616.0938 | 5490.2812 | 5173.875 | 3867.6562 | 1619.4375 | 5566.9688 | 5566.9688 | 5566.9688 | 5566.9688 | 5566.9688 | 5566.9688 | 5566.9688 | 5441.1562 | 5124.75 | 3818.5312 | 1594.9688 | 3959.5312 | 3959.5312 | 3959.5312 | 3959.5312 | 3959.5312 | 3959.5312 | 3959.5312 | 3882.8438 | 3791.9062 | 2908.7812 | 1306.6875 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-27 00:34 | 5636.8125 | 5636.8125 | 5636.8125 | 5636.8125 | 5636.8125 | 5636.8125 | 5636.8125 | 5511 | 5194.5938 | 3888.375 | 1619.4375 | 5587.6875 | 5587.6875 | 5587.6875 | 5587.6875 | 5587.6875 | 5587.6875 | 5587.6875 | 5461.875 | 5145.4688 | 3839.25 | 1594.9688 | 3980.25 | 3980.25 | 3980.25 | 3980.25 | 3980.25 | 3980.25 | 3980.25 | 3903.5625 | 3812.625 | 2929.5 | 1306.6875 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-28 01:08 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5535.5625 | 5219.1562 | 3912.9375 | 1644 | 5612.25 | 5612.25 | 5612.25 | 5612.25 | 5612.25 | 5612.25 | 5612.25 | 5486.4375 | 5170.0312 | 3863.8125 | 1619.5312 | 4004.8125 | 4004.8125 | 4004.8125 | 4004.8125 | 4004.8125 | 4004.8125 | 4004.8125 | 3928.125 | 3837.1875 | 2954.0625 | 1331.25 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-29 01:47 | 5686.0312 | 5686.0312 | 5686.0312 | 5686.0312 | 5686.0312 | 5686.0312 | 5686.0312 | 5560.2188 | 5243.8125 | 3912.9375 | 1644 | 5636.9062 | 5636.9062 | 5636.9062 | 5636.9062 | 5636.9062 | 5636.9062 | 5636.9062 | 5511.0938 | 5194.6875 | 3863.8125 | 1619.5312 | 4029.4688 | 4029.4688 | 4029.4688 | 4029.4688 | 4029.4688 | 4029.4688 | 4029.4688 | 3952.7812 | 3861.8438 | 2954.0625 | 1331.25 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-30 02:15 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5584.6875 | 5268.2812 | 3937.4062 | 1668.4688 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5661.375 | 5535.5625 | 5219.1562 | 3888.2812 | 1644 | 4053.9375 | 4053.9375 | 4053.9375 | 4053.9375 | 4053.9375 | 4053.9375 | 4053.9375 | 3977.25 | 3886.3125 | 2978.5312 | 1355.7188 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-10-31 02:43 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5609.1562 | 5292.75 | 3937.4062 | 1668.4688 | 5685.8438 | 5685.8438 | 5685.8438 | 5685.8438 | 5685.8438 | 5685.8438 | 5685.8438 | 5560.0312 | 5243.625 | 3888.2812 | 1644 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4001.7188 | 3910.7812 | 2978.5312 | 1355.7188 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-01 03:22 | 5759.625 | 5759.625 | 5759.625 | 5759.625 | 5759.625 | 5759.625 | 5759.625 | 5633.8125 | 5317.4062 | 3962.0625 | 1693.125 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5710.5 | 5584.6875 | 5268.2812 | 3912.9375 | 1668.6562 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4078.4062 | 4001.7188 | 3910.7812 | 2978.5312 | 1355.7188 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-02 03:51 | 5784.0938 | 5784.0938 | 5784.0938 | 5784.0938 | 5784.0938 | 5784.0938 | 5784.0938 | 5658.2812 | 5341.875 | 3986.5312 | 1693.125 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5734.9688 | 5609.1562 | 5292.75 | 3937.4062 | 1668.6562 | 4102.875 | 4102.875 | 4102.875 | 4102.875 | 4102.875 | 4102.875 | 4102.875 | 4026.1875 | 3935.25 | 3003 | 1355.7188 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-03 00:17 | 5804.5312 | 5804.5312 | 5804.5312 | 5804.5312 | 5804.5312 | 5804.5312 | 5804.5312 | 5678.7188 | 5362.3125 | 4006.9688 | 1713.5625 | 5755.4062 | 5755.4062 | 5755.4062 | 5755.4062 | 5755.4062 | 5755.4062 | 5755.4062 | 5629.5938 | 5313.1875 | 3957.8438 | 1689.0938 | 4123.3125 | 4123.3125 | 4123.3125 | 4123.3125 | 4123.3125 | 4123.3125 | 4123.3125 | 4046.625 | 3955.6875 | 3023.4375 | 1376.1562 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1754.625 | 1514.625 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-04 00:45 | 5829 | 5829 | 5829 | 5829 | 5829 | 5829 | 5829 | 5703.1875 | 5386.7812 | 4031.4375 | 1713.5625 | 5779.875 | 5779.875 | 5779.875 | 5779.875 | 5779.875 | 5779.875 | 5779.875 | 5654.0625 | 5337.6562 | 3982.3125 | 1689.0938 | 4147.7812 | 4147.7812 | 4147.7812 | 4147.7812 | 4147.7812 | 4147.7812 | 4147.7812 | 4071.0938 | 3980.1562 | 3047.9062 | 1376.1562 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1539.0938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-05 01:19 | 5853.5625 | 5853.5625 | 5853.5625 | 5853.5625 | 5853.5625 | 5853.5625 | 5853.5625 | 5727.75 | 5411.3438 | 4031.4375 | 1713.5625 | 5804.4375 | 5804.4375 | 5804.4375 | 5804.4375 | 5804.4375 | 5804.4375 | 5804.4375 | 5678.625 | 5362.2188 | 3982.3125 | 1689.0938 | 4172.3438 | 4172.3438 | 4172.3438 | 4172.3438 | 4172.3438 | 4172.3438 | 4172.3438 | 4095.6562 | 4004.7188 | 3047.9062 | 1376.1562 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1539.0938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-06 01:41 | 5877.9375 | 5877.9375 | 5877.9375 | 5877.9375 | 5877.9375 | 5877.9375 | 5877.9375 | 5752.125 | 5435.7188 | 4031.4375 | 1713.5625 | 5828.8125 | 5828.8125 | 5828.8125 | 5828.8125 | 5828.8125 | 5828.8125 | 5828.8125 | 5703 | 5386.5938 | 3982.3125 | 1689.0938 | 4196.7188 | 4196.7188 | 4196.7188 | 4196.7188 | 4196.7188 | 4196.7188 | 4196.7188 | 4120.0312 | 4029.0938 | 3047.9062 | 1376.1562 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1539.0938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-07 02:09 | 5902.4062 | 5902.4062 | 5902.4062 | 5902.4062 | 5902.4062 | 5902.4062 | 5902.4062 | 5776.5938 | 5460.1875 | 4055.9062 | 1713.5625 | 5853.2812 | 5853.2812 | 5853.2812 | 5853.2812 | 5853.2812 | 5853.2812 | 5853.2812 | 5727.4688 | 5411.0625 | 4006.7812 | 1689.0938 | 4221.1875 | 4221.1875 | 4221.1875 | 4221.1875 | 4221.1875 | 4221.1875 | 4221.1875 | 4144.5 | 4053.5625 | 3072.375 | 1376.1562 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1539.0938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-08 03:17 | 5927.5312 | 5927.5312 | 5927.5312 | 5927.5312 | 5927.5312 | 5927.5312 | 5927.5312 | 5801.7188 | 5485.3125 | 4055.9062 | 1713.5625 | 5878.4062 | 5878.4062 | 5878.4062 | 5878.4062 | 5878.4062 | 5878.4062 | 5878.4062 | 5752.5938 | 5436.1875 | 4006.7812 | 1689.0938 | 4246.3125 | 4246.3125 | 4246.3125 | 4246.3125 | 4246.3125 | 4246.3125 | 4246.3125 | 4169.625 | 4078.6875 | 3072.375 | 1376.1562 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1779.0938 | 1539.0938 | 693.4688 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 595.125 | 260.5312 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-09 03:51 | 5952.0938 | 5952.0938 | 5952.0938 | 5952.0938 | 5952.0938 | 5952.0938 | 5952.0938 | 5826.2812 | 5509.875 | 4080.4688 | 1738.125 | 5902.9688 | 5902.9688 | 5902.9688 | 5902.9688 | 5902.9688 | 5902.9688 | 5902.9688 | 5777.1562 | 5460.75 | 4031.3438 | 1713.6562 | 4270.875 | 4270.875 | 4270.875 | 4270.875 | 4270.875 | 4270.875 | 4270.875 | 4194.1875 | 4103.25 | 3096.9375 | 1400.7188 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1563.6562 | 718.0312 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-10 00:17 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5846.7188 | 5530.3125 | 4080.4688 | 1738.125 | 5923.4062 | 5923.4062 | 5923.4062 | 5923.4062 | 5923.4062 | 5923.4062 | 5923.4062 | 5797.5938 | 5481.1875 | 4031.3438 | 1713.6562 | 4291.3125 | 4291.3125 | 4291.3125 | 4291.3125 | 4291.3125 | 4291.3125 | 4291.3125 | 4214.625 | 4123.6875 | 3096.9375 | 1400.7188 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1803.6562 | 1563.6562 | 718.0312 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-11 00:45 | 5997 | 5997 | 5997 | 5997 | 5997 | 5997 | 5997 | 5871.1875 | 5554.7812 | 4104.9375 | 1738.125 | 5947.875 | 5947.875 | 5947.875 | 5947.875 | 5947.875 | 5947.875 | 5947.875 | 5822.0625 | 5505.6562 | 4055.8125 | 1713.6562 | 4315.7812 | 4315.7812 | 4315.7812 | 4315.7812 | 4315.7812 | 4315.7812 | 4315.7812 | 4239.0938 | 4148.1562 | 3121.4062 | 1400.7188 | 1828.125 | 1828.125 | 1828.125 | 1828.125 | 1828.125 | 1828.125 | 1828.125 | 1828.125 | 1828.125 | 1588.125 | 718.0312 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 619.6875 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-12 01:24 | 6021.6562 | 6021.6562 | 6021.6562 | 6021.6562 | 6021.6562 | 6021.6562 | 6021.6562 | 5895.8438 | 5579.4375 | 4129.5938 | 1738.125 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5972.5312 | 5846.7188 | 5530.3125 | 4080.4688 | 1713.6562 | 4340.4375 | 4340.4375 | 4340.4375 | 4340.4375 | 4340.4375 | 4340.4375 | 4340.4375 | 4263.75 | 4172.8125 | 3146.0625 | 1400.7188 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-13 01:52 | 6046.125 | 6046.125 | 6046.125 | 6046.125 | 6046.125 | 6046.125 | 6046.125 | 5920.3125 | 5603.9062 | 4154.0625 | 1738.125 | 5997 | 5997 | 5997 | 5997 | 5997 | 5997 | 5997 | 5871.1875 | 5554.7812 | 4104.9375 | 1713.6562 | 4364.9062 | 4364.9062 | 4364.9062 | 4364.9062 | 4364.9062 | 4364.9062 | 4364.9062 | 4288.2188 | 4197.2812 | 3170.5312 | 1400.7188 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-14 02:15 | 6070.5 | 6070.5 | 6070.5 | 6070.5 | 6070.5 | 6070.5 | 6070.5 | 5944.6875 | 5628.2812 | 4154.0625 | 1738.125 | 6021.375 | 6021.375 | 6021.375 | 6021.375 | 6021.375 | 6021.375 | 6021.375 | 5895.5625 | 5579.1562 | 4104.9375 | 1713.6562 | 4389.2812 | 4389.2812 | 4389.2812 | 4389.2812 | 4389.2812 | 4389.2812 | 4389.2812 | 4312.5938 | 4221.6562 | 3170.5312 | 1400.7188 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-15 01:41 | 6093.9375 | 6093.9375 | 6093.9375 | 6093.9375 | 6093.9375 | 6093.9375 | 6093.9375 | 5968.125 | 5651.7188 | 4154.0625 | 1738.125 | 6044.8125 | 6044.8125 | 6044.8125 | 6044.8125 | 6044.8125 | 6044.8125 | 6044.8125 | 5919 | 5602.5938 | 4104.9375 | 1713.6562 | 4412.7188 | 4412.7188 | 4412.7188 | 4412.7188 | 4412.7188 | 4412.7188 | 4412.7188 | 4336.0312 | 4245.0938 | 3170.5312 | 1400.7188 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-16 02:21 | 6118.5938 | 6118.5938 | 6118.5938 | 6118.5938 | 6118.5938 | 6118.5938 | 6118.5938 | 5992.7812 | 5676.375 | 4154.0625 | 1738.125 | 6069.4688 | 6069.4688 | 6069.4688 | 6069.4688 | 6069.4688 | 6069.4688 | 6069.4688 | 5943.6562 | 5627.25 | 4104.9375 | 1713.6562 | 4437.375 | 4437.375 | 4437.375 | 4437.375 | 4437.375 | 4437.375 | 4437.375 | 4360.6875 | 4269.75 | 3170.5312 | 1400.7188 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-17 01:47 | 6142.0312 | 6142.0312 | 6142.0312 | 6142.0312 | 6142.0312 | 6142.0312 | 6142.0312 | 6016.2188 | 5699.8125 | 4177.5 | 1738.125 | 6092.9062 | 6092.9062 | 6092.9062 | 6092.9062 | 6092.9062 | 6092.9062 | 6092.9062 | 5967.0938 | 5650.6875 | 4128.375 | 1713.6562 | 4460.8125 | 4460.8125 | 4460.8125 | 4460.8125 | 4460.8125 | 4460.8125 | 4460.8125 | 4384.125 | 4293.1875 | 3193.9688 | 1400.7188 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-18 02:26 | 6166.6875 | 6166.6875 | 6166.6875 | 6166.6875 | 6166.6875 | 6166.6875 | 6166.6875 | 6040.875 | 5724.4688 | 4202.1562 | 1762.7812 | 6117.5625 | 6117.5625 | 6117.5625 | 6117.5625 | 6117.5625 | 6117.5625 | 6117.5625 | 5991.75 | 5675.3438 | 4153.0312 | 1738.3125 | 4485.4688 | 4485.4688 | 4485.4688 | 4485.4688 | 4485.4688 | 4485.4688 | 4485.4688 | 4408.7812 | 4317.8438 | 3218.625 | 1425.375 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-19 03:00 | 6191.25 | 6191.25 | 6191.25 | 6191.25 | 6191.25 | 6191.25 | 6191.25 | 6065.4375 | 5749.0312 | 4202.1562 | 1762.7812 | 6142.125 | 6142.125 | 6142.125 | 6142.125 | 6142.125 | 6142.125 | 6142.125 | 6016.3125 | 5699.9062 | 4153.0312 | 1738.3125 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4433.3438 | 4342.4062 | 3218.625 | 1425.375 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-20 03:28 | 6215.7188 | 6215.7188 | 6215.7188 | 6215.7188 | 6215.7188 | 6215.7188 | 6215.7188 | 6089.9062 | 5749.0312 | 4202.1562 | 1762.7812 | 6166.5938 | 6166.5938 | 6166.5938 | 6166.5938 | 6166.5938 | 6166.5938 | 6166.5938 | 6040.7812 | 5699.9062 | 4153.0312 | 1738.3125 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4433.3438 | 4342.4062 | 3218.625 | 1425.375 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-21 03:51 | 6240.0938 | 6240.0938 | 6240.0938 | 6240.0938 | 6240.0938 | 6240.0938 | 6240.0938 | 6114.2812 | 5773.4062 | 4226.5312 | 1787.1562 | 6190.9688 | 6190.9688 | 6190.9688 | 6190.9688 | 6190.9688 | 6190.9688 | 6190.9688 | 6065.1562 | 5724.2812 | 4177.4062 | 1762.6875 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4433.3438 | 4342.4062 | 3218.625 | 1425.375 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-22 00:34 | 6260.8125 | 6260.8125 | 6260.8125 | 6260.8125 | 6260.8125 | 6260.8125 | 6260.8125 | 6135 | 5794.125 | 4247.25 | 1787.1562 | 6211.6875 | 6211.6875 | 6211.6875 | 6211.6875 | 6211.6875 | 6211.6875 | 6211.6875 | 6085.875 | 5745 | 4198.125 | 1762.6875 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4510.0312 | 4433.3438 | 4342.4062 | 3218.625 | 1425.375 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-23 00:56 | 6285.1875 | 6285.1875 | 6285.1875 | 6285.1875 | 6285.1875 | 6285.1875 | 6285.1875 | 6159.375 | 5818.5 | 4271.625 | 1811.5312 | 6236.0625 | 6236.0625 | 6236.0625 | 6236.0625 | 6236.0625 | 6236.0625 | 6236.0625 | 6110.25 | 5769.375 | 4222.5 | 1787.0625 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4457.7188 | 4366.7812 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-24 01:36 | 6309.8438 | 6309.8438 | 6309.8438 | 6309.8438 | 6309.8438 | 6309.8438 | 6309.8438 | 6184.0312 | 5818.5 | 4271.625 | 1811.5312 | 6260.7188 | 6260.7188 | 6260.7188 | 6260.7188 | 6260.7188 | 6260.7188 | 6260.7188 | 6134.9062 | 5769.375 | 4222.5 | 1787.0625 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4534.4062 | 4457.7188 | 4366.7812 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-25 01:58 | 6334.2188 | 6334.2188 | 6334.2188 | 6334.2188 | 6334.2188 | 6334.2188 | 6334.2188 | 6208.4062 | 5842.875 | 4271.625 | 1811.5312 | 6285.0938 | 6285.0938 | 6285.0938 | 6285.0938 | 6285.0938 | 6285.0938 | 6285.0938 | 6159.2812 | 5793.75 | 4222.5 | 1787.0625 | 4558.7812 | 4558.7812 | 4558.7812 | 4558.7812 | 4558.7812 | 4558.7812 | 4558.7812 | 4482.0938 | 4391.1562 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-26 02:26 | 6358.6875 | 6358.6875 | 6358.6875 | 6358.6875 | 6358.6875 | 6358.6875 | 6358.6875 | 6232.875 | 5867.3438 | 4271.625 | 1811.5312 | 6309.5625 | 6309.5625 | 6309.5625 | 6309.5625 | 6309.5625 | 6309.5625 | 6309.5625 | 6183.75 | 5818.2188 | 4222.5 | 1787.0625 | 4583.25 | 4583.25 | 4583.25 | 4583.25 | 4583.25 | 4583.25 | 4583.25 | 4506.5625 | 4415.625 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-27 02:49 | 6383.0625 | 6383.0625 | 6383.0625 | 6383.0625 | 6383.0625 | 6383.0625 | 6383.0625 | 6257.25 | 5867.3438 | 4271.625 | 1811.5312 | 6333.9375 | 6333.9375 | 6333.9375 | 6333.9375 | 6333.9375 | 6333.9375 | 6333.9375 | 6208.125 | 5818.2188 | 4222.5 | 1787.0625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4530.9375 | 4415.625 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-28 03:22 | 6407.625 | 6407.625 | 6407.625 | 6407.625 | 6407.625 | 6407.625 | 6407.625 | 6281.8125 | 5891.9062 | 4296.1875 | 1836.0938 | 6358.5 | 6358.5 | 6358.5 | 6358.5 | 6358.5 | 6358.5 | 6358.5 | 6232.6875 | 5842.7812 | 4247.0625 | 1811.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4607.625 | 4530.9375 | 4415.625 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-29 04:02 | 6432.2812 | 6432.2812 | 6432.2812 | 6432.2812 | 6432.2812 | 6432.2812 | 6432.2812 | 6306.4688 | 5891.9062 | 4296.1875 | 1836.0938 | 6383.1562 | 6383.1562 | 6383.1562 | 6383.1562 | 6383.1562 | 6383.1562 | 6383.1562 | 6257.3438 | 5842.7812 | 4247.0625 | 1811.625 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4555.5938 | 4415.625 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-11-30 00:34 | 6452.8125 | 6452.8125 | 6452.8125 | 6452.8125 | 6452.8125 | 6452.8125 | 6452.8125 | 6327 | 5912.4375 | 4316.7188 | 1836.0938 | 6403.6875 | 6403.6875 | 6403.6875 | 6403.6875 | 6403.6875 | 6403.6875 | 6403.6875 | 6277.875 | 5863.3125 | 4267.5938 | 1811.625 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4555.5938 | 4415.625 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-01 04:19 | 6480.5625 | 6480.5625 | 6480.5625 | 6480.5625 | 6480.5625 | 6480.5625 | 6480.5625 | 6354.75 | 5940.1875 | 4316.7188 | 1836.0938 | 6431.4375 | 6431.4375 | 6431.4375 | 6431.4375 | 6431.4375 | 6431.4375 | 6431.4375 | 6305.625 | 5891.0625 | 4267.5938 | 1811.625 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4632.2812 | 4555.5938 | 4415.625 | 3243 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-02 00:51 | 6501.0938 | 6501.0938 | 6501.0938 | 6501.0938 | 6501.0938 | 6501.0938 | 6501.0938 | 6375.2812 | 5960.7188 | 4337.25 | 1836.0938 | 6451.9688 | 6451.9688 | 6451.9688 | 6451.9688 | 6451.9688 | 6451.9688 | 6451.9688 | 6326.1562 | 5911.5938 | 4288.125 | 1811.625 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4576.125 | 4436.1562 | 3263.5312 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-03 01:13 | 6525.4688 | 6525.4688 | 6525.4688 | 6525.4688 | 6525.4688 | 6525.4688 | 6525.4688 | 6399.6562 | 5985.0938 | 4361.625 | 1860.4688 | 6476.3438 | 6476.3438 | 6476.3438 | 6476.3438 | 6476.3438 | 6476.3438 | 6476.3438 | 6350.5312 | 5935.9688 | 4312.5 | 1836 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4652.8125 | 4576.125 | 4436.1562 | 3263.5312 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-04 01:41 | 6549.9375 | 6549.9375 | 6549.9375 | 6549.9375 | 6549.9375 | 6549.9375 | 6549.9375 | 6424.125 | 6009.5625 | 4361.625 | 1860.4688 | 6500.8125 | 6500.8125 | 6500.8125 | 6500.8125 | 6500.8125 | 6500.8125 | 6500.8125 | 6375 | 5960.4375 | 4312.5 | 1836 | 4677.2812 | 4677.2812 | 4677.2812 | 4677.2812 | 4677.2812 | 4677.2812 | 4677.2812 | 4600.5938 | 4460.625 | 3263.5312 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-05 02:09 | 6574.4062 | 6574.4062 | 6574.4062 | 6574.4062 | 6574.4062 | 6574.4062 | 6574.4062 | 6448.5938 | 6034.0312 | 4361.625 | 1860.4688 | 6525.2812 | 6525.2812 | 6525.2812 | 6525.2812 | 6525.2812 | 6525.2812 | 6525.2812 | 6399.4688 | 5984.9062 | 4312.5 | 1836 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4625.0625 | 4485.0938 | 3263.5312 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-06 02:43 | 6598.9688 | 6598.9688 | 6598.9688 | 6598.9688 | 6598.9688 | 6598.9688 | 6598.9688 | 6473.1562 | 6058.5938 | 4361.625 | 1860.4688 | 6549.8438 | 6549.8438 | 6549.8438 | 6549.8438 | 6549.8438 | 6549.8438 | 6549.8438 | 6424.0312 | 6009.4688 | 4312.5 | 1836 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4625.0625 | 4485.0938 | 3263.5312 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-07 03:11 | 6623.4375 | 6623.4375 | 6623.4375 | 6623.4375 | 6623.4375 | 6623.4375 | 6623.4375 | 6497.625 | 6083.0625 | 4386.0938 | 1860.4688 | 6574.3125 | 6574.3125 | 6574.3125 | 6574.3125 | 6574.3125 | 6574.3125 | 6574.3125 | 6448.5 | 6033.9375 | 4336.9688 | 1836 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4701.75 | 4625.0625 | 4485.0938 | 3263.5312 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-08 03:39 | 6647.9062 | 6647.9062 | 6647.9062 | 6647.9062 | 6647.9062 | 6647.9062 | 6647.9062 | 6522.0938 | 6107.5312 | 4410.5625 | 1860.4688 | 6598.7812 | 6598.7812 | 6598.7812 | 6598.7812 | 6598.7812 | 6598.7812 | 6598.7812 | 6472.9688 | 6058.4062 | 4361.4375 | 1836 | 4726.2188 | 4726.2188 | 4726.2188 | 4726.2188 | 4726.2188 | 4726.2188 | 4726.2188 | 4649.5312 | 4509.5625 | 3288 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-09 00:17 | 6668.5312 | 6668.5312 | 6668.5312 | 6668.5312 | 6668.5312 | 6668.5312 | 6668.5312 | 6542.7188 | 6128.1562 | 4410.5625 | 1860.4688 | 6619.4062 | 6619.4062 | 6619.4062 | 6619.4062 | 6619.4062 | 6619.4062 | 6619.4062 | 6493.5938 | 6079.0312 | 4361.4375 | 1836 | 4746.8438 | 4746.8438 | 4746.8438 | 4746.8438 | 4746.8438 | 4746.8438 | 4746.8438 | 4670.1562 | 4530.1875 | 3288 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-10 00:45 | 6693 | 6693 | 6693 | 6693 | 6693 | 6693 | 6693 | 6567.1875 | 6152.625 | 4410.5625 | 1860.4688 | 6643.875 | 6643.875 | 6643.875 | 6643.875 | 6643.875 | 6643.875 | 6643.875 | 6518.0625 | 6103.5 | 4361.4375 | 1836 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4694.625 | 4554.6562 | 3288 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-11 01:08 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6591.5625 | 6177 | 4434.9375 | 1884.8438 | 6668.25 | 6668.25 | 6668.25 | 6668.25 | 6668.25 | 6668.25 | 6668.25 | 6542.4375 | 6127.875 | 4385.8125 | 1860.375 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4771.3125 | 4694.625 | 4554.6562 | 3288 | 1449.75 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1852.7812 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-12 01:41 | 6741.9375 | 6741.9375 | 6741.9375 | 6741.9375 | 6741.9375 | 6741.9375 | 6741.9375 | 6616.125 | 6201.5625 | 4434.9375 | 1884.8438 | 6692.8125 | 6692.8125 | 6692.8125 | 6692.8125 | 6692.8125 | 6692.8125 | 6692.8125 | 6567 | 6152.4375 | 4385.8125 | 1860.375 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4719.1875 | 4579.2188 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-13 02:15 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6640.6875 | 6226.125 | 4459.5 | 1884.8438 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6717.375 | 6591.5625 | 6177 | 4410.375 | 1860.375 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4795.875 | 4719.1875 | 4579.2188 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-14 02:54 | 6791.1562 | 6791.1562 | 6791.1562 | 6791.1562 | 6791.1562 | 6791.1562 | 6791.1562 | 6665.3438 | 6250.7812 | 4459.5 | 1884.8438 | 6742.0312 | 6742.0312 | 6742.0312 | 6742.0312 | 6742.0312 | 6742.0312 | 6742.0312 | 6616.2188 | 6201.6562 | 4410.375 | 1860.375 | 4820.5312 | 4820.5312 | 4820.5312 | 4820.5312 | 4820.5312 | 4820.5312 | 4820.5312 | 4743.8438 | 4603.875 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-15 03:22 | 6815.625 | 6815.625 | 6815.625 | 6815.625 | 6815.625 | 6815.625 | 6815.625 | 6689.8125 | 6250.7812 | 4459.5 | 1884.8438 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6766.5 | 6640.6875 | 6201.6562 | 4410.375 | 1860.375 | 4845 | 4845 | 4845 | 4845 | 4845 | 4845 | 4845 | 4768.3125 | 4603.875 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-16 03:56 | 6840.1875 | 6840.1875 | 6840.1875 | 6840.1875 | 6840.1875 | 6840.1875 | 6840.1875 | 6714.375 | 6275.3438 | 4459.5 | 1884.8438 | 6791.0625 | 6791.0625 | 6791.0625 | 6791.0625 | 6791.0625 | 6791.0625 | 6791.0625 | 6665.25 | 6226.2188 | 4410.375 | 1860.375 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4792.875 | 4628.4375 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-17 00:28 | 6860.7188 | 6860.7188 | 6860.7188 | 6860.7188 | 6860.7188 | 6860.7188 | 6860.7188 | 6734.9062 | 6295.875 | 4480.0312 | 1905.375 | 6811.5938 | 6811.5938 | 6811.5938 | 6811.5938 | 6811.5938 | 6811.5938 | 6811.5938 | 6685.7812 | 6246.75 | 4430.9062 | 1880.9062 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4792.875 | 4628.4375 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-18 00:56 | 6885.1875 | 6885.1875 | 6885.1875 | 6885.1875 | 6885.1875 | 6885.1875 | 6885.1875 | 6759.375 | 6320.3438 | 4504.5 | 1905.375 | 6836.0625 | 6836.0625 | 6836.0625 | 6836.0625 | 6836.0625 | 6836.0625 | 6836.0625 | 6710.25 | 6271.2188 | 4455.375 | 1880.9062 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4869.5625 | 4792.875 | 4628.4375 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-19 01:24 | 6909.6562 | 6909.6562 | 6909.6562 | 6909.6562 | 6909.6562 | 6909.6562 | 6909.6562 | 6783.8438 | 6344.8125 | 4504.5 | 1905.375 | 6860.5312 | 6860.5312 | 6860.5312 | 6860.5312 | 6860.5312 | 6860.5312 | 6860.5312 | 6734.7188 | 6295.6875 | 4455.375 | 1880.9062 | 4894.0312 | 4894.0312 | 4894.0312 | 4894.0312 | 4894.0312 | 4894.0312 | 4894.0312 | 4817.3438 | 4652.9062 | 3288 | 1449.75 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-20 01:47 | 6934.0312 | 6934.0312 | 6934.0312 | 6934.0312 | 6934.0312 | 6934.0312 | 6934.0312 | 6808.2188 | 6369.1875 | 4528.875 | 1929.75 | 6884.9062 | 6884.9062 | 6884.9062 | 6884.9062 | 6884.9062 | 6884.9062 | 6884.9062 | 6759.0938 | 6320.0625 | 4479.75 | 1905.2812 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4841.7188 | 4677.2812 | 3312.375 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-21 02:15 | 6958.5 | 6958.5 | 6958.5 | 6958.5 | 6958.5 | 6958.5 | 6958.5 | 6832.6875 | 6393.6562 | 4553.3438 | 1929.75 | 6909.375 | 6909.375 | 6909.375 | 6909.375 | 6909.375 | 6909.375 | 6909.375 | 6783.5625 | 6344.5312 | 4504.2188 | 1905.2812 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4841.7188 | 4677.2812 | 3312.375 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-22 02:43 | 6982.9688 | 6982.9688 | 6982.9688 | 6982.9688 | 6982.9688 | 6982.9688 | 6982.9688 | 6857.1562 | 6418.125 | 4577.8125 | 1954.2188 | 6933.8438 | 6933.8438 | 6933.8438 | 6933.8438 | 6933.8438 | 6933.8438 | 6933.8438 | 6808.0312 | 6369 | 4528.6875 | 1929.75 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4841.7188 | 4677.2812 | 3312.375 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-23 03:11 | 7007.4375 | 7007.4375 | 7007.4375 | 7007.4375 | 7007.4375 | 7007.4375 | 7007.4375 | 6881.625 | 6442.5938 | 4602.2812 | 1954.2188 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6832.5 | 6393.4688 | 4553.1562 | 1929.75 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4841.7188 | 4677.2812 | 3312.375 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-24 03:39 | 7031.9062 | 7031.9062 | 7031.9062 | 7031.9062 | 7031.9062 | 7031.9062 | 7031.9062 | 6906.0938 | 6467.0625 | 4602.2812 | 1954.2188 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6958.3125 | 6832.5 | 6393.4688 | 4553.1562 | 1929.75 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4841.7188 | 4677.2812 | 3312.375 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-25 04:02 | 7056.2812 | 7056.2812 | 7056.2812 | 7056.2812 | 7056.2812 | 7056.2812 | 7056.2812 | 6930.4688 | 6491.4375 | 4626.6562 | 1954.2188 | 6982.6875 | 6982.6875 | 6982.6875 | 6982.6875 | 6982.6875 | 6982.6875 | 6982.6875 | 6856.875 | 6417.8438 | 4577.5312 | 1929.75 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4918.4062 | 4841.7188 | 4677.2812 | 3312.375 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-26 00:22 | 7076.625 | 7076.625 | 7076.625 | 7076.625 | 7076.625 | 7076.625 | 7076.625 | 6950.8125 | 6511.7812 | 4647 | 1954.2188 | 7003.0312 | 7003.0312 | 7003.0312 | 7003.0312 | 7003.0312 | 7003.0312 | 7003.0312 | 6877.2188 | 6438.1875 | 4597.875 | 1929.75 | 4938.75 | 4938.75 | 4938.75 | 4938.75 | 4938.75 | 4938.75 | 4938.75 | 4862.0625 | 4697.625 | 3332.7188 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-27 00:51 | 7101.0938 | 7101.0938 | 7101.0938 | 7101.0938 | 7101.0938 | 7101.0938 | 7101.0938 | 6975.2812 | 6536.25 | 4671.4688 | 1954.2188 | 7027.5 | 7027.5 | 7027.5 | 7027.5 | 7027.5 | 7027.5 | 7027.5 | 6901.6875 | 6462.6562 | 4622.3438 | 1929.75 | 4963.2188 | 4963.2188 | 4963.2188 | 4963.2188 | 4963.2188 | 4963.2188 | 4963.2188 | 4886.5312 | 4722.0938 | 3357.1875 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-28 01:24 | 7125.6562 | 7125.6562 | 7125.6562 | 7125.6562 | 7125.6562 | 7125.6562 | 7125.6562 | 6999.8438 | 6560.8125 | 4671.4688 | 1954.2188 | 7052.0625 | 7052.0625 | 7052.0625 | 7052.0625 | 7052.0625 | 7052.0625 | 7052.0625 | 6926.25 | 6487.2188 | 4622.3438 | 1929.75 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4911.0938 | 4746.6562 | 3357.1875 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-29 01:13 | 7149.4688 | 7149.4688 | 7149.4688 | 7149.4688 | 7149.4688 | 7149.4688 | 7149.4688 | 7023.6562 | 6584.625 | 4671.4688 | 1954.2188 | 7075.875 | 7075.875 | 7075.875 | 7075.875 | 7075.875 | 7075.875 | 7075.875 | 6950.0625 | 6511.0312 | 4622.3438 | 1929.75 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4987.7812 | 4911.0938 | 4746.6562 | 3357.1875 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-30 00:39 | 7172.9062 | 7172.9062 | 7172.9062 | 7172.9062 | 7172.9062 | 7172.9062 | 7172.9062 | 7047.0938 | 6608.0625 | 4694.9062 | 1954.2188 | 7099.3125 | 7099.3125 | 7099.3125 | 7099.3125 | 7099.3125 | 7099.3125 | 7099.3125 | 6973.5 | 6534.4688 | 4645.7812 | 1929.75 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 4934.5312 | 4770.0938 | 3380.625 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2005-12-31 00:34 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7071 | 6631.9688 | 4718.8125 | 1978.125 | 7123.2188 | 7123.2188 | 7123.2188 | 7123.2188 | 7123.2188 | 7123.2188 | 7123.2188 | 6997.4062 | 6558.375 | 4669.6875 | 1953.6562 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 5011.2188 | 4934.5312 | 4770.0938 | 3380.625 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-01 01:02 | 7221.2812 | 7221.2812 | 7221.2812 | 7221.2812 | 7221.2812 | 7221.2812 | 7221.2812 | 7095.4688 | 6656.4375 | 4743.2812 | 1978.125 | 7147.6875 | 7147.6875 | 7147.6875 | 7147.6875 | 7147.6875 | 7147.6875 | 7147.6875 | 7021.875 | 6582.8438 | 4694.1562 | 1953.6562 | 5035.6875 | 5035.6875 | 5035.6875 | 5035.6875 | 5035.6875 | 5035.6875 | 5035.6875 | 4959 | 4794.5625 | 3405.0938 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-02 01:41 | 7245.9375 | 7245.9375 | 7245.9375 | 7245.9375 | 7245.9375 | 7245.9375 | 7245.9375 | 7120.125 | 6681.0938 | 4767.9375 | 1978.125 | 7172.3438 | 7172.3438 | 7172.3438 | 7172.3438 | 7172.3438 | 7172.3438 | 7172.3438 | 7046.5312 | 6607.5 | 4718.8125 | 1953.6562 | 5060.3438 | 5060.3438 | 5060.3438 | 5060.3438 | 5060.3438 | 5060.3438 | 5060.3438 | 4983.6562 | 4819.2188 | 3429.75 | 1474.125 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-03 02:09 | 7270.4062 | 7270.4062 | 7270.4062 | 7270.4062 | 7270.4062 | 7270.4062 | 7270.4062 | 7144.5938 | 6705.5625 | 4792.4062 | 2002.5938 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7196.8125 | 7071 | 6631.9688 | 4743.2812 | 1978.125 | 5084.8125 | 5084.8125 | 5084.8125 | 5084.8125 | 5084.8125 | 5084.8125 | 5084.8125 | 5008.125 | 4843.6875 | 3454.2188 | 1498.5938 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1877.3438 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-04 02:43 | 7294.9688 | 7294.9688 | 7294.9688 | 7294.9688 | 7294.9688 | 7294.9688 | 7294.9688 | 7169.1562 | 6730.125 | 4792.4062 | 2002.5938 | 7221.375 | 7221.375 | 7221.375 | 7221.375 | 7221.375 | 7221.375 | 7221.375 | 7095.5625 | 6656.5312 | 4743.2812 | 1978.125 | 5109.375 | 5109.375 | 5109.375 | 5109.375 | 5109.375 | 5109.375 | 5109.375 | 5032.6875 | 4868.25 | 3454.2188 | 1498.5938 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-05 01:02 | 7317.2812 | 7317.2812 | 7317.2812 | 7317.2812 | 7317.2812 | 7317.2812 | 7317.2812 | 7191.4688 | 6752.4375 | 4792.4062 | 2002.5938 | 7243.6875 | 7243.6875 | 7243.6875 | 7243.6875 | 7243.6875 | 7243.6875 | 7243.6875 | 7117.875 | 6678.8438 | 4743.2812 | 1978.125 | 5131.6875 | 5131.6875 | 5131.6875 | 5131.6875 | 5131.6875 | 5131.6875 | 5131.6875 | 5055 | 4890.5625 | 3454.2188 | 1498.5938 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-06 01:19 | 7341.5625 | 7341.5625 | 7341.5625 | 7341.5625 | 7341.5625 | 7341.5625 | 7341.5625 | 7215.75 | 6776.7188 | 4816.6875 | 2002.5938 | 7267.9688 | 7267.9688 | 7267.9688 | 7267.9688 | 7267.9688 | 7267.9688 | 7267.9688 | 7142.1562 | 6703.125 | 4767.5625 | 1978.125 | 5155.9688 | 5155.9688 | 5155.9688 | 5155.9688 | 5155.9688 | 5155.9688 | 5155.9688 | 5079.2812 | 4914.8438 | 3478.5 | 1498.5938 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-07 01:47 | 7366.0312 | 7366.0312 | 7366.0312 | 7366.0312 | 7366.0312 | 7366.0312 | 7366.0312 | 7240.2188 | 6801.1875 | 4841.1562 | 2027.0625 | 7292.4375 | 7292.4375 | 7292.4375 | 7292.4375 | 7292.4375 | 7292.4375 | 7292.4375 | 7166.625 | 6727.5938 | 4792.0312 | 2002.5938 | 5180.4375 | 5180.4375 | 5180.4375 | 5180.4375 | 5180.4375 | 5180.4375 | 5180.4375 | 5103.75 | 4939.3125 | 3502.9688 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-08 01:19 | 7389.5625 | 7389.5625 | 7389.5625 | 7389.5625 | 7389.5625 | 7389.5625 | 7389.5625 | 7263.75 | 6824.7188 | 4864.6875 | 2027.0625 | 7315.9688 | 7315.9688 | 7315.9688 | 7315.9688 | 7315.9688 | 7315.9688 | 7315.9688 | 7190.1562 | 6751.125 | 4815.5625 | 2002.5938 | 5203.9688 | 5203.9688 | 5203.9688 | 5203.9688 | 5203.9688 | 5203.9688 | 5203.9688 | 5127.2812 | 4962.8438 | 3526.5 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-09 01:41 | 7413.9375 | 7413.9375 | 7413.9375 | 7413.9375 | 7413.9375 | 7413.9375 | 7413.9375 | 7288.125 | 6849.0938 | 4864.6875 | 2027.0625 | 7340.3438 | 7340.3438 | 7340.3438 | 7340.3438 | 7340.3438 | 7340.3438 | 7340.3438 | 7214.5312 | 6775.5 | 4815.5625 | 2002.5938 | 5228.3438 | 5228.3438 | 5228.3438 | 5228.3438 | 5228.3438 | 5228.3438 | 5228.3438 | 5151.6562 | 4987.2188 | 3526.5 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-10 02:21 | 7438.5938 | 7438.5938 | 7438.5938 | 7438.5938 | 7438.5938 | 7438.5938 | 7438.5938 | 7312.7812 | 6873.75 | 4864.6875 | 2027.0625 | 7365 | 7365 | 7365 | 7365 | 7365 | 7365 | 7365 | 7239.1875 | 6800.1562 | 4815.5625 | 2002.5938 | 5253 | 5253 | 5253 | 5253 | 5253 | 5253 | 5253 | 5176.3125 | 5011.875 | 3526.5 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-11 02:43 | 7462.9688 | 7462.9688 | 7462.9688 | 7462.9688 | 7462.9688 | 7462.9688 | 7462.9688 | 7337.1562 | 6898.125 | 4864.6875 | 2027.0625 | 7389.375 | 7389.375 | 7389.375 | 7389.375 | 7389.375 | 7389.375 | 7389.375 | 7263.5625 | 6824.5312 | 4815.5625 | 2002.5938 | 5277.375 | 5277.375 | 5277.375 | 5277.375 | 5277.375 | 5277.375 | 5277.375 | 5200.6875 | 5036.25 | 3526.5 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-12 03:11 | 7487.4375 | 7487.4375 | 7487.4375 | 7487.4375 | 7487.4375 | 7487.4375 | 7487.4375 | 7361.625 | 6922.5938 | 4864.6875 | 2027.0625 | 7413.8438 | 7413.8438 | 7413.8438 | 7413.8438 | 7413.8438 | 7413.8438 | 7413.8438 | 7288.0312 | 6849 | 4815.5625 | 2002.5938 | 5301.8438 | 5301.8438 | 5301.8438 | 5301.8438 | 5301.8438 | 5301.8438 | 5301.8438 | 5225.1562 | 5060.7188 | 3526.5 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-13 03:45 | 7512 | 7512 | 7512 | 7512 | 7512 | 7512 | 7512 | 7386.1875 | 6947.1562 | 4889.25 | 2027.0625 | 7438.4062 | 7438.4062 | 7438.4062 | 7438.4062 | 7438.4062 | 7438.4062 | 7438.4062 | 7312.5938 | 6873.5625 | 4840.125 | 2002.5938 | 5326.4062 | 5326.4062 | 5326.4062 | 5326.4062 | 5326.4062 | 5326.4062 | 5326.4062 | 5249.7188 | 5085.2812 | 3551.0625 | 1523.0625 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-14 00:06 | 7532.3438 | 7532.3438 | 7532.3438 | 7532.3438 | 7532.3438 | 7532.3438 | 7532.3438 | 7406.5312 | 6967.5 | 4909.5938 | 2047.4062 | 7458.75 | 7458.75 | 7458.75 | 7458.75 | 7458.75 | 7458.75 | 7458.75 | 7332.9375 | 6893.9062 | 4860.4688 | 2022.9375 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5270.0625 | 5105.625 | 3571.4062 | 1543.4062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-15 00:34 | 7556.8125 | 7556.8125 | 7556.8125 | 7556.8125 | 7556.8125 | 7556.8125 | 7556.8125 | 7431 | 6991.9688 | 4934.0625 | 2071.875 | 7483.2188 | 7483.2188 | 7483.2188 | 7483.2188 | 7483.2188 | 7483.2188 | 7483.2188 | 7357.4062 | 6918.375 | 4884.9375 | 2047.4062 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5346.75 | 5270.0625 | 5105.625 | 3571.4062 | 1543.4062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-16 01:02 | 7581.2812 | 7581.2812 | 7581.2812 | 7581.2812 | 7581.2812 | 7581.2812 | 7581.2812 | 7455.4688 | 7016.4375 | 4934.0625 | 2071.875 | 7507.6875 | 7507.6875 | 7507.6875 | 7507.6875 | 7507.6875 | 7507.6875 | 7507.6875 | 7381.875 | 6942.8438 | 4884.9375 | 2047.4062 | 5371.2188 | 5371.2188 | 5371.2188 | 5371.2188 | 5371.2188 | 5371.2188 | 5371.2188 | 5294.5312 | 5130.0938 | 3571.4062 | 1543.4062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-17 01:30 | 7605.75 | 7605.75 | 7605.75 | 7605.75 | 7605.75 | 7605.75 | 7605.75 | 7479.9375 | 7040.9062 | 4958.5312 | 2096.3438 | 7532.1562 | 7532.1562 | 7532.1562 | 7532.1562 | 7532.1562 | 7532.1562 | 7532.1562 | 7406.3438 | 6967.3125 | 4909.4062 | 2071.875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5319 | 5154.5625 | 3595.875 | 1567.875 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-18 01:52 | 7630.125 | 7630.125 | 7630.125 | 7630.125 | 7630.125 | 7630.125 | 7630.125 | 7504.3125 | 7065.2812 | 4982.9062 | 2120.7188 | 7556.5312 | 7556.5312 | 7556.5312 | 7556.5312 | 7556.5312 | 7556.5312 | 7556.5312 | 7430.7188 | 6991.6875 | 4933.7812 | 2096.25 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5395.6875 | 5319 | 5154.5625 | 3595.875 | 1567.875 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-19 02:21 | 7654.5938 | 7654.5938 | 7654.5938 | 7654.5938 | 7654.5938 | 7654.5938 | 7654.5938 | 7528.7812 | 7065.2812 | 4982.9062 | 2120.7188 | 7581 | 7581 | 7581 | 7581 | 7581 | 7581 | 7581 | 7455.1875 | 6991.6875 | 4933.7812 | 2096.25 | 5420.1562 | 5420.1562 | 5420.1562 | 5420.1562 | 5420.1562 | 5420.1562 | 5420.1562 | 5343.4688 | 5154.5625 | 3595.875 | 1567.875 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-20 03:11 | 7679.4375 | 7679.4375 | 7679.4375 | 7679.4375 | 7679.4375 | 7679.4375 | 7679.4375 | 7553.625 | 7090.125 | 5007.75 | 2120.7188 | 7605.8438 | 7605.8438 | 7605.8438 | 7605.8438 | 7605.8438 | 7605.8438 | 7605.8438 | 7480.0312 | 7016.5312 | 4958.625 | 2096.25 | 5445 | 5445 | 5445 | 5445 | 5445 | 5445 | 5445 | 5368.3125 | 5179.4062 | 3620.7188 | 1567.875 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-21 02:38 | 7702.875 | 7702.875 | 7702.875 | 7702.875 | 7702.875 | 7702.875 | 7702.875 | 7577.0625 | 7113.5625 | 5031.1875 | 2144.1562 | 7629.2812 | 7629.2812 | 7629.2812 | 7629.2812 | 7629.2812 | 7629.2812 | 7629.2812 | 7503.4688 | 7039.9688 | 4982.0625 | 2119.6875 | 5468.4375 | 5468.4375 | 5468.4375 | 5468.4375 | 5468.4375 | 5468.4375 | 5468.4375 | 5391.75 | 5202.8438 | 3644.1562 | 1591.3125 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1901.9062 | 1612.7812 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-22 03:00 | 7727.25 | 7727.25 | 7727.25 | 7727.25 | 7727.25 | 7727.25 | 7727.25 | 7601.4375 | 7137.9375 | 5055.5625 | 2144.1562 | 7653.6562 | 7653.6562 | 7653.6562 | 7653.6562 | 7653.6562 | 7653.6562 | 7653.6562 | 7527.8438 | 7064.3438 | 5006.4375 | 2119.6875 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5416.125 | 5227.2188 | 3668.5312 | 1591.3125 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1637.1562 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-23 03:34 | 7751.8125 | 7751.8125 | 7751.8125 | 7751.8125 | 7751.8125 | 7751.8125 | 7751.8125 | 7626 | 7162.5 | 5080.125 | 2168.7188 | 7678.2188 | 7678.2188 | 7678.2188 | 7678.2188 | 7678.2188 | 7678.2188 | 7678.2188 | 7552.4062 | 7088.9062 | 5031 | 2144.25 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5416.125 | 5227.2188 | 3668.5312 | 1591.3125 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1637.1562 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-24 03:56 | 7776.1875 | 7776.1875 | 7776.1875 | 7776.1875 | 7776.1875 | 7776.1875 | 7776.1875 | 7650.375 | 7186.875 | 5104.5 | 2168.7188 | 7702.5938 | 7702.5938 | 7702.5938 | 7702.5938 | 7702.5938 | 7702.5938 | 7702.5938 | 7576.7812 | 7113.2812 | 5055.375 | 2144.25 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5492.8125 | 5416.125 | 5227.2188 | 3668.5312 | 1591.3125 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1926.2812 | 1637.1562 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-25 00:17 | 7796.5312 | 7796.5312 | 7796.5312 | 7796.5312 | 7796.5312 | 7796.5312 | 7796.5312 | 7670.7188 | 7207.2188 | 5124.8438 | 2168.7188 | 7722.9375 | 7722.9375 | 7722.9375 | 7722.9375 | 7722.9375 | 7722.9375 | 7722.9375 | 7597.125 | 7133.625 | 5075.7188 | 2144.25 | 5513.1562 | 5513.1562 | 5513.1562 | 5513.1562 | 5513.1562 | 5513.1562 | 5513.1562 | 5436.4688 | 5247.5625 | 3688.875 | 1591.3125 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1657.5 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-26 00:56 | 7821.1875 | 7821.1875 | 7821.1875 | 7821.1875 | 7821.1875 | 7821.1875 | 7821.1875 | 7695.375 | 7207.2188 | 5124.8438 | 2168.7188 | 7747.5938 | 7747.5938 | 7747.5938 | 7747.5938 | 7747.5938 | 7747.5938 | 7747.5938 | 7621.7812 | 7133.625 | 5075.7188 | 2144.25 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5461.125 | 5247.5625 | 3688.875 | 1591.3125 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1657.5 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-27 01:41 | 7845.9375 | 7845.9375 | 7845.9375 | 7845.9375 | 7845.9375 | 7845.9375 | 7845.9375 | 7720.125 | 7231.9688 | 5149.5938 | 2193.4688 | 7772.3438 | 7772.3438 | 7772.3438 | 7772.3438 | 7772.3438 | 7772.3438 | 7772.3438 | 7646.5312 | 7158.375 | 5100.4688 | 2169 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5537.8125 | 5461.125 | 5247.5625 | 3688.875 | 1591.3125 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1946.625 | 1657.5 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-28 02:09 | 7870.4062 | 7870.4062 | 7870.4062 | 7870.4062 | 7870.4062 | 7870.4062 | 7870.4062 | 7744.5938 | 7256.4375 | 5174.0625 | 2193.4688 | 7796.8125 | 7796.8125 | 7796.8125 | 7796.8125 | 7796.8125 | 7796.8125 | 7796.8125 | 7671 | 7182.8438 | 5124.9375 | 2169 | 5562.2812 | 5562.2812 | 5562.2812 | 5562.2812 | 5562.2812 | 5562.2812 | 5562.2812 | 5485.5938 | 5272.0312 | 3713.3438 | 1591.3125 | 1971.0938 | 1971.0938 | 1971.0938 | 1971.0938 | 1971.0938 | 1971.0938 | 1971.0938 | 1971.0938 | 1971.0938 | 1681.9688 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-29 02:43 | 7894.9688 | 7894.9688 | 7894.9688 | 7894.9688 | 7894.9688 | 7894.9688 | 7894.9688 | 7769.1562 | 7281 | 5198.625 | 2193.4688 | 7821.375 | 7821.375 | 7821.375 | 7821.375 | 7821.375 | 7821.375 | 7821.375 | 7695.5625 | 7207.4062 | 5149.5 | 2169 | 5586.8438 | 5586.8438 | 5586.8438 | 5586.8438 | 5586.8438 | 5586.8438 | 5586.8438 | 5510.1562 | 5296.5938 | 3737.9062 | 1591.3125 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1706.5312 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-30 03:11 | 7919.4375 | 7919.4375 | 7919.4375 | 7919.4375 | 7919.4375 | 7919.4375 | 7919.4375 | 7793.625 | 7305.4688 | 5223.0938 | 2193.4688 | 7845.8438 | 7845.8438 | 7845.8438 | 7845.8438 | 7845.8438 | 7845.8438 | 7845.8438 | 7720.0312 | 7231.875 | 5173.9688 | 2169 | 5611.3125 | 5611.3125 | 5611.3125 | 5611.3125 | 5611.3125 | 5611.3125 | 5611.3125 | 5534.625 | 5321.0625 | 3762.375 | 1591.3125 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1706.5312 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-01-31 03:34 | 7943.8125 | 7943.8125 | 7943.8125 | 7943.8125 | 7943.8125 | 7943.8125 | 7943.8125 | 7818 | 7329.8438 | 5223.0938 | 2193.4688 | 7870.2188 | 7870.2188 | 7870.2188 | 7870.2188 | 7870.2188 | 7870.2188 | 7870.2188 | 7744.4062 | 7256.25 | 5173.9688 | 2169 | 5635.6875 | 5635.6875 | 5635.6875 | 5635.6875 | 5635.6875 | 5635.6875 | 5635.6875 | 5559 | 5345.4375 | 3762.375 | 1591.3125 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1706.5312 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-01 04:02 | 7968.2812 | 7968.2812 | 7968.2812 | 7968.2812 | 7968.2812 | 7968.2812 | 7968.2812 | 7842.4688 | 7354.3125 | 5247.5625 | 2217.9375 | 7894.6875 | 7894.6875 | 7894.6875 | 7894.6875 | 7894.6875 | 7894.6875 | 7894.6875 | 7768.875 | 7280.7188 | 5198.4375 | 2193.4688 | 5660.1562 | 5660.1562 | 5660.1562 | 5660.1562 | 5660.1562 | 5660.1562 | 5660.1562 | 5583.4688 | 5369.9062 | 3786.8438 | 1615.7812 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1706.5312 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-02 00:22 | 7988.625 | 7988.625 | 7988.625 | 7988.625 | 7988.625 | 7988.625 | 7988.625 | 7862.8125 | 7374.6562 | 5247.5625 | 2217.9375 | 7915.0312 | 7915.0312 | 7915.0312 | 7915.0312 | 7915.0312 | 7915.0312 | 7915.0312 | 7789.2188 | 7301.0625 | 5198.4375 | 2193.4688 | 5680.5 | 5680.5 | 5680.5 | 5680.5 | 5680.5 | 5680.5 | 5680.5 | 5603.8125 | 5390.25 | 3786.8438 | 1615.7812 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1995.6562 | 1706.5312 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-03 01:02 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 7887.4688 | 7399.3125 | 5272.2188 | 2217.9375 | 7939.6875 | 7939.6875 | 7939.6875 | 7939.6875 | 7939.6875 | 7939.6875 | 7939.6875 | 7813.875 | 7325.7188 | 5223.0938 | 2193.4688 | 5705.1562 | 5705.1562 | 5705.1562 | 5705.1562 | 5705.1562 | 5705.1562 | 5705.1562 | 5628.4688 | 5414.9062 | 3811.5 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-04 01:24 | 8037.6562 | 8037.6562 | 8037.6562 | 8037.6562 | 8037.6562 | 8037.6562 | 8037.6562 | 7911.8438 | 7423.6875 | 5272.2188 | 2217.9375 | 7964.0625 | 7964.0625 | 7964.0625 | 7964.0625 | 7964.0625 | 7964.0625 | 7964.0625 | 7838.25 | 7350.0938 | 5223.0938 | 2193.4688 | 5729.5312 | 5729.5312 | 5729.5312 | 5729.5312 | 5729.5312 | 5729.5312 | 5729.5312 | 5652.8438 | 5439.2812 | 3811.5 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-05 02:04 | 8062.3125 | 8062.3125 | 8062.3125 | 8062.3125 | 8062.3125 | 8062.3125 | 8062.3125 | 7936.5 | 7448.3438 | 5272.2188 | 2217.9375 | 7988.7188 | 7988.7188 | 7988.7188 | 7988.7188 | 7988.7188 | 7988.7188 | 7988.7188 | 7862.9062 | 7374.75 | 5223.0938 | 2193.4688 | 5754.1875 | 5754.1875 | 5754.1875 | 5754.1875 | 5754.1875 | 5754.1875 | 5754.1875 | 5677.5 | 5463.9375 | 3811.5 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-06 02:38 | 8086.875 | 8086.875 | 8086.875 | 8086.875 | 8086.875 | 8086.875 | 8086.875 | 7961.0625 | 7472.9062 | 5296.7812 | 2217.9375 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 8013.2812 | 7887.4688 | 7399.3125 | 5247.6562 | 2193.4688 | 5778.75 | 5778.75 | 5778.75 | 5778.75 | 5778.75 | 5778.75 | 5778.75 | 5702.0625 | 5488.5 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-07 03:11 | 8111.4375 | 8111.4375 | 8111.4375 | 8111.4375 | 8111.4375 | 8111.4375 | 8111.4375 | 7985.625 | 7497.4688 | 5296.7812 | 2217.9375 | 8037.8438 | 8037.8438 | 8037.8438 | 8037.8438 | 8037.8438 | 8037.8438 | 8037.8438 | 7912.0312 | 7423.875 | 5247.6562 | 2193.4688 | 5803.3125 | 5803.3125 | 5803.3125 | 5803.3125 | 5803.3125 | 5803.3125 | 5803.3125 | 5726.625 | 5513.0625 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-08 03:34 | 8135.8125 | 8135.8125 | 8135.8125 | 8135.8125 | 8135.8125 | 8135.8125 | 8135.8125 | 8010 | 7521.8438 | 5296.7812 | 2217.9375 | 8062.2188 | 8062.2188 | 8062.2188 | 8062.2188 | 8062.2188 | 8062.2188 | 8062.2188 | 7936.4062 | 7448.25 | 5247.6562 | 2193.4688 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5751 | 5537.4375 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-09 00:06 | 8156.3438 | 8156.3438 | 8156.3438 | 8156.3438 | 8156.3438 | 8156.3438 | 8156.3438 | 8030.5312 | 7542.375 | 5317.3125 | 2238.4688 | 8082.75 | 8082.75 | 8082.75 | 8082.75 | 8082.75 | 8082.75 | 8082.75 | 7956.9375 | 7468.7812 | 5268.1875 | 2214 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5751 | 5537.4375 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-10 00:39 | 8180.9062 | 8180.9062 | 8180.9062 | 8180.9062 | 8180.9062 | 8180.9062 | 8180.9062 | 8055.0938 | 7566.9375 | 5341.875 | 2263.0312 | 8107.3125 | 8107.3125 | 8107.3125 | 8107.3125 | 8107.3125 | 8107.3125 | 8107.3125 | 7981.5 | 7493.3438 | 5292.75 | 2238.5625 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5751 | 5537.4375 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-11 01:13 | 8205.4688 | 8205.4688 | 8205.4688 | 8205.4688 | 8205.4688 | 8205.4688 | 8205.4688 | 8079.6562 | 7591.5 | 5366.4375 | 2263.0312 | 8131.875 | 8131.875 | 8131.875 | 8131.875 | 8131.875 | 8131.875 | 8131.875 | 8006.0625 | 7517.9062 | 5317.3125 | 2238.5625 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5827.6875 | 5751 | 5537.4375 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-12 01:36 | 8229.8438 | 8229.8438 | 8229.8438 | 8229.8438 | 8229.8438 | 8229.8438 | 8229.8438 | 8104.0312 | 7615.875 | 5366.4375 | 2263.0312 | 8156.25 | 8156.25 | 8156.25 | 8156.25 | 8156.25 | 8156.25 | 8156.25 | 8030.4375 | 7542.2812 | 5317.3125 | 2238.5625 | 5852.0625 | 5852.0625 | 5852.0625 | 5852.0625 | 5852.0625 | 5852.0625 | 5852.0625 | 5775.375 | 5561.8125 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-13 02:09 | 8254.4062 | 8254.4062 | 8254.4062 | 8254.4062 | 8254.4062 | 8254.4062 | 8254.4062 | 8128.5938 | 7615.875 | 5366.4375 | 2263.0312 | 8180.8125 | 8180.8125 | 8180.8125 | 8180.8125 | 8180.8125 | 8180.8125 | 8180.8125 | 8055 | 7542.2812 | 5317.3125 | 2238.5625 | 5876.625 | 5876.625 | 5876.625 | 5876.625 | 5876.625 | 5876.625 | 5876.625 | 5799.9375 | 5561.8125 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-14 02:38 | 8278.875 | 8278.875 | 8278.875 | 8278.875 | 8278.875 | 8278.875 | 8278.875 | 8153.0625 | 7640.3438 | 5366.4375 | 2263.0312 | 8205.2812 | 8205.2812 | 8205.2812 | 8205.2812 | 8205.2812 | 8205.2812 | 8205.2812 | 8079.4688 | 7566.75 | 5317.3125 | 2238.5625 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5824.4062 | 5586.2812 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-15 03:06 | 8303.3438 | 8303.3438 | 8303.3438 | 8303.3438 | 8303.3438 | 8303.3438 | 8303.3438 | 8177.5312 | 7664.8125 | 5390.9062 | 2263.0312 | 8229.75 | 8229.75 | 8229.75 | 8229.75 | 8229.75 | 8229.75 | 8229.75 | 8103.9375 | 7591.2188 | 5341.7812 | 2238.5625 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5824.4062 | 5586.2812 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-16 03:28 | 8327.7188 | 8327.7188 | 8327.7188 | 8327.7188 | 8327.7188 | 8327.7188 | 8327.7188 | 8201.9062 | 7689.1875 | 5390.9062 | 2263.0312 | 8254.125 | 8254.125 | 8254.125 | 8254.125 | 8254.125 | 8254.125 | 8254.125 | 8128.3125 | 7615.5938 | 5341.7812 | 2238.5625 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5901.0938 | 5824.4062 | 5586.2812 | 3836.0625 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-17 00:11 | 8348.4375 | 8348.4375 | 8348.4375 | 8348.4375 | 8348.4375 | 8348.4375 | 8348.4375 | 8222.625 | 7709.9062 | 5411.625 | 2263.0312 | 8274.8438 | 8274.8438 | 8274.8438 | 8274.8438 | 8274.8438 | 8274.8438 | 8274.8438 | 8149.0312 | 7636.3125 | 5362.5 | 2238.5625 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5845.125 | 5607 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-18 00:34 | 8372.8125 | 8372.8125 | 8372.8125 | 8372.8125 | 8372.8125 | 8372.8125 | 8372.8125 | 8247 | 7734.2812 | 5436 | 2287.4062 | 8299.2188 | 8299.2188 | 8299.2188 | 8299.2188 | 8299.2188 | 8299.2188 | 8299.2188 | 8173.4062 | 7660.6875 | 5386.875 | 2262.9375 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5845.125 | 5607 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-19 01:02 | 8397.2812 | 8397.2812 | 8397.2812 | 8397.2812 | 8397.2812 | 8397.2812 | 8397.2812 | 8271.4688 | 7758.75 | 5460.4688 | 2287.4062 | 8323.6875 | 8323.6875 | 8323.6875 | 8323.6875 | 8323.6875 | 8323.6875 | 8323.6875 | 8197.875 | 7685.1562 | 5411.3438 | 2262.9375 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5921.8125 | 5845.125 | 5607 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-20 01:30 | 8421.75 | 8421.75 | 8421.75 | 8421.75 | 8421.75 | 8421.75 | 8421.75 | 8295.9375 | 7783.2188 | 5460.4688 | 2287.4062 | 8348.1562 | 8348.1562 | 8348.1562 | 8348.1562 | 8348.1562 | 8348.1562 | 8348.1562 | 8222.3438 | 7709.625 | 5411.3438 | 2262.9375 | 5946.2812 | 5946.2812 | 5946.2812 | 5946.2812 | 5946.2812 | 5946.2812 | 5946.2812 | 5869.5938 | 5631.4688 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-21 01:52 | 8446.125 | 8446.125 | 8446.125 | 8446.125 | 8446.125 | 8446.125 | 8446.125 | 8320.3125 | 7807.5938 | 5460.4688 | 2287.4062 | 8372.5312 | 8372.5312 | 8372.5312 | 8372.5312 | 8372.5312 | 8372.5312 | 8372.5312 | 8246.7188 | 7734 | 5411.3438 | 2262.9375 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5893.9688 | 5655.8438 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-22 02:15 | 8470.5 | 8470.5 | 8470.5 | 8470.5 | 8470.5 | 8470.5 | 8470.5 | 8344.6875 | 7831.9688 | 5484.8438 | 2311.7812 | 8396.9062 | 8396.9062 | 8396.9062 | 8396.9062 | 8396.9062 | 8396.9062 | 8396.9062 | 8271.0938 | 7758.375 | 5435.7188 | 2287.3125 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5893.9688 | 5655.8438 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-23 01:36 | 8493.8438 | 8493.8438 | 8493.8438 | 8493.8438 | 8493.8438 | 8493.8438 | 8493.8438 | 8368.0312 | 7855.3125 | 5484.8438 | 2311.7812 | 8420.25 | 8420.25 | 8420.25 | 8420.25 | 8420.25 | 8420.25 | 8420.25 | 8294.4375 | 7781.7188 | 5435.7188 | 2287.3125 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5893.9688 | 5655.8438 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-24 02:09 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8392.5938 | 7879.875 | 5509.4062 | 2336.3438 | 8444.8125 | 8444.8125 | 8444.8125 | 8444.8125 | 8444.8125 | 8444.8125 | 8444.8125 | 8319 | 7806.2812 | 5460.2812 | 2311.875 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5970.6562 | 5893.9688 | 5655.8438 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-25 02:54 | 8543.1562 | 8543.1562 | 8543.1562 | 8543.1562 | 8543.1562 | 8543.1562 | 8543.1562 | 8417.3438 | 7904.625 | 5509.4062 | 2336.3438 | 8469.5625 | 8469.5625 | 8469.5625 | 8469.5625 | 8469.5625 | 8469.5625 | 8469.5625 | 8343.75 | 7831.0312 | 5460.2812 | 2311.875 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5918.7188 | 5680.5938 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-26 03:22 | 8567.625 | 8567.625 | 8567.625 | 8567.625 | 8567.625 | 8567.625 | 8567.625 | 8441.8125 | 7929.0938 | 5533.875 | 2336.3438 | 8494.0312 | 8494.0312 | 8494.0312 | 8494.0312 | 8494.0312 | 8494.0312 | 8494.0312 | 8368.2188 | 7855.5 | 5484.75 | 2311.875 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5918.7188 | 5680.5938 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-27 03:45 | 8592 | 8592 | 8592 | 8592 | 8592 | 8592 | 8592 | 8466.1875 | 7953.4688 | 5558.25 | 2360.7188 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8518.4062 | 8392.5938 | 7879.875 | 5509.125 | 2336.25 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5995.4062 | 5918.7188 | 5680.5938 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-28 00:06 | 8612.3438 | 8612.3438 | 8612.3438 | 8612.3438 | 8612.3438 | 8612.3438 | 8612.3438 | 8486.5312 | 7973.8125 | 5558.25 | 2360.7188 | 8538.75 | 8538.75 | 8538.75 | 8538.75 | 8538.75 | 8538.75 | 8538.75 | 8412.9375 | 7900.2188 | 5509.125 | 2336.25 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 5939.0625 | 5700.9375 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-02-28 04:13 | 8616.4688 | 8616.4688 | 8616.4688 | 8616.4688 | 8616.4688 | 8616.4688 | 8616.4688 | 8490.6562 | 7977.9375 | 5562.375 | 2364.8438 | 8542.875 | 8542.875 | 8542.875 | 8542.875 | 8542.875 | 8542.875 | 8542.875 | 8417.0625 | 7904.3438 | 5513.25 | 2340.375 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 6015.75 | 5939.0625 | 5700.9375 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-01 00:34 | 8636.8125 | 8636.8125 | 8636.8125 | 8636.8125 | 8636.8125 | 8636.8125 | 8636.8125 | 8511 | 7998.2812 | 5562.375 | 2364.8438 | 8563.2188 | 8563.2188 | 8563.2188 | 8563.2188 | 8563.2188 | 8563.2188 | 8563.2188 | 8437.4062 | 7924.6875 | 5513.25 | 2340.375 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 5959.4062 | 5721.2812 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-01 04:36 | 8640.8438 | 8640.8438 | 8640.8438 | 8640.8438 | 8640.8438 | 8640.8438 | 8640.8438 | 8515.0312 | 8002.3125 | 5566.4062 | 2368.875 | 8567.25 | 8567.25 | 8567.25 | 8567.25 | 8567.25 | 8567.25 | 8567.25 | 8441.4375 | 7928.7188 | 5517.2812 | 2344.4062 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 6036.0938 | 5959.4062 | 5721.2812 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-02 01:08 | 8661.375 | 8661.375 | 8661.375 | 8661.375 | 8661.375 | 8661.375 | 8661.375 | 8535.5625 | 8022.8438 | 5566.4062 | 2368.875 | 8587.7812 | 8587.7812 | 8587.7812 | 8587.7812 | 8587.7812 | 8587.7812 | 8587.7812 | 8461.9688 | 7949.25 | 5517.2812 | 2344.4062 | 6056.625 | 6056.625 | 6056.625 | 6056.625 | 6056.625 | 6056.625 | 6056.625 | 5979.9375 | 5741.8125 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-03 01:52 | 8686.125 | 8686.125 | 8686.125 | 8686.125 | 8686.125 | 8686.125 | 8686.125 | 8560.3125 | 8047.5938 | 5566.4062 | 2368.875 | 8612.5312 | 8612.5312 | 8612.5312 | 8612.5312 | 8612.5312 | 8612.5312 | 8612.5312 | 8486.7188 | 7974 | 5517.2812 | 2344.4062 | 6081.375 | 6081.375 | 6081.375 | 6081.375 | 6081.375 | 6081.375 | 6081.375 | 6004.6875 | 5766.5625 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-04 02:21 | 8710.5938 | 8710.5938 | 8710.5938 | 8710.5938 | 8710.5938 | 8710.5938 | 8710.5938 | 8584.7812 | 8072.0625 | 5566.4062 | 2368.875 | 8637 | 8637 | 8637 | 8637 | 8637 | 8637 | 8637 | 8511.1875 | 7998.4688 | 5517.2812 | 2344.4062 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6029.1562 | 5791.0312 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-05 02:49 | 8735.0625 | 8735.0625 | 8735.0625 | 8735.0625 | 8735.0625 | 8735.0625 | 8735.0625 | 8609.25 | 8096.5312 | 5590.875 | 2368.875 | 8661.4688 | 8661.4688 | 8661.4688 | 8661.4688 | 8661.4688 | 8661.4688 | 8661.4688 | 8535.6562 | 8022.9375 | 5541.75 | 2344.4062 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6105.8438 | 6029.1562 | 5791.0312 | 3856.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-06 03:22 | 8759.625 | 8759.625 | 8759.625 | 8759.625 | 8759.625 | 8759.625 | 8759.625 | 8633.8125 | 8121.0938 | 5615.4375 | 2368.875 | 8686.0312 | 8686.0312 | 8686.0312 | 8686.0312 | 8686.0312 | 8686.0312 | 8686.0312 | 8560.2188 | 8047.5 | 5566.3125 | 2344.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6053.7188 | 5815.5938 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-07 03:45 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8658.1875 | 8145.4688 | 5615.4375 | 2368.875 | 8710.4062 | 8710.4062 | 8710.4062 | 8710.4062 | 8710.4062 | 8710.4062 | 8710.4062 | 8584.5938 | 8071.875 | 5566.3125 | 2344.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6053.7188 | 5815.5938 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-08 00:06 | 8804.3438 | 8804.3438 | 8804.3438 | 8804.3438 | 8804.3438 | 8804.3438 | 8804.3438 | 8678.5312 | 8165.8125 | 5635.7812 | 2389.2188 | 8730.75 | 8730.75 | 8730.75 | 8730.75 | 8730.75 | 8730.75 | 8730.75 | 8604.9375 | 8092.2188 | 5586.6562 | 2364.75 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6053.7188 | 5815.5938 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-09 00:39 | 8828.9062 | 8828.9062 | 8828.9062 | 8828.9062 | 8828.9062 | 8828.9062 | 8828.9062 | 8703.0938 | 8190.375 | 5660.3438 | 2389.2188 | 8755.3125 | 8755.3125 | 8755.3125 | 8755.3125 | 8755.3125 | 8755.3125 | 8755.3125 | 8629.5 | 8116.7812 | 5611.2188 | 2364.75 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6053.7188 | 5815.5938 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-10 01:02 | 8853.2812 | 8853.2812 | 8853.2812 | 8853.2812 | 8853.2812 | 8853.2812 | 8853.2812 | 8727.4688 | 8214.75 | 5684.7188 | 2389.2188 | 8779.6875 | 8779.6875 | 8779.6875 | 8779.6875 | 8779.6875 | 8779.6875 | 8779.6875 | 8653.875 | 8141.1562 | 5635.5938 | 2364.75 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6130.4062 | 6053.7188 | 5815.5938 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-11 01:30 | 8877.75 | 8877.75 | 8877.75 | 8877.75 | 8877.75 | 8877.75 | 8877.75 | 8751.9375 | 8239.2188 | 5684.7188 | 2389.2188 | 8804.1562 | 8804.1562 | 8804.1562 | 8804.1562 | 8804.1562 | 8804.1562 | 8804.1562 | 8678.3438 | 8165.625 | 5635.5938 | 2364.75 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6078.1875 | 5840.0625 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-12 02:09 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8776.5938 | 8263.875 | 5709.375 | 2389.2188 | 8828.8125 | 8828.8125 | 8828.8125 | 8828.8125 | 8828.8125 | 8828.8125 | 8828.8125 | 8703 | 8190.2812 | 5660.25 | 2364.75 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6154.875 | 6078.1875 | 5840.0625 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-13 02:43 | 8926.9688 | 8926.9688 | 8926.9688 | 8926.9688 | 8926.9688 | 8926.9688 | 8926.9688 | 8801.1562 | 8288.4375 | 5709.375 | 2389.2188 | 8853.375 | 8853.375 | 8853.375 | 8853.375 | 8853.375 | 8853.375 | 8853.375 | 8727.5625 | 8214.8438 | 5660.25 | 2364.75 | 6179.4375 | 6179.4375 | 6179.4375 | 6179.4375 | 6179.4375 | 6179.4375 | 6179.4375 | 6102.75 | 5864.625 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-14 03:17 | 8951.5312 | 8951.5312 | 8951.5312 | 8951.5312 | 8951.5312 | 8951.5312 | 8951.5312 | 8825.7188 | 8313 | 5709.375 | 2389.2188 | 8877.9375 | 8877.9375 | 8877.9375 | 8877.9375 | 8877.9375 | 8877.9375 | 8877.9375 | 8752.125 | 8239.4062 | 5660.25 | 2364.75 | 6204 | 6204 | 6204 | 6204 | 6204 | 6204 | 6204 | 6127.3125 | 5889.1875 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-15 03:45 | 8976 | 8976 | 8976 | 8976 | 8976 | 8976 | 8976 | 8850.1875 | 8337.4688 | 5709.375 | 2389.2188 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8902.4062 | 8776.5938 | 8263.875 | 5660.25 | 2364.75 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6151.7812 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-16 00:17 | 8996.5312 | 8996.5312 | 8996.5312 | 8996.5312 | 8996.5312 | 8996.5312 | 8996.5312 | 8870.7188 | 8358 | 5729.9062 | 2409.75 | 8922.9375 | 8922.9375 | 8922.9375 | 8922.9375 | 8922.9375 | 8922.9375 | 8922.9375 | 8797.125 | 8284.4062 | 5680.7812 | 2385.2812 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6151.7812 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-17 03:56 | 9024.1875 | 9024.1875 | 9024.1875 | 9024.1875 | 9024.1875 | 9024.1875 | 9024.1875 | 8898.375 | 8385.6562 | 5757.5625 | 2409.75 | 8950.5938 | 8950.5938 | 8950.5938 | 8950.5938 | 8950.5938 | 8950.5938 | 8950.5938 | 8824.7812 | 8312.0625 | 5708.4375 | 2385.2812 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6228.4688 | 6151.7812 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-18 00:11 | 9044.4375 | 9044.4375 | 9044.4375 | 9044.4375 | 9044.4375 | 9044.4375 | 9044.4375 | 8918.625 | 8385.6562 | 5757.5625 | 2409.75 | 8970.8438 | 8970.8438 | 8970.8438 | 8970.8438 | 8970.8438 | 8970.8438 | 8970.8438 | 8845.0312 | 8312.0625 | 5708.4375 | 2385.2812 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6172.0312 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-19 00:45 | 9069 | 9069 | 9069 | 9069 | 9069 | 9069 | 9069 | 8943.1875 | 8410.2188 | 5782.125 | 2409.75 | 8995.4062 | 8995.4062 | 8995.4062 | 8995.4062 | 8995.4062 | 8995.4062 | 8995.4062 | 8869.5938 | 8336.625 | 5733 | 2385.2812 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6172.0312 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-20 01:24 | 9093.6562 | 9093.6562 | 9093.6562 | 9093.6562 | 9093.6562 | 9093.6562 | 9093.6562 | 8967.8438 | 8434.875 | 5806.7812 | 2434.4062 | 9020.0625 | 9020.0625 | 9020.0625 | 9020.0625 | 9020.0625 | 9020.0625 | 9020.0625 | 8894.25 | 8361.2812 | 5757.6562 | 2409.9375 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6172.0312 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-21 01:52 | 9118.125 | 9118.125 | 9118.125 | 9118.125 | 9118.125 | 9118.125 | 9118.125 | 8992.3125 | 8459.3438 | 5831.25 | 2458.875 | 9044.5312 | 9044.5312 | 9044.5312 | 9044.5312 | 9044.5312 | 9044.5312 | 9044.5312 | 8918.7188 | 8385.75 | 5782.125 | 2434.4062 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6248.7188 | 6172.0312 | 5913.6562 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-22 02:26 | 9142.6875 | 9142.6875 | 9142.6875 | 9142.6875 | 9142.6875 | 9142.6875 | 9142.6875 | 9016.875 | 8483.9062 | 5831.25 | 2458.875 | 9069.0938 | 9069.0938 | 9069.0938 | 9069.0938 | 9069.0938 | 9069.0938 | 9069.0938 | 8943.2812 | 8410.3125 | 5782.125 | 2434.4062 | 6273.2812 | 6273.2812 | 6273.2812 | 6273.2812 | 6273.2812 | 6273.2812 | 6273.2812 | 6196.5938 | 5938.2188 | 3881.3438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-23 03:11 | 9167.4375 | 9167.4375 | 9167.4375 | 9167.4375 | 9167.4375 | 9167.4375 | 9167.4375 | 9041.625 | 8508.6562 | 5856 | 2458.875 | 9093.8438 | 9093.8438 | 9093.8438 | 9093.8438 | 9093.8438 | 9093.8438 | 9093.8438 | 8968.0312 | 8435.0625 | 5806.875 | 2434.4062 | 6298.0312 | 6298.0312 | 6298.0312 | 6298.0312 | 6298.0312 | 6298.0312 | 6298.0312 | 6221.3438 | 5962.9688 | 3906.0938 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-24 03:56 | 9192.1875 | 9192.1875 | 9192.1875 | 9192.1875 | 9192.1875 | 9192.1875 | 9192.1875 | 9066.375 | 8533.4062 | 5880.75 | 2458.875 | 9118.5938 | 9118.5938 | 9118.5938 | 9118.5938 | 9118.5938 | 9118.5938 | 9118.5938 | 8992.7812 | 8459.8125 | 5831.625 | 2434.4062 | 6322.7812 | 6322.7812 | 6322.7812 | 6322.7812 | 6322.7812 | 6322.7812 | 6322.7812 | 6246.0938 | 5987.7188 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-25 03:22 | 9215.625 | 9215.625 | 9215.625 | 9215.625 | 9215.625 | 9215.625 | 9215.625 | 9089.8125 | 8556.8438 | 5880.75 | 2458.875 | 9142.0312 | 9142.0312 | 9142.0312 | 9142.0312 | 9142.0312 | 9142.0312 | 9142.0312 | 9016.2188 | 8483.25 | 5831.625 | 2434.4062 | 6346.2188 | 6346.2188 | 6346.2188 | 6346.2188 | 6346.2188 | 6346.2188 | 6346.2188 | 6269.5312 | 6011.1562 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-26 03:56 | 9240.1875 | 9240.1875 | 9240.1875 | 9240.1875 | 9240.1875 | 9240.1875 | 9240.1875 | 9114.375 | 8556.8438 | 5880.75 | 2458.875 | 9166.5938 | 9166.5938 | 9166.5938 | 9166.5938 | 9166.5938 | 9166.5938 | 9166.5938 | 9040.7812 | 8483.25 | 5831.625 | 2434.4062 | 6370.7812 | 6370.7812 | 6370.7812 | 6370.7812 | 6370.7812 | 6370.7812 | 6370.7812 | 6294.0938 | 6011.1562 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-27 00:22 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9134.8125 | 8577.2812 | 5880.75 | 2458.875 | 9187.0312 | 9187.0312 | 9187.0312 | 9187.0312 | 9187.0312 | 9187.0312 | 9187.0312 | 9061.2188 | 8503.6875 | 5831.625 | 2434.4062 | 6391.2188 | 6391.2188 | 6391.2188 | 6391.2188 | 6391.2188 | 6391.2188 | 6391.2188 | 6314.5312 | 6031.5938 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-28 00:51 | 9285.0938 | 9285.0938 | 9285.0938 | 9285.0938 | 9285.0938 | 9285.0938 | 9285.0938 | 9159.2812 | 8601.75 | 5880.75 | 2458.875 | 9211.5 | 9211.5 | 9211.5 | 9211.5 | 9211.5 | 9211.5 | 9211.5 | 9085.6875 | 8528.1562 | 5831.625 | 2434.4062 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6339 | 6056.0625 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-29 01:24 | 9309.6562 | 9309.6562 | 9309.6562 | 9309.6562 | 9309.6562 | 9309.6562 | 9309.6562 | 9183.8438 | 8626.3125 | 5905.3125 | 2483.4375 | 9236.0625 | 9236.0625 | 9236.0625 | 9236.0625 | 9236.0625 | 9236.0625 | 9236.0625 | 9110.25 | 8552.7188 | 5856.1875 | 2458.9688 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6415.6875 | 6339 | 6056.0625 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-30 01:58 | 9334.2188 | 9334.2188 | 9334.2188 | 9334.2188 | 9334.2188 | 9334.2188 | 9334.2188 | 9208.4062 | 8650.875 | 5905.3125 | 2483.4375 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9260.625 | 9134.8125 | 8577.2812 | 5856.1875 | 2458.9688 | 6440.25 | 6440.25 | 6440.25 | 6440.25 | 6440.25 | 6440.25 | 6440.25 | 6363.5625 | 6080.625 | 3930.8438 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-03-31 02:54 | 9359.1562 | 9359.1562 | 9359.1562 | 9359.1562 | 9359.1562 | 9359.1562 | 9359.1562 | 9233.3438 | 8675.8125 | 5930.25 | 2483.4375 | 9285.5625 | 9285.5625 | 9285.5625 | 9285.5625 | 9285.5625 | 9285.5625 | 9285.5625 | 9159.75 | 8602.2188 | 5881.125 | 2458.9688 | 6465.1875 | 6465.1875 | 6465.1875 | 6465.1875 | 6465.1875 | 6465.1875 | 6465.1875 | 6388.5 | 6105.5625 | 3955.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-01 03:28 | 9383.7188 | 9383.7188 | 9383.7188 | 9383.7188 | 9383.7188 | 9383.7188 | 9383.7188 | 9257.9062 | 8700.375 | 5930.25 | 2483.4375 | 9310.125 | 9310.125 | 9310.125 | 9310.125 | 9310.125 | 9310.125 | 9310.125 | 9184.3125 | 8626.7812 | 5881.125 | 2458.9688 | 6489.75 | 6489.75 | 6489.75 | 6489.75 | 6489.75 | 6489.75 | 6489.75 | 6413.0625 | 6130.125 | 3955.7812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-02 | 9404.25 | 9404.25 | 9404.25 | 9404.25 | 9404.25 | 9404.25 | 9404.25 | 9278.4375 | 8720.9062 | 5950.7812 | 2483.4375 | 9330.6562 | 9330.6562 | 9330.6562 | 9330.6562 | 9330.6562 | 9330.6562 | 9330.6562 | 9204.8438 | 8647.3125 | 5901.6562 | 2458.9688 | 6510.2812 | 6510.2812 | 6510.2812 | 6510.2812 | 6510.2812 | 6510.2812 | 6510.2812 | 6433.5938 | 6150.6562 | 3976.3125 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-03 00:39 | 9428.9062 | 9428.9062 | 9428.9062 | 9428.9062 | 9428.9062 | 9428.9062 | 9428.9062 | 9303.0938 | 8745.5625 | 5975.4375 | 2483.4375 | 9355.3125 | 9355.3125 | 9355.3125 | 9355.3125 | 9355.3125 | 9355.3125 | 9355.3125 | 9229.5 | 8671.9688 | 5926.3125 | 2458.9688 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6458.25 | 6175.3125 | 4000.9688 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-04 01:08 | 9453.375 | 9453.375 | 9453.375 | 9453.375 | 9453.375 | 9453.375 | 9453.375 | 9327.5625 | 8770.0312 | 5999.9062 | 2483.4375 | 9379.7812 | 9379.7812 | 9379.7812 | 9379.7812 | 9379.7812 | 9379.7812 | 9379.7812 | 9253.9688 | 8696.4375 | 5950.7812 | 2458.9688 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6458.25 | 6175.3125 | 4000.9688 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-05 02:32 | 9478.7812 | 9478.7812 | 9478.7812 | 9478.7812 | 9478.7812 | 9478.7812 | 9478.7812 | 9352.9688 | 8795.4375 | 6025.3125 | 2483.4375 | 9405.1875 | 9405.1875 | 9405.1875 | 9405.1875 | 9405.1875 | 9405.1875 | 9405.1875 | 9279.375 | 8721.8438 | 5976.1875 | 2458.9688 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6458.25 | 6175.3125 | 4000.9688 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-06 03:17 | 9503.5312 | 9503.5312 | 9503.5312 | 9503.5312 | 9503.5312 | 9503.5312 | 9503.5312 | 9377.7188 | 8820.1875 | 6050.0625 | 2508.1875 | 9429.9375 | 9429.9375 | 9429.9375 | 9429.9375 | 9429.9375 | 9429.9375 | 9429.9375 | 9304.125 | 8746.5938 | 6000.9375 | 2483.7188 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6534.9375 | 6458.25 | 6175.3125 | 4000.9688 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-07 03:51 | 9528.0938 | 9528.0938 | 9528.0938 | 9528.0938 | 9528.0938 | 9528.0938 | 9528.0938 | 9402.2812 | 8844.75 | 6074.625 | 2508.1875 | 9454.5 | 9454.5 | 9454.5 | 9454.5 | 9454.5 | 9454.5 | 9454.5 | 9328.6875 | 8771.1562 | 6025.5 | 2483.7188 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6482.8125 | 6199.875 | 4025.5312 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-08 00:17 | 9548.5312 | 9548.5312 | 9548.5312 | 9548.5312 | 9548.5312 | 9548.5312 | 9548.5312 | 9422.7188 | 8865.1875 | 6095.0625 | 2508.1875 | 9474.9375 | 9474.9375 | 9474.9375 | 9474.9375 | 9474.9375 | 9474.9375 | 9474.9375 | 9349.125 | 8791.5938 | 6045.9375 | 2483.7188 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6482.8125 | 6199.875 | 4025.5312 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-09 01:13 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9447.6562 | 8890.125 | 6095.0625 | 2508.1875 | 9499.875 | 9499.875 | 9499.875 | 9499.875 | 9499.875 | 9499.875 | 9499.875 | 9374.0625 | 8816.5312 | 6045.9375 | 2483.7188 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6559.5 | 6482.8125 | 6199.875 | 4025.5312 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-10 01:58 | 9598.2188 | 9598.2188 | 9598.2188 | 9598.2188 | 9598.2188 | 9598.2188 | 9598.2188 | 9472.4062 | 8914.875 | 6119.8125 | 2508.1875 | 9524.625 | 9524.625 | 9524.625 | 9524.625 | 9524.625 | 9524.625 | 9524.625 | 9398.8125 | 8841.2812 | 6070.6875 | 2483.7188 | 6584.25 | 6584.25 | 6584.25 | 6584.25 | 6584.25 | 6584.25 | 6584.25 | 6507.5625 | 6224.625 | 4050.2812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-11 02:26 | 9622.6875 | 9622.6875 | 9622.6875 | 9622.6875 | 9622.6875 | 9622.6875 | 9622.6875 | 9496.875 | 8939.3438 | 6119.8125 | 2508.1875 | 9549.0938 | 9549.0938 | 9549.0938 | 9549.0938 | 9549.0938 | 9549.0938 | 9549.0938 | 9423.2812 | 8865.75 | 6070.6875 | 2483.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6532.0312 | 6249.0938 | 4050.2812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-12 02:49 | 9647.0625 | 9647.0625 | 9647.0625 | 9647.0625 | 9647.0625 | 9647.0625 | 9647.0625 | 9521.25 | 8963.7188 | 6144.1875 | 2532.5625 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9573.4688 | 9447.6562 | 8890.125 | 6095.0625 | 2508.0938 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6532.0312 | 6249.0938 | 4050.2812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-13 03:11 | 9671.4375 | 9671.4375 | 9671.4375 | 9671.4375 | 9671.4375 | 9671.4375 | 9671.4375 | 9545.625 | 8988.0938 | 6168.5625 | 2532.5625 | 9597.8438 | 9597.8438 | 9597.8438 | 9597.8438 | 9597.8438 | 9597.8438 | 9597.8438 | 9472.0312 | 8914.5 | 6119.4375 | 2508.0938 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6608.7188 | 6532.0312 | 6249.0938 | 4050.2812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-14 03:34 | 9695.8125 | 9695.8125 | 9695.8125 | 9695.8125 | 9695.8125 | 9695.8125 | 9695.8125 | 9570 | 9012.4688 | 6168.5625 | 2532.5625 | 9622.2188 | 9622.2188 | 9622.2188 | 9622.2188 | 9622.2188 | 9622.2188 | 9622.2188 | 9496.4062 | 8938.875 | 6119.4375 | 2508.0938 | 6633.0938 | 6633.0938 | 6633.0938 | 6633.0938 | 6633.0938 | 6633.0938 | 6633.0938 | 6556.4062 | 6273.4688 | 4050.2812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-15 04:02 | 9720.2812 | 9720.2812 | 9720.2812 | 9720.2812 | 9720.2812 | 9720.2812 | 9720.2812 | 9594.4688 | 9036.9375 | 6168.5625 | 2532.5625 | 9646.6875 | 9646.6875 | 9646.6875 | 9646.6875 | 9646.6875 | 9646.6875 | 9646.6875 | 9520.875 | 8963.3438 | 6119.4375 | 2508.0938 | 6657.5625 | 6657.5625 | 6657.5625 | 6657.5625 | 6657.5625 | 6657.5625 | 6657.5625 | 6580.875 | 6297.9375 | 4050.2812 | 1615.7812 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-16 01:30 | 9741.75 | 9741.75 | 9741.75 | 9741.75 | 9741.75 | 9741.75 | 9741.75 | 9615.9375 | 9058.4062 | 6190.0312 | 2554.0312 | 9668.1562 | 9668.1562 | 9668.1562 | 9668.1562 | 9668.1562 | 9668.1562 | 9668.1562 | 9542.3438 | 8984.8125 | 6140.9062 | 2529.5625 | 6679.0312 | 6679.0312 | 6679.0312 | 6679.0312 | 6679.0312 | 6679.0312 | 6679.0312 | 6602.3438 | 6319.4062 | 4071.75 | 1637.25 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 2020.3125 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-17 02:15 | 9766.5 | 9766.5 | 9766.5 | 9766.5 | 9766.5 | 9766.5 | 9766.5 | 9640.6875 | 9083.1562 | 6190.0312 | 2554.0312 | 9692.9062 | 9692.9062 | 9692.9062 | 9692.9062 | 9692.9062 | 9692.9062 | 9692.9062 | 9567.0938 | 9009.5625 | 6140.9062 | 2529.5625 | 6703.7812 | 6703.7812 | 6703.7812 | 6703.7812 | 6703.7812 | 6703.7812 | 6703.7812 | 6627.0938 | 6344.1562 | 4071.75 | 1637.25 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-18 02:38 | 9790.875 | 9790.875 | 9790.875 | 9790.875 | 9790.875 | 9790.875 | 9790.875 | 9665.0625 | 9083.1562 | 6190.0312 | 2554.0312 | 9717.2812 | 9717.2812 | 9717.2812 | 9717.2812 | 9717.2812 | 9717.2812 | 9717.2812 | 9591.4688 | 9009.5625 | 6140.9062 | 2529.5625 | 6728.1562 | 6728.1562 | 6728.1562 | 6728.1562 | 6728.1562 | 6728.1562 | 6728.1562 | 6651.4688 | 6344.1562 | 4071.75 | 1637.25 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-19 02:54 | 9815.1562 | 9815.1562 | 9815.1562 | 9815.1562 | 9815.1562 | 9815.1562 | 9815.1562 | 9689.3438 | 9107.4375 | 6190.0312 | 2554.0312 | 9741.5625 | 9741.5625 | 9741.5625 | 9741.5625 | 9741.5625 | 9741.5625 | 9741.5625 | 9615.75 | 9033.8438 | 6140.9062 | 2529.5625 | 6752.4375 | 6752.4375 | 6752.4375 | 6752.4375 | 6752.4375 | 6752.4375 | 6752.4375 | 6675.75 | 6368.4375 | 4071.75 | 1637.25 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-20 03:28 | 9839.7188 | 9839.7188 | 9839.7188 | 9839.7188 | 9839.7188 | 9839.7188 | 9839.7188 | 9713.9062 | 9132 | 6214.5938 | 2578.5938 | 9766.125 | 9766.125 | 9766.125 | 9766.125 | 9766.125 | 9766.125 | 9766.125 | 9640.3125 | 9058.4062 | 6165.4688 | 2554.125 | 6777 | 6777 | 6777 | 6777 | 6777 | 6777 | 6777 | 6700.3125 | 6393 | 4096.3125 | 1661.8125 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-21 04:02 | 9864.2812 | 9864.2812 | 9864.2812 | 9864.2812 | 9864.2812 | 9864.2812 | 9864.2812 | 9738.4688 | 9156.5625 | 6214.5938 | 2578.5938 | 9790.6875 | 9790.6875 | 9790.6875 | 9790.6875 | 9790.6875 | 9790.6875 | 9790.6875 | 9664.875 | 9082.9688 | 6165.4688 | 2554.125 | 6801.5625 | 6801.5625 | 6801.5625 | 6801.5625 | 6801.5625 | 6801.5625 | 6801.5625 | 6724.875 | 6417.5625 | 4096.3125 | 1661.8125 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 2045.0625 | 1731.1875 | 718.0312 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-22 00:39 | 9884.9062 | 9884.9062 | 9884.9062 | 9884.9062 | 9884.9062 | 9884.9062 | 9884.9062 | 9759.0938 | 9177.1875 | 6235.2188 | 2599.2188 | 9811.3125 | 9811.3125 | 9811.3125 | 9811.3125 | 9811.3125 | 9811.3125 | 9811.3125 | 9685.5 | 9103.5938 | 6186.0938 | 2574.75 | 6822.1875 | 6822.1875 | 6822.1875 | 6822.1875 | 6822.1875 | 6822.1875 | 6822.1875 | 6745.5 | 6438.1875 | 4116.9375 | 1682.4375 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 1751.8125 | 738.6562 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-23 01:41 | 9909.9375 | 9909.9375 | 9909.9375 | 9909.9375 | 9909.9375 | 9909.9375 | 9909.9375 | 9784.125 | 9202.2188 | 6260.25 | 2599.2188 | 9836.3438 | 9836.3438 | 9836.3438 | 9836.3438 | 9836.3438 | 9836.3438 | 9836.3438 | 9710.5312 | 9128.625 | 6211.125 | 2574.75 | 6847.2188 | 6847.2188 | 6847.2188 | 6847.2188 | 6847.2188 | 6847.2188 | 6847.2188 | 6770.5312 | 6463.2188 | 4141.9688 | 1682.4375 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 1751.8125 | 738.6562 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-24 02:09 | 9934.4062 | 9934.4062 | 9934.4062 | 9934.4062 | 9934.4062 | 9934.4062 | 9934.4062 | 9808.5938 | 9226.6875 | 6284.7188 | 2599.2188 | 9860.8125 | 9860.8125 | 9860.8125 | 9860.8125 | 9860.8125 | 9860.8125 | 9860.8125 | 9735 | 9153.0938 | 6235.5938 | 2574.75 | 6871.6875 | 6871.6875 | 6871.6875 | 6871.6875 | 6871.6875 | 6871.6875 | 6871.6875 | 6795 | 6487.6875 | 4166.4375 | 1682.4375 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 2065.6875 | 1751.8125 | 738.6562 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-25 02:26 | 9958.6875 | 9958.6875 | 9958.6875 | 9958.6875 | 9958.6875 | 9958.6875 | 9958.6875 | 9832.875 | 9250.9688 | 6284.7188 | 2599.2188 | 9885.0938 | 9885.0938 | 9885.0938 | 9885.0938 | 9885.0938 | 9885.0938 | 9885.0938 | 9759.2812 | 9177.375 | 6235.5938 | 2574.75 | 6895.9688 | 6895.9688 | 6895.9688 | 6895.9688 | 6895.9688 | 6895.9688 | 6895.9688 | 6819.2812 | 6511.9688 | 4166.4375 | 1682.4375 | 2089.9688 | 2089.9688 | 2089.9688 | 2089.9688 | 2089.9688 | 2089.9688 | 2089.9688 | 2089.9688 | 2089.9688 | 1751.8125 | 738.6562 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-26 02:49 | 9983.0625 | 9983.0625 | 9983.0625 | 9983.0625 | 9983.0625 | 9983.0625 | 9983.0625 | 9857.25 | 9275.3438 | 6309.0938 | 2599.2188 | 9909.4688 | 9909.4688 | 9909.4688 | 9909.4688 | 9909.4688 | 9909.4688 | 9909.4688 | 9783.6562 | 9201.75 | 6259.9688 | 2574.75 | 6920.3438 | 6920.3438 | 6920.3438 | 6920.3438 | 6920.3438 | 6920.3438 | 6920.3438 | 6843.6562 | 6536.3438 | 4190.8125 | 1682.4375 | 2114.3438 | 2114.3438 | 2114.3438 | 2114.3438 | 2114.3438 | 2114.3438 | 2114.3438 | 2114.3438 | 2114.3438 | 1776.1875 | 738.6562 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-27 02:26 | 10006.6875 | 10006.6875 | 10006.6875 | 10006.6875 | 10006.6875 | 10006.6875 | 10006.6875 | 9880.875 | 9298.9688 | 6332.7188 | 2622.8438 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9807.2812 | 9225.375 | 6283.5938 | 2598.375 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6867.2812 | 6559.9688 | 4214.4375 | 1706.0625 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-28 03:00 | 10031.25 | 10031.25 | 10031.25 | 10031.25 | 10031.25 | 10031.25 | 10031.25 | 9905.4375 | 9323.5312 | 6357.2812 | 2647.4062 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9933.0938 | 9807.2812 | 9225.375 | 6283.5938 | 2598.375 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6867.2812 | 6559.9688 | 4214.4375 | 1706.0625 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-29 03:28 | 10055.7188 | 10055.7188 | 10055.7188 | 10055.7188 | 10055.7188 | 10055.7188 | 10055.7188 | 9929.9062 | 9348 | 6381.75 | 2647.4062 | 9957.5625 | 9957.5625 | 9957.5625 | 9957.5625 | 9957.5625 | 9957.5625 | 9957.5625 | 9831.75 | 9249.8438 | 6308.0625 | 2598.375 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6943.9688 | 6867.2812 | 6559.9688 | 4214.4375 | 1706.0625 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-04-30 03:45 | 10080 | 10080 | 10080 | 10080 | 10080 | 10080 | 10080 | 9954.1875 | 9372.2812 | 6406.0312 | 2647.4062 | 9981.8438 | 9981.8438 | 9981.8438 | 9981.8438 | 9981.8438 | 9981.8438 | 9981.8438 | 9856.0312 | 9274.125 | 6332.3438 | 2598.375 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6891.5625 | 6584.25 | 4238.7188 | 1706.0625 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-01 00:11 | 10100.4375 | 10100.4375 | 10100.4375 | 10100.4375 | 10100.4375 | 10100.4375 | 10100.4375 | 9974.625 | 9392.7188 | 6426.4688 | 2667.8438 | 10002.2812 | 10002.2812 | 10002.2812 | 10002.2812 | 10002.2812 | 10002.2812 | 10002.2812 | 9876.4688 | 9294.5625 | 6352.7812 | 2618.8125 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6968.25 | 6891.5625 | 6584.25 | 4238.7188 | 1706.0625 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-02 00:28 | 10124.7188 | 10124.7188 | 10124.7188 | 10124.7188 | 10124.7188 | 10124.7188 | 10124.7188 | 9998.9062 | 9417 | 6450.75 | 2667.8438 | 10026.5625 | 10026.5625 | 10026.5625 | 10026.5625 | 10026.5625 | 10026.5625 | 10026.5625 | 9900.75 | 9318.8438 | 6377.0625 | 2618.8125 | 6992.5312 | 6992.5312 | 6992.5312 | 6992.5312 | 6992.5312 | 6992.5312 | 6992.5312 | 6915.8438 | 6608.5312 | 4263 | 1706.0625 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-03 00:51 | 10149.0938 | 10149.0938 | 10149.0938 | 10149.0938 | 10149.0938 | 10149.0938 | 10149.0938 | 10023.2812 | 9441.375 | 6475.125 | 2692.2188 | 10050.9375 | 10050.9375 | 10050.9375 | 10050.9375 | 10050.9375 | 10050.9375 | 10050.9375 | 9925.125 | 9343.2188 | 6401.4375 | 2643.1875 | 7016.9062 | 7016.9062 | 7016.9062 | 7016.9062 | 7016.9062 | 7016.9062 | 7016.9062 | 6940.2188 | 6632.9062 | 4287.375 | 1730.4375 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-04 01:24 | 10173.6562 | 10173.6562 | 10173.6562 | 10173.6562 | 10173.6562 | 10173.6562 | 10173.6562 | 10047.8438 | 9465.9375 | 6499.6875 | 2716.7812 | 10075.5 | 10075.5 | 10075.5 | 10075.5 | 10075.5 | 10075.5 | 10075.5 | 9949.6875 | 9367.7812 | 6426 | 2667.75 | 7041.4688 | 7041.4688 | 7041.4688 | 7041.4688 | 7041.4688 | 7041.4688 | 7041.4688 | 6964.7812 | 6657.4688 | 4311.9375 | 1755 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-05 01:52 | 10198.125 | 10198.125 | 10198.125 | 10198.125 | 10198.125 | 10198.125 | 10198.125 | 10072.3125 | 9490.4062 | 6524.1562 | 2716.7812 | 10099.9688 | 10099.9688 | 10099.9688 | 10099.9688 | 10099.9688 | 10099.9688 | 10099.9688 | 9974.1562 | 9392.25 | 6450.4688 | 2667.75 | 7065.9375 | 7065.9375 | 7065.9375 | 7065.9375 | 7065.9375 | 7065.9375 | 7065.9375 | 6989.25 | 6681.9375 | 4336.4062 | 1755 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-06 02:15 | 10222.5 | 10222.5 | 10222.5 | 10222.5 | 10222.5 | 10222.5 | 10222.5 | 10096.6875 | 9514.7812 | 6548.5312 | 2716.7812 | 10124.3438 | 10124.3438 | 10124.3438 | 10124.3438 | 10124.3438 | 10124.3438 | 10124.3438 | 9998.5312 | 9416.625 | 6474.8438 | 2667.75 | 7090.3125 | 7090.3125 | 7090.3125 | 7090.3125 | 7090.3125 | 7090.3125 | 7090.3125 | 7013.625 | 6706.3125 | 4360.7812 | 1755 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312
2006-05-07 02:38 | 10246.875 | 10246.875 | 10246.875 | 10246.875 | 10246.875 | 10246.875 | 10246.875 | 10121.0625 | 9539.1562 | 6572.9062 | 2741.1562 | 10148.7188 | 10148.7188 | 10148.7188 | 10148.7188 | 10148.7188 | 10148.7188 | 10148.7188 | 10022.9062 | 9441 | 6499.2188 | 2692.125 | 7114.6875 | 7114.6875 | 7114.6875 | 7114.6875 | 7114.6875 | 7114.6875 | 7114.6875 | 7038 | 6730.6875 | 4385.1562 | 1779.375 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 2137.9688 | 1799.8125 | 762.2812 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 644.3438 | 285.0938 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 158.625 | 45.0938 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 43.875 | 20.5312

## LAMP AGING FACTOR
Train | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Reactor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Bank | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Train 1, Bank 1 | Train 1, Bank 2 | Train 1, Bank 3 | Train 1, Bank 4 | Train 1, Bank 5 | Train 1, Bank 6 | Train 1, Bank 7 | Train 1, Bank 8 | Train 1, Bank 9 | Train 1, Bank 10 | Train 1, Bank 11 | Train 2, Bank 1 | Train 2, Bank 2 | Train 2, Bank 3 | Train 2, Bank 4 | Train 2, Bank 5 | Train 2, Bank 6 | Train 2, Bank 7 | Train 2, Bank 8 | Train 2, Bank 9 | Train 2, Bank 10 | Train 2, Bank 11 | Train 3, Bank 1 | Train 3, Bank 2 | Train 3, Bank 3 | Train 3, Bank 4 | Train 3, Bank 5 | Train 3, Bank 6 | Train 3, Bank 7 | Train 3, Bank 8 | Train 3, Bank 9 | Train 3, Bank 10 | Train 3, Bank 11 | Train 4, Bank 1 | Train 4, Bank 2 | Train 4, Bank 3 | Train 4, Bank 4 | Train 4, Bank 5 | Train 4, Bank 6 | Train 4, Bank 7 | Train 4, Bank 8 | Train 4, Bank 9 | Train 4, Bank 10 | Train 4, Bank 11 | Train 5, Bank 1 | Train 5, Bank 2 | Train 5, Bank 3 | Train 5, Bank 4 | Train 5, Bank 5 | Train 5, Bank 6 | Train 5, Bank 7 | Train 5, Bank 8 | Train 5, Bank 9 | Train 5, Bank 10 | Train 5, Bank 11 | Train 6, Bank 1 | Train 6, Bank 2 | Train 6, Bank 3 | Train 6, Bank 4 | Train 6, Bank 5 | Train 6, Bank 6 | Train 6, Bank 7 | Train 6, Bank 8 | Train 6, Bank 9 | Train 6, Bank 10 | Train 6, Bank 11 | Train 7, Bank 1 | Train 7, Bank 2 | Train 7, Bank 3 | Train 7, Bank 4 | Train 7, Bank 5 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 6 | Train 7, Bank 7 | Train 7, Bank 8 | Train 7, Bank 9 | Train 7, Bank 10 | Train 7, Bank 11 | Train 7, Bank 12
Date/Time | Lamp Aging Factor
2005-03-06 03:45 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-07 00:06 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.0343 | 1.0343 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.028 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-08 00:39 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.028 | 1.0343 | 1.0343 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.028 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-09 01:02 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.0206 | 1.0268 | 1.0343 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.0206 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-10 01:30 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.014 | 1.0195 | 1.0343 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.014 | 1.0195 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-11 02:09 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0076 | 1.0195 | 1.0343 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0018 | 1.0076 | 1.0195 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-12 02:43 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0076 | 1.0195 | 1.0343 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0076 | 1.0195 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-13 03:17 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 1.0018 | 1.0195 | 1.0343 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 1.0018 | 1.0195 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-14 03:45 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.99071 | 1.0018 | 1.0195 | 1.0343 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.99071 | 1.0018 | 1.0195 | 1.0343 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-15 00:17 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.9866 | 0.99698 | 1.0195 | 1.0343 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.9866 | 0.99698 | 1.0195 | 1.0343 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-16 03:56 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.9866 | 0.99698 | 1.0195 | 1.0343 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.9866 | 0.99698 | 1.0195 | 1.0343 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-17 00:11 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.98267 | 0.99261 | 1.014 | 1.028 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.97314 | 0.98267 | 0.99261 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-18 00:45 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.97797 | 0.99261 | 1.014 | 1.028 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.96888 | 0.97797 | 0.99261 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-19 01:24 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.97349 | 0.99261 | 1.014 | 1.028 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.9648 | 0.97349 | 0.99261 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-20 01:52 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96938 | 0.98741 | 1.014 | 1.028 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96938 | 0.98741 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-21 02:26 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.96938 | 0.98741 | 1.014 | 1.028 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.95728 | 0.96938 | 0.98741 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-22 03:11 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.96528 | 0.98267 | 1.014 | 1.028 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.96528 | 0.98267 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-23 03:56 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.96135 | 0.97797 | 1.014 | 1.028 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.95032 | 0.96135 | 0.97797 | 1.014 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-24 03:22 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.95787 | 0.97366 | 1.0078 | 1.028 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.9471 | 0.95787 | 0.97366 | 1.0078 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-25 03:56 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.95423 | 0.96954 | 1.0078 | 1.028 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.95423 | 0.96954 | 1.0078 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-26 00:22 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.95142 | 0.96608 | 1.003 | 1.028 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.94134 | 0.95142 | 0.96608 | 1.003 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-27 00:51 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.94816 | 0.96228 | 0.99743 | 1.028 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.93841 | 0.94816 | 0.96228 | 0.99743 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-28 01:24 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.94488 | 0.95847 | 0.99197 | 1.028 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.93545 | 0.94488 | 0.95847 | 0.99197 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-29 01:58 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.94171 | 0.95495 | 0.98681 | 1.028 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.9327 | 0.94171 | 0.95495 | 0.98681 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-30 02:54 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.93877 | 0.95142 | 0.9819 | 1.028 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.92992 | 0.93877 | 0.95142 | 0.9819 | 1.028 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0187 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-03-31 03:28 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.9358 | 0.95142 | 0.9819 | 1.028 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.92722 | 0.9358 | 0.95142 | 0.9819 | 1.028 | 1.0119 | 1.0119 | 1.0119 | 1.0119 | 1.0119 | 1.0119 | 1.0119 | 1.0265 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-01 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.93338 | 0.95142 | 0.9819 | 1.028 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.93338 | 0.95142 | 0.9819 | 1.028 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-02 00:39 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.93069 | 0.94803 | 0.97742 | 1.028 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.93069 | 0.94803 | 0.97742 | 1.028 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-03 01:08 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92797 | 0.94488 | 0.97296 | 1.0206 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92017 | 0.92797 | 0.94488 | 0.97296 | 1.0206 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-04 02:32 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.92533 | 0.94488 | 0.97296 | 1.0206 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.92533 | 0.94488 | 0.97296 | 1.0206 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-05 03:17 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.92276 | 0.94171 | 0.97296 | 1.0206 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.91529 | 0.92276 | 0.94171 | 0.97296 | 1.0206 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-06 03:51 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.92276 | 0.94171 | 0.97296 | 1.0206 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.91308 | 0.92276 | 0.94171 | 0.97296 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-07 00:17 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.92076 | 0.93925 | 0.96954 | 1.0206 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.9112 | 0.92076 | 0.93925 | 0.96954 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-08 01:13 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.91832 | 0.93627 | 0.96954 | 1.0206 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.90909 | 0.91832 | 0.93627 | 0.96954 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-09 01:58 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.91595 | 0.93338 | 0.96954 | 1.0206 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.91595 | 0.93338 | 0.96954 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-10 02:26 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.91372 | 0.93058 | 0.96954 | 1.0206 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.90485 | 0.91372 | 0.93058 | 0.96954 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-11 02:49 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.91146 | 0.93058 | 0.96954 | 1.0206 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.90289 | 0.91146 | 0.93058 | 0.96954 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-12 03:11 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90935 | 0.92797 | 0.9656 | 1.0206 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90096 | 0.90935 | 0.92797 | 0.9656 | 1.0206 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-13 03:34 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.9072 | 0.92543 | 0.96166 | 1.014 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.89901 | 0.9072 | 0.92543 | 0.96166 | 1.014 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-14 04:02 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.90518 | 0.92543 | 0.96166 | 1.014 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.89717 | 0.90518 | 0.92543 | 0.96166 | 1.014 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0009 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-15 01:30 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.90345 | 0.92543 | 0.96166 | 1.014 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.89551 | 0.90345 | 0.92543 | 0.96166 | 1.014 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-16 02:15 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.90144 | 0.92286 | 0.96166 | 1.014 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.89375 | 0.90144 | 0.92286 | 0.96166 | 1.014 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-17 02:38 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89947 | 0.92046 | 0.95802 | 1.014 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89194 | 0.89947 | 0.92046 | 0.95802 | 1.014 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-18 02:54 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89762 | 0.91803 | 0.95452 | 1.0078 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89024 | 0.89762 | 0.91803 | 0.95452 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-19 03:28 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.89581 | 0.91576 | 0.95101 | 1.0078 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.88851 | 0.89581 | 0.91576 | 0.95101 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-20 04:02 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.89397 | 0.91345 | 0.94763 | 1.0078 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.88688 | 0.89397 | 0.91345 | 0.94763 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-21 00:39 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.89244 | 0.91164 | 0.94763 | 1.0078 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.88547 | 0.89244 | 0.91164 | 0.94763 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-21 04:47 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.89216 | 0.91164 | 0.94763 | 1.0078 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.88521 | 0.89216 | 0.91164 | 0.94763 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-22 01:41 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.89067 | 0.90979 | 0.94763 | 1.0078 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.88383 | 0.89067 | 0.90979 | 0.94763 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-23 02:09 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88899 | 0.90763 | 0.94449 | 1.0078 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88229 | 0.88899 | 0.90763 | 0.94449 | 1.0078 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 1.0146 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-24 02:26 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.88735 | 0.9056 | 0.94449 | 1.0078 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.8807 | 0.88735 | 0.9056 | 0.94449 | 1.0078 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 1.0083 | 1.0268 | 1.0343 | 1.0343 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-25 02:49 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.88567 | 0.90354 | 0.94146 | 1.0078 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.87921 | 0.88567 | 0.90354 | 0.94146 | 1.0078 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 1.0083 | 1.0268 | 1.0343 | 1.0343 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-26 02:26 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.88416 | 0.90168 | 0.93853 | 1.002 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.87774 | 0.88416 | 0.90168 | 0.93853 | 1.002 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 1.0083 | 1.0268 | 1.0343 | 1.0343 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-27 03:00 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.88254 | 0.89971 | 0.93853 | 1.002 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.8763 | 0.88254 | 0.89971 | 0.93853 | 1.002 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 0.99071 | 1.0083 | 1.0268 | 1.0343 | 1.0343 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-28 03:28 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.88102 | 0.89785 | 0.93557 | 0.99654 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.87482 | 0.88102 | 0.89785 | 0.93557 | 0.99654 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 0.9858 | 1.0025 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-29 03:45 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87946 | 0.89604 | 0.93557 | 0.99654 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87343 | 0.87946 | 0.89604 | 0.93557 | 0.99654 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.99676 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-04-30 00:11 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87823 | 0.89448 | 0.93557 | 0.99654 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87228 | 0.87823 | 0.89448 | 0.93557 | 0.99654 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.99676 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-01 00:28 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87678 | 0.89273 | 0.93281 | 0.99113 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87088 | 0.87678 | 0.89273 | 0.93281 | 0.99113 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.99676 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-02 00:51 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.87529 | 0.89095 | 0.93014 | 0.9862 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.87529 | 0.89095 | 0.93014 | 0.9862 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.99676 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-03 01:24 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.87389 | 0.88927 | 0.92743 | 0.9862 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.86818 | 0.87389 | 0.88927 | 0.92743 | 0.9862 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.98114 | 0.99676 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-04 01:52 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.87246 | 0.88755 | 0.92491 | 0.9862 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.87246 | 0.88755 | 0.92491 | 0.9862 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.99155 | 1.0066 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-05 02:15 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.8711 | 0.88755 | 0.92491 | 0.9862 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.8711 | 0.88755 | 0.92491 | 0.9862 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.97651 | 0.99155 | 1.0066 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-06 02:38 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86971 | 0.88594 | 0.92236 | 0.9862 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86431 | 0.86971 | 0.88594 | 0.92236 | 0.9862 | 0.97227 | 0.97227 | 0.97227 | 0.97227 | 0.97227 | 0.97227 | 0.97227 | 0.9866 | 1.0009 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-07 02:49 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.8684 | 0.88435 | 0.92236 | 0.9862 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.8684 | 0.88435 | 0.92236 | 0.9862 | 0.96821 | 0.96821 | 0.96821 | 0.96821 | 0.96821 | 0.96821 | 0.96821 | 0.98171 | 0.99543 | 1.013 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-08 03:11 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.8671 | 0.88273 | 0.91997 | 0.9862 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.8671 | 0.88273 | 0.91997 | 0.9862 | 0.96416 | 0.96416 | 0.96416 | 0.96416 | 0.96416 | 0.96416 | 0.96416 | 0.97724 | 0.99029 | 1.0066 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-09 03:34 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86578 | 0.88121 | 0.91997 | 0.9862 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86578 | 0.88121 | 0.91997 | 0.9862 | 0.96043 | 0.96043 | 0.96043 | 0.96043 | 0.96043 | 0.96043 | 0.96043 | 0.97296 | 0.98521 | 1.0066 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-10 03:51 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.86452 | 0.8797 | 0.91765 | 0.9862 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.85944 | 0.86452 | 0.8797 | 0.91765 | 0.9862 | 0.95684 | 0.95684 | 0.95684 | 0.95684 | 0.95684 | 0.95684 | 0.95684 | 0.96871 | 0.98057 | 1.0009 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-11 00:17 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.86349 | 0.87841 | 0.91765 | 0.9862 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.86349 | 0.87841 | 0.91765 | 0.9862 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.95381 | 0.96544 | 0.97669 | 1.0009 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-12 00:34 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.86222 | 0.87696 | 0.91529 | 0.9862 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.85727 | 0.86222 | 0.87696 | 0.91529 | 0.9862 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.96166 | 0.97244 | 0.99543 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-13 00:56 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.86102 | 0.87553 | 0.91308 | 0.9862 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.86102 | 0.87553 | 0.91308 | 0.9862 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.95046 | 0.96166 | 0.97244 | 0.99543 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-14 01:19 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85983 | 0.87553 | 0.91308 | 0.9862 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85497 | 0.85983 | 0.87553 | 0.91308 | 0.9862 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.95787 | 0.97244 | 0.99543 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-15 01:36 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85861 | 0.87407 | 0.91308 | 0.9862 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85387 | 0.85861 | 0.87407 | 0.91308 | 0.9862 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.94723 | 0.95787 | 0.97244 | 0.99543 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-16 01:58 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85746 | 0.87268 | 0.91308 | 0.9862 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85278 | 0.85746 | 0.87268 | 0.91308 | 0.9862 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.94398 | 0.95438 | 0.96838 | 0.99543 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-17 02:21 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85632 | 0.87132 | 0.91093 | 0.9862 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85166 | 0.85632 | 0.87132 | 0.91093 | 0.9862 | 0.94097 | 0.94097 | 0.94097 | 0.94097 | 0.94097 | 0.94097 | 0.94097 | 0.95087 | 0.96432 | 0.99008 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-18 02:43 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.85515 | 0.86993 | 0.91093 | 0.9862 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.8506 | 0.85515 | 0.86993 | 0.91093 | 0.9862 | 0.93793 | 0.93793 | 0.93793 | 0.93793 | 0.93793 | 0.93793 | 0.93793 | 0.94763 | 0.96058 | 0.99008 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-19 03:00 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.85405 | 0.86861 | 0.90874 | 0.9862 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.84955 | 0.85405 | 0.86861 | 0.90874 | 0.9862 | 0.9351 | 0.9351 | 0.9351 | 0.9351 | 0.9351 | 0.9351 | 0.9351 | 0.94449 | 0.95699 | 0.98521 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-20 03:17 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.85296 | 0.86732 | 0.90669 | 0.98152 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.84847 | 0.85296 | 0.86732 | 0.90669 | 0.98152 | 0.93236 | 0.93236 | 0.93236 | 0.93236 | 0.93236 | 0.93236 | 0.93236 | 0.94146 | 0.95338 | 0.98057 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-21 03:45 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.85184 | 0.86599 | 0.90669 | 0.98152 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.84745 | 0.85184 | 0.86599 | 0.90669 | 0.98152 | 0.92959 | 0.92959 | 0.92959 | 0.92959 | 0.92959 | 0.92959 | 0.92959 | 0.93841 | 0.95005 | 0.98057 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-22 00:06 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.85095 | 0.86494 | 0.90502 | 0.98152 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.84661 | 0.85095 | 0.86494 | 0.90502 | 0.98152 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.93603 | 0.94736 | 0.97669 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-22 04:08 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.85077 | 0.86473 | 0.90469 | 0.98152 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.84644 | 0.85077 | 0.86473 | 0.90469 | 0.98152 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.93603 | 0.94736 | 0.97669 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-23 00:17 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.8499 | 0.8637 | 0.90305 | 0.98152 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.84557 | 0.8499 | 0.8637 | 0.90305 | 0.98152 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.93603 | 0.94736 | 0.97669 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-24 00:39 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84881 | 0.8637 | 0.90305 | 0.98152 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84458 | 0.84881 | 0.8637 | 0.90305 | 0.98152 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.92743 | 0.93603 | 0.94736 | 0.97669 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-25 01:02 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84779 | 0.86242 | 0.90305 | 0.98152 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84361 | 0.84779 | 0.86242 | 0.90305 | 0.98152 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 0.93315 | 0.94411 | 0.97669 | 1.0195 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0268 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-26 00:28 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84682 | 0.86127 | 0.90112 | 0.98152 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84265 | 0.84682 | 0.86127 | 0.90112 | 0.98152 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.93058 | 0.94121 | 0.97262 | 1.0195 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-27 01:02 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84578 | 0.86003 | 0.89924 | 0.97687 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84169 | 0.84578 | 0.86003 | 0.89924 | 0.97687 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.92246 | 0.93058 | 0.94121 | 0.97262 | 1.0195 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-28 01:41 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84475 | 0.85885 | 0.89732 | 0.97687 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84071 | 0.84475 | 0.85885 | 0.89732 | 0.97687 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92786 | 0.93817 | 0.96838 | 1.0195 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-29 02:04 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.84377 | 0.85765 | 0.89551 | 0.97687 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.83978 | 0.84377 | 0.85765 | 0.89551 | 0.97687 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92786 | 0.93817 | 0.96838 | 1.0195 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-30 02:32 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.84276 | 0.85651 | 0.89367 | 0.97687 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.83883 | 0.84276 | 0.85651 | 0.89367 | 0.97687 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92786 | 0.93817 | 0.96838 | 1.0195 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-05-31 03:00 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.84181 | 0.85534 | 0.89194 | 0.97262 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.83792 | 0.84181 | 0.85534 | 0.89194 | 0.97262 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92007 | 0.92786 | 0.93817 | 0.96838 | 1.0195 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-01 03:39 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.84083 | 0.85423 | 0.89017 | 0.96838 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.83698 | 0.84083 | 0.85423 | 0.89017 | 0.96838 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.91765 | 0.92533 | 0.93533 | 0.96448 | 1.013 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-02 03:06 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83994 | 0.85314 | 0.89017 | 0.96838 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83994 | 0.85314 | 0.89017 | 0.96838 | 0.91548 | 0.91548 | 0.91548 | 0.91548 | 0.91548 | 0.91548 | 0.91548 | 0.92286 | 0.93259 | 0.96448 | 1.013 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-03 02:32 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83902 | 0.8521 | 0.88858 | 0.96448 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83525 | 0.83902 | 0.8521 | 0.88858 | 0.96448 | 0.91327 | 0.91327 | 0.91327 | 0.91327 | 0.91327 | 0.91327 | 0.91327 | 0.92056 | 0.93003 | 0.96073 | 1.0069 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-04 03:00 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83811 | 0.85099 | 0.88688 | 0.96073 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83438 | 0.83811 | 0.85099 | 0.88688 | 0.96073 | 0.91111 | 0.91111 | 0.91111 | 0.91111 | 0.91111 | 0.91111 | 0.91111 | 0.91813 | 0.92733 | 0.95713 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-05 03:34 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83717 | 0.84994 | 0.88528 | 0.96073 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83348 | 0.83717 | 0.84994 | 0.88528 | 0.96073 | 0.90892 | 0.90892 | 0.90892 | 0.90892 | 0.90892 | 0.90892 | 0.90892 | 0.91585 | 0.92481 | 0.95352 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-06 04:02 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83628 | 0.84886 | 0.88364 | 0.96073 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83263 | 0.83628 | 0.84886 | 0.88364 | 0.96073 | 0.90686 | 0.90686 | 0.90686 | 0.90686 | 0.90686 | 0.90686 | 0.90686 | 0.91354 | 0.92226 | 0.95019 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-07 00:39 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83551 | 0.848 | 0.88229 | 0.96073 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83551 | 0.848 | 0.88229 | 0.96073 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.91173 | 0.92027 | 0.94736 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-08 01:08 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83463 | 0.84694 | 0.88077 | 0.95713 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83189 | 0.83551 | 0.848 | 0.88229 | 0.96073 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.9051 | 0.91173 | 0.92027 | 0.94736 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-09 01:36 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.83373 | 0.84594 | 0.88077 | 0.95713 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83106 | 0.83463 | 0.84694 | 0.88229 | 0.96073 | 0.90305 | 0.90305 | 0.90305 | 0.90305 | 0.90305 | 0.90305 | 0.90305 | 0.90952 | 0.91784 | 0.94736 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-10 02:09 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.83288 | 0.84491 | 0.88077 | 0.95713 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.8302 | 0.83373 | 0.84594 | 0.88229 | 0.96073 | 0.90112 | 0.90112 | 0.90112 | 0.90112 | 0.90112 | 0.90112 | 0.90112 | 0.90745 | 0.91557 | 0.94736 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-11 02:43 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.832 | 0.84393 | 0.87921 | 0.95713 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.82938 | 0.83288 | 0.84491 | 0.88077 | 0.96073 | 0.89916 | 0.89916 | 0.89916 | 0.89916 | 0.89916 | 0.89916 | 0.89916 | 0.90535 | 0.91327 | 0.94424 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-12 03:11 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.83116 | 0.84292 | 0.87774 | 0.95713 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.82854 | 0.832 | 0.84393 | 0.87921 | 0.96073 | 0.89732 | 0.89732 | 0.89732 | 0.89732 | 0.89732 | 0.89732 | 0.89732 | 0.90337 | 0.91111 | 0.94109 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-13 03:39 | 0.82691 | 0.82691 | 0.82691 | 0.82691 | 0.82691 | 0.82691 | 0.82691 | 0.8303 | 0.84197 | 0.87774 | 0.95713 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.82774 | 0.83116 | 0.84292 | 0.87921 | 0.96073 | 0.89544 | 0.89544 | 0.89544 | 0.89544 | 0.89544 | 0.89544 | 0.89544 | 0.90136 | 0.90892 | 0.94109 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-14 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82962 | 0.84114 | 0.87654 | 0.95713 | 0.82704 | 0.82704 | 0.82704 | 0.82704 | 0.82704 | 0.82704 | 0.82704 | 0.83044 | 0.84213 | 0.87799 | 0.96073 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89978 | 0.9072 | 0.93865 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-15 00:34 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82877 | 0.84021 | 0.87506 | 0.95713 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82625 | 0.82962 | 0.84114 | 0.87648 | 0.96073 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89978 | 0.9072 | 0.93865 | 1.0011 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-16 01:02 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82797 | 0.83925 | 0.87366 | 0.95352 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82544 | 0.82877 | 0.84021 | 0.87506 | 0.95713 | 0.89223 | 0.89223 | 0.89223 | 0.89223 | 0.89223 | 0.89223 | 0.89223 | 0.89785 | 0.9051 | 0.93568 | 0.99543 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-17 01:41 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82714 | 0.83833 | 0.87223 | 0.95352 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82797 | 0.83925 | 0.8736 | 0.95713 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89604 | 0.90313 | 0.93292 | 0.99543 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-18 02:21 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82635 | 0.83739 | 0.87223 | 0.95352 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82388 | 0.82714 | 0.83833 | 0.8736 | 0.95713 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.89419 | 0.90112 | 0.93292 | 0.99543 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-19 02:49 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82554 | 0.8365 | 0.87082 | 0.95019 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82635 | 0.83739 | 0.87223 | 0.95352 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.89244 | 0.89916 | 0.93014 | 0.99029 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0198 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-20 03:17 | 0.82157 | 0.82157 | 0.82157 | 0.82157 | 0.82157 | 0.82157 | 0.82157 | 0.82477 | 0.83558 | 0.87082 | 0.95019 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82234 | 0.82554 | 0.8365 | 0.87223 | 0.95352 | 0.88541 | 0.88541 | 0.88541 | 0.88541 | 0.88541 | 0.88541 | 0.88541 | 0.89067 | 0.89732 | 0.93014 | 0.99029 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-21 00:11 | 0.82095 | 0.82095 | 0.82095 | 0.82095 | 0.82095 | 0.82095 | 0.82095 | 0.8241 | 0.83481 | 0.87082 | 0.95019 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82486 | 0.83572 | 0.87223 | 0.95352 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.8892 | 0.89574 | 0.93014 | 0.99029 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-22 00:51 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82331 | 0.83395 | 0.86949 | 0.94683 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.8241 | 0.83481 | 0.87082 | 0.95005 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.8892 | 0.89574 | 0.93014 | 0.99029 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0271 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-26 00:22 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.82037 | 0.83058 | 0.86437 | 0.93498 | 0.81807 | 0.81807 | 0.81807 | 0.81807 | 0.81807 | 0.81807 | 0.81807 | 0.8211 | 0.83144 | 0.86567 | 0.93793 | 0.87805 | 0.87805 | 0.87805 | 0.87805 | 0.87805 | 0.87805 | 0.87805 | 0.88286 | 0.88892 | 0.92027 | 0.9721 | 0.9864 | 0.9864 | 0.9864 | 0.9864 | 0.9864 | 0.9864 | 0.9864 | 0.9864 | 0.9864 | 1.0016 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-27 00:51 | 0.81664 | 0.81664 | 0.81664 | 0.81664 | 0.81664 | 0.81664 | 0.81664 | 0.81962 | 0.82975 | 0.86313 | 0.93498 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.81734 | 0.82037 | 0.83058 | 0.86437 | 0.93793 | 0.87654 | 0.87654 | 0.87654 | 0.87654 | 0.87654 | 0.87654 | 0.87654 | 0.88127 | 0.88722 | 0.91784 | 0.9721 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.99609 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-28 00:22 | 0.81595 | 0.81595 | 0.81595 | 0.81595 | 0.81595 | 0.81595 | 0.81595 | 0.81893 | 0.82894 | 0.86313 | 0.93498 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81965 | 0.82979 | 0.86437 | 0.93793 | 0.87518 | 0.87518 | 0.87518 | 0.87518 | 0.87518 | 0.87518 | 0.87518 | 0.87983 | 0.88567 | 0.91784 | 0.9721 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.99609 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-29 03:51 | 0.81518 | 0.81518 | 0.81518 | 0.81518 | 0.81518 | 0.81518 | 0.81518 | 0.8181 | 0.82803 | 0.86172 | 0.93191 | 0.81586 | 0.81586 | 0.81586 | 0.81586 | 0.81586 | 0.81586 | 0.81586 | 0.81884 | 0.82884 | 0.86298 | 0.93464 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87811 | 0.88383 | 0.91529 | 0.96755 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.99609 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-06-30 00:28 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81751 | 0.82734 | 0.86072 | 0.93191 | 0.81529 | 0.81529 | 0.81529 | 0.81529 | 0.81529 | 0.81529 | 0.81529 | 0.81822 | 0.82813 | 0.86192 | 0.93464 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87811 | 0.88383 | 0.91529 | 0.96755 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.99609 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-01 00:51 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81679 | 0.82655 | 0.85949 | 0.92926 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81459 | 0.81751 | 0.82734 | 0.86072 | 0.93191 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87666 | 0.88229 | 0.91299 | 0.96353 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.98171 | 0.99609 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-02 03:22 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81604 | 0.82567 | 0.85823 | 0.92926 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81673 | 0.82645 | 0.85939 | 0.93191 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87506 | 0.88058 | 0.91067 | 0.96353 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.99029 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-03 03:51 | 0.8125 | 0.8125 | 0.8125 | 0.8125 | 0.8125 | 0.8125 | 0.8125 | 0.81532 | 0.8249 | 0.85703 | 0.92926 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81316 | 0.81604 | 0.82567 | 0.85823 | 0.93191 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87071 | 0.87506 | 0.88058 | 0.91067 | 0.96353 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.99029 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-04 00:45 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81473 | 0.82422 | 0.85604 | 0.92926 | 0.81258 | 0.81258 | 0.81258 | 0.81258 | 0.81258 | 0.81258 | 0.81258 | 0.81544 | 0.82499 | 0.85722 | 0.93191 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.86954 | 0.87383 | 0.87927 | 0.90883 | 0.96353 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.99029 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-05 02:38 | 0.81122 | 0.81122 | 0.81122 | 0.81122 | 0.81122 | 0.81122 | 0.81122 | 0.814 | 0.8234 | 0.85604 | 0.92926 | 0.8119 | 0.8119 | 0.8119 | 0.8119 | 0.8119 | 0.8119 | 0.8119 | 0.8147 | 0.82416 | 0.85722 | 0.93191 | 0.86812 | 0.86812 | 0.86812 | 0.86812 | 0.86812 | 0.86812 | 0.86812 | 0.87234 | 0.87768 | 0.90883 | 0.96353 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.97669 | 0.99029 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-06 01:24 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.81338 | 0.82268 | 0.85502 | 0.92926 | 0.81127 | 0.81127 | 0.81127 | 0.81127 | 0.81127 | 0.81127 | 0.81127 | 0.81405 | 0.82343 | 0.85614 | 0.93191 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.86689 | 0.8711 | 0.87636 | 0.90686 | 0.96353 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.98561 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-07 01:08 | 0.80998 | 0.80998 | 0.80998 | 0.80998 | 0.80998 | 0.80998 | 0.80998 | 0.81272 | 0.82194 | 0.85391 | 0.92926 | 0.81063 | 0.81063 | 0.81063 | 0.81063 | 0.81063 | 0.81063 | 0.81063 | 0.81338 | 0.82271 | 0.85502 | 0.93191 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86562 | 0.86976 | 0.87494 | 0.90485 | 0.96353 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.98561 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-08 01:52 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.81203 | 0.8212 | 0.85391 | 0.92926 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.81272 | 0.82194 | 0.85502 | 0.93191 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.8684 | 0.87349 | 0.90485 | 0.96353 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.98561 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-09 02:21 | 0.80867 | 0.80867 | 0.80867 | 0.80867 | 0.80867 | 0.80867 | 0.80867 | 0.81138 | 0.82043 | 0.85391 | 0.92926 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.81203 | 0.8212 | 0.85502 | 0.93191 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.8671 | 0.87211 | 0.90485 | 0.96353 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.98561 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-10 02:43 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.81071 | 0.81971 | 0.85282 | 0.92926 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.81138 | 0.82043 | 0.85391 | 0.93191 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86578 | 0.87071 | 0.90289 | 0.96353 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.97279 | 0.98561 | 1.0071 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-11 03:17 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.81006 | 0.81896 | 0.8517 | 0.92659 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.80804 | 0.81071 | 0.81971 | 0.85278 | 0.92915 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86452 | 0.86938 | 0.90089 | 0.95982 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.98095 | 1.0013 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-12 03:56 | 0.80678 | 0.80678 | 0.80678 | 0.80678 | 0.80678 | 0.80678 | 0.80678 | 0.8094 | 0.81822 | 0.8506 | 0.92398 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.80739 | 0.81006 | 0.81896 | 0.8517 | 0.92659 | 0.85939 | 0.85939 | 0.85939 | 0.85939 | 0.85939 | 0.85939 | 0.85939 | 0.86323 | 0.86802 | 0.89901 | 0.95611 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.96854 | 0.98095 | 1.0013 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-13 00:28 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80887 | 0.81763 | 0.84972 | 0.92398 | 0.80688 | 0.80688 | 0.80688 | 0.80688 | 0.80688 | 0.80688 | 0.80688 | 0.80951 | 0.81834 | 0.85077 | 0.92659 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.85842 | 0.86222 | 0.86694 | 0.8974 | 0.95611 | 0.96512 | 0.96512 | 0.96512 | 0.96512 | 0.96512 | 0.96512 | 0.96512 | 0.96512 | 0.96512 | 0.97706 | 1.0013 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-14 01:08 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80822 | 0.8169 | 0.84864 | 0.92156 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80624 | 0.80885 | 0.81763 | 0.84972 | 0.92398 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 0.86097 | 0.86562 | 0.89559 | 0.95254 | 0.96135 | 0.96135 | 0.96135 | 0.96135 | 0.96135 | 0.96135 | 0.96135 | 0.96135 | 0.96135 | 0.97279 | 0.99565 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0265 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-15 01:41 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80757 | 0.81621 | 0.84762 | 0.92156 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80564 | 0.80822 | 0.8169 | 0.84864 | 0.92398 | 0.85609 | 0.85609 | 0.85609 | 0.85609 | 0.85609 | 0.85609 | 0.85609 | 0.85973 | 0.86431 | 0.89375 | 0.95254 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.96854 | 0.99565 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0265 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-16 02:15 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80696 | 0.81549 | 0.84762 | 0.92156 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80501 | 0.80757 | 0.81621 | 0.84864 | 0.92398 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85856 | 0.86308 | 0.89375 | 0.95254 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.96854 | 0.99565 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0265 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-17 02:38 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.80632 | 0.81481 | 0.84762 | 0.92156 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80441 | 0.80696 | 0.81549 | 0.84864 | 0.92398 | 0.85382 | 0.85382 | 0.85382 | 0.85382 | 0.85382 | 0.85382 | 0.85382 | 0.85736 | 0.86182 | 0.89375 | 0.95254 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.95758 | 0.96854 | 0.99565 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 1.0265 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-18 02:54 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80571 | 0.81411 | 0.84657 | 0.91909 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.8038 | 0.80634 | 0.81481 | 0.84762 | 0.92156 | 0.85269 | 0.85269 | 0.85269 | 0.85269 | 0.85269 | 0.85269 | 0.85269 | 0.85623 | 0.86062 | 0.89201 | 0.94924 | 0.95409 | 0.95409 | 0.95409 | 0.95409 | 0.95409 | 0.95409 | 0.95409 | 0.95409 | 0.95409 | 0.96464 | 0.9905 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 1.0195 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-19 03:39 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.80508 | 0.81344 | 0.84557 | 0.91909 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80321 | 0.80571 | 0.81411 | 0.84657 | 0.92156 | 0.85161 | 0.85161 | 0.85161 | 0.85161 | 0.85161 | 0.85161 | 0.85161 | 0.85506 | 0.85939 | 0.89024 | 0.94924 | 0.9506 | 0.9506 | 0.9506 | 0.9506 | 0.9506 | 0.9506 | 0.9506 | 0.9506 | 0.9506 | 0.96073 | 0.9905 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 1.0195 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0206 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343
2005-07-20 00:11 | 0.80212 | 0.80212 | 0.80212 | 0.80212 | 0.80212 | 0.80212 | 0.80212 | 0.80459 | 0.81286 | 0.84471 | 0.91717 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.80518 | 0.81355 | 0.84569 | 0.91948 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85414 | 0.85842 | 0.88879 | 0.94657 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.95758 | 0.9862 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 1.014 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-21 00:51 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80397 | 0.8122 | 0.84369 | 0.91717 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.8027 | 0.80518 | 0.81355 | 0.84569 | 0.91948 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85068 | 0.85414 | 0.85842 | 0.88879 | 0.94657 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.94789 | 0.95758 | 0.9862 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 0.99698 | 1.014 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-22 01:30 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80338 | 0.81152 | 0.84272 | 0.91483 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80459 | 0.81286 | 0.84471 | 0.91717 | 0.84964 | 0.84964 | 0.84964 | 0.84964 | 0.84964 | 0.84964 | 0.84964 | 0.853 | 0.85722 | 0.88715 | 0.94334 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.95409 | 0.98152 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-23 02:09 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80277 | 0.81084 | 0.84173 | 0.91263 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80152 | 0.80397 | 0.81217 | 0.84369 | 0.91483 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.85192 | 0.85609 | 0.88547 | 0.94023 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.9506 | 0.97687 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-24 02:32 | 0.79977 | 0.79977 | 0.79977 | 0.79977 | 0.79977 | 0.79977 | 0.79977 | 0.80216 | 0.8102 | 0.84079 | 0.91263 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80092 | 0.80338 | 0.81152 | 0.84272 | 0.91483 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.84856 | 0.85192 | 0.85609 | 0.88547 | 0.94023 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.94146 | 0.9506 | 0.97687 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 0.99155 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-25 02:54 | 0.79921 | 0.79921 | 0.79921 | 0.79921 | 0.79921 | 0.79921 | 0.79921 | 0.80159 | 0.80953 | 0.83982 | 0.91263 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80035 | 0.80277 | 0.81087 | 0.84173 | 0.91483 | 0.84753 | 0.84753 | 0.84753 | 0.84753 | 0.84753 | 0.84753 | 0.84753 | 0.85082 | 0.85492 | 0.8839 | 0.94023 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.94736 | 0.97687 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-26 03:22 | 0.79863 | 0.79863 | 0.79863 | 0.79863 | 0.79863 | 0.79863 | 0.79863 | 0.80102 | 0.8089 | 0.83982 | 0.91263 | 0.79979 | 0.79979 | 0.79979 | 0.79979 | 0.79979 | 0.79979 | 0.79979 | 0.80219 | 0.8102 | 0.84173 | 0.91483 | 0.84648 | 0.84648 | 0.84648 | 0.84648 | 0.84648 | 0.84648 | 0.84648 | 0.84977 | 0.85382 | 0.8839 | 0.94023 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.94736 | 0.97687 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-27 02:49 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.80045 | 0.8083 | 0.83894 | 0.91049 | 0.79923 | 0.79923 | 0.79923 | 0.79923 | 0.79923 | 0.79923 | 0.79923 | 0.80161 | 0.80959 | 0.84083 | 0.91272 | 0.84553 | 0.84553 | 0.84553 | 0.84553 | 0.84553 | 0.84553 | 0.84553 | 0.84873 | 0.85273 | 0.88235 | 0.93745 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.94736 | 0.97687 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-28 03:17 | 0.79753 | 0.79753 | 0.79753 | 0.79753 | 0.79753 | 0.79753 | 0.79753 | 0.79989 | 0.80765 | 0.83894 | 0.91049 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.80104 | 0.80893 | 0.84083 | 0.91272 | 0.8445 | 0.8445 | 0.8445 | 0.8445 | 0.8445 | 0.8445 | 0.8445 | 0.8477 | 0.85166 | 0.88235 | 0.93745 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.93853 | 0.94736 | 0.97687 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-29 03:51 | 0.79699 | 0.79699 | 0.79699 | 0.79699 | 0.79699 | 0.79699 | 0.79699 | 0.7993 | 0.80703 | 0.83799 | 0.91049 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.7981 | 0.80045 | 0.8083 | 0.83986 | 0.91272 | 0.84353 | 0.84353 | 0.84353 | 0.84353 | 0.84353 | 0.84353 | 0.84353 | 0.84665 | 0.85055 | 0.88083 | 0.93745 | 0.93557 | 0.93557 | 0.93557 | 0.93557 | 0.93557 | 0.93557 | 0.93557 | 0.93557 | 0.93557 | 0.94411 | 0.97687 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 0.9866 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-30 00:22 | 0.79652 | 0.79652 | 0.79652 | 0.79652 | 0.79652 | 0.79652 | 0.79652 | 0.79884 | 0.8065 | 0.83724 | 0.91049 | 0.79763 | 0.79763 | 0.79763 | 0.79763 | 0.79763 | 0.79763 | 0.79763 | 0.79998 | 0.80775 | 0.83909 | 0.91272 | 0.84268 | 0.84268 | 0.84268 | 0.84268 | 0.84268 | 0.84268 | 0.84268 | 0.84582 | 0.84968 | 0.87952 | 0.93745 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.94159 | 0.97687 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-07-31 00:51 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79826 | 0.80589 | 0.83631 | 0.9084 | 0.79708 | 0.79708 | 0.79708 | 0.79708 | 0.79708 | 0.79708 | 0.79708 | 0.7994 | 0.80714 | 0.83814 | 0.91049 | 0.84173 | 0.84173 | 0.84173 | 0.84173 | 0.84173 | 0.84173 | 0.84173 | 0.84479 | 0.8486 | 0.87805 | 0.93452 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.94159 | 0.97687 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-01 01:19 | 0.79543 | 0.79543 | 0.79543 | 0.79543 | 0.79543 | 0.79543 | 0.79543 | 0.79772 | 0.80526 | 0.83543 | 0.9084 | 0.79654 | 0.79654 | 0.79654 | 0.79654 | 0.79654 | 0.79654 | 0.79654 | 0.79884 | 0.8065 | 0.83724 | 0.91049 | 0.84075 | 0.84075 | 0.84075 | 0.84075 | 0.84075 | 0.84075 | 0.84075 | 0.84381 | 0.84758 | 0.87654 | 0.93452 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.93326 | 0.94159 | 0.97687 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-02 01:52 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.79715 | 0.80466 | 0.83543 | 0.9084 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79598 | 0.79826 | 0.80589 | 0.83724 | 0.91049 | 0.83982 | 0.83982 | 0.83982 | 0.83982 | 0.83982 | 0.83982 | 0.83982 | 0.8428 | 0.84652 | 0.87654 | 0.93452 | 0.93047 | 0.93047 | 0.93047 | 0.93047 | 0.93047 | 0.93047 | 0.93047 | 0.93047 | 0.93047 | 0.94159 | 0.97687 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-03 02:21 | 0.79435 | 0.79435 | 0.79435 | 0.79435 | 0.79435 | 0.79435 | 0.79435 | 0.79661 | 0.80404 | 0.83452 | 0.9084 | 0.79545 | 0.79545 | 0.79545 | 0.79545 | 0.79545 | 0.79545 | 0.79545 | 0.79772 | 0.80526 | 0.83631 | 0.91049 | 0.83886 | 0.83886 | 0.83886 | 0.83886 | 0.83886 | 0.83886 | 0.83886 | 0.84185 | 0.84553 | 0.87512 | 0.93452 | 0.92786 | 0.92786 | 0.92786 | 0.92786 | 0.92786 | 0.92786 | 0.92786 | 0.92786 | 0.92786 | 0.93853 | 0.97687 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-04 02:54 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79605 | 0.80343 | 0.83366 | 0.9084 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.7949 | 0.79715 | 0.80466 | 0.83543 | 0.91049 | 0.83795 | 0.83795 | 0.83795 | 0.83795 | 0.83795 | 0.83795 | 0.83795 | 0.84087 | 0.8445 | 0.87366 | 0.93452 | 0.92522 | 0.92522 | 0.92522 | 0.92522 | 0.92522 | 0.92522 | 0.92522 | 0.92522 | 0.92522 | 0.93568 | 0.97687 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 0.98248 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-05 03:17 | 0.79329 | 0.79329 | 0.79329 | 0.79329 | 0.79329 | 0.79329 | 0.79329 | 0.79552 | 0.80284 | 0.83277 | 0.9084 | 0.79438 | 0.79438 | 0.79438 | 0.79438 | 0.79438 | 0.79438 | 0.79438 | 0.79661 | 0.80404 | 0.83456 | 0.91049 | 0.83702 | 0.83702 | 0.83702 | 0.83702 | 0.83702 | 0.83702 | 0.83702 | 0.83994 | 0.84353 | 0.87228 | 0.93452 | 0.92276 | 0.92276 | 0.92276 | 0.92276 | 0.92276 | 0.92276 | 0.92276 | 0.92276 | 0.92276 | 0.93281 | 0.97687 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-06 03:39 | 0.79278 | 0.79278 | 0.79278 | 0.79278 | 0.79278 | 0.79278 | 0.79278 | 0.79497 | 0.80226 | 0.83193 | 0.90627 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79383 | 0.79605 | 0.80345 | 0.83366 | 0.9084 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83613 | 0.83898 | 0.84253 | 0.87093 | 0.9318 | 0.92037 | 0.92037 | 0.92037 | 0.92037 | 0.92037 | 0.92037 | 0.92037 | 0.92037 | 0.92037 | 0.93014 | 0.97262 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 0.97797 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-07 04:02 | 0.79227 | 0.79227 | 0.79227 | 0.79227 | 0.79227 | 0.79227 | 0.79227 | 0.79444 | 0.80166 | 0.83109 | 0.90627 | 0.79332 | 0.79332 | 0.79332 | 0.79332 | 0.79332 | 0.79332 | 0.79332 | 0.79552 | 0.80284 | 0.83281 | 0.9084 | 0.83521 | 0.83521 | 0.83521 | 0.83521 | 0.83521 | 0.83521 | 0.83521 | 0.83807 | 0.84157 | 0.86954 | 0.9318 | 0.91794 | 0.91794 | 0.91794 | 0.91794 | 0.91794 | 0.91794 | 0.91794 | 0.91794 | 0.91794 | 0.92743 | 0.97262 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 0.97349 | 1.0076 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-08 00:22 | 0.79182 | 0.79182 | 0.79182 | 0.79182 | 0.79182 | 0.79182 | 0.79182 | 0.79401 | 0.80118 | 0.83037 | 0.9046 | 0.79286 | 0.79286 | 0.79286 | 0.79286 | 0.79286 | 0.79286 | 0.79286 | 0.79508 | 0.80236 | 0.83207 | 0.90661 | 0.83449 | 0.83449 | 0.83449 | 0.83449 | 0.83449 | 0.83449 | 0.83449 | 0.83732 | 0.84079 | 0.86845 | 0.92959 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.92533 | 0.96904 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 1.0027 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-09 00:56 | 0.79132 | 0.79132 | 0.79132 | 0.79132 | 0.79132 | 0.79132 | 0.79132 | 0.79347 | 0.80059 | 0.82955 | 0.9046 | 0.79235 | 0.79235 | 0.79235 | 0.79235 | 0.79235 | 0.79235 | 0.79235 | 0.79453 | 0.80178 | 0.83123 | 0.90661 | 0.83359 | 0.83359 | 0.83359 | 0.83359 | 0.83359 | 0.83359 | 0.83359 | 0.83639 | 0.83982 | 0.8671 | 0.92959 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.92533 | 0.96904 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 1.0027 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-10 00:22 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79297 | 0.80005 | 0.82874 | 0.9046 | 0.79185 | 0.79185 | 0.79185 | 0.79185 | 0.79185 | 0.79185 | 0.79185 | 0.79403 | 0.80121 | 0.8304 | 0.90661 | 0.83277 | 0.83277 | 0.83277 | 0.83277 | 0.83277 | 0.83277 | 0.83277 | 0.83554 | 0.83894 | 0.86588 | 0.92959 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.91604 | 0.92533 | 0.96904 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 0.97005 | 1.0027 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-11 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79246 | 0.79949 | 0.82797 | 0.90264 | 0.79136 | 0.79136 | 0.79136 | 0.79136 | 0.79136 | 0.79136 | 0.79136 | 0.79351 | 0.80066 | 0.82962 | 0.90469 | 0.83193 | 0.83193 | 0.83193 | 0.83193 | 0.83193 | 0.83193 | 0.83193 | 0.83467 | 0.83803 | 0.86463 | 0.92701 | 0.91381 | 0.91381 | 0.91381 | 0.91381 | 0.91381 | 0.91381 | 0.91381 | 0.91381 | 0.91381 | 0.92286 | 0.96528 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.96608 | 0.99721 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-12 00:39 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.79193 | 0.79893 | 0.82714 | 0.90073 | 0.79084 | 0.79084 | 0.79084 | 0.79084 | 0.79084 | 0.79084 | 0.79084 | 0.79297 | 0.80007 | 0.82877 | 0.90264 | 0.83109 | 0.83109 | 0.83109 | 0.83109 | 0.83109 | 0.83109 | 0.83109 | 0.83377 | 0.83709 | 0.86339 | 0.9244 | 0.91164 | 0.91164 | 0.91164 | 0.91164 | 0.91164 | 0.91164 | 0.91164 | 0.91164 | 0.91164 | 0.92046 | 0.96135 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.96228 | 0.99176 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-12 04:41 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.79185 | 0.79884 | 0.82701 | 0.90073 | 0.79076 | 0.79076 | 0.79076 | 0.79076 | 0.79076 | 0.79076 | 0.79076 | 0.79289 | 0.79998 | 0.82864 | 0.90264 | 0.83095 | 0.83095 | 0.83095 | 0.83095 | 0.83095 | 0.83095 | 0.83095 | 0.83363 | 0.83694 | 0.86318 | 0.9244 | 0.91129 | 0.91129 | 0.91129 | 0.91129 | 0.91129 | 0.91129 | 0.91129 | 0.91129 | 0.91129 | 0.92007 | 0.96135 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.99176 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-13 01:08 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.79142 | 0.79836 | 0.82635 | 0.89908 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79034 | 0.79246 | 0.79949 | 0.82797 | 0.90104 | 0.83023 | 0.83023 | 0.83023 | 0.83023 | 0.83023 | 0.83023 | 0.83023 | 0.83291 | 0.8362 | 0.86212 | 0.92236 | 0.90944 | 0.90944 | 0.90944 | 0.90944 | 0.90944 | 0.90944 | 0.90944 | 0.90944 | 0.90944 | 0.91803 | 0.95832 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.99176 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-14 01:30 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.79092 | 0.79781 | 0.82554 | 0.89724 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.79195 | 0.79893 | 0.82714 | 0.89908 | 0.82941 | 0.82941 | 0.82941 | 0.82941 | 0.82941 | 0.82941 | 0.82941 | 0.83207 | 0.83532 | 0.86092 | 0.91997 | 0.90737 | 0.90737 | 0.90737 | 0.90737 | 0.90737 | 0.90737 | 0.90737 | 0.90737 | 0.90737 | 0.91576 | 0.95466 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.99176 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-15 01:52 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.7904 | 0.79726 | 0.82477 | 0.89724 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.79142 | 0.79838 | 0.82635 | 0.89908 | 0.8286 | 0.8286 | 0.8286 | 0.8286 | 0.8286 | 0.8286 | 0.8286 | 0.8312 | 0.83442 | 0.85968 | 0.91997 | 0.90527 | 0.90527 | 0.90527 | 0.90527 | 0.90527 | 0.90527 | 0.90527 | 0.90527 | 0.90527 | 0.91354 | 0.95466 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.99176 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-16 02:15 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78991 | 0.7967 | 0.82397 | 0.89537 | 0.78885 | 0.78885 | 0.78885 | 0.78885 | 0.78885 | 0.78885 | 0.78885 | 0.79092 | 0.79781 | 0.82557 | 0.89724 | 0.82777 | 0.82777 | 0.82777 | 0.82777 | 0.82777 | 0.82777 | 0.82777 | 0.83037 | 0.83355 | 0.85852 | 0.91755 | 0.90329 | 0.90329 | 0.90329 | 0.90329 | 0.90329 | 0.90329 | 0.90329 | 0.90329 | 0.90329 | 0.91129 | 0.95129 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.96166 | 0.99176 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0148 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277 | 1.0277
2005-08-17 01:36 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78942 | 0.79618 | 0.82324 | 0.89537 | 0.78836 | 0.78836 | 0.78836 | 0.78836 | 0.78836 | 0.78836 | 0.78836 | 0.79044 | 0.79729 | 0.8248 | 0.89724 | 0.82701 | 0.82701 | 0.82701 | 0.82701 | 0.82701 | 0.82701 | 0.82701 | 0.82958 | 0.8327 | 0.85741 | 0.91755 | 0.90144 | 0.90144 | 0.90144 | 0.90144 | 0.90144 | 0.90144 | 0.90144 | 0.90144 | 0.90144 | 0.90926 | 0.95129 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.95802 | 0.99176 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0089 | 1.0277 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-18 02:09 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.78893 | 0.79563 | 0.82249 | 0.8936 | 0.78788 | 0.78788 | 0.78788 | 0.78788 | 0.78788 | 0.78788 | 0.78788 | 0.78993 | 0.79672 | 0.82403 | 0.89537 | 0.82619 | 0.82619 | 0.82619 | 0.82619 | 0.82619 | 0.82619 | 0.82619 | 0.82874 | 0.83186 | 0.85623 | 0.91529 | 0.89947 | 0.89947 | 0.89947 | 0.89947 | 0.89947 | 0.89947 | 0.89947 | 0.89947 | 0.89947 | 0.90711 | 0.94789 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-19 02:43 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78842 | 0.7951 | 0.82172 | 0.8936 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78738 | 0.78942 | 0.79618 | 0.82324 | 0.89537 | 0.82541 | 0.82541 | 0.82541 | 0.82541 | 0.82541 | 0.82541 | 0.82541 | 0.8279 | 0.83099 | 0.85506 | 0.91529 | 0.89762 | 0.89762 | 0.89762 | 0.89762 | 0.89762 | 0.89762 | 0.89762 | 0.89762 | 0.89762 | 0.9051 | 0.94789 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-20 03:11 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78794 | 0.79455 | 0.82095 | 0.8918 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.7869 | 0.78893 | 0.79563 | 0.82249 | 0.8936 | 0.82461 | 0.82461 | 0.82461 | 0.82461 | 0.82461 | 0.82461 | 0.82461 | 0.82711 | 0.83016 | 0.85396 | 0.91299 | 0.89574 | 0.89574 | 0.89574 | 0.89574 | 0.89574 | 0.89574 | 0.89574 | 0.89574 | 0.89574 | 0.90305 | 0.94475 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.95452 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-21 03:34 | 0.78545 | 0.78545 | 0.78545 | 0.78545 | 0.78545 | 0.78545 | 0.78545 | 0.78744 | 0.79403 | 0.82022 | 0.8918 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78641 | 0.78844 | 0.7951 | 0.82172 | 0.8936 | 0.82384 | 0.82384 | 0.82384 | 0.82384 | 0.82384 | 0.82384 | 0.82384 | 0.82632 | 0.82931 | 0.85287 | 0.91299 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.89397 | 0.90112 | 0.94475 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-22 03:56 | 0.78499 | 0.78499 | 0.78499 | 0.78499 | 0.78499 | 0.78499 | 0.78499 | 0.78696 | 0.79349 | 0.8195 | 0.8918 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78594 | 0.78794 | 0.79457 | 0.82098 | 0.8936 | 0.82306 | 0.82306 | 0.82306 | 0.82306 | 0.82306 | 0.82306 | 0.82306 | 0.82551 | 0.8285 | 0.85175 | 0.91299 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89924 | 0.94475 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-23 00:11 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.78657 | 0.79306 | 0.8195 | 0.8918 | 0.78555 | 0.78555 | 0.78555 | 0.78555 | 0.78555 | 0.78555 | 0.78555 | 0.78754 | 0.79411 | 0.82098 | 0.8936 | 0.82243 | 0.82243 | 0.82243 | 0.82243 | 0.82243 | 0.82243 | 0.82243 | 0.82486 | 0.82783 | 0.85175 | 0.91299 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89216 | 0.89924 | 0.94475 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-24 00:45 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78608 | 0.79254 | 0.81875 | 0.8901 | 0.78506 | 0.78506 | 0.78506 | 0.78506 | 0.78506 | 0.78506 | 0.78506 | 0.78704 | 0.7936 | 0.82022 | 0.8918 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82169 | 0.82407 | 0.82701 | 0.85068 | 0.91084 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89045 | 0.89732 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-25 01:19 | 0.78365 | 0.78365 | 0.78365 | 0.78365 | 0.78365 | 0.78365 | 0.78365 | 0.78561 | 0.79201 | 0.81804 | 0.8901 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.7846 | 0.78657 | 0.79306 | 0.8195 | 0.8918 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82092 | 0.82331 | 0.82622 | 0.84959 | 0.91084 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.89544 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-26 01:36 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78512 | 0.79151 | 0.81731 | 0.8901 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.78412 | 0.7861 | 0.79254 | 0.81875 | 0.8918 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82019 | 0.82256 | 0.82541 | 0.84856 | 0.91084 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.89544 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-27 02:15 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78466 | 0.79099 | 0.81661 | 0.8901 | 0.78367 | 0.78367 | 0.78367 | 0.78367 | 0.78367 | 0.78367 | 0.78367 | 0.78561 | 0.79201 | 0.81804 | 0.8918 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.82178 | 0.82464 | 0.84749 | 0.91084 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.89544 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-28 02:38 | 0.78228 | 0.78228 | 0.78228 | 0.78228 | 0.78228 | 0.78228 | 0.78228 | 0.78418 | 0.79049 | 0.81589 | 0.88837 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78319 | 0.78514 | 0.79151 | 0.81731 | 0.8901 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.81944 | 0.82178 | 0.82464 | 0.84749 | 0.91084 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.88872 | 0.89544 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-29 03:06 | 0.78183 | 0.78183 | 0.78183 | 0.78183 | 0.78183 | 0.78183 | 0.78183 | 0.78372 | 0.78997 | 0.81589 | 0.88837 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78274 | 0.78466 | 0.79099 | 0.81731 | 0.8901 | 0.81872 | 0.81872 | 0.81872 | 0.81872 | 0.81872 | 0.81872 | 0.81872 | 0.82101 | 0.82384 | 0.84749 | 0.91084 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.88708 | 0.89544 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-30 01:30 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78331 | 0.78952 | 0.81527 | 0.88837 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78424 | 0.79053 | 0.81667 | 0.8901 | 0.81804 | 0.81804 | 0.81804 | 0.81804 | 0.81804 | 0.81804 | 0.81804 | 0.82034 | 0.82315 | 0.84657 | 0.91084 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.89382 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-08-31 02:54 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78282 | 0.78899 | 0.81456 | 0.88668 | 0.78185 | 0.78185 | 0.78185 | 0.78185 | 0.78185 | 0.78185 | 0.78185 | 0.78374 | 0.79001 | 0.81595 | 0.88837 | 0.81731 | 0.81731 | 0.81731 | 0.81731 | 0.81731 | 0.81731 | 0.81731 | 0.81959 | 0.82237 | 0.84549 | 0.90857 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.88554 | 0.89382 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-01 02:21 | 0.78051 | 0.78051 | 0.78051 | 0.78051 | 0.78051 | 0.78051 | 0.78051 | 0.78239 | 0.78852 | 0.81456 | 0.88668 | 0.78142 | 0.78142 | 0.78142 | 0.78142 | 0.78142 | 0.78142 | 0.78142 | 0.78331 | 0.78952 | 0.81595 | 0.88837 | 0.81661 | 0.81661 | 0.81661 | 0.81661 | 0.81661 | 0.81661 | 0.81661 | 0.81887 | 0.82163 | 0.84549 | 0.90857 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.89382 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-02 02:43 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78192 | 0.78804 | 0.81386 | 0.88668 | 0.78097 | 0.78097 | 0.78097 | 0.78097 | 0.78097 | 0.78097 | 0.78097 | 0.78284 | 0.78903 | 0.81524 | 0.88837 | 0.81592 | 0.81592 | 0.81592 | 0.81592 | 0.81592 | 0.81592 | 0.81592 | 0.81816 | 0.82089 | 0.8445 | 0.90857 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.88403 | 0.89382 | 0.94159 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-03 03:11 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.78148 | 0.78754 | 0.81319 | 0.88508 | 0.78053 | 0.78053 | 0.78053 | 0.78053 | 0.78053 | 0.78053 | 0.78053 | 0.78239 | 0.78852 | 0.81456 | 0.88668 | 0.81524 | 0.81524 | 0.81524 | 0.81524 | 0.81524 | 0.81524 | 0.81524 | 0.81743 | 0.82013 | 0.84353 | 0.90652 | 0.88241 | 0.88241 | 0.88241 | 0.88241 | 0.88241 | 0.88241 | 0.88241 | 0.88241 | 0.88241 | 0.89209 | 0.93865 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.95101 | 0.98681 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-04 03:34 | 0.77919 | 0.77919 | 0.77919 | 0.77919 | 0.77919 | 0.77919 | 0.77919 | 0.78102 | 0.78706 | 0.8125 | 0.88344 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78007 | 0.78194 | 0.78804 | 0.81386 | 0.88508 | 0.81453 | 0.81453 | 0.81453 | 0.81453 | 0.81453 | 0.81453 | 0.81453 | 0.81673 | 0.81941 | 0.84253 | 0.90444 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.89031 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-05 03:56 | 0.77876 | 0.77876 | 0.77876 | 0.77876 | 0.77876 | 0.77876 | 0.77876 | 0.78058 | 0.78657 | 0.8125 | 0.88344 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.77964 | 0.78148 | 0.78756 | 0.81386 | 0.88508 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81386 | 0.81604 | 0.81866 | 0.84253 | 0.90444 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.89031 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-06 00:11 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.78022 | 0.78617 | 0.8125 | 0.88344 | 0.77928 | 0.77928 | 0.77928 | 0.77928 | 0.77928 | 0.77928 | 0.77928 | 0.78111 | 0.78714 | 0.81386 | 0.88508 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.81544 | 0.81807 | 0.84253 | 0.90444 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.89031 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-07 00:45 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.78022 | 0.78617 | 0.8125 | 0.88344 | 0.77883 | 0.77883 | 0.77883 | 0.77883 | 0.77883 | 0.77883 | 0.77883 | 0.78111 | 0.78714 | 0.81386 | 0.88508 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.8133 | 0.81544 | 0.81807 | 0.84253 | 0.90444 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.88089 | 0.89031 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-08 01:02 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77978 | 0.7857 | 0.81184 | 0.88344 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.77841 | 0.78067 | 0.78667 | 0.81319 | 0.88508 | 0.81261 | 0.81261 | 0.81261 | 0.81261 | 0.81261 | 0.81261 | 0.81261 | 0.81475 | 0.81737 | 0.84157 | 0.90444 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.88865 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-09 02:32 | 0.77709 | 0.77709 | 0.77709 | 0.77709 | 0.77709 | 0.77709 | 0.77709 | 0.77932 | 0.7852 | 0.81114 | 0.88184 | 0.77795 | 0.77795 | 0.77795 | 0.77795 | 0.77795 | 0.77795 | 0.77795 | 0.7802 | 0.78617 | 0.8125 | 0.88338 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81192 | 0.81405 | 0.81661 | 0.84056 | 0.9024 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.88865 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-10 02:54 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77889 | 0.78474 | 0.81049 | 0.88026 | 0.77753 | 0.77753 | 0.77753 | 0.77753 | 0.77753 | 0.77753 | 0.77753 | 0.77977 | 0.78569 | 0.81181 | 0.88184 | 0.81125 | 0.81125 | 0.81125 | 0.81125 | 0.81125 | 0.81125 | 0.81125 | 0.81335 | 0.81592 | 0.83963 | 0.90049 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.8794 | 0.88865 | 0.93568 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-11 03:17 | 0.77624 | 0.77624 | 0.77624 | 0.77624 | 0.77624 | 0.77624 | 0.77624 | 0.77844 | 0.78428 | 0.80985 | 0.87878 | 0.77711 | 0.77711 | 0.77711 | 0.77711 | 0.77711 | 0.77711 | 0.77711 | 0.77932 | 0.78522 | 0.81116 | 0.88026 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.8106 | 0.81269 | 0.81524 | 0.83871 | 0.89854 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.88701 | 0.93292 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-12 03:34 | 0.77583 | 0.77583 | 0.77583 | 0.77583 | 0.77583 | 0.77583 | 0.77583 | 0.77802 | 0.7838 | 0.80919 | 0.87732 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77668 | 0.77889 | 0.78476 | 0.81052 | 0.87878 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.81201 | 0.81453 | 0.83777 | 0.89671 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.88701 | 0.93292 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-13 01:58 | 0.77546 | 0.77546 | 0.77546 | 0.77546 | 0.77546 | 0.77546 | 0.77546 | 0.77763 | 0.78338 | 0.80861 | 0.87732 | 0.7763 | 0.7763 | 0.7763 | 0.7763 | 0.7763 | 0.7763 | 0.7763 | 0.7785 | 0.78431 | 0.8099 | 0.87878 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.81201 | 0.81453 | 0.83777 | 0.89671 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.88701 | 0.93292 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-14 01:24 | 0.77505 | 0.77505 | 0.77505 | 0.77505 | 0.77505 | 0.77505 | 0.77505 | 0.77721 | 0.78295 | 0.80801 | 0.87588 | 0.77588 | 0.77588 | 0.77588 | 0.77588 | 0.77588 | 0.77588 | 0.77588 | 0.77807 | 0.78388 | 0.8093 | 0.87738 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.80932 | 0.81138 | 0.81388 | 0.83691 | 0.89492 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.88701 | 0.93292 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-15 01:41 | 0.77464 | 0.77464 | 0.77464 | 0.77464 | 0.77464 | 0.77464 | 0.77464 | 0.7768 | 0.78248 | 0.80737 | 0.87588 | 0.77547 | 0.77547 | 0.77547 | 0.77547 | 0.77547 | 0.77547 | 0.77547 | 0.77765 | 0.7834 | 0.80864 | 0.87738 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.80869 | 0.81073 | 0.81322 | 0.83602 | 0.89492 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.87786 | 0.88701 | 0.93292 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.94776 | 0.9819 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-16 02:04 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77638 | 0.78203 | 0.80675 | 0.87447 | 0.77507 | 0.77507 | 0.77507 | 0.77507 | 0.77507 | 0.77507 | 0.77507 | 0.77723 | 0.78295 | 0.80801 | 0.87588 | 0.80807 | 0.80807 | 0.80807 | 0.80807 | 0.80807 | 0.80807 | 0.80807 | 0.81006 | 0.81253 | 0.8351 | 0.89317 | 0.87642 | 0.87642 | 0.87642 | 0.87642 | 0.87642 | 0.87642 | 0.87642 | 0.87642 | 0.87642 | 0.88534 | 0.93025 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-17 02:21 | 0.77382 | 0.77382 | 0.77382 | 0.77382 | 0.77382 | 0.77382 | 0.77382 | 0.77595 | 0.78159 | 0.80675 | 0.87447 | 0.77466 | 0.77466 | 0.77466 | 0.77466 | 0.77466 | 0.77466 | 0.77466 | 0.7768 | 0.7825 | 0.80801 | 0.87588 | 0.80742 | 0.80742 | 0.80742 | 0.80742 | 0.80742 | 0.80742 | 0.80742 | 0.80943 | 0.81187 | 0.8351 | 0.89317 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.88534 | 0.93025 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-18 02:43 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77554 | 0.78113 | 0.80614 | 0.87447 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77424 | 0.77638 | 0.78203 | 0.80739 | 0.87588 | 0.8068 | 0.8068 | 0.8068 | 0.8068 | 0.8068 | 0.8068 | 0.8068 | 0.8088 | 0.81122 | 0.83424 | 0.89317 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.87354 | 0.88377 | 0.93025 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-19 03:11 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77512 | 0.78069 | 0.80551 | 0.87447 | 0.77384 | 0.77384 | 0.77384 | 0.77384 | 0.77384 | 0.77384 | 0.77384 | 0.77597 | 0.78159 | 0.80675 | 0.87588 | 0.80619 | 0.80619 | 0.80619 | 0.80619 | 0.80619 | 0.80619 | 0.80619 | 0.80814 | 0.81055 | 0.83334 | 0.89317 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.88216 | 0.93025 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-20 03:28 | 0.77262 | 0.77262 | 0.77262 | 0.77262 | 0.77262 | 0.77262 | 0.77262 | 0.77471 | 0.78024 | 0.80491 | 0.87308 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77342 | 0.77554 | 0.78115 | 0.80614 | 0.87447 | 0.80556 | 0.80556 | 0.80556 | 0.80556 | 0.80556 | 0.80556 | 0.80556 | 0.80752 | 0.8099 | 0.83249 | 0.89144 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.88216 | 0.93025 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-21 03:45 | 0.77222 | 0.77222 | 0.77222 | 0.77222 | 0.77222 | 0.77222 | 0.77222 | 0.77431 | 0.7798 | 0.80431 | 0.87308 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77303 | 0.77513 | 0.78069 | 0.80554 | 0.87447 | 0.80496 | 0.80496 | 0.80496 | 0.80496 | 0.80496 | 0.80496 | 0.80496 | 0.80691 | 0.80927 | 0.83165 | 0.89144 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.87217 | 0.88216 | 0.93025 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-22 03:17 | 0.77183 | 0.77183 | 0.77183 | 0.77183 | 0.77183 | 0.77183 | 0.77183 | 0.77391 | 0.77939 | 0.80372 | 0.87172 | 0.77265 | 0.77265 | 0.77265 | 0.77265 | 0.77265 | 0.77265 | 0.77265 | 0.77473 | 0.78027 | 0.80493 | 0.87314 | 0.80436 | 0.80436 | 0.80436 | 0.80436 | 0.80436 | 0.80436 | 0.80436 | 0.80629 | 0.80864 | 0.83082 | 0.88976 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.8807 | 0.92765 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-23 03:45 | 0.77145 | 0.77145 | 0.77145 | 0.77145 | 0.77145 | 0.77145 | 0.77145 | 0.77351 | 0.77894 | 0.80313 | 0.87172 | 0.77224 | 0.77224 | 0.77224 | 0.77224 | 0.77224 | 0.77224 | 0.77224 | 0.77433 | 0.77982 | 0.80434 | 0.87314 | 0.80377 | 0.80377 | 0.80377 | 0.80377 | 0.80377 | 0.80377 | 0.80377 | 0.80569 | 0.80801 | 0.82999 | 0.88976 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.87082 | 0.8807 | 0.92765 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-24 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77318 | 0.77859 | 0.80262 | 0.87172 | 0.77192 | 0.77192 | 0.77192 | 0.77192 | 0.77192 | 0.77192 | 0.77192 | 0.77399 | 0.77946 | 0.80382 | 0.87314 | 0.80328 | 0.80328 | 0.80328 | 0.80328 | 0.80328 | 0.80328 | 0.80328 | 0.80516 | 0.80747 | 0.82931 | 0.88976 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.8794 | 0.92765 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-25 00:28 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77276 | 0.77816 | 0.80204 | 0.87037 | 0.77151 | 0.77151 | 0.77151 | 0.77151 | 0.77151 | 0.77151 | 0.77151 | 0.77357 | 0.77903 | 0.80323 | 0.87172 | 0.80267 | 0.80267 | 0.80267 | 0.80267 | 0.80267 | 0.80267 | 0.80267 | 0.80456 | 0.80685 | 0.82847 | 0.8881 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.86971 | 0.8794 | 0.92765 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-26 00:56 | 0.77034 | 0.77034 | 0.77034 | 0.77034 | 0.77034 | 0.77034 | 0.77034 | 0.77237 | 0.77772 | 0.80144 | 0.869 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77112 | 0.77318 | 0.77859 | 0.80265 | 0.87037 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80209 | 0.80397 | 0.80622 | 0.82767 | 0.88641 | 0.8684 | 0.8684 | 0.8684 | 0.8684 | 0.8684 | 0.8684 | 0.8684 | 0.8684 | 0.8684 | 0.87793 | 0.92512 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-27 01:24 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77196 | 0.7773 | 0.80087 | 0.869 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77072 | 0.77276 | 0.77816 | 0.80204 | 0.87037 | 0.80149 | 0.80149 | 0.80149 | 0.80149 | 0.80149 | 0.80149 | 0.80149 | 0.80335 | 0.80561 | 0.82684 | 0.88641 | 0.86705 | 0.86705 | 0.86705 | 0.86705 | 0.86705 | 0.86705 | 0.86705 | 0.86705 | 0.86705 | 0.87648 | 0.92512 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.94462 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-28 03:56 | 0.76953 | 0.76953 | 0.76953 | 0.76953 | 0.76953 | 0.76953 | 0.76953 | 0.77154 | 0.77683 | 0.80024 | 0.869 | 0.77031 | 0.77031 | 0.77031 | 0.77031 | 0.77031 | 0.77031 | 0.77031 | 0.77234 | 0.77769 | 0.8014 | 0.87037 | 0.80087 | 0.80087 | 0.80087 | 0.80087 | 0.80087 | 0.80087 | 0.80087 | 0.8027 | 0.80493 | 0.82599 | 0.88641 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.87488 | 0.92512 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-29 00:11 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.7712 | 0.77649 | 0.79977 | 0.869 | 0.76999 | 0.76999 | 0.76999 | 0.76999 | 0.76999 | 0.76999 | 0.76999 | 0.772 | 0.77734 | 0.80092 | 0.87037 | 0.8004 | 0.8004 | 0.8004 | 0.8004 | 0.8004 | 0.8004 | 0.8004 | 0.80221 | 0.80444 | 0.82531 | 0.88641 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.87488 | 0.92512 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-09-30 00:34 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.77082 | 0.77606 | 0.79921 | 0.86769 | 0.7696 | 0.7696 | 0.7696 | 0.7696 | 0.7696 | 0.7696 | 0.7696 | 0.77161 | 0.77692 | 0.80035 | 0.869 | 0.79982 | 0.79982 | 0.79982 | 0.79982 | 0.79982 | 0.79982 | 0.79982 | 0.80164 | 0.80384 | 0.82454 | 0.88481 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.86567 | 0.87488 | 0.92512 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-01 00:56 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.77043 | 0.77565 | 0.79863 | 0.86636 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.76922 | 0.77122 | 0.77649 | 0.79979 | 0.86769 | 0.79926 | 0.79926 | 0.79926 | 0.79926 | 0.79926 | 0.79926 | 0.79926 | 0.80106 | 0.80323 | 0.82378 | 0.88325 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.87349 | 0.92256 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-02 01:24 | 0.76807 | 0.76807 | 0.76807 | 0.76807 | 0.76807 | 0.76807 | 0.76807 | 0.77004 | 0.77524 | 0.79808 | 0.86636 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.77082 | 0.77607 | 0.79921 | 0.86769 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.79868 | 0.80047 | 0.80265 | 0.82299 | 0.88325 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.86437 | 0.87349 | 0.92256 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.94121 | 0.97742 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-03 01:52 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.76966 | 0.77481 | 0.79751 | 0.86509 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.76845 | 0.77043 | 0.77565 | 0.79865 | 0.86636 | 0.79813 | 0.79813 | 0.79813 | 0.79813 | 0.79813 | 0.79813 | 0.79813 | 0.79991 | 0.80207 | 0.82224 | 0.88165 | 0.86313 | 0.86313 | 0.86313 | 0.86313 | 0.86313 | 0.86313 | 0.86313 | 0.86313 | 0.86313 | 0.87206 | 0.92017 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.97296 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-04 02:15 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76927 | 0.77441 | 0.79697 | 0.86385 | 0.76808 | 0.76808 | 0.76808 | 0.76808 | 0.76808 | 0.76808 | 0.76808 | 0.77004 | 0.77524 | 0.79808 | 0.86509 | 0.79758 | 0.79758 | 0.79758 | 0.79758 | 0.79758 | 0.79758 | 0.79758 | 0.79933 | 0.80147 | 0.82147 | 0.88014 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.87071 | 0.91784 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.97296 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-05 02:49 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76889 | 0.77399 | 0.79641 | 0.86385 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.7677 | 0.76966 | 0.77481 | 0.79753 | 0.86509 | 0.79701 | 0.79701 | 0.79701 | 0.79701 | 0.79701 | 0.79701 | 0.79701 | 0.79877 | 0.8009 | 0.82074 | 0.88014 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.86187 | 0.87071 | 0.91784 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.93829 | 0.97296 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-06 03:17 | 0.76657 | 0.76657 | 0.76657 | 0.76657 | 0.76657 | 0.76657 | 0.76657 | 0.7685 | 0.77359 | 0.79587 | 0.86385 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76733 | 0.76927 | 0.77441 | 0.79697 | 0.86509 | 0.79645 | 0.79645 | 0.79645 | 0.79645 | 0.79645 | 0.79645 | 0.79645 | 0.7982 | 0.80031 | 0.81998 | 0.88014 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86932 | 0.91784 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.97296 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-07 03:39 | 0.76621 | 0.76621 | 0.76621 | 0.76621 | 0.76621 | 0.76621 | 0.76621 | 0.76813 | 0.77318 | 0.79587 | 0.86385 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76695 | 0.76889 | 0.77399 | 0.79697 | 0.86509 | 0.79592 | 0.79592 | 0.79592 | 0.79592 | 0.79592 | 0.79592 | 0.79592 | 0.79765 | 0.79974 | 0.81998 | 0.88014 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86932 | 0.91784 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.97296 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-08 04:02 | 0.76585 | 0.76585 | 0.76585 | 0.76585 | 0.76585 | 0.76585 | 0.76585 | 0.76776 | 0.77278 | 0.79534 | 0.86385 | 0.76658 | 0.76658 | 0.76658 | 0.76658 | 0.76658 | 0.76658 | 0.76658 | 0.76852 | 0.77359 | 0.79643 | 0.86509 | 0.79539 | 0.79539 | 0.79539 | 0.79539 | 0.79539 | 0.79539 | 0.79539 | 0.79708 | 0.79916 | 0.81926 | 0.88014 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86067 | 0.86932 | 0.91784 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.97296 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0027 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-09 00:28 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76744 | 0.77245 | 0.79488 | 0.86385 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76819 | 0.77326 | 0.79596 | 0.86509 | 0.79492 | 0.79492 | 0.79492 | 0.79492 | 0.79492 | 0.79492 | 0.79492 | 0.79663 | 0.7987 | 0.81866 | 0.88014 | 0.85963 | 0.85963 | 0.85963 | 0.85963 | 0.85963 | 0.85963 | 0.85963 | 0.85963 | 0.85963 | 0.86823 | 0.91784 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.97296 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-10 00:51 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76707 | 0.77205 | 0.79488 | 0.86385 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76782 | 0.77285 | 0.79596 | 0.86509 | 0.7944 | 0.7944 | 0.7944 | 0.7944 | 0.7944 | 0.7944 | 0.7944 | 0.79609 | 0.79815 | 0.81866 | 0.88014 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.86823 | 0.91784 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.97296 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-11 01:24 | 0.76481 | 0.76481 | 0.76481 | 0.76481 | 0.76481 | 0.76481 | 0.76481 | 0.76669 | 0.77166 | 0.79435 | 0.86257 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76553 | 0.76744 | 0.77245 | 0.79543 | 0.8638 | 0.79385 | 0.79385 | 0.79385 | 0.79385 | 0.79385 | 0.79385 | 0.79385 | 0.79554 | 0.79758 | 0.81793 | 0.8786 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.86823 | 0.91784 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.97296 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-12 01:52 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76633 | 0.77125 | 0.79381 | 0.86137 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76518 | 0.76707 | 0.77205 | 0.79488 | 0.86257 | 0.79334 | 0.79334 | 0.79334 | 0.79334 | 0.79334 | 0.79334 | 0.79334 | 0.79501 | 0.79704 | 0.81719 | 0.87714 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.85847 | 0.86823 | 0.91784 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.93304 | 0.97296 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 0.99811 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-13 02:21 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76595 | 0.77087 | 0.79329 | 0.86137 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76669 | 0.77166 | 0.79435 | 0.86257 | 0.7928 | 0.7928 | 0.7928 | 0.7928 | 0.7928 | 0.7928 | 0.7928 | 0.79446 | 0.79647 | 0.8165 | 0.87714 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.86689 | 0.91784 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-14 02:54 | 0.76373 | 0.76373 | 0.76373 | 0.76373 | 0.76373 | 0.76373 | 0.76373 | 0.76559 | 0.77047 | 0.79276 | 0.86013 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76445 | 0.76633 | 0.77125 | 0.79381 | 0.86132 | 0.79229 | 0.79229 | 0.79229 | 0.79229 | 0.79229 | 0.79229 | 0.79229 | 0.79394 | 0.79592 | 0.81578 | 0.87565 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.85732 | 0.86689 | 0.91784 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-15 03:39 | 0.76337 | 0.76337 | 0.76337 | 0.76337 | 0.76337 | 0.76337 | 0.76337 | 0.76522 | 0.77007 | 0.79276 | 0.86013 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76408 | 0.76595 | 0.77085 | 0.79381 | 0.86132 | 0.79176 | 0.79176 | 0.79176 | 0.79176 | 0.79176 | 0.79176 | 0.79176 | 0.7934 | 0.79539 | 0.81578 | 0.87565 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.86689 | 0.91784 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-16 00:06 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76491 | 0.76975 | 0.79276 | 0.86013 | 0.76379 | 0.76379 | 0.76379 | 0.76379 | 0.76379 | 0.76379 | 0.76379 | 0.76565 | 0.77053 | 0.79381 | 0.86132 | 0.79134 | 0.79134 | 0.79134 | 0.79134 | 0.79134 | 0.79134 | 0.79134 | 0.79295 | 0.79492 | 0.81578 | 0.87565 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.86689 | 0.91784 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-17 00:28 | 0.76272 | 0.76272 | 0.76272 | 0.76272 | 0.76272 | 0.76272 | 0.76272 | 0.76455 | 0.76938 | 0.79225 | 0.85895 | 0.76343 | 0.76343 | 0.76343 | 0.76343 | 0.76343 | 0.76343 | 0.76343 | 0.76528 | 0.77015 | 0.79329 | 0.86013 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79082 | 0.79244 | 0.7944 | 0.81509 | 0.87424 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.86689 | 0.91784 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-18 00:56 | 0.76238 | 0.76238 | 0.76238 | 0.76238 | 0.76238 | 0.76238 | 0.76238 | 0.7642 | 0.76898 | 0.79225 | 0.85895 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76308 | 0.76492 | 0.76975 | 0.79329 | 0.86013 | 0.79032 | 0.79032 | 0.79032 | 0.79032 | 0.79032 | 0.79032 | 0.79032 | 0.79193 | 0.79385 | 0.81509 | 0.87424 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.85614 | 0.86689 | 0.91784 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.93025 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-19 00:22 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76385 | 0.76862 | 0.79174 | 0.85895 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76457 | 0.76939 | 0.79278 | 0.86013 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.78983 | 0.79142 | 0.79336 | 0.81444 | 0.87424 | 0.85502 | 0.85502 | 0.85502 | 0.85502 | 0.85502 | 0.85502 | 0.85502 | 0.85502 | 0.85502 | 0.86567 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-19 04:30 | 0.76198 | 0.76198 | 0.76198 | 0.76198 | 0.76198 | 0.76198 | 0.76198 | 0.76379 | 0.76855 | 0.79166 | 0.85895 | 0.76268 | 0.76268 | 0.76268 | 0.76268 | 0.76268 | 0.76268 | 0.76268 | 0.76451 | 0.76933 | 0.79269 | 0.86013 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.78974 | 0.79134 | 0.79327 | 0.81433 | 0.87424 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.86546 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-20 00:51 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.7635 | 0.76824 | 0.79124 | 0.85895 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76422 | 0.769 | 0.79227 | 0.86013 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.78933 | 0.79092 | 0.79284 | 0.81374 | 0.87424 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.86546 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-21 01:19 | 0.76134 | 0.76134 | 0.76134 | 0.76134 | 0.76134 | 0.76134 | 0.76134 | 0.76314 | 0.76787 | 0.79071 | 0.85775 | 0.76205 | 0.76205 | 0.76205 | 0.76205 | 0.76205 | 0.76205 | 0.76205 | 0.76385 | 0.76862 | 0.79176 | 0.85895 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.78883 | 0.7904 | 0.79231 | 0.81308 | 0.8728 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.85483 | 0.86546 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-22 01:47 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.76279 | 0.76748 | 0.79022 | 0.85775 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.76169 | 0.7635 | 0.76824 | 0.79124 | 0.85895 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78991 | 0.7918 | 0.81239 | 0.8728 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.86416 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-23 02:21 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76243 | 0.76712 | 0.7897 | 0.85661 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76314 | 0.76787 | 0.79071 | 0.85775 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78834 | 0.78991 | 0.7918 | 0.81239 | 0.8728 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.85373 | 0.86416 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-24 02:49 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76209 | 0.76674 | 0.7897 | 0.85661 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.76279 | 0.76748 | 0.79071 | 0.85775 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.78786 | 0.7894 | 0.79128 | 0.81239 | 0.8728 | 0.8526 | 0.8526 | 0.8526 | 0.8526 | 0.8526 | 0.8526 | 0.8526 | 0.8526 | 0.8526 | 0.86416 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-25 03:28 | 0.75997 | 0.75997 | 0.75997 | 0.75997 | 0.75997 | 0.75997 | 0.75997 | 0.76174 | 0.76636 | 0.78921 | 0.85661 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76065 | 0.76243 | 0.76712 | 0.79022 | 0.85775 | 0.78736 | 0.78736 | 0.78736 | 0.78736 | 0.78736 | 0.78736 | 0.78736 | 0.78891 | 0.79076 | 0.81173 | 0.8728 | 0.85152 | 0.85152 | 0.85152 | 0.85152 | 0.85152 | 0.85152 | 0.85152 | 0.85152 | 0.85152 | 0.86293 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-26 03:51 | 0.75964 | 0.75964 | 0.75964 | 0.75964 | 0.75964 | 0.75964 | 0.75964 | 0.7614 | 0.766 | 0.7887 | 0.85661 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76032 | 0.76209 | 0.76674 | 0.7897 | 0.85775 | 0.78686 | 0.78686 | 0.78686 | 0.78686 | 0.78686 | 0.78686 | 0.78686 | 0.7884 | 0.79026 | 0.81106 | 0.8728 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-27 00:34 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.7611 | 0.76568 | 0.7883 | 0.85661 | 0.76003 | 0.76003 | 0.76003 | 0.76003 | 0.76003 | 0.76003 | 0.76003 | 0.76179 | 0.76643 | 0.78929 | 0.85775 | 0.78647 | 0.78647 | 0.78647 | 0.78647 | 0.78647 | 0.78647 | 0.78647 | 0.78798 | 0.78983 | 0.81049 | 0.8728 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-28 01:08 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.76075 | 0.76532 | 0.7878 | 0.85543 | 0.75969 | 0.75969 | 0.75969 | 0.75969 | 0.75969 | 0.75969 | 0.75969 | 0.76145 | 0.76606 | 0.78878 | 0.85656 | 0.78598 | 0.78598 | 0.78598 | 0.78598 | 0.78598 | 0.78598 | 0.78598 | 0.7875 | 0.78933 | 0.80985 | 0.87144 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-29 01:47 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.76042 | 0.76495 | 0.7878 | 0.85543 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.75935 | 0.7611 | 0.76568 | 0.78878 | 0.85656 | 0.78551 | 0.78551 | 0.78551 | 0.78551 | 0.78551 | 0.78551 | 0.78551 | 0.787 | 0.78883 | 0.80985 | 0.87144 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-30 02:15 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.76007 | 0.7646 | 0.78732 | 0.85432 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.75902 | 0.76075 | 0.76532 | 0.7883 | 0.85543 | 0.78503 | 0.78503 | 0.78503 | 0.78503 | 0.78503 | 0.78503 | 0.78503 | 0.78653 | 0.78834 | 0.80919 | 0.87004 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-10-31 02:43 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75974 | 0.76423 | 0.78732 | 0.85432 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.75868 | 0.76042 | 0.76495 | 0.7883 | 0.85543 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78604 | 0.78784 | 0.80919 | 0.87004 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-01 03:22 | 0.75768 | 0.75768 | 0.75768 | 0.75768 | 0.75768 | 0.75768 | 0.75768 | 0.75939 | 0.76388 | 0.78682 | 0.85318 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.75835 | 0.76007 | 0.7646 | 0.7878 | 0.85428 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78456 | 0.78604 | 0.78784 | 0.80919 | 0.87004 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-02 03:51 | 0.75736 | 0.75736 | 0.75736 | 0.75736 | 0.75736 | 0.75736 | 0.75736 | 0.75906 | 0.76352 | 0.78633 | 0.85318 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75802 | 0.75974 | 0.76423 | 0.78732 | 0.85428 | 0.78409 | 0.78409 | 0.78409 | 0.78409 | 0.78409 | 0.78409 | 0.78409 | 0.78557 | 0.78736 | 0.80856 | 0.87004 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-03 00:17 | 0.75708 | 0.75708 | 0.75708 | 0.75708 | 0.75708 | 0.75708 | 0.75708 | 0.75878 | 0.76323 | 0.78594 | 0.85224 | 0.75775 | 0.75775 | 0.75775 | 0.75775 | 0.75775 | 0.75775 | 0.75775 | 0.75945 | 0.76394 | 0.7869 | 0.85336 | 0.78371 | 0.78371 | 0.78371 | 0.78371 | 0.78371 | 0.78371 | 0.78371 | 0.78516 | 0.78694 | 0.80804 | 0.86894 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.85042 | 0.86167 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-04 00:45 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75845 | 0.76287 | 0.78547 | 0.85224 | 0.75741 | 0.75741 | 0.75741 | 0.75741 | 0.75741 | 0.75741 | 0.75741 | 0.75912 | 0.76357 | 0.78643 | 0.85336 | 0.78323 | 0.78323 | 0.78323 | 0.78323 | 0.78323 | 0.78323 | 0.78323 | 0.7847 | 0.78647 | 0.80739 | 0.86894 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.86047 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-05 01:19 | 0.75643 | 0.75643 | 0.75643 | 0.75643 | 0.75643 | 0.75643 | 0.75643 | 0.75811 | 0.76252 | 0.78547 | 0.85224 | 0.75709 | 0.75709 | 0.75709 | 0.75709 | 0.75709 | 0.75709 | 0.75709 | 0.75878 | 0.76323 | 0.78643 | 0.85336 | 0.78278 | 0.78278 | 0.78278 | 0.78278 | 0.78278 | 0.78278 | 0.78278 | 0.78422 | 0.78598 | 0.80739 | 0.86894 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.86047 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-06 01:41 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75779 | 0.76216 | 0.78547 | 0.85224 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75676 | 0.75845 | 0.76287 | 0.78643 | 0.85336 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78231 | 0.78376 | 0.78551 | 0.80739 | 0.86894 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.86047 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-07 02:09 | 0.7558 | 0.7558 | 0.7558 | 0.7558 | 0.7558 | 0.7558 | 0.7558 | 0.75745 | 0.76182 | 0.78499 | 0.85224 | 0.75644 | 0.75644 | 0.75644 | 0.75644 | 0.75644 | 0.75644 | 0.75644 | 0.75812 | 0.76252 | 0.78594 | 0.85336 | 0.78187 | 0.78187 | 0.78187 | 0.78187 | 0.78187 | 0.78187 | 0.78187 | 0.78331 | 0.78503 | 0.80678 | 0.86894 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.86047 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-08 03:17 | 0.75546 | 0.75546 | 0.75546 | 0.75546 | 0.75546 | 0.75546 | 0.75546 | 0.75712 | 0.76147 | 0.78499 | 0.85224 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75611 | 0.75777 | 0.76216 | 0.78594 | 0.85336 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78141 | 0.78282 | 0.78454 | 0.80678 | 0.86894 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.84938 | 0.86047 | 0.91784 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.92775 | 0.97296 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-09 03:51 | 0.75515 | 0.75515 | 0.75515 | 0.75515 | 0.75515 | 0.75515 | 0.75515 | 0.7568 | 0.76112 | 0.78453 | 0.85117 | 0.75578 | 0.75578 | 0.75578 | 0.75578 | 0.75578 | 0.75578 | 0.75578 | 0.75745 | 0.76181 | 0.78547 | 0.85224 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78095 | 0.78237 | 0.78409 | 0.80614 | 0.86759 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.85924 | 0.91548 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-10 00:17 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75652 | 0.76083 | 0.78453 | 0.85117 | 0.75552 | 0.75552 | 0.75552 | 0.75552 | 0.75552 | 0.75552 | 0.75552 | 0.75717 | 0.76152 | 0.78547 | 0.85224 | 0.78058 | 0.78058 | 0.78058 | 0.78058 | 0.78058 | 0.78058 | 0.78058 | 0.78198 | 0.78369 | 0.80614 | 0.86759 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.8483 | 0.85924 | 0.91548 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-11 00:45 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.7562 | 0.76048 | 0.78405 | 0.85117 | 0.7552 | 0.7552 | 0.7552 | 0.7552 | 0.7552 | 0.7552 | 0.7552 | 0.75685 | 0.76117 | 0.78499 | 0.85224 | 0.78013 | 0.78013 | 0.78013 | 0.78013 | 0.78013 | 0.78013 | 0.78013 | 0.78153 | 0.78323 | 0.80554 | 0.86759 | 0.84728 | 0.84728 | 0.84728 | 0.84728 | 0.84728 | 0.84728 | 0.84728 | 0.84728 | 0.84728 | 0.85808 | 0.91548 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.92512 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-12 01:24 | 0.75424 | 0.75424 | 0.75424 | 0.75424 | 0.75424 | 0.75424 | 0.75424 | 0.75588 | 0.76015 | 0.78357 | 0.85117 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75487 | 0.75652 | 0.76083 | 0.78453 | 0.85224 | 0.77969 | 0.77969 | 0.77969 | 0.77969 | 0.77969 | 0.77969 | 0.77969 | 0.78108 | 0.78276 | 0.80491 | 0.86759 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-13 01:52 | 0.75394 | 0.75394 | 0.75394 | 0.75394 | 0.75394 | 0.75394 | 0.75394 | 0.75556 | 0.7598 | 0.78312 | 0.85117 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.75456 | 0.7562 | 0.76048 | 0.78405 | 0.85224 | 0.77925 | 0.77925 | 0.77925 | 0.77925 | 0.77925 | 0.77925 | 0.77925 | 0.78064 | 0.78231 | 0.80429 | 0.86759 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-14 02:15 | 0.75363 | 0.75363 | 0.75363 | 0.75363 | 0.75363 | 0.75363 | 0.75363 | 0.75524 | 0.75947 | 0.78312 | 0.85117 | 0.75426 | 0.75426 | 0.75426 | 0.75426 | 0.75426 | 0.75426 | 0.75426 | 0.75588 | 0.76015 | 0.78405 | 0.85224 | 0.77882 | 0.77882 | 0.77882 | 0.77882 | 0.77882 | 0.77882 | 0.77882 | 0.78018 | 0.78185 | 0.80429 | 0.86759 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-15 01:41 | 0.75333 | 0.75333 | 0.75333 | 0.75333 | 0.75333 | 0.75333 | 0.75333 | 0.75494 | 0.75914 | 0.78312 | 0.85117 | 0.75395 | 0.75395 | 0.75395 | 0.75395 | 0.75395 | 0.75395 | 0.75395 | 0.75558 | 0.75982 | 0.78405 | 0.85224 | 0.77839 | 0.77839 | 0.77839 | 0.77839 | 0.77839 | 0.77839 | 0.77839 | 0.77977 | 0.78142 | 0.80429 | 0.86759 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-16 02:21 | 0.75301 | 0.75301 | 0.75301 | 0.75301 | 0.75301 | 0.75301 | 0.75301 | 0.75462 | 0.75882 | 0.78312 | 0.85117 | 0.75364 | 0.75364 | 0.75364 | 0.75364 | 0.75364 | 0.75364 | 0.75364 | 0.75525 | 0.75949 | 0.78405 | 0.85224 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77797 | 0.77932 | 0.78097 | 0.80429 | 0.86759 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-17 01:47 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75432 | 0.75849 | 0.78267 | 0.85117 | 0.75334 | 0.75334 | 0.75334 | 0.75334 | 0.75334 | 0.75334 | 0.75334 | 0.75495 | 0.75916 | 0.78361 | 0.85224 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77755 | 0.77891 | 0.78055 | 0.80372 | 0.86759 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-18 02:26 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.754 | 0.75817 | 0.78222 | 0.85007 | 0.75302 | 0.75302 | 0.75302 | 0.75302 | 0.75302 | 0.75302 | 0.75302 | 0.75463 | 0.75883 | 0.78314 | 0.85117 | 0.77713 | 0.77713 | 0.77713 | 0.77713 | 0.77713 | 0.77713 | 0.77713 | 0.77846 | 0.78009 | 0.80311 | 0.8663 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-19 03:00 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75369 | 0.75783 | 0.78222 | 0.85007 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75272 | 0.75432 | 0.75849 | 0.78314 | 0.85117 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77804 | 0.77966 | 0.80311 | 0.8663 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-20 03:28 | 0.7518 | 0.7518 | 0.7518 | 0.7518 | 0.7518 | 0.7518 | 0.7518 | 0.75338 | 0.75783 | 0.78222 | 0.85007 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.75241 | 0.754 | 0.75849 | 0.78314 | 0.85117 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77804 | 0.77966 | 0.80311 | 0.8663 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-21 03:51 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.75307 | 0.75751 | 0.78176 | 0.84903 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.75369 | 0.75817 | 0.78269 | 0.85007 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77804 | 0.77966 | 0.80311 | 0.8663 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-22 00:34 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75281 | 0.75723 | 0.78139 | 0.84903 | 0.75185 | 0.75185 | 0.75185 | 0.75185 | 0.75185 | 0.75185 | 0.75185 | 0.75343 | 0.75788 | 0.78229 | 0.85007 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77804 | 0.77966 | 0.80311 | 0.8663 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-23 00:56 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75251 | 0.75691 | 0.78093 | 0.84796 | 0.75155 | 0.75155 | 0.75155 | 0.75155 | 0.75155 | 0.75155 | 0.75155 | 0.75312 | 0.75756 | 0.78185 | 0.84903 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.7776 | 0.77921 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-24 01:36 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.7522 | 0.75691 | 0.78093 | 0.84796 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75124 | 0.75281 | 0.75756 | 0.78185 | 0.84903 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.77628 | 0.7776 | 0.77921 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-25 01:58 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.7519 | 0.75657 | 0.78093 | 0.84796 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75095 | 0.75251 | 0.75723 | 0.78185 | 0.84903 | 0.77585 | 0.77585 | 0.77585 | 0.77585 | 0.77585 | 0.77585 | 0.77585 | 0.77718 | 0.77878 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-26 02:26 | 0.75005 | 0.75005 | 0.75005 | 0.75005 | 0.75005 | 0.75005 | 0.75005 | 0.75159 | 0.75626 | 0.78093 | 0.84796 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.75064 | 0.7522 | 0.75691 | 0.78185 | 0.84903 | 0.77544 | 0.77544 | 0.77544 | 0.77544 | 0.77544 | 0.77544 | 0.77544 | 0.77675 | 0.77834 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-27 02:49 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.75129 | 0.75626 | 0.78093 | 0.84796 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.75035 | 0.7519 | 0.75691 | 0.78185 | 0.84903 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77633 | 0.77834 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-28 03:22 | 0.74946 | 0.74946 | 0.74946 | 0.74946 | 0.74946 | 0.74946 | 0.74946 | 0.75099 | 0.75593 | 0.78049 | 0.84694 | 0.75006 | 0.75006 | 0.75006 | 0.75006 | 0.75006 | 0.75006 | 0.75006 | 0.75159 | 0.75657 | 0.78139 | 0.84796 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77502 | 0.77633 | 0.77834 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-29 04:02 | 0.74917 | 0.74917 | 0.74917 | 0.74917 | 0.74917 | 0.74917 | 0.74917 | 0.75069 | 0.75593 | 0.78049 | 0.84694 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.74976 | 0.75129 | 0.75657 | 0.78139 | 0.84796 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.7759 | 0.77834 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-11-30 00:34 | 0.74892 | 0.74892 | 0.74892 | 0.74892 | 0.74892 | 0.74892 | 0.74892 | 0.75044 | 0.75567 | 0.78011 | 0.84694 | 0.7495 | 0.7495 | 0.7495 | 0.7495 | 0.7495 | 0.7495 | 0.7495 | 0.75103 | 0.75631 | 0.781 | 0.84796 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.7759 | 0.77834 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-01 04:19 | 0.74859 | 0.74859 | 0.74859 | 0.74859 | 0.74859 | 0.74859 | 0.74859 | 0.7501 | 0.7553 | 0.78011 | 0.84694 | 0.74918 | 0.74918 | 0.74918 | 0.74918 | 0.74918 | 0.74918 | 0.74918 | 0.75069 | 0.75594 | 0.781 | 0.84796 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.77461 | 0.7759 | 0.77834 | 0.80253 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-02 00:51 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74985 | 0.75503 | 0.77975 | 0.84694 | 0.74893 | 0.74893 | 0.74893 | 0.74893 | 0.74893 | 0.74893 | 0.74893 | 0.75045 | 0.75567 | 0.78064 | 0.84796 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77556 | 0.77799 | 0.80202 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-03 01:13 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74955 | 0.75472 | 0.7793 | 0.84594 | 0.74864 | 0.74864 | 0.74864 | 0.74864 | 0.74864 | 0.74864 | 0.74864 | 0.75014 | 0.75535 | 0.7802 | 0.84694 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77426 | 0.77556 | 0.77799 | 0.80202 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-04 01:41 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74926 | 0.7544 | 0.7793 | 0.84594 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74835 | 0.74985 | 0.75504 | 0.7802 | 0.84694 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77513 | 0.77755 | 0.80202 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-05 02:09 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74897 | 0.75409 | 0.7793 | 0.84594 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74807 | 0.74956 | 0.75472 | 0.7802 | 0.84694 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77473 | 0.77713 | 0.80202 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-06 02:43 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.74868 | 0.75377 | 0.7793 | 0.84594 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74777 | 0.74926 | 0.75441 | 0.7802 | 0.84694 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77473 | 0.77713 | 0.80202 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-07 03:11 | 0.74692 | 0.74692 | 0.74692 | 0.74692 | 0.74692 | 0.74692 | 0.74692 | 0.74838 | 0.75347 | 0.77887 | 0.84594 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74749 | 0.74898 | 0.75409 | 0.77975 | 0.84694 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77344 | 0.77473 | 0.77713 | 0.80202 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-08 03:39 | 0.74663 | 0.74663 | 0.74663 | 0.74663 | 0.74663 | 0.74663 | 0.74663 | 0.7481 | 0.75315 | 0.77843 | 0.84594 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.7472 | 0.74868 | 0.75378 | 0.77932 | 0.84694 | 0.77304 | 0.77304 | 0.77304 | 0.77304 | 0.77304 | 0.77304 | 0.77304 | 0.77431 | 0.77669 | 0.80144 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-09 00:17 | 0.74639 | 0.74639 | 0.74639 | 0.74639 | 0.74639 | 0.74639 | 0.74639 | 0.74785 | 0.7529 | 0.77843 | 0.84594 | 0.74697 | 0.74697 | 0.74697 | 0.74697 | 0.74697 | 0.74697 | 0.74697 | 0.74843 | 0.75352 | 0.77932 | 0.84694 | 0.7727 | 0.7727 | 0.7727 | 0.7727 | 0.7727 | 0.7727 | 0.7727 | 0.77397 | 0.77635 | 0.80144 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-10 00:45 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74757 | 0.75258 | 0.77843 | 0.84594 | 0.74668 | 0.74668 | 0.74668 | 0.74668 | 0.74668 | 0.74668 | 0.74668 | 0.74815 | 0.7532 | 0.77932 | 0.84694 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77356 | 0.77592 | 0.80144 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-11 01:08 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74728 | 0.75228 | 0.778 | 0.84491 | 0.7464 | 0.7464 | 0.7464 | 0.7464 | 0.7464 | 0.7464 | 0.7464 | 0.74787 | 0.7529 | 0.77887 | 0.84594 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77231 | 0.77356 | 0.77592 | 0.80144 | 0.86499 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.84623 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-12 01:41 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.747 | 0.75197 | 0.778 | 0.84491 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74611 | 0.74757 | 0.7526 | 0.77887 | 0.84594 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.77316 | 0.77551 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-13 02:15 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74671 | 0.75167 | 0.77756 | 0.84491 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74728 | 0.75228 | 0.77844 | 0.84594 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.7719 | 0.77316 | 0.77551 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-14 02:54 | 0.745 | 0.745 | 0.745 | 0.745 | 0.745 | 0.745 | 0.745 | 0.74643 | 0.75137 | 0.77756 | 0.84491 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.74555 | 0.747 | 0.75197 | 0.77844 | 0.84594 | 0.77149 | 0.77149 | 0.77149 | 0.77149 | 0.77149 | 0.77149 | 0.77149 | 0.77275 | 0.77508 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-15 03:22 | 0.74472 | 0.74472 | 0.74472 | 0.74472 | 0.74472 | 0.74472 | 0.74472 | 0.74615 | 0.75137 | 0.77756 | 0.84491 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74528 | 0.74671 | 0.75197 | 0.77844 | 0.84594 | 0.77111 | 0.77111 | 0.77111 | 0.77111 | 0.77111 | 0.77111 | 0.77111 | 0.77236 | 0.77508 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-16 03:56 | 0.74445 | 0.74445 | 0.74445 | 0.74445 | 0.74445 | 0.74445 | 0.74445 | 0.74587 | 0.75107 | 0.77756 | 0.84491 | 0.745 | 0.745 | 0.745 | 0.745 | 0.745 | 0.745 | 0.745 | 0.74643 | 0.75167 | 0.77844 | 0.84594 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77195 | 0.77468 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-17 00:28 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74563 | 0.75081 | 0.77721 | 0.84409 | 0.74476 | 0.74476 | 0.74476 | 0.74476 | 0.74476 | 0.74476 | 0.74476 | 0.74619 | 0.75142 | 0.77807 | 0.84507 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77195 | 0.77468 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-18 00:56 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74536 | 0.75052 | 0.7768 | 0.84409 | 0.74449 | 0.74449 | 0.74449 | 0.74449 | 0.74449 | 0.74449 | 0.74449 | 0.74592 | 0.75112 | 0.77765 | 0.84507 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77071 | 0.77195 | 0.77468 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-19 01:24 | 0.74367 | 0.74367 | 0.74367 | 0.74367 | 0.74367 | 0.74367 | 0.74367 | 0.74508 | 0.75022 | 0.7768 | 0.84409 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74421 | 0.74563 | 0.75081 | 0.77765 | 0.84507 | 0.77032 | 0.77032 | 0.77032 | 0.77032 | 0.77032 | 0.77032 | 0.77032 | 0.77156 | 0.77426 | 0.80144 | 0.86499 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-20 01:47 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.74481 | 0.74993 | 0.77637 | 0.84309 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74394 | 0.74536 | 0.75052 | 0.77721 | 0.84409 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77116 | 0.77386 | 0.80087 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-21 02:15 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74452 | 0.74962 | 0.77595 | 0.84309 | 0.74368 | 0.74368 | 0.74368 | 0.74368 | 0.74368 | 0.74368 | 0.74368 | 0.74508 | 0.75022 | 0.7768 | 0.84409 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77116 | 0.77386 | 0.80087 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-22 02:43 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74426 | 0.74934 | 0.77553 | 0.84213 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.7434 | 0.74481 | 0.74993 | 0.77637 | 0.84309 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77116 | 0.77386 | 0.80087 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-23 03:11 | 0.7426 | 0.7426 | 0.7426 | 0.7426 | 0.7426 | 0.7426 | 0.7426 | 0.74398 | 0.74904 | 0.77512 | 0.84213 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74454 | 0.74964 | 0.77595 | 0.84309 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77116 | 0.77386 | 0.80087 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-24 03:39 | 0.74233 | 0.74233 | 0.74233 | 0.74233 | 0.74233 | 0.74233 | 0.74233 | 0.74371 | 0.74875 | 0.77512 | 0.84213 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74314 | 0.74454 | 0.74964 | 0.77595 | 0.84309 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77116 | 0.77386 | 0.80087 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-25 04:02 | 0.74206 | 0.74206 | 0.74206 | 0.74206 | 0.74206 | 0.74206 | 0.74206 | 0.74344 | 0.74847 | 0.7747 | 0.84213 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74286 | 0.74426 | 0.74934 | 0.77553 | 0.84309 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.76994 | 0.77116 | 0.77386 | 0.80087 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-26 00:22 | 0.74184 | 0.74184 | 0.74184 | 0.74184 | 0.74184 | 0.74184 | 0.74184 | 0.74321 | 0.74822 | 0.77436 | 0.84213 | 0.74264 | 0.74264 | 0.74264 | 0.74264 | 0.74264 | 0.74264 | 0.74264 | 0.74403 | 0.7491 | 0.77519 | 0.84309 | 0.76961 | 0.76961 | 0.76961 | 0.76961 | 0.76961 | 0.76961 | 0.76961 | 0.77083 | 0.77351 | 0.80038 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-27 00:51 | 0.74158 | 0.74158 | 0.74158 | 0.74158 | 0.74158 | 0.74158 | 0.74158 | 0.74295 | 0.74794 | 0.77396 | 0.84213 | 0.74237 | 0.74237 | 0.74237 | 0.74237 | 0.74237 | 0.74237 | 0.74237 | 0.74375 | 0.7488 | 0.77478 | 0.84309 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.77043 | 0.77311 | 0.79982 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-28 01:24 | 0.74131 | 0.74131 | 0.74131 | 0.74131 | 0.74131 | 0.74131 | 0.74131 | 0.74267 | 0.74764 | 0.77396 | 0.84213 | 0.74211 | 0.74211 | 0.74211 | 0.74211 | 0.74211 | 0.74211 | 0.74211 | 0.74349 | 0.74851 | 0.77478 | 0.84309 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.77005 | 0.7727 | 0.79982 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-29 01:13 | 0.74106 | 0.74106 | 0.74106 | 0.74106 | 0.74106 | 0.74106 | 0.74106 | 0.74241 | 0.74736 | 0.77396 | 0.84213 | 0.74185 | 0.74185 | 0.74185 | 0.74185 | 0.74185 | 0.74185 | 0.74185 | 0.74322 | 0.74823 | 0.77478 | 0.84309 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.77005 | 0.7727 | 0.79982 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-30 00:39 | 0.74081 | 0.74081 | 0.74081 | 0.74081 | 0.74081 | 0.74081 | 0.74081 | 0.74216 | 0.74709 | 0.77356 | 0.84213 | 0.7416 | 0.7416 | 0.7416 | 0.7416 | 0.7416 | 0.7416 | 0.7416 | 0.74296 | 0.74796 | 0.77438 | 0.84309 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76967 | 0.77232 | 0.79926 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2005-12-31 00:34 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.7419 | 0.74682 | 0.77316 | 0.84118 | 0.74134 | 0.74134 | 0.74134 | 0.74134 | 0.74134 | 0.74134 | 0.74134 | 0.74271 | 0.74768 | 0.77397 | 0.84213 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76849 | 0.76967 | 0.77232 | 0.79926 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-01 01:02 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.74164 | 0.74654 | 0.77276 | 0.84118 | 0.74107 | 0.74107 | 0.74107 | 0.74107 | 0.74107 | 0.74107 | 0.74107 | 0.74243 | 0.74739 | 0.77357 | 0.84213 | 0.7681 | 0.7681 | 0.7681 | 0.7681 | 0.7681 | 0.7681 | 0.7681 | 0.7693 | 0.77192 | 0.7987 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-02 01:41 | 0.74003 | 0.74003 | 0.74003 | 0.74003 | 0.74003 | 0.74003 | 0.74003 | 0.74137 | 0.74625 | 0.77236 | 0.84118 | 0.74082 | 0.74082 | 0.74082 | 0.74082 | 0.74082 | 0.74082 | 0.74082 | 0.74216 | 0.74709 | 0.77316 | 0.84213 | 0.76773 | 0.76773 | 0.76773 | 0.76773 | 0.76773 | 0.76773 | 0.76773 | 0.76891 | 0.77153 | 0.79813 | 0.86375 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-03 02:09 | 0.73978 | 0.73978 | 0.73978 | 0.73978 | 0.73978 | 0.73978 | 0.73978 | 0.74111 | 0.74596 | 0.77196 | 0.84021 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.74055 | 0.7419 | 0.74682 | 0.77276 | 0.84118 | 0.76735 | 0.76735 | 0.76735 | 0.76735 | 0.76735 | 0.76735 | 0.76735 | 0.76853 | 0.77112 | 0.79758 | 0.86247 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.84524 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-04 02:43 | 0.73952 | 0.73952 | 0.73952 | 0.73952 | 0.73952 | 0.73952 | 0.73952 | 0.74085 | 0.74569 | 0.77196 | 0.84021 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.7403 | 0.74163 | 0.74653 | 0.77276 | 0.84118 | 0.76698 | 0.76698 | 0.76698 | 0.76698 | 0.76698 | 0.76698 | 0.76698 | 0.76814 | 0.77074 | 0.79758 | 0.86247 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-05 01:02 | 0.73929 | 0.73929 | 0.73929 | 0.73929 | 0.73929 | 0.73929 | 0.73929 | 0.74062 | 0.74544 | 0.77196 | 0.84021 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 0.7414 | 0.74627 | 0.77276 | 0.84118 | 0.76663 | 0.76663 | 0.76663 | 0.76663 | 0.76663 | 0.76663 | 0.76663 | 0.76781 | 0.77037 | 0.79758 | 0.86247 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-06 01:19 | 0.73903 | 0.73903 | 0.73903 | 0.73903 | 0.73903 | 0.73903 | 0.73903 | 0.74035 | 0.74516 | 0.77156 | 0.84021 | 0.7398 | 0.7398 | 0.7398 | 0.7398 | 0.7398 | 0.7398 | 0.7398 | 0.74114 | 0.746 | 0.77236 | 0.84118 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76627 | 0.76744 | 0.76999 | 0.79704 | 0.86247 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-07 01:47 | 0.73878 | 0.73878 | 0.73878 | 0.73878 | 0.73878 | 0.73878 | 0.73878 | 0.7401 | 0.74488 | 0.77117 | 0.83928 | 0.73955 | 0.73955 | 0.73955 | 0.73955 | 0.73955 | 0.73955 | 0.73955 | 0.74087 | 0.74571 | 0.77196 | 0.84021 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76706 | 0.76961 | 0.79647 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-08 01:19 | 0.73853 | 0.73853 | 0.73853 | 0.73853 | 0.73853 | 0.73853 | 0.73853 | 0.73984 | 0.74461 | 0.77079 | 0.83928 | 0.7393 | 0.7393 | 0.7393 | 0.7393 | 0.7393 | 0.7393 | 0.7393 | 0.74063 | 0.74545 | 0.77157 | 0.84021 | 0.76555 | 0.76555 | 0.76555 | 0.76555 | 0.76555 | 0.76555 | 0.76555 | 0.76671 | 0.76923 | 0.79596 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-09 01:41 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73959 | 0.74435 | 0.77079 | 0.83928 | 0.73905 | 0.73905 | 0.73905 | 0.73905 | 0.73905 | 0.73905 | 0.73905 | 0.74036 | 0.74517 | 0.77157 | 0.84021 | 0.76519 | 0.76519 | 0.76519 | 0.76519 | 0.76519 | 0.76519 | 0.76519 | 0.76633 | 0.76886 | 0.79596 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-10 02:21 | 0.73803 | 0.73803 | 0.73803 | 0.73803 | 0.73803 | 0.73803 | 0.73803 | 0.73933 | 0.74407 | 0.77079 | 0.83928 | 0.73879 | 0.73879 | 0.73879 | 0.73879 | 0.73879 | 0.73879 | 0.73879 | 0.74011 | 0.7449 | 0.77157 | 0.84021 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76482 | 0.76597 | 0.76847 | 0.79596 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-11 02:43 | 0.73778 | 0.73778 | 0.73778 | 0.73778 | 0.73778 | 0.73778 | 0.73778 | 0.73908 | 0.7438 | 0.77079 | 0.83928 | 0.73854 | 0.73854 | 0.73854 | 0.73854 | 0.73854 | 0.73854 | 0.73854 | 0.73984 | 0.74461 | 0.77157 | 0.84021 | 0.76447 | 0.76447 | 0.76447 | 0.76447 | 0.76447 | 0.76447 | 0.76447 | 0.76559 | 0.7681 | 0.79596 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-12 03:11 | 0.73754 | 0.73754 | 0.73754 | 0.73754 | 0.73754 | 0.73754 | 0.73754 | 0.73882 | 0.74352 | 0.77079 | 0.83928 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73828 | 0.73959 | 0.74435 | 0.77157 | 0.84021 | 0.7641 | 0.7641 | 0.7641 | 0.7641 | 0.7641 | 0.7641 | 0.7641 | 0.76523 | 0.76771 | 0.79596 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-13 03:45 | 0.73728 | 0.73728 | 0.73728 | 0.73728 | 0.73728 | 0.73728 | 0.73728 | 0.73857 | 0.74326 | 0.7704 | 0.83928 | 0.73804 | 0.73804 | 0.73804 | 0.73804 | 0.73804 | 0.73804 | 0.73804 | 0.73933 | 0.74407 | 0.77119 | 0.84021 | 0.76375 | 0.76375 | 0.76375 | 0.76375 | 0.76375 | 0.76375 | 0.76375 | 0.76486 | 0.76735 | 0.79541 | 0.86127 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-14 00:06 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73835 | 0.74303 | 0.77007 | 0.83852 | 0.73782 | 0.73782 | 0.73782 | 0.73782 | 0.73782 | 0.73782 | 0.73782 | 0.73912 | 0.74384 | 0.77087 | 0.83944 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76457 | 0.76702 | 0.79497 | 0.86027 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-15 00:34 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73811 | 0.74276 | 0.76969 | 0.83758 | 0.73758 | 0.73758 | 0.73758 | 0.73758 | 0.73758 | 0.73758 | 0.73758 | 0.73887 | 0.74358 | 0.77047 | 0.83852 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76344 | 0.76457 | 0.76702 | 0.79497 | 0.86027 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-16 01:02 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73786 | 0.7425 | 0.76969 | 0.83758 | 0.73732 | 0.73732 | 0.73732 | 0.73732 | 0.73732 | 0.73732 | 0.73732 | 0.73861 | 0.7433 | 0.77047 | 0.83852 | 0.7631 | 0.7631 | 0.7631 | 0.7631 | 0.7631 | 0.7631 | 0.7631 | 0.7642 | 0.76666 | 0.79497 | 0.86027 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-17 01:30 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73761 | 0.74223 | 0.7693 | 0.83668 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73708 | 0.73836 | 0.74304 | 0.77009 | 0.83758 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76385 | 0.76628 | 0.79442 | 0.85905 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-18 01:52 | 0.73609 | 0.73609 | 0.73609 | 0.73609 | 0.73609 | 0.73609 | 0.73609 | 0.73736 | 0.74197 | 0.76892 | 0.83576 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73683 | 0.73811 | 0.74276 | 0.76969 | 0.83668 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76274 | 0.76385 | 0.76628 | 0.79442 | 0.85905 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-19 02:21 | 0.73584 | 0.73584 | 0.73584 | 0.73584 | 0.73584 | 0.73584 | 0.73584 | 0.73711 | 0.74197 | 0.76892 | 0.83576 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73658 | 0.73786 | 0.74276 | 0.76969 | 0.83668 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.76239 | 0.7635 | 0.76628 | 0.79442 | 0.85905 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-20 03:11 | 0.73561 | 0.73561 | 0.73561 | 0.73561 | 0.73561 | 0.73561 | 0.73561 | 0.73686 | 0.7417 | 0.76853 | 0.83576 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73633 | 0.73761 | 0.74249 | 0.7693 | 0.83668 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76203 | 0.76314 | 0.76592 | 0.79388 | 0.85905 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-21 02:38 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73662 | 0.74144 | 0.76818 | 0.83492 | 0.7361 | 0.7361 | 0.7361 | 0.7361 | 0.7361 | 0.7361 | 0.7361 | 0.73737 | 0.74224 | 0.76894 | 0.8358 | 0.76171 | 0.76171 | 0.76171 | 0.76171 | 0.76171 | 0.76171 | 0.76171 | 0.76279 | 0.76556 | 0.79338 | 0.85794 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.84422 | 0.85689 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-22 03:00 | 0.73513 | 0.73513 | 0.73513 | 0.73513 | 0.73513 | 0.73513 | 0.73513 | 0.73638 | 0.74118 | 0.76779 | 0.83492 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73712 | 0.74198 | 0.76856 | 0.8358 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76245 | 0.76521 | 0.79284 | 0.85794 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.85576 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-23 03:34 | 0.73489 | 0.73489 | 0.73489 | 0.73489 | 0.73489 | 0.73489 | 0.73489 | 0.73613 | 0.74092 | 0.76742 | 0.83402 | 0.73562 | 0.73562 | 0.73562 | 0.73562 | 0.73562 | 0.73562 | 0.73562 | 0.73688 | 0.74171 | 0.76818 | 0.83492 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76245 | 0.76521 | 0.79284 | 0.85794 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.85576 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-24 03:56 | 0.73465 | 0.73465 | 0.73465 | 0.73465 | 0.73465 | 0.73465 | 0.73465 | 0.73589 | 0.74066 | 0.76706 | 0.83402 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73537 | 0.73662 | 0.74145 | 0.76781 | 0.83492 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76135 | 0.76245 | 0.76521 | 0.79284 | 0.85794 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.84325 | 0.85576 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-25 00:17 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73568 | 0.74045 | 0.76674 | 0.83402 | 0.73517 | 0.73517 | 0.73517 | 0.73517 | 0.73517 | 0.73517 | 0.73517 | 0.73642 | 0.74122 | 0.76748 | 0.83492 | 0.76107 | 0.76107 | 0.76107 | 0.76107 | 0.76107 | 0.76107 | 0.76107 | 0.76216 | 0.76489 | 0.79242 | 0.85794 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.85478 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-26 00:56 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73545 | 0.74045 | 0.76674 | 0.83402 | 0.73492 | 0.73492 | 0.73492 | 0.73492 | 0.73492 | 0.73492 | 0.73492 | 0.73617 | 0.74122 | 0.76748 | 0.83492 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76181 | 0.76489 | 0.79242 | 0.85794 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.85478 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-27 01:41 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.7352 | 0.74018 | 0.76636 | 0.83316 | 0.73469 | 0.73469 | 0.73469 | 0.73469 | 0.73469 | 0.73469 | 0.73469 | 0.73592 | 0.74097 | 0.76712 | 0.83402 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76072 | 0.76181 | 0.76489 | 0.79242 | 0.85794 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.84241 | 0.85478 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-28 02:09 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73495 | 0.73993 | 0.766 | 0.83316 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73444 | 0.73568 | 0.7407 | 0.76674 | 0.83402 | 0.76039 | 0.76039 | 0.76039 | 0.76039 | 0.76039 | 0.76039 | 0.76039 | 0.76145 | 0.76454 | 0.79191 | 0.85794 | 0.84146 | 0.84146 | 0.84146 | 0.84146 | 0.84146 | 0.84146 | 0.84146 | 0.84146 | 0.84146 | 0.85368 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-29 02:43 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73472 | 0.73966 | 0.76562 | 0.83316 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73421 | 0.73544 | 0.74045 | 0.76636 | 0.83402 | 0.76004 | 0.76004 | 0.76004 | 0.76004 | 0.76004 | 0.76004 | 0.76004 | 0.76112 | 0.76417 | 0.79138 | 0.85794 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.85255 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-30 03:11 | 0.73326 | 0.73326 | 0.73326 | 0.73326 | 0.73326 | 0.73326 | 0.73326 | 0.73447 | 0.73941 | 0.76526 | 0.83316 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.73397 | 0.7352 | 0.74018 | 0.766 | 0.83402 | 0.75971 | 0.75971 | 0.75971 | 0.75971 | 0.75971 | 0.75971 | 0.75971 | 0.76076 | 0.76382 | 0.79088 | 0.85794 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.85255 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-01-31 03:34 | 0.73302 | 0.73302 | 0.73302 | 0.73302 | 0.73302 | 0.73302 | 0.73302 | 0.73424 | 0.73915 | 0.76526 | 0.83316 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73374 | 0.73496 | 0.73993 | 0.766 | 0.83402 | 0.75936 | 0.75936 | 0.75936 | 0.75936 | 0.75936 | 0.75936 | 0.75936 | 0.76043 | 0.76347 | 0.79088 | 0.85794 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.85255 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-01 04:02 | 0.7328 | 0.7328 | 0.7328 | 0.7328 | 0.7328 | 0.7328 | 0.7328 | 0.73401 | 0.7389 | 0.76489 | 0.83228 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73349 | 0.73472 | 0.73966 | 0.76564 | 0.83316 | 0.75904 | 0.75904 | 0.75904 | 0.75904 | 0.75904 | 0.75904 | 0.75904 | 0.7601 | 0.76311 | 0.79036 | 0.85675 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.85255 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-02 00:22 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7338 | 0.73869 | 0.76489 | 0.83228 | 0.7333 | 0.7333 | 0.7333 | 0.7333 | 0.7333 | 0.7333 | 0.7333 | 0.73452 | 0.73946 | 0.76564 | 0.83316 | 0.75876 | 0.75876 | 0.75876 | 0.75876 | 0.75876 | 0.75876 | 0.75876 | 0.7598 | 0.76282 | 0.79036 | 0.85675 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.84048 | 0.85255 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-03 01:02 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73357 | 0.73844 | 0.76454 | 0.83228 | 0.73306 | 0.73306 | 0.73306 | 0.73306 | 0.73306 | 0.73306 | 0.73306 | 0.73428 | 0.73919 | 0.76526 | 0.83316 | 0.75842 | 0.75842 | 0.75842 | 0.75842 | 0.75842 | 0.75842 | 0.75842 | 0.75947 | 0.76246 | 0.78985 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-04 01:24 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73333 | 0.73818 | 0.76454 | 0.83228 | 0.73283 | 0.73283 | 0.73283 | 0.73283 | 0.73283 | 0.73283 | 0.73283 | 0.73405 | 0.73894 | 0.76526 | 0.83316 | 0.75808 | 0.75808 | 0.75808 | 0.75808 | 0.75808 | 0.75808 | 0.75808 | 0.75913 | 0.76212 | 0.78985 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-05 02:04 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7331 | 0.73793 | 0.76454 | 0.83228 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7326 | 0.7338 | 0.73869 | 0.76526 | 0.83316 | 0.75776 | 0.75776 | 0.75776 | 0.75776 | 0.75776 | 0.75776 | 0.75776 | 0.75879 | 0.76176 | 0.78985 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-06 02:38 | 0.73167 | 0.73167 | 0.73167 | 0.73167 | 0.73167 | 0.73167 | 0.73167 | 0.73286 | 0.73768 | 0.76417 | 0.83228 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73237 | 0.73357 | 0.73844 | 0.76489 | 0.83316 | 0.75743 | 0.75743 | 0.75743 | 0.75743 | 0.75743 | 0.75743 | 0.75743 | 0.75846 | 0.76143 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-07 03:11 | 0.73144 | 0.73144 | 0.73144 | 0.73144 | 0.73144 | 0.73144 | 0.73144 | 0.73262 | 0.73743 | 0.76417 | 0.83228 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73213 | 0.73333 | 0.73818 | 0.76489 | 0.83316 | 0.75711 | 0.75711 | 0.75711 | 0.75711 | 0.75711 | 0.75711 | 0.75711 | 0.75812 | 0.76107 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-08 03:34 | 0.73121 | 0.73121 | 0.73121 | 0.73121 | 0.73121 | 0.73121 | 0.73121 | 0.7324 | 0.73718 | 0.76417 | 0.83228 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7319 | 0.7331 | 0.73793 | 0.76489 | 0.83316 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.7578 | 0.76074 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-09 00:06 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.7322 | 0.73698 | 0.76388 | 0.83158 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 0.7329 | 0.73772 | 0.7646 | 0.83242 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.7578 | 0.76074 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-10 00:39 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73197 | 0.73672 | 0.76352 | 0.83071 | 0.73148 | 0.73148 | 0.73148 | 0.73148 | 0.73148 | 0.73148 | 0.73148 | 0.73266 | 0.73747 | 0.76423 | 0.83154 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.7578 | 0.76074 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-11 01:13 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73174 | 0.73647 | 0.76317 | 0.83071 | 0.73125 | 0.73125 | 0.73125 | 0.73125 | 0.73125 | 0.73125 | 0.73125 | 0.73243 | 0.73722 | 0.76388 | 0.83154 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.75677 | 0.7578 | 0.76074 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-12 01:36 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73151 | 0.73623 | 0.76317 | 0.83071 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73102 | 0.73221 | 0.73698 | 0.76388 | 0.83154 | 0.75646 | 0.75646 | 0.75646 | 0.75646 | 0.75646 | 0.75646 | 0.75646 | 0.75748 | 0.76039 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-13 02:09 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73128 | 0.73623 | 0.76317 | 0.83071 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73079 | 0.73197 | 0.73698 | 0.76388 | 0.83154 | 0.75613 | 0.75613 | 0.75613 | 0.75613 | 0.75613 | 0.75613 | 0.75613 | 0.75715 | 0.76039 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-14 02:38 | 0.72989 | 0.72989 | 0.72989 | 0.72989 | 0.72989 | 0.72989 | 0.72989 | 0.73105 | 0.73599 | 0.76317 | 0.83071 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73057 | 0.73174 | 0.73672 | 0.76388 | 0.83154 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75683 | 0.76005 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-15 03:06 | 0.72967 | 0.72967 | 0.72967 | 0.72967 | 0.72967 | 0.72967 | 0.72967 | 0.73082 | 0.73574 | 0.76281 | 0.83071 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73034 | 0.73151 | 0.73648 | 0.76352 | 0.83154 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75683 | 0.76005 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-16 03:28 | 0.72944 | 0.72944 | 0.72944 | 0.72944 | 0.72944 | 0.72944 | 0.72944 | 0.7306 | 0.73551 | 0.76281 | 0.83071 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73012 | 0.73129 | 0.73623 | 0.76352 | 0.83154 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75581 | 0.75683 | 0.76005 | 0.78935 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-17 00:11 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.7304 | 0.7353 | 0.76251 | 0.83071 | 0.72993 | 0.72993 | 0.72993 | 0.72993 | 0.72993 | 0.72993 | 0.72993 | 0.73109 | 0.73603 | 0.76323 | 0.83154 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75655 | 0.75976 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-18 00:34 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.73018 | 0.73506 | 0.76216 | 0.82989 | 0.72971 | 0.72971 | 0.72971 | 0.72971 | 0.72971 | 0.72971 | 0.72971 | 0.73087 | 0.73578 | 0.76287 | 0.83071 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75655 | 0.75976 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-19 01:02 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72996 | 0.73482 | 0.76182 | 0.82989 | 0.72948 | 0.72948 | 0.72948 | 0.72948 | 0.72948 | 0.72948 | 0.72948 | 0.73064 | 0.73555 | 0.76252 | 0.83071 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75554 | 0.75655 | 0.75976 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-20 01:30 | 0.72859 | 0.72859 | 0.72859 | 0.72859 | 0.72859 | 0.72859 | 0.72859 | 0.72973 | 0.73458 | 0.76182 | 0.82989 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.72926 | 0.73041 | 0.7353 | 0.76252 | 0.83071 | 0.75522 | 0.75522 | 0.75522 | 0.75522 | 0.75522 | 0.75522 | 0.75522 | 0.75622 | 0.75943 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-21 01:52 | 0.72838 | 0.72838 | 0.72838 | 0.72838 | 0.72838 | 0.72838 | 0.72838 | 0.72952 | 0.73434 | 0.76182 | 0.82989 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.72903 | 0.73018 | 0.73506 | 0.76252 | 0.83071 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7559 | 0.75909 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-22 02:15 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72929 | 0.7341 | 0.76147 | 0.82904 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72882 | 0.72996 | 0.73483 | 0.76216 | 0.82989 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7559 | 0.75909 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-23 01:36 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72908 | 0.73388 | 0.76147 | 0.82904 | 0.72861 | 0.72861 | 0.72861 | 0.72861 | 0.72861 | 0.72861 | 0.72861 | 0.72975 | 0.73459 | 0.76216 | 0.82989 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7559 | 0.75909 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-24 02:09 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72885 | 0.73364 | 0.76113 | 0.82823 | 0.72839 | 0.72839 | 0.72839 | 0.72839 | 0.72839 | 0.72839 | 0.72839 | 0.72952 | 0.73436 | 0.76182 | 0.82904 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7549 | 0.7559 | 0.75909 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-25 02:54 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72864 | 0.7334 | 0.76113 | 0.82823 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.72816 | 0.7293 | 0.73411 | 0.76182 | 0.82904 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75558 | 0.75875 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-26 03:22 | 0.72729 | 0.72729 | 0.72729 | 0.72729 | 0.72729 | 0.72729 | 0.72729 | 0.72841 | 0.73317 | 0.76078 | 0.82823 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72795 | 0.72908 | 0.73387 | 0.76147 | 0.82904 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75558 | 0.75875 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-27 03:45 | 0.72708 | 0.72708 | 0.72708 | 0.72708 | 0.72708 | 0.72708 | 0.72708 | 0.7282 | 0.73294 | 0.76044 | 0.8274 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72773 | 0.72885 | 0.73364 | 0.76113 | 0.82823 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75459 | 0.75558 | 0.75875 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-28 00:06 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.72801 | 0.73274 | 0.76044 | 0.8274 | 0.72755 | 0.72755 | 0.72755 | 0.72755 | 0.72755 | 0.72755 | 0.72755 | 0.72867 | 0.73345 | 0.76113 | 0.82823 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75532 | 0.75848 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-02-28 04:13 | 0.72687 | 0.72687 | 0.72687 | 0.72687 | 0.72687 | 0.72687 | 0.72687 | 0.72797 | 0.7327 | 0.76039 | 0.82727 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72751 | 0.72864 | 0.73341 | 0.76107 | 0.8281 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75432 | 0.75532 | 0.75848 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-01 00:34 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.7278 | 0.73251 | 0.76039 | 0.82727 | 0.72734 | 0.72734 | 0.72734 | 0.72734 | 0.72734 | 0.72734 | 0.72734 | 0.72846 | 0.73321 | 0.76107 | 0.8281 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75506 | 0.75821 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-01 04:36 | 0.72665 | 0.72665 | 0.72665 | 0.72665 | 0.72665 | 0.72665 | 0.72665 | 0.72776 | 0.73247 | 0.76033 | 0.82714 | 0.7273 | 0.7273 | 0.7273 | 0.7273 | 0.7273 | 0.7273 | 0.7273 | 0.72842 | 0.73317 | 0.76102 | 0.82797 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75406 | 0.75506 | 0.75821 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-02 01:08 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72757 | 0.73227 | 0.76033 | 0.82714 | 0.72712 | 0.72712 | 0.72712 | 0.72712 | 0.72712 | 0.72712 | 0.72712 | 0.72823 | 0.73298 | 0.76102 | 0.82797 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.75478 | 0.75792 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-03 01:52 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72736 | 0.73204 | 0.76033 | 0.82714 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.7269 | 0.72801 | 0.73274 | 0.76102 | 0.82797 | 0.75349 | 0.75349 | 0.75349 | 0.75349 | 0.75349 | 0.75349 | 0.75349 | 0.75446 | 0.75759 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-04 02:21 | 0.72604 | 0.72604 | 0.72604 | 0.72604 | 0.72604 | 0.72604 | 0.72604 | 0.72714 | 0.73181 | 0.76033 | 0.82714 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.72669 | 0.7278 | 0.73251 | 0.76102 | 0.82797 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75415 | 0.75727 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-05 02:49 | 0.72583 | 0.72583 | 0.72583 | 0.72583 | 0.72583 | 0.72583 | 0.72583 | 0.72693 | 0.73158 | 0.75998 | 0.82714 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72648 | 0.72757 | 0.73227 | 0.76067 | 0.82797 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75318 | 0.75415 | 0.75727 | 0.78893 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-06 03:22 | 0.72562 | 0.72562 | 0.72562 | 0.72562 | 0.72562 | 0.72562 | 0.72562 | 0.72671 | 0.73135 | 0.75965 | 0.82714 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72626 | 0.72736 | 0.73204 | 0.76033 | 0.82797 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75383 | 0.75693 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-07 03:45 | 0.72541 | 0.72541 | 0.72541 | 0.72541 | 0.72541 | 0.72541 | 0.72541 | 0.7265 | 0.73113 | 0.75965 | 0.82714 | 0.72605 | 0.72605 | 0.72605 | 0.72605 | 0.72605 | 0.72605 | 0.72605 | 0.72714 | 0.73181 | 0.76033 | 0.82797 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75383 | 0.75693 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-08 00:06 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72632 | 0.73093 | 0.75936 | 0.82648 | 0.72587 | 0.72587 | 0.72587 | 0.72587 | 0.72587 | 0.72587 | 0.72587 | 0.72697 | 0.73162 | 0.76004 | 0.82727 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75383 | 0.75693 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-09 00:39 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72611 | 0.73071 | 0.75904 | 0.82648 | 0.72566 | 0.72566 | 0.72566 | 0.72566 | 0.72566 | 0.72566 | 0.72566 | 0.72675 | 0.73139 | 0.75971 | 0.82727 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75383 | 0.75693 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-10 01:02 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.7259 | 0.73048 | 0.75869 | 0.82648 | 0.72544 | 0.72544 | 0.72544 | 0.72544 | 0.72544 | 0.72544 | 0.72544 | 0.72654 | 0.73116 | 0.75936 | 0.82727 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75287 | 0.75383 | 0.75693 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-11 01:30 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72569 | 0.73026 | 0.75869 | 0.82648 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72524 | 0.72633 | 0.73093 | 0.75936 | 0.82727 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75353 | 0.75661 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-12 02:09 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.72547 | 0.73003 | 0.75837 | 0.82648 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72502 | 0.72611 | 0.73071 | 0.75904 | 0.82727 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75256 | 0.75353 | 0.75661 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-13 02:43 | 0.72419 | 0.72419 | 0.72419 | 0.72419 | 0.72419 | 0.72419 | 0.72419 | 0.72526 | 0.72981 | 0.75837 | 0.82648 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72589 | 0.73048 | 0.75904 | 0.82727 | 0.75226 | 0.75226 | 0.75226 | 0.75226 | 0.75226 | 0.75226 | 0.75226 | 0.75321 | 0.75628 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-14 03:17 | 0.72398 | 0.72398 | 0.72398 | 0.72398 | 0.72398 | 0.72398 | 0.72398 | 0.72505 | 0.72958 | 0.75837 | 0.82648 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72461 | 0.72569 | 0.73026 | 0.75904 | 0.82727 | 0.75195 | 0.75195 | 0.75195 | 0.75195 | 0.75195 | 0.75195 | 0.75195 | 0.75291 | 0.75597 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-15 03:45 | 0.72378 | 0.72378 | 0.72378 | 0.72378 | 0.72378 | 0.72378 | 0.72378 | 0.72485 | 0.72936 | 0.75837 | 0.82648 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.7244 | 0.72547 | 0.73003 | 0.75904 | 0.82727 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.7526 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-16 00:17 | 0.7236 | 0.7236 | 0.7236 | 0.7236 | 0.7236 | 0.7236 | 0.7236 | 0.72467 | 0.72917 | 0.75808 | 0.8258 | 0.72423 | 0.72423 | 0.72423 | 0.72423 | 0.72423 | 0.72423 | 0.72423 | 0.7253 | 0.72984 | 0.75875 | 0.82661 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.7526 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-17 03:56 | 0.72338 | 0.72338 | 0.72338 | 0.72338 | 0.72338 | 0.72338 | 0.72338 | 0.72444 | 0.72892 | 0.75771 | 0.8258 | 0.72399 | 0.72399 | 0.72399 | 0.72399 | 0.72399 | 0.72399 | 0.72399 | 0.72506 | 0.72959 | 0.75838 | 0.82661 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.75165 | 0.7526 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-18 00:11 | 0.72321 | 0.72321 | 0.72321 | 0.72321 | 0.72321 | 0.72321 | 0.72321 | 0.72426 | 0.72892 | 0.75771 | 0.8258 | 0.72382 | 0.72382 | 0.72382 | 0.72382 | 0.72382 | 0.72382 | 0.72382 | 0.72489 | 0.72959 | 0.75838 | 0.82661 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75235 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-19 00:45 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.72406 | 0.7287 | 0.75739 | 0.8258 | 0.72362 | 0.72362 | 0.72362 | 0.72362 | 0.72362 | 0.72362 | 0.72362 | 0.72468 | 0.72936 | 0.75804 | 0.82661 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75235 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-20 01:24 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72385 | 0.72848 | 0.75705 | 0.82502 | 0.72341 | 0.72341 | 0.72341 | 0.72341 | 0.72341 | 0.72341 | 0.72341 | 0.72447 | 0.72914 | 0.75771 | 0.8258 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75235 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-21 01:52 | 0.7226 | 0.7226 | 0.7226 | 0.7226 | 0.7226 | 0.7226 | 0.7226 | 0.72364 | 0.72826 | 0.75673 | 0.82422 | 0.7232 | 0.7232 | 0.7232 | 0.7232 | 0.7232 | 0.7232 | 0.7232 | 0.72426 | 0.72892 | 0.75739 | 0.82502 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75139 | 0.75235 | 0.75564 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-22 02:26 | 0.72239 | 0.72239 | 0.72239 | 0.72239 | 0.72239 | 0.72239 | 0.72239 | 0.72344 | 0.72804 | 0.75673 | 0.82422 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.72406 | 0.7287 | 0.75739 | 0.82502 | 0.7511 | 0.7511 | 0.7511 | 0.7511 | 0.7511 | 0.7511 | 0.7511 | 0.75203 | 0.75533 | 0.78844 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-23 03:11 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72323 | 0.72781 | 0.7564 | 0.82422 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72279 | 0.72385 | 0.72848 | 0.75705 | 0.82502 | 0.75079 | 0.75079 | 0.75079 | 0.75079 | 0.75079 | 0.75079 | 0.75079 | 0.75174 | 0.755 | 0.78794 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-24 03:56 | 0.72199 | 0.72199 | 0.72199 | 0.72199 | 0.72199 | 0.72199 | 0.72199 | 0.72303 | 0.7276 | 0.75607 | 0.82422 | 0.72259 | 0.72259 | 0.72259 | 0.72259 | 0.72259 | 0.72259 | 0.72259 | 0.72364 | 0.72825 | 0.75672 | 0.82502 | 0.75048 | 0.75048 | 0.75048 | 0.75048 | 0.75048 | 0.75048 | 0.75048 | 0.75143 | 0.75468 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-25 03:22 | 0.72179 | 0.72179 | 0.72179 | 0.72179 | 0.72179 | 0.72179 | 0.72179 | 0.72283 | 0.72739 | 0.75607 | 0.82422 | 0.7224 | 0.7224 | 0.7224 | 0.7224 | 0.7224 | 0.7224 | 0.7224 | 0.72344 | 0.72805 | 0.75672 | 0.82502 | 0.7502 | 0.7502 | 0.7502 | 0.7502 | 0.7502 | 0.7502 | 0.7502 | 0.75113 | 0.75438 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-26 03:56 | 0.7216 | 0.7216 | 0.7216 | 0.7216 | 0.7216 | 0.7216 | 0.7216 | 0.72263 | 0.72739 | 0.75607 | 0.82422 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72219 | 0.72324 | 0.72805 | 0.75672 | 0.82502 | 0.7499 | 0.7499 | 0.7499 | 0.7499 | 0.7499 | 0.7499 | 0.7499 | 0.75084 | 0.75438 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-27 00:22 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72246 | 0.72721 | 0.75607 | 0.82422 | 0.72203 | 0.72203 | 0.72203 | 0.72203 | 0.72203 | 0.72203 | 0.72203 | 0.72307 | 0.72786 | 0.75672 | 0.82502 | 0.74966 | 0.74966 | 0.74966 | 0.74966 | 0.74966 | 0.74966 | 0.74966 | 0.75058 | 0.75412 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-28 00:51 | 0.72123 | 0.72123 | 0.72123 | 0.72123 | 0.72123 | 0.72123 | 0.72123 | 0.72226 | 0.72699 | 0.75607 | 0.82422 | 0.72182 | 0.72182 | 0.72182 | 0.72182 | 0.72182 | 0.72182 | 0.72182 | 0.72286 | 0.72765 | 0.75672 | 0.82502 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.75029 | 0.75381 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-29 01:24 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72205 | 0.72678 | 0.75576 | 0.82346 | 0.72163 | 0.72163 | 0.72163 | 0.72163 | 0.72163 | 0.72163 | 0.72163 | 0.72266 | 0.72742 | 0.7564 | 0.82422 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.74936 | 0.75029 | 0.75381 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-30 01:58 | 0.72083 | 0.72083 | 0.72083 | 0.72083 | 0.72083 | 0.72083 | 0.72083 | 0.72186 | 0.72656 | 0.75576 | 0.82346 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72143 | 0.72246 | 0.72721 | 0.7564 | 0.82422 | 0.74907 | 0.74907 | 0.74907 | 0.74907 | 0.74907 | 0.74907 | 0.74907 | 0.74999 | 0.75349 | 0.78744 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-03-31 02:54 | 0.72063 | 0.72063 | 0.72063 | 0.72063 | 0.72063 | 0.72063 | 0.72063 | 0.72165 | 0.72635 | 0.75543 | 0.82346 | 0.72122 | 0.72122 | 0.72122 | 0.72122 | 0.72122 | 0.72122 | 0.72122 | 0.72225 | 0.72699 | 0.75607 | 0.82422 | 0.74878 | 0.74878 | 0.74878 | 0.74878 | 0.74878 | 0.74878 | 0.74878 | 0.7497 | 0.75318 | 0.78694 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-01 03:28 | 0.72043 | 0.72043 | 0.72043 | 0.72043 | 0.72043 | 0.72043 | 0.72043 | 0.72145 | 0.72614 | 0.75543 | 0.82346 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72103 | 0.72205 | 0.72677 | 0.75607 | 0.82422 | 0.74848 | 0.74848 | 0.74848 | 0.74848 | 0.74848 | 0.74848 | 0.74848 | 0.7494 | 0.75287 | 0.78694 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-02 | 0.72027 | 0.72027 | 0.72027 | 0.72027 | 0.72027 | 0.72027 | 0.72027 | 0.72129 | 0.72595 | 0.75516 | 0.82346 | 0.72086 | 0.72086 | 0.72086 | 0.72086 | 0.72086 | 0.72086 | 0.72086 | 0.72188 | 0.7266 | 0.7558 | 0.82422 | 0.74824 | 0.74824 | 0.74824 | 0.74824 | 0.74824 | 0.74824 | 0.74824 | 0.74915 | 0.75261 | 0.78655 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-03 00:39 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72108 | 0.72574 | 0.75485 | 0.82346 | 0.72067 | 0.72067 | 0.72067 | 0.72067 | 0.72067 | 0.72067 | 0.72067 | 0.72168 | 0.72638 | 0.75548 | 0.82422 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74886 | 0.75231 | 0.78606 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-04 01:08 | 0.71988 | 0.71988 | 0.71988 | 0.71988 | 0.71988 | 0.71988 | 0.71988 | 0.72088 | 0.72553 | 0.75453 | 0.82346 | 0.72046 | 0.72046 | 0.72046 | 0.72046 | 0.72046 | 0.72046 | 0.72046 | 0.72148 | 0.72617 | 0.75516 | 0.82422 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74886 | 0.75231 | 0.78606 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-05 02:32 | 0.71968 | 0.71968 | 0.71968 | 0.71968 | 0.71968 | 0.71968 | 0.71968 | 0.72068 | 0.72532 | 0.75421 | 0.82346 | 0.72026 | 0.72026 | 0.72026 | 0.72026 | 0.72026 | 0.72026 | 0.72026 | 0.72128 | 0.72595 | 0.75484 | 0.82422 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74886 | 0.75231 | 0.78606 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-06 03:17 | 0.71948 | 0.71948 | 0.71948 | 0.71948 | 0.71948 | 0.71948 | 0.71948 | 0.72048 | 0.7251 | 0.75389 | 0.82268 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72007 | 0.72108 | 0.72573 | 0.75451 | 0.82343 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74795 | 0.74886 | 0.75231 | 0.78606 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-07 03:51 | 0.71929 | 0.71929 | 0.71929 | 0.71929 | 0.71929 | 0.71929 | 0.71929 | 0.72029 | 0.72489 | 0.75357 | 0.82268 | 0.71987 | 0.71987 | 0.71987 | 0.71987 | 0.71987 | 0.71987 | 0.71987 | 0.72087 | 0.72552 | 0.75419 | 0.82343 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74856 | 0.752 | 0.78557 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-08 00:17 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.72012 | 0.72472 | 0.75331 | 0.82268 | 0.71971 | 0.71971 | 0.71971 | 0.71971 | 0.71971 | 0.71971 | 0.71971 | 0.72071 | 0.72534 | 0.75394 | 0.82343 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74856 | 0.752 | 0.78557 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-09 01:13 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71992 | 0.72451 | 0.75331 | 0.82268 | 0.71951 | 0.71951 | 0.71951 | 0.71951 | 0.71951 | 0.71951 | 0.71951 | 0.72051 | 0.72513 | 0.75394 | 0.82343 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74765 | 0.74856 | 0.752 | 0.78557 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-10 01:58 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71973 | 0.72429 | 0.753 | 0.82268 | 0.71931 | 0.71931 | 0.71931 | 0.71931 | 0.71931 | 0.71931 | 0.71931 | 0.72031 | 0.72492 | 0.75362 | 0.82343 | 0.74737 | 0.74737 | 0.74737 | 0.74737 | 0.74737 | 0.74737 | 0.74737 | 0.74827 | 0.75169 | 0.7851 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-11 02:26 | 0.71854 | 0.71854 | 0.71854 | 0.71854 | 0.71854 | 0.71854 | 0.71854 | 0.71953 | 0.72409 | 0.753 | 0.82268 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.71912 | 0.72012 | 0.72471 | 0.75362 | 0.82343 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74798 | 0.75139 | 0.7851 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-12 02:49 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71934 | 0.72388 | 0.7527 | 0.8219 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71894 | 0.71992 | 0.72451 | 0.75331 | 0.82268 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74798 | 0.75139 | 0.7851 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-13 03:11 | 0.71817 | 0.71817 | 0.71817 | 0.71817 | 0.71817 | 0.71817 | 0.71817 | 0.71915 | 0.72368 | 0.75238 | 0.8219 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71874 | 0.71973 | 0.7243 | 0.75301 | 0.82268 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74708 | 0.74798 | 0.75139 | 0.7851 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-14 03:34 | 0.71798 | 0.71798 | 0.71798 | 0.71798 | 0.71798 | 0.71798 | 0.71798 | 0.71896 | 0.72348 | 0.75238 | 0.8219 | 0.71855 | 0.71855 | 0.71855 | 0.71855 | 0.71855 | 0.71855 | 0.71855 | 0.71954 | 0.72409 | 0.75301 | 0.82268 | 0.7468 | 0.7468 | 0.7468 | 0.7468 | 0.7468 | 0.7468 | 0.7468 | 0.7477 | 0.7511 | 0.7851 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-15 04:02 | 0.71779 | 0.71779 | 0.71779 | 0.71779 | 0.71779 | 0.71779 | 0.71779 | 0.71877 | 0.72327 | 0.75238 | 0.8219 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71836 | 0.71934 | 0.72389 | 0.75301 | 0.82268 | 0.74652 | 0.74652 | 0.74652 | 0.74652 | 0.74652 | 0.74652 | 0.74652 | 0.74741 | 0.75079 | 0.7851 | 0.85675 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-16 01:30 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.7186 | 0.72309 | 0.75212 | 0.82126 | 0.71819 | 0.71819 | 0.71819 | 0.71819 | 0.71819 | 0.71819 | 0.71819 | 0.71918 | 0.7237 | 0.75273 | 0.822 | 0.74627 | 0.74627 | 0.74627 | 0.74627 | 0.74627 | 0.74627 | 0.74627 | 0.74716 | 0.75053 | 0.78468 | 0.85576 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.83955 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-17 02:15 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.7184 | 0.72289 | 0.75212 | 0.82126 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.71898 | 0.72349 | 0.75273 | 0.822 | 0.74599 | 0.74599 | 0.74599 | 0.74599 | 0.74599 | 0.74599 | 0.74599 | 0.74687 | 0.75023 | 0.78468 | 0.85576 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-18 02:38 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71822 | 0.72289 | 0.75212 | 0.82126 | 0.71782 | 0.71782 | 0.71782 | 0.71782 | 0.71782 | 0.71782 | 0.71782 | 0.71879 | 0.72349 | 0.75273 | 0.822 | 0.74571 | 0.74571 | 0.74571 | 0.74571 | 0.74571 | 0.74571 | 0.74571 | 0.7466 | 0.75023 | 0.78468 | 0.85576 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-19 02:54 | 0.71706 | 0.71706 | 0.71706 | 0.71706 | 0.71706 | 0.71706 | 0.71706 | 0.71803 | 0.72269 | 0.75212 | 0.82126 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.71762 | 0.7186 | 0.72329 | 0.75273 | 0.822 | 0.74544 | 0.74544 | 0.74544 | 0.74544 | 0.74544 | 0.74544 | 0.74544 | 0.74631 | 0.74994 | 0.78468 | 0.85576 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-20 03:28 | 0.71687 | 0.71687 | 0.71687 | 0.71687 | 0.71687 | 0.71687 | 0.71687 | 0.71784 | 0.72248 | 0.75181 | 0.8205 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71744 | 0.71841 | 0.72309 | 0.75243 | 0.82126 | 0.74516 | 0.74516 | 0.74516 | 0.74516 | 0.74516 | 0.74516 | 0.74516 | 0.74603 | 0.74964 | 0.78422 | 0.8546 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-21 04:02 | 0.71669 | 0.71669 | 0.71669 | 0.71669 | 0.71669 | 0.71669 | 0.71669 | 0.71765 | 0.72228 | 0.75181 | 0.8205 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71725 | 0.71822 | 0.72289 | 0.75243 | 0.82126 | 0.74487 | 0.74487 | 0.74487 | 0.74487 | 0.74487 | 0.74487 | 0.74487 | 0.74575 | 0.74934 | 0.78422 | 0.8546 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.8386 | 0.85148 | 0.91548 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-22 00:39 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71749 | 0.72211 | 0.75156 | 0.81989 | 0.71709 | 0.71709 | 0.71709 | 0.71709 | 0.71709 | 0.71709 | 0.71709 | 0.71805 | 0.72271 | 0.75217 | 0.82062 | 0.74465 | 0.74465 | 0.74465 | 0.74465 | 0.74465 | 0.74465 | 0.74465 | 0.74551 | 0.7491 | 0.78382 | 0.85368 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.85055 | 0.91354 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-23 01:41 | 0.71634 | 0.71634 | 0.71634 | 0.71634 | 0.71634 | 0.71634 | 0.71634 | 0.7173 | 0.72191 | 0.75126 | 0.81989 | 0.7169 | 0.7169 | 0.7169 | 0.7169 | 0.7169 | 0.7169 | 0.7169 | 0.71786 | 0.72251 | 0.75186 | 0.82062 | 0.74437 | 0.74437 | 0.74437 | 0.74437 | 0.74437 | 0.74437 | 0.74437 | 0.74522 | 0.7488 | 0.78335 | 0.85368 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.85055 | 0.91354 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-24 02:09 | 0.71616 | 0.71616 | 0.71616 | 0.71616 | 0.71616 | 0.71616 | 0.71616 | 0.71711 | 0.7217 | 0.75095 | 0.81989 | 0.71671 | 0.71671 | 0.71671 | 0.71671 | 0.71671 | 0.71671 | 0.71671 | 0.71768 | 0.72231 | 0.75155 | 0.82062 | 0.74409 | 0.74409 | 0.74409 | 0.74409 | 0.74409 | 0.74409 | 0.74409 | 0.74495 | 0.7485 | 0.78289 | 0.85368 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.8378 | 0.85055 | 0.91354 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-25 02:26 | 0.71597 | 0.71597 | 0.71597 | 0.71597 | 0.71597 | 0.71597 | 0.71597 | 0.71693 | 0.72151 | 0.75095 | 0.81989 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71653 | 0.71749 | 0.72211 | 0.75155 | 0.82062 | 0.74382 | 0.74382 | 0.74382 | 0.74382 | 0.74382 | 0.74382 | 0.74382 | 0.74468 | 0.74822 | 0.78289 | 0.85368 | 0.83691 | 0.83691 | 0.83691 | 0.83691 | 0.83691 | 0.83691 | 0.83691 | 0.83691 | 0.83691 | 0.85055 | 0.91354 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-26 02:49 | 0.71579 | 0.71579 | 0.71579 | 0.71579 | 0.71579 | 0.71579 | 0.71579 | 0.71674 | 0.72131 | 0.75065 | 0.81989 | 0.71635 | 0.71635 | 0.71635 | 0.71635 | 0.71635 | 0.71635 | 0.71635 | 0.7173 | 0.72191 | 0.75126 | 0.82062 | 0.74356 | 0.74356 | 0.74356 | 0.74356 | 0.74356 | 0.74356 | 0.74356 | 0.7444 | 0.74794 | 0.78243 | 0.85368 | 0.83602 | 0.83602 | 0.83602 | 0.83602 | 0.83602 | 0.83602 | 0.83602 | 0.83602 | 0.83602 | 0.84951 | 0.91354 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-27 02:26 | 0.71561 | 0.71561 | 0.71561 | 0.71561 | 0.71561 | 0.71561 | 0.71561 | 0.71656 | 0.72112 | 0.75036 | 0.81917 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71712 | 0.72172 | 0.75096 | 0.81992 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74414 | 0.74765 | 0.782 | 0.8526 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-28 03:00 | 0.71543 | 0.71543 | 0.71543 | 0.71543 | 0.71543 | 0.71543 | 0.71543 | 0.71638 | 0.72092 | 0.75007 | 0.81846 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71617 | 0.71712 | 0.72172 | 0.75096 | 0.81992 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74414 | 0.74765 | 0.782 | 0.8526 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-29 03:28 | 0.71525 | 0.71525 | 0.71525 | 0.71525 | 0.71525 | 0.71525 | 0.71525 | 0.71619 | 0.72072 | 0.74977 | 0.81846 | 0.71598 | 0.71598 | 0.71598 | 0.71598 | 0.71598 | 0.71598 | 0.71598 | 0.71693 | 0.72151 | 0.75067 | 0.81992 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74329 | 0.74414 | 0.74765 | 0.782 | 0.8526 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-04-30 03:45 | 0.71507 | 0.71507 | 0.71507 | 0.71507 | 0.71507 | 0.71507 | 0.71507 | 0.71601 | 0.72053 | 0.74948 | 0.81846 | 0.7158 | 0.7158 | 0.7158 | 0.7158 | 0.7158 | 0.7158 | 0.7158 | 0.71675 | 0.72132 | 0.75037 | 0.81992 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74387 | 0.74737 | 0.78153 | 0.8526 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-01 00:11 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71585 | 0.72036 | 0.74924 | 0.81784 | 0.71565 | 0.71565 | 0.71565 | 0.71565 | 0.71565 | 0.71565 | 0.71565 | 0.7166 | 0.72115 | 0.75012 | 0.81929 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74303 | 0.74387 | 0.74737 | 0.78153 | 0.8526 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-02 00:28 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71567 | 0.72017 | 0.74894 | 0.81784 | 0.71546 | 0.71546 | 0.71546 | 0.71546 | 0.71546 | 0.71546 | 0.71546 | 0.71641 | 0.72096 | 0.74983 | 0.81929 | 0.74275 | 0.74275 | 0.74275 | 0.74275 | 0.74275 | 0.74275 | 0.74275 | 0.7436 | 0.74708 | 0.78109 | 0.8526 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-03 00:51 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71549 | 0.71998 | 0.74866 | 0.81714 | 0.71528 | 0.71528 | 0.71528 | 0.71528 | 0.71528 | 0.71528 | 0.71528 | 0.71623 | 0.72076 | 0.74954 | 0.81858 | 0.74249 | 0.74249 | 0.74249 | 0.74249 | 0.74249 | 0.74249 | 0.74249 | 0.74333 | 0.7468 | 0.78065 | 0.85152 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-04 01:24 | 0.71437 | 0.71437 | 0.71437 | 0.71437 | 0.71437 | 0.71437 | 0.71437 | 0.71531 | 0.71978 | 0.74836 | 0.81641 | 0.7151 | 0.7151 | 0.7151 | 0.7151 | 0.7151 | 0.7151 | 0.7151 | 0.71604 | 0.72056 | 0.74924 | 0.81784 | 0.74223 | 0.74223 | 0.74223 | 0.74223 | 0.74223 | 0.74223 | 0.74223 | 0.74306 | 0.74653 | 0.7802 | 0.85042 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-05 01:52 | 0.7142 | 0.7142 | 0.7142 | 0.7142 | 0.7142 | 0.7142 | 0.7142 | 0.71513 | 0.71959 | 0.74808 | 0.81641 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71492 | 0.71586 | 0.72037 | 0.74895 | 0.81784 | 0.74196 | 0.74196 | 0.74196 | 0.74196 | 0.74196 | 0.74196 | 0.74196 | 0.7428 | 0.74624 | 0.77977 | 0.85042 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-06 02:15 | 0.71402 | 0.71402 | 0.71402 | 0.71402 | 0.71402 | 0.71402 | 0.71402 | 0.71494 | 0.71939 | 0.74778 | 0.81641 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71474 | 0.71567 | 0.72017 | 0.74866 | 0.81784 | 0.7417 | 0.7417 | 0.7417 | 0.7417 | 0.7417 | 0.7417 | 0.7417 | 0.74252 | 0.74596 | 0.77932 | 0.85042 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277
2006-05-07 02:38 | 0.71384 | 0.71384 | 0.71384 | 0.71384 | 0.71384 | 0.71384 | 0.71384 | 0.71476 | 0.7192 | 0.7475 | 0.81572 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71456 | 0.71549 | 0.71998 | 0.74837 | 0.81714 | 0.74143 | 0.74143 | 0.74143 | 0.74143 | 0.74143 | 0.74143 | 0.74143 | 0.74226 | 0.74568 | 0.77889 | 0.84938 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.83514 | 0.84847 | 0.91146 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.92266 | 0.96888 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 1.0206 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0209 | 1.0277