## CH 9 Summary
Results Analysis Example
[37 empty] | Coefficient A | 330.867 | 411.29 | 194.4896 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732
| UV Systems Comparison | [5 empty] | Impact of dose pacing on total and O&M costs | [12 empty] | Reactor | MP Reactor 1 - Hoerl Model |  |  |  | MP Reactor 2 - Mod Exp Model |  |  |  | Amalgam Reactor - Power function model |  |  |  | Non-amalgam Reactor - Mod Exp Model |  |  |  | Coefficient B | -891.6219 | -1830.9318 | -343.378 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343
[20 empty] | Lamp life | 5000 hrs |  |  |  | 5000 hrs |  |  |  | 12000 hrs |  |  |  | 12000 hrs |  |  |  | Coefficient C | -0.17604 | -0.18796 | -0.10815 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| System |  | A | B | C |  | A | B | C | A | B | C | A | B | C | A | B | C | [18 empty] | Coefficient D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamp Type |  | MP1 | MP2 | LPHO |  | MP | MP | LPHO | MP | MP | LPHO | MP | MP | LPHO | MP | MP | LPHO | Electricity |  | Power Costs ($/yr) | [15 empty] | Coefficient E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | $/kWhr | Location | MS | QS | ES | ET | MS | QS | ES | ET | MS | QS | ES | ET | MS | QS | ES | ET | Coefficient F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Design Criteria | Flow | mgd | 46.6667 | 46.6667 | 46.6667 |  | 46.6667 | 46.6667 | 46.6667 | 47 | 47 | 47 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 0.05 | No Dose Pacing | 97928.6016 | 95988.9609 | 98356.3594 | 112003.7109 | 110923.9375 | 111276.1094 | 115736.7969 | 121941.7344 | 21420.4043 | 22155.9883 | 23347.4023 | 28720.2891 | 21429.0312 | 22077.4492 | 25590.1055 | 23072.043 | Lamp Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UVT | % | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0.05 | Flow Pacing | 48964.3008 | 47994.4805 | 49178.1797 | 56001.8555 | 55461.9688 | 55638.0547 | 57868.3984 | 60970.8672 | 10710.2021 | 11077.9941 | 11673.7002 | 14360.1445 | 10714.5156 | 11038.7246 | 12795.0527 | 11536.0215
| Aging | % | 71.7675 | 78.2386 | 70.2112 |  | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 0.05 | Flow/UVT Pacing | 34536.6719 | 33852.6172 | 34687.5273 | 39500.5625 | 41792.6211 | 41925.3086 | 43605.9492 | 45943.7734 | 7819.1123 | 8087.6226 | 8522.5254 | 10483.7969 | 7822.2617 | 8058.9536 | 9341.1826 | 8422.0117 |  | Industry Data |  |  | Measured Data
| Fouling | % | 85 | 95 | 85 |  | 85 | 95 | 85 | 85 | 95 | 85 | 85 | 95 | 85 | 85 | 95 | 85 | 0.05 | Full Dose Pacing | 24251.0215 | 25127.8633 | 25398.1855 | 24752.502 | 36679.5898 | 36342.4258 | 35935.5312 | 38237.5547 | 6129.9697 | 6118.4121 | 6098.4424 | 5998.8418 | 6129.8677 | 6119.6274 | 6058.2256 | 6103.1914 |  |  |  |  | MP1 |  |  |  | MP1 |  |  |  | Amalgam |  |  |  | Non-amalgam
| Dose | mJ/cm2 | 32 | 32 | 28 |  | 32 | 32 | 28 | 32 | 32 | 28 | 32 | 32 | 28 | 32 | 32 | 28 | 0.1 | No Dose Pacing | 195857.2031 | 191977.9219 | 196712.7188 | 224007.4219 | 221847.875 | 222552.2188 | 231473.5938 | 243883.4688 | 42840.8086 | 44311.9766 | 46694.8047 | 57440.5781 | 42858.0625 | 44154.8984 | 51180.2109 | 46144.0859 | Lamp Life | MP1 | MP2 | LPHO1 | Center Side | Quartile Side | End Side | End Top | Center Side | Quartile Side | End Side | End Top | Center Side | Quartile Side | End Side | End Top | Center Side | Quartile Side | End Side | End Top
[19 empty] | 0.1 | Flow Pacing | 97928.6016 | 95988.9609 | 98356.3594 | 112003.7109 | 110923.9375 | 111276.1094 | 115736.7969 | 121941.7344 | 21420.4043 | 22155.9883 | 23347.4004 | 28720.2891 | 21429.0312 | 22077.4492 | 25590.1055 | 23072.043 | 100 | 98.2123 | 99.2104 | 100.6114 | 100 | 100 | 100 | 100 | 99.4322 | 99.287 | 98.9426 | 99.4037 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
[19 empty] | 0.1 | Flow/UVT Pacing | 69073.3438 | 67705.2344 | 69375.0547 | 79001.125 | 83585.2422 | 83850.6172 | 87211.8984 | 91887.5469 | 15638.2246 | 16175.2451 | 17045.0508 | 20967.5938 | 15644.5234 | 16117.9072 | 18682.3652 | 16844.0234 | 200 | 96.5651 | 98.2733 | 98.4225 | 100 | 100 | 100 | 100 | 98.8832 | 98.6057 | 97.939 | 98.8115 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
[19 empty] | 0.1 | Full Dose Pacing | 48502.043 | 50255.7266 | 50796.3711 | 49505.0039 | 73359.1797 | 72684.8516 | 71871.0625 | 76475.1094 | 12259.9395 | 12236.8242 | 12196.8848 | 11997.6836 | 12259.7354 | 12239.2549 | 12116.4512 | 12206.3828 | 300 | 95.0865 | 97.3894 | 96.6407 | 100 | 100 | 100 | 100 | 98.3524 | 97.9547 | 96.9866 | 98.2234 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
System | No. Reactors |  | 2 + 1 | 3 + 1 | 2 + 1 |  | 2 + 1 | 3 + 1 | 2 + 1 | 2 + 1 | 3 + 1 | 2 + 1 | 2 + 1 | 3 + 1 | 2 + 1 | 2 + 1 | 3 + 1 | 2 + 1 | 0.15 | No Dose Pacing | 293785.8125 | 287966.9062 | 295069.0938 | 336011.125 | 332771.8125 | 333828.3438 | 347210.375 | 365825.2188 | 64261.2148 | 66467.9688 | 70042.2031 | 86160.8672 | 64287.0977 | 66232.3516 | 76770.3203 | 69216.1328 | 400 | 93.7471 | 96.5536 | 95.1424 | 97.381 | 98.004 | 98.0189 | 96.9504 | 97.8391 | 97.3327 | 96.0827 | 97.6394 | 99.2355 | 99.0738 | 98.8234 | 97.8398 | 99.2335 | 99.0908 | 98.3866 | 98.8801
| Lamps per Reactor |  | 6 | 8 | 96 |  | 6 | 8 | 96 | 6 | 8 | 96 | 6 | 8 | 96 | 6 | 8 | 96 | 0.15 | Flow Pacing | 146892.9062 | 143983.4531 | 147534.5469 | 168005.5625 | 166385.9062 | 166914.1719 | 173605.1875 | 182912.6094 | 32130.6074 | 33233.9844 | 35021.1016 | 43080.4336 | 32143.5488 | 33116.1758 | 38385.1602 | 34608.0664 | 500 | 92.5245 | 95.7611 | 93.8526 | 93.2822 | 94.8429 | 94.8652 | 92.1412 | 97.3427 | 96.7383 | 95.2248 | 97.0594 | 97.9709 | 97.545 | 96.8881 | 94.3335 | 97.9658 | 97.5897 | 95.7484 | 97.0365
| Lamp Power | kW | 20 | 12 | 0.36 |  | 20 | 12 | 0.36 | 20 | 12 | 0.36 | 20 | 12 | 0.36 | 20 | 12 | 0.36 | 0.15 | Flow/UVT Pacing | 103610.0156 | 101557.8516 | 104062.5859 | 118501.6953 | 125377.8672 | 125775.9219 | 130817.8516 | 137831.3281 | 23457.3379 | 24262.8691 | 25567.5762 | 31451.3906 | 23466.7871 | 24176.8613 | 28023.5488 | 25266.0352 | 600 | 91.4011 | 95.008 | 92.7221 | 90.1968 | 92.429 | 92.4395 | 88.4759 | 96.8627 | 96.1703 | 94.4106 | 96.4835 | 96.9496 | 96.3135 | 95.335 | 91.5621 | 96.942 | 96.3802 | 93.6454 | 95.5558
| Total Duty Power | kW | 360 | 384 | 103.68 |  | 360 | 384 | 103.68 | 360 | 384 | 103.68 | 360 | 384 | 103.68 | 360 | 384 | 103.68 | 0.15 | Full Dose Pacing | 72753.0703 | 75383.5938 | 76194.5547 | 74257.5078 | 110038.7734 | 109027.2812 | 107806.5938 | 114712.6719 | 18389.9102 | 18355.2363 | 18295.3281 | 17996.5254 | 18389.6035 | 18358.8828 | 18174.6777 | 18309.5742 | 700 | 90.3629 | 94.2908 | 91.7173 | 87.7791 | 90.5132 | 90.4996 | 85.5614 | 96.3986 | 95.6276 | 93.6379 | 95.9116 | 96.0944 | 95.2844 | 94.0413 | 89.2826 | 96.0847 | 95.3692 | 91.9034 | 94.3214
[37 empty] | 800 | 89.3987 | 93.6065 | 90.8139 | 85.8313 | 88.9512 | 88.9052 | 83.1739 | 95.9499 | 95.1091 | 92.9046 | 95.3436 | 95.3597 | 94.4018 | 92.9348 | 87.3539 | 95.3482 | 94.5021 | 90.4207 | 93.2651
| Dose pacing |  | None | None | None |  | None | None | None | Flow | Flow | Flow | Flow | Flow | Flow | Flow | Flow | Flow | Electricity |  | Total O&M Costs ($/yr) | [15 empty] | 900 | 88.4994 | 92.9525 | 89.9941 | 84.2306 | 87.6528 | 87.5683 | 81.1744 | 95.5159 | 94.6135 | 92.2086 | 94.7796 | 94.7163 | 93.6301 | 91.9697 | 85.6872 | 94.7033 | 93.7438 | 89.1327 | 92.3432
[13 empty] | UVT | UVT | UVT | UVT | UVT | UVT | $/kWhr | Location | MS | QS | ES | ET | MS | QS | ES | ET | MS | QS | ES | ET | MS | QS | ES | ET | 1000 | 87.6572 | 92.3263 | 89.2444 | 82.8956 | 86.5577 | 86.4302 | 79.4713 | 95.0963 | 94.14 | 91.5481 | 94.2195 | 94.1445 | 92.9452 | 91.1148 | 84.2233 | 94.1301 | 93.0706 | 87.996 | 91.5262
[16 empty] | Sleeve Ag | Sleeve Ag | Sleeve Ag | 0.05 | No Dose Pacing | 117268.7656 | 115329.125 | 117696.5156 | 136178.9062 | 168149.2812 | 168501.4375 | 172962.125 | 179167.0625 | 53173.6094 | 53909.1875 | 57334.2031 | 69407.8906 | 53182.2344 | 53830.6406 | 61810.5 | 57058.8438 | 2000 | 81.347 | 87.2232 | 84.0324 | 76.7484 | 81.2029 | 80.5249 | 70.3983 | 91.5918 | 90.4216 | 86.5373 | 88.8281 | 90.4676 | 88.5622 | 85.6855 | 75.1968 | 90.4446 | 88.7607 | 80.8714 | 86.3288
[16 empty] | Lamp Ag | Lamp Ag | Lamp Ag | 0.05 | Flow Pacing | 58634.375 | 57664.5625 | 58848.2656 | 70506.9688 | 93612.2031 | 93788.2812 | 96018.625 | 99121.0938 | 29061.7969 | 29429.5938 | 32258.9062 | 37178.9375 | 29066.1094 | 29390.3281 | 33380.25 | 32121.2188 | 3000 | 77.203 | 83.5025 | 80.8639 | 75.9059 | 80.0349 | 78.706 | 67.0486 | 89.0874 | 88.062 | 83.5666 | 83.7997 | 88.3837 | 86.0948 | 82.6609 | 70.3719 | 88.356 | 86.3327 | 76.9742 | 83.4265
[19 empty] | 0.05 | Flow/UVT Pacing | 44206.75 | 43522.7031 | 44357.6094 | 49170.6406 | 60867.7344 | 61000.4219 | 81756.1719 | 84094 | 23937.1094 | 24205.625 | 24640.5312 | 28835.3906 | 23940.2656 | 24176.9531 | 25459.1875 | 24540.0156 | 4000 | 74.1565 | 80.6013 | 78.6076 | 77.1291 | 80.4945 | 78.4526 | 65.7816 | 87.2976 | 86.5647 | 81.8054 | 79.1097 | 86.9343 | 84.386 | 80.5798 | 67.1376 | 86.9034 | 84.6504 | 74.3236 | 81.4266
O&M | Power | $/yr | 105202.9609 | 118236.9609 | 24096.2715 |  | 105202.9609 | 118236.9609 | 24096.2715 | 52862.9727 | 59402.5508 | 12115.3936 | 37102.1289 | 44547.9375 | 8795.8867 | 26904.2305 | 36797.375 | 6101.1543 | 0.05 | Full Dose Pacing | 29086.0625 | 29962.9062 | 30233.2188 | 29587.5469 | 55754.7031 | 55417.5469 | 55010.6406 | 57312.6719 | 20014.375 | 20002.8125 | 19982.8438 | 19883.25 | 20014.2656 | 20004.0312 | 19942.625 | 19987.5938 | 5000 | 71.7675 | 78.2386 | 76.8656 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 85.8264 | 83.0839 | 79.0017 | 64.7316 | 85.7932 | 83.3681 | 72.3306 | 79.9084
| Consumables | [17 empty] | 0.1 | No Dose Pacing | 215197.375 | 211318.0938 | 216052.875 | 248182.625 | 279073.2188 | 279777.5625 | 288698.9375 | 301108.8125 | 74594 | 76065.1719 | 80681.6094 | 98128.1875 | 74611.2656 | 75908.0938 | 87400.6094 | 80130.8906 | 6000 | 69.8139 | 76.2551 | 75.4526 | 82.8009 | 83.8306 | 80.1858 | 66.0881 | 85.1043 | 85.0117 | 80.1422 | 70.6556 | 84.9317 | 82.0349 | 77.7353 | 62.8299 | 84.8966 | 82.3349 | 70.7419 | 78.689
| Lamps | $/yr | 15111 | 11563.2002 | 18220.8008 |  | 15111 | 11563.2002 | 18220.8008 | 9066.5996 | 7708.7998 | 9811.2002 | 6044.3999 | 7708.7998 | 7008 | 6044.3999 | 3854.3999 | 5606.3999 | 0.1 | Flow Pacing | 107598.6875 | 105659.0469 | 108026.4375 | 126508.8281 | 149074.1562 | 149426.3438 | 153887.0312 | 160091.9688 | 39772 | 40507.5938 | 43932.5938 | 51539.0938 | 39780.625 | 40429.0469 | 46175.3125 | 43657.25 | 7000 | 68.1683 | 74.5519 | 74.2675 | 86.753 | 86.2665 | 81.7255 | 67.0576 | 84.4511 | 84.6291 | 79.7752 | 66.8504 | 84.1826 | 81.1584 | 76.6805 | 61.2656 | 84.1458 | 81.4712 | 69.426 | 77.6726
| Sleeves | $/yr | 1050 | 840 | 1560 |  | 1050 | 840 | 1560 | 630 | 560 | 840 | 420 | 560 | 600 | 420 | 280 | 480 | 0.1 | Flow/UVT Pacing | 78743.4219 | 77375.3125 | 79045.1406 | 88671.2031 | 102660.3594 | 102925.7344 | 125362.125 | 130037.7812 | 31756.2188 | 32293.25 | 33163.0469 | 39319.1875 | 31762.5312 | 32235.9062 | 34800.3594 | 32962.0312 | 8000 | 66.7515 | 73.0638 | 73.2491 | 91.3248 | 89.0879 | 83.5814 | 68.3957 | 83.9842 | 84.3863 | 79.5576 | 63.3013 | 83.539 | 80.4066 | 75.7783 | 59.9422 | 83.5009 | 80.7305 | 68.3059 | 76.8027
| Ballasts | $/yr | 2700 | 14400 | 4680 |  | 2700 | 14400 | 4680 | 1620 | 9600 | 2520 | 1080 | 9600 | 1800 | 1080 | 4800 | 1440 | 0.1 | Full Dose Pacing | 53337.0781 | 55090.7656 | 55631.4062 | 54340.0469 | 92434.2969 | 91759.9688 | 90946.1719 | 95550.2188 | 26144.3438 | 26121.2188 | 26081.2812 | 25882.0781 | 26144.1406 | 26123.6562 | 26000.8438 | 26090.7812 | 9000 | 65.5107 | 71.7455 | 72.3578 | 96.4855 | 92.2505 | 85.7039 | 70.0378 | 83.6506 | 84.2323 | 79.4286 | 59.9911 | 82.9753 | 79.7493 | 74.9913 | 58.7985 | 82.9361 | 80.0826 | 67.3329 | 76.0435
| Sensors | $/yr | 3600 | 16800 | 845 |  | 3600 | 16800 | 845 | 2160 | 11200 | 455 | 1440 | 11200 | 325 | 1440 | 5600 | 260 | 0.15 | No Dose Pacing | 313125.9688 | 307307.0625 | 314409.25 | 360186.3125 | 389997.1562 | 391053.6875 | 404435.6875 | 423050.5625 | 96014.4062 | 98221.1719 | 104029 | 126848.4688 | 96040.2969 | 97985.5469 | 112990.7188 | 103202.9375 | 10000 | 64.4094 | 70.5644 | 71.5665 | 102.2289 | 95.7292 | 88.0624 | 71.9441 | 83.4121 | 84.1345 | 79.3522 | 56.9038 | 82.4744 | 79.1659 | 74.2942 | 57.794 | 82.4341 | 79.5076 | 66.4743 | 75.3708
| Calibration | $/yr | 1050 | 13200 | 2990 |  | 1050 | 13200 | 2990 | 630 | 8800 | 1610 | 420 | 8800 | 1150 | 420 | 4400 | 920 | 0.15 | Flow Pacing | 156563 | 153653.5312 | 157204.625 | 182510.6875 | 204536.125 | 205064.4062 | 211755.4062 | 221062.8438 | 50482.2031 | 51585.5781 | 55606.2969 | 65899.2344 | 50495.1562 | 51467.7812 | 58970.3594 | 55193.2656 | 12000 | 62.5259 | 68.5229 | 70.2112 | 115.5118 | 103.5889 | 93.4168 | 76.459 | 83.1199 | 84.0331 | 79.2799 | 51.3386 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206
| Total Consumables | $/yr | 23511 | 56803.1992 | 28295.8008 |  | 23511 | 56803.1992 | 28295.8008 | 14106.5996 | 37868.8008 | 15236.2002 | 9404.4004 | 37868.8008 | 10883 | 9404.4004 | 18934.4004 | 8706.4004 | 0.15 | Flow/UVT Pacing | 113280.0938 | 111227.9375 | 113732.6719 | 128171.7812 | 144452.9688 | 144851.0312 | 168968.0938 | 175981.5625 | 39575.3438 | 40380.875 | 41685.5781 | 49802.9844 | 39584.7812 | 40294.8594 | 44141.5469 | 41384.0312 | 14000 | 60.9584 | 66.8053 | 69.0802 | 131.3671 | 112.6371 | 99.5629 | 81.8359 | 82.9707 | 83.9923 | 79.2546 | 46.4974 | 80.8947 | 77.3312 | 72.1113 | 54.6995 | 80.8513 | 77.6985 | 63.8049 | 73.2619
| Labor | $/yr | 664.2 | 422.144 | 5691.0005 |  | 664.2 | 422.144 | 5691.0005 | 398.52 | 281.4293 | 5349 | 265.68 | 281.4293 | 5235 | 265.68 | 140.7147 | 5178 | 0.15 | Full Dose Pacing | 77588.1094 | 80218.6406 | 81029.5938 | 79092.5469 | 129113.8906 | 128102.3906 | 126881.7031 | 133787.7812 | 32274.3125 | 32239.6406 | 32179.7344 | 31880.9219 | 32274 | 32243.2812 | 32059.0781 | 32193.9688 | 16000 | 59.621 | 65.328 | 68.1118 | 150.1072 | 122.9099 | 106.4785 | 88.0472 | 82.8945 | 83.9758 | 79.2456 | 42.286 | 80.2763 | 76.6149 | 71.2629 | 53.5179 | 80.2316 | 76.992 | 62.7754 | 72.4414
| Patent | $/yr | 127750 | 127750 | 127750 |  | 127750 | 127750 | 127750 | 128662.5 | 128662.5 | 128662.5 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | [18 empty] | 18000 | 58.458 | 64.0356 | 67.2667 | 172.1416 | 134.4825 | 114.1735 | 95.1064 | 82.8556 | 83.9692 | 79.2425 | 38.6226 | 79.7346 | 75.9887 | 70.5228 | 52.4968 | 79.6889 | 76.3742 | 61.8812 | 71.7253
| Total O&M | $/yr | 257128.1562 | 303212.3125 | 185833.0781 |  | 257128.1562 | 303212.3125 | 185833.0781 | 196030.5938 | 226215.2812 | 161363.0938 | 174522.2031 | 210448.1719 | 152663.8906 | 164324.3125 | 183622.4844 | 147735.5625 |  |  | Max UV Dose Under Design flow, UVT, lamp aging, and fouling | [15 empty] | 20000 | 57.4315 | 62.8895 | 66.518 | 197.9739 | 147.4588 | 122.6783 | 103.0537 | 82.8357 | 83.9666 | 79.2414 | 35.4357 | 79.2533 | 75.4328 | 69.8673 | 51.6 | 79.2066 | 75.8258 | 61.0921 | 71.0908
| Total Capital | $ | 750709 | 1000000 | 750000 |  | 750709 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 |  | Location | MS | QS | ES | ET | MS | QS | ES | ET | MS | QS | ES | ET | MS | QS | ES | ET
| Total Present Worth | $ | 3609559.5 | 4371232 | 2816164 |  | 3609559.5 | 4371232 | 2816164 | 2929544 | 3515149 | 2544097.25 | 2690405.5 | 3339844.25 | 2447376.25 | 2577021.25 | 3041586 | 2392581.25 |  | No Dose Pacing | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409
| Present Worth O&M | $ | 2858850.5 | 3371232 | 2066164 |  | 2858850.5 | 3371232 | 2066164 | 2179544 | 2515149 | 1794097.25 | 1940405.5 | 2339844.25 | 1697376.25 | 1827021.25 | 2041586 | 1642581.25 |  | Flow Pacing | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409
[20 empty] | Flow/UVT Pacing | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409
|  |  | MP 1 | MP 2 | LPHO |  | MP 1 | MP 2 | LPHO | MP 1 | MP 2 | LPHO | MP 1 | MP 2 | LPHO | MP 1 | MP 2 | LPHO |  | Full Dose Pacing | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409
|  | Reactor capital | 750.709 | 1000 | 750 | Reactor capital | 750.709 | 1000 | 750 | 750 | 1000 | 750 | 750 | 1000 | 750 | 750 | 1000 | 750
|  | Building and Piping | 1100 | 1100 | 1100 | Building and Piping | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100
|  | UPS | 360 | 384 | 103.68 | UPS | 360 | 384 | 103.68 | 360 | 384 | 103.68 | 360 | 384 | 103.68 | 360 | 384 | 103.68
|  | Other Consumables | 93.3945 | 502.9959 | 112.0177 | Other Consumables | 93.3945 | 502.9959 | 112.0177 | 56.0367 | 335.3305 | 60.3172 | 37.3578 | 335.3306 | 43.0838 | 37.3578 | 167.6653 | 34.467
|  | Labor | 7.3848 | 4.6936 | 63.2747 | Labor | 7.3848 | 4.6936 | 63.2747 | 4.4309 | 3.129 | 59.4722 | 2.9539 | 3.129 | 58.2048 | 2.9539 | 1.5645 | 57.571
|  | Lamps | 168.01 | 128.5641 | 202.5859 | Lamps | 168.01 | 128.5641 | 202.5859 | 100.806 | 85.7094 | 109.0847 | 67.204 | 85.7094 | 77.9177 | 67.204 | 42.8547 | 62.3341
|  | Power | 1169.6873 | 1314.6044 | 267.9117 | Power | 1169.6873 | 1314.6044 | 267.9117 | 587.751 | 660.4605 | 134.7036 | 412.5159 | 495.3012 | 97.7961 | 299.1316 | 409.1275 | 67.835
|  | Patent | 1420.374 | 1420.374 | 1420.3739 | Patent | 1420.374 | 1420.374 | 1420.3739 | 1430.5195 | 1430.5194 | 1430.5194 | 1420.374 | 1420.374 | 1420.374 | 1420.3739 | 1420.374 | 1420.374

## STANDARD LCA
NYSERDA - Life Cycle Cost Analysis Tool
Starting Column | 1
Ending Column | 1
Analysis Using Lamp Aging Data Developed in This Project
Lamp Aging Functions |  | Analysis Using UV Vendor Lamp Aging Data | [11 empty] | 5 cents/kwhr | [63 empty] | 10 cents/kwhr | [63 empty] | 10 cents/kwhr
Units: y = %, x = hrs
MMF: y=(a*b+c*x^d)/(b+x^d) | [13 empty] | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Hoerl Model | Hoerl Model | Hoerl Model | Hoerl Model | Mod Exp | Mod Exp | Mod Exp | Mod Exp | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr | Pwr
EXP: y=a*e^(b*x) | [13 empty] | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top | Middle Side | Quartile Side | End Side | End Top
LIN: Y = ax+b
[11 empty] | Flow, UVT, Sleeve and Lamp | [50 empty] | Flow, UVT, Sleeve and Lamp | [63 empty] | Flow, UVT, Sleeve and Lamp | [63 empty] | Flow, UVT, Sleeve and Lamp
COMMENTS | Vendor | No dose pacing |  |  | Flow dosing pacing |  |  | Flow and UVT dosing pacing |  |  | Dose Pacing |  |  | No dose pacing | [15 empty] | Flow dosing pacing | [15 empty] | Flow and UVT dosing pacing | [15 empty] | Dose Pacing | [15 empty] | No dose pacing | [15 empty] | Flow dosing pacing | [15 empty] | Flow and UVT dosing pacing | [15 empty] | Dose Pacing | [15 empty] | No dose pacing | [15 empty] | Flow dosing pacing | [15 empty] | Flow and UVT dosing pacing | [15 empty] | Dose Pacing
| Lamp Type | MP | MP | LPHO | MP | MP | LPHO | MP | MP | LPHO | MP | MP | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO | MP1 | MP1 | MP1 | MP1 | MP2 | MP2 | MP2 | MP2 | Amalgam | Amalgam | Amalgam | Amalgam | LPHO | LPHO | LPHO | LPHO
| Vendor | A | B | C | A | B | C | A | B | C | A | B | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C | A | A | A | A | B | B | B | B | C | C | C | C | C | C | C | C
OUTPUTS | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204
Lamp Life |  | 5000 | 5000 | 12000 | 5000 | 5000 | 12000 | 5000 | 5000 | 12000 | 5000 | 5000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000
Age Factor |  | 0.71768 | 0.78239 | 0.70211 | 0.71768 | 0.78239 | 0.70211 | 0.71768 | 0.78239 | 0.70211 | 0.71768 | 0.78239 | 0.70211 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221 | 0.79541 | 0.81858 | 0.79045 | 0.65597 | 0.86018 | 0.85615 | 0.80761 | 0.74735 | 0.81615 | 0.78166 | 0.73103 | 0.56096 | 0.81573 | 0.78522 | 0.65014 | 0.74221
Average # Lamps |  | 15 | 24 | 156 | 9 | 16 | 84 | 6 | 16 | 60 | 6 | 8 | 48 | 12 | 12 | 12 | 15 | 24 | 24 | 24 | 24 | 144 | 144 | 156 | 192 | 144 | 144 | 168 | 156 | 6 | 6 | 6 | 9 | 16 | 16 | 16 | 16 | 72 | 72 | 84 | 96 | 72 | 72 | 84 | 84 | 6 | 6 | 6 | 6 | 8 | 8 | 16 | 16 | 60 | 60 | 60 | 72 | 60 | 60 | 60 | 60 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 12 | 12 | 12 | 15 | 24 | 24 | 24 | 24 | 144 | 144 | 156 | 192 | 144 | 144 | 168 | 156 | 6 | 6 | 6 | 9 | 16 | 16 | 16 | 16 | 72 | 72 | 84 | 96 | 72 | 72 | 84 | 84 | 6 | 6 | 6 | 6 | 8 | 8 | 16 | 16 | 60 | 60 | 60 | 72 | 60 | 60 | 60 | 60 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 12 | 12 | 12 | 15 | 24 | 24 | 24 | 24 | 144 | 144 | 156 | 192 | 144 | 144 | 168 | 156 | 6 | 6 | 6 | 9 | 16 | 16 | 16 | 16 | 72 | 72 | 84 | 96 | 72 | 72 | 84 | 84 | 6 | 6 | 6 | 6 | 8 | 8 | 16 | 16 | 60 | 60 | 60 | 72 | 60 | 60 | 60 | 60 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
Average Power Level | % | 0.80063 | 0.93732 | 0.9796 | 0.67051 | 0.70637 | 0.91471 | 0.7059 | 0.52973 | 0.92972 | 0.51188 | 0.87513 | 0.80611 | 0.93159 | 0.91314 | 0.93566 | 0.85239 | 0.87934 | 0.88214 | 0.9175 | 0.96669 | 0.94338 | 0.97578 | 0.94916 | 0.94866 | 0.94376 | 0.97232 | 0.96602 | 0.93796 | 0.93159 | 0.91314 | 0.93566 | 0.71032 | 0.65951 | 0.6616 | 0.68812 | 0.72502 | 0.94338 | 0.97578 | 0.88136 | 0.94866 | 0.94376 | 0.97232 | 0.96602 | 0.87096 | 0.65709 | 0.64408 | 0.65996 | 0.75153 | 0.99393 | 0.99708 | 0.51853 | 0.54633 | 0.82647 | 0.85486 | 0.90082 | 0.92344 | 0.82681 | 0.85183 | 0.98736 | 0.8902 | 0.92279 | 0.95616 | 0.96645 | 0.94188 | 0.87233 | 0.86431 | 0.85463 | 0.90938 | 0.80992 | 0.80839 | 0.80575 | 0.79259 | 0.8099 | 0.80855 | 0.80044 | 0.80638 | 0.93159 | 0.91314 | 0.93566 | 0.85239 | 0.87934 | 0.88214 | 0.9175 | 0.96669 | 0.94338 | 0.97578 | 0.94916 | 0.94866 | 0.94376 | 0.97232 | 0.96602 | 0.93796 | 0.93159 | 0.91314 | 0.93566 | 0.71032 | 0.65951 | 0.6616 | 0.68812 | 0.72502 | 0.94338 | 0.97578 | 0.88136 | 0.94866 | 0.94376 | 0.97232 | 0.96602 | 0.87096 | 0.65709 | 0.64408 | 0.65996 | 0.75153 | 0.99393 | 0.99708 | 0.51853 | 0.54633 | 0.82647 | 0.85486 | 0.90082 | 0.92344 | 0.82681 | 0.85183 | 0.98736 | 0.8902 | 0.92279 | 0.95616 | 0.96645 | 0.94188 | 0.87233 | 0.86431 | 0.85463 | 0.90938 | 0.80992 | 0.80839 | 0.80575 | 0.79259 | 0.8099 | 0.80855 | 0.80044 | 0.80638 | 0.93159 | 0.91314 | 0.93566 | 0.85239 | 0.87934 | 0.88214 | 0.9175 | 0.96669 | 0.94338 | 0.97578 | 0.94916 | 0.94866 | 0.94376 | 0.97232 | 0.96602 | 0.93796 | 0.93159 | 0.91314 | 0.93566 | 0.71032 | 0.65951 | 0.6616 | 0.68812 | 0.72502 | 0.94338 | 0.97578 | 0.88136 | 0.94866 | 0.94376 | 0.97232 | 0.96602 | 0.87096 | 0.65709 | 0.64408 | 0.65996 | 0.75153 | 0.99393 | 0.99708 | 0.51853 | 0.54633 | 0.82647 | 0.85486 | 0.90082 | 0.92344 | 0.82681 | 0.85183 | 0.98736 | 0.8902 | 0.92279 | 0.95616 | 0.96645 | 0.94188 | 0.87233 | 0.86431 | 0.85463 | 0.90938 | 0.80992 | 0.80839 | 0.80575 | 0.79259 | 0.8099 | 0.80855 | 0.80044 | 0.80638
Power | $/yr | 105202.9609 | 118236.9609 | 24096.2715 | 52862.9727 | 59402.5508 | 12115.3936 | 37102.1289 | 44547.9375 | 8795.8867 | 26904.2305 | 36797.375 | 6101.1543 | 97928.6016 | 95988.9609 | 98356.3594 | 112003.7109 | 110923.9375 | 111276.1094 | 115736.7969 | 121941.7344 | 21420.4043 | 22155.9883 | 23347.4023 | 28720.2891 | 21429.0312 | 22077.4492 | 25590.1055 | 23072.043 | 48964.3008 | 47994.4805 | 49178.1797 | 56001.8555 | 55461.9688 | 55638.0547 | 57868.3984 | 60970.8672 | 10710.2021 | 11077.9941 | 11673.7002 | 14360.1445 | 10714.5156 | 11038.7246 | 12795.0527 | 11536.0215 | 34536.6719 | 33852.6172 | 34687.5273 | 39500.5625 | 41792.6211 | 41925.3086 | 43605.9492 | 45943.7734 | 7819.1123 | 8087.6226 | 8522.5254 | 10483.7969 | 7822.2617 | 8058.9536 | 9341.1826 | 8422.0117 | 24251.0215 | 25127.8633 | 25398.1855 | 24752.502 | 36679.5898 | 36342.4258 | 35935.5312 | 38237.5547 | 6129.9697 | 6118.4121 | 6098.4424 | 5998.8418 | 6129.8677 | 6119.6274 | 6058.2256 | 6103.1914 | 195857.2031 | 191977.9219 | 196712.7188 | 224007.4219 | 221847.875 | 222552.2188 | 231473.5938 | 243883.4688 | 42840.8086 | 44311.9766 | 46694.8047 | 57440.5781 | 42858.0625 | 44154.8984 | 51180.2109 | 46144.0859 | 97928.6016 | 95988.9609 | 98356.3594 | 112003.7109 | 110923.9375 | 111276.1094 | 115736.7969 | 121941.7344 | 21420.4043 | 22155.9883 | 23347.4004 | 28720.2891 | 21429.0312 | 22077.4492 | 25590.1055 | 23072.043 | 69073.3438 | 67705.2344 | 69375.0547 | 79001.125 | 83585.2422 | 83850.6172 | 87211.8984 | 91887.5469 | 15638.2246 | 16175.2451 | 17045.0508 | 20967.5938 | 15644.5234 | 16117.9072 | 18682.3652 | 16844.0234 | 48502.043 | 50255.7266 | 50796.3711 | 49505.0039 | 73359.1797 | 72684.8516 | 71871.0625 | 76475.1094 | 12259.9395 | 12236.8242 | 12196.8848 | 11997.6836 | 12259.7354 | 12239.2549 | 12116.4512 | 12206.3828 | 293785.8125 | 287966.9062 | 295069.0938 | 336011.125 | 332771.8125 | 333828.3438 | 347210.375 | 365825.2188 | 64261.2148 | 66467.9688 | 70042.2031 | 86160.8672 | 64287.0977 | 66232.3516 | 76770.3203 | 69216.1328 | 146892.9062 | 143983.4531 | 147534.5469 | 168005.5625 | 166385.9062 | 166914.1719 | 173605.1875 | 182912.6094 | 32130.6074 | 33233.9844 | 35021.1016 | 43080.4336 | 32143.5488 | 33116.1758 | 38385.1602 | 34608.0664 | 103610.0156 | 101557.8516 | 104062.5859 | 118501.6953 | 125377.8672 | 125775.9219 | 130817.8516 | 137831.3281 | 23457.3379 | 24262.8691 | 25567.5762 | 31451.3906 | 23466.7871 | 24176.8613 | 28023.5488 | 25266.0352 | 72753.0703 | 75383.5938 | 76194.5547 | 74257.5078 | 110038.7734 | 109027.2812 | 107806.5938 | 114712.6719 | 18389.9102 | 18355.2363 | 18295.3281 | 17996.5254 | 18389.6035 | 18358.8828 | 18174.6777 | 18309.5742
Consumables
Lamps | $/yr | 15111 | 11563.2002 | 18220.8008 | 9066.5996 | 7708.7998 | 9811.2002 | 6044.3999 | 7708.7998 | 7008 | 6044.3999 | 3854.3999 | 5606.3999 | 12088.7998 | 12088.7998 | 12088.7998 | 15111 | 11563.2002 | 11563.2002 | 11563.2002 | 11563.2002 | 16819.1992 | 16819.1992 | 18220.8008 | 22425.5996 | 16819.1992 | 16819.1992 | 19622.4004 | 18220.8008 | 6044.3999 | 6044.3999 | 6044.3999 | 9066.5996 | 7708.7998 | 7708.7998 | 7708.7998 | 7708.7998 | 8409.5996 | 8409.5996 | 9811.2002 | 11212.7998 | 8409.5996 | 8409.5996 | 9811.2002 | 9811.2002 | 6044.3999 | 6044.3999 | 6044.3999 | 6044.3999 | 3854.3999 | 3854.3999 | 7708.7998 | 7708.7998 | 7008 | 7008 | 7008 | 8409.5996 | 7008 | 7008 | 7008 | 7008 | 3022.2 | 3022.2 | 3022.2 | 3022.2 | 3854.3999 | 3854.3999 | 3854.3999 | 3854.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 12088.7998 | 12088.7998 | 12088.7998 | 15111 | 11563.2002 | 11563.2002 | 11563.2002 | 11563.2002 | 16819.1992 | 16819.1992 | 18220.8008 | 22425.5996 | 16819.1992 | 16819.1992 | 19622.4004 | 18220.8008 | 6044.3999 | 6044.3999 | 6044.3999 | 9066.5996 | 7708.7998 | 7708.7998 | 7708.7998 | 7708.7998 | 8409.5996 | 8409.5996 | 9811.2002 | 11212.7998 | 8409.5996 | 8409.5996 | 9811.2002 | 9811.2002 | 6044.3999 | 6044.3999 | 6044.3999 | 6044.3999 | 3854.3999 | 3854.3999 | 7708.7998 | 7708.7998 | 7008 | 7008 | 7008 | 8409.5996 | 7008 | 7008 | 7008 | 7008 | 3022.2 | 3022.2 | 3022.2 | 3022.2 | 3854.3999 | 3854.3999 | 3854.3999 | 3854.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 12088.7998 | 12088.7998 | 12088.7998 | 15111 | 11563.2002 | 11563.2002 | 11563.2002 | 11563.2002 | 16819.1992 | 16819.1992 | 18220.8008 | 22425.5996 | 16819.1992 | 16819.1992 | 19622.4004 | 18220.8008 | 6044.3999 | 6044.3999 | 6044.3999 | 9066.5996 | 7708.7998 | 7708.7998 | 7708.7998 | 7708.7998 | 8409.5996 | 8409.5996 | 9811.2002 | 11212.7998 | 8409.5996 | 8409.5996 | 9811.2002 | 9811.2002 | 6044.3999 | 6044.3999 | 6044.3999 | 6044.3999 | 3854.3999 | 3854.3999 | 7708.7998 | 7708.7998 | 7008 | 7008 | 7008 | 8409.5996 | 7008 | 7008 | 7008 | 7008 | 3022.2 | 3022.2 | 3022.2 | 3022.2 | 3854.3999 | 3854.3999 | 3854.3999 | 3854.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999 | 5606.3999
Sleeves | $/yr | 1050 | 840 | 1560 | 630 | 560 | 840 | 420 | 560 | 600 | 420 | 280 | 480 | 840 | 840 | 840 | 1050 | 840 | 840 | 840 | 840 | 1440 | 1440 | 1560 | 1920 | 1440 | 1440 | 1680 | 1560 | 420 | 420 | 420 | 630 | 560 | 560 | 560 | 560 | 720 | 720 | 840 | 960 | 720 | 720 | 840 | 840 | 420 | 420 | 420 | 420 | 280 | 280 | 560 | 560 | 600 | 600 | 600 | 720 | 600 | 600 | 600 | 600 | 210 | 210 | 210 | 210 | 280 | 280 | 280 | 280 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 840 | 840 | 840 | 1050 | 840 | 840 | 840 | 840 | 1440 | 1440 | 1560 | 1920 | 1440 | 1440 | 1680 | 1560 | 420 | 420 | 420 | 630 | 560 | 560 | 560 | 560 | 720 | 720 | 840 | 960 | 720 | 720 | 840 | 840 | 420 | 420 | 420 | 420 | 280 | 280 | 560 | 560 | 600 | 600 | 600 | 720 | 600 | 600 | 600 | 600 | 210 | 210 | 210 | 210 | 280 | 280 | 280 | 280 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 840 | 840 | 840 | 1050 | 840 | 840 | 840 | 840 | 1440 | 1440 | 1560 | 1920 | 1440 | 1440 | 1680 | 1560 | 420 | 420 | 420 | 630 | 560 | 560 | 560 | 560 | 720 | 720 | 840 | 960 | 720 | 720 | 840 | 840 | 420 | 420 | 420 | 420 | 280 | 280 | 560 | 560 | 600 | 600 | 600 | 720 | 600 | 600 | 600 | 600 | 210 | 210 | 210 | 210 | 280 | 280 | 280 | 280 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480
Ballasts | $/yr | 2700 | 14400 | 4680 | 1620 | 9600 | 2520 | 1080 | 9600 | 1800 | 1080 | 4800 | 1440 | 2160 | 2160 | 2160 | 2700 | 14400 | 14400 | 14400 | 14400 | 4320 | 4320 | 4680 | 5760 | 4320 | 4320 | 5040 | 4680 | 1080 | 1080 | 1080 | 1620 | 9600 | 9600 | 9600 | 9600 | 2160 | 2160 | 2520 | 2880 | 2160 | 2160 | 2520 | 2520 | 1080 | 1080 | 1080 | 1080 | 4800 | 4800 | 9600 | 9600 | 1800 | 1800 | 1800 | 2160 | 1800 | 1800 | 1800 | 1800 | 540 | 540 | 540 | 540 | 4800 | 4800 | 4800 | 4800 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 2160 | 2160 | 2160 | 2700 | 14400 | 14400 | 14400 | 14400 | 4320 | 4320 | 4680 | 5760 | 4320 | 4320 | 5040 | 4680 | 1080 | 1080 | 1080 | 1620 | 9600 | 9600 | 9600 | 9600 | 2160 | 2160 | 2520 | 2880 | 2160 | 2160 | 2520 | 2520 | 1080 | 1080 | 1080 | 1080 | 4800 | 4800 | 9600 | 9600 | 1800 | 1800 | 1800 | 2160 | 1800 | 1800 | 1800 | 1800 | 540 | 540 | 540 | 540 | 4800 | 4800 | 4800 | 4800 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 2160 | 2160 | 2160 | 2700 | 14400 | 14400 | 14400 | 14400 | 4320 | 4320 | 4680 | 5760 | 4320 | 4320 | 5040 | 4680 | 1080 | 1080 | 1080 | 1620 | 9600 | 9600 | 9600 | 9600 | 2160 | 2160 | 2520 | 2880 | 2160 | 2160 | 2520 | 2520 | 1080 | 1080 | 1080 | 1080 | 4800 | 4800 | 9600 | 9600 | 1800 | 1800 | 1800 | 2160 | 1800 | 1800 | 1800 | 1800 | 540 | 540 | 540 | 540 | 4800 | 4800 | 4800 | 4800 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440
Sensors | $/yr | 3600 | 16800 | 845 | 2160 | 11200 | 455 | 1440 | 11200 | 325 | 1440 | 5600 | 260 | 2880 | 2880 | 2880 | 3600 | 16800 | 16800 | 16800 | 16800 | 780 | 780 | 845 | 1040 | 780 | 780 | 910 | 845 | 1440 | 1440 | 1440 | 2160 | 11200 | 11200 | 11200 | 11200 | 390 | 390 | 455 | 520 | 390 | 390 | 455 | 455 | 1440 | 1440 | 1440 | 1440 | 5600 | 5600 | 11200 | 11200 | 325 | 325 | 325 | 390 | 325 | 325 | 325 | 325 | 720 | 720 | 720 | 720 | 5600 | 5600 | 5600 | 5600 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 2880 | 2880 | 2880 | 3600 | 16800 | 16800 | 16800 | 16800 | 780 | 780 | 845 | 1040 | 780 | 780 | 910 | 845 | 1440 | 1440 | 1440 | 2160 | 11200 | 11200 | 11200 | 11200 | 390 | 390 | 455 | 520 | 390 | 390 | 455 | 455 | 1440 | 1440 | 1440 | 1440 | 5600 | 5600 | 11200 | 11200 | 325 | 325 | 325 | 390 | 325 | 325 | 325 | 325 | 720 | 720 | 720 | 720 | 5600 | 5600 | 5600 | 5600 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 2880 | 2880 | 2880 | 3600 | 16800 | 16800 | 16800 | 16800 | 780 | 780 | 845 | 1040 | 780 | 780 | 910 | 845 | 1440 | 1440 | 1440 | 2160 | 11200 | 11200 | 11200 | 11200 | 390 | 390 | 455 | 520 | 390 | 390 | 455 | 455 | 1440 | 1440 | 1440 | 1440 | 5600 | 5600 | 11200 | 11200 | 325 | 325 | 325 | 390 | 325 | 325 | 325 | 325 | 720 | 720 | 720 | 720 | 5600 | 5600 | 5600 | 5600 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260
Calibration | $/yr | 1050 | 13200 | 2990 | 630 | 8800 | 1610 | 420 | 8800 | 1150 | 420 | 4400 | 920 | 840 | 840 | 840 | 1050 | 13200 | 13200 | 13200 | 13200 | 2760 | 2760 | 2990 | 3680 | 2760 | 2760 | 3220 | 2990 | 420 | 420 | 420 | 630 | 8800 | 8800 | 8800 | 8800 | 1380 | 1380 | 1610 | 1840 | 1380 | 1380 | 1610 | 1610 | 420 | 420 | 420 | 420 | 4400 | 4400 | 8800 | 8800 | 1150 | 1150 | 1150 | 1380 | 1150 | 1150 | 1150 | 1150 | 210 | 210 | 210 | 210 | 4400 | 4400 | 4400 | 4400 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 840 | 840 | 840 | 1050 | 13200 | 13200 | 13200 | 13200 | 2760 | 2760 | 2990 | 3680 | 2760 | 2760 | 3220 | 2990 | 420 | 420 | 420 | 630 | 8800 | 8800 | 8800 | 8800 | 1380 | 1380 | 1610 | 1840 | 1380 | 1380 | 1610 | 1610 | 420 | 420 | 420 | 420 | 4400 | 4400 | 8800 | 8800 | 1150 | 1150 | 1150 | 1380 | 1150 | 1150 | 1150 | 1150 | 210 | 210 | 210 | 210 | 4400 | 4400 | 4400 | 4400 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 840 | 840 | 840 | 1050 | 13200 | 13200 | 13200 | 13200 | 2760 | 2760 | 2990 | 3680 | 2760 | 2760 | 3220 | 2990 | 420 | 420 | 420 | 630 | 8800 | 8800 | 8800 | 8800 | 1380 | 1380 | 1610 | 1840 | 1380 | 1380 | 1610 | 1610 | 420 | 420 | 420 | 420 | 4400 | 4400 | 8800 | 8800 | 1150 | 1150 | 1150 | 1380 | 1150 | 1150 | 1150 | 1150 | 210 | 210 | 210 | 210 | 4400 | 4400 | 4400 | 4400 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920
Total Consumables | $/yr | 23511 | 56803.1992 | 28295.8008 | 14106.5996 | 37868.8008 | 15236.2002 | 9404.4004 | 37868.8008 | 10883 | 9404.4004 | 18934.4004 | 8706.4004 | 18808.8008 | 18808.8008 | 18808.8008 | 23511 | 56803.1992 | 56803.1992 | 56803.1992 | 56803.1992 | 26119.1992 | 26119.1992 | 28295.8008 | 34825.6016 | 26119.1992 | 26119.1992 | 30472.4004 | 28295.8008 | 9404.4004 | 9404.4004 | 9404.4004 | 14106.5996 | 37868.8008 | 37868.8008 | 37868.8008 | 37868.8008 | 13059.5996 | 13059.5996 | 15236.2002 | 17412.8008 | 13059.5996 | 13059.5996 | 15236.2002 | 15236.2002 | 9404.4004 | 9404.4004 | 9404.4004 | 9404.4004 | 18934.4004 | 18934.4004 | 37868.8008 | 37868.8008 | 10883 | 10883 | 10883 | 13059.5996 | 10883 | 10883 | 10883 | 10883 | 4702.2002 | 4702.2002 | 4702.2002 | 4702.2002 | 18934.4004 | 18934.4004 | 18934.4004 | 18934.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 18808.8008 | 18808.8008 | 18808.8008 | 23511 | 56803.1992 | 56803.1992 | 56803.1992 | 56803.1992 | 26119.1992 | 26119.1992 | 28295.8008 | 34825.6016 | 26119.1992 | 26119.1992 | 30472.4004 | 28295.8008 | 9404.4004 | 9404.4004 | 9404.4004 | 14106.5996 | 37868.8008 | 37868.8008 | 37868.8008 | 37868.8008 | 13059.5996 | 13059.5996 | 15236.2002 | 17412.8008 | 13059.5996 | 13059.5996 | 15236.2002 | 15236.2002 | 9404.4004 | 9404.4004 | 9404.4004 | 9404.4004 | 18934.4004 | 18934.4004 | 37868.8008 | 37868.8008 | 10883 | 10883 | 10883 | 13059.5996 | 10883 | 10883 | 10883 | 10883 | 4702.2002 | 4702.2002 | 4702.2002 | 4702.2002 | 18934.4004 | 18934.4004 | 18934.4004 | 18934.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 18808.8008 | 18808.8008 | 18808.8008 | 23511 | 56803.1992 | 56803.1992 | 56803.1992 | 56803.1992 | 26119.1992 | 26119.1992 | 28295.8008 | 34825.6016 | 26119.1992 | 26119.1992 | 30472.4004 | 28295.8008 | 9404.4004 | 9404.4004 | 9404.4004 | 14106.5996 | 37868.8008 | 37868.8008 | 37868.8008 | 37868.8008 | 13059.5996 | 13059.5996 | 15236.2002 | 17412.8008 | 13059.5996 | 13059.5996 | 15236.2002 | 15236.2002 | 9404.4004 | 9404.4004 | 9404.4004 | 9404.4004 | 18934.4004 | 18934.4004 | 37868.8008 | 37868.8008 | 10883 | 10883 | 10883 | 13059.5996 | 10883 | 10883 | 10883 | 10883 | 4702.2002 | 4702.2002 | 4702.2002 | 4702.2002 | 18934.4004 | 18934.4004 | 18934.4004 | 18934.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004 | 8706.4004
Labor | $/yr | 664.2 | 422.144 | 5691.0005 | 398.52 | 281.4293 | 5349 | 265.68 | 281.4293 | 5235 | 265.68 | 140.7147 | 5178 | 531.36 | 531.36 | 531.36 | 664.2 | 422.144 | 422.144 | 422.144 | 422.144 | 5633.9995 | 5633.9995 | 5691.0005 | 5862.0005 | 5633.9995 | 5633.9995 | 5747.9995 | 5691.0005 | 265.68 | 265.68 | 265.68 | 398.52 | 281.4293 | 281.4293 | 281.4293 | 281.4293 | 5292.0005 | 5292.0005 | 5349 | 5406 | 5292.0005 | 5292.0005 | 5349 | 5349 | 265.68 | 265.68 | 265.68 | 265.68 | 140.7147 | 140.7147 | 281.4293 | 281.4293 | 5235 | 5235 | 5235 | 5292.0005 | 5235 | 5235 | 5235 | 5235 | 132.84 | 132.84 | 132.84 | 132.84 | 140.7147 | 140.7147 | 140.7147 | 140.7147 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 531.36 | 531.36 | 531.36 | 664.2 | 422.144 | 422.144 | 422.144 | 422.144 | 5633.9995 | 5633.9995 | 5691.0005 | 5862.0005 | 5633.9995 | 5633.9995 | 5747.9995 | 5691.0005 | 265.68 | 265.68 | 265.68 | 398.52 | 281.4293 | 281.4293 | 281.4293 | 281.4293 | 5292.0005 | 5292.0005 | 5349 | 5406 | 5292.0005 | 5292.0005 | 5349 | 5349 | 265.68 | 265.68 | 265.68 | 265.68 | 140.7147 | 140.7147 | 281.4293 | 281.4293 | 5235 | 5235 | 5235 | 5292.0005 | 5235 | 5235 | 5235 | 5235 | 132.84 | 132.84 | 132.84 | 132.84 | 140.7147 | 140.7147 | 140.7147 | 140.7147 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 531.36 | 531.36 | 531.36 | 664.2 | 422.144 | 422.144 | 422.144 | 422.144 | 5633.9995 | 5633.9995 | 5691.0005 | 5862.0005 | 5633.9995 | 5633.9995 | 5747.9995 | 5691.0005 | 265.68 | 265.68 | 265.68 | 398.52 | 281.4293 | 281.4293 | 281.4293 | 281.4293 | 5292.0005 | 5292.0005 | 5349 | 5406 | 5292.0005 | 5292.0005 | 5349 | 5349 | 265.68 | 265.68 | 265.68 | 265.68 | 140.7147 | 140.7147 | 281.4293 | 281.4293 | 5235 | 5235 | 5235 | 5292.0005 | 5235 | 5235 | 5235 | 5235 | 132.84 | 132.84 | 132.84 | 132.84 | 140.7147 | 140.7147 | 140.7147 | 140.7147 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178
Patent | $/yr | 127750 | 127750 | 127750 | 128662.5 | 128662.5 | 128662.5 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750 | 127750
Total O&M | $/yr | 257128.1562 | 303212.3125 | 185833.0781 | 196030.5938 | 226215.2812 | 161363.0938 | 174522.2031 | 210448.1719 | 152663.8906 | 164324.3125 | 183622.4844 | 147735.5625 | 245018.7656 | 243079.125 | 245446.5156 | 263928.9062 | 295899.2812 | 296251.4375 | 300712.125 | 306917.0625 | 180923.6094 | 181659.1875 | 185084.2031 | 197157.8906 | 180932.2344 | 181580.6406 | 189560.5 | 184808.8438 | 186384.375 | 185414.5625 | 186598.2656 | 198256.9688 | 221362.2031 | 221538.2812 | 223768.625 | 226871.0938 | 156811.7969 | 157179.5938 | 160008.9062 | 164928.9375 | 156816.1094 | 157140.3281 | 161130.25 | 159871.2188 | 171956.75 | 171272.7031 | 172107.6094 | 176920.6406 | 188617.7344 | 188750.4219 | 209506.1719 | 211844 | 151687.1094 | 151955.625 | 152390.5312 | 156585.3906 | 151690.2656 | 151926.9531 | 153209.1875 | 152290.0156 | 156836.0625 | 157712.9062 | 157983.2188 | 157337.5469 | 183504.7031 | 183167.5469 | 182760.6406 | 185062.6719 | 147764.375 | 147752.8125 | 147732.8438 | 147633.25 | 147764.2656 | 147754.0312 | 147692.625 | 147737.5938 | 342947.375 | 339068.0938 | 343802.875 | 375932.625 | 406823.2188 | 407527.5625 | 416448.9375 | 428858.8125 | 202344 | 203815.1719 | 208431.6094 | 225878.1875 | 202361.2656 | 203658.0938 | 215150.6094 | 207880.8906 | 235348.6875 | 233409.0469 | 235776.4375 | 254258.8281 | 276824.1562 | 277176.3438 | 281637.0312 | 287841.9688 | 167522 | 168257.5938 | 171682.5938 | 179289.0938 | 167530.625 | 168179.0469 | 173925.3125 | 171407.25 | 206493.4219 | 205125.3125 | 206795.1406 | 216421.2031 | 230410.3594 | 230675.7344 | 253112.125 | 257787.7812 | 159506.2188 | 160043.25 | 160913.0469 | 167069.1875 | 159512.5312 | 159985.9062 | 162550.3594 | 160712.0312 | 181087.0781 | 182840.7656 | 183381.4062 | 182090.0469 | 220184.2969 | 219509.9688 | 218696.1719 | 223300.2188 | 153894.3438 | 153871.2188 | 153831.2812 | 153632.0781 | 153894.1406 | 153873.6562 | 153750.8438 | 153840.7812 | 440875.9688 | 435057.0625 | 442159.25 | 487936.3125 | 517747.1562 | 518803.6875 | 532185.6875 | 550800.5625 | 223764.4062 | 225971.1719 | 231779 | 254598.4688 | 223790.2969 | 225735.5469 | 240740.7188 | 230952.9375 | 284313 | 281403.5312 | 284954.625 | 310260.6875 | 332286.125 | 332814.4062 | 339505.4062 | 348812.8438 | 178232.2031 | 179335.5781 | 183356.2969 | 193649.2344 | 178245.1562 | 179217.7812 | 186720.3594 | 182943.2656 | 241030.0938 | 238977.9375 | 241482.6719 | 255921.7812 | 272202.9688 | 272601.0312 | 296718.0938 | 303731.5625 | 167325.3438 | 168130.875 | 169435.5781 | 177552.9844 | 167334.7812 | 168044.8594 | 171891.5469 | 169134.0312 | 205338.1094 | 207968.6406 | 208779.5938 | 206842.5469 | 256863.8906 | 255852.3906 | 254631.7031 | 261537.7812 | 160024.3125 | 159989.6406 | 159929.7344 | 159630.9219 | 160024 | 159993.2812 | 159809.0781 | 159943.9688
Total Capital | $ | 750709 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000
Total Present Worth | $ | 3609559.5 | 4371232 | 2816164 | 2929544 | 3515149 | 2544097.25 | 2690405.5 | 3339844.25 | 2447376.25 | 2577021.25 | 3041586 | 2392581.25 | 3474213.5 | 3452647.75 | 3478969.5 | 3684463.75 | 4289923 | 4293838 | 4343434 | 4412422.5 | 2761578.75 | 2769757.25 | 2807837.75 | 2942077.75 | 2761674.75 | 2768883.75 | 2857607 | 2804776.25 | 2822293.75 | 2811511 | 2824671.75 | 2954297.75 | 3461190.75 | 3463148.5 | 3487946.25 | 3522440.75 | 2493494.25 | 2497583.5 | 2529041 | 2583743.75 | 2493542.25 | 2497147 | 2541508.5 | 2527510 | 2661881.75 | 2654276.25 | 2663559 | 2717072.25 | 3097125 | 3098600.25 | 3329370.75 | 3355363.5 | 2436516 | 2439501.5 | 2444337 | 2490977 | 2436551 | 2439182.75 | 2453439 | 2443219.25 | 2493764 | 2503513.25 | 2506518.5 | 2499339.75 | 3040276.25 | 3036527.75 | 3032003.5 | 3057598.5 | 2392901.5 | 2392773 | 2392551 | 2391443.75 | 2392900.25 | 2392786.5 | 2392103.75 | 2392603.75 | 4563021.5 | 4519890.5 | 4572533.5 | 4929764.5 | 5523218 | 5531049 | 5630240.5 | 5768218.5 | 2999739 | 3016096 | 3067423.25 | 3261401.25 | 2999931 | 3014349.5 | 3142127.75 | 3061300.25 | 3366697.75 | 3345132.25 | 3371453.75 | 3576948 | 4077838.25 | 4081754 | 4131349.5 | 4200338.5 | 2612574.5 | 2620753 | 2658833.5 | 2743405.5 | 2612670.25 | 2619879.75 | 2683769 | 2655772.25 | 3045873.75 | 3030662.75 | 3049228.5 | 3156254.75 | 3561791.5 | 3564742.25 | 3814198.5 | 3866184.25 | 2523452 | 2529422.75 | 2539093.5 | 2607540 | 2523522 | 2528785.25 | 2557297.75 | 2536858.5 | 2763396.25 | 2782894.5 | 2788905.5 | 2774547.75 | 3448094.25 | 3440596.75 | 3431548.75 | 3482738.25 | 2461057 | 2460799.75 | 2460355.75 | 2458141 | 2461054.75 | 2460827 | 2459461.5 | 2460461.5 | 5651829.5 | 5587133 | 5666098 | 6175065 | 6756513.5 | 6768260.5 | 6917046.5 | 7124014 | 3237899.25 | 3262435 | 3327008.75 | 3580724.25 | 3238187.25 | 3259815.25 | 3426648.5 | 3317824.25 | 3911102 | 3878753.5 | 3918235.75 | 4199598.5 | 4694486 | 4700359.5 | 4774752.5 | 4878236.5 | 2731654.75 | 2743922.5 | 2788626.25 | 2903067.25 | 2731798.75 | 2742612.75 | 2826029.25 | 2784034 | 3429866 | 3407049.25 | 3434897.75 | 3595437.5 | 4026458 | 4030883.75 | 4299026.5 | 4377005 | 2610388 | 2619344.25 | 2633850.25 | 2724102.75 | 2610493 | 2618387.75 | 2661156.75 | 2630497.75 | 3033028.5 | 3062276 | 3071292.25 | 3049755.5 | 3855912.25 | 3844666 | 3831093.75 | 3907878.25 | 2529212.25 | 2528826.75 | 2528160.75 | 2524838.5 | 2529208.75 | 2528867.25 | 2526819.25 | 2528319
Present Worth O&M | $ | 2858850.5 | 3371232 | 2066164 | 2179544 | 2515149 | 1794097.25 | 1940405.5 | 2339844.25 | 1697376.25 | 1827021.25 | 2041586 | 1642581.25 | 2724213.5 | 2702647.75 | 2728969.5 | 2934463.75 | 3289923 | 3293838 | 3343434 | 3412422.5 | 2011578.75 | 2019757.25 | 2057837.75 | 2192077.75 | 2011674.75 | 2018883.75 | 2107607 | 2054776.25 | 2072293.75 | 2061511 | 2074671.75 | 2204297.75 | 2461190.75 | 2463148.5 | 2487946.25 | 2522440.75 | 1743494.25 | 1747583.5 | 1779041 | 1833743.75 | 1743542.25 | 1747147 | 1791508.5 | 1777510 | 1911881.75 | 1904276.25 | 1913559 | 1967072.25 | 2097125 | 2098600.25 | 2329370.75 | 2355363.5 | 1686516 | 1689501.5 | 1694337 | 1740977 | 1686551 | 1689182.75 | 1703439 | 1693219.25 | 1743764 | 1753513.25 | 1756518.5 | 1749339.75 | 2040276.25 | 2036527.75 | 2032003.5 | 2057598.5 | 1642901.5 | 1642773 | 1642551 | 1641443.75 | 1642900.25 | 1642786.5 | 1642103.75 | 1642603.75 | 3813021.5 | 3769890.5 | 3822533.5 | 4179764.5 | 4523218 | 4531049 | 4630240.5 | 4768218.5 | 2249739 | 2266096 | 2317423.25 | 2511401.25 | 2249931 | 2264349.5 | 2392127.75 | 2311300.25 | 2616697.75 | 2595132.25 | 2621453.75 | 2826948 | 3077838.25 | 3081754 | 3131349.5 | 3200338.5 | 1862574.5 | 1870753 | 1908833.5 | 1993405.5 | 1862670.25 | 1869879.75 | 1933769 | 1905772.25 | 2295873.75 | 2280662.75 | 2299228.5 | 2406254.75 | 2561791.5 | 2564742.25 | 2814198.5 | 2866184.25 | 1773452 | 1779422.75 | 1789093.5 | 1857540 | 1773522 | 1778785.25 | 1807297.75 | 1786858.5 | 2013396.25 | 2032894.5 | 2038905.5 | 2024547.75 | 2448094.25 | 2440596.75 | 2431548.75 | 2482738.25 | 1711057 | 1710799.75 | 1710355.75 | 1708141 | 1711054.75 | 1710827 | 1709461.5 | 1710461.5 | 4901829.5 | 4837133 | 4916098 | 5425065 | 5756513.5 | 5768260.5 | 5917046.5 | 6124014 | 2487899.25 | 2512435 | 2577008.75 | 2830724.25 | 2488187.25 | 2509815.25 | 2676648.5 | 2567824.25 | 3161102 | 3128753.5 | 3168235.75 | 3449598.5 | 3694486 | 3700359.5 | 3774752.5 | 3878236.5 | 1981654.75 | 1993922.5 | 2038626.25 | 2153067.25 | 1981798.75 | 1992612.75 | 2076029.25 | 2034034 | 2679866 | 2657049.25 | 2684897.75 | 2845437.5 | 3026458 | 3030883.75 | 3299026.5 | 3377005 | 1860388 | 1869344.25 | 1883850.25 | 1974102.75 | 1860493 | 1868387.75 | 1911156.75 | 1880497.75 | 2283028.5 | 2312276 | 2321292.25 | 2299755.5 | 2855912.25 | 2844666 | 2831093.75 | 2907878.25 | 1779212.25 | 1778826.75 | 1778160.75 | 1774838.5 | 1779208.75 | 1778867.25 | 1776819.25 | 1778319
UV SYSTEM SIZING CRITERIA
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 47 | 47 | 47 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 46.6667
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 23.5 | 23.5 | 23.5 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333
Average UVT | % | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
Design UVT | % | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Design UV Dose | mJ/cm^2 | 32 | 32 | 28 | 32 | 32 | 28 | 32 | 32 | 28 | 32 | 32 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
REACTOR DESIGN INPUTS
Configuration
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7
Number of Trains |  | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Banks/Reactor |  | 2 | 1 | 8 | 2 | 1 | 8 | 2 | 1 | 8 | 2 | 1 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Lamps/Bank |  | 3 | 8 | 12 | 3 | 8 | 12 | 3 | 8 | 12 | 3 | 8 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Lamps/Ballast |  | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Sensors/bank |  | 3 | 8 | 1 | 3 | 8 | 1 | 3 | 8 | 1 | 3 | 8 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Redundancy
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 20 | 12 | 0.36 | 20 | 12 | 0.36 | 20 | 12 | 0.36 | 20 | 12 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
Lamp Life | hrs | 5000 | 5000 | 12000 | 5000 | 5000 | 12000 | 5000 | 5000 | 12000 | 5000 | 5000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000
Lamp Aging Factor | % | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206
Lamp Cost | $ | 575 | 275 | 160 | 575 | 275 | 160 | 575 | 275 | 160 | 575 | 275 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 575 | 575 | 575 | 575 | 275 | 275 | 275 | 275 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
Lamp Replacement Time | min | 15 | 3 | 5 | 15 | 3 | 5 | 15 | 3 | 5 | 15 | 3 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM | CUSTOM
Coefficient A |  | 330.867 | 411.29 | 194.4896 | 330.867 | 411.29 | 194.4896 | 330.867 | 411.29 | 194.4896 | 330.867 | 411.29 | 194.4896 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732
Coefficient B |  | -891.6219 | -1830.9318 | -343.378 | -891.6219 | -1830.9318 | -343.378 | -891.6219 | -1830.9318 | -343.378 | -891.6219 | -1830.9318 | -343.378 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 1.0001 | 1.0001 | 1 | 1.0001 | 0.8868 | 1.0029 | 1.0107 | -2.0993 | -0.057476 | -0.069688 | -0.088634 | -0.16355 | -0.057622 | -0.068404 | -0.12181 | -0.084343
Coefficient C |  | -0.17604 | -0.18796 | -0.10815 | -0.17604 | -0.18796 | -0.10815 | -0.17604 | -0.18796 | -0.10815 | -0.17604 | -0.18796 | -0.10815 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 0.038 | 0.0396 | 0.0412 | 0.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coefficient D |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coefficient E |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coefficient F |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lamp Power | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lamp Aging Equation | 9999 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 71.7675 | 78.2386 | 70.2112 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 81.5726 | 78.5221 | 65.0142 | 74.2206
Sleeve Data
Sleeve Life | yrs | 5 | 10 | 10 | 5 | 10 | 10 | 5 | 10 | 10 | 5 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Sleeve Cost | $ | 350 | 350 | 100 | 350 | 350 | 100 | 350 | 350 | 100 | 350 | 350 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Sleeve Replacement Time | min | 25 | 10 | 5 | 25 | 10 | 5 | 25 | 10 | 5 | 25 | 10 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Sleeve Cleaning Type (Rinse, Wiper) |  | Wiper | Wiper | Rinse | Wiper | Wiper | Rinse | Wiper | Wiper | Rinse | Wiper | Wiper | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Wiper | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse | Rinse
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Sleeve Cleaning Time/Reactor | min | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
Fouling Factor | % | 85 | 95 | 85 | 85 | 95 | 85 | 85 | 95 | 85 | 85 | 95 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Ballast Data
Ballast Life | yrs | 10 | 5 | 5 | 10 | 5 | 5 | 10 | 5 | 5 | 10 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Ballast Costs | $ | 1800 | 6000 | 300 | 1800 | 6000 | 300 | 1800 | 6000 | 300 | 1800 | 6000 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 1800 | 1800 | 1800 | 1800 | 6000 | 6000 | 6000 | 6000 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Ballast replacement | min | 60 | 30 | 1 | 60 | 30 | 1 | 60 | 30 | 1 | 60 | 30 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sensor Data
Sensor life | yrs | 5 | 3 | 10 | 5 | 3 | 10 | 5 | 3 | 10 | 5 | 3 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Sensor cost | $ | 1200 | 2100 | 650 | 1200 | 2100 | 650 | 1200 | 2100 | 650 | 1200 | 2100 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 1200 | 1200 | 1200 | 1200 | 2100 | 2100 | 2100 | 2100 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
Sensor replacement | min | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Sensor cal period | months | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Sensor calibration cost | $ | 70 | 550 | 230 | 70 | 550 | 230 | 70 | 550 | 230 | 70 | 550 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 70 | 70 | 70 | 70 | 550 | 550 | 550 | 550 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
Sensor calibration | min | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Dose Pacing | Enter if dose pacing responds to the following parameters.
Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling
Peak dose will be equal to or greater than the design dose.
Peak UV Dose ** | mJ/cm^2 | 31.9748 | 34.14 | 35.1792 | 31.8166 | 33.9767 | 34.9839 | 31.9748 | 34.14 | 35.1792 | 31.9748 | 34.14 | 35.1792 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 39.5579 | 38.3961 | 33.1256 | 36.7409
Flow (y/n) |  | n | n | n | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y
Lamp Age (y/n) |  | n | n | n | n | n | n | n | n | n | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y
UVT (y/n) |  | n | n | n | n | n | n | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y
Fouling (y/n) |  | n | n | n | n | n | n | n | n | n | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | n | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y | y
WTP INPUTS
Labor rate | $/hr | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Electricity Cost | $/kWhr | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
Interest rate | % | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Period | yrs | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
CAPITAL COSTS INPUTS
Reactor | Total $ | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 1000000 | 1000000 | 1000000 | 1000000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000 | 750000
Install Factor | Total $
Validation | Total $
Inlet/Oultet Piping
Valves | Total $
Flowmeters | Total $
Piping and Appurtences | Total $
Channels | Total $
Power
Switch gear | Total $
Transformer | Total $
Distribution Panels | Total $
Generator | Total $
UPS | Total $
Misc Electrical | Total $
Other
Yard piping | Total $
Chlorine contactor | Total $
Low lift pumps | Total $
UV Building
Demolition | Total $
Civil/sitework | Total $
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves. Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 124.6793 | 95.039 | 131.6744 | 124.0626 | 94.5845 | 130.9434 | 124.6793 | 95.039 | 131.6744 | 124.6793 | 95.039 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 124.6793 | 124.6793 | 124.6793 | 124.6793 | 95.039 | 95.039 | 95.039 | 95.039 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744 | 131.6744
95% UVT | mJ/cm2 | 80.2288 | 66.4797 | 88.4972 | 79.8319 | 66.1618 | 88.006 | 80.2288 | 66.4797 | 88.4972 | 80.2288 | 66.4797 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 80.2288 | 80.2288 | 80.2288 | 80.2288 | 66.4797 | 66.4797 | 66.4797 | 66.4797 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972 | 88.4972
90% UVT | mJ/cm2 | 45.1189 | 41.6914 | 52.6773 | 44.8957 | 41.492 | 52.3849 | 45.1189 | 41.6914 | 52.6773 | 45.1189 | 41.6914 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 45.1189 | 45.1189 | 45.1189 | 45.1189 | 41.6914 | 41.6914 | 41.6914 | 41.6914 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773 | 52.6773
85% UVT | mJ/cm2 | 28.2197 | 28.4989 | 34.5086 | 28.0801 | 28.3626 | 34.3171 | 28.2197 | 28.4989 | 34.5086 | 28.2197 | 28.4989 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 28.2197 | 28.2197 | 28.2197 | 28.2197 | 28.4989 | 28.4989 | 28.4989 | 28.4989 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086 | 34.5086
80% UVT | mJ/cm2 | 18.938 | 20.6256 | 24.0881 | 18.8443 | 20.527 | 23.9543 | 18.938 | 20.6256 | 24.0881 | 18.938 | 20.6256 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 18.938 | 18.938 | 18.938 | 18.938 | 20.6256 | 20.6256 | 20.6256 | 20.6256 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881 | 24.0881
75% UVT | mJ/cm2 | 13.4289 | 15.6092 | 17.6701 | 13.3624 | 15.5345 | 17.572 | 13.4289 | 15.6092 | 17.6701 | 13.4289 | 15.6092 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 13.4289 | 13.4289 | 13.4289 | 13.4289 | 15.6092 | 15.6092 | 15.6092 | 15.6092 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701 | 17.6701
70% UVT | mJ/cm2 | 9.9859 | 12.2768 | 13.5294 | 9.9365 | 12.2181 | 13.4543 | 9.9859 | 12.2768 | 13.5294 | 9.9859 | 12.2768 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 12.2768 | 12.2768 | 12.2768 | 12.2768 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294 | 13.5294
65% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999
|  | 2.1514 | 2.3676 | 2.4987 | 2.1514 | 2.3676 | 2.4987 | 2.1514 | 2.3676 | 2.4987 | 2.1514 | 2.3676 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.1514 | 2.1514 | 2.1514 | 2.1514 | 2.3676 | 2.3676 | 2.3676 | 2.3676 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987 | 2.4987
|  | 10.2072 | 8.2746 | 9.2 | 10.2072 | 8.2746 | 9.2 | 10.2072 | 8.2746 | 9.2 | 10.2072 | 8.2746 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.2072 | 10.2072 | 10.2072 | 10.2072 | 8.2746 | 8.2746 | 8.2746 | 8.2746 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2
|  | 0.69671 | 0.67349 | 0.78215 | 0.69671 | 0.67349 | 0.78215 | 0.69671 | 0.67349 | 0.78215 | 0.69671 | 0.67349 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.69671 | 0.69671 | 0.69671 | 0.69671 | 0.67349 | 0.67349 | 0.67349 | 0.67349 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215 | 0.78215
|  | 1.0956 | 0.93411 | 0.94868 | 1.0956 | 0.93411 | 0.94868 | 1.0956 | 0.93411 | 0.94868 | 1.0956 | 0.93411 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.93411 | 0.93411 | 0.93411 | 0.93411 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868 | 0.94868
Note on A43: Example. Enter 95% as "95" as opposed to "0.95"
Note on A44: Example. Enter 95% as "95" as opposed to "0.95"
LCA

## LAMP AGE LCA TOOL (1)
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 1
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions
Units: y = %, x = hrs
MMF: y=(a*b+c*x^d)/(b+x^d) |  | Power | 0.15
EXP: y=a*e^(b*x) |  | Interest | 4
LIN: Y = ax+b |  | Period | 15
| 0 | 1 | 2 | 3 | Simulation - Cost Benefit Analysis for Case 1
Lamp Type |  |  |  |  | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Vendor |  |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment |  |  |  |  | 200 | 0.96565 | 9 | 0.99172 | 234561.5 | 226665 | 630 | 1620 | 2160 | 630 | 231705 | 6075.0005 | 127750 | 600091.5 | 557402.3125 | 7229452
[5 empty] | 400 | 0.93747 | 12 | 0.76615 | 241612.2656 | 151110 | 840 | 2160 | 2880 | 840 | 157830 | 4157.9995 | 127750 | 531350.25 | 574157.5 | 6481915.5
UV SYSTEM SIZING CRITERIA |  |  |  |  | 600 | 0.91401 | 12 | 0.78581 | 247814.0156 | 100740 | 840 | 2160 | 2880 | 840 | 107460 | 2844 | 127750 | 485868 | 588895 | 5990963.5
[5 empty] | 800 | 0.89399 | 12 | 0.80341 | 253364.4375 | 75555 | 840 | 2160 | 2880 | 840 | 82275 | 2187 | 127750 | 465576.4375 | 602084.8125 | 5778544
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 1000 | 0.87657 | 12 | 0.81937 | 258398.0625 | 60444 | 840 | 2160 | 2880 | 840 | 67164 | 1792.8 | 127750 | 455104.875 | 614046.5625 | 5674079
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 2000 | 0.81347 | 12 | 0.88293 | 278442.3438 | 30222 | 840 | 2160 | 2880 | 840 | 36942 | 1004.4 | 127750 | 444138.75 | 661679 | 5599785.5
Average UVT | % | 93 | 93 | 93 | 3000 | 0.77203 | 12 | 0.93033 | 293388.4688 | 20148 | 840 | 2160 | 2880 | 840 | 26868 | 741.6 | 127750 | 448748.0625 | 697196.3125 | 5686551
Design UVT | % | 90 | 90 | 90 | 4000 | 0.74156 | 12 | 0.96855 | 305441.5312 | 15111 | 840 | 2160 | 2880 | 840 | 21831 | 610.2 | 127750 | 455632.7188 | 725838.6875 | 5791739.5
Design UV Dose | mJ/cm^2 | 32 | 32 | 28 | 5000 | 0.71768 | 15 | 0.80063 | 315608.875 | 15111 | 1050 | 2700 | 3600 | 1050 | 23511 | 664.2 | 127750 | 467534.0625 | 750000 | 5948224.5
REACTOR DESIGN INPUTS |  |  |  |  | 6000 | 0.69814 | 15 | 0.82304 | 324440.75 | 12592.5 | 1050 | 2700 | 3600 | 1050 | 20992.5 | 598.5 | 127750 | 473781.75 | 770987.6875 | 6038676.5
Configuration |  |  |  |  | 7000 | 0.68168 | 15 | 0.8429 | 332272.7188 | 10793.5713 | 1050 | 2700 | 3600 | 1050 | 19193.5703 | 551.5715 | 127750 | 479767.875 | 789599.1875 | 6123844
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 8000 | 0.66751 | 15 | 0.86079 | 339325.375 | 9444.375 | 1050 | 2700 | 3600 | 1050 | 17844.375 | 516.375 | 127750 | 485436.125 | 806358.875 | 6203625.5
Number of Trains |  | 3 | 4 | 3 | 9000 | 0.65511 | 15 | 0.8771 | 345752.0625 | 8395 | 1050 | 2700 | 3600 | 1050 | 16795 | 489 | 127750 | 490786.0625 | 821631 | 6278380.5
Number of Reactors/Train |  | 1 | 1 | 1 | 10000 | 0.64409 | 15 | 0.8921 | 351663.9062 | 7555.5 | 1050 | 2700 | 3600 | 1050 | 15955.5 | 467.1 | 127750 | 495836.5 | 835679.6875 | 6348582
Banks/Reactor |  | 2 | 1 | 8 | 11000 | 0.63421 | 15 | 0.906 | 357144.2188 | 6868.6362 | 1050 | 2700 | 3600 | 1050 | 15268.6367 | 449.1818 | 127750 | 500612.0312 | 848702.8125 | 6414701
Lamps/Bank |  | 3 | 8 | 12 | 12000 | 0.62526 | 15 | 0.91897 | 362257.0312 | 6296.25 | 1050 | 2700 | 3600 | 1050 | 14696.25 | 434.25 | 127750 | 505137.5312 | 860852.75 | 6477167.5
Lamps/Ballast |  | 1 | 2 | 2 | 13000 | 0.61709 | 15 | 0.93113 | 367052.875 | 5811.9229 | 1050 | 2700 | 3600 | 1050 | 14211.9229 | 421.6154 | 127750 | 509436.4062 | 872249.4375 | 6536360.5
Sensors/bank |  | 3 | 8 | 1 | 14000 | 0.60958 | 15 | 0.9426 | 371572.2188 | 5396.7856 | 1050 | 2700 | 3600 | 1050 | 13796.7852 | 410.7857 | 127750 | 513529.7812 | 882988.9375 | 6592612
Redundancy |  |  |  |  | 15000 | 0.60265 | 15 | 0.95344 | 375848 | 5037 | 1050 | 2700 | 3600 | 1050 | 13437 | 401.4 | 127750 | 517436.4062 | 893149.75 | 6646208
No. of Redundant Trains |  | 1 | 1 | 1 | 16000 | 0.59621 | 15 | 0.96374 | 379907.5938 | 4722.1875 | 1050 | 2700 | 3600 | 1050 | 13122.1875 | 393.1875 | 127750 | 521172.9688 | 902796.8125 | 6697399.5
No. of Redundant Reactors per train |  | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 20 | 12 | 0.36
Lamp Life | hrs | 5000 | 5000 | 12000 | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | 71.7675 | 78.2386 | 70.2112 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | 575 | 275 | 160 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 15 | 3 | 5 | 200 | 0.98273 | 24 | 0.74623 | 282397.1875 | 289080 | 840 | 14400 | 16800 | 13200 | 334320 | 3449.6001 | 127750 | 747916.8125 | 796133.375 | 9111762
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | 400 | 0.96554 | 24 | 0.75952 | 287426.875 | 144540 | 840 | 14400 | 16800 | 13200 | 189780 | 1872.8 | 127750 | 606829.6875 | 810313.125 | 7557280.5
Coefficient A |  | 330.867 | 411.29 | 194.4896 | 600 | 0.95008 | 24 | 0.77188 | 292102.8125 | 96360 | 840 | 14400 | 16800 | 13200 | 141600 | 1347.2001 | 127750 | 562800 | 823495.4375 | 7080924
Coefficient B |  | -891.6219 | -1830.9318 | -343.378 | 800 | 0.93607 | 24 | 0.78343 | 296476.0938 | 72270 | 840 | 14400 | 16800 | 13200 | 117510 | 1084.4 | 127750 | 542820.5 | 835824.5625 | 6871113
Coefficient C |  | -0.17604 | -0.18796 | -0.10815 | 1000 | 0.92326 | 24 | 0.7943 | 300587.2188 | 57816 | 840 | 14400 | 16800 | 13200 | 103056 | 926.72 | 127750 | 532319.9375 | 847414.625 | 6765954
Coefficient D |  | 0 | 0 | 0 | 2000 | 0.87223 | 24 | 0.84077 | 318173.2812 | 28908 | 840 | 14400 | 16800 | 13200 | 74148 | 611.36 | 127750 | 520682.6562 | 896993.1875 | 6686144.5
Coefficient E |  | 0 | 0 | 0 | 3000 | 0.83503 | 24 | 0.87823 | 332350.375 | 19272 | 840 | 14400 | 16800 | 13200 | 64512 | 506.2401 | 127750 | 525118.625 | 936961.3125 | 6775433.5
Coefficient F |  | 0 | 0 | 0 | 4000 | 0.80601 | 24 | 0.90984 | 344313.2812 | 14454 | 840 | 14400 | 16800 | 13200 | 59694 | 453.68 | 127750 | 532210.9375 | 970687.125 | 6888014.5
Lamp Power | kW | 0 | 0 | 0 | 5000 | 0.78239 | 24 | 0.93732 | 354710.875 | 11563.2002 | 840 | 14400 | 16800 | 13200 | 56803.1992 | 422.144 | 127750 | 539686.1875 | 999999.9375 | 7000440
Lamp Aging Equation | 9999 | 71.7675 | 78.2386 | 70.2112 | 6000 | 0.76255 | 24 | 0.9617 | 363937.5 | 9636 | 840 | 14400 | 16800 | 13200 | 54876 | 401.12 | 127750 | 546964.625 | 1026011.625 | 7107376
Sleeve Data |  |  |  |  | 7000 | 0.74552 | 24 | 0.98367 | 372251.9688 | 8259.4287 | 840 | 14400 | 16800 | 13200 | 53499.4297 | 386.1028 | 127750 | 553887.5 | 1049451.75 | 7207787.5
Sleeve Life | yrs | 5 | 10 | 10 | 8000 | 0.73064 | 32 | 0.75278 | 379833.875 | 9636 | 1120 | 19200 | 22400 | 17600 | 69956 | 499.7867 | 127750 | 578039.6875 | 1070826.625 | 7497695.5
Sleeve Cost | $ | 350 | 350 | 100 | 9000 | 0.71745 | 32 | 0.76661 | 386813.25 | 8565.333 | 1120 | 19200 | 22400 | 17600 | 68885.3359 | 488.1067 | 127750 | 583936.6875 | 1090502.875 | 7582937
Sleeve Replacement Time | min | 25 | 10 | 5 | 10000 | 0.70564 | 32 | 0.77944 | 393287.5312 | 7708.7998 | 1120 | 19200 | 22400 | 17600 | 68028.7969 | 478.7627 | 127750 | 589545.0625 | 1108755.125 | 7663545.5
Sleeve Cleaning Type (Rinse, Wiper) |  | Wiper | Wiper | Rinse | 11000 | 0.69496 | 32 | 0.79142 | 399331.6562 | 7008 | 1120 | 19200 | 22400 | 17600 | 67328 | 471.1176 | 127750 | 594880.75 | 1125794.75 | 7739909.5
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 12000 | 0.68523 | 32 | 0.80266 | 405004.5625 | 6424 | 1120 | 19200 | 22400 | 17600 | 66744 | 464.7466 | 127750 | 599963.3125 | 1141787.75 | 7812412
Sleeve Cleaning Time/Reactor | min | 0 | 0 | 180 | 13000 | 0.6763 | 32 | 0.81326 | 410353.6562 | 5929.8462 | 1120 | 19200 | 22400 | 17600 | 66249.8438 | 459.3559 | 127750 | 604812.875 | 1156867.875 | 7881411.5
Fouling Factor | % | 85 | 95 | 85 | 14000 | 0.66805 | 32 | 0.8233 | 415417.4375 | 5506.2856 | 1120 | 19200 | 22400 | 17600 | 65826.2891 | 454.7352 | 127750 | 609448.4375 | 1171143.75 | 7947227.5
[5 empty] | 15000 | 0.66041 | 32 | 0.83283 | 420227.8125 | 5139.2002 | 1120 | 19200 | 22400 | 17600 | 65459.1992 | 450.7307 | 127750 | 613887.75 | 1184705 | 8010146.5
Ballast Data |  |  |  |  | 16000 | 0.65328 | 32 | 0.84192 | 424811.3438 | 4818 | 1120 | 19200 | 22400 | 17600 | 65138 | 447.2267 | 127750 | 618146.5625 | 1197627 | 8070420
Ballast Life | yrs | 10 | 5 | 5
Ballast Costs | $ | 1800 | 6000 | 300
Ballast replacement | min | 60 | 30 | 1
Sensor Data |  |  |  |  | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | 5 | 3 | 10 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | 1200 | 2100 | 650 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 10 | 10 | 10 | 200 | 0.98422 | 120 | 0.90846 | 51568.375 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1059390.375 | 535024.4375 | 12313737
Sensor cal period | months | 12 | 12 | 12 | 400 | 0.95142 | 120 | 0.93978 | 53346.2109 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 627548.1875 | 553469.5 | 7530793
Sensor calibration cost | $ | 70 | 550 | 230 | 600 | 0.92722 | 120 | 0.96431 | 54738.7031 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 484400.6875 | 567916.6875 | 5953671
Sensor calibration | min | 5 | 5 | 5 | 800 | 0.90814 | 120 | 0.98457 | 55888.8945 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 413280.9062 | 579849.9375 | 5174867
[5 empty] | 1000 | 0.89244 | 132 | 0.9108 | 56871.793 | 185011.2031 | 1320 | 3960 | 715 | 2530 | 193536.2031 | 10876.7998 | 127750 | 389034.7812 | 590047.625 | 4915487
Dose Pacing | Enter if dose pacing responds to the following parameters. |  |  |  | 2000 | 0.84032 | 132 | 0.9673 | 60399.1484 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 297165.75 | 626644.125 | 3930648
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling |  |  |  | 3000 | 0.80864 | 144 | 0.92143 | 62765.8008 | 67276.7969 | 1440 | 4320 | 780 | 2760 | 76576.7969 | 7210.7998 | 127750 | 274303.4062 | 651198.1875 | 3701009.75
| Peak dose will be equal to or greater than the design dose. |  |  |  | 4000 | 0.78608 | 144 | 0.94788 | 64567.4336 | 50457.6016 | 1440 | 4320 | 780 | 2760 | 59757.6016 | 6685.1997 | 127750 | 258760.2344 | 669890.1875 | 3546886.75
Peak UV Dose ** | mJ/cm^2 | 31.9748 | 34.14 | 35.1792 | 5000 | 0.76866 | 144 | 0.96936 | 66030.6797 | 40366.0781 | 1440 | 4320 | 780 | 2760 | 49666.0781 | 6369.8398 | 127750 | 249816.5938 | 685071.4375 | 3462629
Flow (y/n) |  | n | n | n | 6000 | 0.75453 | 144 | 0.98751 | 67267.2188 | 33638.3984 | 1440 | 4320 | 780 | 2760 | 42938.3984 | 6159.5996 | 127750 | 244115.2188 | 697900.625 | 3412068.25
Lamp Age (y/n) |  | n | n | n | 7000 | 0.74267 | 156 | 0.9261 | 68340.6484 | 31235.6562 | 1560 | 4680 | 845 | 2990 | 41310.6562 | 6097.7148 | 127750 | 243499.0156 | 709037.5625 | 3416354
UVT (y/n) |  | n | n | n | 8000 | 0.73249 | 156 | 0.93897 | 69290.8125 | 27331.1992 | 1560 | 4680 | 845 | 2990 | 37406.1992 | 5975.7007 | 127750 | 240422.7188 | 718895.5 | 3392008.5
Fouling (y/n) |  | n | n | n | 9000 | 0.72358 | 156 | 0.95054 | 70144.3281 | 24294.4004 | 1560 | 4680 | 845 | 2990 | 34369.3984 | 5880.8003 | 127750 | 238144.5312 | 727750.75 | 3375533.75
[5 empty] | 10000 | 0.71566 | 156 | 0.96105 | 70919.9219 | 21864.9609 | 1560 | 4680 | 845 | 2990 | 31939.9609 | 5804.8804 | 127750 | 236414.7656 | 735797.625 | 3364348.5
WTP INPUTS |  |  |  |  | 11000 | 0.70856 | 156 | 0.97069 | 71631.3125 | 19877.2363 | 1560 | 4680 | 845 | 2990 | 29952.2363 | 5742.7637 | 127750 | 235076.3125 | 743178.375 | 3356847.75
Labor rate | $/hr | 60 | 60 | 60 | 12000 | 0.70211 | 156 | 0.9796 | 72288.8203 | 18220.8008 | 1560 | 4680 | 845 | 2990 | 28295.8008 | 5691.0005 | 127750 | 234025.625 | 750000 | 3351987.5
Electricity Cost | $/kWhr | 0.15 | 0.15 | 0.15 | 13000 | 0.69622 | 156 | 0.98789 | 72900.4297 | 16819.1992 | 1560 | 4680 | 845 | 2990 | 26894.1992 | 5647.2002 | 127750 | 233191.8281 | 756345.4375 | 3349062.5
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 14000 | 0.6908 | 156 | 0.99564 | 73472.4297 | 15617.8281 | 1560 | 4680 | 845 | 2990 | 25692.8281 | 5609.6577 | 127750 | 232524.9219 | 762280.0625 | 3347582.25
Interest rate | % | 4 | 4 | 4 | 15000 | 0.68578 | 168 | 0.93129 | 74009.9219 | 15697.9199 | 1680 | 5040 | 910 | 3220 | 26547.9199 | 5625.3594 | 127750 | 233933.2031 | 767856.5 | 3368816.5
Period | yrs | 15 | 15 | 15 | 16000 | 0.68112 | 168 | 0.93767 | 74517.0234 | 14716.7998 | 1680 | 5040 | 910 | 3220 | 25566.8008 | 5594.6997 | 127750 | 233428.5312 | 773117.75 | 3368466.5
CAPITAL COSTS INPUTS |  |  |  |  | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | 750000 | 1000000 | 750000 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $
Inlet/Oultet Piping
Valves | Total $
Flowmeters | Total $
Piping and Appurtences | Total $
Channels | Total $
Power
Switch gear | Total $
Transformer | Total $
Distribution Panels | Total $
Generator | Total $
UPS | Total $
Misc Electrical | Total $
Other
Yard piping | Total $
Chlorine contactor | Total $
Low lift pumps | Total $
UV Building
Demolition | Total $
Civil/sitework | Total $
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 124.6793 | 95.039 | 131.6744
95% UVT | mJ/cm2 | 80.2288 | 66.4797 | 88.4972
90% UVT | mJ/cm2 | 45.1189 | 41.6914 | 52.6773
85% UVT | mJ/cm2 | 28.2197 | 28.4989 | 34.5086
80% UVT | mJ/cm2 | 18.938 | 20.6256 | 24.0881
75% UVT | mJ/cm2 | 13.4289 | 15.6092 | 17.6701
70% UVT | mJ/cm2 | 9.9859 | 12.2768 | 13.5294
65% UVT | mJ/cm2 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999
|  | 2.1514 | 2.3676 | 2.4987
|  | 10.2072 | 8.2746 | 9.2
|  | 0.69671 | 0.67349 | 0.78215
|  | 1.0956 | 0.93411 | 0.94868
Note on B56: This cell contains a lamp aging equation for fit types MMF, EXP, and LIN that can be copied to other columns.
Lamp Analysis
Clear

## LAMP AGE LCA TOOL (2)
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 4
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions |  | MP Reactor 1 - Hoerl Model
Units: y = %, x = hrs |  | Power | 0.15
MMF: y=(a*b+c*x^d)/(b+x^d) |  | Interest | 4
EXP: y=a*e^(b*x) |  | Period | 15
LIN: Y = ax+b |  | Dose pacing | No
| 0 | 1 | 2 | 3 | 4 | Simulation - Cost Benefit Analysis for Case 1
Lamp Type | [5 empty] | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Vendor | [5 empty] | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment | [5 empty] | 200 | 1 | 9 | 0.988 | 233681.0781 | 226665 | 630 | 1620 | 2160 | 630 | 231705 | 6075.0005 | 127750 | 599211.0625 | 596559.8125 | 7258820.5
[6 empty] | 400 | 0.97381 | 12 | 0.76093 | 239965.875 | 151110 | 840 | 2160 | 2880 | 840 | 157830 | 4157.9995 | 127750 | 529703.875 | 612604.125 | 6502057
UV SYSTEM SIZING CRITERIA | [5 empty] | 600 | 0.90197 | 12 | 0.82153 | 259079 | 100740 | 840 | 2160 | 2880 | 840 | 107460 | 2844 | 127750 | 497133 | 661397.6875 | 6188715
[6 empty] | 800 | 0.85831 | 12 | 0.86332 | 272256.1875 | 75555 | 840 | 2160 | 2880 | 840 | 82275 | 2187 | 127750 | 484468.1875 | 695037.5 | 6081542.5
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 1000 | 0.82896 | 12 | 0.89389 | 281898.0312 | 60444 | 840 | 2160 | 2880 | 840 | 67164 | 1792.8 | 127750 | 478604.8438 | 719651.9375 | 6040966
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 2000 | 0.76748 | 12 | 0.96549 | 304476.625 | 30222 | 840 | 2160 | 2880 | 840 | 36942 | 1004.4 | 127750 | 470173.0312 | 777292.3125 | 6004858
Average UVT | % | 93 | 93 | 93 | 93 | 3000 | 0.75906 | 12 | 0.97621 | 307856.3438 | 20148 | 840 | 2160 | 2880 | 840 | 26868 | 741.6 | 127750 | 463215.9375 | 785920.375 | 5936134.5
Design UVT | % | 90 | 90 | 90 | 90 | 4000 | 0.77129 | 12 | 0.96072 | 302973.8438 | 15111 | 840 | 2160 | 2880 | 840 | 21831 | 610.2 | 127750 | 453165.0312 | 773455.9375 | 5811920
Design UV Dose | mJ/cm^2 | 32 | 32 | 32 | 32 | 5000 | 0.79541 | 12 | 0.93159 | 293785.8125 | 12088.7998 | 840 | 2160 | 2880 | 840 | 18808.8008 | 531.36 | 127750 | 440875.9688 | 750000.0625 | 5651830
REACTOR DESIGN INPUTS | [5 empty] | 6000 | 0.82801 | 12 | 0.89492 | 282220.5312 | 10074 | 840 | 2160 | 2880 | 840 | 16794 | 478.8 | 127750 | 427243.3438 | 720475.25 | 5470732
Configuration | [5 empty] | 7000 | 0.86753 | 12 | 0.85415 | 269363.75 | 8634.8574 | 840 | 2160 | 2880 | 840 | 15354.8574 | 441.2571 | 127750 | 412909.875 | 687653.375 | 5278545.5
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 25.7 | 8000 | 0.91325 | 12 | 0.81139 | 255879.1875 | 7555.5 | 840 | 2160 | 2880 | 840 | 14275.5 | 413.1 | 127750 | 398317.7812 | 653228.9375 | 5081880.5
Number of Trains |  | 3 | 3 | 3 | 3 | 9000 | 0.96486 | 12 | 0.76799 | 242192.9062 | 6716 | 840 | 2160 | 2880 | 840 | 13436 | 391.2 | 127750 | 383770.0938 | 618289.5 | 4885194
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 10000 | 1.0223 | 9 | 0.96646 | 228586.1562 | 4533.2998 | 630 | 1620 | 2160 | 630 | 9573.2998 | 280.26 | 127750 | 366189.7188 | 583553.125 | 4654992
Banks/Reactor |  | 2 | 2 | 2 | 2 | 11000 | 1.0856 | 9 | 0.91006 | 215246.9531 | 4121.1816 | 630 | 1620 | 2160 | 630 | 9161.1816 | 269.5091 | 127750 | 352427.6562 | 549499.6875 | 4467927
Lamps/Bank |  | 3 | 3 | 3 | 3 | 12000 | 1.1551 | 9 | 0.85532 | 202300.5625 | 3777.75 | 630 | 1620 | 2160 | 630 | 8817.75 | 260.55 | 127750 | 339128.875 | 516449.0938 | 4287015
Lamps/Ballast |  | 1 | 1 | 1 | 1 | 13000 | 1.231 | 9 | 0.80259 | 189829.0625 | 3487.1538 | 630 | 1620 | 2160 | 630 | 8527.1543 | 252.9692 | 127750 | 326359.1875 | 484610.8438 | 4113198.75
Sensors/bank |  | 3 | 3 | 3 | 3 | 14000 | 1.3137 | 9 | 0.75209 | 177884 | 3238.0715 | 630 | 1620 | 2160 | 630 | 8278.0713 | 246.4714 | 127750 | 314158.5312 | 454116.5625 | 3947052.75
Redundancy | [5 empty] | 15000 | 1.4035 | 9 | 0.70394 | 166495.0781 | 3022.2 | 630 | 1620 | 2160 | 630 | 8062.2002 | 240.84 | 127750 | 302548.125 | 425042 | 3788889.25
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 16000 | 1.5011 | 6 | 0.98729 | 155676.1094 | 1888.875 | 420 | 1080 | 1440 | 420 | 5248.875 | 157.275 | 127750 | 288832.25 | 397422.5 | 3608771.25
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 20 | 20 | 20 | 20
Lamp Life | hrs | 5000 | 5000 | 5000 | 5000 | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | 79.5413 | 81.8584 | 79.0453 | 65.5965 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | 575 | 575 | 575 | 575 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 15 | 15 | 15 | 15 | 200 | 1 | 9 | 0.99664 | 235725 | 226665 | 630 | 1620 | 2160 | 630 | 231705 | 6075.0005 | 127750 | 601255 | 613937.75 | 7298923.5
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | 400 | 0.98004 | 12 | 0.7627 | 240525.9375 | 151110 | 840 | 2160 | 2880 | 840 | 157830 | 4157.9995 | 127750 | 530263.9375 | 626441.5625 | 6522121.5
Coefficient A |  | 0.65189 | 0.43162 | 0.3407 | 0.57696 | 600 | 0.92429 | 12 | 0.80871 | 255033.5312 | 100740 | 840 | 2160 | 2880 | 840 | 107460 | 2844 | 127750 | 493087.5312 | 664226.125 | 6146564
Coefficient B |  | 1.0001 | 1.0001 | 1 | 1.0001 | 800 | 0.88951 | 12 | 0.84032 | 265004.7812 | 75555 | 840 | 2160 | 2880 | 840 | 82275 | 2187 | 127750 | 477216.7812 | 690195.9375 | 5996077
Coefficient C |  | -0.22945 | -0.17162 | -0.16659 | -0.25193 | 1000 | 0.86558 | 12 | 0.86356 | 272332.6875 | 60444 | 840 | 2160 | 2880 | 840 | 67164 | 1792.8 | 127750 | 469039.5 | 709281.1875 | 5924244
Coefficient D |  | 0 | 0 | 0 | 0 | 2000 | 0.81203 | 12 | 0.92051 | 290291.4375 | 30222 | 840 | 2160 | 2880 | 840 | 36942 | 1004.4 | 127750 | 455987.8438 | 756054.125 | 5825903.5
Coefficient E |  | 0 | 0 | 0 | 0 | 3000 | 0.80035 | 12 | 0.93394 | 294527.8438 | 20148 | 840 | 2160 | 2880 | 840 | 26868 | 741.6 | 127750 | 449887.4375 | 767087.75 | 5769110.5
Coefficient F |  | 0 | 0 | 0 | 0 | 4000 | 0.80494 | 12 | 0.92861 | 292846.25 | 15111 | 840 | 2160 | 2880 | 840 | 21831 | 610.2 | 127750 | 443037.4375 | 762708.0625 | 5688570
Lamp Power | kW | 0 | 0 | 0 | 0 | 5000 | 0.81858 | 12 | 0.91314 | 287966.9062 | 12088.7998 | 840 | 2160 | 2880 | 840 | 18808.8008 | 531.36 | 127750 | 435057.0625 | 750000 | 5587133
Lamp Aging Equation | 9999 | 79.5413 | 81.8584 | 79.0453 | 65.5965 | 6000 | 0.83831 | 12 | 0.89165 | 281191.9375 | 10074 | 840 | 2160 | 2880 | 840 | 16794 | 478.8 | 127750 | 426214.75 | 732354.8125 | 5471175.5
Sleeve Data | [5 empty] | 7000 | 0.86267 | 12 | 0.86648 | 273252.0625 | 8634.8574 | 840 | 2160 | 2880 | 840 | 15354.8574 | 441.2571 | 127750 | 416798.1875 | 711675.625 | 5345799.5
Sleeve Life | yrs | 5 | 5 | 5 | 5 | 8000 | 0.89088 | 12 | 0.83904 | 264598.375 | 7555.5 | 840 | 2160 | 2880 | 840 | 14275.5 | 413.1 | 127750 | 407036.9688 | 689137.4375 | 5214732
Sleeve Cost | $ | 350 | 350 | 350 | 350 | 9000 | 0.9225 | 12 | 0.81027 | 255527.1719 | 6716 | 840 | 2160 | 2880 | 840 | 13436 | 391.2 | 127750 | 397104.375 | 665511.8125 | 5080672
Sleeve Replacement Time | min | 25 | 25 | 25 | 25 | 10000 | 0.95729 | 12 | 0.78083 | 246241.4219 | 6044.3999 | 840 | 2160 | 2880 | 840 | 12764.4004 | 373.68 | 127750 | 387129.5 | 641327.375 | 4945583
Sleeve Cleaning Type (Rinse, Wiper) |  | Wiper | Wiper | Wiper | Wiper | 11000 | 0.99511 | 12 | 0.75115 | 236884.1562 | 5494.9092 | 840 | 2160 | 2880 | 840 | 12214.9092 | 359.3455 | 127750 | 377208.4062 | 616956.75 | 4810906
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 12000 | 1.0359 | 9 | 0.96211 | 227558.1562 | 3777.75 | 630 | 1620 | 2160 | 630 | 8817.75 | 260.55 | 127750 | 364386.4688 | 592667.5 | 4644057.5
Sleeve Cleaning Time/Reactor | min | 0 | 0 | 0 | 0 | 13000 | 1.0796 | 9 | 0.92313 | 218338.0469 | 3487.1538 | 630 | 1620 | 2160 | 630 | 8527.1543 | 252.9692 | 127750 | 354868.1562 | 568654 | 4514215.5
Fouling Factor | % | 85 | 85 | 85 | 85 | 14000 | 1.1264 | 9 | 0.88482 | 209278.2344 | 3238.0715 | 630 | 1620 | 2160 | 630 | 8278.0713 | 246.4714 | 127750 | 345552.7812 | 545058 | 4387047.5
[6 empty] | 15000 | 1.1762 | 9 | 0.84736 | 200418.3125 | 3022.2 | 630 | 1620 | 2160 | 630 | 8062.2002 | 240.84 | 127750 | 336471.3438 | 521982.6875 | 4263001.5
Ballast Data | [5 empty] | 16000 | 1.2291 | 9 | 0.81087 | 191786.8438 | 2833.3125 | 630 | 1620 | 2160 | 630 | 7873.3125 | 235.9125 | 127750 | 327646.0625 | 499502.25 | 4142398
Ballast Life | yrs | 10 | 10 | 10 | 10
Ballast Costs | $ | 1800 | 1800 | 1800 | 1800
Ballast replacement | min | 60 | 60 | 60 | 60
Sensor Data | [5 empty] | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | 5 | 5 | 5 | 5 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | 1200 | 1200 | 1200 | 1200 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 10 | 10 | 10 | 10 | 200 | 1 | 9 | 0.98612 | 233238.0938 | 226665 | 630 | 1620 | 2160 | 630 | 231705 | 6075.0005 | 127750 | 598768.125 | 592839.375 | 7250175
Sensor cal period | months | 12 | 12 | 12 | 12 | 400 | 0.98019 | 12 | 0.75454 | 237952.125 | 151110 | 840 | 2160 | 2880 | 840 | 157830 | 4157.9995 | 127750 | 527690.125 | 604821.375 | 6471884.5
Sensor calibration cost | $ | 70 | 70 | 70 | 70 | 600 | 0.9244 | 12 | 0.80008 | 252314.2344 | 100740 | 840 | 2160 | 2880 | 840 | 107460 | 2844 | 127750 | 490368.25 | 641326.625 | 6093430.5
Sensor calibration | min | 5 | 5 | 5 | 5 | 800 | 0.88905 | 12 | 0.83189 | 262344.8125 | 75555 | 840 | 2160 | 2880 | 840 | 82275 | 2187 | 127750 | 474556.8125 | 666822.1875 | 5943128.5
[6 empty] | 1000 | 0.8643 | 12 | 0.85571 | 269857.1875 | 60444 | 840 | 2160 | 2880 | 840 | 67164 | 1792.8 | 127750 | 466564 | 685917 | 5873356
Dose Pacing | Enter if dose pacing responds to the following parameters. |  |  |  |  | 2000 | 0.80525 | 12 | 0.91847 | 289647.2188 | 30222 | 840 | 2160 | 2880 | 840 | 36942 | 1004.4 | 127750 | 455343.625 | 736218.8125 | 5798905.5
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling |  |  |  |  | 3000 | 0.78706 | 12 | 0.93969 | 296340.8438 | 20148 | 840 | 2160 | 2880 | 840 | 26868 | 741.6 | 127750 | 451700.4375 | 753232.5 | 5775413
| Peak dose will be equal to or greater than the design dose. |  |  |  |  | 4000 | 0.78453 | 12 | 0.94273 | 297298.1562 | 15111 | 840 | 2160 | 2880 | 840 | 21831 | 610.2 | 127750 | 447489.3438 | 755665.8125 | 5731025.5
Peak UV Dose ** | mJ/cm^2 | 34.3499 | 35.044 | 34.2005 | 30.0333 | 5000 | 0.79045 | 12 | 0.93566 | 295069.0938 | 12088.7998 | 840 | 2160 | 2880 | 840 | 18808.8008 | 531.36 | 127750 | 442159.25 | 750000 | 5666098
Flow (y/n) |  | n | n | n | n | 6000 | 0.80186 | 12 | 0.92235 | 290871.9062 | 10074 | 840 | 2160 | 2880 | 840 | 16794 | 478.8 | 127750 | 435894.7188 | 739331.6875 | 5585778
Lamp Age (y/n) |  | n | n | n | n | 7000 | 0.81726 | 12 | 0.90497 | 285392 | 8634.8574 | 840 | 2160 | 2880 | 840 | 15354.8574 | 441.2571 | 127750 | 428938.125 | 725403 | 5494503
UVT (y/n) |  | n | n | n | n | 8000 | 0.83581 | 12 | 0.88488 | 279055.125 | 7555.5 | 840 | 2160 | 2880 | 840 | 14275.5 | 413.1 | 127750 | 421493.7188 | 709296.0625 | 5395626.5
Fouling (y/n) |  | n | n | n | n | 9000 | 0.85704 | 12 | 0.86296 | 272144.0625 | 6716 | 840 | 2160 | 2880 | 840 | 13436 | 391.2 | 127750 | 413721.25 | 691729.6875 | 5291642.5
[6 empty] | 10000 | 0.88062 | 12 | 0.83985 | 264855.5 | 6044.3999 | 840 | 2160 | 2880 | 840 | 12764.4004 | 373.68 | 127750 | 405743.5938 | 673203.75 | 5184418
WTP INPUTS | [5 empty] | 11000 | 0.90637 | 12 | 0.81599 | 257330.9062 | 5494.9092 | 840 | 2160 | 2880 | 840 | 12214.9092 | 359.3455 | 127750 | 397655.1562 | 654077.9375 | 5075362
Labor rate | $/hr | 60 | 60 | 60 | 60 | 12000 | 0.93417 | 12 | 0.79171 | 249674.7031 | 5037 | 840 | 2160 | 2880 | 840 | 11757 | 347.4 | 127750 | 389529.0938 | 634617.5625 | 4965553
Electricity Cost | $/kWhr | 0.15 | 0.15 | 0.15 | 0.15 | 13000 | 0.96393 | 12 | 0.76727 | 241965.2031 | 4649.5386 | 840 | 2160 | 2880 | 840 | 11369.5391 | 337.2923 | 127750 | 381422.0312 | 615021.75 | 4855819.5
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 14000 | 0.99563 | 9 | 0.99045 | 234262.0625 | 3238.0715 | 630 | 1620 | 2160 | 630 | 8278.0713 | 246.4714 | 127750 | 370536.5938 | 595442.0625 | 4715211.5
Interest rate | % | 4 | 4 | 4 | 4 | 15000 | 1.0292 | 9 | 0.9581 | 226610.9688 | 3022.2 | 630 | 1620 | 2160 | 630 | 8062.2002 | 240.84 | 127750 | 362664 | 575994.75 | 4608233.5
Period | yrs | 15 | 15 | 15 | 15 | 16000 | 1.0648 | 9 | 0.92613 | 219047.1562 | 2833.3125 | 630 | 1620 | 2160 | 630 | 7873.3125 | 235.9125 | 127750 | 354906.375 | 556769.1875 | 4502755.5
CAPITAL COSTS INPUTS | [5 empty] | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | 750000 | 750000 | 750000 | 750000 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ |  |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $ |  |  |  |  | 200 | 1 | 9 | 0.93189 | 220411.625 | 226665 | 630 | 1620 | 2160 | 630 | 231705 | 6075.0005 | 127750 | 585941.625 | 491973.9062 | 7006700
Inlet/Oultet Piping | [5 empty] | 400 | 0.9695 | 9 | 0.96121 | 227344.75 | 113332.5 | 630 | 1620 | 2160 | 630 | 118372.5 | 3118.5002 | 127750 | 476585.75 | 507449.125 | 5806314
Valves | Total $ |  |  |  |  | 600 | 0.88476 | 12 | 0.78996 | 249120.6406 | 100740 | 840 | 2160 | 2880 | 840 | 107460 | 2844 | 127750 | 487174.625 | 556054.375 | 5972650.5
Flowmeters | Total $ |  |  |  |  | 800 | 0.83174 | 12 | 0.84031 | 265001 | 75555 | 840 | 2160 | 2880 | 840 | 82275 | 2187 | 127750 | 477213 | 591500.5 | 5897339.5
Piping and Appurtences | Total $ |  |  |  |  | 1000 | 0.79471 | 12 | 0.87946 | 277347.375 | 60444 | 840 | 2160 | 2880 | 840 | 67164 | 1792.8 | 127750 | 474054.1875 | 619058.4375 | 5889776.5
Channels | Total $ |  |  |  |  | 2000 | 0.70398 | 12 | 0.99281 | 313092.1875 | 30222 | 840 | 2160 | 2880 | 840 | 36942 | 1004.4 | 127750 | 478788.5938 | 698843.375 | 6022200.5
Power | [5 empty] | 3000 | 0.67049 | 15 | 0.83393 | 328733.8438 | 25185 | 1050 | 2700 | 3600 | 1050 | 33585 | 927 | 127750 | 490995.8438 | 733756.625 | 6192838.5
Switch gear | Total $ |  |  |  |  | 4000 | 0.65782 | 15 | 0.84999 | 335065.5312 | 18888.75 | 1050 | 2700 | 3600 | 1050 | 27288.75 | 762.75 | 127750 | 490867.0312 | 747889.3125 | 6205539
Transformer | Total $ |  |  |  |  | 5000 | 0.65597 | 15 | 0.85239 | 336011.1562 | 15111 | 1050 | 2700 | 3600 | 1050 | 23511 | 664.2 | 127750 | 487936.3438 | 750000.0625 | 6175065.5
Distribution Panels | Total $ |  |  |  |  | 6000 | 0.66088 | 15 | 0.84605 | 333511.8438 | 12592.5 | 1050 | 2700 | 3600 | 1050 | 20992.5 | 598.5 | 127750 | 482852.8438 | 744421.3125 | 6112966
Generator | Total $ |  |  |  |  | 7000 | 0.67058 | 15 | 0.83382 | 328690.0312 | 10793.5713 | 1050 | 2700 | 3600 | 1050 | 19193.5703 | 551.5715 | 127750 | 476185.1875 | 733658.75 | 6028070
UPS | Total $ |  |  |  |  | 8000 | 0.68396 | 15 | 0.8175 | 322259.5625 | 9444.375 | 1050 | 2700 | 3600 | 1050 | 17844.375 | 516.375 | 127750 | 468370.3125 | 719305.5 | 5926828
Misc Electrical | Total $ |  |  |  |  | 9000 | 0.70038 | 12 | 0.99792 | 314703.8438 | 6716 | 840 | 2160 | 2880 | 840 | 13436 | 391.2 | 127750 | 456281.0312 | 702440.625 | 5775550
Other | [5 empty] | 10000 | 0.71944 | 12 | 0.97148 | 306364.9375 | 6044.3999 | 840 | 2160 | 2880 | 840 | 12764.4004 | 373.68 | 127750 | 447253.0312 | 683827.625 | 5656560
Yard piping | Total $ |  |  |  |  | 11000 | 0.7409 | 12 | 0.94334 | 297492.8125 | 5494.9092 | 840 | 2160 | 2880 | 840 | 12214.9092 | 359.3455 | 127750 | 437817.0625 | 664024.4375 | 5531844
Chlorine contactor | Total $ |  |  |  |  | 12000 | 0.76459 | 12 | 0.91411 | 288274.2812 | 5037 | 840 | 2160 | 2880 | 840 | 11757 | 347.4 | 127750 | 428128.6875 | 643448 | 5403548.5
Low lift pumps | Total $ |  |  |  |  | 13000 | 0.79043 | 12 | 0.88423 | 278851.4062 | 4649.5386 | 840 | 2160 | 2880 | 840 | 11369.5391 | 337.2923 | 127750 | 418308.25 | 622415.5 | 5273328.5
UV Building | [5 empty] | 14000 | 0.81836 | 12 | 0.85405 | 269333.5625 | 4317.4287 | 840 | 2160 | 2880 | 840 | 11037.4287 | 328.6286 | 127750 | 408449.625 | 601171 | 5142472
Demolition | Total $ |  |  |  |  | 15000 | 0.84837 | 12 | 0.82384 | 259805.5625 | 4029.6001 | 840 | 2160 | 2880 | 840 | 10749.5996 | 321.12 | 127750 | 398626.2812 | 579903.875 | 5011985
Civil/sitework | Total $ |  |  |  |  | 16000 | 0.88047 | 12 | 0.7938 | 250333.5469 | 3777.75 | 840 | 2160 | 2880 | 840 | 10497.75 | 314.55 | 127750 | 388895.8438 | 558761.6875 | 4882656.5
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 124.6793 | 124.6793 | 124.6793 | 124.6793
95% UVT | mJ/cm2 | 80.2288 | 80.2288 | 80.2288 | 80.2288
90% UVT | mJ/cm2 | 45.1189 | 45.1189 | 45.1189 | 45.1189
85% UVT | mJ/cm2 | 28.2197 | 28.2197 | 28.2197 | 28.2197
80% UVT | mJ/cm2 | 18.938 | 18.938 | 18.938 | 18.938
75% UVT | mJ/cm2 | 13.4289 | 13.4289 | 13.4289 | 13.4289
70% UVT | mJ/cm2 | 9.9859 | 9.9859 | 9.9859 | 9.9859
65% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
|  | 2.1514 | 2.1514 | 2.1514 | 2.1514
|  | 10.2072 | 10.2072 | 10.2072 | 10.2072
|  | 0.69671 | 0.69671 | 0.69671 | 0.69671
|  | 1.0956 | 1.0956 | 1.0956 | 1.0956
Lamp Analysis
Clear

## LAMP AGE LCA TOOL (3)
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 4
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions |  | MP Reactor 2 - Modified Exponential Model
Units: y = %, x = hrs |  | Power | 0.05
MMF: y=(a*b+c*x^d)/(b+x^d) |  | Interest | 4
EXP: y=a*e^(b*x) |  | Period | 15
LIN: Y = ax+b |  | Dose pacing | full
| 0 | 1 | 2 | 3 | 4 | Simulation - Cost Benefit Analysis for Case 1
Lamp Type | [5 empty] | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Vendor | [5 empty] | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment | [5 empty] | 200 | 0.98883 | 8 | 0.83817 | 35243.2539 | 96360 | 280 | 4800 | 5600 | 4400 | 111440 | 1149.8667 | 127750 | 275583.125 | 869899.25 | 3933939.25
[6 empty] | 400 | 0.97839 | 8 | 0.84239 | 35420.8438 | 48180 | 280 | 4800 | 5600 | 4400 | 63260 | 624.2667 | 127750 | 227055.1094 | 879183.1875 | 3403669.75
UV SYSTEM SIZING CRITERIA | [5 empty] | 600 | 0.96863 | 8 | 0.84627 | 35584.0117 | 32120 | 280 | 4800 | 5600 | 4400 | 47200 | 449.0667 | 127750 | 210983.0781 | 888044.9375 | 3233836.5
[6 empty] | 800 | 0.9595 | 8 | 0.84978 | 35731.5547 | 24090 | 280 | 4800 | 5600 | 4400 | 39170 | 361.4667 | 127750 | 203013.0156 | 896493.9375 | 3153671.25
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 1000 | 0.95096 | 8 | 0.85298 | 35866.0391 | 19272 | 280 | 4800 | 5600 | 4400 | 34352 | 308.9067 | 127750 | 198276.9531 | 904540.6875 | 3109060.75
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 2000 | 0.91592 | 8 | 0.86466 | 36357.1172 | 9636 | 280 | 4800 | 5600 | 4400 | 24716 | 203.7867 | 127750 | 189026.9062 | 939149.8125 | 3040824.25
Average UVT | % | 93 | 93 | 93 | 93 | 3000 | 0.89087 | 8 | 0.87065 | 36609.043 | 6424 | 280 | 4800 | 5600 | 4400 | 21504 | 168.7467 | 127750 | 186031.7969 | 965551.625 | 3033925.25
Design UVT | % | 90 | 90 | 90 | 90 | 4000 | 0.87298 | 8 | 0.87275 | 36697.543 | 4818 | 280 | 4800 | 5600 | 4400 | 19898 | 151.2267 | 127750 | 184496.7656 | 985347.8125 | 3036654.25
Design UV Dose | mJ/cm^2 | 32 | 32 | 32 | 32 | 5000 | 0.86018 | 8 | 0.87233 | 36679.5898 | 3854.3999 | 280 | 4800 | 5600 | 4400 | 18934.4004 | 140.7147 | 127750 | 183504.7031 | 1000000 | 3040276.25
REACTOR DESIGN INPUTS | [5 empty] | 6000 | 0.85104 | 8 | 0.87033 | 36595.668 | 3212 | 280 | 4800 | 5600 | 4400 | 18292 | 133.7067 | 127750 | 182771.375 | 1010741.125 | 3042864
Configuration | [5 empty] | 7000 | 0.84451 | 8 | 0.86749 | 36476.1719 | 2753.1428 | 280 | 4800 | 5600 | 4400 | 17833.1426 | 128.701 | 127750 | 182188.0156 | 1018559.6875 | 3044196.5
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 25.7 | 8000 | 0.83984 | 8 | 0.86424 | 36339.7148 | 2409 | 280 | 4800 | 5600 | 4400 | 17489 | 124.9467 | 127750 | 181703.6562 | 1024221.75 | 3044473.25
Number of Trains |  | 4 | 4 | 4 | 4 | 9000 | 0.83651 | 8 | 0.86093 | 36200.1914 | 2141.3333 | 280 | 4800 | 5600 | 4400 | 17221.334 | 122.0267 | 127750 | 181293.5469 | 1028306.9375 | 3043998.75
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 10000 | 0.83412 | 8 | 0.85769 | 36064.3008 | 1927.2 | 280 | 4800 | 5600 | 4400 | 17007.1992 | 119.6907 | 127750 | 180941.1875 | 1031246.4375 | 3043020.5
Banks/Reactor |  | 1 | 1 | 1 | 1 | 11000 | 0.83242 | 8 | 0.85468 | 35937.5117 | 1752 | 280 | 4800 | 5600 | 4400 | 16832 | 117.7794 | 127750 | 180637.2969 | 1033357.5 | 3041753
Lamps/Bank |  | 8 | 8 | 8 | 8 | 12000 | 0.8312 | 8 | 0.85192 | 35821.3633 | 1606 | 280 | 4800 | 5600 | 4400 | 16686 | 116.1867 | 127750 | 180373.5469 | 1034871.4375 | 3040334.5
Lamps/Ballast |  | 2 | 2 | 2 | 2 | 13000 | 0.83033 | 8 | 0.84944 | 35717.1484 | 1482.4615 | 280 | 4800 | 5600 | 4400 | 16562.4609 | 114.839 | 127750 | 180144.4531 | 1035956.125 | 3038872
Sensors/bank |  | 8 | 8 | 8 | 8 | 14000 | 0.82971 | 8 | 0.84724 | 35624.6055 | 1376.5714 | 280 | 4800 | 5600 | 4400 | 16456.5723 | 113.6838 | 127750 | 179944.8594 | 1036732.625 | 3037429.25
Redundancy | [5 empty] | 15000 | 0.82926 | 8 | 0.84531 | 35543.4531 | 1284.8 | 280 | 4800 | 5600 | 4400 | 16364.7998 | 112.6827 | 127750 | 179770.9375 | 1037288.375 | 3036051.25
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 16000 | 0.82895 | 8 | 0.84362 | 35472.4883 | 1204.5 | 280 | 4800 | 5600 | 4400 | 16284.5 | 111.8067 | 127750 | 179618.7969 | 1037685.875 | 3034757.25
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 12 | 12 | 12 | 12
Lamp Life | hrs | 5000 | 5000 | 5000 | 5000 | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | 86.0185 | 85.6146 | 80.7612 | 74.7354 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | 275 | 275 | 275 | 275 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 3 | 3 | 3 | 3 | 200 | 0.98606 | 8 | 0.838 | 35236.1367 | 96360 | 280 | 4800 | 5600 | 4400 | 111440 | 1149.8667 | 127750 | 275576 | 868251.375 | 3932212
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | 400 | 0.97333 | 8 | 0.84308 | 35449.7539 | 48180 | 280 | 4800 | 5600 | 4400 | 63260 | 624.2667 | 127750 | 227084.0156 | 879607.5 | 3404415.5
Coefficient A |  | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 600 | 0.9617 | 8 | 0.84758 | 35639.2227 | 32120 | 280 | 4800 | 5600 | 4400 | 47200 | 449.0667 | 127750 | 211038.2969 | 890238.75 | 3236644.25
Coefficient B |  | 0.8868 | 1.0029 | 1.0107 | -2.0993 | 800 | 0.95109 | 8 | 0.85145 | 35801.625 | 24090 | 280 | 4800 | 5600 | 4400 | 39170 | 361.4667 | 127750 | 203083.0938 | 900172.625 | 3158129
Coefficient C |  | 0.038 | 0.0396 | 0.0412 | 0.0237 | 1000 | 0.9414 | 8 | 0.85487 | 35945.4727 | 19272 | 280 | 4800 | 5600 | 4400 | 34352 | 308.9067 | 127750 | 198356.375 | 909438.25 | 3114841.25
Coefficient D |  | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 2000 | 0.90422 | 8 | 0.86547 | 36391.4883 | 9636 | 280 | 4800 | 5600 | 4400 | 24716 | 203.7867 | 127750 | 189061.2812 | 946837.8125 | 3048894.25
Coefficient E |  | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 3000 | 0.88062 | 8 | 0.8686 | 36523.0703 | 6424 | 280 | 4800 | 5600 | 4400 | 21504 | 168.7467 | 127750 | 185945.8125 | 972208 | 3039625.5
Coefficient F |  | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 4000 | 0.86565 | 8 | 0.8675 | 36476.5977 | 4818 | 280 | 4800 | 5600 | 4400 | 19898 | 151.2267 | 127750 | 184275.8281 | 989024.125 | 3037874.25
Lamp Power | kW | 12 | 12 | 12 | 12 | 5000 | 0.85615 | 8 | 0.86431 | 36342.4258 | 3854.3999 | 280 | 4800 | 5600 | 4400 | 18934.4004 | 140.7147 | 127750 | 183167.5469 | 1000000 | 3036527.75
Lamp Aging Equation | 9999 | 86.0185 | 85.6146 | 80.7612 | 74.7354 | 6000 | 0.85012 | 8 | 0.86028 | 36173.1523 | 3212 | 280 | 4800 | 5600 | 4400 | 18292 | 133.7067 | 127750 | 182348.8594 | 1007092.0625 | 3034517.25
Sleeve Data | [5 empty] | 7000 | 0.84629 | 8 | 0.85614 | 35998.9375 | 2753.1428 | 280 | 4800 | 5600 | 4400 | 17833.1426 | 128.701 | 127750 | 181710.7812 | 1011644.75 | 3031975.5
Sleeve Life | yrs | 10 | 10 | 10 | 10 | 8000 | 0.84386 | 8 | 0.85226 | 35836.0195 | 2409 | 280 | 4800 | 5600 | 4400 | 17489 | 124.9467 | 127750 | 181199.9688 | 1014555.125 | 3029206.5
Sleeve Cost | $ | 350 | 350 | 350 | 350 | 9000 | 0.84232 | 8 | 0.84881 | 35690.875 | 2141.3333 | 280 | 4800 | 5600 | 4400 | 17221.334 | 122.0267 | 127750 | 180784.2344 | 1016410.625 | 3026439.75
Sleeve Replacement Time | min | 10 | 10 | 10 | 10 | 10000 | 0.84135 | 8 | 0.84584 | 35565.7539 | 1927.2 | 280 | 4800 | 5600 | 4400 | 17007.1992 | 119.6907 | 127750 | 180442.6406 | 1017591.625 | 3023822.75
Sleeve Cleaning Type (Rinse, Wiper) |  | Wiper | Wiper | Wiper | Wiper | 11000 | 0.84072 | 8 | 0.84333 | 35460.1875 | 1752 | 280 | 4800 | 5600 | 4400 | 16832 | 117.7794 | 127750 | 180159.9688 | 1018342.375 | 3021430.75
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 12000 | 0.84033 | 8 | 0.84124 | 35372.2656 | 1606 | 280 | 4800 | 5600 | 4400 | 16686 | 116.1867 | 127750 | 179924.4531 | 1018819.4375 | 3019289.25
Sleeve Cleaning Time/Reactor | min | 0 | 0 | 0 | 0 | 13000 | 0.84008 | 8 | 0.83951 | 35299.8672 | 1482.4615 | 280 | 4800 | 5600 | 4400 | 16562.4609 | 114.839 | 127750 | 179727.1719 | 1019122.3125 | 3017398.5
Fouling Factor | % | 95 | 95 | 95 | 95 | 14000 | 0.83992 | 8 | 0.83811 | 35240.7344 | 1376.5714 | 280 | 4800 | 5600 | 4400 | 16456.5723 | 113.6838 | 127750 | 179560.9844 | 1019314.625 | 3015743.25
[6 empty] | 15000 | 0.83982 | 8 | 0.83697 | 35192.7227 | 1284.8 | 280 | 4800 | 5600 | 4400 | 16364.7998 | 112.6827 | 127750 | 179420.2031 | 1019436.6875 | 3014300
Ballast Data | [5 empty] | 16000 | 0.83976 | 8 | 0.83604 | 35153.8398 | 1204.5 | 280 | 4800 | 5600 | 4400 | 16284.5 | 111.8067 | 127750 | 179300.1406 | 1019514.125 | 3013042.5
Ballast Life | yrs | 5 | 5 | 5 | 5
Ballast Costs | $ | 6000 | 6000 | 6000 | 6000
Ballast replacement | min | 30 | 30 | 30 | 30
Sensor Data | [5 empty] | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | 3 | 3 | 3 | 3 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | 2100 | 2100 | 2100 | 2100 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 10 | 10 | 10 | 10 | 200 | 0.97939 | 8 | 0.82488 | 34684.5039 | 96360 | 280 | 4800 | 5600 | 4400 | 111440 | 1149.8667 | 127750 | 275024.375 | 824607 | 3882434.5
Sensor cal period | months | 12 | 12 | 12 | 12 | 400 | 0.96083 | 8 | 0.83221 | 34992.6836 | 48180 | 280 | 4800 | 5600 | 4400 | 63260 | 624.2667 | 127750 | 226626.9531 | 840538.75 | 3360265
Sensor calibration cost | $ | 550 | 550 | 550 | 550 | 600 | 0.94411 | 8 | 0.83848 | 35256.2891 | 32120 | 280 | 4800 | 5600 | 4400 | 47200 | 449.0667 | 127750 | 210655.3594 | 855425 | 3197572.75
Sensor calibration | min | 5 | 5 | 5 | 5 | 800 | 0.92905 | 8 | 0.84391 | 35484.8867 | 24090 | 280 | 4800 | 5600 | 4400 | 39170 | 361.4667 | 127750 | 202766.3594 | 869292.0625 | 3123727
[6 empty] | 1000 | 0.91548 | 8 | 0.84858 | 35680.918 | 19272 | 280 | 4800 | 5600 | 4400 | 34352 | 308.9067 | 127750 | 198091.8281 | 882172.9375 | 3084634.5
Dose Pacing | Enter if dose pacing responds to the following parameters. |  |  |  |  | 2000 | 0.86537 | 8 | 0.86172 | 36233.4219 | 9636 | 280 | 4800 | 5600 | 4400 | 24716 | 203.7867 | 127750 | 188903.2031 | 933253.75 | 3033552.75
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling |  |  |  |  | 3000 | 0.83567 | 8 | 0.86383 | 36322.457 | 6424 | 280 | 4800 | 5600 | 4400 | 21504 | 168.7467 | 127750 | 185745.2031 | 966429.875 | 3031617
| Peak dose will be equal to or greater than the design dose. |  |  |  |  | 4000 | 0.81805 | 8 | 0.86038 | 36177.0664 | 4818 | 280 | 4800 | 5600 | 4400 | 19898 | 151.2267 | 127750 | 183976.2969 | 987236.3125 | 3032756
Peak UV Dose ** | mJ/cm^2 | 36.3908 | 36.2756 | 34.8775 | 33.1028 | 5000 | 0.80761 | 8 | 0.85463 | 35935.5312 | 3854.3999 | 280 | 4800 | 5600 | 4400 | 18934.4004 | 140.7147 | 127750 | 182760.6406 | 1000000.0625 | 3032003.75
Flow (y/n) |  | y | y | y | y | 6000 | 0.80142 | 8 | 0.8484 | 35673.5195 | 3212 | 280 | 4800 | 5600 | 4400 | 18292 | 133.7067 | 127750 | 181849.2188 | 1007724.125 | 3029594.25
Lamp Age (y/n) |  | y | y | y | y | 7000 | 0.79775 | 8 | 0.84253 | 35426.8867 | 2753.1428 | 280 | 4800 | 5600 | 4400 | 17833.1426 | 128.701 | 127750 | 181138.7344 | 1012360.0625 | 3026330.75
UVT (y/n) |  | y | y | y | y | 8000 | 0.79558 | 8 | 0.83742 | 35211.7266 | 2409 | 280 | 4800 | 5600 | 4400 | 17489 | 124.9467 | 127750 | 180575.6719 | 1015128.75 | 3022839
Fouling (y/n) |  | y | y | y | y | 9000 | 0.79429 | 8 | 0.83312 | 35031.2266 | 2141.3333 | 280 | 4800 | 5600 | 4400 | 17221.334 | 122.0267 | 127750 | 180124.5938 | 1016777.3125 | 3019472.25
[6 empty] | 10000 | 0.79352 | 8 | 0.82961 | 34883.4727 | 1927.2 | 280 | 4800 | 5600 | 4400 | 17007.1992 | 119.6907 | 127750 | 179760.3594 | 1017757.1875 | 3016402.5
WTP INPUTS | [5 empty] | 11000 | 0.79307 | 8 | 0.82678 | 34764.4727 | 1752 | 280 | 4800 | 5600 | 4400 | 16832 | 117.7794 | 127750 | 179464.25 | 1018339.0625 | 3013692
Labor rate | $/hr | 60 | 60 | 60 | 60 | 12000 | 0.7928 | 8 | 0.82454 | 34670.2305 | 1606 | 280 | 4800 | 5600 | 4400 | 16686 | 116.1867 | 127750 | 179222.4219 | 1018684.3125 | 3011348.5
Electricity Cost | $/kWhr | 0.05 | 0.05 | 0.05 | 0.05 | 13000 | 0.79264 | 8 | 0.82277 | 34595.9102 | 1482.4615 | 280 | 4800 | 5600 | 4400 | 16562.4609 | 114.839 | 127750 | 179023.2031 | 1018889.125 | 3009338.5
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 14000 | 0.79255 | 8 | 0.82138 | 34537.5586 | 1376.5714 | 280 | 4800 | 5600 | 4400 | 16456.5723 | 113.6838 | 127750 | 178857.8125 | 1019010.5625 | 3007621
Interest rate | % | 4 | 4 | 4 | 4 | 15000 | 0.79249 | 8 | 0.8203 | 34492.1562 | 1284.8 | 280 | 4800 | 5600 | 4400 | 16364.7998 | 112.6827 | 127750 | 178719.6406 | 1019082.5625 | 3006156.75
Period | yrs | 15 | 15 | 15 | 15 | 16000 | 0.79246 | 8 | 0.81946 | 34456.8047 | 1204.5 | 280 | 4800 | 5600 | 4400 | 16284.5 | 111.8067 | 127750 | 178603.1094 | 1019125.3125 | 3004903.75
CAPITAL COSTS INPUTS | [5 empty] | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | 1000000 | 1000000 | 1000000 | 1000000 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ |  |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $ |  |  |  |  | 200 | 0.98811 | 8 | 0.80091 | 33676.4805 | 96360 | 280 | 4800 | 5600 | 4400 | 111440 | 1149.8667 | 127750 | 274016.3438 | 756343.375 | 3802963.25
Inlet/Oultet Piping | [5 empty] | 400 | 0.97639 | 8 | 0.80564 | 33875.6836 | 48180 | 280 | 4800 | 5600 | 4400 | 63260 | 624.2667 | 127750 | 225509.9531 | 765422.8125 | 3272729.75
Valves | Total $ |  |  |  |  | 600 | 0.96483 | 8 | 0.81039 | 34075.4531 | 32120 | 280 | 4800 | 5600 | 4400 | 47200 | 449.0667 | 127750 | 209474.5156 | 774592.625 | 3103611.5
Flowmeters | Total $ |  |  |  |  | 800 | 0.95344 | 8 | 0.81511 | 34273.7422 | 24090 | 280 | 4800 | 5600 | 4400 | 39170 | 361.4667 | 127750 | 201555.2031 | 783853.1875 | 3024822
Piping and Appurtences | Total $ |  |  |  |  | 1000 | 0.9422 | 8 | 0.81979 | 34470.5 | 19272 | 280 | 4800 | 5600 | 4400 | 34352 | 308.9067 | 127750 | 196881.4062 | 793205.0625 | 2982208.75
Channels | Total $ |  |  |  |  | 2000 | 0.88828 | 8 | 0.84301 | 35446.7383 | 9636 | 280 | 4800 | 5600 | 4400 | 24716 | 203.7867 | 127750 | 188116.5312 | 841348.3125 | 2932900.75
Power | [5 empty] | 3000 | 0.838 | 8 | 0.8657 | 36400.9414 | 6424 | 280 | 4800 | 5600 | 4400 | 21504 | 168.7467 | 127750 | 185823.6875 | 891834.125 | 2957893.75
Switch gear | Total $ |  |  |  |  | 4000 | 0.7911 | 8 | 0.88789 | 37333.8359 | 4818 | 280 | 4800 | 5600 | 4400 | 19898 | 151.2267 | 127750 | 185133.0625 | 944706.1875 | 3003087.25
Transformer | Total $ |  |  |  |  | 5000 | 0.74735 | 8 | 0.90938 | 38237.5547 | 3854.3999 | 280 | 4800 | 5600 | 4400 | 18934.4004 | 140.7147 | 127750 | 185062.6719 | 1000000 | 3057598.5
Distribution Panels | Total $ |  |  |  |  | 6000 | 0.70656 | 8 | 0.93025 | 39115.2656 | 3212 | 280 | 4800 | 5600 | 4400 | 18292 | 133.7067 | 127750 | 185290.9688 | 1057742.625 | 3117879.25
Generator | Total $ |  |  |  |  | 7000 | 0.6685 | 8 | 0.95032 | 39959.1328 | 2753.1428 | 280 | 4800 | 5600 | 4400 | 17833.1426 | 128.701 | 127750 | 185670.9688 | 1117950.625 | 3182312.25
UPS | Total $ |  |  |  |  | 8000 | 0.63301 | 8 | 0.96962 | 40770.3867 | 2409 | 280 | 4800 | 5600 | 4400 | 17489 | 124.9467 | 127750 | 186134.3281 | 1180629.75 | 3250143.25
Misc Electrical | Total $ |  |  |  |  | 9000 | 0.59991 | 8 | 0.98806 | 41545.9336 | 2141.3333 | 280 | 4800 | 5600 | 4400 | 17221.334 | 122.0267 | 127750 | 186639.2969 | 1245773.875 | 3320901.75
Other | [5 empty] | 10000 | 0.56904 | 16 | 0.50282 | 42285.1367 | 3854.3999 | 560 | 9600 | 11200 | 8800 | 34014.3984 | 239.3813 | 127750 | 204288.9219 | 1313363.875 | 3584727.25
Yard piping | Total $ |  |  |  |  | 11000 | 0.54024 | 16 | 0.51114 | 42985.1836 | 3504 | 560 | 9600 | 11200 | 8800 | 33664 | 235.5588 | 127750 | 204634.75 | 1383366.75 | 3658575.25
Chlorine contactor | Total $ |  |  |  |  | 12000 | 0.51339 | 16 | 0.519 | 43645.8086 | 3212 | 560 | 9600 | 11200 | 8800 | 33372 | 232.3733 | 127750 | 205000.1875 | 1455735 | 3735006.5
Low lift pumps | Total $ |  |  |  |  | 13000 | 0.48834 | 16 | 0.52639 | 44266.9805 | 2964.9231 | 560 | 9600 | 11200 | 8800 | 33124.9219 | 229.6779 | 127750 | 205371.5781 | 1530406.375 | 3813807
UV Building | [5 empty] | 14000 | 0.46497 | 16 | 0.53325 | 44844.0508 | 2753.1428 | 560 | 9600 | 11200 | 8800 | 32913.1445 | 227.3676 | 127750 | 205734.5625 | 1607302.375 | 3894739
Demolition | Total $ |  |  |  |  | 15000 | 0.44318 | 16 | 0.53962 | 45379.793 | 2569.6001 | 560 | 9600 | 11200 | 8800 | 32729.5996 | 225.3653 | 127750 | 206084.7656 | 1686329.5 | 3977659.75
Civil/sitework | Total $ |  |  |  |  | 16000 | 0.42286 | 16 | 0.54551 | 45874.8242 | 2409 | 560 | 9600 | 11200 | 8800 | 32569 | 223.6133 | 127750 | 206417.4375 | 1767377.5 | 4062406.5
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 95.039 | 95.039 | 95.039 | 95.039
95% UVT | mJ/cm2 | 66.4797 | 66.4797 | 66.4797 | 66.4797
90% UVT | mJ/cm2 | 41.6914 | 41.6914 | 41.6914 | 41.6914
85% UVT | mJ/cm2 | 28.4989 | 28.4989 | 28.4989 | 28.4989
80% UVT | mJ/cm2 | 20.6256 | 20.6256 | 20.6256 | 20.6256
75% UVT | mJ/cm2 | 15.6092 | 15.6092 | 15.6092 | 15.6092
70% UVT | mJ/cm2 | 12.2768 | 12.2768 | 12.2768 | 12.2768
65% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
|  | 2.3676 | 2.3676 | 2.3676 | 2.3676
|  | 8.2746 | 8.2746 | 8.2746 | 8.2746
|  | 0.67349 | 0.67349 | 0.67349 | 0.67349
|  | 0.93411 | 0.93411 | 0.93411 | 0.93411
Lamp Analysis
Clear

## LAMP AGE LCA TOOL (3.1)
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 4
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions |  | MP Reactor 2 - Modified Exponential Model
Units: y = %, x = hrs |  | Power | 0.15
MMF: y=(a*b+c*x^d)/(b+x^d) |  | Interest | 4
EXP: y=a*e^(b*x) |  | Period | 15
LIN: Y = ax+b |  | Dose pacing | none
| 0 | 1 | 2 | 3 | 4 | Simulation - Cost Benefit Analysis for Case 1
Lamp Type | [5 empty] | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Vendor | [5 empty] | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment | [5 empty] | 200 | 0.96888 | 24 | 0.77118 | 291837.875 | 289080 | 840 | 14400 | 16800 | 13200 | 334320 | 3449.6001 | 127750 | 757357.5 | 855088.5625 | 9275683
[6 empty] | 400 | 0.94337 | 24 | 0.79203 | 299729.7812 | 144540 | 840 | 14400 | 16800 | 13200 | 189780 | 1872.8 | 127750 | 619132.5625 | 878211.9375 | 7761967.5
UV SYSTEM SIZING CRITERIA | [5 empty] | 600 | 0.92246 | 24 | 0.80999 | 306525.5938 | 96360 | 840 | 14400 | 16800 | 13200 | 141600 | 1347.2001 | 127750 | 577222.8125 | 898123.75 | 7315910.5
[6 empty] | 800 | 0.90531 | 24 | 0.82533 | 312331.3125 | 72270 | 840 | 14400 | 16800 | 13200 | 117510 | 1084.4 | 127750 | 558675.6875 | 915134.6875 | 7126707.5
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 1000 | 0.89125 | 24 | 0.83835 | 317257.8438 | 57816 | 840 | 14400 | 16800 | 13200 | 103056 | 926.72 | 127750 | 548990.5625 | 929569.375 | 7033459
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 2000 | 0.85097 | 24 | 0.87803 | 332274.7188 | 28908 | 840 | 14400 | 16800 | 13200 | 74148 | 611.36 | 127750 | 534784.0625 | 973569 | 6919505.5
Average UVT | % | 93 | 93 | 93 | 93 | 3000 | 0.83605 | 24 | 0.8937 | 338204.125 | 19272 | 840 | 14400 | 16800 | 13200 | 64512 | 506.2401 | 127750 | 530972.375 | 990942.25 | 6894498.5
Design UVT | % | 90 | 90 | 90 | 90 | 4000 | 0.83053 | 24 | 0.89964 | 340454.4062 | 14454 | 840 | 14400 | 16800 | 13200 | 59694 | 453.68 | 127750 | 528352.0625 | 997535.5625 | 6871958.5
Design UV Dose | mJ/cm^2 | 32 | 32 | 32 | 32 | 5000 | 0.82848 | 24 | 0.90187 | 341295.5312 | 11563.2002 | 840 | 14400 | 16800 | 13200 | 56803.1992 | 422.144 | 127750 | 526270.875 | 1000000.0625 | 6851283.5
REACTOR DESIGN INPUTS | [5 empty] | 6000 | 0.82772 | 24 | 0.90269 | 341608.125 | 9636 | 840 | 14400 | 16800 | 13200 | 54876 | 401.12 | 127750 | 524635.25 | 1000916 | 6834014
Configuration | [5 empty] | 7000 | 0.82744 | 24 | 0.903 | 341724.0312 | 8259.4287 | 840 | 14400 | 16800 | 13200 | 53499.4297 | 386.1028 | 127750 | 523359.5625 | 1001255.625 | 6820170
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 25.7 | 8000 | 0.82734 | 24 | 0.90311 | 341767 | 7227 | 840 | 14400 | 16800 | 13200 | 52467 | 374.84 | 127750 | 522358.8438 | 1001381.5 | 6809169.5
Number of Trains |  | 4 | 4 | 4 | 4 | 9000 | 0.8273 | 24 | 0.90316 | 341782.875 | 6424 | 840 | 14400 | 16800 | 13200 | 51664 | 366.08 | 127750 | 521562.9688 | 1001428.125 | 6800367
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 10000 | 0.82729 | 24 | 0.90317 | 341788.8125 | 5781.6001 | 840 | 14400 | 16800 | 13200 | 51021.6016 | 359.072 | 127750 | 520919.5 | 1001445.4375 | 6793230
Banks/Reactor |  | 1 | 1 | 1 | 1 | 11000 | 0.82728 | 24 | 0.90318 | 341791 | 5256 | 840 | 14400 | 16800 | 13200 | 50496 | 353.3382 | 127750 | 520390.3438 | 1001451.8125 | 6787353
Lamps/Bank |  | 8 | 8 | 8 | 8 | 12000 | 0.82728 | 24 | 0.90318 | 341791.8125 | 4818 | 840 | 14400 | 16800 | 13200 | 50058 | 348.56 | 127750 | 519948.375 | 1001454.1875 | 6782441.5
Lamps/Ballast |  | 2 | 2 | 2 | 2 | 13000 | 0.82728 | 24 | 0.90318 | 341792.0938 | 4447.3848 | 840 | 14400 | 16800 | 13200 | 49687.3828 | 344.5169 | 127750 | 519574 | 1001455.0625 | 6778280
Sensors/bank |  | 8 | 8 | 8 | 8 | 14000 | 0.82728 | 24 | 0.90318 | 341792.2188 | 4129.7144 | 840 | 14400 | 16800 | 13200 | 49369.7148 | 341.0514 | 127750 | 519253 | 1001455.375 | 6774711.5
Redundancy | [5 empty] | 15000 | 0.82728 | 24 | 0.90318 | 341792.25 | 3854.3999 | 840 | 14400 | 16800 | 13200 | 49094.3984 | 338.048 | 127750 | 518974.6875 | 1001455.4375 | 6771617
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 16000 | 0.82728 | 24 | 0.90318 | 341792.2812 | 3613.5 | 840 | 14400 | 16800 | 13200 | 48853.5 | 335.42 | 127750 | 518731.1875 | 1001455.5625 | 6768910
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 12 | 12 | 12 | 12
Lamp Life | hrs | 5000 | 5000 | 5000 | 5000 | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | 82.8481 | 79.2047 | 70.7809 | 73.2445 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | 275 | 275 | 275 | 275 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 3 | 3 | 3 | 3 | 200 | 0.96497 | 24 | 0.76302 | 288750.4062 | 289080 | 840 | 14400 | 16800 | 13200 | 334320 | 3449.6001 | 127750 | 754270 | 820800.8125 | 9207067
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | 400 | 0.93578 | 24 | 0.78682 | 297757.9375 | 144540 | 840 | 14400 | 16800 | 13200 | 189780 | 1872.8 | 127750 | 617160.75 | 846405.5625 | 7708238
Coefficient A |  | 0.0313 | 0.0243 | 0.0179 | 2.3784 | 600 | 0.91145 | 24 | 0.80782 | 305704.7188 | 96360 | 840 | 14400 | 16800 | 13200 | 141600 | 1347.2001 | 127750 | 576401.9375 | 868995 | 7277655
Coefficient B |  | 0.8868 | 1.0029 | 1.0107 | -2.0993 | 800 | 0.89118 | 24 | 0.82619 | 312658.2188 | 72270 | 840 | 14400 | 16800 | 13200 | 117510 | 1084.4 | 127750 | 559002.625 | 888761 | 7103968.5
Coefficient C |  | 0.038 | 0.0396 | 0.0412 | 0.0237 | 1000 | 0.87429 | 24 | 0.84216 | 318698.9375 | 57816 | 840 | 14400 | 16800 | 13200 | 103056 | 926.72 | 127750 | 550431.6875 | 905932.3125 | 7025845
Coefficient D |  | 0.8842 | 0.8521 | 0.7217 | 1.0582 | 2000 | 0.82378 | 24 | 0.8938 | 338241 | 28908 | 840 | 14400 | 16800 | 13200 | 74148 | 611.36 | 127750 | 540750.375 | 961482.625 | 6973754.5
Coefficient E |  | 0.0872 | 0.0161 | 0.0093 | 0.0045 | 3000 | 0.80348 | 24 | 0.91637 | 346785.4375 | 19272 | 840 | 14400 | 16800 | 13200 | 64512 | 506.2401 | 127750 | 539553.6875 | 985770.9375 | 6984738
Coefficient F |  | -2.6733 | -1.7152 | -1.3843 | -2.0043 | 4000 | 0.79532 | 24 | 0.92577 | 350341.5625 | 14454 | 840 | 14400 | 16800 | 13200 | 59694 | 453.68 | 127750 | 538239.25 | 995879.5625 | 6980232
Lamp Power | kW | 8 | 8 | 8 | 8 | 5000 | 0.79205 | 24 | 0.9296 | 351791.0938 | 11563.2002 | 840 | 14400 | 16800 | 13200 | 56803.1992 | 422.144 | 127750 | 536766.4375 | 1000000 | 6967977
Lamp Aging Equation | 9999 | 82.8481 | 79.2047 | 70.7809 | 73.2445 | 6000 | 0.79073 | 24 | 0.93115 | 352376.9688 | 9636 | 840 | 14400 | 16800 | 13200 | 54876 | 401.12 | 127750 | 535404.0625 | 1001665.375 | 6954495
Sleeve Data | [5 empty] | 7000 | 0.7902 | 24 | 0.93177 | 352612.9062 | 8259.4287 | 840 | 14400 | 16800 | 13200 | 53499.4297 | 386.1028 | 127750 | 534248.4375 | 1002336.0625 | 6942317
Sleeve Life | yrs | 10 | 10 | 10 | 10 | 8000 | 0.78999 | 24 | 0.93202 | 352707.7812 | 7227 | 840 | 14400 | 16800 | 13200 | 52467 | 374.84 | 127750 | 533299.625 | 1002605.8125 | 6932037.5
Sleeve Cost | $ | 350 | 350 | 350 | 350 | 9000 | 0.7899 | 24 | 0.93213 | 352745.9688 | 6424 | 840 | 14400 | 16800 | 13200 | 51664 | 366.08 | 127750 | 532526.0625 | 1002714.25 | 6923545
Sleeve Replacement Time | min | 10 | 10 | 10 | 10 | 10000 | 0.78987 | 24 | 0.93217 | 352761.25 | 5781.6001 | 840 | 14400 | 16800 | 13200 | 51021.6016 | 359.072 | 127750 | 531891.9375 | 1002757.8125 | 6916538.5
Sleeve Cleaning Type (Rinse, Wiper) |  | Wiper | Wiper | Wiper | Wiper | 11000 | 0.78986 | 24 | 0.93218 | 352767.4375 | 5256 | 840 | 14400 | 16800 | 13200 | 50496 | 353.3382 | 127750 | 531366.75 | 1002775.3125 | 6910716.5
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 12000 | 0.78985 | 24 | 0.93219 | 352769.875 | 4818 | 840 | 14400 | 16800 | 13200 | 50058 | 348.56 | 127750 | 530926.4375 | 1002782.3125 | 6905828
Sleeve Cleaning Time/Reactor | min | 0 | 0 | 0 | 0 | 13000 | 0.78985 | 24 | 0.93219 | 352770.9062 | 4447.3848 | 840 | 14400 | 16800 | 13200 | 49687.3828 | 344.5169 | 127750 | 530552.8125 | 1002785.1875 | 6901677
Fouling Factor | % | 95 | 95 | 95 | 95 | 14000 | 0.78985 | 24 | 0.93219 | 352771.3125 | 4129.7144 | 840 | 14400 | 16800 | 13200 | 49369.7148 | 341.0514 | 127750 | 530232.0625 | 1002786.3125 | 6898111.5
[6 empty] | 15000 | 0.78985 | 24 | 0.93219 | 352771.4375 | 3854.3999 | 840 | 14400 | 16800 | 13200 | 49094.3984 | 338.048 | 127750 | 529953.875 | 1002786.8125 | 6895019
Ballast Data | [5 empty] | 16000 | 0.78985 | 24 | 0.93219 | 352771.5 | 3613.5 | 840 | 14400 | 16800 | 13200 | 48853.5 | 335.42 | 127750 | 529710.4375 | 1002786.9375 | 6892312.5
Ballast Life | yrs | 5 | 5 | 5 | 5
Ballast Costs | $ | 6000 | 6000 | 6000 | 6000
Ballast replacement | min | 30 | 30 | 30 | 30
Sensor Data | [5 empty] | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | 3 | 3 | 3 | 3 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | 2100 | 2100 | 2100 | 2100 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 10 | 10 | 10 | 10 | 200 | 0.95056 | 24 | 0.74666 | 282560.25 | 289080 | 840 | 14400 | 16800 | 13200 | 334320 | 3449.6001 | 127750 | 748079.875 | 744622.3125 | 9062064
Sensor cal period | months | 12 | 12 | 12 | 12 | 400 | 0.9094 | 24 | 0.78045 | 295348.9375 | 144540 | 840 | 14400 | 16800 | 13200 | 189780 | 1872.8 | 127750 | 614751.75 | 778323.9375 | 7613372
Sensor calibration cost | $ | 550 | 550 | 550 | 550 | 600 | 0.87513 | 24 | 0.81101 | 306913.5625 | 96360 | 840 | 14400 | 16800 | 13200 | 141600 | 1347.2001 | 127750 | 577610.75 | 808799.75 | 7230899.5
Sensor calibration | min | 5 | 5 | 5 | 5 | 800 | 0.84661 | 24 | 0.83834 | 317255.5312 | 72270 | 840 | 14400 | 16800 | 13200 | 117510 | 1084.4 | 127750 | 563599.9375 | 836053.75 | 7102376
[6 empty] | 1000 | 0.82286 | 24 | 0.86254 | 326412.5938 | 57816 | 840 | 14400 | 16800 | 13200 | 103056 | 926.72 | 127750 | 558145.3125 | 860185.0625 | 7065861
Dose Pacing | Enter if dose pacing responds to the following parameters. |  |  |  |  | 2000 | 0.75201 | 24 | 0.9438 | 357164.3438 | 28908 | 840 | 14400 | 16800 | 13200 | 74148 | 611.36 | 127750 | 559673.6875 | 941224.0625 | 7163893
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling |  |  |  |  | 3000 | 0.72367 | 24 | 0.98075 | 371148.9375 | 19272 | 840 | 14400 | 16800 | 13200 | 64512 | 506.2401 | 127750 | 563917.1875 | 978077.375 | 7247927
| Peak dose will be equal to or greater than the design dose. |  |  |  |  | 4000 | 0.71234 | 24 | 0.99636 | 377053.5 | 14454 | 840 | 14400 | 16800 | 13200 | 59694 | 453.68 | 127750 | 564951.1875 | 993637.4375 | 7274983.5
Peak UV Dose ** | mJ/cm^2 | 35.4819 | 34.4233 | 31.9126 | 32.6566 | 5000 | 0.70781 | 32 | 0.75205 | 379467.9062 | 15417.5996 | 1120 | 19200 | 22400 | 17600 | 75737.6016 | 562.8586 | 127750 | 583518.375 | 1000000.0625 | 7487783.5
Flow (y/n) |  | n | n | n | n | 6000 | 0.706 | 32 | 0.75398 | 380442.2188 | 12848 | 1120 | 19200 | 22400 | 17600 | 73168 | 534.8267 | 127750 | 581895.0625 | 1002567.6875 | 7472302.5
Lamp Age (y/n) |  | n | n | n | n | 7000 | 0.70527 | 32 | 0.75476 | 380833.3125 | 11012.5713 | 1120 | 19200 | 22400 | 17600 | 71332.5703 | 514.8038 | 127750 | 580430.6875 | 1003598.25 | 7457051.5
UVT (y/n) |  | n | n | n | n | 8000 | 0.70498 | 32 | 0.75507 | 380989.9688 | 9636 | 1120 | 19200 | 22400 | 17600 | 69956 | 499.7867 | 127750 | 579195.75 | 1004011.0625 | 7443733.5
Fouling (y/n) |  | n | n | n | n | 9000 | 0.70487 | 32 | 0.75519 | 381052.5938 | 8565.333 | 1120 | 19200 | 22400 | 17600 | 68885.3359 | 488.1067 | 127750 | 578176.0625 | 1004176.1875 | 7432561.5
[6 empty] | 10000 | 0.70482 | 32 | 0.75524 | 381077.6875 | 7708.7998 | 1120 | 19200 | 22400 | 17600 | 68028.7969 | 478.7627 | 127750 | 577335.25 | 1004242.25 | 7423279
WTP INPUTS | [5 empty] | 11000 | 0.7048 | 32 | 0.75526 | 381087.7188 | 7008 | 1120 | 19200 | 22400 | 17600 | 67328 | 471.1176 | 127750 | 576636.8125 | 1004268.75 | 7415540
Labor rate | $/hr | 60 | 60 | 60 | 60 | 12000 | 0.70479 | 32 | 0.75527 | 381091.7188 | 6424 | 1120 | 19200 | 22400 | 17600 | 66744 | 464.7466 | 127750 | 576050.4375 | 1004279.25 | 7409031
Electricity Cost | $/kWhr | 0.15 | 0.15 | 0.15 | 0.15 | 13000 | 0.70479 | 32 | 0.75527 | 381093.3438 | 5929.8462 | 1120 | 19200 | 22400 | 17600 | 66249.8438 | 459.3559 | 127750 | 575552.5625 | 1004283.5 | 7403500
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 14000 | 0.70479 | 32 | 0.75528 | 381094 | 5506.2856 | 1120 | 19200 | 22400 | 17600 | 65826.2891 | 454.7352 | 127750 | 575125 | 1004285.1875 | 7398747.5
Interest rate | % | 4 | 4 | 4 | 4 | 15000 | 0.70479 | 32 | 0.75528 | 381094.25 | 5139.2002 | 1120 | 19200 | 22400 | 17600 | 65459.1992 | 450.7307 | 127750 | 574754.1875 | 1004285.875 | 7394625.5
Period | yrs | 15 | 15 | 15 | 15 | 16000 | 0.70479 | 32 | 0.75528 | 381094.3438 | 4818 | 1120 | 19200 | 22400 | 17600 | 65138 | 447.2267 | 127750 | 574429.5625 | 1004286.125 | 7391016.5
CAPITAL COSTS INPUTS | [5 empty] | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | 1000000 | 1000000 | 1000000 | 1000000 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ |  |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $ |  |  |  |  | 200 | 0.98479 | 24 | 0.7288 | 275802.7188 | 289080 | 840 | 14400 | 16800 | 13200 | 334320 | 3449.6001 | 127750 | 741322.3125 | 743756.875 | 8986065
Inlet/Oultet Piping | [5 empty] | 400 | 0.97005 | 24 | 0.73988 | 279993.125 | 144540 | 840 | 14400 | 16800 | 13200 | 189780 | 1872.8 | 127750 | 599395.9375 | 755057.25 | 7419373.5
Valves | Total $ |  |  |  |  | 600 | 0.95577 | 24 | 0.75093 | 284177.3125 | 96360 | 840 | 14400 | 16800 | 13200 | 141600 | 1347.2001 | 127750 | 554874.5 | 766340.6875 | 6935650
Flowmeters | Total $ |  |  |  |  | 800 | 0.94193 | 24 | 0.76197 | 288353.125 | 72270 | 840 | 14400 | 16800 | 13200 | 117510 | 1084.4 | 127750 | 534697.5 | 777601.625 | 6722575.5
Piping and Appurtences | Total $ |  |  |  |  | 1000 | 0.92852 | 24 | 0.77298 | 292518.625 | 57816 | 840 | 14400 | 16800 | 13200 | 103056 | 926.72 | 127750 | 524251.3438 | 788834.6875 | 6617664
Channels | Total $ |  |  |  |  | 2000 | 0.86742 | 24 | 0.82742 | 313121.2812 | 28908 | 840 | 14400 | 16800 | 13200 | 74148 | 611.36 | 127750 | 515630.6562 | 844393.8125 | 6577375
Power | [5 empty] | 3000 | 0.81521 | 24 | 0.88041 | 333176.5938 | 19272 | 840 | 14400 | 16800 | 13200 | 64512 | 506.2401 | 127750 | 525944.8125 | 898477 | 6746135
Switch gear | Total $ |  |  |  |  | 4000 | 0.77058 | 24 | 0.9314 | 352470.7812 | 14454 | 840 | 14400 | 16800 | 13200 | 59694 | 453.68 | 127750 | 540368.4375 | 950507.625 | 6958533
Transformer | Total $ |  |  |  |  | 5000 | 0.73245 | 24 | 0.9799 | 370823.75 | 11563.2002 | 840 | 14400 | 16800 | 13200 | 56803.1992 | 422.144 | 127750 | 555799.0625 | 1000000 | 7179589
Distribution Panels | Total $ |  |  |  |  | 6000 | 0.69985 | 32 | 0.76915 | 388094.25 | 12848 | 1120 | 19200 | 22400 | 17600 | 73168 | 534.8267 | 127750 | 589547.0625 | 1046573.4375 | 7601386
Generator | Total $ |  |  |  |  | 7000 | 0.67199 | 32 | 0.80103 | 404182.2188 | 11012.5713 | 1120 | 19200 | 22400 | 17600 | 71332.5703 | 514.8038 | 127750 | 603779.5625 | 1089957.75 | 7803012.5
UPS | Total $ |  |  |  |  | 8000 | 0.64819 | 32 | 0.83046 | 419027.6875 | 9636 | 1120 | 19200 | 22400 | 17600 | 69956 | 499.7867 | 127750 | 617233.5 | 1129991.5 | 7992632.5
Misc Electrical | Total $ |  |  |  |  | 9000 | 0.62784 | 32 | 0.85737 | 432607.5625 | 8565.333 | 1120 | 19200 | 22400 | 17600 | 68885.3359 | 488.1067 | 127750 | 629731 | 1166612.375 | 8168205.5
Other | [5 empty] | 10000 | 0.61045 | 32 | 0.88179 | 444930.9688 | 7708.7998 | 1120 | 19200 | 22400 | 17600 | 68028.7969 | 478.7627 | 127750 | 641188.5 | 1199844.875 | 8328827
Yard piping | Total $ |  |  |  |  | 11000 | 0.59559 | 32 | 0.9038 | 456033.4688 | 7008 | 1120 | 19200 | 22400 | 17600 | 67328 | 471.1176 | 127750 | 651582.5625 | 1229785 | 8474332
Chlorine contactor | Total $ |  |  |  |  | 12000 | 0.58289 | 32 | 0.92349 | 465970.9062 | 6424 | 1120 | 19200 | 22400 | 17600 | 66744 | 464.7466 | 127750 | 660929.625 | 1256583.25 | 8605055
Low lift pumps | Total $ |  |  |  |  | 13000 | 0.57203 | 32 | 0.94102 | 474813.5938 | 5929.8462 | 1120 | 19200 | 22400 | 17600 | 66249.8438 | 459.3559 | 127750 | 669272.8125 | 1280429.375 | 8721664
UV Building | [5 empty] | 14000 | 0.56275 | 32 | 0.95653 | 482641.3438 | 5506.2856 | 1120 | 19200 | 22400 | 17600 | 65826.2891 | 454.7352 | 127750 | 676672.375 | 1301538.375 | 8825044
Demolition | Total $ |  |  |  |  | 15000 | 0.55482 | 32 | 0.9702 | 489538.75 | 5139.2002 | 1120 | 19200 | 22400 | 17600 | 65459.1992 | 450.7307 | 127750 | 683198.6875 | 1320138.625 | 8916206
Civil/sitework | Total $ |  |  |  |  | 16000 | 0.54805 | 32 | 0.98219 | 495591.8125 | 4818 | 1120 | 19200 | 22400 | 17600 | 65138 | 447.2267 | 127750 | 688927.0625 | 1336461.875 | 8996220
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 95.039 | 95.039 | 95.039 | 95.039
95% UVT | mJ/cm2 | 66.4797 | 66.4797 | 66.4797 | 66.4797
90% UVT | mJ/cm2 | 41.6914 | 41.6914 | 41.6914 | 41.6914
85% UVT | mJ/cm2 | 28.4989 | 28.4989 | 28.4989 | 28.4989
80% UVT | mJ/cm2 | 20.6256 | 20.6256 | 20.6256 | 20.6256
75% UVT | mJ/cm2 | 15.6092 | 15.6092 | 15.6092 | 15.6092
70% UVT | mJ/cm2 | 12.2768 | 12.2768 | 12.2768 | 12.2768
65% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
|  | 2.3676 | 2.3676 | 2.3676 | 2.3676
|  | 8.2746 | 8.2746 | 8.2746 | 8.2746
|  | 0.67349 | 0.67349 | 0.67349 | 0.67349
|  | 0.93411 | 0.93411 | 0.93411 | 0.93411
Lamp Analysis
Clear

## LAMP AGE LCA TOOL (4)
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 4
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions |  | Amalgam Reactor - Power function model
Units: y = %, x = hrs |  | Power | 0.15
MMF: y=(a*b+c*x^d)/(b+x^d) |  | Interest | 4
EXP: y=a*e^(b*x) |  | Period | 15
LIN: Y = ax+b |  | Dose pacing | None
| 0 | 1 | 2 | 3 | 4 | Simulation - Cost Benefit Analysis for Case 1
Lamp Type | [5 empty] | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Vendor | [5 empty] | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment | [5 empty] | 200 | 1 | 120 | 0.92393 | 52446.5547 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1060268.5 | 612109.75 | 12400585
[6 empty] | 400 | 0.99235 | 120 | 0.93105 | 52850.6211 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 627052.625 | 616825.6875 | 7588639.5
UV SYSTEM SIZING CRITERIA | [5 empty] | 600 | 0.9695 | 120 | 0.953 | 54096.7461 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 483758.75 | 631369.3125 | 6009986.5
[6 empty] | 800 | 0.9536 | 120 | 0.96889 | 54998.6562 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412390.6562 | 641895.625 | 5227014.5
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 1000 | 0.94144 | 120 | 0.98139 | 55708.5781 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 369738.5625 | 650181.1875 | 4761077.5
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 2000 | 0.90468 | 132 | 0.92844 | 57972.7656 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 294739.375 | 676606.8125 | 3953633.25
Average UVT | % | 93 | 93 | 93 | 93 | 3000 | 0.88384 | 132 | 0.95033 | 59339.6562 | 61670.3984 | 1320 | 3960 | 715 | 2530 | 70195.3984 | 7022.3999 | 127750 | 264307.4688 | 692559.9375 | 3631232.75
Design UVT | % | 90 | 90 | 90 | 90 | 4000 | 0.86934 | 132 | 0.96617 | 60328.9805 | 46252.8008 | 1320 | 3960 | 715 | 2530 | 54777.8008 | 6540.6001 | 127750 | 249397.375 | 704106.4375 | 3477003
Design UV Dose | mJ/cm^2 | 28 | 28 | 28 | 28 | 5000 | 0.85826 | 132 | 0.97864 | 61107.7031 | 37002.2383 | 1320 | 3960 | 715 | 2530 | 45527.2383 | 6251.52 | 127750 | 240636.4688 | 713195 | 3388684.5
REACTOR DESIGN INPUTS | [5 empty] | 6000 | 0.84932 | 132 | 0.98895 | 61751.4219 | 30835.1992 | 1320 | 3960 | 715 | 2530 | 39360.1992 | 6058.8003 | 127750 | 234920.4219 | 720707.9375 | 3332644.25
Configuration | [5 empty] | 7000 | 0.84183 | 132 | 0.99775 | 62300.9648 | 26430.1719 | 1320 | 3960 | 715 | 2530 | 34955.1719 | 5921.1431 | 127750 | 230927.2812 | 727121.75 | 3294660.75
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 25.7 | 8000 | 0.83539 | 144 | 0.92165 | 62780.957 | 25228.8008 | 1440 | 4320 | 780 | 2760 | 34528.8008 | 5896.7993 | 127750 | 230956.5625 | 732723.6875 | 3300588.25
Number of Trains |  | 3 | 3 | 3 | 3 | 9000 | 0.82975 | 144 | 0.92791 | 63207.4062 | 22425.5996 | 1440 | 4320 | 780 | 2760 | 31725.5996 | 5809.1997 | 127750 | 228492.2031 | 737700.875 | 3278165.75
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 10000 | 0.82474 | 144 | 0.93355 | 63591.332 | 20183.0391 | 1440 | 4320 | 780 | 2760 | 29483.0391 | 5739.1196 | 127750 | 226563.4844 | 742181.75 | 3261202.25
Banks/Reactor |  | 8 | 8 | 8 | 8 | 11000 | 0.82024 | 144 | 0.93868 | 63940.6406 | 18348.2188 | 1440 | 4320 | 780 | 2760 | 27648.2188 | 5681.7812 | 127750 | 225020.6406 | 746258.5625 | 3248125.25
Lamps/Bank |  | 12 | 12 | 12 | 12 | 12000 | 0.81615 | 144 | 0.94338 | 64261.2148 | 16819.1992 | 1440 | 4320 | 780 | 2760 | 26119.1992 | 5633.9995 | 127750 | 223764.4062 | 750000 | 3237899.25
Lamps/Ballast |  | 2 | 2 | 2 | 2 | 13000 | 0.8124 | 144 | 0.94773 | 64557.5312 | 15525.415 | 1440 | 4320 | 780 | 2760 | 24825.4141 | 5593.5688 | 127750 | 222726.5156 | 753458.3125 | 3229818
Sensors/bank |  | 1 | 1 | 1 | 1 | 14000 | 0.80895 | 144 | 0.95178 | 64833.0898 | 14416.457 | 1440 | 4320 | 780 | 2760 | 23716.457 | 5558.9141 | 127750 | 221858.4688 | 756674.4375 | 3223382.75
Redundancy | [5 empty] | 15000 | 0.80575 | 144 | 0.95556 | 65090.6953 | 13455.3604 | 1440 | 4320 | 780 | 2760 | 22755.3594 | 5528.8799 | 127750 | 221124.9375 | 759680.9375 | 3218233.5
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 16000 | 0.80276 | 144 | 0.95911 | 65332.5938 | 12614.4004 | 1440 | 4320 | 780 | 2760 | 21914.4004 | 5502.5996 | 127750 | 220499.5938 | 762504.125 | 3214104
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 0.36 | 0.36 | 0.36 | 0.36
Lamp Life | hrs | 12000 | 12000 | 12000 | 12000 | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | 81.6146 | 78.1664 | 73.1033 | 56.0961 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | 160 | 160 | 160 | 160 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 5 | 5 | 5 | 5 | 200 | 1 | 120 | 0.91528 | 51955.6406 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1059777.625 | 586248.25 | 12369266
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | 400 | 0.99074 | 120 | 0.92384 | 52441.3711 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 626643.375 | 591729.125 | 7558993
Coefficient A |  | 0.010403 | 0.011173 | 0.0096952 | 0.015959 | 600 | 0.96313 | 120 | 0.95031 | 53944.3047 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 483606.3125 | 608687.625 | 5985610
Coefficient B |  | -0.057476 | -0.069688 | -0.088634 | -0.16355 | 800 | 0.94402 | 120 | 0.96956 | 55036.6992 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412428.6875 | 621013.8125 | 5206555.5
Coefficient C |  | 0 | 0 | 0 | 0 | 1000 | 0.92945 | 120 | 0.98475 | 55899.2383 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 369929.25 | 630746.375 | 4743763
Coefficient D |  | 0 | 0 | 0 | 0 | 2000 | 0.88562 | 132 | 0.93953 | 58665.6953 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 295432.3125 | 661962.0625 | 3946693
Coefficient E |  | 0 | 0 | 0 | 0 | 3000 | 0.86095 | 132 | 0.96646 | 60347.0117 | 61670.3984 | 1320 | 3960 | 715 | 2530 | 70195.3984 | 7022.3999 | 127750 | 265314.8125 | 680933.4375 | 3630806.25
Coefficient F |  | 0 | 0 | 0 | 0 | 4000 | 0.84386 | 132 | 0.98603 | 61569.0625 | 46252.8008 | 1320 | 3960 | 715 | 2530 | 54777.8008 | 6540.6001 | 127750 | 250637.4688 | 694722.5625 | 3481407
Lamp Power | kW | 0 | 0 | 0 | 0 | 5000 | 0.83084 | 144 | 0.91803 | 62533.9805 | 40366.0781 | 1440 | 4320 | 780 | 2760 | 49666.0781 | 6369.8398 | 127750 | 246319.9062 | 705610.3125 | 3444290.5
Lamp Aging Equation | 9999 | 81.6146 | 78.1664 | 73.1033 | 56.0961 | 6000 | 0.82035 | 144 | 0.92977 | 63333.582 | 33638.3984 | 1440 | 4320 | 780 | 2760 | 42938.3984 | 6159.5996 | 127750 | 240181.5781 | 714632.8125 | 3385064.5
Sleeve Data | [5 empty] | 7000 | 0.81158 | 144 | 0.93981 | 64017.6133 | 28832.9141 | 1440 | 4320 | 780 | 2760 | 38132.9141 | 6009.4287 | 127750 | 235909.9531 | 722351.125 | 3345289.25
Sleeve Life | yrs | 10 | 10 | 10 | 10 | 8000 | 0.80407 | 144 | 0.94859 | 64616.1172 | 25228.8008 | 1440 | 4320 | 780 | 2760 | 34528.8008 | 5896.7993 | 127750 | 232791.7188 | 729104.4375 | 3317373
Sleeve Cost | $ | 100 | 100 | 100 | 100 | 9000 | 0.79749 | 144 | 0.95641 | 65148.6797 | 22425.5996 | 1440 | 4320 | 780 | 2760 | 31725.5996 | 5809.1997 | 127750 | 230433.4844 | 735113.625 | 3297162.25
Sleeve Replacement Time | min | 5 | 5 | 5 | 5 | 10000 | 0.79166 | 144 | 0.96346 | 65628.7891 | 20183.0391 | 1440 | 4320 | 780 | 2760 | 29483.0391 | 5739.1196 | 127750 | 228600.9531 | 740531.0625 | 3282205
Sleeve Cleaning Type (Rinse, Wiper) |  | Rinse | Rinse | Rinse | Rinse | 11000 | 0.78642 | 144 | 0.96988 | 66066.1484 | 18348.2188 | 1440 | 4320 | 780 | 2760 | 27648.2188 | 5681.7812 | 127750 | 227146.1562 | 745466 | 3270965
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 12000 | 0.78166 | 144 | 0.97578 | 66467.9688 | 16819.1992 | 1440 | 4320 | 780 | 2760 | 26119.1992 | 5633.9995 | 127750 | 225971.1719 | 750000 | 3262435
Sleeve Cleaning Time/Reactor | min | 180 | 180 | 180 | 180 | 13000 | 0.77732 | 144 | 0.98124 | 66839.7656 | 15525.415 | 1440 | 4320 | 780 | 2760 | 24825.4141 | 5593.5688 | 127750 | 225008.75 | 754195.25 | 3255929.75
Fouling Factor | % | 85 | 85 | 85 | 85 | 14000 | 0.77331 | 144 | 0.98632 | 67185.8438 | 14416.457 | 1440 | 4320 | 780 | 2760 | 23716.457 | 5558.9141 | 127750 | 224211.2188 | 758100.3125 | 3250967.5
[6 empty] | 15000 | 0.7696 | 144 | 0.99107 | 67509.6562 | 13455.3604 | 1440 | 4320 | 780 | 2760 | 22755.3594 | 5528.8799 | 127750 | 223543.8906 | 761754.0625 | 3247201.5
Ballast Data | [5 empty] | 16000 | 0.76615 | 144 | 0.99554 | 67813.9688 | 12614.4004 | 1440 | 4320 | 780 | 2760 | 21914.4004 | 5502.5996 | 127750 | 222980.9688 | 765187.8125 | 3244376.5
Ballast Life | yrs | 5 | 5 | 5 | 5
Ballast Costs | $ | 300 | 300 | 300 | 300
Ballast replacement | min | 1 | 1 | 1 | 1
Sensor Data | [5 empty] | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | 10 | 10 | 10 | 10 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | 650 | 650 | 650 | 650 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 10 | 10 | 10 | 10 | 200 | 1 | 120 | 0.90202 | 51203.1719 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1059025.125 | 548274.8125 | 12322926
Sensor cal period | months | 12 | 12 | 12 | 12 | 400 | 0.98823 | 120 | 0.91276 | 51812.7812 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 626014.75 | 554802.4375 | 7515077
Sensor calibration cost | $ | 230 | 230 | 230 | 230 | 600 | 0.95335 | 120 | 0.94616 | 53708.6836 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 483370.6875 | 575103.4375 | 5949406
Sensor calibration | min | 5 | 5 | 5 | 5 | 800 | 0.92935 | 120 | 0.9706 | 55095.7773 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412487.7812 | 589956.25 | 5176155
[6 empty] | 1000 | 0.91115 | 120 | 0.98999 | 56196.3164 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 370226.3125 | 601740.5625 | 4718060
Dose Pacing | Enter if dose pacing responds to the following parameters. |  |  |  |  | 2000 | 0.85686 | 132 | 0.95701 | 59757.0664 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 296523.6562 | 639868.5 | 3936733.25
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling |  |  |  |  | 3000 | 0.82661 | 132 | 0.99203 | 61943.668 | 61670.3984 | 1320 | 3960 | 715 | 2530 | 70195.3984 | 7022.3999 | 127750 | 266911.4688 | 663282.25 | 3630907.25
| Peak dose will be equal to or greater than the design dose. |  |  |  |  | 4000 | 0.8058 | 144 | 0.93285 | 63543.4375 | 50457.6016 | 1440 | 4320 | 780 | 2760 | 59757.6016 | 6685.1997 | 127750 | 257736.2344 | 680412.3125 | 3546023.5
Peak UV Dose ** | mJ/cm^2 | 39.5738 | 38.26 | 36.3076 | 29.5153 | 5000 | 0.79002 | 144 | 0.95148 | 64812.7227 | 40366.0781 | 1440 | 4320 | 780 | 2760 | 49666.0781 | 6369.8398 | 127750 | 248598.6406 | 694003.5625 | 3458019.5
Flow (y/n) |  | n | n | n | n | 6000 | 0.77735 | 144 | 0.96698 | 65868.5859 | 33638.3984 | 1440 | 4320 | 780 | 2760 | 42938.3984 | 6159.5996 | 127750 | 242716.5781 | 705309.625 | 3403926.5
Lamp Age (y/n) |  | n | n | n | n | 7000 | 0.7668 | 144 | 0.98028 | 66774.7188 | 28832.9141 | 1440 | 4320 | 780 | 2760 | 38132.9141 | 6009.4287 | 127750 | 238667.0625 | 715012.375 | 3368605.25
UVT (y/n) |  | n | n | n | n | 8000 | 0.75778 | 144 | 0.99195 | 67569.7266 | 25228.8008 | 1440 | 4320 | 780 | 2760 | 34528.8008 | 5896.7993 | 127750 | 235745.3281 | 723525.125 | 3344633
Fouling (y/n) |  | n | n | n | n | 9000 | 0.74991 | 156 | 0.92526 | 68278.8203 | 24294.4004 | 1560 | 4680 | 845 | 2990 | 34369.3984 | 5880.8003 | 127750 | 236279.0156 | 731118 | 3358159.5
[6 empty] | 10000 | 0.74294 | 156 | 0.93394 | 68919.4297 | 21864.9609 | 1560 | 4680 | 845 | 2990 | 31939.9609 | 5804.8804 | 127750 | 234414.2656 | 737977.5 | 3344286
WTP INPUTS | [5 empty] | 11000 | 0.73669 | 156 | 0.94186 | 69504.1094 | 19877.2363 | 1560 | 4680 | 845 | 2990 | 29952.2363 | 5742.7637 | 127750 | 232949.1094 | 744238.125 | 3334256.5
Labor rate | $/hr | 60 | 60 | 60 | 60 | 12000 | 0.73103 | 156 | 0.94916 | 70042.2031 | 18220.8008 | 1560 | 4680 | 845 | 2990 | 28295.8008 | 5691.0005 | 127750 | 231779 | 750000 | 3327008.75
Electricity Cost | $/kWhr | 0.15 | 0.15 | 0.15 | 0.15 | 13000 | 0.72587 | 156 | 0.95591 | 70540.8828 | 16819.1992 | 1560 | 4680 | 845 | 2990 | 26894.1992 | 5647.2002 | 127750 | 230832.2812 | 755339.8125 | 3321822.5
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 14000 | 0.72111 | 156 | 0.96221 | 71005.7578 | 15617.8281 | 1560 | 4680 | 845 | 2990 | 25692.8281 | 5609.6577 | 127750 | 230058.25 | 760317.5625 | 3318194.25
Interest rate | % | 4 | 4 | 4 | 4 | 15000 | 0.71672 | 156 | 0.96811 | 71441.2969 | 14576.6396 | 1560 | 4680 | 845 | 2990 | 24651.6406 | 5577.1201 | 127750 | 229420.0625 | 764981.1875 | 3315762.25
Period | yrs | 15 | 15 | 15 | 15 | 16000 | 0.71263 | 156 | 0.97367 | 71851.1328 | 13665.5996 | 1560 | 4680 | 845 | 2990 | 23740.5996 | 5548.6499 | 127750 | 228890.375 | 769369.6875 | 3314261.5
CAPITAL COSTS INPUTS | [5 empty] | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | 750000 | 750000 | 750000 | 750000 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ |  |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $ |  |  |  |  | 200 | 1 | 108 | 0.94607 | 48332.8867 | 756864 | 1080 | 3240 | 585 | 2070 | 763839 | 28720.7988 | 127750 | 968642.6875 | 420720.75 | 11190465
Inlet/Oultet Piping | [5 empty] | 400 | 0.9784 | 108 | 0.96695 | 49400.0391 | 378432 | 1080 | 3240 | 585 | 2070 | 385407 | 16894.7988 | 127750 | 579451.8125 | 430009.9375 | 6872579.5
Valves | Total $ |  |  |  |  | 600 | 0.91562 | 120 | 0.92992 | 52787.0039 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 482449 | 459492.2188 | 5823547
Flowmeters | Total $ |  |  |  |  | 800 | 0.87354 | 120 | 0.97472 | 55330 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412722 | 481628.1562 | 5070431
Piping and Appurtences | Total $ |  |  |  |  | 1000 | 0.84223 | 132 | 0.91905 | 57386.5703 | 185011.2031 | 1320 | 3960 | 715 | 2530 | 193536.2031 | 10876.7998 | 127750 | 389549.5625 | 499529.875 | 4830693
Channels | Total $ |  |  |  |  | 2000 | 0.75197 | 144 | 0.94359 | 64275.2344 | 100915.2031 | 1440 | 4320 | 780 | 2760 | 110215.2031 | 8262.001 | 127750 | 310502.4375 | 559493.25 | 4011779.5
Power | [5 empty] | 3000 | 0.70372 | 156 | 0.93072 | 68682.0625 | 72883.2031 | 1560 | 4680 | 845 | 2990 | 82958.2031 | 7399.2002 | 127750 | 286789.4688 | 597853.125 | 3786489.5
Switch gear | Total $ |  |  |  |  | 4000 | 0.67138 | 156 | 0.97556 | 71990.8047 | 54662.3984 | 1560 | 4680 | 845 | 2990 | 64737.3984 | 6829.8003 | 127750 | 271308 | 626654.5625 | 3643162
Transformer | Total $ |  |  |  |  | 5000 | 0.64732 | 168 | 0.93955 | 74666.6406 | 47093.7617 | 1680 | 5040 | 910 | 3220 | 57943.7617 | 6606.4795 | 127750 | 266966.875 | 649946.8125 | 3618188
Distribution Panels | Total $ |  |  |  |  | 6000 | 0.6283 | 168 | 0.96799 | 76926.6172 | 39244.8008 | 1680 | 5040 | 910 | 3220 | 50094.8008 | 6361.1992 | 127750 | 261132.625 | 669619.125 | 3572992.75
Generator | Total $ |  |  |  |  | 7000 | 0.61266 | 168 | 0.9927 | 78890.7031 | 33638.3984 | 1680 | 5040 | 910 | 3220 | 44488.3984 | 6185.9995 | 127750 | 257315.0938 | 686715.75 | 3547644.5
UPS | Total $ |  |  |  |  | 8000 | 0.59942 | 180 | 0.94698 | 80632.5391 | 31536 | 1800 | 5400 | 975 | 3450 | 43161 | 6133.5005 | 127750 | 257677.0469 | 701877.875 | 3566831
Misc Electrical | Total $ |  |  |  |  | 9000 | 0.58799 | 180 | 0.9654 | 82200.8516 | 28032 | 1800 | 5400 | 975 | 3450 | 39657 | 6024 | 127750 | 255631.8438 | 715529.5 | 3557743.25
Other | [5 empty] | 10000 | 0.57794 | 180 | 0.98218 | 83629.5859 | 25228.8008 | 1800 | 5400 | 975 | 3450 | 36853.8008 | 5936.4004 | 127750 | 254169.7812 | 727966.0625 | 3553924
Yard piping | Total $ |  |  |  |  | 11000 | 0.569 | 180 | 0.99761 | 84943.4219 | 22935.2734 | 1800 | 5400 | 975 | 3450 | 34560.2734 | 5864.7275 | 127750 | 253118.4219 | 739402.5625 | 3553671.25
Chlorine contactor | Total $ |  |  |  |  | 12000 | 0.56096 | 192 | 0.94866 | 86160.8594 | 22425.5996 | 1920 | 5760 | 1040 | 3680 | 34825.6016 | 5862.0005 | 127750 | 254598.4688 | 749999.9375 | 3580724.25
Low lift pumps | Total $ |  |  |  |  | 13000 | 0.55367 | 192 | 0.96116 | 87296.2031 | 20700.5547 | 1920 | 5760 | 1040 | 3680 | 33100.5547 | 5808.0928 | 127750 | 253954.8438 | 759882.6875 | 3583451
UV Building | [5 empty] | 14000 | 0.547 | 192 | 0.97288 | 88360.7031 | 19221.9434 | 1920 | 5760 | 1040 | 3680 | 31621.9434 | 5761.8857 | 127750 | 253494.5312 | 769148.8125 | 3587599.25
Demolition | Total $ |  |  |  |  | 15000 | 0.54086 | 192 | 0.98392 | 89363.3984 | 17940.4805 | 1920 | 5760 | 1040 | 3680 | 30340.4805 | 5721.8403 | 127750 | 253175.7188 | 777876.875 | 3592782.5
Civil/sitework | Total $ |  |  |  |  | 16000 | 0.53518 | 192 | 0.99436 | 90311.6328 | 16819.1992 | 1920 | 5760 | 1040 | 3680 | 29219.1992 | 5686.8003 | 127750 | 252967.625 | 786131 | 3598723
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 131.6744 | 131.6744 | 131.6744 | 131.6744
95% UVT | mJ/cm2 | 88.4972 | 88.4972 | 88.4972 | 88.4972
90% UVT | mJ/cm2 | 52.6773 | 52.6773 | 52.6773 | 52.6773
85% UVT | mJ/cm2 | 34.5086 | 34.5086 | 34.5086 | 34.5086
80% UVT | mJ/cm2 | 24.0881 | 24.0881 | 24.0881 | 24.0881
75% UVT | mJ/cm2 | 17.6701 | 17.6701 | 17.6701 | 17.6701
70% UVT | mJ/cm2 | 13.5294 | 13.5294 | 13.5294 | 13.5294
65% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
|  | 2.4987 | 2.4987 | 2.4987 | 2.4987
|  | 9.2 | 9.2 | 9.2 | 9.2
|  | 0.78215 | 0.78215 | 0.78215 | 0.78215
|  | 0.94868 | 0.94868 | 0.94868 | 0.94868
Lamp Analysis
Clear

## LAMP AGE LCA TOOL (5)
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 4
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions |  | Amalgam Reactor - Power function model
Units: y = %, x = hrs |  | Power | 0.15
MMF: y=(a*b+c*x^d)/(b+x^d) |  | Interest | 4
EXP: y=a*e^(b*x) |  | Period | 15
LIN: Y = ax+b |  | Dose pacing | None
| 0 | 1 | 2 | 3 | 4 | Simulation - Cost Benefit Analysis for Case 1
Lamp Type | [5 empty] | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Vendor | [5 empty] | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment | [5 empty] | 200 | 1 | 120 | 0.92382 | 52440.668 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1060262.625 | 611794.6875 | 12400205
[6 empty] | 400 | 0.99234 | 120 | 0.93096 | 52845.7227 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 627047.75 | 616520.125 | 7588280
UV SYSTEM SIZING CRITERIA | [5 empty] | 600 | 0.96942 | 120 | 0.95297 | 54094.9219 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 483756.9375 | 631093.8125 | 6009691
[6 empty] | 800 | 0.95348 | 120 | 0.96889 | 54999.1094 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412391.125 | 641642.4375 | 5226766.5
Design Flow | mgd | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 1000 | 0.9413 | 120 | 0.98143 | 55710.8477 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 369740.8438 | 649945.875 | 4760867.5
Average Flow | mgd | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 2000 | 0.90445 | 132 | 0.92857 | 57980.9844 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 294747.5938 | 676430.25 | 3953548.25
Average UVT | % | 93 | 93 | 93 | 93 | 3000 | 0.88356 | 132 | 0.95052 | 59351.5703 | 61670.3984 | 1320 | 3960 | 715 | 2530 | 70195.3984 | 7022.3999 | 127750 | 264319.375 | 692420.0625 | 3631225.25
Design UVT | % | 90 | 90 | 90 | 90 | 4000 | 0.86903 | 132 | 0.96641 | 60343.6211 | 46252.8008 | 1320 | 3960 | 715 | 2530 | 54777.8008 | 6540.6001 | 127750 | 249412.0156 | 703993.75 | 3477053
Design UV Dose | mJ/cm^2 | 28 | 28 | 28 | 28 | 5000 | 0.85793 | 132 | 0.97891 | 61124.5234 | 37002.2383 | 1320 | 3960 | 715 | 2530 | 45527.2383 | 6251.52 | 127750 | 240653.2812 | 713104.0625 | 3388780.5
REACTOR DESIGN INPUTS | [5 empty] | 6000 | 0.84897 | 132 | 0.98925 | 61770.0586 | 30835.1992 | 1320 | 3960 | 715 | 2530 | 39360.1992 | 6058.8003 | 127750 | 234939.0625 | 720635.1875 | 3332778.75
Configuration | [5 empty] | 7000 | 0.84146 | 132 | 0.99808 | 62321.1719 | 26430.1719 | 1320 | 3960 | 715 | 2530 | 34955.1719 | 5921.1431 | 127750 | 230947.4844 | 727064.6875 | 3294828.25
Max. Flow per reactor | mgd | 25.7 | 25.7 | 25.7 | 25.7 | 8000 | 0.83501 | 144 | 0.92197 | 62802.5391 | 25228.8008 | 1440 | 4320 | 780 | 2760 | 34528.8008 | 5896.7993 | 127750 | 230978.1406 | 732680.5 | 3300785
Number of Trains |  | 3 | 3 | 3 | 3 | 9000 | 0.82936 | 144 | 0.92825 | 63230.2148 | 22425.5996 | 1440 | 4320 | 780 | 2760 | 31725.5996 | 5809.1997 | 127750 | 228515.0156 | 737669.9375 | 3278388.25
Number of Reactors/Train |  | 1 | 1 | 1 | 1 | 10000 | 0.82434 | 144 | 0.9339 | 63615.2578 | 20183.0391 | 1440 | 4320 | 780 | 2760 | 29483.0391 | 5739.1196 | 127750 | 226587.4219 | 742162 | 3261448.75
Banks/Reactor |  | 8 | 8 | 8 | 8 | 11000 | 0.81983 | 144 | 0.93904 | 63965.5859 | 18348.2188 | 1440 | 4320 | 780 | 2760 | 27648.2188 | 5681.7812 | 127750 | 225045.5938 | 746249.125 | 3248393.25
Lamps/Bank |  | 12 | 12 | 12 | 12 | 12000 | 0.81573 | 144 | 0.94376 | 64287.0977 | 16819.1992 | 1440 | 4320 | 780 | 2760 | 26119.1992 | 5633.9995 | 127750 | 223790.2969 | 750000 | 3238187.25
Lamps/Ballast |  | 2 | 2 | 2 | 2 | 13000 | 0.81197 | 144 | 0.94813 | 64584.2852 | 15525.415 | 1440 | 4320 | 780 | 2760 | 24825.4141 | 5593.5688 | 127750 | 222753.2656 | 753467.125 | 3230124.25
Sensors/bank |  | 1 | 1 | 1 | 1 | 14000 | 0.80851 | 144 | 0.95218 | 64860.6641 | 14416.457 | 1440 | 4320 | 780 | 2760 | 23716.457 | 5558.9141 | 127750 | 221886.0312 | 756691.5 | 3223706.25
Redundancy | [5 empty] | 15000 | 0.8053 | 144 | 0.95598 | 65119.0312 | 13455.3604 | 1440 | 4320 | 780 | 2760 | 22755.3594 | 5528.8799 | 127750 | 221153.2656 | 759705.6875 | 3218573.25
No. of Redundant Trains |  | 1 | 1 | 1 | 1 | 16000 | 0.80232 | 144 | 0.95954 | 65361.6445 | 12614.4004 | 1440 | 4320 | 780 | 2760 | 21914.4004 | 5502.5996 | 127750 | 220528.6406 | 762536.125 | 3214459
No. of Redundant Reactors per train |  | 0 | 0 | 0 | 0
Lamp Data
Lamp 100% Power | kW | 0.36 | 0.36 | 0.36 | 0.36
Lamp Life | hrs | 12000 | 12000 | 12000 | 12000 | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | 81.5726 | 78.5221 | 65.0142 | 74.2206 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | 160 | 160 | 160 | 160 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 5 | 5 | 5 | 5 | 200 | 1 | 120 | 0.91618 | 52007.0547 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1059829 | 588916.0625 | 12372505
Fit Type (MMF, EXP, LIN, CUSTOM) |  | CUSTOM | CUSTOM | CUSTOM | CUSTOM | 400 | 0.99091 | 120 | 0.92459 | 52484.2734 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 626686.25 | 594319.9375 | 7562060.5
Coefficient A |  | 0.0054999 | 0.0056948 | 0.0059412 | 0.0048732 | 600 | 0.9638 | 120 | 0.95059 | 53960.3203 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 483622.3125 | 611034.375 | 5988134.5
Coefficient B |  | -0.057622 | -0.068404 | -0.12181 | -0.084343 | 800 | 0.94502 | 120 | 0.96949 | 55032.6953 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412424.6875 | 623177.6875 | 5208675
Coefficient C |  | 0 | 0 | 0 | 0 | 1000 | 0.93071 | 120 | 0.9844 | 55879.1523 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 369909.1562 | 632762.8125 | 4745556
Coefficient D |  | 0 | 0 | 0 | 0 | 2000 | 0.88761 | 132 | 0.93836 | 58592.4297 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 295359.0312 | 663487.3125 | 3947403.5
Coefficient E |  | 0 | 0 | 0 | 0 | 3000 | 0.86333 | 132 | 0.96475 | 60240.2617 | 61670.3984 | 1320 | 3960 | 715 | 2530 | 70195.3984 | 7022.3999 | 127750 | 265208.0625 | 682147 | 3630833
Coefficient F |  | 0 | 0 | 0 | 0 | 4000 | 0.8465 | 132 | 0.98392 | 61437.4492 | 46252.8008 | 1320 | 3960 | 715 | 2530 | 54777.8008 | 6540.6001 | 127750 | 250505.8438 | 695703.625 | 3480924.5
Lamp Power | kW | 0 | 0 | 0 | 0 | 5000 | 0.83368 | 132 | 0.99906 | 62382.4141 | 37002.2383 | 1320 | 3960 | 715 | 2530 | 45527.2383 | 6251.52 | 127750 | 241911.1719 | 706404.25 | 3396066.25
Lamp Aging Equation | 9999 | 81.5726 | 78.5221 | 65.0142 | 74.2206 | 6000 | 0.82335 | 144 | 0.9273 | 63165.2891 | 33638.3984 | 1440 | 4320 | 780 | 2760 | 42938.3984 | 6159.5996 | 127750 | 240013.2812 | 715269.375 | 3383830
Sleeve Data | [5 empty] | 7000 | 0.81471 | 144 | 0.93713 | 63834.8672 | 28832.9141 | 1440 | 4320 | 780 | 2760 | 38132.9141 | 6009.4287 | 127750 | 235727.2031 | 722851.4375 | 3343757.75
Sleeve Life | yrs | 10 | 10 | 10 | 10 | 8000 | 0.8073 | 144 | 0.94572 | 64420.6016 | 25228.8008 | 1440 | 4320 | 780 | 2760 | 34528.8008 | 5896.7993 | 127750 | 232596.2031 | 729484.25 | 3315579
Sleeve Cost | $ | 100 | 100 | 100 | 100 | 9000 | 0.80083 | 144 | 0.95337 | 64941.7305 | 22425.5996 | 1440 | 4320 | 780 | 2760 | 31725.5996 | 5809.1997 | 127750 | 230226.5312 | 735385.3125 | 3295133
Sleeve Replacement Time | min | 5 | 5 | 5 | 5 | 10000 | 0.79508 | 144 | 0.96027 | 65411.4609 | 20183.0391 | 1440 | 4320 | 780 | 2760 | 29483.0391 | 5739.1196 | 127750 | 228383.625 | 740704.5 | 3279962
Sleeve Cleaning Type (Rinse, Wiper) |  | Rinse | Rinse | Rinse | Rinse | 11000 | 0.78991 | 144 | 0.96655 | 65839.3125 | 18348.2188 | 1440 | 4320 | 780 | 2760 | 27648.2188 | 5681.7812 | 127750 | 226919.3125 | 745549.3125 | 3268526
Sleeve Cleaning Period | weeks | 4 | 4 | 4 | 4 | 12000 | 0.78522 | 144 | 0.97232 | 66232.3516 | 16819.1992 | 1440 | 4320 | 780 | 2760 | 26119.1992 | 5633.9995 | 127750 | 225735.5469 | 750000 | 3259815.25
Sleeve Cleaning Time/Reactor | min | 180 | 180 | 180 | 180 | 13000 | 0.78093 | 144 | 0.97766 | 66595.9844 | 15525.415 | 1440 | 4320 | 780 | 2760 | 24825.4141 | 5593.5688 | 127750 | 224764.9688 | 754117.6875 | 3253141.75
Fouling Factor | % | 85 | 85 | 85 | 85 | 14000 | 0.77699 | 144 | 0.98263 | 66934.4297 | 14416.457 | 1440 | 4320 | 780 | 2760 | 23716.457 | 5558.9141 | 127750 | 223959.7969 | 757950.25 | 3248022
[6 empty] | 15000 | 0.77333 | 144 | 0.98728 | 67251.0703 | 13455.3604 | 1440 | 4320 | 780 | 2760 | 22755.3594 | 5528.8799 | 127750 | 223285.3125 | 761535.8125 | 3244108.5
Ballast Data | [5 empty] | 16000 | 0.76992 | 144 | 0.99164 | 67548.6172 | 12614.4004 | 1440 | 4320 | 780 | 2760 | 21914.4004 | 5502.5996 | 127750 | 222715.625 | 764905.1875 | 3241143.75
Ballast Life | yrs | 5 | 5 | 5 | 5
Ballast Costs | $ | 300 | 300 | 300 | 300
Ballast replacement | min | 1 | 1 | 1 | 1
Sensor Data | [5 empty] | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | 10 | 10 | 10 | 10 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | 650 | 650 | 650 | 650 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 10 | 10 | 10 | 10 | 200 | 1 | 108 | 0.97697 | 49911.6406 | 756864 | 1080 | 3240 | 585 | 2070 | 763839 | 28720.7988 | 127750 | 970221.4375 | 487606.8125 | 11274904
Sensor cal period | months | 12 | 12 | 12 | 12 | 400 | 0.98387 | 108 | 0.99299 | 50730.1172 | 378432 | 1080 | 3240 | 585 | 2070 | 385407 | 16894.7988 | 127750 | 580781.9375 | 495602.8125 | 6952961.5
Sensor calibration cost | $ | 230 | 230 | 230 | 230 | 600 | 0.93645 | 120 | 0.93894 | 53298.5547 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 482960.5625 | 520694.9375 | 5890437.5
Sensor calibration | min | 5 | 5 | 5 | 5 | 800 | 0.90421 | 120 | 0.97242 | 55199.3789 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412591.375 | 539264.8125 | 5126615.5
[6 empty] | 1000 | 0.87996 | 120 | 0.99922 | 56720.3242 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 370750.3125 | 554123.5625 | 4676269
Dose Pacing | Enter if dose pacing responds to the following parameters. |  |  |  |  | 2000 | 0.80871 | 132 | 0.98841 | 61717.3242 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 298483.9375 | 602941.25 | 3921601.25
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling |  |  |  |  | 3000 | 0.76974 | 144 | 0.95191 | 64842.0391 | 67276.7969 | 1440 | 4320 | 780 | 2760 | 76576.7969 | 7210.7998 | 127750 | 276379.625 | 633467.875 | 3706363.5
| Peak dose will be equal to or greater than the design dose. |  |  |  |  | 4000 | 0.74324 | 144 | 0.98586 | 67154.5469 | 50457.6016 | 1440 | 4320 | 780 | 2760 | 59757.6016 | 6685.1997 | 127750 | 261347.3438 | 656059.625 | 3561820.5
Peak UV Dose ** | mJ/cm^2 | 39.5579 | 38.3961 | 33.1256 | 36.7409 | 5000 | 0.72331 | 156 | 0.9351 | 69004.9062 | 43729.9219 | 1560 | 4680 | 845 | 2990 | 53804.9219 | 6488.1602 | 127750 | 257047.9844 | 674136.5625 | 3532095.5
Flow (y/n) |  | n | n | n | n | 6000 | 0.70742 | 156 | 0.9561 | 70554.5469 | 36441.6016 | 1560 | 4680 | 845 | 2990 | 46516.6016 | 6260.4004 | 127750 | 251081.5469 | 689275.625 | 3480897.5
Lamp Age (y/n) |  | n | n | n | n | 7000 | 0.69426 | 156 | 0.97422 | 71891.8672 | 31235.6562 | 1560 | 4680 | 845 | 2990 | 41310.6562 | 6097.7148 | 127750 | 247050.2344 | 702340.4375 | 3449140.5
UVT (y/n) |  | n | n | n | n | 8000 | 0.68306 | 156 | 0.9902 | 73070.7734 | 27331.1992 | 1560 | 4680 | 845 | 2990 | 37406.1992 | 5975.7007 | 127750 | 244202.6719 | 713857.6875 | 3428997.5
Fouling (y/n) |  | n | n | n | n | 9000 | 0.67333 | 168 | 0.93275 | 74126.6875 | 26163.1992 | 1680 | 5040 | 910 | 3220 | 37013.1992 | 5952.3994 | 127750 | 244842.2812 | 724173.25 | 3446424.5
[6 empty] | 10000 | 0.66474 | 168 | 0.9448 | 75084.1562 | 23546.8809 | 1680 | 5040 | 910 | 3220 | 34396.8828 | 5870.6396 | 127750 | 243101.6719 | 733527.125 | 3436425.75
WTP INPUTS | [5 empty] | 11000 | 0.65707 | 168 | 0.95584 | 75960.9375 | 21406.2539 | 1680 | 5040 | 910 | 3220 | 32256.2539 | 5803.7446 | 127750 | 241770.9375 | 742092.8125 | 3430195.75
Labor rate | $/hr | 60 | 60 | 60 | 60 | 12000 | 0.65014 | 168 | 0.96602 | 76770.3125 | 19622.4004 | 1680 | 5040 | 910 | 3220 | 30472.4004 | 5747.9995 | 127750 | 240740.7188 | 749999.9375 | 3426648.5
Electricity Cost | $/kWhr | 0.15 | 0.15 | 0.15 | 0.15 | 13000 | 0.64383 | 168 | 0.97548 | 77522.4766 | 18112.9844 | 1680 | 5040 | 910 | 3220 | 28962.9844 | 5700.8306 | 127750 | 239936.2969 | 757348.1875 | 3425052.75
Patent fees | $/1000 gal | 0.015 | 0.015 | 0.015 | 0.015 | 14000 | 0.63805 | 168 | 0.98433 | 78225.4531 | 16819.1992 | 1680 | 5040 | 910 | 3220 | 27669.1992 | 5660.3999 | 127750 | 239305.0469 | 764215.75 | 3424902
Interest rate | % | 4 | 4 | 4 | 4 | 15000 | 0.63271 | 168 | 0.99264 | 78885.625 | 15697.9199 | 1680 | 5040 | 910 | 3220 | 26547.9199 | 5625.3594 | 127750 | 238808.9062 | 770665.25 | 3425835.25
Period | yrs | 15 | 15 | 15 | 15 | 16000 | 0.62775 | 180 | 0.93377 | 79508.2188 | 15768 | 1800 | 5400 | 975 | 3450 | 27393 | 5640.7505 | 127750 | 240291.9688 | 776747.6875 | 3448406.75
CAPITAL COSTS INPUTS | [5 empty] | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | 750000 | 750000 | 750000 | 750000 | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ |  |  |  |  | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $ |  |  |  |  | 200 | 1 | 120 | 0.90501 | 51372.6523 | 840960 | 1200 | 3600 | 650 | 2300 | 848710 | 31362 | 127750 | 1059194.625 | 556654.75 | 12333191
Inlet/Oultet Piping | [5 empty] | 400 | 0.9888 | 120 | 0.91526 | 51954.5 | 420480 | 1200 | 3600 | 650 | 2300 | 428230 | 18222 | 127750 | 626156.5 | 562959.4375 | 7524810
Valves | Total $ |  |  |  |  | 600 | 0.95556 | 120 | 0.9471 | 53761.9648 | 280320 | 1200 | 3600 | 650 | 2300 | 288070 | 13842 | 127750 | 483423.9688 | 582544.5 | 5957439.5
Flowmeters | Total $ |  |  |  |  | 800 | 0.93265 | 120 | 0.97036 | 55082.3945 | 210240 | 1200 | 3600 | 650 | 2300 | 217990 | 11652 | 127750 | 412474.4062 | 596852.125 | 5182902.5
Piping and Appurtences | Total $ |  |  |  |  | 1000 | 0.91526 | 120 | 0.9888 | 56128.8906 | 168192 | 1200 | 3600 | 650 | 2300 | 175942 | 10338 | 127750 | 370158.875 | 608191.5625 | 4723761.5
Channels | Total $ |  |  |  |  | 2000 | 0.86329 | 132 | 0.95302 | 59508.0977 | 92505.6016 | 1320 | 3960 | 715 | 2530 | 101030.6016 | 7986.0005 | 127750 | 296274.6875 | 644807.375 | 3938904
Power | [5 empty] | 3000 | 0.83426 | 132 | 0.98618 | 61578.3516 | 61670.3984 | 1320 | 3960 | 715 | 2530 | 70195.3984 | 7022.3999 | 127750 | 266546.1562 | 667239.875 | 3630803.25
Switch gear | Total $ |  |  |  |  | 4000 | 0.81427 | 144 | 0.9262 | 63090.75 | 50457.6016 | 1440 | 4320 | 780 | 2760 | 59757.6016 | 6685.1997 | 127750 | 257283.5469 | 683627.6875 | 3544205.75
Transformer | Total $ |  |  |  |  | 5000 | 0.79908 | 144 | 0.9438 | 64289.3945 | 40366.0781 | 1440 | 4320 | 780 | 2760 | 49666.0781 | 6369.8398 | 127750 | 248075.3125 | 696615.75 | 3454813.25
Distribution Panels | Total $ |  |  |  |  | 6000 | 0.78689 | 144 | 0.95842 | 65285.6367 | 33638.3984 | 1440 | 4320 | 780 | 2760 | 42938.3984 | 6159.5996 | 127750 | 242133.6406 | 707410.6875 | 3399546.25
Generator | Total $ |  |  |  |  | 7000 | 0.77673 | 144 | 0.97097 | 66140 | 28832.9141 | 1440 | 4320 | 780 | 2760 | 38132.9141 | 6009.4287 | 127750 | 238032.3438 | 716668.125 | 3363204
UPS | Total $ |  |  |  |  | 8000 | 0.76803 | 144 | 0.98196 | 66889.1016 | 25228.8008 | 1440 | 4320 | 780 | 2760 | 34528.8008 | 5896.7993 | 127750 | 235064.7031 | 724785.1875 | 3338325.5
Misc Electrical | Total $ |  |  |  |  | 9000 | 0.76044 | 144 | 0.99177 | 67556.8984 | 22425.5996 | 1440 | 4320 | 780 | 2760 | 31725.5996 | 5809.1997 | 127750 | 232841.7031 | 732021.125 | 3320845.25
Other | [5 empty] | 10000 | 0.75371 | 156 | 0.92365 | 68159.9062 | 21864.9609 | 1560 | 4680 | 845 | 2990 | 31939.9609 | 5804.8804 | 127750 | 233654.75 | 738555.125 | 3336419
Yard piping | Total $ |  |  |  |  | 11000 | 0.74767 | 156 | 0.9311 | 68710.0234 | 19877.2363 | 1560 | 4680 | 845 | 2990 | 29952.2363 | 5742.7637 | 127750 | 232155.0312 | 744516.0625 | 3325705.5
Chlorine contactor | Total $ |  |  |  |  | 12000 | 0.74221 | 156 | 0.93796 | 69216.1328 | 18220.8008 | 1560 | 4680 | 845 | 2990 | 28295.8008 | 5691.0005 | 127750 | 230952.9375 | 750000 | 3317824.25
Low lift pumps | Total $ |  |  |  |  | 13000 | 0.73721 | 156 | 0.94431 | 69684.9844 | 16819.1992 | 1560 | 4680 | 845 | 2990 | 26894.1992 | 5647.2002 | 127750 | 229976.3906 | 755080.375 | 3312047
UV Building | [5 empty] | 14000 | 0.73262 | 156 | 0.95024 | 70121.9141 | 15617.8281 | 1560 | 4680 | 845 | 2990 | 25692.8281 | 5609.6577 | 127750 | 229174.4062 | 759814.75 | 3307864.5
Demolition | Total $ |  |  |  |  | 15000 | 0.72837 | 156 | 0.95578 | 70531.1484 | 14576.6396 | 1560 | 4680 | 845 | 2990 | 24651.6406 | 5577.1201 | 127750 | 228509.9062 | 764249 | 3304910.5
Civil/sitework | Total $ |  |  |  |  | 16000 | 0.72441 | 156 | 0.961 | 70916.1172 | 13665.5996 | 1560 | 4680 | 845 | 2990 | 23740.5996 | 5548.6499 | 127750 | 227955.3594 | 768420.4375 | 3302916.5
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2 | 131.6744 | 131.6744 | 131.6744 | 131.6744
95% UVT | mJ/cm2 | 88.4972 | 88.4972 | 88.4972 | 88.4972
90% UVT | mJ/cm2 | 52.6773 | 52.6773 | 52.6773 | 52.6773
85% UVT | mJ/cm2 | 34.5086 | 34.5086 | 34.5086 | 34.5086
80% UVT | mJ/cm2 | 24.0881 | 24.0881 | 24.0881 | 24.0881
75% UVT | mJ/cm2 | 17.6701 | 17.6701 | 17.6701 | 17.6701
70% UVT | mJ/cm2 | 13.5294 | 13.5294 | 13.5294 | 13.5294
65% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
60% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
55% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
50% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
45% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
40% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
35% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
30% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
25% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
20% UVT | mJ/cm2 | 9999 | 9999 | 9999 | 9999
|  | 2.4987 | 2.4987 | 2.4987 | 2.4987
|  | 9.2 | 9.2 | 9.2 | 9.2
|  | 0.78215 | 0.78215 | 0.78215 | 0.78215
|  | 0.94868 | 0.94868 | 0.94868 | 0.94868
Lamp Analysis
Clear