## STANDARD LCA
NYSERDA - Life Cycle Cost Analysis Tool
Starting Column | 1
Ending Column | 3
Lamp Aging Functions
Units: y = %, x = hrs
MMF: y=(a*b+c*x^d)/(b+x^d)
EXP: y=a*e^(b*x)
LIN: Y = ax+b
COMMENTS | Vendor
Lamp Type
Vendor
OUTPUTS | 0
Lamp Life
Age Factor
Average # Lamps
Average Power Level | %
Power | $/yr
Consumables
Lamps | $/yr
Sleeves | $/yr
Ballasts | $/yr
Sensors | $/yr
Calibration | $/yr
Total Consumables | $/yr
Labor | $/yr
Patent | $/yr
Total O&M | $/yr
Total Capital | $
Total Present Worth | $
Present Worth O&M | $
Lamps
Peak Power
UV SYSTEM SIZING CRITERIA
Design Flow | mgd
Average Flow | mgd
Average UVT | %/cm
Design UVT | %/cm
Design UV Dose | mJ/cm^2
REACTOR DESIGN INPUTS
Configuration
Max. Flow per reactor | mgd
Number of Trains
Number of Reactors/Train
Banks/Reactor
Lamps/Bank
Lamps/Ballast
Sensors/bank
Redundancy
No. of Redundant Trains
No. of Redundant Reactors per train
Lamp Data
Lamp 100% Power | kW
Lamp Life | hrs
Lamp Aging Factor | %
Lamp Cost | $
Lamp Replacement Time | min
Fit Type (MMF, EXP, LIN, CUSTOM)
Coefficient A
Coefficient B
Coefficient C
Coefficient D
Coefficient E
Coefficient F
Lamp Power | kW
Lamp Aging Equation | 9999
Sleeve Data
Sleeve Life | yrs
Sleeve Cost | $
Sleeve Replacement Time | min
Sleeve Cleaning Type (Rinse, Wiper)
Sleeve Cleaning Period | weeks
Sleeve Cleaning Time/Reactor | min
Fouling Factor | %
Ballast Data
Ballast Life | yrs
Ballast Costs | $
Ballast replacement | min
Sensor Data
Sensor life | yrs
Sensor cost | $
Sensor replacement | min
Sensor cal period | months
Sensor calibration cost | $
Sensor calibration | min
Dose Pacing | Enter if dose pacing responds to the following parameters.
Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling
Peak dose will be equal to or greater than the design dose.
Peak UV Dose ** | mJ/cm^2
Flow (y/n)
Lamp Age (y/n)
UVT (y/n)
Fouling (y/n)
WTP INPUTS
Labor rate | $/hr
Electricity Cost | $/kWhr
Patent fees | $/1000 gal
Interest rate | %
Period | yrs
CAPITAL COSTS INPUTS
Reactor | Total $
Install Factor | Total $
Validation | Total $
Inlet/Oultet Piping
Valves | Total $
Flowmeters | Total $
Piping and Appurtences | Total $
Channels | Total $
Power
Switch gear | Total $
Transformer | Total $
Distribution Panels | Total $
Generator | Total $
UPS | Total $
Misc Electrical | Total $
Other
Yard piping | Total $
Chlorine contactor | Total $
Low lift pumps | Total $
UV Building
Demolition | Total $
Civil/sitework | Total $
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2
95% UVT | mJ/cm2
90% UVT | mJ/cm2
85% UVT | mJ/cm2
80% UVT | mJ/cm2
75% UVT | mJ/cm2
70% UVT | mJ/cm2
65% UVT | mJ/cm2
60% UVT | mJ/cm2
55% UVT | mJ/cm2
50% UVT | mJ/cm2
45% UVT | mJ/cm2
40% UVT | mJ/cm2
35% UVT | mJ/cm2
30% UVT | mJ/cm2
25% UVT | mJ/cm2
20% UVT | mJ/cm2
Note on A43: Example. Enter 95% as "95" as opposed to "0.95"
Note on A44: Example. Enter 95% as "95" as opposed to "0.95"
Note on B72: This cell contains a lamp aging equation for fit types MMF, EXP, and LIN that can be copied to other columns.
LCA

## LAMP AGE LCA TOOL
NYSERDA - Lamp Aging Analysis Tool
Starting Column | 1
Ending Column | 1
Lamp Aging Analysis Type | 1
1 = Adjust capital
0 = Do not adjust capital
Lamp Aging Functions
Units: y = %, x = hrs
MMF: y=(a*b+c*x^d)/(b+x^d)
EXP: y=a*e^(b*x)
LIN: Y = ax+b
Simulation - Cost Benefit Analysis for Example
|  | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
ID | 0 | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Comment |  | 1000
2000
UV SYSTEM SIZING CRITERIA |  | 3000
4000
Design Flow | mgd | 5000
Average Flow | mgd | 6000
Average UVT | %/cm | 7000
Design UVT | %/cm | 8000
Design UV Dose | mJ/cm^2 | 9000
REACTOR DESIGN INPUTS |  | 10000
Configuration |  | 11000
Max. Flow per reactor | mgd | 12000
Number of Trains |  | 13000
Number of Reactors/Train |  | 14000
Banks/Reactor |  | 15000
Lamps/Bank |  | 16000
Lamps/Ballast |  | 17000
Sensors/bank |  | 18000
Redundancy |  | 19000
No. of Redundant Trains |  | 20000
No. of Redundant Reactors per train
Lamp Data
Lamp 100% Power | kW
Lamp Life | hrs | Simulation - Cost Benefit Analysis for Case 2
Lamp Aging Factor | % | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Lamp Cost | $ | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Lamp Replacement Time | min | 1000
Fit Type (MMF, EXP, LIN, CUSTOM) |  | 2000
Coefficient A |  | 3000
Coefficient B |  | 4000
Coefficient C |  | 5000
Coefficient D |  | 6000
Coefficient E |  | 7000
Coefficient F |  | 8000
Lamp Power | kW | 9000
Lamp Aging Equation | 9999 | 10000
Sleeve Data |  | 11000
Sleeve Life | yrs | 12000
Sleeve Cost | $ | 13000
Sleeve Replacement Time | min | 14000
Sleeve Cleaning Type (Rinse, Wiper) |  | 15000
Sleeve Cleaning Period | weeks | 16000
Sleeve Cleaning Time/Reactor | min | 17000
Fouling Factor | % | 18000
19000
Ballast Data |  | 20000
Ballast Life | yrs
Ballast Costs | $
Ballast replacement | min
Sensor Data |  | Simulation - Cost Benefit Analysis for Case 3
Sensor life | yrs | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Sensor cost | $ | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Sensor replacement | min | 1000
Sensor cal period | months | 2000
Sensor calibration cost | $ | 3000
Sensor calibration | min | 4000
5000
Dose Pacing | Enter if dose pacing responds to the following parameters. | 6000
| Peak dose is defined as UV dose delivered by reactor with all lamps on at 100% ballast power under design conditions of flow, UVT, lamp aging, and fouling | 7000
| Peak dose will be equal to or greater than the design dose. | 8000
Peak UV Dose ** | mJ/cm^2 | 9000
Flow (y/n) |  | 10000
Lamp Age (y/n) |  | 11000
UVT (y/n) |  | 12000
Fouling (y/n) |  | 13000
14000
WTP INPUTS |  | 15000
Labor rate | $/hr | 16000
Electricity Cost | $/kWhr | 17000
Patent fees | $/1000 gal | 18000
Interest rate | % | 19000
Period | yrs | 20000
CAPITAL COSTS INPUTS |  | Simulation - Cost Benefit Analysis for Case 4
Reactor | Total $ | Lamp | Age | Average | Power | Power | Consumables ($) |  |  |  |  | Cons. | Labor | Patent | T O&M | Capital | NPV
Install Factor | Total $ | Life | Factor | # lamps | Setting (%) | $ | Lamps | Sleeves | Ballasts | Sensors | Cal | Total | $ | $ | $ | $ | $
Validation | Total $
Inlet/Oultet Piping
Valves | Total $
Flowmeters | Total $
Piping and Appurtences | Total $
Channels | Total $
Power
Switch gear | Total $
Transformer | Total $
Distribution Panels | Total $
Generator | Total $
UPS | Total $
Misc Electrical | Total $
Other
Yard piping | Total $
Chlorine contactor | Total $
Low lift pumps | Total $
UV Building
Demolition | Total $
Civil/sitework | Total $
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC | Total $
Misc Electrical | Total $
Civil/Site Work | Total $
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
DOSE DELIVERY | Enter the UV dose delivered by the UV reactor at the design flowrate with new lamps operating at 100% ballast power and new unfouled sleeves.
Entered values should include the full range of UVT that occurs at the WTP including one data point above and below that range. Enter 9999 for all other values.
98% UVT | mJ/cm2
95% UVT | mJ/cm2
90% UVT | mJ/cm2
85% UVT | mJ/cm2
80% UVT | mJ/cm2
75% UVT | mJ/cm2
70% UVT | mJ/cm2
65% UVT | mJ/cm2
60% UVT | mJ/cm2
55% UVT | mJ/cm2
50% UVT | mJ/cm2
45% UVT | mJ/cm2
40% UVT | mJ/cm2
35% UVT | mJ/cm2
30% UVT | mJ/cm2
25% UVT | mJ/cm2
20% UVT | mJ/cm2
Note on A27: Example. Enter 95% as "95" as opposed to "0.95"
Note on A28: Example. Enter 95% as "95" as opposed to "0.95"
Note on B56: This cell contains a lamp aging equation for fit types MMF, EXP, and LIN that can be copied to other columns.
Lamp Analysis
Clear

## ADVANCED LCA
NYSERDA - Advanced Life Cycle Cost Analysis Tool
Starting Column | 1
Ending Column | 1
Save Directory | C:\Documents and Settings\hwright\Desktop\Task 4 - Risk Based Design
Save Name | NYSERDA Output Case xxx
Lamp Aging Functions
Units: y = %, x = hrs
MMF: y=(a*b+c*x^d)/(b+x^d)
EXP: y=a*e^(b*x)
LIN: Y = ax+b
COMMENTS |  | Example
OUTPUTS | 0 | 1
Lamp Life
Age Factor
Average # Lamps
Average Power Level | %
Power | $/yr
Consumables
Lamps | $/yr
Sleeves | $/yr
Ballasts | $/yr
Sensors | $/yr
Calibration | $/yr
Total Consumables | $/yr
Labor | $/yr
Patent | $/yr
Total O&M | $/yr
Total Capital | $
Total Present Worth | $
Present Worth O&M | $
Design Power Setting | %
UV SYSTEM SIZING CRITERIA
Design Flow | mgd
Average Flow | mgd
Average UVT | %/cm
Design UVT | %/cm
Design UV Dose | mJ/cm^2
Minimum Number of Trains
REACTOR DESIGN INPUTS
Configuration
Max. Flow per reactor | mgd
Number of Trains
Number of Reactors/Train
Banks/Reactor
Lamps/Bank
Lamps/Ballast
Sensors/bank
Redundancy
No. of Redundant Trains
No. of Redundant Reactors per train
Lamp Data
Lamp 100% Power | kW
Lamp Life | hrs
Lamp Aging Factor | %
Lamp Cost | $
Lamp Replacement Time | min
Fit Type (MMF, EXP, LIN, CUSTOM)
Coefficient A
Coefficient B
Coefficient C
Coefficient D
Coefficient E
Coefficient F
Lamp Power | kW
Lamp Aging Equation | 9999
Sleeve Data
Sleeve Life | yrs
Sleeve Cost | $
Sleeve Replacement Time | min
Sleeve Cleaning Type (Rinse, Wiper)
Sleeve Cleaning Period | weeks
Sleeve Cleaning Time/Reactor | min
Fouling Factor | %
Ballast Data
Ballast Life | yrs
Ballast Costs | $
Ballast replacement | min
Sensor Data
Sensor life | yrs
Sensor cost | $
Sensor replacement | min
Sensor cal period | months
Sensor calibration cost | $
Sensor calibration | min
Dose Model and Pacing | Enter if dose pacing responds to the following parameters.
Dose Model | 1
Dose Model | Drinking Water - MP
Failure Data
Supply Voltage Lower Limit | % nom
PQ Event Duration Lower Limit | s
UPS (y/n)
Generator (y/n)
Generator Startup Time | s
Automatic Flow Shutoff Valve (y/n)
Shut Off Valve Response Time | s
Lamp Cool-down Time | min
Lamp Warmup Time | min
Lamp Failure Probability | per day
Ballast Failure Probability | per day
UV Sensor Failure Probability | per day
UVT Monitor Failure Probability | per day
WTP INPUTS
Labor rate | $/hr
Electricity Cost | $/kWhr
Patent fees | $/1000 gal
Interest rate | %
Period | yrs
Supply Voltage | volts
Population
CAPITAL COSTS INPUTS
Reactor | Total $
Install Factor | Total $
Validation | Total $
Inlet/Oultet Piping
Valves | Total $
Flowmeters | Total $
Piping and Appurtences | Total $
Channels | Total $
Power
Switch gear | Total $
Transformer | Total $
Distribution Panels | Total $
Generator | Total $
UPS | Total $
Misc Electrical | Total $
Other
Yard piping | Total $
Chlorine contactor | Total $
Low lift pumps | Total $
UV Building
Demolition | Total $
Civil/sitework | Total $
Building | Total $
HVAC | Total $
Instrumentation | Total $
HVAC
Misc Electrical
Civil/Site Work
Contingency | Total $
General conditions | Total $
Contractor O&P | Total $
Engineering, Legal, Admin | Total $
Total | Total $
Ballast Power Settings (%)
Setting 1
Setting 2
Setting 3
Setting 4
Setting 5
Setting 6
Setting 7
Setting 8
Setting 9
Setting 10
Setting 11
Setting 12
Setting 13
Setting 14
Setting 15
Setting 16
Setting 17
Setting 18
Setting 19
Setting 20
Setting 21
Setting 22
Setting 23
Setting 24
Note on A44: Example. Enter 95% as "95" as opposed to "0.95"
Note on A45: Example. Enter 95% as "95" as opposed to "0.95"
Note on A163: Enter ballast power settings in ascending order. Enter "9999" to indicate last ballast setting. UVCAT uses the "9999" to indicate the end of the ballast settings list.
Note on B76: This cell contains a lamp aging equation for fit types MMF, EXP, and LIN that can be copied to other columns.
Note on B101: Copy this cell to next column to get name of dose model selected in row 100
Advanced LCA
Clear

## WQ
Starting Row | 15
Ending Row | 1676
WATER QUALITY INPUTS | [5 empty] | OUTPUTS
[13 empty] | Ideal |  | Daily |  | Sum
Date_Time | Flow | UVT | Pathogens | Supply | PQ | Target | Trains | Reactors | Banks/ | Flow/ | Fouling | Total | Total |  | Power | Power | Power | Offspec | Offspec | Offspec | UV System | Risk | Annual | Accumulated
|  |  |  | Voltage | Event | RED |  | Per Train | Reactor | Reactor | Factor | Power | Power | Ratio | Costs | Costs | Costs | Flag | Time | Volume | Log Kill |  | Risk | Illness
|  |  | Microbes |  | Duration | mJ/cm2 |  |  |  | mgd |  | kW | kW |  | $ | $ | $ |  | % of month | % of month
| mgd | %/cm | per L | V | s
0
Note on C14: Example. Enter 95% as "95" as opposed to "0.95"

## REDMODEL
UV SYSTEM SENSOR AND DOSE MODEL
Drinking Water - LPHO - Full Dose Pacing - Case 4
Product ID | Model ID | Location | Drinking Water - MP |  |  | Drinking Water - MP - Case 1 |  |  | Drinking Water - MP - Case 2 |  |  | Drinking Water - LPHO - Full Pacing - Case 3 |  |  | Drinking Water - LPHO - Flow and UVT Pacing - Case 3 |  |  | Drinking Water - LPHO - Flow Pacing - Case 3 |  |  | Drinking Water - LPHO - No Dose Pacing - Case 3 |  |  | Drinking Water - LPHO - Full Dose Pacing - Case 4 |  |  | Wastewater - Ideal |  |  | Wastewater - Flow pacing |  |  | Wastewater - Flow & lamp pacing |  |  | Wright et al, 2005
Drinking Water - MP | 1 | G | [9 empty] | 11 bank reactor of 12 lamps per bank |  |  | 11 bank reactor of 12 lamps per bank |  |  | 11 bank reactor of 12 lamps per bank |  |  | 11 bank reactor of 12 lamps per bank |  |  | One bank reactor of 11 x 12 lamps
Drinking Water - MP - Case 1 | 2 | K | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 24 | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 40 | Target RED/Reactor | mJ/cm2 | 4.1 | Target RED/Reactor | mJ/cm2 | 11 | Target RED/Reactor | mJ/cm2 | 11 | Target RED/Reactor | mJ/cm2 | 23.6
Drinking Water - MP - Case 2 | 3 | O | Flow/Reactor | mgd | 10 | Flow/Reactor | mgd | 14.7977 | Flow/Reactor | mgd | 14.7977 | Flow/Reactor | mgd | 14.7977 | Flow/Reactor | mgd | 14.7977 | Flow/Reactor | mgd | 11.0983 | Flow/Reactor | mgd | 11.0983 | Flow/Reactor | mgd | 14.7977 | Flow/Reactor | mgd | 17.494 | Flow/Reactor | mgd | 8.8786 | Flow/Reactor | mgd | 8.8786 | Flow/Reactor | mgd | 10
Drinking Water - LPHO - Full Pacing - Case 3 | 4 | S | UVT | % | 80 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 93.4236 | UVT | % | 92.406 | UVT | % | 92.406 | UVT | % | 75
Drinking Water - LPHO - Flow and UVT Pacing - Case 3 | 5 | W | Lamp Aging Factor | % | 100 | Lamp Aging Factor | % | 87.9877 | Lamp Aging Factor | % | 89.8529 | Lamp Aging Factor | % | 76.5131 | Lamp Aging Factor | % | 82.9312 | Lamp Aging Factor | % | 102.6783 | Lamp Aging Factor | % | 79.4332 | Lamp Aging Factor | % | 90.8829 | Lamp Aging Factor | % | 100 | Lamp Aging Factor | % | 71.9859 | Lamp Aging Factor | % | 84.3487 | Lamp Aging Factor | % | 100
Drinking Water - LPHO - Flow Pacing - Case 3 | 6 | AA | Fouling Factor | % | 100 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 98.3929 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 100 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 95.1786 | Fouling Factor | % | 100
Drinking Water - LPHO - No Dose Pacing - Case 3 | 7 | AE | Number Operating Banks/Reactor |  | 2 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 9 | Number Operating Banks/Reactor |  | 10 | Number Operating Banks/Reactor |  | 9 | Number Operating Banks/Reactor |  | 11 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 1 | Number Operating Banks/Reactor |  | 2
Drinking Water - LPHO - Full Dose Pacing - Case 4 | 8 | AI | Actual Power 1 | kW | 17.01 | Actual Power 1 | kW | 20 | Actual Power 1 | kW | 12 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 0.36 | Actual Power 1 | kW | 100 | Actual Power 1 | kW | 80 | Actual Power 1 | kW | 80 | Actual Power 1 | kW | 15
Wastewater - Ideal | 9 | AM | Actual Power 2 | kW |  | Actual Power 2 | kW | 20 | Actual Power 2 | kW |  | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW | 0.36 | Actual Power 2 | kW |  | Actual Power 2 | kW |  | Actual Power 2 | kW |  | Actual Power 2 | kW
Wastewater - Flow pacing | 10 | AQ | # Type 1 Lamps / Bank |  | 3 | # Type 1 Lamps / Bank |  | 3 | # Type 1 Lamps / Bank |  | 8 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 12 | # Type 1 Lamps / Bank |  | 132 | # Type 1 Lamps / Bank |  | 64 | # Type 1 Lamps / Bank |  | 64 | # Type 1 Lamps / Bank |  | 64 | # Type 1 Lamps / Bank |  | 3
Wastewater - Flow & lamp pacing | 11 | AU | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0 | # Type 2 Lamps / Bank |  | 0
Wright et al, 2005 | 12 | AY | Model Calc |  | G17:G34 | Model Calc |  | K17:K34 | Model Calc |  | O17:O34 | Model Calc |  | S17:S34 | Model Calc |  | W17:W34 | Model Calc |  | AA17:AA38 | Model Calc |  | AE17:AE38 | Model Calc |  | AI17:AI34 | Model Calc |  | AM17:AM27 | Model Calc |  | AQ17:AQ27 | Model Calc |  | AU17:AU27 | Model Calc |  | AY17:AY34
Not used | 13 | BC
Not used | 14 | BG | Target Lamp Power 1 | kW | 22.6786 | Target Lamp Power 1 | kW | 14.7117 | Target Lamp Power 1 | kW | 7.331 | Target Lamp Power 1 | kW | 0.30836 | Target Lamp Power 1 | kW | 0.33978 | Target Lamp Power 1 | kW | 0.35258 | Target Lamp Power 1 | kW | 0.34405 | Target Lamp Power 1 | kW | 0.21253 | Target Lamp Power 1 | kW | 0.016139 | Target Lamp Power 1 | kW | 0.0559 | Target Lamp Power 1 | kW | 0.046391 | Target Lamp Power 1 | kW | 15.7487
Not used | 15 | BK | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW |  | Target Lamp Power 2 | kW | 0 | Target Lamp Power 2 | kW | 0 | Target Lamp Power 2 | kW | 0 | Target Lamp Power 2 | kW
Not used | 16 | BO | Target Sensor | W/m2 | 182.7677 | Target Sensor | W/m2 | 274.9209 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 4.8842 | Target Sensor | W/m2 | 4.3971 | Target Sensor | W/m2 | 3.5963 | Target Sensor | W/m2 | 3.5094 | Target Sensor | W/m2 | 3.9985 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 1 | Target Sensor | W/m2 | 27.9765
Not used | 17 | BS | Sensor | W/m2 | 108.9079 | Sensor | W/m2 | 477.825 | Sensor | W/m2 | 1 | Sensor | W/m2 | 5.7021 | Sensor | W/m2 | 6.1804 | Sensor | W/m2 | 7.652 | Sensor | W/m2 | 5.9197 | Sensor | W/m2 | 6.773 | Sensor | W/m2 | 1 | Sensor | W/m2 | 1 | Sensor | W/m2 | 1 | Sensor | W/m2 | 26.6465
Not used | 18 | BW | Credited dose | mJ/cm2 | 25.1017 | Credited dose | mJ/cm2 | 65.7832 | Credited dose | mJ/cm2 | 47.8454 | Credited dose | mJ/cm2 | 46.6753 | Credited dose | mJ/cm2 | 56.1617 | Credited dose | mJ/cm2 | 83.3625 | Credited dose | mJ/cm2 | 78.7899 | Credited dose | mJ/cm2 | 67.6428 | Credited dose | mJ/cm2 |  | Credited dose | mJ/cm2 |  | Credited dose | mJ/cm2 |  | Credited dose | mJ/cm2 | 23.0582
Not used | 19 | CA | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0 | Off Spec Performance | y=1, n=0 | 0
Not used | 20 | CE | UVA | cm-1 | 0.09691 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.029543 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.0343 | UVA | cm-1 | 0.12494
|  |  | Output factor | % | 100 | Output factor | % | 83.7454 | Output factor | % | 88.4089 | Output factor | % | 72.8241 | Output factor | % | 78.9327 | Output factor | % | 97.7277 | Output factor | % | 75.6034 | Output factor | % | 86.501 | Output factor | % | 100 | Output factor | % | 68.5151 | Output factor | % | 80.2819 | Output factor | % | 100
|  |  | Min banks |  | 1 | Min banks |  | 1 | Min banks |  | 1 | Min banks |  | 2 | Min banks |  | 2 | Min banks |  | 2 | Min banks |  | 11 | Min banks |  | 1 | Residence Time | s | 0.68606 | Residence Time | s | 1.3518 | Residence Time | s | 1.3518 | Min banks |  | 1
|  |  | Min UVT | % | 75 | Min UVT | % | 75 | Min UVT | % | 75 | Min UVT | % | 85 | Min UVT | % | 85 | Min UVT | % | 85 | Min UVT | % | 85 | Min UVT | % | 85 | Iavg | mW/cm2 | 24.9947 | Iavg | mW/cm2 | 16.5143 | Iavg | mW/cm2 | 16.5143 | Min UVT | % | 75
|  |  | Max UVT | % | 95 | Max UVT | % | 95 | Max UVT | % | 95 | Max UVT | % | 96 | Max UVT | % | 96 | Max UVT | % | 96 | Max UVT | % | 96 | Max UVT | % | 96 | [9 empty] | Max UVT | % | 98
|  |  | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | Min Flow | mgd | 5 | [9 empty] | Min Flow | mgd | 5
|  |  | Max Flow | mgd | 36 | Max Flow | mgd | 36 | Max Flow | mgd | 36 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | Max Flow | mgd | 30 | RED Model |  |  | RED Model |  |  | RED Model |  |  | Max Flow | mgd | 40
|  |  | Dose calc UVT | % | 80 | Dose calc UVT | % | 95 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Dose calc UVT | % | 92.406 | Lamps x-direction |  | 8 | Lamps x-direction |  | 8 | Lamps x-direction |  | 8 | Dose calc UVT | % | 75
|  |  | Dose calc UVA | cm-1 | 0.09691 | Dose calc UVA | cm-1 | 0.022276 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Dose calc UVA | cm-1 | 0.0343 | Lamps y-direction |  | 8 | Lamps y-direction |  | 8 | Lamps y-direction |  | 8 | Dose calc UVA | cm-1 | 0.12494
|  |  | Dose calc flow | mgd | 10 | Dose calc flow | mgd | 14.7977 | Dose calc flow | mgd | 14.7977 | Dose calc flow | mgd | 14.7977 | Dose calc flow | mgd | 14.7977 | Dose calc flow | mgd | 11.0983 | Dose calc flow | mgd | 11.0983 | Dose calc flow | mgd | 14.7977 | Lamp spacing | cm | 7.62 | Lamp spacing | cm | 7.62 | Lamp spacing | cm | 7.62 | Dose calc flow | mgd | 10
|  |  | S Nominal | W/m2 | 145.7624 | S Nominal | W/m2 | 758.9817 | Fraction of Peak Power | % | 0.5401 | S Nominal | W/m2 | 7.8299 | S Nominal | W/m2 | 7.8299 | S Nominal | W/m2 | 7.8299 | S Nominal | W/m2 | 7.8299 | S Nominal | W/m2 | 7.8299 | Lamp length | cm | 147 | Lamp length | cm | 147 | Lamp length | cm | 147 | S Nominal | W/m2 | 26.6465
|  |  | S Nominal *Q | W/m2/mgd | 1457.6237 | S Nominal *Q | W/m2/mgd | 11231.1592 |  |  |  | S Nominal *Q | W/m2/mgd | 115.8644 | S Nominal *Q | W/m2/mgd | 115.8644 | S Nominal *Q | W/m2/mgd | 86.8983 | S Nominal *Q | W/m2/mgd | 86.8983 | S Nominal *Q | W/m2/mgd | 115.8644 | Sleeve diameter | cm | 2.54 | Sleeve diameter | cm | 2.54 | Sleeve diameter | cm | 2.54 | S Nominal *Q | W/m2/mgd | 266.465
[27 empty] | 100% Lamp Power | kW | 0.0675 | 100% Lamp Power | kW | 0.0675 | 100% Lamp Power | kW | 0.0675
|  |  | Sensor Model Coefficients |  |  | Sensor Model Coefficients |  |  | Model Coefficients |  |  | Sensor Model Coefficients |  |  | Sensor Model Coefficients |  |  | S Nominal Default | W/m2 | 6.1714 | S Nominal Default | W/m2 | 6.1714 | Sensor Model Coefficients | [11 empty] | Sensor Model Coefficients
|  |  | A |  | -4 | A |  | -4 | A |  | 1e-11 | A |  | -1.383 | A |  | -1.383 | S Nominal *Q Default | W/m2/mgd | 68.4921 | S Nominal *Q Default | W/m2/mgd | 81.6419 | A |  | -1.383 | Logistic Model: y=a/(1+b*exp(-cx)) |  |  | Logistic Model: y=a/(1+b*exp(-cx)) |  |  | Logistic Model: y=a/(1+b*exp(-cx)) |  |  | A |  | 1.3577
|  |  | B |  | 0.11 | B |  | 0.11 | B |  | -0.9 | B |  | 0.056732 | B |  | 0.056732 | Default UVA | cm-1 | 0.05448 | Default UVA | cm-1 | 0.05448 | B |  | 0.056732 | Coefficient Data: |  |  | Coefficient Data: |  |  | Coefficient Data: |  |  | B |  | 0.08262
|  |  | C |  | 1.8 | C |  | 1.8 | C |  | 5.6 | [6 empty] | Sensor Model Coefficients |  |  | Sensor Model Coefficients | [5 empty] | a = |  | -9.7123 | a = |  | -9.7123 | a = |  | -9.7123 | C |  | -1.8933
[9 empty] | D |  | 1.4 | RED Model Coefficients |  |  | RED Model Coefficients |  |  | A |  | -1.383 | A |  | -1.383 | RED Model Coefficients |  |  | b = |  | -6.156 | b = |  | -6.156 | b = |  | -6.156
|  |  | RED Model Coefficients |  |  | RED Model Coefficients |  |  | E |  |  | A |  | 1.3314 | A |  | 1.3314 | B |  | 0.056732 | B |  | 0.056732 | A |  | 1.3314 | c = |  | 0.01594 | c = |  | 0.01594 | c = |  | 0.01594 | RED Model Coefficients
|  |  | A |  | 1.4 | A |  | 1.4 | Lamp Power (100%) | kW | 12 | B |  | -0.47312 | B |  | -0.47312 | [6 empty] | B |  | -0.47312 | [9 empty] | A |  | 3.0794
|  |  | B |  | -1 | B |  | -1 |  |  |  | C |  | 0.99684 | C |  | 0.99684 | RED Model Coefficients |  |  | RED Model Coefficients |  |  | C |  | 0.99684 |  |  |  | Default UVT | % | 85 | Default UVT | % | 85 | B |  | -22.8474
|  |  | C |  | 0.9 | C |  | 0.9 | Validated Range |  |  | D |  | 0.99397 | D |  | 0.99397 | A |  | 1.3314 | A |  | 1.3314 | D |  | 0.99397 |  |  |  | Default Lamp aging | % | 70 | Default Lamp aging | % | 70 | C |  | 0.80207
[6 empty] | Nominal Power |  | 20 | Min Banks |  | 1 | [6 empty] | B |  | -0.47312 | B |  | -0.47312 | [6 empty] | Default Fouling | % | 85 | Default Fouling | % | 85 | D |  | 1.9267
|  |  | Nominal Power |  | 20 | Default UVT |  | 95 | Max Banks |  | 3 | Nominal Power |  | 0.36 | Nominal Power |  | 0.36 | C |  | 0.99684 | C |  | 0.99684 | Nominal Power |  | 0.36 | [9 empty] | E |  | -36.2535
[6 empty] | Default UVA |  | 0.022276 | Min UVT (%) |  |  | Default Flow |  | 13.229 | Default Flow |  | 13.229 | D |  | 0.99397 | D |  | 0.99397 | Default Flow |  | 16.5362 | [9 empty] | Nominal Power |  | 15
[9 empty] | 1 bank |  | 75 | Default UVT |  | 88.2104 | Default UVT |  | 88.2104 | [6 empty] | Default UVT |  | 88.2104
|  |  | Validated Range |  |  | Validated Range |  |  | 2 banks |  | 75 | Default Output Factor |  | 59.5 | Default Output Factor |  | 59.5 | Nominal Power |  | 0.36 | Nominal Power |  | 0.36 | Default Output Factor |  | 59.5
|  |  | Min Banks |  | 1 | Min Banks |  | 1 | 3 banks |  | 75 | Default Trains |  | 3 | Default Trains |  | 3 | Default Flow |  | 13.229 | Default Flow |  | 13.229 | Default Trains |  | 3 | [9 empty] | Validated Range
|  |  | Max Banks |  | 3 | Max Banks |  | 3 | Max UVT (%) |  |  | Default Reactors |  | 1 | Default Reactors |  | 1 | Default UVT |  | 88.2104 | Default UVT |  | 88.2104 | Default Reactors |  | 1 | [9 empty] | Min Banks |  | 1
|  |  | Min UVT (%) |  |  | Min UVT (%) |  |  | 1 bank |  | 95 | Default Banks |  | 11 | Default Banks |  | 11 | Default Output Factor |  | 59.5 | Default Output Factor |  | 59.5 | Default Banks |  | 11 | [9 empty] | Max Banks |  | 1
|  |  | 1 bank |  | 75 | 1 bank |  | 75 | 2 banks |  | 95 | [6 empty] | Default Trains |  | 3 | Default Trains |  | 3 | [12 empty] | Min UVT (%)
|  |  | 2 banks |  | 75 | 2 banks |  | 75 | 3 banks |  | 95 | Validated Range |  |  | Validated Range |  |  | Default Reactors |  | 1 | Default Reactors |  | 1 | Validated Range |  |  | UVDIS Data | UVT | Iavg | [6 empty] | 1 bank |  | 75
|  |  | 3 banks |  | 75 | 3 banks |  | 75 | Min Flow (mgd) |  |  | Min Banks |  | 2 | Min Banks |  | 2 | Default Banks |  | 11 | Default Banks |  | 11 | Min Banks |  | 1 |  | % | mW/cm2 | [6 empty] | 2 banks |  | 75
|  |  | Max UVT (%) |  |  | Max UVT (%) |  |  | 1 bank |  | 5 | Max Banks |  | 11 | Max Banks |  | 11 | [6 empty] | Max Banks |  | 11 |  | 95 | 27.4 | [6 empty] | 3 banks |  | 75
|  |  | 1 bank |  | 95 | 1 bank |  | 95 | 2 banks |  | 5 | Min UVT (%) |  |  | Min UVT (%) |  |  | Validated Range |  |  | Validated Range |  |  | Min UVT (%) |  |  |  | 90 | 20.92 | [6 empty] | Max UVT (%)
|  |  | 2 banks |  | 95 | 2 banks |  | 95 | 3 banks |  | 5 | 1 bank |  | 85 | 1 bank |  | 85 | Min Banks |  | 2 | Min Banks |  | 11 | 1 bank |  | 85 |  | 85 | 16.48 | [6 empty] | 1 bank |  | 98
|  |  | 3 banks |  | 95 | 3 banks |  | 95 | Max Flow (mgd) |  |  | 2 banks |  | 85 | 2 banks |  | 85 | Max Banks |  | 11 | Max Banks |  | 11 | Max UVT (%) |  |  |  | 80 | 13.45 | [6 empty] | 2 banks |  | 98
|  |  | Min Flow (mgd) |  |  | Min Flow (mgd) |  |  | 1 bank |  | 36 | 3 banks |  | 85 | 3 banks |  | 85 | Min UVT (%) |  |  | Min UVT (%) |  |  | Min UVT (%) |  |  |  | 75 | 11.2 | [6 empty] | 3 banks |  | 98
|  |  | 1 bank |  | 5 | 1 bank |  | 5 | 2 banks |  | 36 | 4 banks |  | 85 | 4 banks |  | 85 | 1 bank |  | 85 | 1 bank |  | 85 | 1 bank |  | 96 |  | 70 | 9.51 | [6 empty] | Min Flow (mgd)
|  |  | 2 banks |  | 5 | 2 banks |  | 5 | 3 banks |  | 36 | 5 banks |  | 85 | 5 banks |  | 85 | 2 banks |  | 85 | 2 banks |  | 85 | Min Flow (mgd) |  |  |  | 65 | 8.191 | [6 empty] | 1 bank |  | 5
|  |  | 3 banks |  | 5 | 3 banks |  | 5 |  |  |  | 6 banks |  | 85 | 6 banks |  | 85 | 3 banks |  | 85 | 3 banks |  | 85 | 1 bank |  | 5 |  | 60 | 7.131 | [6 empty] | 2 banks |  | 5
|  |  | Max Flow (mgd) |  |  | Max Flow (mgd) | [5 empty] | 7 banks |  | 85 | 7 banks |  | 85 | 4 banks |  | 85 | 4 banks |  | 85 | Max Flow (mgd) |  |  |  | 55 | 6.259 | [6 empty] | 3 banks |  | 5
|  |  | 1 bank |  | 36 | 1 bank |  | 36 |  |  |  | 8 banks |  | 85 | 8 banks |  | 85 | 5 banks |  | 85 | 5 banks |  | 85 | 1 bank |  | 30 |  | 50 | 5.531 | [6 empty] | Max Flow (mgd)
|  |  | 2 banks |  | 36 | 2 banks |  | 36 |  |  |  | 9 banks |  | 85 | 9 banks |  | 85 | 6 banks |  | 85 | 6 banks |  | 85 |  |  |  |  | 45 | 4.904 | [6 empty] | 1 bank |  | 40
|  |  | 3 banks |  | 36 | 3 banks |  | 36 |  |  |  | 10 banks |  | 85 | 10 banks |  | 85 | 7 banks |  | 85 | 7 banks |  | 85 |  |  |  |  | 40 | 4.367 | [6 empty] | 2 banks |  | 40
[12 empty] | 11 banks |  | 85 | 11 banks |  | 85 | 8 banks |  | 85 | 8 banks |  | 85 |  |  |  |  | 35 | 3.894 | [6 empty] | 3 banks |  | 40
[12 empty] | Max UVT (%) |  |  | Max UVT (%) |  |  | 9 banks |  | 85 | 9 banks |  | 85 |  |  |  |  | 30 | 3.469
[12 empty] | Min UVT (%) |  |  | Min UVT (%) |  |  | 10 banks |  | 85 | 10 banks |  | 85 |  |  |  |  | 25 | 3.087
[12 empty] | 1 bank |  | 96 | 1 bank |  | 96 | 11 banks |  | 85 | 11 banks |  | 85 |  |  |  |  | 20 | 2.735
[12 empty] | 2 banks |  | 96 | 2 banks |  | 96 | Max UVT (%) |  |  | Max UVT (%) | [6 empty] | 15 | 2.391
[12 empty] | 3 banks |  | 96 | 3 banks |  | 96 | Min UVT (%) |  |  | Min UVT (%)
[12 empty] | 4 banks |  | 96 | 4 banks |  | 96 | 1 bank |  | 96 | 1 bank |  | 96
[12 empty] | 5 banks |  | 96 | 5 banks |  | 96 | 2 banks |  | 96 | 2 banks |  | 96
[12 empty] | 6 banks |  | 96 | 6 banks |  | 96 | 3 banks |  | 96 | 3 banks |  | 96
[12 empty] | 7 banks |  | 96 | 7 banks |  | 96 | 4 banks |  | 96 | 4 banks |  | 96
[12 empty] | 8 banks |  | 96 | 8 banks |  | 96 | 5 banks |  | 96 | 5 banks |  | 96
[12 empty] | 9 banks |  | 96 | 9 banks |  | 96 | 6 banks |  | 96 | 6 banks |  | 96
[12 empty] | 10 banks |  | 96 | 10 banks |  | 96 | 7 banks |  | 96 | 7 banks |  | 96
[12 empty] | 11 banks |  | 96 | 11 banks |  | 96 | 8 banks |  | 96 | 8 banks |  | 96
[12 empty] | Min Flow (mgd) |  |  | Min Flow (mgd) |  |  | 9 banks |  | 96 | 9 banks |  | 96
[12 empty] | 1 bank |  | 5 | 1 bank |  | 5 | 10 banks |  | 96 | 10 banks |  | 96
[12 empty] | 2 banks |  | 5 | 2 banks |  | 5 | 11 banks |  | 96 | 11 banks |  | 96
[12 empty] | 3 banks |  | 5 | 3 banks |  | 5 | Min Flow (mgd) |  |  | Min Flow (mgd)
[12 empty] | 4 banks |  | 5 | 4 banks |  | 5 | 1 bank |  | 5 | 1 bank |  | 5
[12 empty] | 5 banks |  | 5 | 5 banks |  | 5 | 2 banks |  | 5 | 2 banks |  | 5
[12 empty] | 6 banks |  | 5 | 6 banks |  | 5 | 3 banks |  | 5 | 3 banks |  | 5
[12 empty] | 7 banks |  | 5 | 7 banks |  | 5 | 4 banks |  | 5 | 4 banks |  | 5
[12 empty] | 8 banks |  | 5 | 8 banks |  | 5 | 5 banks |  | 5 | 5 banks |  | 5
[12 empty] | 9 banks |  | 5 | 9 banks |  | 5 | 6 banks |  | 5 | 6 banks |  | 5
[12 empty] | 10 banks |  | 5 | 10 banks |  | 5 | 7 banks |  | 5 | 7 banks |  | 5
[12 empty] | 11 banks |  | 5 | 11 banks |  | 5 | 8 banks |  | 5 | 8 banks |  | 5
[12 empty] | Max Flow (mgd) |  |  | Max Flow (mgd) |  |  | 9 banks |  | 5 | 9 banks |  | 5
[12 empty] | 1 bank |  | 30 | 1 bank |  | 30 | 10 banks |  | 5 | 10 banks |  | 5
[12 empty] | 2 banks |  | 30 | 2 banks |  | 30 | 11 banks |  | 5 | 11 banks |  | 5
[12 empty] | 3 banks |  | 30 | 3 banks |  | 30 | Max Flow (mgd) |  |  | Max Flow (mgd)
[12 empty] | 4 banks |  | 30 | 4 banks |  | 30 | 1 bank |  | 30 | 1 bank |  | 30
[12 empty] | 5 banks |  | 30 | 5 banks |  | 30 | 2 banks |  | 30 | 2 banks |  | 30
[12 empty] | 6 banks |  | 30 | 6 banks |  | 30 | 3 banks |  | 30 | 3 banks |  | 30
[12 empty] | 7 banks |  | 30 | 7 banks |  | 30 | 4 banks |  | 30 | 4 banks |  | 30
[12 empty] | 8 banks |  | 30 | 8 banks |  | 30 | 5 banks |  | 30 | 5 banks |  | 30
[12 empty] | 9 banks |  | 30 | 9 banks |  | 30 | 6 banks |  | 30 | 6 banks |  | 30
[12 empty] | 10 banks |  | 30 | 10 banks |  | 30 | 7 banks |  | 30 | 7 banks |  | 30
[12 empty] | 11 banks |  | 30 | 11 banks |  | 30 | 8 banks |  | 30 | 8 banks |  | 30
[18 empty] | 9 banks |  | 30 | 9 banks |  | 30
[18 empty] | 10 banks |  | 30 | 10 banks |  | 30
[18 empty] | 11 banks |  | 30 | 11 banks |  | 30

## RISKMODEL
Pathogen UV Dose-response |  |  | Risk Model
UV Dose | mJ/cm2 | 42.5002 | Pathogen concentration | #/L | 3
log Inactivation |  | 3.2387 | Filter log Removal |  | 2
Max Credit |  | 6 | UV Log Inactivation |  | 3.1981
Credit |  | 3.2387 | Chemical log Inactivation |  | 0
|  |  | Water consumption | L/day | 1.2
MMF Model: y=(a*b+c*x^d)/(b+x^d) |  |  | Infections per dose |  | 0.028
Coefficient Data: |  |  | Delta Time | days | 1
a = |  | -0.0087794 | Risk |  | 6.3879e-07
b = |  | 157.8254 | Annual risk |  | 0.00022355
c = |  | 4.5861 | Population |  | 1000000
d = |  | 1.5845 | Infectons |  | 0.63879

## REACTORDOSE
Reactor
Bank
Date/Time | Reactor Dose (mJ/cm2)

## TARGET POWER 1
Train
Reactor
Bank
Date/Time | Target Power 1 (kW)

## TARGET POWER 2
Train
Reactor
Bank
Date/Time | Target Power 2 (kW)

## POWER 1
Train
Reactor
Bank
Date/Time | Power 1 (kW)

## POWER 2
Train
Reactor
Bank
Date/Time | Power 1 (kW)

## LAMP HOURS
Train
Reactor
Bank
Date/Time | Lamp Hours (hrs)

## LAMP AGING FACTOR
Train
Reactor
Bank
Date/Time | Lamp Aging Factor

## Pathogen DR
Cryptosporidium |  | Giardia |  | Adenovirus |  | Rotavirus |  | Cryptosporidium |  | Giardia |  | Adenovirus |  | Rotavirus |  | Cryptosporidium |  | Giardia |  | Adenovirus
USEPA UVDGM 2003 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2001 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2003 |  | USEPA UVDGM 2003
80% Credible limits |  | 80% Credible limits |  | 80% Credible limits |  | 80% Credible limits |  | 50% Prediction Interval |  | 50% Prediction Interval |  | 50% Prediction Interval |  | 50% Prediction Interval |  | Tier 1 REDs |  | Tier 1 REDs |  | Tier 1 REDs
UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log | UV Dose | log
mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation | mJ/cm2 | Inactivation
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.6 | 0.5 | 1.5 | 0.5 | 39 | 0.5 | 11.6 | 0.5 | 0.7 | 0.5 | 0.3 | 1 | 0 | 0.5 | 3.2 | 0.5 | 6.8 | 0.5 | 6.6 | 0.5 | 55 | 0.5
2.5 | 1 | 2.1 | 1 | 58 | 1 | 17 | 1 | 1.3 | 1 | 0.3 | 1.5 | 18 | 1 | 8.5 | 1 | 11 | 1 | 9.7 | 1 | 81 | 1
3.9 | 1.5 | 3 | 1.5 | 79 | 1.5 | 22.3 | 1.5 | 1.8 | 1.5 | 0.7 | 2 | 40 | 1.5 | 13.9 | 1.5 | 15 | 1.5 | 13 | 1.5 | 110 | 1.5
5.8 | 2 | 5.2 | 2 | 100 | 2 | 27.7 | 2 | 2.5 | 2 | 0.8 | 2.5 | 62.4 | 2 | 19.2 | 2 | 21 | 2 | 20 | 2 | 139 | 2
8.5 | 2.5 | 7.7 | 2.5 | 121 | 2.5 | 33.1 | 2.5 | 2.9 | 2.5 | 1.3 | 3 | 84.7 | 2.5 | 24.6 | 2.5 | 28 | 2.5 | 26 | 2.5 | 169 | 2.5
12 | 3 | 11 | 3 | 143 | 3 | 38.4 | 3 | 4.3 | 3 |  |  | 107 | 3 | 30 | 3 | 36 | 3 | 34 | 3 | 199 | 3
|  |  |  | 163 | 3.5 | 43.8 | 3.5 |  |  |  |  | 129.3 | 3.5 | 35.3 | 3.5 |  |  |  |  | 227 | 3.5
|  |  |  | 186 | 4 | 49.2 | 4 |  |  |  |  | 151.7 | 4 | 40.7 | 4 |  |  |  |  | 259 | 4
y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d) |  | y=(a*b+c*x^d)/(b+x^d)
Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data: |  | Coefficient Data:
a = | -0.002479 | a = | -0.027557 | a = | -0.028948 | a = | -0.011498 | a = | 0.020396 | a = | 0.0012008 | a = | 0.27179 | a = | 0.048198 | a = | -0.0087794 | a = | -0.020093 | a = | -0.039529
b = | 11.7843 | b = | 8.2545 | b = | 3964.4212 | b = | 1054.6673 | b = | 5.1239 | b = | 1.5929 | b = | 5004.7743 | b = | 1725.009 | b = | 157.8254 | b = | 120.1141 | b = | 6045.8958
c = | 4.0713 | c = | 3.7692 | c = | 14.3494 | c = | 10.8126 | c = | 4.3845 | c = | 6.8477 | c = | 282.7328 | c = | 222.6385 | c = | 4.5861 | c = | 4.384 | c = | 17.1227
d = | 1.3924 | d = | 1.4118 | d = | 1.405 | d = | 1.649 | d = | 1.671 | d = | 0.86615 | d = | 0.83445 | d = | 0.92602 | d = | 1.5845 | d = | 1.5679 | d = | 1.3553
Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log | Dose | log
| Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation |  | Inactivation
0 | -0.002479 | 0 | -0.027557 | 0 | -0.028948 | 0 | -0.011498 | 0 | 0.020396 | 0 | 0.0012008 | 0 | 0.27179 | 0 | 0.048198 | 0 | -0.0087794 | 0 | -0.020093 | 0 | -0.039529
1 | 0.31618 | 1 | 0.3827 | 5 | 0.0057672 | 5 | 0.1324 | 1 | 0.73303 | 1 | 2.6416 | 5 | 0.48782 | 5 | 0.61949 | 1 | 0.020151 | 1 | 0.016271 | 5 | -0.014422
2 | 0.7397 | 2 | 0.89794 | 10 | 0.062619 | 10 | 0.42734 | 2 | 1.6931 | 2 | 3.6548 | 10 | 0.65677 | 10 | 1.1312 | 2 | 0.076908 | 2 | 0.085997 | 10 | 0.024561
3 | 1.1443 | 3 | 1.353 | 15 | 0.13213 | 15 | 0.81309 | 3 | 2.422 | 3 | 4.2403 | 15 | 0.81147 | 15 | 1.6212 | 3 | 0.15143 | 3 | 0.17605 | 20 | 0.12349
4 | 1.5008 | 4 | 1.7253 | 20 | 0.21102 | 20 | 1.2551 | 4 | 2.9196 | 4 | 4.629 | 20 | 0.95754 | 20 | 2.0969 | 4 | 0.23897 | 4 | 0.28023 | 30 | 0.24095
6 | 2.063 | 6 | 2.2627 | 25 | 0.29737 | 25 | 1.7279 | 6 | 3.4933 | 6 | 5.1203 | 25 | 1.0975 | 25 | 2.5618 | 6 | 0.44041 | 6 | 0.51465 | 40 | 0.37148
8 | 2.4644 | 8 | 2.6123 | 30 | 0.38987 | 30 | 2.2126 | 8 | 3.7869 | 8 | 5.4219 | 30 | 1.2327 | 30 | 3.018 | 8 | 0.66194 | 8 | 0.76511 | 50 | 0.51196
10 | 2.7549 | 10 | 2.8492 | 40 | 0.5895 | 40 | 3.1663 | 10 | 3.9546 | 10 | 5.6279 | 40 | 1.4923 | 40 | 3.9088 | 10 | 0.89074 | 10 | 1.0166 | 60 | 0.66024
12 | 2.9703 | 12 | 3.0166 | 50 | 0.80404 | 50 | 4.0495 | 12 | 4.0591 | 12 | 5.7782 | 50 | 1.7408 | 50 | 4.7761 | 12 | 1.1181 | 12 | 1.26 | 70 | 0.81474
14 | 3.134 | 14 | 3.1393 | 60 | 1.0293 | 60 | 4.836 | 14 | 4.1286 | 14 | 5.8933 | 60 | 1.9807 | 60 | 5.6239 | 14 | 1.3385 | 14 | 1.4899 | 80 | 0.9742
16 | 3.2614 | 16 | 3.2323 | 70 | 1.2623 | 70 | 5.5217 | 16 | 4.1774 | 16 | 5.9843 | 70 | 2.2137 | 70 | 6.4548 | 16 | 1.5484 | 16 | 1.704 | 90 | 1.1376
18 | 3.3626 | 18 | 3.3044 | 80 | 1.5004 | 80 | 6.1134 | 18 | 4.2129 | 18 | 6.0584 | 80 | 2.4408 | 80 | 7.2706 | 18 | 1.7459 | 18 | 1.9011 | 100 | 1.3042
20 | 3.4444 | 20 | 3.3618 | 90 | 1.7417 | 90 | 6.6218 | 20 | 4.2397 | 20 | 6.1199 | 90 | 2.6629 | 90 | 8.073 | 20 | 1.9302 | 20 | 2.0815 | 125 | 1.7297
25 | 3.5922 | 25 | 3.463 | 100 | 1.9847 | 100 | 7.0583 | 25 | 4.2837 | 25 | 6.2364 | 100 | 2.8806 | 100 | 8.8628 | 25 | 2.3334 | 25 | 2.4651 | 150 | 2.1621
30 | 3.6895 | 30 | 3.5281 | 110 | 2.2279 | 110 | 7.4339 | 30 | 4.3098 | 30 | 6.3188 | 110 | 3.0944 | 110 | 9.6411 | 30 | 2.6619 | 30 | 2.7671 | 175 | 2.5951
35 | 3.7576 | 35 | 3.5728 | 120 | 2.4704 | 120 | 7.7581 | 35 | 4.3265 | 35 | 6.3804 | 120 | 3.3047 | 120 | 10.4085 | 35 | 2.9285 | 35 | 3.0056 | 200 | 3.0244
40 | 3.8074 | 40 | 3.6051 | 130 | 2.7112 | 130 | 8.039 | 40 | 4.338 | 40 | 6.4283 | 130 | 3.5118 | 130 | 11.1658 | 40 | 3.1455 | 40 | 3.1957 | 225 | 3.447
50 | 3.8745 | 50 | 3.648 | 140 | 2.9495 | 140 | 8.2835 | 50 | 4.3524 | 50 | 6.4983 | 140 | 3.7159 | 140 | 11.9135 | 50 | 3.4703 | 50 | 3.474 | 250 | 3.8605
60 | 3.9169 | 60 | 3.6748 | 150 | 3.185 | 150 | 8.4973 | 60 | 4.3608 | 60 | 6.5471 | 150 | 3.9174 | 150 | 12.6519 | 60 | 3.6961 | 60 | 3.6633 | 275 | 4.2635
70 | 3.9458 | 70 | 3.6929 | 160 | 3.4169 | 160 | 8.6851 | 70 | 4.3661 | 70 | 6.5832 | 160 | 4.1164 | 160 | 13.3816 | 70 | 3.8584 | 70 | 3.7974 | 300 | 4.6547
80 | 3.9666 | 80 | 3.7058 | 170 | 3.645 | 170 | 8.8508 | 80 | 4.3698 | 80 | 6.6111 | 170 | 4.313 | 170 | 14.103 | 80 | 3.9788 | 80 | 3.896 | 325 | 5.0336
100 | 3.994 | 100 | 3.7227 | 180 | 3.8689 | 180 | 8.9977 | 100 | 4.3744 | 100 | 6.6515 | 180 | 4.5075 | 180 | 14.8162 | 100 | 4.1422 | 100 | 4.0284 | 350 | 5.3998
120 | 4.0111 | 120 | 3.7331 | 190 | 4.0884 | 190 | 9.1284 | 120 | 4.377 | 120 | 6.6794 | 190 | 4.6999 | 190 | 15.5218 | 120 | 4.2454 | 120 | 4.1114 | 375 | 5.753
This worksheet provides equations for the UV dose-response of various pathogens. The data has been fitted to a mathematical function y=(a*b+c*x^d)/(b+x^d). The results of that fit can be used to define the UV dose-response of the pathogen in the worksheet RISKMODEL.