## Legend
Legend
| Sheets/Tabs |  | Cells
|  | General |  | Title
|  | Using for calculation |  | Heading
|  | Not Using for calculation |  | Outputs
| *Please change the color of the measure sheets you are using to Green or Yellow as described above. |  |  | Inputs
Optional Inputs
Constants
Notes

## Version Update Log (hidden)
# | Version | Sheet | Location | Update Notes | Old Formula | New Formula
1 | 4.06 | EC Motors (Custom) | F10:F34 | Load Factor no longer uses ratio of existing HP/proposed HP | IF(D10<=C10, 0.9, IF(D10<=1,0.9*(C10/D10),0.75*(C10/D10))) | IF(B10=0,"", IF(D10<=1, 0.9, 0.75))
2 | 4.06 | EC Motors (Custom) | I10:I34 | Upsizing rule implemented: Use Existing HP for Baseline HP & consumption formulas when the SOW upsizes the motor HP. | IF(D10="","", B10*D10*F10*0.746/H10) | IF(D10="","", B10*IF(D10>C10,C10,D10)*F10*0.746/H10)
3 | 4.06 | Summary of Savings | AR19:AS19 | Cool Roof Capping update: 0 Savings claimed for electric and gas | MIN(AM19,0) & MIN(AN19,'Baseline Cons.'!J18*0.01) | AM19*0 & AN19*0
4 | 4.06 | Boiler Clean & Tune (utility) | C6 & C9 | If DHW is heated by boiler use total annual Gas Usage, otherwise use Annual Space Heating Gas Usage | Row to be added & 'Baseline Cons.'!$D$18 | "Is DHW heated by the Space Heating Boiler?" Row Added & =IFERROR( IF($C$6="Yes",'Baseline Cons.'!$D$18, 'Baseline Cons.'!$D$22), "")
5 | 4.06 | Summary of Savings | AR9 | For capping, if DHW is heated by boiler use total annual Gas Usage, otherwise use Annual Space Heating Gas Usage | MIN(MAX(AM9,0),'Baseline Cons.'!$D$22*0.01) | MIN(MAX(AM9,0), IF('Boiler Clean & Tune (utility)'!$C$6="Yes",'Baseline Cons.'!$D$18,'Baseline Cons.'!$D$22)*0.01)
6 | 4.06 | Summary of Savings | AR23:AS23 | Removed "no negative savings summed" note | *ConEd Program Rule: Negative savings are not included in total savings | *Deleted*
7 | 4.06 | Summary of Savings | AG12, AI12:AJ12 | Now interative effects only apply when Air Sealing is selected as part of SOW | -T12 & -5% & -5% | IF(D12="Yes",-T12,"-") & IF(D12="Yes",-0.05,"-") & IF(D12="Yes",-0.05,"-")
8 | 4.07 | Roof & Wall Insulation (TRM) | all | Measure Added | N/A | N/A
9 | 4.07 | Boiler, Furnace, & Unit H (TRM) | all | Measure Added | N/A | N/A
10 | 4.07 | Wi-Fi Thermostats (TRM) | all | Measure Added | N/A | N/A
11 | 4.07 | Learning Thermostats (TRM) | all | Measure Added | N/A | N/A
12 | 4.07 | VFD & Motor (Custom) | all | Measure Added | N/A | N/A
13 | 4.07 | Refrigerators (TRM) | all | Measure Added | N/A | N/A
14 | 4.07 | Window Replacement (Custom) | all | Measure Added | N/A | N/A
15 | 4.07 | Storage Tank Water Heater (TRM) | all | Measure Added | N/A | N/A
16 | 4.07 | Smart TRE (TRM) | all | Measure Added | N/A | N/A
17 | 4.07 | Summary of Savings | Rows for new measures | Linking to respective measures Adding respective measure caps | BLANK | AS NEEDED
18 | 4.07 | Summary of Savings | Column C | Hyperlinking tabs to measure name | N/A | N/A
19 | 4.07 | Master Venting (ConEd Calc) | B63 | Renamed cell | Program Realized Savings (therms) (With interactivity) | Estimated Energy Savings (therms) (With interactivity)
20 | 4.08 | Summary of Savings | AR5:AS29 | Updated to Capping Rules to "AMEEP Comprehensive Measures List and Savings Cap_Ver 1" | Varies | Varies
21 | 4.09 | CA Steam Traps (TRM) | M5 | Updated formula to include F_hr (0.5) | IFERROR(B5*E5*L5*($G$5/'Building Info'!$C$24)*($H$5/100000)*K5, "") | IFERROR(B5*E5*L5*($G$5/'Building Info'!$C$24)*($H$5/100000)*0.5*K5, "")
22 | 4.09 | Master Venting (ConEd Calc) | K8:K14 G21, G34, G48 | Added table for Information Source Set data validation to list | N/A | N/A
23 | 4.09 | Summary of Savings | AT49 AS67:AT70 | Updated formula to incorperate points and incentive rate for Downstate NY Added table for Downstate NY points and incentive rate | 1500*'Building Info'!H11 | VLOOKUP($G$30,$AS$68:$AT$70,2,TRUE)*'Building Info'!H11
24 | 4.09 | CA Steam Traps (TRM) | Row 6-9 | Added more input rows | N/A | N/A
25 | 4.1 | All Sheets | As needed | Protected sheets | N/A | N/A
26 | 4.1 | Summary of Savings | A4:J4 | Added Filters | N/A | N/A
27 | 4.11 | Induction Stovetop (TRM) | all | Measure Added | N/A | N/A
28 | 4.11 | Summary of Savings | Row 24 | Enter formulas as needed to add "Induction Stovetop" measure | Varies | Varies
29 | 4.11 | Summary of Savings | L:S | Deleted legacy columns | N/A | N/A
30 | 4.11 | Summary of Savings | K:T | Grouped and Hidden by default. Can be unhidden in locked mode. | N/A | N/A
31 | 4.11 | Summary of Savings | U:AI | Grouped and Hidden by default. Can be unhidden in locked mode. | N/A | N/A
32 | 4.11 | Summary of Savings | 29 | Hidden Column | N/A | N/A
33 | 4.11 | Summary of Savings | G29 | Set Point for Cool Roof = 0 | IF(D29="yes",10,"-") | IF(D29="yes",0,"-")
34 | 4.11 | All ECM sheets | Varies | Added "Click to go to Summary of Savings" 2 cell right of the ECM Title. | [blank] | Click to go to Summary of Savings
35 | 4.11 | Summary of Savings | C34 | updated text | Click to go to measure | ↑ Click to go to measure ↑
36 | 4.11 | All ECM sheets | Sheet Name | removed () section indicating calculation type | N/A | N/A
37 | 4.11 | In-Unit Lighting | AG3:AG11 | Updated HVACff to TRM v10 | AS NEEDED | AS NEEDED
38 | 4.11 | In-Unit Lighting | Columns V | updated to include "/10" to compensate for TRM v10 update towards MMBtu. | IF(P5="","--",(Q5-R5)*T5) | IF(P5="","--",(Q5-R5)*T5/10)
39 | 4.11 | In-Unit Lighting | Columns I, O | filled gray and locked
40 | 4.11 | In-Unit Lighting | Columns J, P | updated formula, filled gray and locked | 1752/8760*24 | IF(E5>0, 1752/8760*24,"")
41 | 4.11 | Boiler, Furnace, & Unit H | B3:C5 | Deleted "Building Year" & "Building Rise" Updated Heating EFLH formula | [blank] | IFERROR(IF(OR('Building Info'!$C$9="", 'Building Info'!$C$10=""),"", INDEX($AF$20:$AG$23,MATCH('Building Info'!$C$9,$AD$20:$AD$23,1),MATCH('Building Info'!$C$10, $AF$18:$AG$18,1)) ),"")
42 | 4.11 | Boiler, Furnace, & Unit H | AF17:AG18 | Added Look up values for Building Rise | [blank] | Varies
43 | 4.11 | CA Pipe Insulation | N/A | Renamed to "Pipe Insulation (OLD)" changed tab color to Red and hid | N/A | N/A
44 | 4.11 | Pipe Insulation | all | Measure Added | N/A | N/A
45 | 4.11 | Summary of Savings | L21, M21, AE21, AF21 | updated formulas to reference new "Pipe Insulation" Sheet | Varies | Varies
46 | 4.11 | Common Area Lighting | Rows 6-28, 45-64 | added input rows | N/A | N/A
47 | 4.11 | Boiler, Furnace, & Unit H | B3:C4, AD27:AD29 | Added "Gas Provider" Input | Varies | Varies
48 | 4.11 | Boiler, Furnace, & Unit H | AI39:AO58 | Added NG efficiency table | N/A | N/A
49 | 4.11 | Boiler, Furnace, & Unit H | L7:L11 | updated formula to lookup CE/NG based efficiency tables | IF([@[Replacement Heating Equipment Size (MBH)]]="","", VLOOKUP(CONCAT([@[Heating Equipment Type]],[@[Equipment Size Range]]),'Boiler, Furnace, & Unit H'!$AL$19:$AM$36,2,FALSE)) | IFERROR(IFS([@[Replacement Heating Equipment Size (MBH)]]="","", [@[Custom Baseline Efficiency]]<>"", [@[Custom Baseline Efficiency]], 1=1, VLOOKUP(CONCAT([@[Heating Equipment Type]],[@[Equipment Size Range]]), IFS($C$3="ConEd", $AL$20:$AM$37, $C$3="National Grid", $AL$40:$AM$58),2,FALSE)),"")
50 | 4.11 | EMS Controls | C8 | Change from input to output | dropdown: 0, 0.1 | IF('Summary of Savings'!$D$19="Yes", 0.1, 0)
51 | 4.11 | EMS Controls | G25:J34, L15:L17 | added EFLH Table for National Grid | Varies | Varies
52 | 4.11 | Utility Data | All | updated to use up to 3 years of data added charts | Varies | Varies
53 | 4.11 | Building Info | Headings | reformat text, fill | N/A | N/A
54 | 4.11 | Orifice Plates | All | Measure Added | N/A | N/A
55 | 4.11 | Summary of Savings | Row 16 | Enter formulas as needed to add "Orifice Plates" measure | Varies | Varies
56 | 1 | Workbook | Title | Renamed to "Downstate Calculator_vDRAFT 1.0" Final version will be named "Downstate Calculator_v2.0" | N/A | N/A
57 | 1.2 | Roof & Wall Insulation | B4:B13 | Corrected Data Validation list to use Floor list | N/A | N/A
58 | 1.2 | Roof & Wall Insulation | G4:G13 | Corrected Data Validation to Decimal, >=0, <=1 | N/A | N/A
59 | 1.2 | Roof & Wall Insulation | Q4:R13 | Corrected Data Validation to Whole Number, >=0, <=100 | N/A | N/A
60 | 1.2 | Roof & Wall Insulation | F1 | Corrected "Click to go to Summary of Savings" link | N/A | N/A
61 | 1.2 | Summary of Savings | AK6 | Corrected CA Lighting Cap from 95% to 45% | AF6*0.95 | AF6*0.45
62 | 1.2 | Master Venting | multiples section | Rearranged input cells | N/A | N/A
63 | 1.2 | Steam Traps | Row 9-26 | More input rows added | N/A | N/A
64 | 1.2 | Steam Traps | L29:M30 | Summation cells added | N/A | N/A
65 | 1.2 | Central DHW Control | Columns F, G | Effpump was moved right of Tset and made a output formula | [blank] | IFERROR( VLOOKUP(B4,$Z$4:$AA$6,2,FALSE), "")
66 | 1.2 | EMS Controls | B5:D5 | Added input "Is DHW heated by the Space Heating Boiler?" | N/A | N/A
67 | 1.2 | EMS Controls | C6 | Updated Baseline formula to use Total Gas Usage or Space Heating Usage based on the above input. | Utility Data'!$K$47 | IFERROR(IF( C5="Yes", 'Utility Data'!$K$47, 'Utility Data'!$C$8), "")
68 | 1.2 | EC Motors | Sheet Name | Renamed Sheet "EC Motors (OLD)". Changed Tab Color to Red. Hid. | N/A | N/A
69 | 1.2 | EC Motors | All | Measure Added from ConEd Tool | N/A | N/A
70 | 1.2 | Summary of Savings | D5 M9, AF9 | Updated Link Updated Formula to reference new sheet | N/A 'EC Motors (OLD)'!P34 | N/A 'EC Motors'!AK105
71 | 1.2 | Window Film | Column A | Added a row "#" column | N/A | N/A
72 | 1.2 | Window Film | Column D | Added "Window Type" input | N/A | N/A
73 | 1.2 | Window Film | Columns G, H | Switched "SHGCee" & "Window Area (ft2)" Entered formula and changed to output for "Window Area (ft2)" | [blank] | IFERROR(IF(C5="","", E5*F5 ),"")
74 | 1.2 | Window Film | Columns U-AC | Added tables for Window Film constants and Window Type list | Various Constants | IFERROR(IF($C5="","", INDEX(IFS($D5=$W$29, $X$31:$AC$35, $D5=$W$37, $X$39:$AC$43), MATCH($H$1, $W$31:$W$35, 0), MATCH(I$4, $I$4:$N$4, 0)) ),"")
75 | 1.2 | Window Film | Columns I-N | Updated constant values to formula
76 | 1.2 | Window Film | Columns O-Q | Updated formulas with IFERROR | Varies | Varies
77 | 1.2 | Summary of Savings | AJ21 | Updated Cap from 5% of Total Therms usage to % of Space Heating usage | IFERROR(MIN(AE21,'Utility Data'!$K$47*0.05),"-") | IFERROR(MIN(AE21,'Utility Data'!$C$8*0.05),"-")
78 | 1.2 | Steam Traps | Column M | updated formula to use "Post-Inspection type" | IFERROR(B4*E4*L4*($G$4/'Building Info'!$C$24)*($H$4/100000)*0.5*K4), "") | IFERROR(B4*E4*L4*($G$4/'Building Info'!$C$24)*($H$4/100000)*0.5*K4 *VLOOKUP($K$1,$AI$5:$AJ$6,2,FALSE), "")
79 | 1.2 | Steam Traps | Column N | updated formula to use "Post-Inspection type" | IFERROR(B4*E4*L4*(G4/('Building Info'!$C$24+'Summary of Savings'!$V$32))*(I4/100000)*0.5*K4, "") | IFERROR(B4*E4*L4*(G4/('Building Info'!$C$24+'Summary of Savings'!$V$32))*(I4/100000)*0.5*K4 *VLOOKUP($K$1,$AI$5:$AJ$6,2,FALSE), "")
80 | 1.2 | Steam Traps | J1:K1 AI4:AJ6 | Added Post-Inspection type Added Post-Inspection type table | N/A | N/A
81 | 1.2 | Pipe Insulation Building Info | E1:F1 B28:C28 | Moved "Gas Provider" input to Building Info and renamed it to "Gas Utilty" | N/A | N/A
82 | 1.2 | Building Info | B27:C27 | Added "Electric Utilty" input | N/A | N/A
83 | 1.2 | Roof & Wall Insulation | Y21:AB24, BK26:BP35 | Added Capping for National Grid and ConEd based on Roof/Wall & Building Rise | N/A | N/A
84 | 1.2 | Summary of Savings | AJ29 | Updated "Roof & Wall Insulation" therms savings cap | IF(IFERROR(VLOOKUP("Wall",Table_Buildingenvelope[Wall or Roof],1,FALSE),0)="Wall", MIN(0.3*'Utility Data'!$C$8,AE29), MIN(0.1*'Utility Data'!$K$47,AE29)) | IFERROR('Roof & Wall Insulation'!$AA$24, 0)
85 | 1.2 | Summary of Savings | AJ31 | Updated "Window Replacement" therms savings cap for National Grid vs ConEd | IF(ISNUMBER(FIND("single",'Window Replacement'!$H$10)), 0.15, 0.05) * 'Utility Data'!$C$8 | IFERROR(MIN(AE31, IFS('Building Info'!$C$28="National Grid", 0.05 * 'Utility Data'!$K$47, 'Building Info'!$C$28="ConEd", IF(ISNUMBER(FIND("single",'Window Replacement'!$H$10)), 0.15, 0.05) * 'Utility Data'!$C$8) ),"-")
86 | 1.2 | Summary of Savings | AJ14 | Updated "Air Sealing" therms savings cap for National Grid vs ConEd | AE14*0.3 | IFERROR( IFS('Building Info'!$C$28="National Grid", MIN(AE14, 0.01 * 'Utility Data'!$K$47), 'Building Info'!$C$28="ConEd", AE14*0.3),"-")
87 | 1.3 | Smart TRE | K5 | updated formula from "" to 0 to avoid Final Savings Errors | IFERROR(IF(A5=0, 0, ($AC$9*E5+$AD$9)*C5)*10, 0) | IFERROR(IF(A5=0,"", ($AC$9*E5+$AD$9)*C5)*10,"")
88 | 1.3 | Smart TRE | M5 | updated formula from "" to 0 to avoid Final Savings Errors | IFERROR(IF(A5=0, 0, ($AC$9*I5+$AD$9)*H5)*10, 0) | IFERROR(IF(A5=0,"", ($AC$9*I5+$AD$9)*H5)*10,"")
89 | 1.3 | Master Venting | D47 | updated formula from "" to 0 to avoid Final Savings Errors | IFERROR('Master Venting'!F107/100*('Master Venting'!BG80-'Master Venting'!BI80), 0) | IFERROR('Master Venting'!F107/100*('Master Venting'!BG80-'Master Venting'!BI80),"")
90 | 1.3 | Master Venting | D45 | updated formula from "" to 0 to avoid Final Savings Errors | IFERROR('Master Venting'!F107/100*('Master Venting'!BG81-'Master Venting'!BI81),"") | IFERROR('Master Venting'!F107/100*('Master Venting'!BG81-'Master Venting'!BI81), 0)
91 | 1.3 | EC Motors | Columns L, Z | Set Format to Fraction | N/A | N/A
92 | 1.3 | Pipe Insulation | BE112:BU114 | Corrected Minimum Insulation Thickness Table Values | N/A | N/A
93 | 1.3 | Summary of Savings | B2 | Added Version # | [blank] | vDraft 1.3
94 | 1.3 | Steam Traps | B3 | Renamed header to remove "Common Area" | # of Common Area Steam Traps | # of Steam Traps
95 | 2 | Roof & Wall Insulation | Column G | Added Input Message "Enter in decimal format. Example: 0.80" | N/A | N/A
96 | 2 | EC Motors | Column R | Updated lookup formula | IF(E5=0,"",IF(I5="Yes",0.6,INDEX('EC Motors'!$BR$139:$BV$165,MATCH('EC Motors'!L5,'EC Motors'!$BR$140:$BR$165,0),MATCH('EC Motors'!P5,'EC Motors'!$BS$139:$BV$139,0)+1))) | IF(E5=0,"",IF(I5="Yes",0.6,INDEX(BS140:BV165,MATCH('EC Motors'!L5,'EC Motors'!$BR$140:$BR$165,-1),MATCH('EC Motors'!P5,'EC Motors'!$BS$139:$BV$139,-1))))
97 | 2 | EC Motors | Column AC | Updated lookup formula | IF(E5=0,"",INDEX('EC Motors'!$BR$139:$BV$165,MATCH('EC Motors'!Z5,'EC Motors'!$BR$140:$BR$165,0),MATCH('EC Motors'!AB5,'EC Motors'!$BS$139:$BV$139,0)+1)) | IF(E5=0,"",INDEX($BS$140:$BV$165,MATCH('EC Motors'!Z5,'EC Motors'!$BR$140:$BR$165,-1),MATCH('EC Motors'!AB5,'EC Motors'!$BS$139:$BV$139,-1)))
98 | 2 | EC Motors | Column BY | Added updated Motor HP list | N/A | N/A
99 | 2 | EC Motors | BM136, BH4 | Moved Error Box | N/A | N/A
100 | 2 | Summary of Savings | B2 | Updated Version # | vDraft 1.3 | v2.0
101 | 2.0.1 | Utility Data | Rows 14, 16-27, 33, 35-46 | Unlocked Input Cells | N/A | N/A
102 | 2.0.1 | Building Info | C27:C28 | Unlocked Input Cells | N/A | N/A
103 | 2.0.1 | In-Unit Lighting |  | Renamed cell, removed "(Low-Rise Only)" | (Low-Rise Only) HVAC Type: | HVAC Type:
104 | 2.0.1 | Summary of Savings | G15:G16, G18, G21:G22 | Updated points based on NYS AMEEP Manual v2.3 (Oct 2023) | Varies | Varies
105 | 2.0.2 | EC Motors | G20 | Entered missing formula | N/A | N/A
106 | 2.0.2 | Building Info | C24 | Changed format to ##.##% | N/A | N/A
107 | 2.0.2 | Boiler Clean & Tune | C10:C11 | Updated Data Validation to decimal between 0 & 1 Changed format to ##.##% | N/A | N/A
108 | 2.0.2 | Air Sealing | F4:F13 | Updated from input to autopopulate | Building Info'!$C$12/'Building Info'!$C$10 | IFERROR( 'Building Info'!$C$12/'Building Info'!$C$10/(COUNTIF($B$4:$B$28,B4)),"")
109 | 2.0.2 | Air Sealing | Row 14-28 | Added input rows | N/A | N/A
110 | 2.0.2 | Boiler, Furnace, & Unit H | C3 | Updated from input to autopopulate | [blank] | IF('Building Info'!$C$28="","", 'Building Info'!$C$28)
111 | 2.0.2 | Steam Traps | Column B | Added Location input
112 | 2.0.2 | EC Motors | Column D | Added Location input
113 | 2.0.2 | VFD + Motor | Column B | Added Location input
114 | 2.0.2 | Induction Stovetop | Column A | Added Location input
115 | 2.0.2 | Window Film | Column B | Added Location input
116 | 2.0.2 | Pipe Insulation | E4 | Renamed Column Header | Pipe Type | Pipe Material
117 | 2.0.3 | Low Flow A&S | C16, G16 | Updated GPM_baseline based on TRM v11 | IF(G6="Non Lavatory",2.2,1.5) | IF(G6="Non Lavatory",1.5, 1)
118 | 2.0.3 | Low Flow A&S | K15 | Updated GPM_baseline based on TRM v11 | IF(K6="Yes", 2.5,2) | IF(K6="Yes", 2.5, 1.8)
119 | 2.0.3 | Low Flow A&S | Column AB:AY | Moved tables lower | N/A | N/A
120 | 2.0.3 | Pipe Insulation | AJ111:AM126 | Added CPVPC/PEX UA/L_baseline data based on TRM v11 | N/A | N/A
121 | 2.0.3 | Pipe Insulation | AF142:AF143 | Added CPVP/PEX options | N/A | N/A
122 | 2.0.3 | Pipe Insulation | Column E | Updated Data Validation to include CPVP/PEX pipe | N/A | N/A
123 | 2.0.3 | Pipe Insulation | AO114:AZ126 | Updated UA/L_ee based on TRM v11 | N/A | N/A
124 | 2.0.4 | Summary of Savings | C27:C28 | Renamed Measure | Learning Thermostats | Connected Thermostat
125 | 2.0.4 | Connected Thermostat | A1, Title | Renamed Measure | Learning Thermostats | Connected Thermostat
126 | 2.0.4 | Connected Thermostat | AB43:AD43 | Updated Fuel Factors based on TRM v11 | N/A | N/A
127 | 2.0.4 | Wi-Fi Thermostats | All | Locked all cells. Update Tab color to red and Hid. | N/A | N/A
128 | 2.0.4 | Summary of Savings | Row 26 | Hid Row for Wifi Thermostats | N/A | N/A
129 | 2.0.5 | Roof & Wall Insulation | CG20:CH21 | Added Rim Joist & Floor F_Framing | N/A | N/A
130 | 2.0.5 | Roof & Wall Insulation | Column O | Updated Data Validation dropdown list to include Rim Joist & Floor | N/A | N/A
131 | 2.0.5 | Roof & Wall Insulation | O3 | Renamed Header to "Envelope Type" | Roof or Wall | Envelope Type
132 | 2.0.5 | Roof & Wall Insulation | BS17:BT21 | Added Rim Joist & Floor Baseline R values | N/A | N/A
133 | 2.0.5 | Roof & Wall Insulation | Column Q CM17:CM20 | Added Existing Insulation Quality | N/A | N/A
134 | 2.0.5 | Roof & Wall Insulation | Column P CN17:CN20 | Added Replacement Type | N/A | N/A
135 | 2.0.5 | Roof & Wall Insulation | S3 | Renamed Header | Existing R | Existing R Value
136 | 2.0.5 | Roof & Wall Insulation | T3 | Renamed Header | Insulation Type Added | R Value Added
137 | 2.0.5 | Roof & Wall Insulation | Column U | Added autopopulated column for Existing R_Baseline, 1 | N/A | N/A
138 | 2.0.6 | Roof & Wall Insulation | Column V | Added autopopulated column for R_Baseline, 2 | N/A | N/A
139 | 2.0.6 | Roof & Wall Insulation | Column W | Updated "Therms Savings" Formula to use "Existing R Value_Derated" and "R_Baseline, 2" instead of "Existing R Value". | IFERROR(((1/[@[Existing R Value]]-1/([@[Existing R Value]]+[@[R Value Added]]))*[@[Area (sft)]] *(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP([@[HVAC System Type]],'Roof & Wall Insulation'!$DN$55:$DX$61,9,FALSE)) /(100000*[@[Gas Equipment Efficiency]]),"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]] *(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP([@[HVAC System Type]],'Roof & Wall Insulation'!$DN$55:$DX$61,9,FALSE)) /(100000*[@[Gas Equipment Efficiency]]),"")
140 | 2.0.6 | Roof & Wall Insulation | Column X | Updated "Heating kWh Savings" Formula to use "Existing R Value_Derated" and "R_Baseline, 2" instead of "Existing R Value". | IFERROR(((1/[@[Existing R Value]]-1/([@[Existing R Value]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,11,FALSE)) /(1000*[@[Electric Heating Equipment HSPF]]),"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,11,FALSE)) /(1000*[@[Electric Heating Equipment HSPF]]),"")
141 | 2.0.6 | Roof & Wall Insulation | Column Y | Updated "Cooling kWh Savings" Formula to use "Existing R Value_Derated" and "R_Baseline, 2" instead of "Existing R Value". | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$21*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,10,FALSE)) /(1000*[@[Cooling Equipment SEER]]),"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$21*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,10,FALSE)) /(1000*[@[Cooling Equipment SEER]]),"")
142 | 2.0.6 | Roof & Wall Insulation | Column AD | Updated "Therms Savings_Interactive" Formula to use "Existing R Value_Derated" and "R_Baseline, 2" instead of "Existing R Value". | IFERROR(((1/[@[Existing R Value]]-1/([@[Existing R Value]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP([@[HVAC System Type]],'Roof & Wall Insulation'!$DN$55:$DX$61,9,FALSE)) /(100000*[@[Gas Equipment Efficiency_Interactive]]),"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP([@[HVAC System Type]],'Roof & Wall Insulation'!$DN$55:$DX$61,9,FALSE)) /(100000*[@[Gas Equipment Efficiency_Interactive]]),"")
143 | 2.0.6 | Roof & Wall Insulation | Column AE | Updated "Heating kWh Savings_Interactive" Formula to use "Existing R Value_Derated" and "R_Baseline, 2" instead of "Existing R Value". | IFERROR(((1/[@[Existing R Value]]-1/([@[Existing R Value]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,11,FALSE)) /(1000*[@[Electric Heating Equipment HSPF_Interactive]]),"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$18*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,11,FALSE)) /(1000*[@[Electric Heating Equipment HSPF_Interactive]]),"")
144 | 2.0.6 | Roof & Wall Insulation | Column AF | Updated "Cooling kWh Savings_Interactive" Formula to use "Existing R Value_Derated" and "R_Baseline, 2" instead of "Existing R Value". | IFERROR(((1/[@[Existing R Value]]-1/([@[Existing R Value]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$21*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,10,FALSE)) /(1000*[@[Cooling Equipment SEER_Interactive]]),"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*'Roof & Wall Insulation'!$BT$21*24*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,10,FALSE)) /(1000*[@[Cooling Equipment SEER_Interactive]]),"")
145 | 2.0.6 | Roof & Wall Insulation | Column BT:BU | Added Cooling EFLH Table | N/A | N/A
146 | 2.0.6 | Roof & Wall Insulation | Column AA | Updated "kW Savings" Formula based on TRM V11. | IFERROR(((1/[@[Existing R Value]]-1/([@[Existing R Value]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CQ$18:$CR$21,2,FALSE))*VLOOKUP(D4,'Roof & Wall Insulation'!$DN$55:$DX$61,10,FALSE)) /(1000*[@[Cooling Equipment EER]])*'Roof & Wall Insulation'!$BT$24,"") | IFERROR([@[Cooling kWh Saving]]/ INDEX($BU$18:$BV$21, MATCH('Building Info'!$C$9, $BQ$18:$BQ$21,1), MATCH('Building Info'!$C$10, $BO$18:$BO$19, 1)) *$BW$24,"")
147 | 2.0.6 | Roof & Wall Insulation | Column AH | Updated "kW Savings_Interactive" Formula based on TRM V11. | IFERROR([@[Cooling kWh Saving]]/ INDEX($BU$18:$BV$21, MATCH('Building Info'!$C$9, $BQ$18:$BQ$21,1), MATCH('Building Info'!$C$10, $BO$18:$BO$19, 1)) *$BW$24,"") | IFERROR(((1/[@[Existing R ValueDerated]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]]*(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CT$18:$CU$21,2,FALSE))*VLOOKUP(D4,'Roof & Wall Insulation'!$DQ$55:$EA$61,10,FALSE)) /(1000*[@[Cooling Equipment EER]])*'Roof & Wall Insulation'!$BW$24,"")
148 | 2.0.6 | Roof & Wall Insulation | U3 | Added Note | [blank] | Existing R Value_Derated
149 | 2.0.6 | Roof & Wall Insulation | V3 | Added Note | [blank] | Only different from R_Baseline, 1 when Replacement Type = "Existing Insulation - Replacing Insulation"
150 | 2.0.6 | Roof & Wall Insulation | DC:DH | Updated TRM information Deleted TRM Snapshots | N/A | N/A
151 | 2.0.6 | Roof & Wall Insulation | AC3, AI3 | Add text "Net" | N/A | N/A
152 | 2.0.6 | Roof & Wall Insulation | AD22 | Updated formula to include "Rim Joist" | IFERROR(SUMIF(Table_Buildingenvelope[Envelope Type], CT18, Table_Buildingenvelope[Therm Saving_Interactive]), 0) | IFERROR(SUMIF(Table_Buildingenvelope[Envelope Type], $CT$18, Table_Buildingenvelope[Therm Saving_Interactive]) +SUMIF(Table_Buildingenvelope[Envelope Type], $CT$20, Table_Buildingenvelope[Therm Saving_Interactive]), 0)
153 | 2.0.6 | Roof & Wall Insulation | AD23 | Updated formula to include "Floor" | IFERROR(SUMIF(Table_Buildingenvelope[Envelope Type], CT21, Table_Buildingenvelope[Therm Saving_Interactive]), 0) | IFERROR(SUMIF(Table_Buildingenvelope[Envelope Type], $CT$19, Table_Buildingenvelope[Therm Saving_Interactive]) +SUMIF(Table_Buildingenvelope[Envelope Type], $CT$21, Table_Buildingenvelope[Therm Saving_Interactive]), 0)
154 | 2.0.6 | Roof & Wall Insulation | AC | Updated formula to be blank when 0 | IFERROR(IF([@[kWh Saving]]="",0,[@[kWh Saving]]*0.003412) + IF([@[Therm Saving]]="",0,[@[Therm Saving]]*0.1),"") | IFERROR(IF(AND([@[kWh Saving]]="",[@[Therm Saving]]=""),"", IF([@[kWh Saving]]="",0,[@[kWh Saving]]*0.003412) + IF([@[Therm Saving]]="",0,[@[Therm Saving]]*0.1)),"")
155 | 2.0.6 | Roof & Wall Insulation | AI | Updated formula to be blank when 0 | IFERROR(IF([@[kWh Saving_Interactive]]="",0,[@[kWh Saving_Interactive]]*0.003412) + IF([@[Therm Saving_Interactive]]="",0,[@[Therm Saving_Interactive]]*0.1),"") | IFERROR(IF(AND([@[kWh Saving_Interactive]]="",[@[Therm Saving_Interactive]]=""),"", IF([@[kWh Saving_Interactive]]="",0,[@[kWh Saving_Interactive]]*0.003412) + IF([@[Therm Saving_Interactive]]="",0,[@[Therm Saving_Interactive]]*0.1)),"")
156 | 2.0.7 | Summary of Savings | AK10 | Added Capping Note | [blank] | for chilled water pump serving absorption chiller, check with manufacture if variable flow rate is allowed.
157 | 2.0.7 | Storage Tank Water Heater | Column G | Added Input Message | [blank] | For Condensing Water Heaters: Condensing boiler efficiency must be the Efficiency at return temperatures >140F. Must NOT use highest efficiency.
158 | 2.0.7 | Summary of Savings | AJ22 | Updated Pipe Insulation Cap | IFERROR(MIN(AE22*0.75, 'Utility Data'!$C$8*0.02),"-") | IFERROR(MIN(AE22*0.75, IF(IFERROR(FIND("Heating",CONCAT('Pipe Insulation'!$C$5:$C$105)),0) >0, 0.02* 'Utility Data'!$C$8, 0) + IF(IFERROR(FIND("DHW",CONCAT('Pipe Insulation'!$C$5:$C$105)),0) >0, 0.02* 'Utility Data'!$C$7, 0) ),"-")
159 | 2.0.7 | Summary of Savings | AK28 | Updated Connected Thermostat kWh Cap | AF27 | AF27*0.5
160 | 2.0.7 | Summary of Savings | AJ31 | replace FIND with SEARCH, SEARCH is not case sensitive | IFERROR(MIN(AE31, IFS('Building Info'!$C$28="National Grid", 0.05 * 'Utility Data'!$K$47, 'Building Info'!$C$28="ConEd", IF(ISNUMBER(FIND("single",'Window Replacement'!$H$10)), 0.15, 0.05) * 'Utility Data'!$C$8) ),"-") | IFERROR(MIN(AE31, IFS('Building Info'!$C$28="National Grid", 0.05 * 'Utility Data'!$K$47, 'Building Info'!$C$28="ConEd", IF(ISNUMBER(SEARCH("single",'Window Replacement'!$H$10)), 0.15, 0.05) * 'Utility Data'!$C$8) ),"-")
161 | 2.0.7 | Summary of Savings | AK31 | replace FIND with SEARCH, SEARCH is not case sensitive | MIN(AF31, IF(ISNUMBER(FIND("single",'Window Replacement'!$H$10)), 0.1, 0.02) * 'Utility Data'!$N$28) | MIN(AF31, IF(ISNUMBER(SEARCH("single",'Window Replacement'!$H$10)), 0.1, 0.02) * 'Utility Data'!$N$28)
162 | 2.0.7 | Summary of Savings | AJ:AK | Confirmed Savings Caps Align with ConEd "AMEEP Comprehensive Measures List and Savings Cap_Ver 1". | N/A | N/A
163 | 2.0.7 | Summary of Savings | Column AJ | Confirmed Savings Caps Align with National Grid Capping requirements. | N/A | N/A
164 | 2.0.7 | Calculation Notes | Column H | Added Capping column | N/A | N/A
165 | 2.0.7 | Storage Tank Water Heater | Column P CN17:CN20 | Updated GPD per dwelling unit from 46 to 34.4 based on NYS TRM V11. | A4*46 | A4*34.4
166 | 2.0.7 | Storage Tank Water Heater | Rows 6:8 | Added input rows | N/A | N/A
167 | 2.0.7 | Pipe Insulation | Column N | Updated Formula to include CPVC and PEX Pipe Material | IFERROR(IF(B5="","", INDEX($AD$114:$AI$130,MATCH(F5,$AC$114:$AC$130,0),MATCH(CONCATENATE(E5,C5),$AD$113:$AI$113,0)) ),"") | IFERROR(IF(B5="","", INDEX($AD$114:$AM$130,MATCH(F5,$AC$114:$AC$130,0),MATCH(CONCATENATE(E5,C5),$AD$113:$AM$113,0)) ),"")
168 | 2.0.8 | Common Area Lighting | Column I | Corrected kWh Savings Formula | IFERROR(B4*(C4-D4)/1000*E4*(1-F4),"") | IFERROR(B4*(C4-D4)/1000*E4*(1+F4),"")
169 | 2.0.8 | Common Area Lighting | Column J | Corrected kW Savings Formula | IFERROR(B4*(C4-D4)/1000*E4*(1+G4)*H4,"") | IFERROR(B4*(C4-D4)/1000*(1+G4)*H4,"")
170 | 2.0.8 | Common Area Lighting | Rows 34:59 | Updated Prescriptive Tool table input columns | N/A | N/A
171 | 2.0.8 | Common Area Lighting | Columns B:E | Updated mapping since input columns have moved Colored for Optional Input Added Input Message | N/A N/A N/A | N/A N/A Recommended: Enter SOW information on Prescriptive CA Tool's Lighting Measure Table. Then, Copy & Paste Value the inputs and outputs below.
172 | 2.0.8 | Common Area Lighting | Column H | Converted CF into a output column | 0 | IFERROR( IFS(E35="Interior", 0.98, E35="Exterior", 0.000001, 1=1, ""),"")
173 | 2.0.8 | Common Area Lighting | BC66:BF74 | Added HVAC Interactive Effects Coefficients Table | N/A | N/A
174 | 2.0.8 | Common Area Lighting | H3:H29 | Added Column for HVAC_ff | N/A | IFERROR(IF(B4=0, "", VLOOKUP($H$1,$BC$68:$BF$74, 4, FALSE)), "")
175 | 2.0.8 | Common Area Lighting | Column F | Converted HVAC_c into a output column | 0 | IFERROR(IF(B4=0, "", VLOOKUP($H$1,$BC$68:$BF$74, 2, FALSE)), "")
176 | 2.0.8 | Common Area Lighting | Column G | Converted HVAC_d into a output column | 0 | IFERROR(IF(B4=0, "", VLOOKUP($H$1,$BC$68:$BF$74, 3, FALSE)), "")
177 | 2.0.8 | Common Area Lighting | Column L | Added Column for Therms Savings | N/A | IFERROR(B4*(C4-D4)/1000*E4*H4*10,"")
178 | 2.0.8 | Common Area Lighting | F1:J1 | Added HVAC Type Input | N/A | N/A
179 | 2.0.8 | Summary of Savings | L6 | Updated Formula | - | Common Area Lighting'!L29
180 | 2.0.8 | Summary of Savings | AE6 | Updated Formula | - | Common Area Lighting'!L29
181 | 2.0.8 | Summary of Savings | AJ6 | Updated Formula | - | AE6*0.45
182 | 2.0.8 | In-Unit Lighting | AD3:AG11 | Updated HVAC Interactive Effects Coefficients Table based on NYS TRM V11 | N/A | N/A
183 | 2.0.8 | In-Unit Lighting | AD113 | Moved HVAC Interactive Effects Coefficients Table | N/A | N/A
184 | 2.0.8 | In-Unit Lighting | J1 | Updated Data Validation list | N/A | N/A
185 | 2.0.8 | In-Unit Lighting | Column T | Added HVAC_d column | N/A | IFERROR(IF($E5=0, "", 1 + VLOOKUP($J$1,$AF$114:$AI$120,3,FALSE)), "")
186 | 2.0.8 | In-Unit Lighting | Column W | Added Peak kW Savings column | N/A | IFERROR(IF($E5=0, "", (I5-O5)/1000*T5*$AL$114), "")
187 | 2.0.8 | In-Unit Lighting | Column S | Updated Formula | 1 + VLOOKUP($J$1,$AF$3:$AI$11,2,FALSE) | IFERROR(IF($E5=0, "", 1 + VLOOKUP($J$1,$AF$114:$AI$120,2,FALSE)), "")
188 | 2.0.8 | In-Unit Lighting | Column U | Updated Formula | VLOOKUP($J$1,$AF$3:$AI$11,4,FALSE) | IFERROR(IF($E5=0, "", VLOOKUP($J$1,$AF$114:$AI$120,4,FALSE)), "")
189 | 2.0.8 | In-Unit Lighting | Column K | Colored as Optional Input | N/A | N/A
190 | 2.0.8 | In-Unit Lighting | Column X | Corrected Therms Savings Formula | IF(P5="","--",(Q5-R5)*U5/10) | IF(P5="","--",(Q5-R5)*U5*10)
191 | 2.0.8 | In-Unit Lighting | Columns I, J, K, O, P, Q, R, V, X | Update formula from "--" to "" and add IFERROR() | N/A | N/A
192 | 2.0.8 | In-Unit Lighting | Z8:Z9 | Added Total kW Savings Output | N/A | N/A
193 | 2.0.9 | Summary of Savings | AA32 | Capped maximum decrease of EFLH at 5% | SUM(AA5:AA31) | IF(SUM(AA5:AA31) <= (-0.05), (-0.05), SUM(AA5:AA31))
194 | 2.0.9 | Summary of Savings | AB32 | Capped maximum decrease of EFLH at 5% | SUM(AB5:AB31) | IF(SUM(AB5:AB31) <= (-0.05), (-0.05), SUM(AB5:AB31))
195 | 2.0.9 | Summary of Savings | Column N | Added Column for Willdan kW Savings | N/A | N/A
196 | 2.0.9 | Summary of Savings | Column AH | Added Column for kW Savings | N/A | N/A
197 | 2.0.9 | Summary of Savings | Column AK | Added Column for ΔkW Savings | N/A | IFERROR((AH5-N5)/N5,"-")
198 | 2.0.9 | Summary of Savings | Column AO | Added Column for kW Savings | N/A | AH5
199 | 2.0.9 | Summary of Savings | Column AT | Added Column for ΔkW Savings | N/A | IFERROR((AO5-AH5)/AH5,"-")
200 | 2.0.9 | Refrigerators | Column I | Added column for HVAC_d | N/A | VLOOKUP($B$5,$AC$19:$AF$25,3,FALSE)
201 | 2.0.9 | Refrigerators | Column L | Added column for Peak kW Savings | N/A | IFERROR( A8*(E8-F8)/8760*(1+I8)*$AG$29,"")
202 | 2.0.9 | Refrigerators | AC17:AD27, AC41:AG48 | Removed old App. D tables | N/A | N/A
203 | 2.0.9 | Refrigerators | AC17:AF25 | Added new App. D table | N/A | N/A
204 | 2.0.9 | Refrigerators | Column H | Updated formula to use new App. D table | VLOOKUP(B5,AD42:AG48,2,FALSE) | VLOOKUP($B$5,$AC$19:$AF$25,2,FALSE)
205 | 2.0.9 | Refrigerators | Column J | Updated formula to use new App. D table | VLOOKUP(B5,AD42:AG48,4,FALSE) | VLOOKUP($B$5,$AC$19:$AF$25,4,FALSE)
206 | 2.0.9 | Refrigerators | A3:B3 | Removed Building Floors input | N/A | N/A
207 | 2.0.9 | Refrigerators | Column A | Added column for Index | N/A | N/A
208 | 2.0.9 | Refrigerators | Row 9:17 | Added input rows | N/A | N/A
209 | 2.0.9 | Refrigerators | L18:N18 | Added summaries for savings | N/A | N/A
210 | 2.0.9 | Summary of Savings | L5:N5, AF5:AH5 | Updated mapping to Refrigerator Saving Summaries | N/A | N/A
211 | 2.0.10 | Summary of Savings | I23, J32 | Added IFERROR | N/A | N/A
212 | 2.0.10 | Summary of Savings | Column L:N, AF:AH | Added IF condition: If measure is not selected yes, Then "-". | N/A | N/A
213 | 2.0.10 | Summary of Savings | Column AM:AO | Added IFERROR | N/A | N/A
214 | 2.0.11 | Central DHW Control | Column N | Corrected GPD formula | 46*48 | 34.4*'Building Info'!$H$11
215 | 2.0.11 | Central DHW Control | E1:F1 | Add input " Is DHW heated by the Space Heating Boiler?" | N/A | N/A
216 | 2.0.11 | Central DHW Control | Column K | Updated Fuel Efficiency formula to us boiler efficiency when DHW is heated by the boiler. | IFERROR(IF(VLOOKUP(E4,$Z$11:$AD$12,5, FALSE)=0,"",VLOOKUP(E4,$Z$11:$AD$12,5, FALSE)), "") | IFERROR(IFS(VLOOKUP(E4,$AA$11:$AE$12,5, FALSE)=0,"", $F$1="Yes", 'Building Info'!$C$24, 1=1, VLOOKUP(E4,$AA$11:$AE$12,5, FALSE) ), "")
217 | 2.0.11 | Central DHW Control | Column L | Added output Column "Et, fuel, w/Interactivity" | N/A | IFERROR(IF(AND(VLOOKUP(E4,$AA$11:$AE$12,5, FALSE)<>0, $F$1="Yes"), 'Summary of Savings'!$W$36, K4), "")
218 | 2.0.11 | Central DHW Control | Column X | Added output Column "Δtherms w/Interactivity" | N/A | IFERROR(O4*365*8.33*P4/100000*IFERROR(I4/L4,0)*D4/8760*N4,"")
219 | 2.0.12 | Low Flow A&S | C3:D3 | Add input " Is DHW heated by the Space Heating Boiler?" | N/A | N/A
220 | 2.0.12 | Low Flow A&S | B25, F25, J25 | Renamed row headers | UEF | UEF or Et
221 | 2.0.12 | Low Flow A&S | C25, G25, K25 | Modified formula to use boiler efficiency if yes is selected for " Is DHW heated by the Space Heating Boiler?" | IF(WaterHeaterType="Instantaneous Gas-Fired Water Heater",VLOOKUP('Low Flow A&S'!$AS$76,'Low Flow A&S'!$AS$69:$AT$73,2,FALSE),"")) | IF($D$3="Yes", 'Building Info'!$C$24, IF(WaterHeaterType="Gas-Fired Storage Water Heater",VLOOKUP('Low Flow A&S'!$AS$76,'Low Flow A&S'!$AS$54:$AT$68,2,FALSE), IF(WaterHeaterType="Instantaneous Gas-Fired Water Heater",VLOOKUP('Low Flow A&S'!$AS$76,'Low Flow A&S'!$AS$69:$AT$73,2,FALSE),"")))
222 | 2.0.12 | Low Flow A&S | Row 26 | Added output row for "UEF or Et with interactivity" | N/A | IFS($D$3="Yes", 'Summary of Savings'!$W$36, 'Summary of Savings'!$D$23="Yes", 'Low Flow A&S'!C25 + 'Summary of Savings'!$Y$32, 1=1, C25)
223 | 2.0.12 | Low Flow A&S | Row 32 | Added output row for "Therms Savings with interactivity:" | N/A | N/A
224 | 2.0.12 | Low Flow A&S | B36:C36, J36:K36, B38:B38 | Added output fields for summed savings with interactivity | N/A | N/A
225 | 2.0.12 | Low Flow A&S | B35, J35, B27 | renamed to Therms instead of MMBtu | N/A | N/A
226 | 2.0.12 | Low Flow A&S | AS136 | Corrected formula | CONCATENATE(WaterHeaterType,"_",'Low Flow A&S'!$K$10,"_",'Low Flow A&S'!$K$11) | CONCATENATE($K$9,"_",'Low Flow A&S'!$K$10,"_",'Low Flow A&S'!$K$11)
227 | 2.0.12 | Summary of Savings | AF12 | Updated formula to reference saving with interactivity | IF(D12="yes", 'Low Flow A&S'!C35, "-") | IF(D12="yes", 'Low Flow A&S'!C36, "-")
228 | 2.0.12 | Summary of Savings | AF13 | Updated formula to reference saving with interactivity | IF(D13="yes", 'Low Flow A&S'!K35, "-") | IF(D13="yes", 'Low Flow A&S'!K36, "-")
229 | 2.0.12 | EC Motors | Column AB | Format update: center | N/A | N/A
230 | 2.0.12 | EC Motors | BZ114 | Added 1/15 HP | N/A | N/A
231 | 2.0.13 | Orifice Plates | C33 | Edited formula to =0 when the measure is not selected "Yes" | (C12-C23)*(C28/C27)*(C29/C30) | IF('Summary of Savings'!$D$16="yes", (C12-C23)*(C28/C27)*(C29/C30), 0)
232 | 2.0.13 | Summary of Savings | Column AM:AO | Edited formulas to = "-" when the measure is not selected "Yes" | N/A | N/A
233 | 3 | Summary of Savings | B2 | Updated Version # | 2.0 | 3.0
234 | 3.0.1 | Summary of Savings | AO30 | Capped Cool Roof kW savings to 0 | IF(D30="Yes", IFERROR(AH30,"-"), "-") | IF(D30="Yes", IFERROR(AH30*0,"-"), "-")
235 | 3.0.1 | Building Info | B26 | Added "Is DHW heated by the Space Heating Boiler?" Input | N/A | N/A
236 | 3.0.1 | Boiler Clean & Tune | C6 | Converted from input to output/linked value. | INPUT | IF('Building Info'!$C$26="", "", 'Building Info'!$C$26)
237 | 3.0.1 | Low Flow A&S | D3 | Converted from input to output/linked value. | INPUT | IF('Building Info'!$C$26="", "", 'Building Info'!$C$26)
238 | 3.0.1 | Central DHW Control | F1 | Converted from input to output/linked value. | INPUT | IF('Building Info'!$C$26="", "", 'Building Info'!$C$26)
239 | 3.0.1 | EMS Controls | C5 | Converted from input to output/linked value. | INPUT | IF('Building Info'!$C$26="", "", 'Building Info'!$C$26)
240 | 3.0.1 | Pipe Insulation | F2 | Converted from input to output/linked value. | INPUT | IF('Building Info'!$C$26="", "", 'Building Info'!$C$26)
241 | 3.0.1 | Elevator Drive System Upgrade | ALL | Measure Added | N/A | N/A
242 | 3.0.1 | Summary of Savings | Row 11 | Elevator Drive System Upgrade Row added | N/A | N/A
243 | 3.0.1 | Master Venting | D45 | Edited formula to include boiler efficiency | IFERROR('Master Venting'!F107/100*('Master Venting'!BG80-'Master Venting'!BI80), 0) | IFERROR('Master Venting'!F107/100*('Master Venting'!BG80-'Master Venting'!BI80)/'Summary of Savings'!$W$36, 0)
244 | 3.0.1 | Master Venting | D47 | Edited formula to include updated boiler efficiency | IFERROR('Master Venting'!F107/100*('Master Venting'!BG81-'Master Venting'!BI81), 0) | IFERROR('Master Venting'!F107/100*('Master Venting'!BG81-'Master Venting'!BI81)/'Summary of Savings'!$W$37, 0)
245 | 3.0.1 | Summary of Savings | AF20 | Corrected mapping | IF(D20="yes", 'Central DHW Control'!W9, "-") | IF(D20="yes", 'Central DHW Control'!X9, "-")
246 | 3.0.1 | PLSF | All | Added reference sheet | N/A | N/A
247 | 3.0.1 | Summary of Savings | Column AP | Added Peak Day Therms Savings | N/A | N/A
248 | 3.0.1 | Summary of Savings | Column G | Added PC kW Savings | N/A | N/A
249 | 3.0.1 | Summary of Savings | Column AY | Added ΔkW Savings (Final - PC) | N/A | N/A
250 | 3.0.1 | Storage Tank Water Heater | Column Q | Added PPH, Person Per Household | N/A | IFERROR( SUMPRODUCT('Building Info'!$H$5:$H$10,'Building Info'!$J$5:$J$10)/'Building Info'!$H$11, "")
251 | 3.0.1 | Storage Tank Water Heater | Column P | TRM V12 Update: Updated GPM to use PPH. | A4*34.4 | IFERROR(A4*17.2*Q4, "")
252 | 3.0.2 | TRVs | All | TRM V12 Update: Updated to new Savings Methodology | N/A | N/A
253 | 3.0.2 | Summary of Savings | M19, AG19 | Updated mapping | N/A | N/A
254 | 3.0.2 | Central DHW Control | Column P | TRM V12 Update: Updated T_del default from 140 to 125 | IF(F4<>"",F4,140)-60.7 | IF(F4<>"",F4,125)-60.7
255 | 3.0.2 | Central DHW Control | F3 | TRM V12 Update: Updated Header | Tset | Tdel
256 | 3.0.2 | Roof & Wall Insulation | Column O | Remove Rim Joists and Floors from dropdown | N/A | N/A
257 | 3.0.2 | Roof & Wall Insulation | Column U | Removed derating | IFERROR(MAX( [@[Existing R Value]]*VLOOKUP([@[Existing Insulation Quality]], $CV$18:$CW$20,2,FALSE), INDEX($CB$18:$CE$21, MATCH('Building Info'!$C$9,$BQ$18:$BQ$21, 1), MATCH([@[Envelope Type]], $CB$17:$CE$17, 0)) ),"") | IFERROR(MAX( [@[Existing R Value]], INDEX($CB$18:$CE$21, MATCH('Building Info'!$C$9,$BQ$18:$BQ$21, 1), MATCH([@[Envelope Type]], $CB$17:$CE$17, 0)) ),"")
258 | 3.0.2 | Roof & Wall Insulation | BW24 | Updated CF to 0.822 from 0.69 | 0.69 | 0.822
259 | 3.0.2 | Roof & Wall Insulation | Column AA | Updated kW Savings formula to comercial measure from residential measure | IFERROR([@[Cooling kWh Saving]]/ INDEX($BU$18:$BV$21, MATCH('Building Info'!$C$9, $BQ$18:$BQ$21,1), MATCH('Building Info'!$C$10, $BO$18:$BO$19, 1)) *$BW$24,"") | IFERROR(((1/[@[RBaseline, 1]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]] *(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CT$18:$CU$21,2,FALSE))*VLOOKUP([@[HVAC System Type]],'Roof & Wall Insulation'!$BP$44:$BZ$50,10,FALSE)) /(1000*[@[Cooling Equipment EER]])*$BW$24,"")
260 | 3.0.2 | Roof & Wall Insulation | Column AH | Updated kW Savings formula to comercial measure from residential measure | IFERROR([@[Cooling kWh Saving_Interactive]]/ INDEX($BU$18:$BV$21, MATCH('Building Info'!$C$9, $BQ$18:$BQ$21,1), MATCH('Building Info'!$C$10, $BO$18:$BO$19, 1)) *$BW$24,"") | IFERROR(((1/[@[RBaseline, 1]]-1/([@[RBaseline, 2]]+[@[R Value Added]]))*[@[Area (sft)]] *(1-VLOOKUP([@[Envelope Type]],'Roof & Wall Insulation'!$CT$18:$CU$21,2,FALSE))*VLOOKUP([@[HVAC System Type]],'Roof & Wall Insulation'!$BP$44:$BZ$50,10,FALSE)) /(1000*[@[Cooling Equipment EER_Interactive]])*$BW$24,"")
261 | 3.0.2 | Summary of Savings | B2 | Updaed version # | v3.0 | v3.0.2
262 | 3.0.3 | Storage Tank Water Heater | AA16 | TRM V12 Update: Added T_del constant | N/A | 125
263 | 3.0.3 | Storage Tank Water Heater | Column J | TRM V12 Update: T_Main: Replaced T_set with T_del. | I4-$AA$15 | IF(A4="","", $AA$16-$AA$15)
264 | 3.0.4 | TRVs | All | Update from Residential & Multifamily Measure to Commercial and Industrial Measure methodology. | N/A | N/A
265 | 4 | Summary of Savings | B2 | Updated Version # | 3.0 | 4.0

## Calculation Notes (hidden)
Tier | Points | Measure | Is measure part of SOW? | Calculations Source | TRM Modications | Capping
3 | 5 | Refrigerators | Yes | NYS TRM v10 |  | No Cap
3 | 5 | Common Area Lighting | Yes | NYS TRM v10 | conEd some additional Operating Hours categories prescriptive tool is used | Savings x 0.45
3 | 5 | In-Unit Lighting | Yes | NYS TRM v10 | None | Savings x 0.95
3 | 10 | Hydronic Circulator Pump | Yes | NYS TRM v10 | None | No Cap
3 | 10 | EC Motors | Yes | Custom |  | Savings x 0.75
3 | 10 | VFD & Motor | Yes | Custom | N/A | Savings x 0.6 1. for chilled water pump serving absorption chiller, check with manufacture if variable flow rate is allowed.
1 | 5 | Boiler Clean & Tune | Yes | NYS TRM v10 | Utility Data uses Utility Data instead of ELFH*Input Capacity | Min (Savings x 66% if TRM Residential formula is used; <2% of baseline annual space heating energy usage;)
3 | 5 | Low Flow Faucet Aerators | Yes | NYS TRM v10 | ConEd | Savings x 0.75
3 | 5 | Low Flow Showerheads | Yes | NYS TRM v10 | ConEd | Savings x 0.75
2 | 10 | Air Sealing | Yes | NYS TRM v10 | TRM modified | ConEd: Savings x 0.3 National Grid: ≤ 1% of annual therms usage
3 | 10 | Master Venting | Yes | Custom | ConEd | <1.5% of baseline space heating annual usage
3 | 10 | Orifice Plates | Yes | Custom |  | Min (Savings x 0.37, 3% of annual space heating fuel usage if all are replaced)
3 | 10 | Steam Traps | Yes | NYS TRM v10 |  | Min (Savings x 0.75, 10% of annual space heating fuel usage if all traps replaced)
3 | 10 | TRVs | Yes | NYS TRM v10 | None | Savings x 0.4 if (1) TRM is used (2)TRVs for whole building
3 | 10 | Central DHW Control | Yes | NYS TRM v10 |  | < 2% of DHW fuel usage baseline
3 | 20 | EMS Controls | Yes | NYS TRM v10 |  | < 5% of baseline boiler annual heating usage
3 | 20 | Smart TRE | Yes | NYS TRM v10 |  | < 5% of baseline boiler annual heating usage
3 | 20 | Pipe Insulation | Yes | NYS TRM v10 |  | The minimum of 75% of the TRM formula or 2% of the related heating usage* *related heating usage = If both DHW and Space Heating line items, then 2% of both the DHW and Space Heating Baseline. If only DHW line items, then 2% of only the DHW Baseline. If only Space Heating line items, then 2% of only the Space Heating Baseline. (Change confirmed by ConEd) Old Cap Language: 'MIN (Savings x 75% if TRM formula is used; 2% of DHW heating baseline usage)
1 | 30 | Storage Tank DHW replacement | Yes | NYS TRM v10 |  | 1. Willan needs to check measure savings using billing data anaylsis 2. Do not estimate baseline eff degradation by age; 3. Heating/cooling central plant distribution efficiency should be same or similar in baseline and post 4.Condensing boiler efficiency must be the Eff @return temperature >140F. Must NOT use highest eff
1 | 40 | Boiler, Furnace, & Unit Heater Replacement | Yes | NYS TRM v10 |  | 1. Willan needs to check measure savings using billing data anaylsis 2. Do not estimate baseline eff degradation by age; 3. Heating/cooling central plant distribution efficiency should be same or similar in baseline and post 4.Condensing boiler efficiency must be the Eff @return temperature >140F. Must NOT use highest eff
3 | 5 | Induction Stovetop | Yes | NYS TRM v10 |  | No Cap
3 | 10 | Wi-Fi Thermostats | Yes | NYS TRM v10 | Removed From TRM
3 | 10 | Connected Thermostats | Yes | NYS TRM v10 |  | MMBtu savings x 50% if TRM is used
2 | 20 | Window Film | Yes | NYS TRM v10 |  | < 5% of baseline building space heating usage if all windows are installed with film
2 | 40 | Roof & Wall Insulation | Yes | NYS TRM v10 |  | ConEd: Roof: <10% of baseline annual energy usage Wall: <30% of annual baseline fuel space heating usage National Grid: Roof & Low Rise (<5 Floors): <5.5% of baseline annual gas usage Roof & High Rise (≥5 Floors): <3.5% of baseline annual gas usage Wall & Low Rise (<5 Floors): <3.5% of baseline annual gas usage Wall & High Rise (≥5 Floors): <5.5% of baseline annual gas usage
2 | 0 | Cool Roof | Yes | NYS TRM v10 |  | Zero or negative fuel savings; Minimal electric savings
2 | 40 | Window Replacement | Yes | NYS TRM v10 |  | ConEd: Savings Cap % of baseline building space heating usage if ALL windows are replaced: < 15% for single pane windows as baseline < 5% for double pane windows as baseline Savings Cap % of baseline kWh savings if all windows are replaced with low-e types: < 10% for single pane windows as baseline < 2% for double pane windows as baseline National Grid: ≤ 5% Baseline annual therms usage

## PLSF (hidden)
Peak Load Savings Factor
| Measure | PLSF End Use | PLSF | End Use | Multi-Family High-Rise | Multi-Family Low-Rise | Multi-Family High-Rise | Multi-Family Low-Rise
| Refrigerators | Interior Equipment | 0.003 | Hot Water | 0.003 | 0.003 | 0.0033462 | 0.0033462 | TRUE
| Common Area Lighting | Interior Equipment | 0.003 | Heating | 0.042 | 0.042 | 0.041957 | 0.041957 | TRUE
| In-Unit Lighting | Interior Equipment | 0.003 | Total Facility | 0.042 | 0.042 | 0.041957 | 0.041957 | TRUE
| Hydronic Circulator Pump | N/A | 0 | Interior Equipment | 0.003 | 0.003 | 0.0027397 | 0.0027397 | TRUE
| EC Motors | N/A | 0 | Learning Thermostat | 0.007 | 0.007 | 0.007 | 0.007 | TRUE
| VFD & Motor | N/A | 0 | EMS | 0.008 | 0.008 | 0.0082019 | 0.0082019 | TRUE
| Elevator Drive System Upgrade | N/A | 0 | N/A | 0 | 0
| Boiler Clean & Tune | Heating | 0.042
| Low Flow Faucet Aerators | Hot Water | 0.003 | [5 empty] | * Since they are the same between rises, the lookup will exclude rise.
| Low Flow Showerheads | Hot Water | 0.003
| Air Sealing | Heating | 0.042
| Master Venting | Heating | 0.042
| Orifice Plates | Heating | 0.042
| Steam Traps | Heating | 0.042
| TRVs | Heating | 0.042
| Central DHW Control | Hot Water | 0.003
| EMS Controls | EMS | 0.008
| Smart TRE | Heating | 0.042
| Pipe Insulation | N/A | 0
| Storage Tank DHW replacement | Hot Water | 0.003
| Boiler, Furnace, & Unit Heater Replacement | Heating | 0.042
| Induction Stovetop | Interior Equipment | 0.003
| Connected Thermostat | Learning Thermostat | 0.007
| Window Film | Heating | 0.042
| Roof & Wall Insulation | Heating | 0.042
| Window Replacement | Heating | 0.042
^Yellow cells above are flagged

## Summary of Savings
Summary of Savings |  | Summary of Savings
| v4.0 | [19 empty] | Interactivity
|  | PC Savings | [8 empty] | Savings Without Interactivity | [9 empty] | Tier 1 Interactivity |  |  | Tier 2 Interactivity |  |  |  | Savings With Interactivity | [5 empty] | Final Savings
Tier | ECM # | Measure | Is measure part of SOW? | PC Therm Savings | PC kWh Savings | PC kW Savings | Points | Project Cost | % Gas Savings | % kWh Savings | Willdan Therm Savings | Willdan kWh Savings | Willdan kW Savings | % Gas Savings | % SH Savings | % DHW Savings | % kWh Savings | Δtherms Savings | ΔkWh Savings |  | Δ Heating Efficiency | Δ Cooling Efficiency | Δ DHW Efficiency | Δ Heating Load (therms) | Δ Cooling Load (kWh) | Δ Heating ELFH | Δ Cooling EFLH | Therm Savings | kWh Savings | kW Savings | ΔTherm Savings | ΔkWh Savings | ΔkW Savings | Therm Savings | kWh Savings | kW Savings | Peak Day Therms Savings | % Gas Savings | % kWh Savings | ΔTherm Savings | ΔkWh Savings | ΔkW Savings | ΔTherm Savings (Final - PC) | ΔkWh Savings (Final - PC) | ΔkW Savings (Final - PC)
3 |  | Refrigerators | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Common Area Lighting | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | In-Unit Lighting | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Hydronic Circulator Pump | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | EC Motors | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | VFD & Motor | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Elevator Drive System Upgrade | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
1 |  | Boiler Clean & Tune | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Low Flow Faucet Aerators | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Low Flow Showerheads | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2 |  | Air Sealing | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Master Venting | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Orifice Plates | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Steam Traps | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | TRVs | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Central DHW Control | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | EMS Controls | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Smart TRE | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Pipe Insulation | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
1 |  | Storage Tank DHW replacement | No |  |  |  | - |  | - | - | - | - | - |  |  |  |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
1 |  | Boiler, Furnace, & Unit Heater Replacement | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Induction Stovetop | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Wi-Fi Thermostats | No |  |  |  | - |  | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3 |  | Connected Thermostat | No |  |  |  | - |  | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2 |  | Window Film | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2 |  | Roof & Wall Insulation | No |  |  |  | - |  | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2 |  | Cool Roof | No |  |  |  | - |  | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2 |  | Window Replacement | No |  |  |  | - |  | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Total |  | 0 | 0 | 0 | 0 |  | - | - | 0 | 0 | 0 | - |  |  | - | - | - |  | 0% | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0 | 0 | - | - | - | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | -
[20 empty] | Comments | Boiler Eff.
|  | ↑ Click to go to measure ↑ | [17 empty] | before interactivity | 0% | [9 empty] | *Change from Non-Interactive Savings to Interactive Savings | [8 empty] | *Change from Interactive Savings to Capped Savings |  |  | *Change from PC Savings to Capped Savings
[20 empty] | after interactivity | 0%
[35 empty] | Energy Usage (kBTU) |  | EUI (kBTU/ft2)
[34 empty] | Baseline | Gas usage | 0 | #DIV/0!
[35 empty] | Electric usage | 0 | #DIV/0!
[35 empty] | Total | 0 | #DIV/0!
[34 empty] | Proposed | Gas usage | 0 | #DIV/0!
[35 empty] | Electric usage | 0 | #DIV/0!
[35 empty] | Total | 0 | #DIV/0! |  |  | #DIV/0! |  | #DIV/0!
[35 empty] | Δ Energy Usage (kBTU/ft2) |  | #DIV/0!
[35 empty] | Incentive | 0
[35 empty] | $/MMBtu | #DIV/0!
[35 empty] | VLOOKUP Points | Incentive Rate
[35 empty] | 0 | 0
[35 empty] | 100 | 1500
[35 empty] | 150 | 2000
Note on H27: Measure Removed from NYS TRM V11
Note on H31: Not Eligible
Note on S4: Based of main CA electric account
Note on AN30: Capping is done in the Measure Tab
Note on AO10: For chilled water pump serving absorption chiller, check with manufacture if variable flow rate is allowed.
Note on AO29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This cooling load may not account for IU

## Utility Analysis (hidden)
Orifice Plates and Master Venting | [14 empty] | Con Ed Engineering TRV Calc
Temperature Reduction Method | [14 empty] | Units | 1650
[15 empty] | therms/HDD | 0.004318
|  |  | Value | Units | [10 empty] | HDD | 4671
| Select Baseline HDD Temperature |  | 65 | F | [10 empty] | Therm Savings | 33279.4737
| Select Temperature Reduction |  | 4 | F
Estimate from oil
| Output | [6 empty] | Start Date | End Date | Months | units | DHW Load | Heating Load | Months
therm/hr | Heating Usage | #VALUE! | therm/HDD_65 |  | load June | #VALUE! | Therm | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
| Baseline HDD_65 (TMY3) | 4884 | F.days/year |  | load July | #VALUE! | Therm | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
| Proposed HDD_61 (4F Temp Reduc) TMY3 | 3949 | F.days/year |  | load August | #VALUE! | Therm | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
| Baseline Heating Usage | #VALUE! | therm/year |  |  |  |  | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
| Proposed Heating Usage | #VALUE! | therm/year |  | Baseload Avg | #VALUE! | Therm | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
| Savings | #VALUE! | therm/year |  | Heating Usage Yr | #VALUE! | Therm | #VALUE! |  | 12 | #VALUE! | #VALUE! | 0 | January
| Savings (dTherm) | #VALUE! | dTherm/year |  | DHW Usage Yr | #VALUE! | Therm | #VALUE! |  | 12 | #VALUE! | #VALUE! | 0 | January
[8 empty] | #VALUE! |  | 12 | #VALUE! | #VALUE! | 0 | January
[8 empty] | #VALUE! |  | 12 | #VALUE! | #VALUE! | 0 | January
[8 empty] | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
[8 empty] | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January
[8 empty] | #VALUE! |  | 12 | #VALUE! | #VALUE! | #VALUE! | January

## Building Info
Building Info
| Buildings Name |  | Apartment Breakdown
| Street Address |  | Unit Type | Number of Units | Bedrooms/Unit | Occupants/Unit | Baths per Unit | Heaters per Unit | # of Bedrooms | # of Occupants | # of Baths | # of Showers | # of Bath Faucets | # of Heaters
| City/Borough |  | Studio |  | 1 | 1.5 | 1 | 1
| State |  | 1-Bed |  | 1 | 2 | 1 | 2
| Zip Code |  | 2-Bed |  | 2 | 3 | 1 | 3
|  |  | 3-Bed |  | 3 | 5 | 2 | 4
| Year Built |  | 4-Bed |  | 4 | 5.5 | 2 | 5
| # of Floors |  | 5-Bed |  | 5 | 6 | 3 | 6
| Building Height |  | TOTAL | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Building Area
Building Length
Building Width
# of Radiators or Convectors
# of A/C Sleeves
# of Balcony Doors
Boiler Input (MBH)
# of Boilers
Total Boiler Input (MBH)
Boiler Efficiency
| Calculated EFLH | *purposefully blank
Is DHW heated by the Space Heating Boiler?
Electric Utilty
Gas Utilty
[15 empty] | Gas Utility | Electric Utility
[15 empty] | ConEd | ConEd
National Grid

## Utility Data
Utility Data
|  | Value | Units | % of Total
Electric | Electric Baseload | #DIV/0! | kWh | #DIV/0!
| Space Cooling Seasonal Load | #DIV/0! | kWh | #DIV/0!
Gas | DHW Baseload | #DIV/0! | Therms | #DIV/0!
| Space Heating Seasonal Load | #DIV/0! | Therms | #DIV/0!
| Heating Index | #DIV/0! | btu/sqft/HDD
Electric Utility Data
Year | 2022 |  |  |  | 2023 |  |  |  | 2024
Month | Start | End | Demand (kW) | Electric Usage (kWh) | Start | End | Demand (kW) | Electric Usage (kWh) | Start | End | Demand (kW) | Electric Usage (kWh) | Average Electric Usage (kWh) | Average HDD | Average CDD
Jan | [13 empty] | 1008 | 0
Feb | [13 empty] | 861 | 0
Mar | [13 empty] | 713 | 1
Apr | [13 empty] | 392 | 6
May | [13 empty] | 136 | 54
Jun | [13 empty] | 16 | 209
Jul | [13 empty] | 1 | 377
Aug | [13 empty] | 1 | 336
Sep | [13 empty] | 40 | 141
Oct | [13 empty] | 249 | 17
Nov | [13 empty] | 524 | 1
Dec | [13 empty] | 836 | 0
Totals |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 4777 | 1142
Gas Utility Data
Year | 2022 |  |  | 2023 |  |  | 2024
Month | Start | End | Gas Usage (Therms) | Start | End | Gas Usage (Therms) | Start | End | Gas Usage (Therms) | Average Gas Usage (Therms) | Average HDD | Average CDD
Jan | [10 empty] | 1008 | 0
Feb | [10 empty] | 861 | 0
Mar | [10 empty] | 713 | 1
Apr | [10 empty] | 392 | 6
May | [10 empty] | 136 | 54
Jun | [10 empty] | 16 | 209
Jul | [10 empty] | 1 | 377
Aug | [10 empty] | 1 | 336
Sep | [10 empty] | 40 | 141
Oct | [10 empty] | 249 | 17
Nov | [10 empty] | 524 | 1
Dec | [10 empty] | 836 | 0
Totals |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 4777 | 1142

## Bin Calc (hidden)
Envelope Data |  |  |  | Boiler Input | 0 | kbtu/h |  | total area | 8744
Wall |  |  |  | Eff | 0% |  |  | floors | 0
Area | Assumed R-value | U-Value |  | Boiler Output | 0 | kbtu/h |  | perimeter | 533 |  |  | Peri | area | # | total perimeter | total area
0 | 6 | 0.16667 |  | From Utility | #DIV/0! | therms | [5 empty] | 533 | 8744 | 1 | 533 | 8744
Window |  |  |  |  | #DIV/0! | kbtu |  | height | 0
Area | Assumed U-value | U-Value |  | Full Load Hours | #DIV/0! | hrs
0 | 0.65 | 0.65 |  | Total annual output | #DIV/0! | kbtu/h
Roof
Area | Assumed R-value | U-Value
8744 | 17 | 0.058824 |  | Occupancy | 0 | Occupants
Slab
Area | Assumed R-value | U-Value
8744 | 1 | 1
Building Volume | 0 |  | Building Balance Point |  | Balance
|  |  | 65 |  | -1254% | Should be between -2% & +2%
Ventilation |  |  | Indoor Space Temp
ACH | CFM |  | 76
0.6 | 0 | [6 empty] | Conditioned Load Assumptions
[8 empty] | Lighting | 0.2 | W/sqft
[8 empty] | Appliances | 0.1 | W/sqft
U*A (Slab) | 8744 | [6 empty] | Plug Loads | 0.2 | W/sqft
U*A (Exposed) | 514.3529 | [6 empty] | Total | 0.5 | W/sqft
|  |  | Loads |  |  |  | Gains
Bin Temperature | Enthalpy (BTU/lbda) | Hours | Slab | Envelope Load | Ventilation Load | Total | Heating Equipment | Conditioned Loads | People | Total | delta-T hrs
(Range is +/- 2.5 °F)
107.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87.5 | 32.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82.5 | 29.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77.5 | 27.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72.5 | 26.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67.5 | 24.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62.5 | 22.3016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57.5 | 19.5684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52.5 | 17.9623 | 439 | -80610.936 | -5306.3221 | 0 | -85917.2581 | 0 | 6548.6789 | 0 | 6548.6789 | 5487.5
47.5 | 15.8297 | 497 | -91261.128 | -7285.5522 | 0 | -98546.6802 | 0 | 7413.8802 | 0 | 7413.8802 | 8697.5
42.5 | 14.0992 | 434 | -79692.816 | -7478.1774 | 0 | -87170.9934 | 0 | 6474.0926 | 0 | 6474.0926 | 9765
37.5 | 11.7667 | 527 | -96769.848 | -10435.964 | 0 | -107205.812 | 0 | 7861.3981 | 0 | 7861.3981 | 14492.5
32.5 | 9.9661 | 313 | -57474.312 | -7003.1725 | 0 | -64477.4845 | 0 | 4669.1036 | 0 | 4669.1036 | 10172.5
27.5 | 8.5693 | 138 | -25340.112 | -3442.5642 | 0 | -28782.6762 | 0 | 2058.5824 | 0 | 2058.5824 | 5175
22.5 | 6.9471 | 107 | -19647.768 | -2944.4134 | 0 | -22592.1814 | 0 | 1596.1472 | 0 | 1596.1472 | 4547.5
17.5 | 5.3871 | 62 | -11384.688 | -1865.5581 | 0 | -13250.2461 | 0 | 924.8704 | 0 | 924.8704 | 2945
12.5 | 3.5984 | 17 | -3121.608 | -555.244 | 0 | -3676.852 | 0 | 253.5935 | 0 | 253.5935 | 892.5
7.5 | 2.3057 | 4 | -734.496 | -140.9327 | 0 | -875.4287 | 0 | 59.6691 | 0 | 59.6691 | 230
2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Totals | 2538 | -466037.712 | -46457.9007 | 0 | -512495.6127 | 0 | 37860.016 | 0 | 37860.016 | 62405

## Refrigerators
Refrigerators |  |  |  |  | Click to go to Summary of Savings
Occupancy per unit
HVAC
Index | Units | Existing Refrigerator kWh | Proposed Refrigerator kWh | Units | kWh_baseline | kWh_ee | F_occ | HVAC_c | HVAC_d | HVAC_ff | Annual kWh Savings | Peak kW Savings | Annual Therms Savings
1 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
2 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
3 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
4 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
5 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
6 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
8 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
9 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
10 |  |  |  | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
[11 empty] | 0 | 0 | 0
HVAC Interactive Effects Coefficients
[14 empty] | HVAC Type | HVACc (for kWh) | HVACd (for kW) | HVACff (for MMBtu)
[14 empty] | AC with Fuel Heat | 0.0349 | 0.1575 | -0.0016
[14 empty] | Chilled Water with Fuel Heat | 0.0208 | 0.0938 | -0.0016
[14 empty] | Heat Pump | -0.1215 | 0.1575 | 0
[14 empty] | AC with Electric Resistance Heat | -0.3411 | 0.1575 | 0
[14 empty] | Chilled Water with Electric Resistance Heat | -0.3553 | 0.0938 | 0
[14 empty] | Fuel Heat Only | 0 | 0 | -0.0016
[14 empty] | Electric Resistance Heat Only | -0.3761 | 0 | 0
[14 empty] | Number of Occ | F_occ |  | CF | 1
[14 empty] | Unknown | 1
[14 empty] | 1 | 1.05
[14 empty] | 2 | 1.1
[14 empty] | 3 | 1.13
[14 empty] | 4 | 1.15
[14 empty] | 5 | 1.16

## Common Area Lighting
Common Area Lighting |  |  |  |  | HVAC Type: | [5 empty] | Click to go to Summary of Savings
# | Qty | Wattsbaseline | Wattsee | Hours | HVACc | HVACd | HVACff | CF | kWh savings | kW savings | Therms savings
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
[9 empty] | 0 | 0 | 0
*Use CA Lighting Tool and copy & paste value the inputs & output below
| Lighting | [20 empty] | No error in this page |  |  | No error in this table | [15 empty] | 0
Index | Floor # | Location | Height (feet) | Interior/Exterior | Facility Type | Space Type | Self Reported Hours | Existing Measure Type | Existing Measure Description | Existing Light Wattage | Existing Baseline Wattage | Existing Measure Fixture Code | Qty | Replacement Measure Type | Replacement Measure Description | DLC category / Energy Star category | Bi-level Fixture Location | Replacement Measure Fixture Wattage | Will Occupancy Sensors be installed for this measure? | Make | Model | kW Saving | BQ kW Saving | Jamaica kW Saving | WS kW Saving | NT kW Saving | kWh Saving | EUL | MMBTU | LMMBTU | Measure Cost | Notes | Total Price | Final Incentive | Uncapped Incentive | Bonus Incentive | $/kWh | Co-Pay | Depth Category | BQ/Water St/NT incentive Cap | Measure ID | Measure Type for Measure Summary tab | Sector Hours | TDM Co-Pay | Customer Copay
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
HVAC Interactive Effects Coefficients
[46 empty] | HVAC Type | HVACc (for kWh) | HVACd (for kW) | HVACff (for MMBtu)
[46 empty] | AC with Fuel Heat | 0.0349 | 0.1575 | -0.0016
[46 empty] | Chilled Water with Fuel Heat | 0.0208 | 0.0938 | -0.0016
[46 empty] | Heat Pump | -0.1215 | 0.1575 | 0
[46 empty] | AC with Electric Resistance Heat | -0.3411 | 0.1575 | 0
[46 empty] | Chilled Water with Electric Resistance Heat | -0.3553 | 0.0938 | 0
[46 empty] | Fuel Heat Only | 0 | 0 | -0.0016
[46 empty] | Electric Resistance Heat Only | -0.3761 | 0 | 0

## In-Unit Lighting
In-Unit Lighting | [6 empty] | HVAC Type: | [5 empty] | Click to go to Summary of Savings
| Existing Fixture Description | Existing Fixture Description | [7 empty] | Proposed Fixture Description | [5 empty] | Savings
# | Building | Space Type | Location | Qty | Fixture Description | Watts per Lamp | Lamps per Fixture | Total Wattage | Runtime hrs per day | Qty | Fixture Description | Watts per Lamp | Lamps per Fixture | Total Wattage | Runtime hrs per day | Existing Annual kWh | Proposed Annual kWh | HVACc | HVACd | HVACff | Annual kWh Savings | Peak kW Savings | Annual Therms Savings
1 | [14 empty] | 4.8 | [8 empty] | Total kWh Savings
2 | [14 empty] | 4.8 | [8 empty] | 0
3 | [14 empty] | 4.8
4 | [14 empty] | 4.8 | [8 empty] | Total kW Savings
5 | [14 empty] | 4.8 | [8 empty] | 0
6 | [14 empty] | 4.8
7 | [14 empty] | 4.8 | [8 empty] | Total Therms Savings
8 | [14 empty] | 4.8 | [8 empty] | 0
9 | [14 empty] | 4.8
10 | [14 empty] | 4.8
11 | [14 empty] | 4.8
12 | [14 empty] | 4.8
13 | [14 empty] | 4.8
14 | [14 empty] | 4.8
15 | [14 empty] | 4.8
16 | [14 empty] | 4.8
17 | [14 empty] | 4.8
18 | [14 empty] | 4.8
19 | [14 empty] | 4.8
20 | [14 empty] | 4.8
21 | [14 empty] | 4.8
22 | [14 empty] | 4.8
23 | [14 empty] | 4.8
24 | [14 empty] | 4.8
25 | [14 empty] | 4.8
26 | [14 empty] | 4.8
27 | [14 empty] | 4.8
28 | [14 empty] | 4.8
29 | [14 empty] | 4.8
30 | [14 empty] | 4.8
31 | [14 empty] | 4.8
32 | [14 empty] | 4.8
33 | [14 empty] | 4.8
34 | [14 empty] | 4.8
35 | [14 empty] | 4.8
36 | [14 empty] | 4.8
37 | [14 empty] | 4.8
38 | [14 empty] | 4.8
39 | [14 empty] | 4.8
40 | [14 empty] | 4.8
41 | [14 empty] | 4.8
42 | [14 empty] | 4.8
43 | [14 empty] | 4.8
44 | [14 empty] | 4.8
45 | [14 empty] | 4.8
46 | [14 empty] | 4.8
47 | [14 empty] | 4.8
48 | [14 empty] | 4.8
49 | [14 empty] | 4.8
50 | [14 empty] | 4.8
51 | [14 empty] | 4.8
52 | [14 empty] | 4.8
53 | [14 empty] | 4.8
54 | [14 empty] | 4.8
55 | [14 empty] | 4.8
56 | [14 empty] | 4.8
57 | [14 empty] | 4.8
58 | [14 empty] | 4.8
59 | [14 empty] | 4.8
60 | [14 empty] | 4.8
61 | [14 empty] | 4.8
62 | [14 empty] | 4.8
63 | [14 empty] | 4.8
64 | [14 empty] | 4.8
65 | [14 empty] | 4.8
66 | [14 empty] | 4.8
67 | [14 empty] | 4.8
68 | [14 empty] | 4.8
69 | [14 empty] | 4.8
70 | [14 empty] | 4.8
71 | [14 empty] | 4.8
72 | [14 empty] | 4.8
73 | [14 empty] | 4.8
74 | [14 empty] | 4.8
75 | [14 empty] | 4.8
76 | [14 empty] | 4.8
77 | [14 empty] | 4.8
78 | [14 empty] | 4.8
79 | [14 empty] | 4.8
80 | [14 empty] | 4.8
81 | [14 empty] | 4.8
82 | [14 empty] | 4.8
83 | [14 empty] | 4.8
84 | [14 empty] | 4.8
85 | [14 empty] | 4.8
86 | [14 empty] | 4.8
87 | [14 empty] | 4.8
88 | [14 empty] | 4.8
89 | [14 empty] | 4.8
90 | [14 empty] | 4.8
91 | [14 empty] | 4.8
92 | [14 empty] | 4.8
93 | [14 empty] | 4.8
94 | [14 empty] | 4.8
95 | [14 empty] | 4.8
96 | [14 empty] | 4.8
97 | [14 empty] | 4.8
98 | [14 empty] | 4.8
99 | [14 empty] | 4.8
100 | [14 empty] | 4.8
HVAC Interactive Effects Coefficients
[25 empty] | HVAC Type | HVACc (kWh) | HVACd (kW) | HVACff
[25 empty] | AC with Fuel Heat | 0.0349 | 0.1575 | -0.0016 | CF | 0.16
[25 empty] | Chilled Water with Fuel Heat | 0.0208 | 0.0938 | -0.0016
[25 empty] | Heat Pump | -0.1215 | 0.1575 | 0
[25 empty] | AC with Electric Resistance Heat | -0.3411 | 0.1575 | 0
[25 empty] | Chilled Water with Electric Resistance Heat | -0.3553 | 0.0938 | 0
[25 empty] | Fuel Heat Only | 0 | 0 | -0.0016
[25 empty] | Electric Resistance Heat Only | -0.3761 | 0 | 0

## Hydronic Circulator Pump
Hydronic Circulator Pump | [8 empty] | Click to go to Summary of Savings
[22 empty] | TB_Baseline_and_Efficient_Ciculator_Wattages |  |  |  |  | NYS TRM ROR | Commercial and Industrial Measures
Index | Floor # | Location | Circulator Pump Cooling Application | Circulator Pump Heating Application | Circulator Pump DHW Application | Qty | Proposed Circulator Pump hp | Head85% (ft of water) | Q85% (GPM) | Custom Baseline Wattage | Hourscooling | Hoursheating | HoursDHW | hhp85% | Wbaseline | Wee | kW Saving | ΔkWhCooling | ΔkWhHeating | ΔkWhDHW | kWh Saving |  | DL_Approximate_PSC_Circulator_Equivalent_Rated_hp |  |  |  | PDF p.21 | ELECTRONICALLY COMMUTATED (EC) MOTOR – HYDRONIC CIRCULATOR PUMPS
0 | [21 empty] | EC Circulator hhp | Approximate PSC Circulator Equivalent Rated hp | Wbaseline | Wee |  |  | Issue Date – 4/29/2022
1 | [21 empty] | 0.002 | 0.025 | 60 | 15 |  |  | Effective Date – 1/1/2023
2 | [21 empty] | 0.009 | 0.025 | 77 | 29
3 | [21 empty] | 0.16 | 0.04 | 96 | 40
4 | [21 empty] | 0.023 | 0.04 | 124 | 53
5 | [21 empty] | 0.03 | 0.083333 | 132 | 58
6 | [21 empty] | 0.097 | 0.16667 | 269 | 138
7 | [21 empty] | 0.099 | 0.16667 | 282 | 145
8 | [21 empty] | 0.57 | 1 | 962 | 555
9
10
11
12 | [22 empty] | Continuous Heating | 5256
13 | [22 empty] | Continuous Cooling | 2208
14 | [22 empty] | On/Off Control Heating | 5735 | *Dormitory Hours
15 | [22 empty] | On/Off Control Cooling | 2863 | *Dormitory Hours
[17 empty] | 0 | 0 | 0 | 0 | 0 |  | DHW | 8760 | *Dormitory Hours
[23 empty] | Not Applicable | 0 | *Not TRM
TB_Hydronic_Circ_Pump__Cooling_hrs
[23 empty] | DL_Hydronic_Circ_Pump__Cooling_hrs |  | CF
[23 empty] | Continuous Cooling | 2208 | 1
[23 empty] | On/Off Control Cooling | 2863 | 0.8 | *Dormitory Hours
[23 empty] | Not Applicable | 0 | 0 | *Not TRM
TB_Hydronic_Circ_Pump__Heating_hrs
DL_Hydronic_Circ_Pump__Heating_hrs
[23 empty] | Continuous Heating | 5256
[23 empty] | On/Off Control Heating | 5735 | *Dormitory Hours
[23 empty] | Not Applicable | 0 | *Not TRM
TB_Hydronic_Circ_Pump__DHW_hrs
DL_Hydronic_Circ_Pump__DHW_hrs
[23 empty] | DHW | 8760
[23 empty] | Not Applicable | 0 | *Not TRM
[29 empty] | 100% of shutoff head | 7 | ft of water
[29 empty] | 85% of shutoff head | 5.95

## EC Motors
EC Motors | [9 empty] | Click to go to Summary of Savings
[9 empty] | Existing Motor | [16 empty] | Proposed EC Motor | [9 empty] | Savings |  | Costs |  |  |  |  | Incentives
Row | Rebate Type | Early Replacement / Extended Life | Location | End Use | Quantity | Error Flag | Hours of Operation | Error Flag | Existing PSC Motor | Manufacturer | Model | Motor Size (HP) | Motor Size for Calculations (HP) | Load Factor for Calculations | Nameplate Motor Speed (RPM) | Maximum Rated Motor Speed (RPM) | Error Flag | Code Minimum Efficiency | Motor Efficiency | Error Flag | Market Rate and EL/ER? | Affordable OR Affordable and EL/ER? | Blank/Flagged Motor Efficiency? | Efficiency for Calculations | Baseline Electric Demand (kW) | Motor Size (HP) | Nameplate Motor Speed (RPM) | Maximum Rated Motor Speed (RPM) | Code Minimum Efficiency | Load Factor | EC motor efficiency | Error Flag | Installed motor speed (%) | Error Flag | Proposed Electric Demand (kW) | Electric Demand Savings (kW) | Annual Electric Energy Savings (kWh) | Material Cost ($) | Error Flag | Labor Cost ($) | Error Flag | Total Cost ($) | Savings Incentive | Cost Incentive Cap | Total Incentive ($) | Errors? | Error Locations |  | Input error cell locations on EC Motors worksheet
1 |  | No | [45 empty] | 0
2 |  | No
3 |  | No
4 |  | No
5 |  | No
6 |  | No
7 |  | No
8 |  | No
9 |  | No
10 |  | No
11 |  | No
12 |  | No
13 |  | No
14 |  | No
15 |  | No
16 |  | No
17 |  | No
18 |  | No
19 |  | No
20 |  | No
21 |  | No
22 |  | No
23 |  | No
24 |  | No
25 |  | No
26 |  | No
27 |  | No
28 |  | No
29 |  | No
30 |  | No
31 |  | No
32 |  | No
33 |  | No
34 |  | No
35 |  | No
36 |  | No
37 |  | No
38 |  | No
39 |  | No
40 |  | No
41 |  | No
42 |  | No
43 |  | No
44 |  | No
45 |  | No
46 |  | No
47 |  | No
48 |  | No
49 |  | No
50 |  | No
51 |  | No
52 |  | No
53 |  | No
54 |  | No
55 |  | No
56 |  | No
57 |  | No
58 |  | No
59 |  | No
60 |  | No
61 |  | No
62 |  | No
63 |  | No
64 |  | No
65 |  | No
66 |  | No
67 |  | No
68 |  | No
69 |  | No
70 |  | No
71 |  | No
72 |  | No
73 |  | No
74 |  | No
75 |  | No
76 |  | No
77 |  | No
78 |  | No
79 |  | No
80 |  | No
81 |  | No
82 |  | No
83 |  | No
84 |  | No
85 |  | No
86 |  | No
87 |  | No
88 |  | No
89 |  | No
90 |  | No
91 |  | No
92 |  | No
93 |  | No
94 |  | No
95 |  | No
96 |  | No
97 |  | No
98 |  | No
99 |  | No
100 |  | No
[36 empty] | 0 | 0
Commercial and Industrial Energy Efficiency Program 2023
[53 empty] | Data Input List tables | [5 empty] | NYC TRM v10
[52 empty] | Column Input ID | Rebate Type | End Use | Phases | Early Replacement / Extended Life |  | Motor HP List | https://dps.ny.gov/system/files/documents/2023/03/c1e1783c-c3d3-48a4-8647-a5923c39553c.pdf
[52 empty] | Input 1 | Multifamily Affordable | Hydronic Cooling Pump | 1 | Yes |  | 0.066667
[50 empty] | Data Input Tool | * indicates a required field | Input 2 | Multifamily Market Rate | Hydronic Heating Pump | 3 | No |  | 0.083 | EC Motors for HVAC Blower Fans | EC Motors for Circulator Pumps
[52 empty] | Input 3 |  | Furnace Supply Fan |  | 6 |  | 0.125
[50 empty] | Project Details |  | Input 4 |  | Exhaust Fan (24/7) |  | 8 |  | 0.167
[50 empty] | Rebate Type | Multifamily Affordable | Input 5 |  | Custom |  |  |  | 0.25
[50 empty] | Tool Generation Date* | 2026-08-06 | Input 6 | [5 empty] | 0.33
[52 empty] | Input 7 | [5 empty] | 0.5
0.75
[53 empty] | Calculation inputs |  |  |  |  | 1
[53 empty] | Constants | source |  |  |  | 1.5
[53 empty] | 2.3 | Affinity Factor |  |  |  | 2
[53 empty] | 0.746 | HP to kW conversion factor |  |  |  | 3
[53 empty] | 0.65 | Incentive Rate | affordable |  |  | 5
[53 empty] | 0.5 | Incentive Rate | market rate |  |  | 7.5
10
[53 empty] | Hours of Use table |  |  |  |  | 15
[52 empty] | Column Input ID | End Use | Hours of Use |  |  |  | 20
[52 empty] | Input 1 | Hydronic Cooling Pump | 2208 |  |  |  | 25
[52 empty] | Input 2 | Hydronic Heating Pump | 5256 |  |  |  | 30
[52 empty] | Input 3 | Furnace Supply Fan | 3400 |  |  |  | 40
[52 empty] | Input 4 | Exhaust Fan (24/7) | 8760 |  |  |  | 50
[52 empty] | Input 5 | Custom | user entry |  |  |  | 60
75
100
[53 empty] | Motor Efficiency table | Poles |  |  |  | 125
[53 empty] | Motor HP | 3600 | 1800 | 1200 | 900 | 150
[53 empty] | 0.125 | 65.6% | 69.5% | 67.5% | 75.5% | 200
[53 empty] | 0.25 | 65.6% | 69.5% | 67.5% | 75.5% | 250
[53 empty] | 0.33 | 69.5% | 73.4% | 71.4% | 75.5% | 300
[53 empty] | 0.5 | 73.4% | 78.2% | 75.3% | 75.5%
[53 empty] | 0.75 | 76.8% | 81.1% | 81.7% | 75.5%
[53 empty] | 1 | 77% | 85.5% | 82.5% | 75.5%
[53 empty] | 1.5 | 84% | 86.5% | 87.5% | 78.5%
[53 empty] | 2 | 85.5% | 86.5% | 88.5% | 84%
[53 empty] | 3 | 86.5% | 89.5% | 89.5% | 85.5%
[53 empty] | 5 | 88.5% | 89.5% | 89.5% | 86.5%
[53 empty] | 7.5 | 89.5% | 91.7% | 91% | 86.5%
[53 empty] | 10 | 90.2% | 91.7% | 91% | 89.5%
[50 empty] | Updates Log |  |  | 15 | 91% | 92.4% | 91.7% | 89.5%
[50 empty] | 2023-06-22 | Workbook reviewed and locked by Con ED |  | 20 | 91% | 93% | 91.7% | 90.2%
[50 empty] | 2023-07-26 | LF in column AD changed so HP = 1 -> LF = 0.9 |  | 25 | 91.7% | 93.6% | 93% | 90.2%
[51 empty] | Inputs on Project summary page changed to general cell types |  | 30 | 91.7% | 93.6% | 93% | 91.7%
[51 empty] | Column AA formatted not to show decimals |  | 40 | 92.4% | 94.1% | 94.1% | 91.7%
[51 empty] | Column R expanded row 5 formula down through table (was pulling incorrect values after row 5) |  | 50 | 93% | 94.5% | 94.1% | 92.4%
[51 empty] | Changed 1/8 value in resource table to numeric value for proper index matching. |  | 60 | 93.6% | 95% | 94.5% | 92.4%
[53 empty] | 75 | 93.6% | 95.4% | 94.5% | 93.6%
[53 empty] | 100 | 94.1% | 95.4% | 95% | 93.6%
[53 empty] | 125 | 95% | 95.4% | 95% | 94.1%
[53 empty] | 150 | 95% | 95.8% | 95.8% | 94.1%
[53 empty] | 200 | 95.4% | 96.2% | 95.8% | 94.5%
[53 empty] | 250 | 95.8% | 96.2% | 95.8% | 95%
[53 empty] | 300 | 95.8% | 96.2% | 95.8% | 95%
source: 2020 NYCECC table 10.8-1, 2020 ECCCNYS table C405.7

## EC Motors (OLD) (hidden)
EC MOTORS |  |  |  |  | Click to go to Summary of Savings
Description:
EC Motor Replacment with Speed Reduction (includes motors with integrated VFDs)
Code deemed motor only baseline might be more efficient than the EC motor assembly. We have taken a penalty into account.
For motors that are being upsized, please enter individual lines for the load factor
Parameters | [6 empty] | Baseline |  |  | Proposed |  |  |  | Savings
# | Qty | Existing Hp | Proposed Hp | Motor Type | LF | Hours | Efficiency | kW | kWh/Year | Speed | Efficiency | kW | kWh/Year | kW | kWh
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
| 0 | [6 empty] | 0 | 0 |  |  | 0 | 0 | 0 | 0
[8 empty] | Motor | AUDITED | NYC & TRM CODE | MFGR SPEC SHEET
| Notes: | [6 empty] | Horsepower | Phases | Baseline Efficiency | Proposed Efficiency
| TOR motor efficiency. Baseline is from Code. | [6 empty] | <= 1hp & PSC | 1 | 60%
| LF of 90% and 75% are based on Con Edison Engineering direction from TRM type measures. | [6 empty] | 0.125
| Proposed Efficiency is "system" efficiency from cutsheets. | [6 empty] | 0.25
| Affinity Factor of 2.3. | [6 empty] | 0.33333
| No VFD factor (system efficiency takes this into account). | [6 empty] | 0.5
0.75
1
1.5
2
3
Note on E9: If single phase, enter PSC. If triple phase, enter Induction
Note on K37: From NYCECC 2020 Code Compliance Use the TRM V9 App L Table to the left
Note on L37: Must Match Spec Sheet

## VFD + Motor
VFD + Motor |  |  |  |  | Click to go to Summary of Savings
|  |  | Baseline |  |  | Replacement
Index | Location | No. of Motors | Motor HP | Existing Motor eff | Existing hrs/yr | Motor HP | Proposed Motor eff | Hrs/yr (part load) | Hrs/Yr (full load) | VFD Motor Load (part load) | VFD Motor Load (full load) | VFD eff (part load) | VFD eff (full load) | Baseline kWh consumption | Proposed kWh consumption (part load) | Proposed kWh consumption (full load) | kWh Savings | Incentives
0
1
2
3
4
5
6
7
8
9
10
|  |  |  | 0% |  |  | 0% | [6 empty] | 0 | 0 | 0 | 0 | 0
[19 empty] | $/kWh Custom Incentive Rate | 0
[19 empty] | Conversion Factor | 0.746
[19 empty] | Load Factor | 0.75
[19 empty] | Affinity Factor | 2.3
Total Project Cost
70 % Cap
[19 empty] | Total Savings | 0
[19 empty] | Total Incentive | 0
Note on AD25: Surely Mejia: Industry estimate, unless proven otherwise

## Elevator Drive System Upgrade
Elevator Drive System Upgrade | [6 empty] | Click to go to Summary of Savings
# | Elevator Number | Location | Units | Baseline Drive Type | Proposed Drive Type | Is Regerative Braking being installed? | HP | Capacity | OCW | Top Velocity | Hours | EFFmotor | EFFdrive,base | EFFdrive,ee | Hours | Fidle | Fregen | kWhbase | kWhee | kWhregen | ΔkWh | ΔkW
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
[18 empty] | 0 | 0 | 0 | 0 | 0
[23 empty] | Motor hp | Effmotor | Effmech | 0.64 | Drive | Effdrive | Fidle | Multifamily Buildings Dwelling Units Range | Lookup Value | Hours | Regen? | Fregen
[23 empty] | 1 | 82.5% | LFavg | 0.35 | M-G Set | 0.77 | 0.6 | 0 - 6 | 0 | 73 | Yes | 0.5
[23 empty] | 1.5 | 84% | LFmotor,idle | 0.12 | SCR6 | 0.85 | 0 | 7 - 20 | 7 | 182.5 | No | 0
[23 empty] | 2 | 84% | Conversion factor (kW/hp) | 0.746 | SCR12 | 0.9 | 0 | 21 - 50 | 21 | 547.5
[23 empty] | 3 | 87.5% | Conversion factor ((ft-lb/min)/hp) | 33000 | PWM | 0.94 | 0 | 51+ | 50 | 1095
[23 empty] | 5 | 87.5% | Hours per Year | 8760 | VVVF | 0.95 | 0
[23 empty] | 7.5 | 89.5%
[23 empty] | 10 | 89.5%
[23 empty] | 15 | 91%
[23 empty] | 20 | 91%
[23 empty] | 25 | 92.4%
[23 empty] | 30 | 924%
[23 empty] | 40 | 93%
[23 empty] | 50 | 93%
[23 empty] | 60 | 93.6%
[23 empty] | 75 | 94.1%
[23 empty] | 100 | 94.5%
[23 empty] | 125 | 95.4%
[23 empty] | 150 | 95%
[23 empty] | 200 | 95%
Note on D3: Number of Elevators being Upgraded
Note on F3: Must be more efficient than Baseline
Note on H3: Horsepower of motor
Note on I3: Elevator car capacity (lbs)
Note on J3: Overweight of counterbalance as a fraction of car capacity; if unkown, use 0.4
Note on K3: Rate top velocity of car, in ft/min
Note on L3: Optional: Annual hours of elevator operation; if unknown, leave blank.
Note on M3: Nema Premium Efficiency, see table below
Note on N3: Baseline Drive Efficiency
Note on O3: New Drive Efficiency. If unknown, use the following defaults: SCR6 = 0.85, SCR12=0.90, PWM=0.94, VVVF=0.95
Note on Q3: MG Set Baseline Only: Idling factor; used to account for fraction of run hours M-G set system in idling mode; Use 0.7 for timer incorporated, 1.0 for no timer, 0.7 for unknown
Note on R3: Regenerative breaking factor; used to account for fraction of run hours regenerative braking produces energy savings
Note on S3: Baseline Electric Energy Consumption per unit
Note on T3: Proposed Electric Energy Consumption per unit
Note on U3: Regenerated Electric Energy per unit
Note on V3: Annual Electric Energy Savings
Note on W3: Peak Electric Power Savings

## Boiler Clean & Tune
Boiler Clean & Tune Savings |  |  | Click to go to Summary of Savings
Building Vintage
Boiler Make/Model
# of Boilers
Is DHW heated by the Space Heating Boiler?
Value
Baseline Gas Usage (therms)
| Ec,baseline | 0%
Ec,ee
Δtherms w/o interactivity

## Low Flow A&S
(R) Low Flow - Faucet Aerator |  |  | (R) Low Flow - Faucet Aerator |  |  |  | (R) Low Flow - Showerhead
| Is DHW heated by the Space Heating Boiler? |  |  |  |  | Click to go to Summary of Savings
# of Faucet Aerators installed: |  |  | # of Faucet Aerators installed: |  |  |  | # of Faucet Aerators installed:
Faucet Type: | Lavatory |  | Faucet Type: | Non Lavatory |  |  | Is the Building LMI: | Yes
Water Heater Fuel: | Electric Water Heater |  | Water Heater Fuel: | Electric Water Heater |  |  | Water Heater Fuel: | Electric Water Heater
Water Heater Type: | Gas-Fired Storage Water Heater |  | Water Heater Type: | Gas-Fired Storage Water Heater |  |  | Water Heater Type: | Gas-Fired Storage Water Heater
Storage Tank Volume: | 56 | gallons | Storage Tank Volume: | 56 | gallons |  | Storage Tank Volume: | 56 | gallons
First Hour Rating | Unknown |  | First Hour Rating | Unknown |  |  | First Hour Rating | Unknown
[7 empty] | GPM ee: | 1.75 | gallons per minute for energy efficient measure
[7 empty] | person/household: | 2
Throttle Factor baseline | 0.83 |  | Throttle Factor baseline | 0.83
Throttle Factor Eff | 0.95 |  | Throttle Factor Eff | 0.95 |  |  | Tshower: | 104
Tfaucet: | 86 |  | Tfaucet: | 93 |  |  | GPMbaseline: | 2.5
GPMbaseline: | 1.2 |  | GPMbaseline: | 1.8 |  |  | Fshower: | 1.4
GPMee: | 1 |  | GPMee: | 1.5 |  |  | minutes/use: | 8.2
Tmain: | 60.7 |  | Tmain: | 60.7 |  |  | uses/person/day: | 0.75
Ffaucet: | 1.6 |  | Ffaucet: | 1 |  |  | person/household: | 2
minutes/day: | 1.6 |  | minutes/day: | 4.5 |  |  | Throttle Fac | 0.9
person/household: | 2 |  | person/household: | 2 |  |  | Tmain: | 60.7
ΔTmain: | 25.3 |  | ΔTmain: | 32.3 |  |  | ΔTmain: | 43.3
H20 Savings: | 33.58 |  | H20 Savings: | 226.665 |  |  | H20 Savings: | 2164.5804
UEF or Et | 0.7904 |  | UEF or Et | 0.7904 |  |  | UEF or Et | 0.7904
UEF or Et with interactivity | 0.7904 |  | UEF or Et with interactivity | 0.7904 |  |  | UEF or Et with interactivity | 0.7904
kWh Savings: | #VALUE! |  | kWh Savings: | #VALUE! |  |  | kWh Savings: | #VALUE!
kW Savings: | 0 |  | kW Savings: | 0 |  |  | kW Savings: | 0
MMBTU Savings: | #VALUE! |  | MMBTU Savings: | #VALUE! |  |  | MMBTU Savings: | #VALUE!
MMBTU Savings with interactivity: | #VALUE! |  | MMBTU Savings with interactivity: | #VALUE! |  |  | MMBTU Savings with interactivity: | #VALUE!
Aerator Therms Savings: | 0 | [5 empty] | Showerhead Therms Savings: | 0
Aerator Therms Savings with interactivity: | 0 | [5 empty] | Showerhead MMBTU Savings with interactivity: | 0
Total Therms Savings:
Total Therms Savings with interactivity:
[10 empty] | Water Heater Types | Storage Volume | First Hour Rating for Gas-Fired Storage Water Heater | Max GPM for Instantaneous Gas-Fired Water Heater |  | Product Class | Rated Volume Storage (V) | First Hour Rating (FHR) | Draw Pattern | UEF | Concatenate Tree
[10 empty] | Gas-Fired Storage Water Heater | 0 | < 18 gallons | < 1.7 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | < 18 gallons | Very Small | 0.2336 | Water Heater Type | Storage Volume | FHR or Max GPM | Concatenated Logic Tree | UEF | Draw Pattern
[10 empty] | Instantaneous Gas-Fired Water Heater | 20 | ≥ 18 and < 51 gallons | ≥ 1.7 and < 2.8 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | ≥ 18 and < 51 gallons | Low | 0.4918 | Gas-Fired Storage Water Heater | 20 | < 18 gallons | Gas-Fired Storage Water Heater_20_< 18 gallons | 0.2336 | Very Small
[11 empty] | 56 | ≥ 51 and < 75 gallons | ≥ 2.8 and < 4.0 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | ≥ 51 and < 75 gallons | Medium | 0.5531 | Gas-Fired Storage Water Heater | 20 | ≥ 18 and < 51 gallons | Gas-Fired Storage Water Heater_20_≥ 18 and < 51 gallons | 0.4918 | Low
[11 empty] | Unknown | ≥ 75 gallons | ≥ 4.0 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | ≥ 75 gallons | High | 0.6192 | Gas-Fired Storage Water Heater | 20 | ≥ 51 and < 75 gallons | Gas-Fired Storage Water Heater_20_≥ 51 and < 75 gallons | 0.5531 | Medium
[12 empty] | Unknown | Unknown |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | Unknown | Medium | 0.5531 | Gas-Fired Storage Water Heater | 20 | ≥ 75 gallons | Gas-Fired Storage Water Heater_20_≥ 75 gallons | 0.6192 | High
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | < 18 gallons | Very Small | 0.6134 | Gas-Fired Storage Water Heater | 20 | Unknown | Gas-Fired Storage Water Heater_20_Unknown | 0.5531 | Medium
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | ≥ 18 and < 51 gallons | Low | 0.7409 | Gas-Fired Storage Water Heater | 56 | < 18 gallons | Gas-Fired Storage Water Heater_56_< 18 gallons | 0.6134 | Very Small
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | ≥ 51 and < 75 gallons | Medium | 0.7673 | Gas-Fired Storage Water Heater | 56 | ≥ 18 and < 51 gallons | Gas-Fired Storage Water Heater_56_≥ 18 and < 51 gallons | 0.7409 | Low
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | ≥ 75 gallons | High | 0.7904 | Gas-Fired Storage Water Heater | 56 | ≥ 51 and < 75 gallons | Gas-Fired Storage Water Heater_56_≥ 51 and < 75 gallons | 0.7673 | Medium
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | Unknown | High | 0.7904 | Gas-Fired Storage Water Heater | 56 | ≥ 75 gallons | Gas-Fired Storage Water Heater_56_≥ 75 gallons | 0.7904 | High
[15 empty] | Gas-Fired Storage Water Heater | Unknown | < 18 gallons | Very Small | 0.2336 | Gas-Fired Storage Water Heater | 56 | Unknown | Gas-Fired Storage Water Heater_56_Unknown | 0.7904 | High
[15 empty] | Gas-Fired Storage Water Heater | Unknown | ≥ 18 and < 51 gallons | Low | 0.4918 | Gas-Fired Storage Water Heater | Unknown | < 18 gallons | Gas-Fired Storage Water Heater_Unknown_< 18 gallons | 0.2336 | Very Small
[11 empty] | If Gas_Fired_Storage_Water_Heater | If Instantaneous_Gas_Fired_Water_Heater |  |  | Gas-Fired Storage Water Heater | Unknown | ≥ 51 and < 75 gallons | Medium | 0.5531 | Gas-Fired Storage Water Heater | Unknown | ≥ 18 and < 51 gallons | Gas-Fired Storage Water Heater_Unknown_≥ 18 and < 51 gallons | 0.4918 | Low
[15 empty] | Gas-Fired Storage Water Heater | Unknown | ≥ 75 gallons | High | 0.6192 | Gas-Fired Storage Water Heater | Unknown | ≥ 51 and < 75 gallons | Gas-Fired Storage Water Heater_Unknown_≥ 51 and < 75 gallons | 0.5531 | Medium
[15 empty] | Gas-Fired Storage Water Heater | Unknown | Unknown | Medium | 0.5531 | Gas-Fired Storage Water Heater | Unknown | ≥ 75 gallons | Gas-Fired Storage Water Heater_Unknown_≥ 75 gallons | 0.6192 | High
[11 empty] | Storage Volume | Storage Volume | [7 empty] | Gas-Fired Storage Water Heater | Unknown | Unknown | Gas-Fired Storage Water Heater_Unknown_Unknown | 0.5531 | Medium
[11 empty] | 20 | < 2 gal and > 50,000 BTU/h |  |  | Product Class | Input Rating (IR) | Max GPM | Draw Pattern | UEF | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | < 1.7 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_< 1.7 gallons/minute | 0.8 | Very Small
[11 empty] | 56 |  |  |  | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | < 1.7 gallons/minute | Very Small | 0.8 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 1.7 and < 2.8 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_≥ 1.7 and < 2.8 gallons/minute | 0.81 | Low
[11 empty] | Unknown |  |  |  | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 1.7 and < 2.8 gallons/minute | Low | 0.81 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 2.8 and < 4.0 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_≥ 2.8 and < 4.0 gallons/minute | 0.81 | Medium
[15 empty] | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 2.8 and < 4.0 gallons/minute | Medium | 0.81 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 4.0 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_≥ 4.0 gallons/minute | 0.81 | High
[15 empty] | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 4.0 gallons/minute | High | 0.81 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | Unknown | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_Unknown | 0.81 | High
[11 empty] | Gas-Fired Storage Water Heater | Instantaneous Gas-Fired Water Heater | Electric-Fired Storage Water Heater | Instantaneous Electric-Fired Water Heater | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | Unknown | High | 0.81
[10 empty] | Storage Volume dropdown | StorageVolume_GF | StorageVolume_Inst
[10 empty] | FHR/Max GPM dropdown | FHR_GF | MaxGPM_Inst | [9 empty] | Input Cancatenate | Gas-Fired Storage Water Heater_56_Unknown
[22 empty] | Storage Volume | 56
[22 empty] | Draw Pattern | High
[13 empty] | < 18 gallons |  | 20
[13 empty] | ≥ 18 and < 51 gallons |  | 56 |  |  |  |  | *after Storage Volume options for WaterHeaterType="Instantaneous Gas-Fired Water Heater" are restricted to "< 2 gal and > 50,000 BTU/h"
[13 empty] | ≥ 51 and < 75 gallons |  | Unknown |  |  |  |  | -"< 2 gal and > 50,000 BTU/h" can be added to Storage Volume Column and formulas for W23:W27 can be changed
≥ 75 gallons
Unknown
0.7904
List
Electric Water Heater
Gas Fired Water Heater
[10 empty] | Water Heater Types | Storage Volume | First Hour Rating for Gas-Fired Storage Water Heater | Max GPM for Instantaneous Gas-Fired Water Heater |  | Product Class | Rated Volume Storage (V) | First Hour Rating (FHR) | Draw Pattern | UEF | Cancatenate Tree
[10 empty] | Gas-Fired Storage Water Heater | 0 | < 18 gallons | < 1.7 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | < 18 gallons | Very Small | 0.2336 | Water Heater Type | Storage Volume | FHR or Max GPM | Cancatenated Logic Tree | UEF | Draw Pattern
[10 empty] | Instantaneous Gas-Fired Water Heater | 20 | ≥ 18 and < 51 gallons | ≥ 1.7 and < 2.8 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | ≥ 18 and < 51 gallons | Low | 0.4918 | Gas-Fired Storage Water Heater | 20 | < 18 gallons | Gas-Fired Storage Water Heater_20_< 18 gallons | 0.2336 | Very Small
[11 empty] | 56 | ≥ 51 and < 75 gallons | ≥ 2.8 and < 4.0 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | ≥ 51 and < 75 gallons | Medium | 0.5531 | Gas-Fired Storage Water Heater | 20 | ≥ 18 and < 51 gallons | Gas-Fired Storage Water Heater_20_≥ 18 and < 51 gallons | 0.4918 | Low
[11 empty] | Unknown | ≥ 75 gallons | ≥ 4.0 gallons/minute |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | ≥ 75 gallons | High | 0.6192 | Gas-Fired Storage Water Heater | 20 | ≥ 51 and < 75 gallons | Gas-Fired Storage Water Heater_20_≥ 51 and < 75 gallons | 0.5531 | Medium
[12 empty] | Unknown | Unknown |  | Gas-Fired Storage Water Heater | >= 20 gal and <= 55 gal | Unknown | Medium | 0.5531 | Gas-Fired Storage Water Heater | 20 | ≥ 75 gallons | Gas-Fired Storage Water Heater_20_≥ 75 gallons | 0.6192 | High
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | < 18 gallons | Very Small | 0.6134 | Gas-Fired Storage Water Heater | 20 | Unknown | Gas-Fired Storage Water Heater_20_Unknown | 0.5531 | Medium
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | ≥ 18 and < 51 gallons | Low | 0.7409 | Gas-Fired Storage Water Heater | 56 | < 18 gallons | Gas-Fired Storage Water Heater_56_< 18 gallons | 0.6134 | Very Small
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | ≥ 51 and < 75 gallons | Medium | 0.7673 | Gas-Fired Storage Water Heater | 56 | ≥ 18 and < 51 gallons | Gas-Fired Storage Water Heater_56_≥ 18 and < 51 gallons | 0.7409 | Low
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | ≥ 75 gallons | High | 0.7904 | Gas-Fired Storage Water Heater | 56 | ≥ 51 and < 75 gallons | Gas-Fired Storage Water Heater_56_≥ 51 and < 75 gallons | 0.7673 | Medium
[15 empty] | Gas-Fired Storage Water Heater | > 55 gal and <= 100 gal | Unknown | High | 0.7904 | Gas-Fired Storage Water Heater | 56 | ≥ 75 gallons | Gas-Fired Storage Water Heater_56_≥ 75 gallons | 0.7904 | High
[15 empty] | Gas-Fired Storage Water Heater | Unknown | < 18 gallons | Very Small | 0.2336 | Gas-Fired Storage Water Heater | 56 | Unknown | Gas-Fired Storage Water Heater_56_Unknown | 0.7904 | High
[15 empty] | Gas-Fired Storage Water Heater | Unknown | ≥ 18 and < 51 gallons | Low | 0.4918 | Gas-Fired Storage Water Heater | Unknown | < 18 gallons | Gas-Fired Storage Water Heater_Unknown_< 18 gallons | 0.2336 | Very Small
[11 empty] | If Gas_Fired_Storage_Water_Heater | If Instantaneous_Gas_Fired_Water_Heater |  |  | Gas-Fired Storage Water Heater | Unknown | ≥ 51 and < 75 gallons | Medium | 0.5531 | Gas-Fired Storage Water Heater | Unknown | ≥ 18 and < 51 gallons | Gas-Fired Storage Water Heater_Unknown_≥ 18 and < 51 gallons | 0.4918 | Low
[15 empty] | Gas-Fired Storage Water Heater | Unknown | ≥ 75 gallons | High | 0.6192 | Gas-Fired Storage Water Heater | Unknown | ≥ 51 and < 75 gallons | Gas-Fired Storage Water Heater_Unknown_≥ 51 and < 75 gallons | 0.5531 | Medium
[15 empty] | Gas-Fired Storage Water Heater | Unknown | Unknown | Medium | 0.5531 | Gas-Fired Storage Water Heater | Unknown | ≥ 75 gallons | Gas-Fired Storage Water Heater_Unknown_≥ 75 gallons | 0.6192 | High
[11 empty] | Storage Volume | Storage Volume | [7 empty] | Gas-Fired Storage Water Heater | Unknown | Unknown | Gas-Fired Storage Water Heater_Unknown_Unknown | 0.5531 | Medium
[11 empty] | 20 | < 2 gal and > 50,000 BTU/h |  |  | Product Class | Input Rating (IR) | Max GPM | Draw Pattern | UEF | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | < 1.7 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_< 1.7 gallons/minute | 0.8 | Very Small
[11 empty] | 56 |  |  |  | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | < 1.7 gallons/minute | Very Small | 0.8 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 1.7 and < 2.8 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_≥ 1.7 and < 2.8 gallons/minute | 0.81 | Low
[11 empty] | Unknown |  |  |  | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 1.7 and < 2.8 gallons/minute | Low | 0.81 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 2.8 and < 4.0 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_≥ 2.8 and < 4.0 gallons/minute | 0.81 | Medium
[15 empty] | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 2.8 and < 4.0 gallons/minute | Medium | 0.81 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 4.0 gallons/minute | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_≥ 4.0 gallons/minute | 0.81 | High
[15 empty] | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | ≥ 4.0 gallons/minute | High | 0.81 | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | Unknown | Instantaneous Gas-Fired Water Heater_< 2 gal and > 50,000 BTU/h_Unknown | 0.81 | High
[11 empty] | Gas-Fired Storage Water Heater | Instantaneous Gas-Fired Water Heater | Electric-Fired Storage Water Heater | Instantaneous Electric-Fired Water Heater | Instantaneous Gas-Fired Water Heater | < 2 gal and > 50,000 BTU/h | Unknown | High | 0.81
[10 empty] | Storage Volume dropdown | StorageVolume_GF | StorageVolume_Inst
[10 empty] | FHR/Max GPM dropdown | FHR_GF | MaxGPM_Inst | [9 empty] | Input Cancatenate | Gas-Fired Storage Water Heater_56_Unknown
[22 empty] | Storage Volume | 56
[22 empty] | Draw Pattern | High
[13 empty] | < 18 gallons |  | 20
[13 empty] | ≥ 18 and < 51 gallons |  | 56 |  |  |  |  | *after Storage Volume options for WaterHeaterType="Instantaneous Gas-Fired Water Heater" are restricted to "< 2 gal and > 50,000 BTU/h"
[13 empty] | ≥ 51 and < 75 gallons |  | Unknown |  |  |  |  | -"< 2 gal and > 50,000 BTU/h" can be added to Storage Volume Column and formulas for W23:W27 can be changed
≥ 75 gallons
Unknown
0.7904
List
Electric Water Heater
Gas Fired Water Heater

## Air Sealing
Air Sealing | Air Sealing |  |  |  | (Low-Rise Only) HVAC Type: |  | Click to go to Summary of Savings | Air sealing measure | Building Age Lookup | Building age | Low-Rise | High-Rise | Therm/KSF (for high-rise) | Low-Rise |  | Low-Rise
[8 empty] | Fixed Louvers | 0 | 1940 & Prior | 999 | 1012 | 29 | # of Floors | F_h | HVAC_Type | Therm/CFM
Index | Floor # | Location | Measure Description | Qty (Louver/door/window) | Area of the Floor (sqft) | Therm Saving |  | Exterior Doors - Weather stripping | 1941 | 1941-1978 | 757 | 526 | 29 | 1 | 1 | AC with Gas Heat | 1.9
1 | [7 empty] | Exterior Doors - Door sweep | 1979 | 1979-2006 | 723 | 395 | 17 | 1.5 | 0.9 | Heat Pump | 0
2 | [7 empty] | Exterior Doors - Threshold | 2007 | 2007-Now | 503 | 219 | 0 | 2 | 0.81 | AC with Electric Heat | 0
3 | [7 empty] | Exterior Doors - Replace door | [5 empty] | 2.5 | 0.76 | Gas Heat Only | 1.9
4 | [7 empty] | Exterior Doors - Replace complete door with frame | [5 empty] | 3 | 0.7 | Electric Heat Only | 0
5 | [7 empty] | Common Area Windows
6 | [7 empty] | Basement Air Sealing - Level 1
7 | [7 empty] | Basement Air Sealing - Level 2
8 | [7 empty] | Basement Air Sealing - Level 3
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
0

## Master Venting
Master (Steam-Line) Venting |  |  |  |  | Click to go to Summary of Savings | [6 empty] | Assumptions/Principles: |  | Utility Bill Data: | [10 empty] | 8760 Weather File | [8 empty] | Burner Firing Time File |  |  |  |  | Outdoor Reset Control Adjustments | [16 empty] | EMS Control Adjustments
[12 empty] | 1. Complete Boiler Cycle = Establish Heat + Cycle On + Cycle Off + Thermal Lockout (i.e. standard for all Heat Timer controls) | [25 empty] | source: generic operating assumption | source: Heat Timer Corp | [16 empty] | source: Entech Boiler Controls
| Existing Piping | Main Lines |  | Branch & Riser Lines |  |  | Boiler Controls |  |  |  |  | 2. Burner Firing Time = Establish Heat Time + Cycle On Time |  |  | Start Date | End Date | Therms | Cost | [6 empty] | Index | Month | Day | Day of Week | Hour | Drybulb | DB Round |  |  | Midpoint Temp. | Full_Modulation | Hi/Lo | On/Off
| Nominal Size (in) | Length (ft) | Volume (cf) | Length (ft) | Volume (cf) |  | EMS type |  |  |  |  | 3. Burner Off Time = Cycle Off Time + Thermal Lockout Time | [12 empty] | 1 | 1 | 1 | 3 | 1 | 28 | 28 | source: 2018 Weather Data |  | 5 | 100% | 100% | 100% | [20 empty] | Outdoor Temperature
| 2 |  | 0 |  | 0 |  | Boiler Modulation (Firing Rate) |  |  |  |  | 4. Established Heat Time = Total Main Line Vent Time + Total Branch & Riser Line Vent Time | [12 empty] | 2 | 1 | 1 | 3 | 2 | 28 | 28 |  |  | 7 | 100% | 100% | 100% |  |  |  | Outdoor Temperature | [16 empty] | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55
| 2.5 |  | 0 |  | 0 |  | Heat Adjustment Letter | [5 empty] | *cap Establish Heat Time baseline at 10 minutes | [11 empty] | 3 | 1 | 1 | 3 | 3 | 28 | 28 |  | BTU = gpm x 500 x dt | 9 | 100% | 100% | 100% |  |  |  | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | Heat Adjustment Letter | A | 19 | 19 | 17 | 15 | 12 | 10 | 8 | 5 | 3 | 2 | 1
| 3 |  | 0 |  | 0 | [6 empty] | 5. EFLH = # of Hours x Burner Firing Rate x Burner Firing Time | [12 empty] | 4 | 1 | 1 | 3 | 4 | 27 | 27 |  |  | 11 | 100% | 100% | 100% |  | Heat Adjustment Letter | A | 34 | 32 | 30 | 28 | 26 | 24 | 22 | 20 | 18 | 16 | 14 | 12 | 10 | 8 | 6 |  | B | 23 | 23 | 21 | 19 | 16 | 13 | 10 | 7 | 5 | 3 | 2
| 3.5 |  | 0 |  | 0 |  | Standard Air Vents |  |  | Information Source |  | 6. Burner Firing Rate represents the average firing rate that the burner maintains in order to stay at the modulating pressure setpoint depending on the outdoor temperature. | [12 empty] | 5 | 1 | 1 | 3 | 5 | 27 | 27 |  |  | 13 | 100% | 100% | 100% |  |  | B | 38 | 36 | 34 | 32 | 30 | 28 | 26 | 24 | 22 | 20 | 18 | 16 | 14 | 12 | 10 |  | C | 28 | 28 | 26 | 22 | 19 | 15 | 12 | 8 | 6 | 4 | 2
| 4 |  | 0 |  | 0 |  | Make & Model | Rated Capacity @ 2 Psig (CFM) |  | From Pre-inspection Findings |  |  | *Assume the burner is adequately tuned to the manufacturer recommended turndown ratio and does not short cycle (i.e. overshoot modulating pressure setpoint). | [11 empty] | 6 | 1 | 1 | 3 | 6 | 26.1 | 26 |  |  | 15 | 100% | 100% | 100% |  |  | C | 42 | 40 | 38 | 36 | 34 | 32 | 30 | 28 | 26 | 24 | 22 | 20 | 18 | 16 | 14 |  | D | 33 | 33 | 30 | 26 | 22 | 18 | 14 | 10 | 7 | 4 | 3
| 4.5 |  | 0 |  | 0 |  | Gorton #1 | 0.54 |  | From PC's spreadsheet |  | 6. Steam-Line Venting has the effect of reducing Established Heat Time and increasing Thermal Lockout Time. Overall the Complete Boiler Cycle Time is approximately the same. | [12 empty] | 7 | 1 | 1 | 3 | 7 | 27 | 27 |  |  | 17 | 75% | 100% | 100% |  |  | D | 46 | 44 | 42 | 40 | 38 | 36 | 34 | 32 | 30 | 28 | 26 | 24 | 22 | 20 | 18 |  | E | 38 | 38 | 34 | 30 | 25 | 21 | 16 | 11 | 8 | 5 | 3
| 6 |  | 0 |  | 0 |  | Gorton #2 | 1.75 |  | From PC's SOW |  |  | *cap Establish Heat Time reduction at 25% below the baseline. | [11 empty] | 8 | 1 | 1 | 3 | 8 | 27 | 27 |  |  | 19 | 75% | 100% | 100% |  |  | E | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36 | 34 | 32 | 30 | 28 | 26 | 24 | 22 |  | F | 42 | 42 | 39 | 34 | 29 | 23 | 18 | 13 | 9 | 6 | 3
| 8 |  | 0 |  | 0 |  | Gorton D | 0.54 |  | From PC's Main Line map |  | 7. This energy savings calculator only captures the benefits of reduced gas usage resulting from the Established Heat Time Reduction. Additional energy savings will occur as a result of reduced gas usage resulting from the Thermal Lockout Time increase. | [12 empty] | 9 | 1 | 1 | 3 | 9 | 28.9 | 29 |  |  | 21 | 75% | 100% | 100% |  |  | F | 60 | 52 | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36 | 34 | 32 | 30 | 28 | 26 |  | G | 47 | 47 | 43 | 38 | 32 | 26 | 20 | 14 | 10 | 6 | 4
| Total | 0 | 0 | 0 | 0 |  | Hoffman 3 | 0.28 |  |  | *If other, Enter here |  | *Some advanced EMS controls have the ability to automatically adjust the Cycle On and Cycle Off Times as well. In this situation there may be additional energy savings. | [11 empty] | 10 | 1 | 1 | 3 | 10 | 30.9 | 31 |  |  | 23 | 75% | 100% | 100% |  |  | G | 60 | 60 | 60 | 52 | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36 | 34 | 32 | 30 |  | H | 52 | 52 | 47 | 42 | 35 | 28 | 22 | 16 | 11 | 7 | 4
[7 empty] | Hoffman 75 | 0.75 |  |  |  | 8. Program Realized Savings are to be capped at 3% of annual heating gas usage. | [12 empty] | 11 | 1 | 1 | 3 | 11 | 32 | 32 |  |  | 25 | 75% | 100% | 100% |  |  | H | 60 | 60 | 60 | 60 | 60 | 52 | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36 | 34 |  | I | 57 | 57 | 52 | 45 | 38 | 31 | 24 | 17 | 12 | 8 | 5
[7 empty] | Barnes & Jones BM | 2.4 |  |  |  | 9. Complete Boiler Cycle is triggered by a call for heat. A call for heat requires all of the following: | [12 empty] | 12 | 1 | 1 | 3 | 12 | 36 | 36 |  |  | 27 | 75% | 100% | 100% |  |  | I | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 52 | 50 | 48 | 46 | 44 | 42 | 40 | 38 |  | J | 60 | 60 | 56 | 49 | 42 | 34 | 26 | 19 | 13 | 8 | 5
| Existing Venting | Main Lines |  | Branch & Riser Lines |  |  | Maid O Mist #1 | 0.59 |  |  |  | a. | Outdoor Temperature Sensor falls below setpoint* |  |  |  | 0 | 0 | [6 empty] | 13 | 1 | 1 | 3 | 13 | 37 | 37 |  |  | 29 | 75% | 100% | 100% |  |  | J | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 52 | 50 | 48 | 46 | 44 | 42 |  | K | 60 | 60 | 60 | 53 | 45 | 36 | 28 | 20 | 14 | 9 | 6
| Vent Type | Quantity | Venting Capacity (cfm) | Quantity | Venting Capacity (cfm) |  | Dole #5 | 0.116 |  |  |  | b. | Heating System Sensor falls below setpoint (e.g. 150 +/- 25 F) | [11 empty] | 14 | 1 | 1 | 3 | 14 | 36 | 36 |  |  | 31 | 50% | 50% | 100% | [19 empty] | L | 60 | 60 | 60 | 57 | 48 | 39 | 30 | 22 | 15 | 10 | 6
| Gorton #1 |  | 0 |  | 0 |  | Other | 0.75 | *If unknown, leave value at 0.75 |  |  | c. | Apartment Temperature Sensor Average falls below setpoint (EMS applications only) | [11 empty] | 15 | 1 | 1 | 3 | 15 | 36 | 36 |  |  | 33 | 50% | 50% | 100%
| Gorton #2 |  | 0 |  | 0 | [6 empty] | 10. Assume all boiler controls go into Outdoor Air Lockout mode on nights warmer than 40 F. | [12 empty] | 16 | 1 | 1 | 3 | 16 | 37 | 37 |  |  | 35 | 50% | 50% | 100%
| Hoffman 3 |  | 0 |  | 0 | [7 empty] | *Assume 40% of the hours in each temperature bin are night hours. | [11 empty] | 17 | 1 | 1 | 3 | 17 | 35.1 | 35 |  |  | 37 | 50% | 50% | 100%
| Hoffman 75 |  | 0 |  | 0 | [19 empty] | 18 | 1 | 1 | 3 | 18 | 36 | 36 |  |  | 39 | 50% | 50% | 100%
| Other |  | 0 |  | 0 | *For other, manually enter Venting Capacity for Main and Riser vents in L13 | [5 empty] | October 1 thru May 31 | [12 empty] | 20 | 1 | 1 | 3 | 20 | 36 | 36 |  |  | 41 | 50% | 50% | 100%
| Total Venting Capacity (cfm) |  | 0 |  | 0 | [6 empty] | 55 F outside during the day (6am-10pm) | [12 empty] | 21 | 1 | 1 | 3 | 21 | 37.9 | 38 |  |  | 43 | 50% | 50% | 100%
| Vent Time (min) |  | #DIV/0! |  | #DIV/0! | [19 empty] | 22 | 1 | 1 | 3 | 22 | 37.9 | 38 |  |  | 45 | 25% | 50% | 100%
|  | Existing ESTABLISH HEAT TIME (min) |  |  | #DIV/0!
[12 empty] | 40 F outside during the night (10pm-6am) | [12 empty] | 23 | 1 | 1 | 3 | 23 | 37.9 | 38 |  |  | 47 | 25% | 50% | 100%
| Proposed Timing | Main Lines |  | Branch & Riser Lines | [20 empty] | 24 | 1 | 2 | 4 | 0 | 39 | 39 |  |  | 49 | 25% | 50% | 100%
| Vent Time Design (min) | [23 empty] | 25 | 1 | 2 | 4 | 1 | 39.9 | 40 |  |  | 51 | 25% | 50% | 100%
[12 empty] | Instructions: | [12 empty] | 26 | 1 | 2 | 4 | 2 | 39.9 | 40 |  |  | 53 | 25% | 50% | 100%
| Proposed Venting | Main Lines |  | Branch & Riser Lines | [8 empty] | Enter or select from dropdown all fields with this color | [11 empty] | 27 | 1 | 2 | 4 | 3 | 41 | 41 |  |  | 55 | 25% | 50% | 100%
| Vent Type | Quantity | Venting Capacity (cfm) | Quantity | Venting Capacity (cfm) | [9 empty] | Boiler Control Type | EMS | Outdoor_Reset | [5 empty] | Boiler_Modulation |  | 28 | 1 | 2 | 4 | 4 | 39.9 | 40
| Hoffman 75 |  | 0 |  | 0 | [9 empty] | EMS | A | A | [5 empty] | Full_Modulation |  | 29 | 1 | 2 | 4 | 5 | 39.9 | 40
| Gorton #2 |  | 0 |  | 0 | [9 empty] | Outdoor_Reset | B | B | [5 empty] | Hi/Lo | On/Off | 30 | 1 | 2 | 4 | 6 | 39 | 39
| Gorton D |  | 0 |  | 0 | [10 empty] | C | C | [5 empty] | On/Off |  | 31 | 1 | 2 | 4 | 7 | 39 | 39
| Total Vents | 0 |  | 0 | [11 empty] | D | D | [7 empty] | 32 | 1 | 2 | 4 | 8 | 37.9 | 38
| Total Venting Capacity (cfm) |  | 0 |  | 0 | [10 empty] | E | E | [7 empty] | 33 | 1 | 2 | 4 | 9 | 39.9 | 40
| Vent Time Actual (min) |  | #DIV/0! |  | #DIV/0! | [10 empty] | F | F | [7 empty] | 34 | 1 | 2 | 4 | 10 | 41 | 41
|  | Proposed ESTABLISH HEAT TIME (min) |  |  | #DIV/0! | [10 empty] | G | G | [7 empty] | 35 | 1 | 2 | 4 | 11 | 42.1 | 42
[16 empty] | H | H | [7 empty] | 36 | 1 | 2 | 4 | 12 | 44.1 | 44
[16 empty] | I | I | [7 empty] | 37 | 1 | 2 | 4 | 13 | 45 | 45
| Steam-Line Venting Summary Results | [14 empty] | J | J | [5 empty] | EFLH From TRM |  | 38 | 1 | 2 | 4 | 14 | 46 | 46
[16 empty] | K | [6 empty] | 1940 & prior | 1012 | 39 | 1 | 2 | 4 | 15 | 46.9 | 47
| EST HEAT Time Reduction (min/cycle) | [14 empty] | L | [6 empty] | 1941-1978 | 526 | 40 | 1 | 2 | 4 | 16 | 46.9 | 47
| EST HEAT Time Reduction (hours/year) | [18 empty] | Tester |  |  | 1979-2006 | 395 | 41 | 1 | 2 | 4 | 17 | 46 | 46
| Estimated Energy Savings (therms) (Without interactivity) |  | 0 | [16 empty] | EMS |  |  | 2007-Present | 219 | 42 | 1 | 2 | 4 | 18 | 45 | 45
| Estimated Savings Percentage (%) | [18 empty] | D |  |  |  |  | 43 | 1 | 2 | 4 | 19 | 44.1 | 44
| Estimated Energy Savings (therms) (With interactivity) |  | 0 | [21 empty] | 44 | 1 | 2 | 4 | 20 | 43 | 43
| Incentive ($) | [23 empty] | 45 | 1 | 2 | 4 | 21 | 43 | 43
[25 empty] | 46 | 1 | 2 | 4 | 22 | 43 | 43
[25 empty] | 47 | 1 | 2 | 4 | 23 | 42.1 | 42
[25 empty] | 48 | 1 | 3 | 5 | 0 | 39.9 | 40
[15 empty] | Outdoor Temperature (F) |  |  |  | Baseline |  | Proposed |  |  |  | 49 | 1 | 3 | 5 | 1 | 37 | 37
[15 empty] | Mid-Point | Range | # of Hours | Burner Firing Rate (%) | Burner Firing Time (min) | EFLH [Heat] | Burner Firing Time (min) | EFLH [Heat] |  |  | 50 | 1 | 3 | 5 | 2 | 36 | 36
[15 empty] | 5 | 4 to 6 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 51 | 1 | 3 | 5 | 3 | 36 | 36
[15 empty] | 7 | 6 to 8 | 7 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 52 | 1 | 3 | 5 | 4 | 36 | 36
[15 empty] | 9 | 8 to 10 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 53 | 1 | 3 | 5 | 5 | 35.1 | 35
[15 empty] | 11 | 10 to 12 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 54 | 1 | 3 | 5 | 6 | 35.1 | 35
[15 empty] | 13 | 12 to 14 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 55 | 1 | 3 | 5 | 7 | 35.1 | 35
[15 empty] | 15 | 14 to 16 | 17 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 56 | 1 | 3 | 5 | 8 | 36 | 36
[15 empty] | 17 | 16 to 18 | 32 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 57 | 1 | 3 | 5 | 9 | 36 | 36
[15 empty] | 19 | 18 to 20 | 56 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 58 | 1 | 3 | 5 | 10 | 37 | 37
[15 empty] | 21 | 20 to 22 | 44 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 59 | 1 | 3 | 5 | 11 | 37.9 | 38
[15 empty] | 23 | 22 to 24 | 36 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 60 | 1 | 3 | 5 | 12 | 39 | 39
[15 empty] | 25 | 24 to 26 | 87 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 61 | 1 | 3 | 5 | 13 | 39.9 | 40
[15 empty] | 27 | 26 to 28 | 114 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 62 | 1 | 3 | 5 | 14 | 39 | 39
[15 empty] | 29 | 28 to 30 | 133 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 63 | 1 | 3 | 5 | 15 | 39.9 | 40
[15 empty] | 31 | 30 to 32 | 171 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 64 | 1 | 3 | 5 | 16 | 39.9 | 40
[15 empty] | 33 | 32 to 34 | 190 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 65 | 1 | 3 | 5 | 17 | 39 | 39
[15 empty] | 35 | 34 to 36 | 249 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 66 | 1 | 3 | 5 | 18 | 37.9 | 38
[15 empty] | 37 | 36 to 38 | 452 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 67 | 1 | 3 | 5 | 19 | 37.9 | 38
[15 empty] | 39 | 38 to 40 | 267 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 68 | 1 | 3 | 5 | 20 | 37 | 37
[15 empty] | 41 | 40 to 42 | 48.6 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 69 | 1 | 3 | 5 | 21 | 35.1 | 35
[15 empty] | 43 | 42 to 44 | 112.2 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 70 | 1 | 3 | 5 | 22 | 35.1 | 35
[15 empty] | 45 | 44 to 46 | 117.6 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 71 | 1 | 3 | 5 | 23 | 35.1 | 35
[15 empty] | 47 | 46 to 48 | 106.8 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 72 | 1 | 4 | 6 | 0 | 35.1 | 35
[15 empty] | 49 | 48 to 50 | 132.6 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 73 | 1 | 4 | 6 | 1 | 35.1 | 35
[15 empty] | 51 | 50 to 52 | 163.2 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 74 | 1 | 4 | 6 | 2 | 35.1 | 35
[15 empty] | 53 | 52 to 54 | 130.8 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 75 | 1 | 4 | 6 | 3 | 34 | 34
[15 empty] | 55 | 54 to 56 | 185.4 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 76 | 1 | 4 | 6 | 4 | 33.1 | 33
[17 empty] | 2874.2 |  |  | #N/A |  | #N/A |  |  | 77 | 1 | 4 | 6 | 5 | 32 | 32
[15 empty] | Reduced EFLH |  |  |  |  | #N/A |  | #N/A |  |  | 78 | 1 | 4 | 6 | 6 | 30 | 30
[25 empty] | 79 | 1 | 4 | 6 | 7 | 28.9 | 29
[25 empty] | 80 | 1 | 4 | 6 | 8 | 28.9 | 29
[25 empty] | 81 | 1 | 4 | 6 | 9 | 30 | 30
[25 empty] | 82 | 1 | 4 | 6 | 10 | 30 | 30
[25 empty] | 83 | 1 | 4 | 6 | 11 | 32 | 32
[25 empty] | 84 | 1 | 4 | 6 | 12 | 33.1 | 33
[25 empty] | 85 | 1 | 4 | 6 | 13 | 34 | 34
[25 empty] | 86 | 1 | 4 | 6 | 14 | 35.1 | 35
[25 empty] | 87 | 1 | 4 | 6 | 15 | 35.1 | 35
[25 empty] | 88 | 1 | 4 | 6 | 16 | 36 | 36
[25 empty] | 89 | 1 | 4 | 6 | 17 | 35.1 | 35
[25 empty] | 90 | 1 | 4 | 6 | 18 | 35.1 | 35
[25 empty] | 91 | 1 | 4 | 6 | 19 | 35.1 | 35
[25 empty] | 92 | 1 | 4 | 6 | 20 | 34 | 34
[25 empty] | 93 | 1 | 4 | 6 | 21 | 34 | 34
[25 empty] | 94 | 1 | 4 | 6 | 22 | 33.1 | 33
[25 empty] | 95 | 1 | 4 | 6 | 23 | 33.1 | 33
[25 empty] | 96 | 1 | 5 | 7 | 0 | 32 | 32
[25 empty] | 97 | 1 | 5 | 7 | 1 | 32 | 32
| Building Info |  |  | Boiler Nameplate Info | [20 empty] | 98 | 1 | 5 | 7 | 2 | 32 | 32
| Address |  |  | Boiler Type | [20 empty] | 99 | 1 | 5 | 7 | 3 | 30.9 | 31
| City |  |  | Boiler Manufacturer | [20 empty] | 100 | 1 | 5 | 7 | 4 | 30.9 | 31
| State |  |  | Boiler Model # | [20 empty] | 101 | 1 | 5 | 7 | 5 | 30.9 | 31
| Zip |  |  | Year Built | [20 empty] | 102 | 1 | 5 | 7 | 6 | 30 | 30
| Area (sq ft) |  |  | Unit Age [as of 2019] | [20 empty] | 103 | 1 | 5 | 7 | 7 | 30.9 | 31
| Year Built |  |  | Input Capacity (MBH) | 0 | [19 empty] | 104 | 1 | 5 | 7 | 8 | 30.9 | 31
| Annual Gas Consumption (therms) |  |  | Output Capacity (MBH) | 0 | [19 empty] | 105 | 1 | 5 | 7 | 9 | 32 | 32
| # of Floors |  |  | Unit Efficiency | 0 | [19 empty] | 106 | 1 | 5 | 7 | 10 | 34 | 34
| # of Apartments |  |  | Vent Type | [20 empty] | 107 | 1 | 5 | 7 | 11 | 36 | 36
| # Bedrooms |  |  | Combustion Air | [20 empty] | 108 | 1 | 5 | 7 | 12 | 36 | 36
| # of Tenants |  |  | Fuel Type | [20 empty] | 109 | 1 | 5 | 7 | 13 | 37.9 | 38
| # of Exposed Steam Supply Risers |  |  | Combi Boiler [Y/N] | [20 empty] | 110 | 1 | 5 | 7 | 14 | 39 | 39
| # of Blind Steam Supply Risers | [23 empty] | 111 | 1 | 5 | 7 | 15 | 37.9 | 38
[25 empty] | 112 | 1 | 5 | 7 | 16 | 39 | 39
[25 empty] | 113 | 1 | 5 | 7 | 17 | 39.9 | 40
[25 empty] | 114 | 1 | 5 | 7 | 18 | 39.9 | 40
[25 empty] | 115 | 1 | 5 | 7 | 19 | 39.9 | 40
[25 empty] | 116 | 1 | 5 | 7 | 20 | 39.9 | 40
[25 empty] | 117 | 1 | 5 | 7 | 21 | 39 | 39
[25 empty] | 118 | 1 | 5 | 7 | 22 | 39.9 | 40
[25 empty] | 119 | 1 | 5 | 7 | 23 | 39.9 | 40
[25 empty] | 120 | 1 | 6 | 1 | 0 | 39.9 | 40
[25 empty] | 121 | 1 | 6 | 1 | 1 | 39 | 39
[25 empty] | 122 | 1 | 6 | 1 | 2 | 39.9 | 40
[25 empty] | 123 | 1 | 6 | 1 | 3 | 39.9 | 40
[25 empty] | 124 | 1 | 6 | 1 | 4 | 39 | 39
[25 empty] | 125 | 1 | 6 | 1 | 5 | 39.9 | 40
[25 empty] | 126 | 1 | 6 | 1 | 6 | 39.9 | 40
[25 empty] | 127 | 1 | 6 | 1 | 7 | 39.9 | 40
[25 empty] | 128 | 1 | 6 | 1 | 8 | 39.9 | 40
[25 empty] | 129 | 1 | 6 | 1 | 9 | 42.1 | 42
[25 empty] | 130 | 1 | 6 | 1 | 10 | 42.1 | 42
[25 empty] | 131 | 1 | 6 | 1 | 11 | 43 | 43
[25 empty] | 132 | 1 | 6 | 1 | 12 | 43 | 43
[25 empty] | 133 | 1 | 6 | 1 | 13 | 44.1 | 44
[25 empty] | 134 | 1 | 6 | 1 | 14 | 42.1 | 42
[25 empty] | 135 | 1 | 6 | 1 | 15 | 42.1 | 42
[25 empty] | 136 | 1 | 6 | 1 | 16 | 41 | 41
[25 empty] | 137 | 1 | 6 | 1 | 17 | 42.1 | 42
[25 empty] | 138 | 1 | 6 | 1 | 18 | 41 | 41
[25 empty] | 139 | 1 | 6 | 1 | 19 | 41 | 41
[25 empty] | 140 | 1 | 6 | 1 | 20 | 41 | 41
[25 empty] | 141 | 1 | 6 | 1 | 21 | 41 | 41
[25 empty] | 142 | 1 | 6 | 1 | 22 | 39.9 | 40
[25 empty] | 143 | 1 | 6 | 1 | 23 | 39.9 | 40
[25 empty] | 144 | 1 | 7 | 2 | 0 | 39.9 | 40
[25 empty] | 145 | 1 | 7 | 2 | 1 | 39 | 39
[25 empty] | 146 | 1 | 7 | 2 | 2 | 37.9 | 38
[25 empty] | 147 | 1 | 7 | 2 | 3 | 37 | 37
[25 empty] | 148 | 1 | 7 | 2 | 4 | 37 | 37
[25 empty] | 149 | 1 | 7 | 2 | 5 | 37 | 37
[25 empty] | 150 | 1 | 7 | 2 | 6 | 36 | 36
[25 empty] | 151 | 1 | 7 | 2 | 7 | 36 | 36
[25 empty] | 152 | 1 | 7 | 2 | 8 | 36 | 36
[25 empty] | 153 | 1 | 7 | 2 | 9 | 36 | 36
[25 empty] | 154 | 1 | 7 | 2 | 10 | 36 | 36
[25 empty] | 155 | 1 | 7 | 2 | 11 | 36 | 36
[25 empty] | 156 | 1 | 7 | 2 | 12 | 36 | 36
[25 empty] | 157 | 1 | 7 | 2 | 13 | 36 | 36
[25 empty] | 158 | 1 | 7 | 2 | 14 | 35.1 | 35
[25 empty] | 159 | 1 | 7 | 2 | 15 | 35.1 | 35
[25 empty] | 160 | 1 | 7 | 2 | 16 | 35.1 | 35
[25 empty] | 161 | 1 | 7 | 2 | 17 | 34 | 34
[25 empty] | 162 | 1 | 7 | 2 | 18 | 32 | 32
[25 empty] | 163 | 1 | 7 | 2 | 19 | 30.9 | 31
[25 empty] | 164 | 1 | 7 | 2 | 20 | 28.9 | 29
[25 empty] | 165 | 1 | 7 | 2 | 21 | 28 | 28
[25 empty] | 166 | 1 | 7 | 2 | 22 | 27 | 27
[25 empty] | 167 | 1 | 7 | 2 | 23 | 26.1 | 26
[25 empty] | 168 | 1 | 8 | 3 | 0 | 25 | 25
[25 empty] | 169 | 1 | 8 | 3 | 1 | 24.1 | 24
[25 empty] | 170 | 1 | 8 | 3 | 2 | 23 | 23
[25 empty] | 171 | 1 | 8 | 3 | 3 | 21.9 | 22
[25 empty] | 172 | 1 | 8 | 3 | 4 | 21.9 | 22
[25 empty] | 173 | 1 | 8 | 3 | 5 | 21 | 21
[25 empty] | 174 | 1 | 8 | 3 | 6 | 21 | 21
[25 empty] | 175 | 1 | 8 | 3 | 7 | 21 | 21
[25 empty] | 176 | 1 | 8 | 3 | 8 | 21.9 | 22
[25 empty] | 177 | 1 | 8 | 3 | 9 | 21 | 21
[25 empty] | 178 | 1 | 8 | 3 | 10 | 21.9 | 22
[25 empty] | 179 | 1 | 8 | 3 | 11 | 23 | 23
[25 empty] | 180 | 1 | 8 | 3 | 12 | 24.1 | 24
[25 empty] | 181 | 1 | 8 | 3 | 13 | 26.1 | 26
[25 empty] | 182 | 1 | 8 | 3 | 14 | 27 | 27
[25 empty] | 183 | 1 | 8 | 3 | 15 | 28 | 28
[25 empty] | 184 | 1 | 8 | 3 | 16 | 30 | 30
[25 empty] | 185 | 1 | 8 | 3 | 17 | 30 | 30
[25 empty] | 186 | 1 | 8 | 3 | 18 | 30 | 30
[25 empty] | 187 | 1 | 8 | 3 | 19 | 30 | 30
[25 empty] | 188 | 1 | 8 | 3 | 20 | 30.9 | 31
[25 empty] | 189 | 1 | 8 | 3 | 21 | 30 | 30
[25 empty] | 190 | 1 | 8 | 3 | 22 | 30 | 30
[25 empty] | 191 | 1 | 8 | 3 | 23 | 30 | 30
[25 empty] | 192 | 1 | 9 | 4 | 0 | 30 | 30
[25 empty] | 193 | 1 | 9 | 4 | 1 | 28.9 | 29
[25 empty] | 194 | 1 | 9 | 4 | 2 | 28 | 28
[25 empty] | 195 | 1 | 9 | 4 | 3 | 28.9 | 29
[25 empty] | 196 | 1 | 9 | 4 | 4 | 28.9 | 29
[25 empty] | 197 | 1 | 9 | 4 | 5 | 28.9 | 29
[25 empty] | 198 | 1 | 9 | 4 | 6 | 30 | 30
[25 empty] | 199 | 1 | 9 | 4 | 7 | 30.9 | 31
[25 empty] | 200 | 1 | 9 | 4 | 8 | 30.9 | 31
[25 empty] | 201 | 1 | 9 | 4 | 9 | 30.9 | 31
[25 empty] | 202 | 1 | 9 | 4 | 10 | 30.9 | 31
[25 empty] | 203 | 1 | 9 | 4 | 11 | 33.1 | 33
[25 empty] | 204 | 1 | 9 | 4 | 12 | 33.1 | 33
[25 empty] | 205 | 1 | 9 | 4 | 13 | 33.1 | 33
[25 empty] | 206 | 1 | 9 | 4 | 14 | 34 | 34
[25 empty] | 207 | 1 | 9 | 4 | 15 | 34 | 34
[25 empty] | 208 | 1 | 9 | 4 | 16 | 35.1 | 35
[25 empty] | 209 | 1 | 9 | 4 | 17 | 35.1 | 35
[25 empty] | 210 | 1 | 9 | 4 | 18 | 35.1 | 35
[25 empty] | 211 | 1 | 9 | 4 | 19 | 35.1 | 35
[25 empty] | 212 | 1 | 9 | 4 | 20 | 34 | 34
[25 empty] | 213 | 1 | 9 | 4 | 21 | 34 | 34
[25 empty] | 214 | 1 | 9 | 4 | 22 | 35.1 | 35
[25 empty] | 215 | 1 | 9 | 4 | 23 | 37 | 37
[25 empty] | 216 | 1 | 10 | 5 | 0 | 39 | 39
[25 empty] | 217 | 1 | 10 | 5 | 1 | 39.9 | 40
[25 empty] | 218 | 1 | 10 | 5 | 2 | 39 | 39
[25 empty] | 219 | 1 | 10 | 5 | 3 | 39 | 39
[25 empty] | 220 | 1 | 10 | 5 | 4 | 39 | 39
[25 empty] | 221 | 1 | 10 | 5 | 5 | 37.9 | 38
[25 empty] | 222 | 1 | 10 | 5 | 6 | 37.9 | 38
[25 empty] | 223 | 1 | 10 | 5 | 7 | 37.9 | 38
[25 empty] | 224 | 1 | 10 | 5 | 8 | 37.9 | 38
[25 empty] | 225 | 1 | 10 | 5 | 9 | 39 | 39
[25 empty] | 226 | 1 | 10 | 5 | 10 | 39.9 | 40
[25 empty] | 227 | 1 | 10 | 5 | 11 | 39.9 | 40
[25 empty] | 228 | 1 | 10 | 5 | 12 | 39.9 | 40
[25 empty] | 229 | 1 | 10 | 5 | 13 | 39.9 | 40
[25 empty] | 230 | 1 | 10 | 5 | 14 | 39.9 | 40
[25 empty] | 231 | 1 | 10 | 5 | 15 | 39.9 | 40
[25 empty] | 232 | 1 | 10 | 5 | 16 | 39.9 | 40
[25 empty] | 233 | 1 | 10 | 5 | 17 | 39.9 | 40
[25 empty] | 234 | 1 | 10 | 5 | 18 | 37 | 37
[25 empty] | 235 | 1 | 10 | 5 | 19 | 36 | 36
[25 empty] | 236 | 1 | 10 | 5 | 20 | 34 | 34
[25 empty] | 237 | 1 | 10 | 5 | 21 | 32 | 32
[25 empty] | 238 | 1 | 10 | 5 | 22 | 30.9 | 31
[25 empty] | 239 | 1 | 10 | 5 | 23 | 30 | 30
[25 empty] | 240 | 1 | 11 | 6 | 0 | 28 | 28
[25 empty] | 241 | 1 | 11 | 6 | 1 | 27 | 27
[25 empty] | 242 | 1 | 11 | 6 | 2 | 26.1 | 26
[25 empty] | 243 | 1 | 11 | 6 | 3 | 26.1 | 26
[25 empty] | 244 | 1 | 11 | 6 | 4 | 25 | 25
[25 empty] | 245 | 1 | 11 | 6 | 5 | 24.1 | 24
[25 empty] | 246 | 1 | 11 | 6 | 6 | 24.1 | 24
[25 empty] | 247 | 1 | 11 | 6 | 7 | 24.1 | 24
[25 empty] | 248 | 1 | 11 | 6 | 8 | 25 | 25
[25 empty] | 249 | 1 | 11 | 6 | 9 | 25 | 25
[25 empty] | 250 | 1 | 11 | 6 | 10 | 24.1 | 24
[25 empty] | 251 | 1 | 11 | 6 | 11 | 23 | 23
[25 empty] | 252 | 1 | 11 | 6 | 12 | 21 | 21
[25 empty] | 253 | 1 | 11 | 6 | 13 | 23 | 23
[25 empty] | 254 | 1 | 11 | 6 | 14 | 24.1 | 24
[25 empty] | 255 | 1 | 11 | 6 | 15 | 24.1 | 24
[25 empty] | 256 | 1 | 11 | 6 | 16 | 26.1 | 26
[25 empty] | 257 | 1 | 11 | 6 | 17 | 28 | 28
[25 empty] | 258 | 1 | 11 | 6 | 18 | 28.9 | 29
[25 empty] | 259 | 1 | 11 | 6 | 19 | 30 | 30
[25 empty] | 260 | 1 | 11 | 6 | 20 | 28.9 | 29
[25 empty] | 261 | 1 | 11 | 6 | 21 | 30.9 | 31
[25 empty] | 262 | 1 | 11 | 6 | 22 | 30.9 | 31
[25 empty] | 263 | 1 | 11 | 6 | 23 | 33.1 | 33
[25 empty] | 264 | 1 | 12 | 7 | 0 | 34 | 34
[25 empty] | 265 | 1 | 12 | 7 | 1 | 35.1 | 35
[25 empty] | 266 | 1 | 12 | 7 | 2 | 35.1 | 35
[25 empty] | 267 | 1 | 12 | 7 | 3 | 37 | 37
[25 empty] | 268 | 1 | 12 | 7 | 4 | 37.9 | 38
[25 empty] | 269 | 1 | 12 | 7 | 5 | 37 | 37
[25 empty] | 270 | 1 | 12 | 7 | 6 | 37 | 37
[25 empty] | 271 | 1 | 12 | 7 | 7 | 37 | 37
[25 empty] | 272 | 1 | 12 | 7 | 8 | 33.1 | 33
[25 empty] | 273 | 1 | 12 | 7 | 9 | 32 | 32
[25 empty] | 274 | 1 | 12 | 7 | 10 | 32 | 32
[25 empty] | 275 | 1 | 12 | 7 | 11 | 33.1 | 33
[25 empty] | 276 | 1 | 12 | 7 | 12 | 32 | 32
[25 empty] | 277 | 1 | 12 | 7 | 13 | 33.1 | 33
[25 empty] | 278 | 1 | 12 | 7 | 14 | 33.1 | 33
[25 empty] | 279 | 1 | 12 | 7 | 15 | 34 | 34
[25 empty] | 280 | 1 | 12 | 7 | 16 | 34 | 34
[25 empty] | 281 | 1 | 12 | 7 | 17 | 34 | 34
[25 empty] | 282 | 1 | 12 | 7 | 18 | 34 | 34
[25 empty] | 283 | 1 | 12 | 7 | 19 | 34 | 34
[25 empty] | 284 | 1 | 12 | 7 | 20 | 34 | 34
[25 empty] | 285 | 1 | 12 | 7 | 21 | 34 | 34
[25 empty] | 286 | 1 | 12 | 7 | 22 | 35.1 | 35
[25 empty] | 287 | 1 | 12 | 7 | 23 | 35.1 | 35
[25 empty] | 288 | 1 | 13 | 1 | 0 | 36 | 36
[25 empty] | 289 | 1 | 13 | 1 | 1 | 36 | 36
[25 empty] | 290 | 1 | 13 | 1 | 2 | 37 | 37
[25 empty] | 291 | 1 | 13 | 1 | 3 | 37.9 | 38
[25 empty] | 292 | 1 | 13 | 1 | 4 | 37.9 | 38
[25 empty] | 293 | 1 | 13 | 1 | 5 | 36 | 36
[25 empty] | 294 | 1 | 13 | 1 | 6 | 34 | 34
[25 empty] | 295 | 1 | 13 | 1 | 7 | 33.1 | 33
[25 empty] | 296 | 1 | 13 | 1 | 8 | 32 | 32
[25 empty] | 297 | 1 | 13 | 1 | 9 | 30.9 | 31
[25 empty] | 298 | 1 | 13 | 1 | 10 | 30.9 | 31
[25 empty] | 299 | 1 | 13 | 1 | 11 | 30.9 | 31
[25 empty] | 300 | 1 | 13 | 1 | 12 | 32 | 32
[25 empty] | 301 | 1 | 13 | 1 | 13 | 32 | 32
[25 empty] | 302 | 1 | 13 | 1 | 14 | 32 | 32
[25 empty] | 303 | 1 | 13 | 1 | 15 | 32 | 32
[25 empty] | 304 | 1 | 13 | 1 | 16 | 33.1 | 33
[25 empty] | 305 | 1 | 13 | 1 | 17 | 32 | 32
[25 empty] | 306 | 1 | 13 | 1 | 18 | 30.9 | 31
[25 empty] | 307 | 1 | 13 | 1 | 19 | 30.9 | 31
[25 empty] | 308 | 1 | 13 | 1 | 20 | 30 | 30
[25 empty] | 309 | 1 | 13 | 1 | 21 | 28.9 | 29
[25 empty] | 310 | 1 | 13 | 1 | 22 | 28 | 28
[25 empty] | 311 | 1 | 13 | 1 | 23 | 28 | 28
[25 empty] | 312 | 1 | 14 | 2 | 0 | 27 | 27
[25 empty] | 313 | 1 | 14 | 2 | 1 | 27 | 27
[25 empty] | 314 | 1 | 14 | 2 | 2 | 27 | 27
[25 empty] | 315 | 1 | 14 | 2 | 3 | 27 | 27
[25 empty] | 316 | 1 | 14 | 2 | 4 | 26.1 | 26
[25 empty] | 317 | 1 | 14 | 2 | 5 | 26.1 | 26
[25 empty] | 318 | 1 | 14 | 2 | 6 | 26.1 | 26
[25 empty] | 319 | 1 | 14 | 2 | 7 | 26.1 | 26
[25 empty] | 320 | 1 | 14 | 2 | 8 | 27 | 27
[25 empty] | 321 | 1 | 14 | 2 | 9 | 30 | 30
[25 empty] | 322 | 1 | 14 | 2 | 10 | 30.9 | 31
[25 empty] | 323 | 1 | 14 | 2 | 11 | 32 | 32
[25 empty] | 324 | 1 | 14 | 2 | 12 | 33.1 | 33
[25 empty] | 325 | 1 | 14 | 2 | 13 | 33.1 | 33
[25 empty] | 326 | 1 | 14 | 2 | 14 | 36 | 36
[25 empty] | 327 | 1 | 14 | 2 | 15 | 37 | 37
[25 empty] | 328 | 1 | 14 | 2 | 16 | 37 | 37
[25 empty] | 329 | 1 | 14 | 2 | 17 | 37 | 37
[25 empty] | 330 | 1 | 14 | 2 | 18 | 37 | 37
[25 empty] | 331 | 1 | 14 | 2 | 19 | 37 | 37
[25 empty] | 332 | 1 | 14 | 2 | 20 | 37 | 37
[25 empty] | 333 | 1 | 14 | 2 | 21 | 37 | 37
[25 empty] | 334 | 1 | 14 | 2 | 22 | 36 | 36
[25 empty] | 335 | 1 | 14 | 2 | 23 | 35.1 | 35
[25 empty] | 336 | 1 | 15 | 3 | 0 | 35.1 | 35
[25 empty] | 337 | 1 | 15 | 3 | 1 | 35.1 | 35
[25 empty] | 338 | 1 | 15 | 3 | 2 | 35.1 | 35
[25 empty] | 339 | 1 | 15 | 3 | 3 | 36 | 36
[25 empty] | 340 | 1 | 15 | 3 | 4 | 35.1 | 35
[25 empty] | 341 | 1 | 15 | 3 | 5 | 34 | 34
[25 empty] | 342 | 1 | 15 | 3 | 6 | 35.1 | 35
[25 empty] | 343 | 1 | 15 | 3 | 7 | 35.1 | 35
[25 empty] | 344 | 1 | 15 | 3 | 8 | 36 | 36
[25 empty] | 345 | 1 | 15 | 3 | 9 | 39 | 39
[25 empty] | 346 | 1 | 15 | 3 | 10 | 41 | 41
[25 empty] | 347 | 1 | 15 | 3 | 11 | 43 | 43
[25 empty] | 348 | 1 | 15 | 3 | 12 | 44.1 | 44
[25 empty] | 349 | 1 | 15 | 3 | 13 | 46 | 46
[25 empty] | 350 | 1 | 15 | 3 | 14 | 48 | 48
[25 empty] | 351 | 1 | 15 | 3 | 15 | 48.9 | 49
[25 empty] | 352 | 1 | 15 | 3 | 16 | 48.9 | 49
[25 empty] | 353 | 1 | 15 | 3 | 17 | 45 | 45
[25 empty] | 354 | 1 | 15 | 3 | 18 | 43 | 43
[25 empty] | 355 | 1 | 15 | 3 | 19 | 41 | 41
[25 empty] | 356 | 1 | 15 | 3 | 20 | 39.9 | 40
[25 empty] | 357 | 1 | 15 | 3 | 21 | 37.9 | 38
[25 empty] | 358 | 1 | 15 | 3 | 22 | 37 | 37
[25 empty] | 359 | 1 | 15 | 3 | 23 | 37 | 37
[25 empty] | 360 | 1 | 16 | 4 | 0 | 37 | 37
[25 empty] | 361 | 1 | 16 | 4 | 1 | 37 | 37
[25 empty] | 362 | 1 | 16 | 4 | 2 | 37.9 | 38
[25 empty] | 363 | 1 | 16 | 4 | 3 | 37 | 37
[25 empty] | 364 | 1 | 16 | 4 | 4 | 37.9 | 38
[25 empty] | 365 | 1 | 16 | 4 | 5 | 37.9 | 38
[25 empty] | 366 | 1 | 16 | 4 | 6 | 37.9 | 38
[25 empty] | 367 | 1 | 16 | 4 | 7 | 37.9 | 38
[25 empty] | 368 | 1 | 16 | 4 | 8 | 37.9 | 38
[25 empty] | 369 | 1 | 16 | 4 | 9 | 39 | 39
[25 empty] | 370 | 1 | 16 | 4 | 10 | 39.9 | 40
[25 empty] | 371 | 1 | 16 | 4 | 11 | 42.1 | 42
[25 empty] | 372 | 1 | 16 | 4 | 12 | 51.1 | 51
[25 empty] | 373 | 1 | 16 | 4 | 13 | 53.1 | 53
[25 empty] | 374 | 1 | 16 | 4 | 14 | 53.1 | 53
[25 empty] | 375 | 1 | 16 | 4 | 15 | 52 | 52
[25 empty] | 376 | 1 | 16 | 4 | 16 | 53.1 | 53
[25 empty] | 377 | 1 | 16 | 4 | 17 | 52 | 52
[25 empty] | 378 | 1 | 16 | 4 | 18 | 53.1 | 53
[25 empty] | 379 | 1 | 16 | 4 | 19 | 53.1 | 53
[25 empty] | 380 | 1 | 16 | 4 | 20 | 52 | 52
[25 empty] | 381 | 1 | 16 | 4 | 21 | 50 | 50
[25 empty] | 382 | 1 | 16 | 4 | 22 | 51.1 | 51
[25 empty] | 383 | 1 | 16 | 4 | 23 | 50 | 50
[25 empty] | 384 | 1 | 17 | 5 | 0 | 50 | 50
[25 empty] | 385 | 1 | 17 | 5 | 1 | 48.9 | 49
[25 empty] | 386 | 1 | 17 | 5 | 2 | 46.9 | 47
[25 empty] | 387 | 1 | 17 | 5 | 3 | 46.9 | 47
[25 empty] | 388 | 1 | 17 | 5 | 4 | 48 | 48
[25 empty] | 389 | 1 | 17 | 5 | 5 | 46.9 | 47
[25 empty] | 390 | 1 | 17 | 5 | 6 | 46.9 | 47
[25 empty] | 391 | 1 | 17 | 5 | 7 | 46.9 | 47
[25 empty] | 392 | 1 | 17 | 5 | 8 | 46 | 46
[25 empty] | 393 | 1 | 17 | 5 | 9 | 46 | 46
[25 empty] | 394 | 1 | 17 | 5 | 10 | 46.9 | 47
[25 empty] | 395 | 1 | 17 | 5 | 11 | 46.9 | 47
[25 empty] | 396 | 1 | 17 | 5 | 12 | 46 | 46
[25 empty] | 397 | 1 | 17 | 5 | 13 | 45 | 45
[25 empty] | 398 | 1 | 17 | 5 | 14 | 45 | 45
[25 empty] | 399 | 1 | 17 | 5 | 15 | 45 | 45
[25 empty] | 400 | 1 | 17 | 5 | 16 | 44.1 | 44
[25 empty] | 401 | 1 | 17 | 5 | 17 | 44.1 | 44
[25 empty] | 402 | 1 | 17 | 5 | 18 | 43 | 43
[25 empty] | 403 | 1 | 17 | 5 | 19 | 43 | 43
[25 empty] | 404 | 1 | 17 | 5 | 20 | 41 | 41
[25 empty] | 405 | 1 | 17 | 5 | 21 | 41 | 41
[25 empty] | 406 | 1 | 17 | 5 | 22 | 39.9 | 40
[25 empty] | 407 | 1 | 17 | 5 | 23 | 39.9 | 40
[25 empty] | 408 | 1 | 18 | 6 | 0 | 39.9 | 40
[25 empty] | 409 | 1 | 18 | 6 | 1 | 39.9 | 40
[25 empty] | 410 | 1 | 18 | 6 | 2 | 39 | 39
[25 empty] | 411 | 1 | 18 | 6 | 3 | 37.9 | 38
[25 empty] | 412 | 1 | 18 | 6 | 4 | 37.9 | 38
[25 empty] | 413 | 1 | 18 | 6 | 5 | 37.9 | 38
[25 empty] | 414 | 1 | 18 | 6 | 6 | 37.9 | 38
[25 empty] | 415 | 1 | 18 | 6 | 7 | 37.9 | 38
[25 empty] | 416 | 1 | 18 | 6 | 8 | 37.9 | 38
[25 empty] | 417 | 1 | 18 | 6 | 9 | 37.9 | 38
[25 empty] | 418 | 1 | 18 | 6 | 10 | 37.9 | 38
[25 empty] | 419 | 1 | 18 | 6 | 11 | 37.9 | 38
[25 empty] | 420 | 1 | 18 | 6 | 12 | 39 | 39
[25 empty] | 421 | 1 | 18 | 6 | 13 | 39 | 39
[25 empty] | 422 | 1 | 18 | 6 | 14 | 39.9 | 40
[25 empty] | 423 | 1 | 18 | 6 | 15 | 39.9 | 40
[25 empty] | 424 | 1 | 18 | 6 | 16 | 41 | 41
[25 empty] | 425 | 1 | 18 | 6 | 17 | 39 | 39
[25 empty] | 426 | 1 | 18 | 6 | 18 | 39 | 39
[25 empty] | 427 | 1 | 18 | 6 | 19 | 39 | 39
[25 empty] | 428 | 1 | 18 | 6 | 20 | 39 | 39
[25 empty] | 429 | 1 | 18 | 6 | 21 | 39 | 39
[25 empty] | 430 | 1 | 18 | 6 | 22 | 39.9 | 40
[25 empty] | 431 | 1 | 18 | 6 | 23 | 39 | 39
[25 empty] | 432 | 1 | 19 | 7 | 0 | 37.9 | 38
[25 empty] | 433 | 1 | 19 | 7 | 1 | 37.9 | 38
[25 empty] | 434 | 1 | 19 | 7 | 2 | 37.9 | 38
[25 empty] | 435 | 1 | 19 | 7 | 3 | 37.9 | 38
[25 empty] | 436 | 1 | 19 | 7 | 4 | 39 | 39
[25 empty] | 437 | 1 | 19 | 7 | 5 | 37.9 | 38
[25 empty] | 438 | 1 | 19 | 7 | 6 | 37.9 | 38
[25 empty] | 439 | 1 | 19 | 7 | 7 | 37 | 37
[25 empty] | 440 | 1 | 19 | 7 | 8 | 37.9 | 38
[25 empty] | 441 | 1 | 19 | 7 | 9 | 39 | 39
[25 empty] | 442 | 1 | 19 | 7 | 10 | 39.9 | 40
[25 empty] | 443 | 1 | 19 | 7 | 11 | 42.1 | 42
[25 empty] | 444 | 1 | 19 | 7 | 12 | 44.1 | 44
[25 empty] | 445 | 1 | 19 | 7 | 13 | 45 | 45
[25 empty] | 446 | 1 | 19 | 7 | 14 | 46.9 | 47
[25 empty] | 447 | 1 | 19 | 7 | 15 | 48 | 48
[25 empty] | 448 | 1 | 19 | 7 | 16 | 48.9 | 49
[25 empty] | 449 | 1 | 19 | 7 | 17 | 46.9 | 47
[25 empty] | 450 | 1 | 19 | 7 | 18 | 46.9 | 47
[25 empty] | 451 | 1 | 19 | 7 | 19 | 48 | 48
[25 empty] | 452 | 1 | 19 | 7 | 20 | 46 | 46
[25 empty] | 453 | 1 | 19 | 7 | 21 | 46 | 46
[25 empty] | 454 | 1 | 19 | 7 | 22 | 45 | 45
[25 empty] | 455 | 1 | 19 | 7 | 23 | 45 | 45
[25 empty] | 456 | 1 | 20 | 1 | 0 | 45 | 45
[25 empty] | 457 | 1 | 20 | 1 | 1 | 45 | 45
[25 empty] | 458 | 1 | 20 | 1 | 2 | 43 | 43
[25 empty] | 459 | 1 | 20 | 1 | 3 | 42.1 | 42
[25 empty] | 460 | 1 | 20 | 1 | 4 | 42.1 | 42
[25 empty] | 461 | 1 | 20 | 1 | 5 | 42.1 | 42
[25 empty] | 462 | 1 | 20 | 1 | 6 | 42.1 | 42
[25 empty] | 463 | 1 | 20 | 1 | 7 | 42.1 | 42
[25 empty] | 464 | 1 | 20 | 1 | 8 | 41 | 41
[25 empty] | 465 | 1 | 20 | 1 | 9 | 42.1 | 42
[25 empty] | 466 | 1 | 20 | 1 | 10 | 45 | 45
[25 empty] | 467 | 1 | 20 | 1 | 11 | 46.9 | 47
[25 empty] | 468 | 1 | 20 | 1 | 12 | 50 | 50
[25 empty] | 469 | 1 | 20 | 1 | 13 | 51.1 | 51
[25 empty] | 470 | 1 | 20 | 1 | 14 | 52 | 52
[25 empty] | 471 | 1 | 20 | 1 | 15 | 52 | 52
[25 empty] | 472 | 1 | 20 | 1 | 16 | 50 | 50
[25 empty] | 473 | 1 | 20 | 1 | 17 | 48.9 | 49
[25 empty] | 474 | 1 | 20 | 1 | 18 | 48 | 48
[25 empty] | 475 | 1 | 20 | 1 | 19 | 46.9 | 47
[25 empty] | 476 | 1 | 20 | 1 | 20 | 46.9 | 47
[25 empty] | 477 | 1 | 20 | 1 | 21 | 46 | 46
[25 empty] | 478 | 1 | 20 | 1 | 22 | 46 | 46
[25 empty] | 479 | 1 | 20 | 1 | 23 | 45 | 45
[25 empty] | 480 | 1 | 21 | 2 | 0 | 44.1 | 44
[25 empty] | 481 | 1 | 21 | 2 | 1 | 42.1 | 42
[25 empty] | 482 | 1 | 21 | 2 | 2 | 39.9 | 40
[25 empty] | 483 | 1 | 21 | 2 | 3 | 39 | 39
[25 empty] | 484 | 1 | 21 | 2 | 4 | 37 | 37
[25 empty] | 485 | 1 | 21 | 2 | 5 | 36 | 36
[25 empty] | 486 | 1 | 21 | 2 | 6 | 35.1 | 35
[25 empty] | 487 | 1 | 21 | 2 | 7 | 35.1 | 35
[25 empty] | 488 | 1 | 21 | 2 | 8 | 36 | 36
[25 empty] | 489 | 1 | 21 | 2 | 9 | 30 | 30
[25 empty] | 490 | 1 | 21 | 2 | 10 | 27 | 27
[25 empty] | 491 | 1 | 21 | 2 | 11 | 25 | 25
[25 empty] | 492 | 1 | 21 | 2 | 12 | 25 | 25
[25 empty] | 493 | 1 | 21 | 2 | 13 | 24.1 | 24
[25 empty] | 494 | 1 | 21 | 2 | 14 | 26.1 | 26
[25 empty] | 495 | 1 | 21 | 2 | 15 | 25 | 25
[25 empty] | 496 | 1 | 21 | 2 | 16 | 25 | 25
[25 empty] | 497 | 1 | 21 | 2 | 17 | 25 | 25
[25 empty] | 498 | 1 | 21 | 2 | 18 | 24.1 | 24
[25 empty] | 499 | 1 | 21 | 2 | 19 | 23 | 23
[25 empty] | 500 | 1 | 21 | 2 | 20 | 21.9 | 22
[25 empty] | 501 | 1 | 21 | 2 | 21 | 19 | 19
[25 empty] | 502 | 1 | 21 | 2 | 22 | 18 | 18
[25 empty] | 503 | 1 | 21 | 2 | 23 | 17.1 | 17
[25 empty] | 504 | 1 | 22 | 3 | 0 | 16 | 16
[25 empty] | 505 | 1 | 22 | 3 | 1 | 15.1 | 15
[25 empty] | 506 | 1 | 22 | 3 | 2 | 12.9 | 13
[25 empty] | 507 | 1 | 22 | 3 | 3 | 12.9 | 13
[25 empty] | 508 | 1 | 22 | 3 | 4 | 12.9 | 13
[25 empty] | 509 | 1 | 22 | 3 | 5 | 10.9 | 11
[25 empty] | 510 | 1 | 22 | 3 | 6 | 10.9 | 11
[25 empty] | 511 | 1 | 22 | 3 | 7 | 10 | 10
[25 empty] | 512 | 1 | 22 | 3 | 8 | 10 | 10
[25 empty] | 513 | 1 | 22 | 3 | 9 | 10.9 | 11
[25 empty] | 514 | 1 | 22 | 3 | 10 | 12 | 12
[25 empty] | 515 | 1 | 22 | 3 | 11 | 12.9 | 13
[25 empty] | 516 | 1 | 22 | 3 | 12 | 15.1 | 15
[25 empty] | 517 | 1 | 22 | 3 | 13 | 16 | 16
[25 empty] | 518 | 1 | 22 | 3 | 14 | 18 | 18
[25 empty] | 519 | 1 | 22 | 3 | 15 | 19 | 19
[25 empty] | 520 | 1 | 22 | 3 | 16 | 19.9 | 20
[25 empty] | 521 | 1 | 22 | 3 | 17 | 19.9 | 20
[25 empty] | 522 | 1 | 22 | 3 | 18 | 19.9 | 20
[25 empty] | 523 | 1 | 22 | 3 | 19 | 19 | 19
[25 empty] | 524 | 1 | 22 | 3 | 20 | 18 | 18
[25 empty] | 525 | 1 | 22 | 3 | 21 | 18 | 18
[25 empty] | 526 | 1 | 22 | 3 | 22 | 17.1 | 17
[25 empty] | 527 | 1 | 22 | 3 | 23 | 17.1 | 17
[25 empty] | 528 | 1 | 23 | 4 | 0 | 17.1 | 17
[25 empty] | 529 | 1 | 23 | 4 | 1 | 17.1 | 17
[25 empty] | 530 | 1 | 23 | 4 | 2 | 17.1 | 17
[25 empty] | 531 | 1 | 23 | 4 | 3 | 17.1 | 17
[25 empty] | 532 | 1 | 23 | 4 | 4 | 17.1 | 17
[25 empty] | 533 | 1 | 23 | 4 | 5 | 17.1 | 17
[25 empty] | 534 | 1 | 23 | 4 | 6 | 18 | 18
[25 empty] | 535 | 1 | 23 | 4 | 7 | 19.9 | 20
[25 empty] | 536 | 1 | 23 | 4 | 8 | 21 | 21
[25 empty] | 537 | 1 | 23 | 4 | 9 | 24.1 | 24
[25 empty] | 538 | 1 | 23 | 4 | 10 | 27 | 27
[25 empty] | 539 | 1 | 23 | 4 | 11 | 30 | 30
[25 empty] | 540 | 1 | 23 | 4 | 12 | 30.9 | 31
[25 empty] | 541 | 1 | 23 | 4 | 13 | 33.1 | 33
[25 empty] | 542 | 1 | 23 | 4 | 14 | 34 | 34
[25 empty] | 543 | 1 | 23 | 4 | 15 | 35.1 | 35
[25 empty] | 544 | 1 | 23 | 4 | 16 | 35.1 | 35
[25 empty] | 545 | 1 | 23 | 4 | 17 | 35.1 | 35
[25 empty] | 546 | 1 | 23 | 4 | 18 | 35.1 | 35
[25 empty] | 547 | 1 | 23 | 4 | 19 | 35.1 | 35
[25 empty] | 548 | 1 | 23 | 4 | 20 | 36 | 36
[25 empty] | 549 | 1 | 23 | 4 | 21 | 35.1 | 35
[25 empty] | 550 | 1 | 23 | 4 | 22 | 35.1 | 35
[25 empty] | 551 | 1 | 23 | 4 | 23 | 35.1 | 35
[25 empty] | 552 | 1 | 24 | 5 | 0 | 35.1 | 35
[25 empty] | 553 | 1 | 24 | 5 | 1 | 34 | 34
[25 empty] | 554 | 1 | 24 | 5 | 2 | 34 | 34
[25 empty] | 555 | 1 | 24 | 5 | 3 | 35.1 | 35
[25 empty] | 556 | 1 | 24 | 5 | 4 | 35.1 | 35
[25 empty] | 557 | 1 | 24 | 5 | 5 | 35.1 | 35
[25 empty] | 558 | 1 | 24 | 5 | 6 | 35.1 | 35
[25 empty] | 559 | 1 | 24 | 5 | 7 | 34 | 34
[25 empty] | 560 | 1 | 24 | 5 | 8 | 35.1 | 35
[25 empty] | 561 | 1 | 24 | 5 | 9 | 36 | 36
[25 empty] | 562 | 1 | 24 | 5 | 10 | 37 | 37
[25 empty] | 563 | 1 | 24 | 5 | 11 | 39 | 39
[25 empty] | 564 | 1 | 24 | 5 | 12 | 39 | 39
[25 empty] | 565 | 1 | 24 | 5 | 13 | 39 | 39
[25 empty] | 566 | 1 | 24 | 5 | 14 | 39 | 39
[25 empty] | 567 | 1 | 24 | 5 | 15 | 39 | 39
[25 empty] | 568 | 1 | 24 | 5 | 16 | 39 | 39
[25 empty] | 569 | 1 | 24 | 5 | 17 | 39 | 39
[25 empty] | 570 | 1 | 24 | 5 | 18 | 37 | 37
[25 empty] | 571 | 1 | 24 | 5 | 19 | 35.1 | 35
[25 empty] | 572 | 1 | 24 | 5 | 20 | 33.1 | 33
[25 empty] | 573 | 1 | 24 | 5 | 21 | 33.1 | 33
[25 empty] | 574 | 1 | 24 | 5 | 22 | 30.9 | 31
[25 empty] | 575 | 1 | 24 | 5 | 23 | 28 | 28
[25 empty] | 576 | 1 | 25 | 6 | 0 | 26.1 | 26
[25 empty] | 577 | 1 | 25 | 6 | 1 | 25 | 25
[25 empty] | 578 | 1 | 25 | 6 | 2 | 24.1 | 24
[25 empty] | 579 | 1 | 25 | 6 | 3 | 23 | 23
[25 empty] | 580 | 1 | 25 | 6 | 4 | 21 | 21
[25 empty] | 581 | 1 | 25 | 6 | 5 | 19.9 | 20
[25 empty] | 582 | 1 | 25 | 6 | 6 | 19 | 19
[25 empty] | 583 | 1 | 25 | 6 | 7 | 19 | 19
[25 empty] | 584 | 1 | 25 | 6 | 8 | 18 | 18
[25 empty] | 585 | 1 | 25 | 6 | 9 | 18 | 18
[25 empty] | 586 | 1 | 25 | 6 | 10 | 19 | 19
[25 empty] | 587 | 1 | 25 | 6 | 11 | 19 | 19
[25 empty] | 588 | 1 | 25 | 6 | 12 | 19.9 | 20
[25 empty] | 589 | 1 | 25 | 6 | 13 | 21 | 21
[25 empty] | 590 | 1 | 25 | 6 | 14 | 21.9 | 22
[25 empty] | 591 | 1 | 25 | 6 | 15 | 23 | 23
[25 empty] | 592 | 1 | 25 | 6 | 16 | 24.1 | 24
[25 empty] | 593 | 1 | 25 | 6 | 17 | 24.1 | 24
[25 empty] | 594 | 1 | 25 | 6 | 18 | 24.1 | 24
[25 empty] | 595 | 1 | 25 | 6 | 19 | 24.1 | 24
[25 empty] | 596 | 1 | 25 | 6 | 20 | 25 | 25
[25 empty] | 597 | 1 | 25 | 6 | 21 | 25 | 25
[25 empty] | 598 | 1 | 25 | 6 | 22 | 25 | 25
[25 empty] | 599 | 1 | 25 | 6 | 23 | 24.1 | 24
[25 empty] | 600 | 1 | 26 | 7 | 0 | 25 | 25
[25 empty] | 601 | 1 | 26 | 7 | 1 | 25 | 25
[25 empty] | 602 | 1 | 26 | 7 | 2 | 24.1 | 24
[25 empty] | 603 | 1 | 26 | 7 | 3 | 24.1 | 24
[25 empty] | 604 | 1 | 26 | 7 | 4 | 23 | 23
[25 empty] | 605 | 1 | 26 | 7 | 5 | 23 | 23
[25 empty] | 606 | 1 | 26 | 7 | 6 | 21.9 | 22
[25 empty] | 607 | 1 | 26 | 7 | 7 | 21.9 | 22
[25 empty] | 608 | 1 | 26 | 7 | 8 | 23 | 23
[25 empty] | 609 | 1 | 26 | 7 | 9 | 24.1 | 24
[25 empty] | 610 | 1 | 26 | 7 | 10 | 26.1 | 26
[25 empty] | 611 | 1 | 26 | 7 | 11 | 27 | 27
[25 empty] | 612 | 1 | 26 | 7 | 12 | 28.9 | 29
[25 empty] | 613 | 1 | 26 | 7 | 13 | 30 | 30
[25 empty] | 614 | 1 | 26 | 7 | 14 | 30.9 | 31
[25 empty] | 615 | 1 | 26 | 7 | 15 | 32 | 32
[25 empty] | 616 | 1 | 26 | 7 | 16 | 33.1 | 33
[25 empty] | 617 | 1 | 26 | 7 | 17 | 32 | 32
[25 empty] | 618 | 1 | 26 | 7 | 18 | 32 | 32
[25 empty] | 619 | 1 | 26 | 7 | 19 | 33.1 | 33
[25 empty] | 620 | 1 | 26 | 7 | 20 | 33.1 | 33
[25 empty] | 621 | 1 | 26 | 7 | 21 | 33.1 | 33
[25 empty] | 622 | 1 | 26 | 7 | 22 | 34 | 34
[25 empty] | 623 | 1 | 26 | 7 | 23 | 34 | 34
[25 empty] | 624 | 1 | 27 | 1 | 0 | 34 | 34
[25 empty] | 625 | 1 | 27 | 1 | 1 | 33.1 | 33
[25 empty] | 626 | 1 | 27 | 1 | 2 | 33.1 | 33
[25 empty] | 627 | 1 | 27 | 1 | 3 | 32 | 32
[25 empty] | 628 | 1 | 27 | 1 | 4 | 32 | 32
[25 empty] | 629 | 1 | 27 | 1 | 5 | 30.9 | 31
[25 empty] | 630 | 1 | 27 | 1 | 6 | 30.9 | 31
[25 empty] | 631 | 1 | 27 | 1 | 7 | 30 | 30
[25 empty] | 632 | 1 | 27 | 1 | 8 | 30 | 30
[25 empty] | 633 | 1 | 27 | 1 | 9 | 30.9 | 31
[25 empty] | 634 | 1 | 27 | 1 | 10 | 33.1 | 33
[25 empty] | 635 | 1 | 27 | 1 | 11 | 35.1 | 35
[25 empty] | 636 | 1 | 27 | 1 | 12 | 36 | 36
[25 empty] | 637 | 1 | 27 | 1 | 13 | 37 | 37
[25 empty] | 638 | 1 | 27 | 1 | 14 | 37.9 | 38
[25 empty] | 639 | 1 | 27 | 1 | 15 | 39 | 39
[25 empty] | 640 | 1 | 27 | 1 | 16 | 39.9 | 40
[25 empty] | 641 | 1 | 27 | 1 | 17 | 39 | 39
[25 empty] | 642 | 1 | 27 | 1 | 18 | 37 | 37
[25 empty] | 643 | 1 | 27 | 1 | 19 | 37 | 37
[25 empty] | 644 | 1 | 27 | 1 | 20 | 37 | 37
[25 empty] | 645 | 1 | 27 | 1 | 21 | 39 | 39
[25 empty] | 646 | 1 | 27 | 1 | 22 | 39 | 39
[25 empty] | 647 | 1 | 27 | 1 | 23 | 39.9 | 40
[25 empty] | 648 | 1 | 28 | 2 | 0 | 39.9 | 40
[25 empty] | 649 | 1 | 28 | 2 | 1 | 43 | 43
[25 empty] | 650 | 1 | 28 | 2 | 2 | 45 | 45
[25 empty] | 651 | 1 | 28 | 2 | 3 | 44.1 | 44
[25 empty] | 652 | 1 | 28 | 2 | 4 | 43 | 43
[25 empty] | 653 | 1 | 28 | 2 | 5 | 43 | 43
[25 empty] | 654 | 1 | 28 | 2 | 6 | 43 | 43
[25 empty] | 655 | 1 | 28 | 2 | 7 | 45 | 45
[25 empty] | 656 | 1 | 28 | 2 | 8 | 44.1 | 44
[25 empty] | 657 | 1 | 28 | 2 | 9 | 43 | 43
[25 empty] | 658 | 1 | 28 | 2 | 10 | 43 | 43
[25 empty] | 659 | 1 | 28 | 2 | 11 | 44.1 | 44
[25 empty] | 660 | 1 | 28 | 2 | 12 | 45 | 45
[25 empty] | 661 | 1 | 28 | 2 | 13 | 46 | 46
[25 empty] | 662 | 1 | 28 | 2 | 14 | 48 | 48
[25 empty] | 663 | 1 | 28 | 2 | 15 | 46.9 | 47
[25 empty] | 664 | 1 | 28 | 2 | 16 | 48.9 | 49
[25 empty] | 665 | 1 | 28 | 2 | 17 | 46 | 46
[25 empty] | 666 | 1 | 28 | 2 | 18 | 45 | 45
[25 empty] | 667 | 1 | 28 | 2 | 19 | 42.1 | 42
[25 empty] | 668 | 1 | 28 | 2 | 20 | 43 | 43
[25 empty] | 669 | 1 | 28 | 2 | 21 | 42.1 | 42
[25 empty] | 670 | 1 | 28 | 2 | 22 | 42.1 | 42
[25 empty] | 671 | 1 | 28 | 2 | 23 | 39.9 | 40
[25 empty] | 672 | 1 | 29 | 3 | 0 | 39 | 39
[25 empty] | 673 | 1 | 29 | 3 | 1 | 37.9 | 38
[25 empty] | 674 | 1 | 29 | 3 | 2 | 37 | 37
[25 empty] | 675 | 1 | 29 | 3 | 3 | 37 | 37
[25 empty] | 676 | 1 | 29 | 3 | 4 | 39 | 39
[25 empty] | 677 | 1 | 29 | 3 | 5 | 37.9 | 38
[25 empty] | 678 | 1 | 29 | 3 | 6 | 35.1 | 35
[25 empty] | 679 | 1 | 29 | 3 | 7 | 36 | 36
[25 empty] | 680 | 1 | 29 | 3 | 8 | 37.9 | 38
[25 empty] | 681 | 1 | 29 | 3 | 9 | 41 | 41
[25 empty] | 682 | 1 | 29 | 3 | 10 | 43 | 43
[25 empty] | 683 | 1 | 29 | 3 | 11 | 45 | 45
[25 empty] | 684 | 1 | 29 | 3 | 12 | 46 | 46
[25 empty] | 685 | 1 | 29 | 3 | 13 | 48 | 48
[25 empty] | 686 | 1 | 29 | 3 | 14 | 48 | 48
[25 empty] | 687 | 1 | 29 | 3 | 15 | 48.9 | 49
[25 empty] | 688 | 1 | 29 | 3 | 16 | 48 | 48
[25 empty] | 689 | 1 | 29 | 3 | 17 | 45 | 45
[25 empty] | 690 | 1 | 29 | 3 | 18 | 44.1 | 44
[25 empty] | 691 | 1 | 29 | 3 | 19 | 44.1 | 44
[25 empty] | 692 | 1 | 29 | 3 | 20 | 39 | 39
[25 empty] | 693 | 1 | 29 | 3 | 21 | 44.1 | 44
[25 empty] | 694 | 1 | 29 | 3 | 22 | 44.1 | 44
[25 empty] | 695 | 1 | 29 | 3 | 23 | 45 | 45
[25 empty] | 696 | 1 | 30 | 4 | 0 | 46 | 46
[25 empty] | 697 | 1 | 30 | 4 | 1 | 43 | 43
[25 empty] | 698 | 1 | 30 | 4 | 2 | 42.1 | 42
[25 empty] | 699 | 1 | 30 | 4 | 3 | 42.1 | 42
[25 empty] | 700 | 1 | 30 | 4 | 4 | 41 | 41
[25 empty] | 701 | 1 | 30 | 4 | 5 | 42.1 | 42
[25 empty] | 702 | 1 | 30 | 4 | 6 | 41 | 41
[25 empty] | 703 | 1 | 30 | 4 | 7 | 41 | 41
[25 empty] | 704 | 1 | 30 | 4 | 8 | 43 | 43
[25 empty] | 705 | 1 | 30 | 4 | 9 | 43 | 43
[25 empty] | 706 | 1 | 30 | 4 | 10 | 46 | 46
[25 empty] | 707 | 1 | 30 | 4 | 11 | 48.9 | 49
[25 empty] | 708 | 1 | 30 | 4 | 12 | 54 | 54
[25 empty] | 709 | 1 | 30 | 4 | 13 | 54 | 54
[25 empty] | 710 | 1 | 30 | 4 | 14 | 51.1 | 51
[25 empty] | 711 | 1 | 30 | 4 | 15 | 51.1 | 51
[25 empty] | 712 | 1 | 30 | 4 | 16 | 51.1 | 51
[25 empty] | 713 | 1 | 30 | 4 | 17 | 50 | 50
[25 empty] | 714 | 1 | 30 | 4 | 18 | 52 | 52
[25 empty] | 715 | 1 | 30 | 4 | 19 | 51.1 | 51
[25 empty] | 716 | 1 | 30 | 4 | 20 | 51.1 | 51
[25 empty] | 717 | 1 | 30 | 4 | 21 | 46 | 46
[25 empty] | 718 | 1 | 30 | 4 | 22 | 46.9 | 47
[25 empty] | 719 | 1 | 30 | 4 | 23 | 46.9 | 47
[25 empty] | 720 | 1 | 31 | 5 | 0 | 48 | 48
[25 empty] | 721 | 1 | 31 | 5 | 1 | 46.9 | 47
[25 empty] | 722 | 1 | 31 | 5 | 2 | 46 | 46
[25 empty] | 723 | 1 | 31 | 5 | 3 | 45 | 45
[25 empty] | 724 | 1 | 31 | 5 | 4 | 44.1 | 44
[25 empty] | 725 | 1 | 31 | 5 | 5 | 41 | 41
[25 empty] | 726 | 1 | 31 | 5 | 6 | 37 | 37
[25 empty] | 727 | 1 | 31 | 5 | 7 | 35.1 | 35
[25 empty] | 728 | 1 | 31 | 5 | 8 | 34 | 34
[25 empty] | 729 | 1 | 31 | 5 | 9 | 35.1 | 35
[25 empty] | 730 | 1 | 31 | 5 | 10 | 36 | 36
[25 empty] | 731 | 1 | 31 | 5 | 11 | 37.9 | 38
[25 empty] | 732 | 1 | 31 | 5 | 12 | 37 | 37
[25 empty] | 733 | 1 | 31 | 5 | 13 | 36 | 36
[25 empty] | 734 | 1 | 31 | 5 | 14 | 32 | 32
[25 empty] | 735 | 1 | 31 | 5 | 15 | 34 | 34
[25 empty] | 736 | 1 | 31 | 5 | 16 | 33.1 | 33
[25 empty] | 737 | 1 | 31 | 5 | 17 | 32 | 32
[25 empty] | 738 | 1 | 31 | 5 | 18 | 32 | 32
[25 empty] | 739 | 1 | 31 | 5 | 19 | 30.9 | 31
[25 empty] | 740 | 1 | 31 | 5 | 20 | 28.9 | 29
[25 empty] | 741 | 1 | 31 | 5 | 21 | 28 | 28
[25 empty] | 742 | 1 | 31 | 5 | 22 | 29.5 | 30
[25 empty] | 743 | 1 | 31 | 5 | 23 | 30.7 | 31
[25 empty] | 744 | 2 | 1 | 6 | 0 | 32 | 32
[25 empty] | 745 | 2 | 1 | 6 | 1 | 33.3 | 33
[25 empty] | 746 | 2 | 1 | 6 | 2 | 34.5 | 35
[25 empty] | 747 | 2 | 1 | 6 | 3 | 35.8 | 36
[25 empty] | 748 | 2 | 1 | 6 | 4 | 37 | 37
[25 empty] | 749 | 2 | 1 | 6 | 5 | 36 | 36
[25 empty] | 750 | 2 | 1 | 6 | 6 | 35.1 | 35
[25 empty] | 751 | 2 | 1 | 6 | 7 | 36 | 36
[25 empty] | 752 | 2 | 1 | 6 | 8 | 37.9 | 38
[25 empty] | 753 | 2 | 1 | 6 | 9 | 39.9 | 40
[25 empty] | 754 | 2 | 1 | 6 | 10 | 41 | 41
[25 empty] | 755 | 2 | 1 | 6 | 11 | 44.1 | 44
[25 empty] | 756 | 2 | 1 | 6 | 12 | 45 | 45
[25 empty] | 757 | 2 | 1 | 6 | 13 | 46 | 46
[25 empty] | 758 | 2 | 1 | 6 | 14 | 46 | 46
[25 empty] | 759 | 2 | 1 | 6 | 15 | 46.9 | 47
[25 empty] | 760 | 2 | 1 | 6 | 16 | 46 | 46
[25 empty] | 761 | 2 | 1 | 6 | 17 | 45 | 45
[25 empty] | 762 | 2 | 1 | 6 | 18 | 45 | 45
[25 empty] | 763 | 2 | 1 | 6 | 19 | 44.1 | 44
[25 empty] | 764 | 2 | 1 | 6 | 20 | 44.1 | 44
[25 empty] | 765 | 2 | 1 | 6 | 21 | 44.1 | 44
[25 empty] | 766 | 2 | 1 | 6 | 22 | 44.1 | 44
[25 empty] | 767 | 2 | 1 | 6 | 23 | 43 | 43
[25 empty] | 768 | 2 | 2 | 7 | 0 | 43 | 43
[25 empty] | 769 | 2 | 2 | 7 | 1 | 42.1 | 42
[25 empty] | 770 | 2 | 2 | 7 | 2 | 42.1 | 42
[25 empty] | 771 | 2 | 2 | 7 | 3 | 42.1 | 42
[25 empty] | 772 | 2 | 2 | 7 | 4 | 41 | 41
[25 empty] | 773 | 2 | 2 | 7 | 5 | 41 | 41
[25 empty] | 774 | 2 | 2 | 7 | 6 | 39.9 | 40
[25 empty] | 775 | 2 | 2 | 7 | 7 | 37.9 | 38
[25 empty] | 776 | 2 | 2 | 7 | 8 | 37.9 | 38
[25 empty] | 777 | 2 | 2 | 7 | 9 | 37.9 | 38
[25 empty] | 778 | 2 | 2 | 7 | 10 | 39.9 | 40
[25 empty] | 779 | 2 | 2 | 7 | 11 | 39.9 | 40
[25 empty] | 780 | 2 | 2 | 7 | 12 | 41 | 41
[25 empty] | 781 | 2 | 2 | 7 | 13 | 41 | 41
[25 empty] | 782 | 2 | 2 | 7 | 14 | 41 | 41
[25 empty] | 783 | 2 | 2 | 7 | 15 | 39 | 39
[25 empty] | 784 | 2 | 2 | 7 | 16 | 37.9 | 38
[25 empty] | 785 | 2 | 2 | 7 | 17 | 37 | 37
[25 empty] | 786 | 2 | 2 | 7 | 18 | 35.1 | 35
[25 empty] | 787 | 2 | 2 | 7 | 19 | 33.1 | 33
[25 empty] | 788 | 2 | 2 | 7 | 20 | 30.9 | 31
[25 empty] | 789 | 2 | 2 | 7 | 21 | 28.9 | 29
[25 empty] | 790 | 2 | 2 | 7 | 22 | 28 | 28
[25 empty] | 791 | 2 | 2 | 7 | 23 | 26.1 | 26
[25 empty] | 792 | 2 | 3 | 1 | 0 | 24.1 | 24
[25 empty] | 793 | 2 | 3 | 1 | 1 | 23 | 23
[25 empty] | 794 | 2 | 3 | 1 | 2 | 21.9 | 22
[25 empty] | 795 | 2 | 3 | 1 | 3 | 21 | 21
[25 empty] | 796 | 2 | 3 | 1 | 4 | 19.9 | 20
[25 empty] | 797 | 2 | 3 | 1 | 5 | 19 | 19
[25 empty] | 798 | 2 | 3 | 1 | 6 | 18 | 18
[25 empty] | 799 | 2 | 3 | 1 | 7 | 18 | 18
[25 empty] | 800 | 2 | 3 | 1 | 8 | 19 | 19
[25 empty] | 801 | 2 | 3 | 1 | 9 | 19.9 | 20
[25 empty] | 802 | 2 | 3 | 1 | 10 | 23 | 23
[25 empty] | 803 | 2 | 3 | 1 | 11 | 24.1 | 24
[25 empty] | 804 | 2 | 3 | 1 | 12 | 27 | 27
[25 empty] | 805 | 2 | 3 | 1 | 13 | 30 | 30
[25 empty] | 806 | 2 | 3 | 1 | 14 | 30.9 | 31
[25 empty] | 807 | 2 | 3 | 1 | 15 | 32 | 32
[25 empty] | 808 | 2 | 3 | 1 | 16 | 32 | 32
[25 empty] | 809 | 2 | 3 | 1 | 17 | 30 | 30
[25 empty] | 810 | 2 | 3 | 1 | 18 | 28.9 | 29
[25 empty] | 811 | 2 | 3 | 1 | 19 | 28 | 28
[25 empty] | 812 | 2 | 3 | 1 | 20 | 28 | 28
[25 empty] | 813 | 2 | 3 | 1 | 21 | 28.9 | 29
[25 empty] | 814 | 2 | 3 | 1 | 22 | 28.9 | 29
[25 empty] | 815 | 2 | 3 | 1 | 23 | 30 | 30
[25 empty] | 816 | 2 | 4 | 2 | 0 | 30 | 30
[25 empty] | 817 | 2 | 4 | 2 | 1 | 28 | 28
[25 empty] | 818 | 2 | 4 | 2 | 2 | 28 | 28
[25 empty] | 819 | 2 | 4 | 2 | 3 | 28 | 28
[25 empty] | 820 | 2 | 4 | 2 | 4 | 28.9 | 29
[25 empty] | 821 | 2 | 4 | 2 | 5 | 30 | 30
[25 empty] | 822 | 2 | 4 | 2 | 6 | 30.9 | 31
[25 empty] | 823 | 2 | 4 | 2 | 7 | 32 | 32
[25 empty] | 824 | 2 | 4 | 2 | 8 | 32 | 32
[25 empty] | 825 | 2 | 4 | 2 | 9 | 32 | 32
[25 empty] | 826 | 2 | 4 | 2 | 10 | 34 | 34
[25 empty] | 827 | 2 | 4 | 2 | 11 | 35.1 | 35
[25 empty] | 828 | 2 | 4 | 2 | 12 | 36 | 36
[25 empty] | 829 | 2 | 4 | 2 | 13 | 36 | 36
[25 empty] | 830 | 2 | 4 | 2 | 14 | 37 | 37
[25 empty] | 831 | 2 | 4 | 2 | 15 | 34 | 34
[25 empty] | 832 | 2 | 4 | 2 | 16 | 33.1 | 33
[25 empty] | 833 | 2 | 4 | 2 | 17 | 32 | 32
[25 empty] | 834 | 2 | 4 | 2 | 18 | 32 | 32
[25 empty] | 835 | 2 | 4 | 2 | 19 | 32 | 32
[25 empty] | 836 | 2 | 4 | 2 | 20 | 32 | 32
[25 empty] | 837 | 2 | 4 | 2 | 21 | 30.9 | 31
[25 empty] | 838 | 2 | 4 | 2 | 22 | 30.9 | 31
[25 empty] | 839 | 2 | 4 | 2 | 23 | 30 | 30
[25 empty] | 840 | 2 | 5 | 3 | 0 | 28.9 | 29
[25 empty] | 841 | 2 | 5 | 3 | 1 | 28.9 | 29
[25 empty] | 842 | 2 | 5 | 3 | 2 | 28.9 | 29
[25 empty] | 843 | 2 | 5 | 3 | 3 | 28.9 | 29
[25 empty] | 844 | 2 | 5 | 3 | 4 | 28 | 28
[25 empty] | 845 | 2 | 5 | 3 | 5 | 27 | 27
[25 empty] | 846 | 2 | 5 | 3 | 6 | 26.1 | 26
[25 empty] | 847 | 2 | 5 | 3 | 7 | 23 | 23
[25 empty] | 848 | 2 | 5 | 3 | 8 | 21.9 | 22
[25 empty] | 849 | 2 | 5 | 3 | 9 | 21 | 21
[25 empty] | 850 | 2 | 5 | 3 | 10 | 21 | 21
[25 empty] | 851 | 2 | 5 | 3 | 11 | 21.9 | 22
[25 empty] | 852 | 2 | 5 | 3 | 12 | 21.9 | 22
[25 empty] | 853 | 2 | 5 | 3 | 13 | 23 | 23
[25 empty] | 854 | 2 | 5 | 3 | 14 | 21.9 | 22
[25 empty] | 855 | 2 | 5 | 3 | 15 | 21 | 21
[25 empty] | 856 | 2 | 5 | 3 | 16 | 19.9 | 20
[25 empty] | 857 | 2 | 5 | 3 | 17 | 19 | 19
[25 empty] | 858 | 2 | 5 | 3 | 18 | 18 | 18
[25 empty] | 859 | 2 | 5 | 3 | 19 | 16 | 16
[25 empty] | 860 | 2 | 5 | 3 | 20 | 12.9 | 13
[25 empty] | 861 | 2 | 5 | 3 | 21 | 12 | 12
[25 empty] | 862 | 2 | 5 | 3 | 22 | 10 | 10
[25 empty] | 863 | 2 | 5 | 3 | 23 | 7 | 7
[25 empty] | 864 | 2 | 6 | 4 | 0 | 6.1 | 6
[25 empty] | 865 | 2 | 6 | 4 | 1 | 6.1 | 6
[25 empty] | 866 | 2 | 6 | 4 | 2 | 5 | 5
[25 empty] | 867 | 2 | 6 | 4 | 3 | 6.1 | 6
[25 empty] | 868 | 2 | 6 | 4 | 4 | 5 | 5
[25 empty] | 869 | 2 | 6 | 4 | 5 | 5 | 5
[25 empty] | 870 | 2 | 6 | 4 | 6 | 6.1 | 6
[25 empty] | 871 | 2 | 6 | 4 | 7 | 6.1 | 6
[25 empty] | 872 | 2 | 6 | 4 | 8 | 7 | 7
[25 empty] | 873 | 2 | 6 | 4 | 9 | 9 | 9
[25 empty] | 874 | 2 | 6 | 4 | 10 | 10.9 | 11
[25 empty] | 875 | 2 | 6 | 4 | 11 | 14 | 14
[25 empty] | 876 | 2 | 6 | 4 | 12 | 15.1 | 15
[25 empty] | 877 | 2 | 6 | 4 | 13 | 16 | 16
[25 empty] | 878 | 2 | 6 | 4 | 14 | 17.1 | 17
[25 empty] | 879 | 2 | 6 | 4 | 15 | 19 | 19
[25 empty] | 880 | 2 | 6 | 4 | 16 | 19 | 19
[25 empty] | 881 | 2 | 6 | 4 | 17 | 19.9 | 20
[25 empty] | 882 | 2 | 6 | 4 | 18 | 17.1 | 17
[25 empty] | 883 | 2 | 6 | 4 | 19 | 17.1 | 17
[25 empty] | 884 | 2 | 6 | 4 | 20 | 17.1 | 17
[25 empty] | 885 | 2 | 6 | 4 | 21 | 17.1 | 17
[25 empty] | 886 | 2 | 6 | 4 | 22 | 16 | 16
[25 empty] | 887 | 2 | 6 | 4 | 23 | 16 | 16
[25 empty] | 888 | 2 | 7 | 5 | 0 | 16 | 16
[25 empty] | 889 | 2 | 7 | 5 | 1 | 15.1 | 15
[25 empty] | 890 | 2 | 7 | 5 | 2 | 15.1 | 15
[25 empty] | 891 | 2 | 7 | 5 | 3 | 15.1 | 15
[25 empty] | 892 | 2 | 7 | 5 | 4 | 15.1 | 15
[25 empty] | 893 | 2 | 7 | 5 | 5 | 15.1 | 15
[25 empty] | 894 | 2 | 7 | 5 | 6 | 15.1 | 15
[25 empty] | 895 | 2 | 7 | 5 | 7 | 15.1 | 15
[25 empty] | 896 | 2 | 7 | 5 | 8 | 17.1 | 17
[25 empty] | 897 | 2 | 7 | 5 | 9 | 19 | 19
[25 empty] | 898 | 2 | 7 | 5 | 10 | 19.9 | 20
[25 empty] | 899 | 2 | 7 | 5 | 11 | 21.9 | 22
[25 empty] | 900 | 2 | 7 | 5 | 12 | 23 | 23
[25 empty] | 901 | 2 | 7 | 5 | 13 | 25 | 25
[25 empty] | 902 | 2 | 7 | 5 | 14 | 25 | 25
[25 empty] | 903 | 2 | 7 | 5 | 15 | 27 | 27
[25 empty] | 904 | 2 | 7 | 5 | 16 | 26.1 | 26
[25 empty] | 905 | 2 | 7 | 5 | 17 | 25 | 25
[25 empty] | 906 | 2 | 7 | 5 | 18 | 24.1 | 24
[25 empty] | 907 | 2 | 7 | 5 | 19 | 24.1 | 24
[25 empty] | 908 | 2 | 7 | 5 | 20 | 24.1 | 24
[25 empty] | 909 | 2 | 7 | 5 | 21 | 23 | 23
[25 empty] | 910 | 2 | 7 | 5 | 22 | 23 | 23
[25 empty] | 911 | 2 | 7 | 5 | 23 | 24.1 | 24
[25 empty] | 912 | 2 | 8 | 6 | 0 | 24.1 | 24
[25 empty] | 913 | 2 | 8 | 6 | 1 | 24.1 | 24
[25 empty] | 914 | 2 | 8 | 6 | 2 | 25 | 25
[25 empty] | 915 | 2 | 8 | 6 | 3 | 23 | 23
[25 empty] | 916 | 2 | 8 | 6 | 4 | 23 | 23
[25 empty] | 917 | 2 | 8 | 6 | 5 | 21.9 | 22
[25 empty] | 918 | 2 | 8 | 6 | 6 | 21 | 21
[25 empty] | 919 | 2 | 8 | 6 | 7 | 19.9 | 20
[25 empty] | 920 | 2 | 8 | 6 | 8 | 21 | 21
[25 empty] | 921 | 2 | 8 | 6 | 9 | 21 | 21
[25 empty] | 922 | 2 | 8 | 6 | 10 | 21.9 | 22
[25 empty] | 923 | 2 | 8 | 6 | 11 | 23 | 23
[25 empty] | 924 | 2 | 8 | 6 | 12 | 26.1 | 26
[25 empty] | 925 | 2 | 8 | 6 | 13 | 27 | 27
[25 empty] | 926 | 2 | 8 | 6 | 14 | 26.1 | 26
[25 empty] | 927 | 2 | 8 | 6 | 15 | 27 | 27
[25 empty] | 928 | 2 | 8 | 6 | 16 | 27 | 27
[25 empty] | 929 | 2 | 8 | 6 | 17 | 26.1 | 26
[25 empty] | 930 | 2 | 8 | 6 | 18 | 24.1 | 24
[25 empty] | 931 | 2 | 8 | 6 | 19 | 24.1 | 24
[25 empty] | 932 | 2 | 8 | 6 | 20 | 23 | 23
[25 empty] | 933 | 2 | 8 | 6 | 21 | 21.9 | 22
[25 empty] | 934 | 2 | 8 | 6 | 22 | 21 | 21
[25 empty] | 935 | 2 | 8 | 6 | 23 | 19 | 19
[25 empty] | 936 | 2 | 9 | 7 | 0 | 19 | 19
[25 empty] | 937 | 2 | 9 | 7 | 1 | 18 | 18
[25 empty] | 938 | 2 | 9 | 7 | 2 | 17.1 | 17
[25 empty] | 939 | 2 | 9 | 7 | 3 | 17.1 | 17
[25 empty] | 940 | 2 | 9 | 7 | 4 | 17.1 | 17
[25 empty] | 941 | 2 | 9 | 7 | 5 | 18 | 18
[25 empty] | 942 | 2 | 9 | 7 | 6 | 18 | 18
[25 empty] | 943 | 2 | 9 | 7 | 7 | 17.1 | 17
[25 empty] | 944 | 2 | 9 | 7 | 8 | 18 | 18
[25 empty] | 945 | 2 | 9 | 7 | 9 | 19 | 19
[25 empty] | 946 | 2 | 9 | 7 | 10 | 21 | 21
[25 empty] | 947 | 2 | 9 | 7 | 11 | 24.1 | 24
[25 empty] | 948 | 2 | 9 | 7 | 12 | 27 | 27
[25 empty] | 949 | 2 | 9 | 7 | 13 | 30 | 30
[25 empty] | 950 | 2 | 9 | 7 | 14 | 30 | 30
[25 empty] | 951 | 2 | 9 | 7 | 15 | 30.9 | 31
[25 empty] | 952 | 2 | 9 | 7 | 16 | 30.9 | 31
[25 empty] | 953 | 2 | 9 | 7 | 17 | 28 | 28
[25 empty] | 954 | 2 | 9 | 7 | 18 | 28 | 28
[25 empty] | 955 | 2 | 9 | 7 | 19 | 28 | 28
[25 empty] | 956 | 2 | 9 | 7 | 20 | 28.9 | 29
[25 empty] | 957 | 2 | 9 | 7 | 21 | 28.9 | 29
[25 empty] | 958 | 2 | 9 | 7 | 22 | 30 | 30
[25 empty] | 959 | 2 | 9 | 7 | 23 | 30.9 | 31
[25 empty] | 960 | 2 | 10 | 1 | 0 | 30 | 30
[25 empty] | 961 | 2 | 10 | 1 | 1 | 30 | 30
[25 empty] | 962 | 2 | 10 | 1 | 2 | 28.9 | 29
[25 empty] | 963 | 2 | 10 | 1 | 3 | 30 | 30
[25 empty] | 964 | 2 | 10 | 1 | 4 | 30 | 30
[25 empty] | 965 | 2 | 10 | 1 | 5 | 30 | 30
[25 empty] | 966 | 2 | 10 | 1 | 6 | 28.9 | 29
[25 empty] | 967 | 2 | 10 | 1 | 7 | 30 | 30
[25 empty] | 968 | 2 | 10 | 1 | 8 | 30 | 30
[25 empty] | 969 | 2 | 10 | 1 | 9 | 32 | 32
[25 empty] | 970 | 2 | 10 | 1 | 10 | 36 | 36
[25 empty] | 971 | 2 | 10 | 1 | 11 | 37 | 37
[25 empty] | 972 | 2 | 10 | 1 | 12 | 39 | 39
[25 empty] | 973 | 2 | 10 | 1 | 13 | 42.1 | 42
[25 empty] | 974 | 2 | 10 | 1 | 14 | 39 | 39
[25 empty] | 975 | 2 | 10 | 1 | 15 | 39.9 | 40
[25 empty] | 976 | 2 | 10 | 1 | 16 | 39 | 39
[25 empty] | 977 | 2 | 10 | 1 | 17 | 37.9 | 38
[25 empty] | 978 | 2 | 10 | 1 | 18 | 37 | 37
[25 empty] | 979 | 2 | 10 | 1 | 19 | 37.9 | 38
[25 empty] | 980 | 2 | 10 | 1 | 20 | 39 | 39
[25 empty] | 981 | 2 | 10 | 1 | 21 | 37.9 | 38
[25 empty] | 982 | 2 | 10 | 1 | 22 | 37 | 37
[25 empty] | 983 | 2 | 10 | 1 | 23 | 37 | 37
[25 empty] | 984 | 2 | 11 | 2 | 0 | 37 | 37
[25 empty] | 985 | 2 | 11 | 2 | 1 | 37.9 | 38
[25 empty] | 986 | 2 | 11 | 2 | 2 | 37 | 37
[25 empty] | 987 | 2 | 11 | 2 | 3 | 36 | 36
[25 empty] | 988 | 2 | 11 | 2 | 4 | 35.1 | 35
[25 empty] | 989 | 2 | 11 | 2 | 5 | 36 | 36
[25 empty] | 990 | 2 | 11 | 2 | 6 | 35.1 | 35
[25 empty] | 991 | 2 | 11 | 2 | 7 | 34 | 34
[25 empty] | 992 | 2 | 11 | 2 | 8 | 37 | 37
[25 empty] | 993 | 2 | 11 | 2 | 9 | 39.9 | 40
[25 empty] | 994 | 2 | 11 | 2 | 10 | 43 | 43
[25 empty] | 995 | 2 | 11 | 2 | 11 | 42.1 | 42
[25 empty] | 996 | 2 | 11 | 2 | 12 | 44.1 | 44
[25 empty] | 997 | 2 | 11 | 2 | 13 | 45 | 45
[25 empty] | 998 | 2 | 11 | 2 | 14 | 45 | 45
[25 empty] | 999 | 2 | 11 | 2 | 15 | 46 | 46
[25 empty] | 1000 | 2 | 11 | 2 | 16 | 45 | 45
[25 empty] | 1001 | 2 | 11 | 2 | 17 | 45 | 45
[25 empty] | 1002 | 2 | 11 | 2 | 18 | 43 | 43
[25 empty] | 1003 | 2 | 11 | 2 | 19 | 42.1 | 42
[25 empty] | 1004 | 2 | 11 | 2 | 20 | 39.9 | 40
[25 empty] | 1005 | 2 | 11 | 2 | 21 | 39 | 39
[25 empty] | 1006 | 2 | 11 | 2 | 22 | 36 | 36
[25 empty] | 1007 | 2 | 11 | 2 | 23 | 33.1 | 33
[25 empty] | 1008 | 2 | 12 | 3 | 0 | 32 | 32
[25 empty] | 1009 | 2 | 12 | 3 | 1 | 28.9 | 29
[25 empty] | 1010 | 2 | 12 | 3 | 2 | 27 | 27
[25 empty] | 1011 | 2 | 12 | 3 | 3 | 25 | 25
[25 empty] | 1012 | 2 | 12 | 3 | 4 | 23 | 23
[25 empty] | 1013 | 2 | 12 | 3 | 5 | 19.9 | 20
[25 empty] | 1014 | 2 | 12 | 3 | 6 | 17.1 | 17
[25 empty] | 1015 | 2 | 12 | 3 | 7 | 12.9 | 13
[25 empty] | 1016 | 2 | 12 | 3 | 8 | 10.9 | 11
[25 empty] | 1017 | 2 | 12 | 3 | 9 | 10.9 | 11
[25 empty] | 1018 | 2 | 12 | 3 | 10 | 12 | 12
[25 empty] | 1019 | 2 | 12 | 3 | 11 | 14 | 14
[25 empty] | 1020 | 2 | 12 | 3 | 12 | 16 | 16
[25 empty] | 1021 | 2 | 12 | 3 | 13 | 19 | 19
[25 empty] | 1022 | 2 | 12 | 3 | 14 | 19.9 | 20
[25 empty] | 1023 | 2 | 12 | 3 | 15 | 19.9 | 20
[25 empty] | 1024 | 2 | 12 | 3 | 16 | 21.9 | 22
[25 empty] | 1025 | 2 | 12 | 3 | 17 | 23 | 23
[25 empty] | 1026 | 2 | 12 | 3 | 18 | 21.9 | 22
[25 empty] | 1027 | 2 | 12 | 3 | 19 | 21 | 21
[25 empty] | 1028 | 2 | 12 | 3 | 20 | 19.9 | 20
[25 empty] | 1029 | 2 | 12 | 3 | 21 | 19 | 19
[25 empty] | 1030 | 2 | 12 | 3 | 22 | 19 | 19
[25 empty] | 1031 | 2 | 12 | 3 | 23 | 18 | 18
[25 empty] | 1032 | 2 | 13 | 4 | 0 | 18 | 18
[25 empty] | 1033 | 2 | 13 | 4 | 1 | 17.1 | 17
[25 empty] | 1034 | 2 | 13 | 4 | 2 | 17.1 | 17
[25 empty] | 1035 | 2 | 13 | 4 | 3 | 16 | 16
[25 empty] | 1036 | 2 | 13 | 4 | 4 | 15.1 | 15
[25 empty] | 1037 | 2 | 13 | 4 | 5 | 15.1 | 15
[25 empty] | 1038 | 2 | 13 | 4 | 6 | 14 | 14
[25 empty] | 1039 | 2 | 13 | 4 | 7 | 14 | 14
[25 empty] | 1040 | 2 | 13 | 4 | 8 | 15.1 | 15
[25 empty] | 1041 | 2 | 13 | 4 | 9 | 17.1 | 17
[25 empty] | 1042 | 2 | 13 | 4 | 10 | 18 | 18
[25 empty] | 1043 | 2 | 13 | 4 | 11 | 19 | 19
[25 empty] | 1044 | 2 | 13 | 4 | 12 | 21 | 21
[25 empty] | 1045 | 2 | 13 | 4 | 13 | 21.9 | 22
[25 empty] | 1046 | 2 | 13 | 4 | 14 | 23 | 23
[25 empty] | 1047 | 2 | 13 | 4 | 15 | 25 | 25
[25 empty] | 1048 | 2 | 13 | 4 | 16 | 26.1 | 26
[25 empty] | 1049 | 2 | 13 | 4 | 17 | 26.1 | 26
[25 empty] | 1050 | 2 | 13 | 4 | 18 | 25 | 25
[25 empty] | 1051 | 2 | 13 | 4 | 19 | 25 | 25
[25 empty] | 1052 | 2 | 13 | 4 | 20 | 25 | 25
[25 empty] | 1053 | 2 | 13 | 4 | 21 | 25 | 25
[25 empty] | 1054 | 2 | 13 | 4 | 22 | 25 | 25
[25 empty] | 1055 | 2 | 13 | 4 | 23 | 26.1 | 26
[25 empty] | 1056 | 2 | 14 | 5 | 0 | 26.1 | 26
[25 empty] | 1057 | 2 | 14 | 5 | 1 | 26.1 | 26
[25 empty] | 1058 | 2 | 14 | 5 | 2 | 26.1 | 26
[25 empty] | 1059 | 2 | 14 | 5 | 3 | 26.1 | 26
[25 empty] | 1060 | 2 | 14 | 5 | 4 | 25 | 25
[25 empty] | 1061 | 2 | 14 | 5 | 5 | 26.1 | 26
[25 empty] | 1062 | 2 | 14 | 5 | 6 | 26.1 | 26
[25 empty] | 1063 | 2 | 14 | 5 | 7 | 25 | 25
[25 empty] | 1064 | 2 | 14 | 5 | 8 | 26.1 | 26
[25 empty] | 1065 | 2 | 14 | 5 | 9 | 27 | 27
[25 empty] | 1066 | 2 | 14 | 5 | 10 | 27 | 27
[25 empty] | 1067 | 2 | 14 | 5 | 11 | 28 | 28
[25 empty] | 1068 | 2 | 14 | 5 | 12 | 28.9 | 29
[25 empty] | 1069 | 2 | 14 | 5 | 13 | 30.9 | 31
[25 empty] | 1070 | 2 | 14 | 5 | 14 | 30.9 | 31
[25 empty] | 1071 | 2 | 14 | 5 | 15 | 33.1 | 33
[25 empty] | 1072 | 2 | 14 | 5 | 16 | 33.1 | 33
[25 empty] | 1073 | 2 | 14 | 5 | 17 | 33.1 | 33
[25 empty] | 1074 | 2 | 14 | 5 | 18 | 32 | 32
[25 empty] | 1075 | 2 | 14 | 5 | 19 | 30.9 | 31
[25 empty] | 1076 | 2 | 14 | 5 | 20 | 30.9 | 31
[25 empty] | 1077 | 2 | 14 | 5 | 21 | 30 | 30
[25 empty] | 1078 | 2 | 14 | 5 | 22 | 28.9 | 29
[25 empty] | 1079 | 2 | 14 | 5 | 23 | 28 | 28
[25 empty] | 1080 | 2 | 15 | 6 | 0 | 28 | 28
[25 empty] | 1081 | 2 | 15 | 6 | 1 | 27 | 27
[25 empty] | 1082 | 2 | 15 | 6 | 2 | 26.1 | 26
[25 empty] | 1083 | 2 | 15 | 6 | 3 | 24.1 | 24
[25 empty] | 1084 | 2 | 15 | 6 | 4 | 24.1 | 24
[25 empty] | 1085 | 2 | 15 | 6 | 5 | 24.1 | 24
[25 empty] | 1086 | 2 | 15 | 6 | 6 | 23 | 23
[25 empty] | 1087 | 2 | 15 | 6 | 7 | 23 | 23
[25 empty] | 1088 | 2 | 15 | 6 | 8 | 26.1 | 26
[25 empty] | 1089 | 2 | 15 | 6 | 9 | 28 | 28
[25 empty] | 1090 | 2 | 15 | 6 | 10 | 30.9 | 31
[25 empty] | 1091 | 2 | 15 | 6 | 11 | 32 | 32
[25 empty] | 1092 | 2 | 15 | 6 | 12 | 35.1 | 35
[25 empty] | 1093 | 2 | 15 | 6 | 13 | 37 | 37
[25 empty] | 1094 | 2 | 15 | 6 | 14 | 36 | 36
[25 empty] | 1095 | 2 | 15 | 6 | 15 | 36 | 36
[25 empty] | 1096 | 2 | 15 | 6 | 16 | 36 | 36
[25 empty] | 1097 | 2 | 15 | 6 | 17 | 35.1 | 35
[25 empty] | 1098 | 2 | 15 | 6 | 18 | 36 | 36
[25 empty] | 1099 | 2 | 15 | 6 | 19 | 37 | 37
[25 empty] | 1100 | 2 | 15 | 6 | 20 | 36 | 36
[25 empty] | 1101 | 2 | 15 | 6 | 21 | 35.1 | 35
[25 empty] | 1102 | 2 | 15 | 6 | 22 | 35.1 | 35
[25 empty] | 1103 | 2 | 15 | 6 | 23 | 36 | 36
[25 empty] | 1104 | 2 | 16 | 7 | 0 | 37 | 37
[25 empty] | 1105 | 2 | 16 | 7 | 1 | 39 | 39
[25 empty] | 1106 | 2 | 16 | 7 | 2 | 37.9 | 38
[25 empty] | 1107 | 2 | 16 | 7 | 3 | 39 | 39
[25 empty] | 1108 | 2 | 16 | 7 | 4 | 37.9 | 38
[25 empty] | 1109 | 2 | 16 | 7 | 5 | 37.9 | 38
[25 empty] | 1110 | 2 | 16 | 7 | 6 | 37.9 | 38
[25 empty] | 1111 | 2 | 16 | 7 | 7 | 37 | 37
[25 empty] | 1112 | 2 | 16 | 7 | 8 | 39 | 39
[25 empty] | 1113 | 2 | 16 | 7 | 9 | 41 | 41
[25 empty] | 1114 | 2 | 16 | 7 | 10 | 43 | 43
[25 empty] | 1115 | 2 | 16 | 7 | 11 | 45 | 45
[25 empty] | 1116 | 2 | 16 | 7 | 12 | 46 | 46
[25 empty] | 1117 | 2 | 16 | 7 | 13 | 44.1 | 44
[25 empty] | 1118 | 2 | 16 | 7 | 14 | 44.1 | 44
[25 empty] | 1119 | 2 | 16 | 7 | 15 | 43 | 43
[25 empty] | 1120 | 2 | 16 | 7 | 16 | 43 | 43
[25 empty] | 1121 | 2 | 16 | 7 | 17 | 44.1 | 44
[25 empty] | 1122 | 2 | 16 | 7 | 18 | 43 | 43
[25 empty] | 1123 | 2 | 16 | 7 | 19 | 43 | 43
[25 empty] | 1124 | 2 | 16 | 7 | 20 | 41 | 41
[25 empty] | 1125 | 2 | 16 | 7 | 21 | 39 | 39
[25 empty] | 1126 | 2 | 16 | 7 | 22 | 39 | 39
[25 empty] | 1127 | 2 | 16 | 7 | 23 | 37.9 | 38
[25 empty] | 1128 | 2 | 17 | 1 | 0 | 37.9 | 38
[25 empty] | 1129 | 2 | 17 | 1 | 1 | 37.9 | 38
[25 empty] | 1130 | 2 | 17 | 1 | 2 | 37 | 37
[25 empty] | 1131 | 2 | 17 | 1 | 3 | 36 | 36
[25 empty] | 1132 | 2 | 17 | 1 | 4 | 36 | 36
[25 empty] | 1133 | 2 | 17 | 1 | 5 | 35.1 | 35
[25 empty] | 1134 | 2 | 17 | 1 | 6 | 34 | 34
[25 empty] | 1135 | 2 | 17 | 1 | 7 | 33.1 | 33
[25 empty] | 1136 | 2 | 17 | 1 | 8 | 33.1 | 33
[25 empty] | 1137 | 2 | 17 | 1 | 9 | 36 | 36
[25 empty] | 1138 | 2 | 17 | 1 | 10 | 37.9 | 38
[25 empty] | 1139 | 2 | 17 | 1 | 11 | 39.9 | 40
[25 empty] | 1140 | 2 | 17 | 1 | 12 | 42.1 | 42
[25 empty] | 1141 | 2 | 17 | 1 | 13 | 45 | 45
[25 empty] | 1142 | 2 | 17 | 1 | 14 | 46 | 46
[25 empty] | 1143 | 2 | 17 | 1 | 15 | 46 | 46
[25 empty] | 1144 | 2 | 17 | 1 | 16 | 45 | 45
[25 empty] | 1145 | 2 | 17 | 1 | 17 | 45 | 45
[25 empty] | 1146 | 2 | 17 | 1 | 18 | 43 | 43
[25 empty] | 1147 | 2 | 17 | 1 | 19 | 43 | 43
[25 empty] | 1148 | 2 | 17 | 1 | 20 | 43 | 43
[25 empty] | 1149 | 2 | 17 | 1 | 21 | 41 | 41
[25 empty] | 1150 | 2 | 17 | 1 | 22 | 37.9 | 38
[25 empty] | 1151 | 2 | 17 | 1 | 23 | 37 | 37
[25 empty] | 1152 | 2 | 18 | 2 | 0 | 39 | 39
[25 empty] | 1153 | 2 | 18 | 2 | 1 | 39 | 39
[25 empty] | 1154 | 2 | 18 | 2 | 2 | 36 | 36
[25 empty] | 1155 | 2 | 18 | 2 | 3 | 37 | 37
[25 empty] | 1156 | 2 | 18 | 2 | 4 | 35.1 | 35
[25 empty] | 1157 | 2 | 18 | 2 | 5 | 33.1 | 33
[25 empty] | 1158 | 2 | 18 | 2 | 6 | 32 | 32
[25 empty] | 1159 | 2 | 18 | 2 | 7 | 33.1 | 33
[25 empty] | 1160 | 2 | 18 | 2 | 8 | 36 | 36
[25 empty] | 1161 | 2 | 18 | 2 | 9 | 37.9 | 38
[25 empty] | 1162 | 2 | 18 | 2 | 10 | 42.1 | 42
[25 empty] | 1163 | 2 | 18 | 2 | 11 | 43 | 43
[25 empty] | 1164 | 2 | 18 | 2 | 12 | 44.1 | 44
[25 empty] | 1165 | 2 | 18 | 2 | 13 | 46 | 46
[25 empty] | 1166 | 2 | 18 | 2 | 14 | 48.9 | 49
[25 empty] | 1167 | 2 | 18 | 2 | 15 | 50 | 50
[25 empty] | 1168 | 2 | 18 | 2 | 16 | 48.9 | 49
[25 empty] | 1169 | 2 | 18 | 2 | 17 | 46.9 | 47
[25 empty] | 1170 | 2 | 18 | 2 | 18 | 44.1 | 44
[25 empty] | 1171 | 2 | 18 | 2 | 19 | 41 | 41
[25 empty] | 1172 | 2 | 18 | 2 | 20 | 41 | 41
[25 empty] | 1173 | 2 | 18 | 2 | 21 | 41 | 41
[25 empty] | 1174 | 2 | 18 | 2 | 22 | 39 | 39
[25 empty] | 1175 | 2 | 18 | 2 | 23 | 37 | 37
[25 empty] | 1176 | 2 | 19 | 3 | 0 | 37 | 37
[25 empty] | 1177 | 2 | 19 | 3 | 1 | 35.1 | 35
[25 empty] | 1178 | 2 | 19 | 3 | 2 | 34 | 34
[25 empty] | 1179 | 2 | 19 | 3 | 3 | 32 | 32
[25 empty] | 1180 | 2 | 19 | 3 | 4 | 32 | 32
[25 empty] | 1181 | 2 | 19 | 3 | 5 | 30.9 | 31
[25 empty] | 1182 | 2 | 19 | 3 | 6 | 32 | 32
[25 empty] | 1183 | 2 | 19 | 3 | 7 | 30.9 | 31
[25 empty] | 1184 | 2 | 19 | 3 | 8 | 33.1 | 33
[25 empty] | 1185 | 2 | 19 | 3 | 9 | 36 | 36
[25 empty] | 1186 | 2 | 19 | 3 | 10 | 39.9 | 40
[25 empty] | 1187 | 2 | 19 | 3 | 11 | 43 | 43
[25 empty] | 1188 | 2 | 19 | 3 | 12 | 48 | 48
[25 empty] | 1189 | 2 | 19 | 3 | 13 | 51.1 | 51
[25 empty] | 1190 | 2 | 19 | 3 | 14 | 53.1 | 53
[25 empty] | 1191 | 2 | 19 | 3 | 15 | 54 | 54
[25 empty] | 1192 | 2 | 19 | 3 | 16 | 53.1 | 53
[25 empty] | 1193 | 2 | 19 | 3 | 17 | 52 | 52
[25 empty] | 1194 | 2 | 19 | 3 | 18 | 50 | 50
[25 empty] | 1195 | 2 | 19 | 3 | 19 | 48.9 | 49
[25 empty] | 1196 | 2 | 19 | 3 | 20 | 48 | 48
[25 empty] | 1197 | 2 | 19 | 3 | 21 | 48 | 48
[25 empty] | 1198 | 2 | 19 | 3 | 22 | 48 | 48
[25 empty] | 1199 | 2 | 19 | 3 | 23 | 46.9 | 47
[25 empty] | 1200 | 2 | 20 | 4 | 0 | 45 | 45
[25 empty] | 1201 | 2 | 20 | 4 | 1 | 43 | 43
[25 empty] | 1202 | 2 | 20 | 4 | 2 | 42.1 | 42
[25 empty] | 1203 | 2 | 20 | 4 | 3 | 39.9 | 40
[25 empty] | 1204 | 2 | 20 | 4 | 4 | 41 | 41
[25 empty] | 1205 | 2 | 20 | 4 | 5 | 39 | 39
[25 empty] | 1206 | 2 | 20 | 4 | 6 | 37 | 37
[25 empty] | 1207 | 2 | 20 | 4 | 7 | 37 | 37
[25 empty] | 1208 | 2 | 20 | 4 | 8 | 39.9 | 40
[25 empty] | 1209 | 2 | 20 | 4 | 9 | 42.1 | 42
[25 empty] | 1210 | 2 | 20 | 4 | 10 | 43 | 43
[25 empty] | 1211 | 2 | 20 | 4 | 11 | 44.1 | 44
[25 empty] | 1212 | 2 | 20 | 4 | 12 | 44.1 | 44
[25 empty] | 1213 | 2 | 20 | 4 | 13 | 45 | 45
[25 empty] | 1214 | 2 | 20 | 4 | 14 | 44.1 | 44
[25 empty] | 1215 | 2 | 20 | 4 | 15 | 44.1 | 44
[25 empty] | 1216 | 2 | 20 | 4 | 16 | 45 | 45
[25 empty] | 1217 | 2 | 20 | 4 | 17 | 45 | 45
[25 empty] | 1218 | 2 | 20 | 4 | 18 | 41 | 41
[25 empty] | 1219 | 2 | 20 | 4 | 19 | 39.9 | 40
[25 empty] | 1220 | 2 | 20 | 4 | 20 | 39 | 39
[25 empty] | 1221 | 2 | 20 | 4 | 21 | 37.9 | 38
[25 empty] | 1222 | 2 | 20 | 4 | 22 | 37.9 | 38
[25 empty] | 1223 | 2 | 20 | 4 | 23 | 39 | 39
[25 empty] | 1224 | 2 | 21 | 5 | 0 | 37.9 | 38
[25 empty] | 1225 | 2 | 21 | 5 | 1 | 37 | 37
[25 empty] | 1226 | 2 | 21 | 5 | 2 | 37 | 37
[25 empty] | 1227 | 2 | 21 | 5 | 3 | 37 | 37
[25 empty] | 1228 | 2 | 21 | 5 | 4 | 37 | 37
[25 empty] | 1229 | 2 | 21 | 5 | 5 | 37 | 37
[25 empty] | 1230 | 2 | 21 | 5 | 6 | 37 | 37
[25 empty] | 1231 | 2 | 21 | 5 | 7 | 37 | 37
[25 empty] | 1232 | 2 | 21 | 5 | 8 | 37 | 37
[25 empty] | 1233 | 2 | 21 | 5 | 9 | 35.1 | 35
[25 empty] | 1234 | 2 | 21 | 5 | 10 | 37 | 37
[25 empty] | 1235 | 2 | 21 | 5 | 11 | 37.9 | 38
[25 empty] | 1236 | 2 | 21 | 5 | 12 | 39 | 39
[25 empty] | 1237 | 2 | 21 | 5 | 13 | 39 | 39
[25 empty] | 1238 | 2 | 21 | 5 | 14 | 39.9 | 40
[25 empty] | 1239 | 2 | 21 | 5 | 15 | 39 | 39
[25 empty] | 1240 | 2 | 21 | 5 | 16 | 39.9 | 40
[25 empty] | 1241 | 2 | 21 | 5 | 17 | 39.9 | 40
[25 empty] | 1242 | 2 | 21 | 5 | 18 | 42.1 | 42
[25 empty] | 1243 | 2 | 21 | 5 | 19 | 41 | 41
[25 empty] | 1244 | 2 | 21 | 5 | 20 | 39.9 | 40
[25 empty] | 1245 | 2 | 21 | 5 | 21 | 39.9 | 40
[25 empty] | 1246 | 2 | 21 | 5 | 22 | 39 | 39
[25 empty] | 1247 | 2 | 21 | 5 | 23 | 37 | 37
[25 empty] | 1248 | 2 | 22 | 6 | 0 | 37 | 37
[25 empty] | 1249 | 2 | 22 | 6 | 1 | 37 | 37
[25 empty] | 1250 | 2 | 22 | 6 | 2 | 36 | 36
[25 empty] | 1251 | 2 | 22 | 6 | 3 | 34 | 34
[25 empty] | 1252 | 2 | 22 | 6 | 4 | 33.1 | 33
[25 empty] | 1253 | 2 | 22 | 6 | 5 | 32 | 32
[25 empty] | 1254 | 2 | 22 | 6 | 6 | 30 | 30
[25 empty] | 1255 | 2 | 22 | 6 | 7 | 28.9 | 29
[25 empty] | 1256 | 2 | 22 | 6 | 8 | 28.9 | 29
[25 empty] | 1257 | 2 | 22 | 6 | 9 | 30 | 30
[25 empty] | 1258 | 2 | 22 | 6 | 10 | 30 | 30
[25 empty] | 1259 | 2 | 22 | 6 | 11 | 33.1 | 33
[25 empty] | 1260 | 2 | 22 | 6 | 12 | 34 | 34
[25 empty] | 1261 | 2 | 22 | 6 | 13 | 36 | 36
[25 empty] | 1262 | 2 | 22 | 6 | 14 | 37.9 | 38
[25 empty] | 1263 | 2 | 22 | 6 | 15 | 37.9 | 38
[25 empty] | 1264 | 2 | 22 | 6 | 16 | 39.9 | 40
[25 empty] | 1265 | 2 | 22 | 6 | 17 | 39 | 39
[25 empty] | 1266 | 2 | 22 | 6 | 18 | 37.9 | 38
[25 empty] | 1267 | 2 | 22 | 6 | 19 | 37.9 | 38
[25 empty] | 1268 | 2 | 22 | 6 | 20 | 37.9 | 38
[25 empty] | 1269 | 2 | 22 | 6 | 21 | 37 | 37
[25 empty] | 1270 | 2 | 22 | 6 | 22 | 37.9 | 38
[25 empty] | 1271 | 2 | 22 | 6 | 23 | 37.9 | 38
[25 empty] | 1272 | 2 | 23 | 7 | 0 | 37.9 | 38
[25 empty] | 1273 | 2 | 23 | 7 | 1 | 37.9 | 38
[25 empty] | 1274 | 2 | 23 | 7 | 2 | 37 | 37
[25 empty] | 1275 | 2 | 23 | 7 | 3 | 37.9 | 38
[25 empty] | 1276 | 2 | 23 | 7 | 4 | 37.9 | 38
[25 empty] | 1277 | 2 | 23 | 7 | 5 | 37.9 | 38
[25 empty] | 1278 | 2 | 23 | 7 | 6 | 39 | 39
[25 empty] | 1279 | 2 | 23 | 7 | 7 | 39 | 39
[25 empty] | 1280 | 2 | 23 | 7 | 8 | 39.9 | 40
[25 empty] | 1281 | 2 | 23 | 7 | 9 | 41 | 41
[25 empty] | 1282 | 2 | 23 | 7 | 10 | 42.1 | 42
[25 empty] | 1283 | 2 | 23 | 7 | 11 | 44.1 | 44
[25 empty] | 1284 | 2 | 23 | 7 | 12 | 44.1 | 44
[25 empty] | 1285 | 2 | 23 | 7 | 13 | 46 | 46
[25 empty] | 1286 | 2 | 23 | 7 | 14 | 46 | 46
[25 empty] | 1287 | 2 | 23 | 7 | 15 | 44.1 | 44
[25 empty] | 1288 | 2 | 23 | 7 | 16 | 42.1 | 42
[25 empty] | 1289 | 2 | 23 | 7 | 17 | 42.1 | 42
[25 empty] | 1290 | 2 | 23 | 7 | 18 | 42.1 | 42
[25 empty] | 1291 | 2 | 23 | 7 | 19 | 42.1 | 42
[25 empty] | 1292 | 2 | 23 | 7 | 20 | 42.1 | 42
[25 empty] | 1293 | 2 | 23 | 7 | 21 | 43 | 43
[25 empty] | 1294 | 2 | 23 | 7 | 22 | 44.1 | 44
[25 empty] | 1295 | 2 | 23 | 7 | 23 | 44.1 | 44
[25 empty] | 1296 | 2 | 24 | 1 | 0 | 42.1 | 42
[25 empty] | 1297 | 2 | 24 | 1 | 1 | 42.1 | 42
[25 empty] | 1298 | 2 | 24 | 1 | 2 | 44.1 | 44
[25 empty] | 1299 | 2 | 24 | 1 | 3 | 43 | 43
[25 empty] | 1300 | 2 | 24 | 1 | 4 | 41 | 41
[25 empty] | 1301 | 2 | 24 | 1 | 5 | 39.9 | 40
[25 empty] | 1302 | 2 | 24 | 1 | 6 | 43 | 43
[25 empty] | 1303 | 2 | 24 | 1 | 7 | 42.1 | 42
[25 empty] | 1304 | 2 | 24 | 1 | 8 | 43 | 43
[25 empty] | 1305 | 2 | 24 | 1 | 9 | 44.1 | 44
[25 empty] | 1306 | 2 | 24 | 1 | 10 | 45 | 45
[25 empty] | 1307 | 2 | 24 | 1 | 11 | 42.1 | 42
[25 empty] | 1308 | 2 | 24 | 1 | 12 | 45 | 45
[25 empty] | 1309 | 2 | 24 | 1 | 13 | 46 | 46
[25 empty] | 1310 | 2 | 24 | 1 | 14 | 46.9 | 47
[25 empty] | 1311 | 2 | 24 | 1 | 15 | 46.9 | 47
[25 empty] | 1312 | 2 | 24 | 1 | 16 | 45 | 45
[25 empty] | 1313 | 2 | 24 | 1 | 17 | 42.1 | 42
[25 empty] | 1314 | 2 | 24 | 1 | 18 | 39.9 | 40
[25 empty] | 1315 | 2 | 24 | 1 | 19 | 37.9 | 38
[25 empty] | 1316 | 2 | 24 | 1 | 20 | 35.1 | 35
[25 empty] | 1317 | 2 | 24 | 1 | 21 | 34 | 34
[25 empty] | 1318 | 2 | 24 | 1 | 22 | 32 | 32
[25 empty] | 1319 | 2 | 24 | 1 | 23 | 30 | 30
[25 empty] | 1320 | 2 | 25 | 2 | 0 | 28 | 28
[25 empty] | 1321 | 2 | 25 | 2 | 1 | 28 | 28
[25 empty] | 1322 | 2 | 25 | 2 | 2 | 27 | 27
[25 empty] | 1323 | 2 | 25 | 2 | 3 | 26.1 | 26
[25 empty] | 1324 | 2 | 25 | 2 | 4 | 24.1 | 24
[25 empty] | 1325 | 2 | 25 | 2 | 5 | 24.1 | 24
[25 empty] | 1326 | 2 | 25 | 2 | 6 | 24.1 | 24
[25 empty] | 1327 | 2 | 25 | 2 | 7 | 24.1 | 24
[25 empty] | 1328 | 2 | 25 | 2 | 8 | 26.1 | 26
[25 empty] | 1329 | 2 | 25 | 2 | 9 | 27 | 27
[25 empty] | 1330 | 2 | 25 | 2 | 10 | 28.9 | 29
[25 empty] | 1331 | 2 | 25 | 2 | 11 | 30.9 | 31
[25 empty] | 1332 | 2 | 25 | 2 | 12 | 34 | 34
[25 empty] | 1333 | 2 | 25 | 2 | 13 | 36 | 36
[25 empty] | 1334 | 2 | 25 | 2 | 14 | 37.9 | 38
[25 empty] | 1335 | 2 | 25 | 2 | 15 | 37.9 | 38
[25 empty] | 1336 | 2 | 25 | 2 | 16 | 39 | 39
[25 empty] | 1337 | 2 | 25 | 2 | 17 | 39 | 39
[25 empty] | 1338 | 2 | 25 | 2 | 18 | 39 | 39
[25 empty] | 1339 | 2 | 25 | 2 | 19 | 39 | 39
[25 empty] | 1340 | 2 | 25 | 2 | 20 | 39 | 39
[25 empty] | 1341 | 2 | 25 | 2 | 21 | 39 | 39
[25 empty] | 1342 | 2 | 25 | 2 | 22 | 39 | 39
[25 empty] | 1343 | 2 | 25 | 2 | 23 | 37.9 | 38
[25 empty] | 1344 | 2 | 26 | 3 | 0 | 39 | 39
[25 empty] | 1345 | 2 | 26 | 3 | 1 | 30 | 30
[25 empty] | 1346 | 2 | 26 | 3 | 2 | 28.9 | 29
[25 empty] | 1347 | 2 | 26 | 3 | 3 | 28 | 28
[25 empty] | 1348 | 2 | 26 | 3 | 4 | 27 | 27
[25 empty] | 1349 | 2 | 26 | 3 | 5 | 26.1 | 26
[25 empty] | 1350 | 2 | 26 | 3 | 6 | 24.1 | 24
[25 empty] | 1351 | 2 | 26 | 3 | 7 | 21 | 21
[25 empty] | 1352 | 2 | 26 | 3 | 8 | 19.9 | 20
[25 empty] | 1353 | 2 | 26 | 3 | 9 | 19 | 19
[25 empty] | 1354 | 2 | 26 | 3 | 10 | 19.9 | 20
[25 empty] | 1355 | 2 | 26 | 3 | 11 | 21 | 21
[25 empty] | 1356 | 2 | 26 | 3 | 12 | 21.9 | 22
[25 empty] | 1357 | 2 | 26 | 3 | 13 | 24.1 | 24
[25 empty] | 1358 | 2 | 26 | 3 | 14 | 26.1 | 26
[25 empty] | 1359 | 2 | 26 | 3 | 15 | 27 | 27
[25 empty] | 1360 | 2 | 26 | 3 | 16 | 28 | 28
[25 empty] | 1361 | 2 | 26 | 3 | 17 | 28.9 | 29
[25 empty] | 1362 | 2 | 26 | 3 | 18 | 30 | 30
[25 empty] | 1363 | 2 | 26 | 3 | 19 | 30 | 30
[25 empty] | 1364 | 2 | 26 | 3 | 20 | 30 | 30
[25 empty] | 1365 | 2 | 26 | 3 | 21 | 30 | 30
[25 empty] | 1366 | 2 | 26 | 3 | 22 | 30.9 | 31
[25 empty] | 1367 | 2 | 26 | 3 | 23 | 30.9 | 31
[25 empty] | 1368 | 2 | 27 | 4 | 0 | 30 | 30
[25 empty] | 1369 | 2 | 27 | 4 | 1 | 30.9 | 31
[25 empty] | 1370 | 2 | 27 | 4 | 2 | 30.9 | 31
[25 empty] | 1371 | 2 | 27 | 4 | 3 | 30 | 30
[25 empty] | 1372 | 2 | 27 | 4 | 4 | 30 | 30
[25 empty] | 1373 | 2 | 27 | 4 | 5 | 28.9 | 29
[25 empty] | 1374 | 2 | 27 | 4 | 6 | 28.9 | 29
[25 empty] | 1375 | 2 | 27 | 4 | 7 | 28.9 | 29
[25 empty] | 1376 | 2 | 27 | 4 | 8 | 30 | 30
[25 empty] | 1377 | 2 | 27 | 4 | 9 | 30.9 | 31
[25 empty] | 1378 | 2 | 27 | 4 | 10 | 28.9 | 29
[25 empty] | 1379 | 2 | 27 | 4 | 11 | 28 | 28
[25 empty] | 1380 | 2 | 27 | 4 | 12 | 27 | 27
[25 empty] | 1381 | 2 | 27 | 4 | 13 | 28 | 28
[25 empty] | 1382 | 2 | 27 | 4 | 14 | 28.9 | 29
[25 empty] | 1383 | 2 | 27 | 4 | 15 | 30 | 30
[25 empty] | 1384 | 2 | 27 | 4 | 16 | 30.9 | 31
[25 empty] | 1385 | 2 | 27 | 4 | 17 | 32 | 32
[25 empty] | 1386 | 2 | 27 | 4 | 18 | 32 | 32
[25 empty] | 1387 | 2 | 27 | 4 | 19 | 32 | 32
[25 empty] | 1388 | 2 | 27 | 4 | 20 | 32 | 32
[25 empty] | 1389 | 2 | 27 | 4 | 21 | 30.9 | 31
[25 empty] | 1390 | 2 | 27 | 4 | 22 | 32 | 32
[25 empty] | 1391 | 2 | 27 | 4 | 23 | 33.1 | 33
[25 empty] | 1392 | 2 | 28 | 5 | 0 | 33.1 | 33
[25 empty] | 1393 | 2 | 28 | 5 | 1 | 33.1 | 33
[25 empty] | 1394 | 2 | 28 | 5 | 2 | 33.1 | 33
[25 empty] | 1395 | 2 | 28 | 5 | 3 | 33.1 | 33
[25 empty] | 1396 | 2 | 28 | 5 | 4 | 34 | 34
[25 empty] | 1397 | 2 | 28 | 5 | 5 | 34 | 34
[25 empty] | 1398 | 2 | 28 | 5 | 6 | 34 | 34
[25 empty] | 1399 | 2 | 28 | 5 | 7 | 34 | 34
[25 empty] | 1400 | 2 | 28 | 5 | 8 | 35.1 | 35
[25 empty] | 1401 | 2 | 28 | 5 | 9 | 35.1 | 35
[25 empty] | 1402 | 2 | 28 | 5 | 10 | 37.9 | 38
[25 empty] | 1403 | 2 | 28 | 5 | 11 | 37.9 | 38
[25 empty] | 1404 | 2 | 28 | 5 | 12 | 37 | 37
[25 empty] | 1405 | 2 | 28 | 5 | 13 | 37.9 | 38
[25 empty] | 1406 | 2 | 28 | 5 | 14 | 37.9 | 38
[25 empty] | 1407 | 2 | 28 | 5 | 15 | 39 | 39
[25 empty] | 1408 | 2 | 28 | 5 | 16 | 39.9 | 40
[25 empty] | 1409 | 2 | 28 | 5 | 17 | 41 | 41
[25 empty] | 1410 | 2 | 28 | 5 | 18 | 42.1 | 42
[25 empty] | 1411 | 2 | 28 | 5 | 19 | 41 | 41
[25 empty] | 1412 | 2 | 28 | 5 | 20 | 42.1 | 42
[25 empty] | 1413 | 2 | 28 | 5 | 21 | 41 | 41
[25 empty] | 1414 | 2 | 28 | 5 | 22 | 40.6 | 41
[25 empty] | 1415 | 2 | 28 | 5 | 23 | 40.1 | 40
[25 empty] | 1416 | 3 | 1 | 6 | 0 | 39.7 | 40
[25 empty] | 1417 | 3 | 1 | 6 | 1 | 39.2 | 39
[25 empty] | 1418 | 3 | 1 | 6 | 2 | 38.8 | 39
[25 empty] | 1419 | 3 | 1 | 6 | 3 | 38.3 | 38
[25 empty] | 1420 | 3 | 1 | 6 | 4 | 37.9 | 38
[25 empty] | 1421 | 3 | 1 | 6 | 5 | 37.9 | 38
[25 empty] | 1422 | 3 | 1 | 6 | 6 | 37.9 | 38
[25 empty] | 1423 | 3 | 1 | 6 | 7 | 37 | 37
[25 empty] | 1424 | 3 | 1 | 6 | 8 | 37 | 37
[25 empty] | 1425 | 3 | 1 | 6 | 9 | 37.9 | 38
[25 empty] | 1426 | 3 | 1 | 6 | 10 | 37.9 | 38
[25 empty] | 1427 | 3 | 1 | 6 | 11 | 39.9 | 40
[25 empty] | 1428 | 3 | 1 | 6 | 12 | 41 | 41
[25 empty] | 1429 | 3 | 1 | 6 | 13 | 42.1 | 42
[25 empty] | 1430 | 3 | 1 | 6 | 14 | 42.1 | 42
[25 empty] | 1431 | 3 | 1 | 6 | 15 | 42.1 | 42
[25 empty] | 1432 | 3 | 1 | 6 | 16 | 42.1 | 42
[25 empty] | 1433 | 3 | 1 | 6 | 17 | 42.1 | 42
[25 empty] | 1434 | 3 | 1 | 6 | 18 | 41 | 41
[25 empty] | 1435 | 3 | 1 | 6 | 19 | 41 | 41
[25 empty] | 1436 | 3 | 1 | 6 | 20 | 39.9 | 40
[25 empty] | 1437 | 3 | 1 | 6 | 21 | 39 | 39
[25 empty] | 1438 | 3 | 1 | 6 | 22 | 39 | 39
[25 empty] | 1439 | 3 | 1 | 6 | 23 | 37 | 37
[25 empty] | 1440 | 3 | 2 | 7 | 0 | 36 | 36
[25 empty] | 1441 | 3 | 2 | 7 | 1 | 35.1 | 35
[25 empty] | 1442 | 3 | 2 | 7 | 2 | 33.1 | 33
[25 empty] | 1443 | 3 | 2 | 7 | 3 | 32 | 32
[25 empty] | 1444 | 3 | 2 | 7 | 4 | 30.9 | 31
[25 empty] | 1445 | 3 | 2 | 7 | 5 | 30.9 | 31
[25 empty] | 1446 | 3 | 2 | 7 | 6 | 30 | 30
[25 empty] | 1447 | 3 | 2 | 7 | 7 | 30 | 30
[25 empty] | 1448 | 3 | 2 | 7 | 8 | 30.9 | 31
[25 empty] | 1449 | 3 | 2 | 7 | 9 | 30.9 | 31
[25 empty] | 1450 | 3 | 2 | 7 | 10 | 34 | 34
[25 empty] | 1451 | 3 | 2 | 7 | 11 | 35.1 | 35
[25 empty] | 1452 | 3 | 2 | 7 | 12 | 34 | 34
[25 empty] | 1453 | 3 | 2 | 7 | 13 | 37 | 37
[25 empty] | 1454 | 3 | 2 | 7 | 14 | 37 | 37
[25 empty] | 1455 | 3 | 2 | 7 | 15 | 37.9 | 38
[25 empty] | 1456 | 3 | 2 | 7 | 16 | 37 | 37
[25 empty] | 1457 | 3 | 2 | 7 | 17 | 37 | 37
[25 empty] | 1458 | 3 | 2 | 7 | 18 | 36 | 36
[25 empty] | 1459 | 3 | 2 | 7 | 19 | 35.1 | 35
[25 empty] | 1460 | 3 | 2 | 7 | 20 | 34 | 34
[25 empty] | 1461 | 3 | 2 | 7 | 21 | 32 | 32
[25 empty] | 1462 | 3 | 2 | 7 | 22 | 32 | 32
[25 empty] | 1463 | 3 | 2 | 7 | 23 | 30.9 | 31
[25 empty] | 1464 | 3 | 3 | 1 | 0 | 30.9 | 31
[25 empty] | 1465 | 3 | 3 | 1 | 1 | 30 | 30
[25 empty] | 1466 | 3 | 3 | 1 | 2 | 30 | 30
[25 empty] | 1467 | 3 | 3 | 1 | 3 | 28.9 | 29
[25 empty] | 1468 | 3 | 3 | 1 | 4 | 28.9 | 29
[25 empty] | 1469 | 3 | 3 | 1 | 5 | 28.9 | 29
[25 empty] | 1470 | 3 | 3 | 1 | 6 | 28 | 28
[25 empty] | 1471 | 3 | 3 | 1 | 7 | 28 | 28
[25 empty] | 1472 | 3 | 3 | 1 | 8 | 30.9 | 31
[25 empty] | 1473 | 3 | 3 | 1 | 9 | 32 | 32
[25 empty] | 1474 | 3 | 3 | 1 | 10 | 32 | 32
[25 empty] | 1475 | 3 | 3 | 1 | 11 | 33.1 | 33
[25 empty] | 1476 | 3 | 3 | 1 | 12 | 34 | 34
[25 empty] | 1477 | 3 | 3 | 1 | 13 | 36 | 36
[25 empty] | 1478 | 3 | 3 | 1 | 14 | 36 | 36
[25 empty] | 1479 | 3 | 3 | 1 | 15 | 37 | 37
[25 empty] | 1480 | 3 | 3 | 1 | 16 | 37 | 37
[25 empty] | 1481 | 3 | 3 | 1 | 17 | 37.9 | 38
[25 empty] | 1482 | 3 | 3 | 1 | 18 | 37 | 37
[25 empty] | 1483 | 3 | 3 | 1 | 19 | 36 | 36
[25 empty] | 1484 | 3 | 3 | 1 | 20 | 35.1 | 35
[25 empty] | 1485 | 3 | 3 | 1 | 21 | 36 | 36
[25 empty] | 1486 | 3 | 3 | 1 | 22 | 34 | 34
[25 empty] | 1487 | 3 | 3 | 1 | 23 | 34 | 34
[25 empty] | 1488 | 3 | 4 | 2 | 0 | 34 | 34
[25 empty] | 1489 | 3 | 4 | 2 | 1 | 34 | 34
[25 empty] | 1490 | 3 | 4 | 2 | 2 | 34 | 34
[25 empty] | 1491 | 3 | 4 | 2 | 3 | 34 | 34
[25 empty] | 1492 | 3 | 4 | 2 | 4 | 34 | 34
[25 empty] | 1493 | 3 | 4 | 2 | 5 | 34 | 34
[25 empty] | 1494 | 3 | 4 | 2 | 6 | 35.1 | 35
[25 empty] | 1495 | 3 | 4 | 2 | 7 | 35.1 | 35
[25 empty] | 1496 | 3 | 4 | 2 | 8 | 35.1 | 35
[25 empty] | 1497 | 3 | 4 | 2 | 9 | 35.1 | 35
[25 empty] | 1498 | 3 | 4 | 2 | 10 | 35.1 | 35
[25 empty] | 1499 | 3 | 4 | 2 | 11 | 36 | 36
[25 empty] | 1500 | 3 | 4 | 2 | 12 | 36 | 36
[25 empty] | 1501 | 3 | 4 | 2 | 13 | 37 | 37
[25 empty] | 1502 | 3 | 4 | 2 | 14 | 37 | 37
[25 empty] | 1503 | 3 | 4 | 2 | 15 | 37 | 37
[25 empty] | 1504 | 3 | 4 | 2 | 16 | 37.9 | 38
[25 empty] | 1505 | 3 | 4 | 2 | 17 | 37.9 | 38
[25 empty] | 1506 | 3 | 4 | 2 | 18 | 37.9 | 38
[25 empty] | 1507 | 3 | 4 | 2 | 19 | 37.9 | 38
[25 empty] | 1508 | 3 | 4 | 2 | 20 | 36 | 36
[25 empty] | 1509 | 3 | 4 | 2 | 21 | 36 | 36
[25 empty] | 1510 | 3 | 4 | 2 | 22 | 36 | 36
[25 empty] | 1511 | 3 | 4 | 2 | 23 | 36 | 36
[25 empty] | 1512 | 3 | 5 | 3 | 0 | 35.1 | 35
[25 empty] | 1513 | 3 | 5 | 3 | 1 | 35.1 | 35
[25 empty] | 1514 | 3 | 5 | 3 | 2 | 35.1 | 35
[25 empty] | 1515 | 3 | 5 | 3 | 3 | 34 | 34
[25 empty] | 1516 | 3 | 5 | 3 | 4 | 33.1 | 33
[25 empty] | 1517 | 3 | 5 | 3 | 5 | 33.1 | 33
[25 empty] | 1518 | 3 | 5 | 3 | 6 | 33.1 | 33
[25 empty] | 1519 | 3 | 5 | 3 | 7 | 34 | 34
[25 empty] | 1520 | 3 | 5 | 3 | 8 | 35.1 | 35
[25 empty] | 1521 | 3 | 5 | 3 | 9 | 36 | 36
[25 empty] | 1522 | 3 | 5 | 3 | 10 | 37 | 37
[25 empty] | 1523 | 3 | 5 | 3 | 11 | 39 | 39
[25 empty] | 1524 | 3 | 5 | 3 | 12 | 41 | 41
[25 empty] | 1525 | 3 | 5 | 3 | 13 | 42.1 | 42
[25 empty] | 1526 | 3 | 5 | 3 | 14 | 43 | 43
[25 empty] | 1527 | 3 | 5 | 3 | 15 | 44.1 | 44
[25 empty] | 1528 | 3 | 5 | 3 | 16 | 44.1 | 44
[25 empty] | 1529 | 3 | 5 | 3 | 17 | 43 | 43
[25 empty] | 1530 | 3 | 5 | 3 | 18 | 42.1 | 42
[25 empty] | 1531 | 3 | 5 | 3 | 19 | 43 | 43
[25 empty] | 1532 | 3 | 5 | 3 | 20 | 43 | 43
[25 empty] | 1533 | 3 | 5 | 3 | 21 | 42.1 | 42
[25 empty] | 1534 | 3 | 5 | 3 | 22 | 39.9 | 40
[25 empty] | 1535 | 3 | 5 | 3 | 23 | 39 | 39
[25 empty] | 1536 | 3 | 6 | 4 | 0 | 37.9 | 38
[25 empty] | 1537 | 3 | 6 | 4 | 1 | 37.9 | 38
[25 empty] | 1538 | 3 | 6 | 4 | 2 | 37.9 | 38
[25 empty] | 1539 | 3 | 6 | 4 | 3 | 37.9 | 38
[25 empty] | 1540 | 3 | 6 | 4 | 4 | 37.9 | 38
[25 empty] | 1541 | 3 | 6 | 4 | 5 | 37.9 | 38
[25 empty] | 1542 | 3 | 6 | 4 | 6 | 39 | 39
[25 empty] | 1543 | 3 | 6 | 4 | 7 | 41 | 41
[25 empty] | 1544 | 3 | 6 | 4 | 8 | 42.1 | 42
[25 empty] | 1545 | 3 | 6 | 4 | 9 | 45 | 45
[25 empty] | 1546 | 3 | 6 | 4 | 10 | 46 | 46
[25 empty] | 1547 | 3 | 6 | 4 | 11 | 46 | 46
[25 empty] | 1548 | 3 | 6 | 4 | 12 | 50 | 50
[25 empty] | 1549 | 3 | 6 | 4 | 13 | 51.1 | 51
[25 empty] | 1550 | 3 | 6 | 4 | 14 | 53.1 | 53
[25 empty] | 1551 | 3 | 6 | 4 | 15 | 54 | 54
[25 empty] | 1552 | 3 | 6 | 4 | 16 | 52 | 52
[25 empty] | 1553 | 3 | 6 | 4 | 17 | 55 | 55
[25 empty] | 1554 | 3 | 6 | 4 | 18 | 48.9 | 49
[25 empty] | 1555 | 3 | 6 | 4 | 19 | 50 | 50
[25 empty] | 1556 | 3 | 6 | 4 | 20 | 51.1 | 51
[25 empty] | 1557 | 3 | 6 | 4 | 21 | 50 | 50
[25 empty] | 1558 | 3 | 6 | 4 | 22 | 48.9 | 49
[25 empty] | 1559 | 3 | 6 | 4 | 23 | 46 | 46
[25 empty] | 1560 | 3 | 7 | 5 | 0 | 41 | 41
[25 empty] | 1561 | 3 | 7 | 5 | 1 | 41 | 41
[25 empty] | 1562 | 3 | 7 | 5 | 2 | 41 | 41
[25 empty] | 1563 | 3 | 7 | 5 | 3 | 41 | 41
[25 empty] | 1564 | 3 | 7 | 5 | 4 | 39.9 | 40
[25 empty] | 1565 | 3 | 7 | 5 | 5 | 39.9 | 40
[25 empty] | 1566 | 3 | 7 | 5 | 6 | 39 | 39
[25 empty] | 1567 | 3 | 7 | 5 | 7 | 39.9 | 40
[25 empty] | 1568 | 3 | 7 | 5 | 8 | 41 | 41
[25 empty] | 1569 | 3 | 7 | 5 | 9 | 43 | 43
[25 empty] | 1570 | 3 | 7 | 5 | 10 | 46 | 46
[25 empty] | 1571 | 3 | 7 | 5 | 11 | 52 | 52
[25 empty] | 1572 | 3 | 7 | 5 | 12 | 51.1 | 51
[25 empty] | 1573 | 3 | 7 | 5 | 13 | 50 | 50
[25 empty] | 1574 | 3 | 7 | 5 | 14 | 50 | 50
[25 empty] | 1575 | 3 | 7 | 5 | 15 | 50 | 50
[25 empty] | 1576 | 3 | 7 | 5 | 16 | 52 | 52
[25 empty] | 1577 | 3 | 7 | 5 | 17 | 51.1 | 51
[25 empty] | 1578 | 3 | 7 | 5 | 18 | 51.1 | 51
[25 empty] | 1579 | 3 | 7 | 5 | 19 | 51.1 | 51
[25 empty] | 1580 | 3 | 7 | 5 | 20 | 50 | 50
[25 empty] | 1581 | 3 | 7 | 5 | 21 | 48 | 48
[25 empty] | 1582 | 3 | 7 | 5 | 22 | 48 | 48
[25 empty] | 1583 | 3 | 7 | 5 | 23 | 48 | 48
[25 empty] | 1584 | 3 | 8 | 6 | 0 | 48 | 48
[25 empty] | 1585 | 3 | 8 | 6 | 1 | 48.9 | 49
[25 empty] | 1586 | 3 | 8 | 6 | 2 | 48.9 | 49
[25 empty] | 1587 | 3 | 8 | 6 | 3 | 50 | 50
[25 empty] | 1588 | 3 | 8 | 6 | 4 | 48 | 48
[25 empty] | 1589 | 3 | 8 | 6 | 5 | 48 | 48
[25 empty] | 1590 | 3 | 8 | 6 | 6 | 48.9 | 49
[25 empty] | 1591 | 3 | 8 | 6 | 7 | 51.1 | 51
[25 empty] | 1592 | 3 | 8 | 6 | 8 | 53.1 | 53
[25 empty] | 1593 | 3 | 8 | 6 | 9 | 54 | 54
[25 empty] | 1594 | 3 | 8 | 6 | 10 | 55.9 | 56
[25 empty] | 1595 | 3 | 8 | 6 | 11 | 60.1 | 60
[25 empty] | 1596 | 3 | 8 | 6 | 12 | 60.1 | 60
[25 empty] | 1597 | 3 | 8 | 6 | 13 | 61 | 61
[25 empty] | 1598 | 3 | 8 | 6 | 14 | 59 | 59
[25 empty] | 1599 | 3 | 8 | 6 | 15 | 57.9 | 58
[25 empty] | 1600 | 3 | 8 | 6 | 16 | 57.9 | 58
[25 empty] | 1601 | 3 | 8 | 6 | 17 | 57.9 | 58
[25 empty] | 1602 | 3 | 8 | 6 | 18 | 57 | 57
[25 empty] | 1603 | 3 | 8 | 6 | 19 | 57.9 | 58
[25 empty] | 1604 | 3 | 8 | 6 | 20 | 44.1 | 44
[25 empty] | 1605 | 3 | 8 | 6 | 21 | 43 | 43
[25 empty] | 1606 | 3 | 8 | 6 | 22 | 42.1 | 42
[25 empty] | 1607 | 3 | 8 | 6 | 23 | 41 | 41
[25 empty] | 1608 | 3 | 9 | 7 | 0 | 39.9 | 40
[25 empty] | 1609 | 3 | 9 | 7 | 1 | 37 | 37
[25 empty] | 1610 | 3 | 9 | 7 | 2 | 37 | 37
[25 empty] | 1611 | 3 | 9 | 7 | 3 | 34 | 34
[25 empty] | 1612 | 3 | 9 | 7 | 4 | 32 | 32
[25 empty] | 1613 | 3 | 9 | 7 | 5 | 32 | 32
[25 empty] | 1614 | 3 | 9 | 7 | 6 | 32 | 32
[25 empty] | 1615 | 3 | 9 | 7 | 7 | 30 | 30
[25 empty] | 1616 | 3 | 9 | 7 | 8 | 28 | 28
[25 empty] | 1617 | 3 | 9 | 7 | 9 | 28 | 28
[25 empty] | 1618 | 3 | 9 | 7 | 10 | 28.9 | 29
[25 empty] | 1619 | 3 | 9 | 7 | 11 | 30.9 | 31
[25 empty] | 1620 | 3 | 9 | 7 | 12 | 30.9 | 31
[25 empty] | 1621 | 3 | 9 | 7 | 13 | 32 | 32
[25 empty] | 1622 | 3 | 9 | 7 | 14 | 33.1 | 33
[25 empty] | 1623 | 3 | 9 | 7 | 15 | 34 | 34
[25 empty] | 1624 | 3 | 9 | 7 | 16 | 33.1 | 33
[25 empty] | 1625 | 3 | 9 | 7 | 17 | 33.1 | 33
[25 empty] | 1626 | 3 | 9 | 7 | 18 | 30.9 | 31
[25 empty] | 1627 | 3 | 9 | 7 | 19 | 28.9 | 29
[25 empty] | 1628 | 3 | 9 | 7 | 20 | 27 | 27
[25 empty] | 1629 | 3 | 9 | 7 | 21 | 26.1 | 26
[25 empty] | 1630 | 3 | 9 | 7 | 22 | 25 | 25
[25 empty] | 1631 | 3 | 9 | 7 | 23 | 25 | 25
[25 empty] | 1632 | 3 | 10 | 1 | 0 | 24.1 | 24
[25 empty] | 1633 | 3 | 10 | 1 | 1 | 24.1 | 24
[25 empty] | 1634 | 3 | 10 | 1 | 2 | 24.1 | 24
[25 empty] | 1635 | 3 | 10 | 1 | 3 | 23 | 23
[25 empty] | 1636 | 3 | 10 | 1 | 4 | 23 | 23
[25 empty] | 1637 | 3 | 10 | 1 | 5 | 21.9 | 22
[25 empty] | 1638 | 3 | 10 | 1 | 6 | 21.9 | 22
[25 empty] | 1639 | 3 | 10 | 1 | 7 | 23 | 23
[25 empty] | 1640 | 3 | 10 | 1 | 8 | 23 | 23
[25 empty] | 1641 | 3 | 10 | 1 | 9 | 25 | 25
[25 empty] | 1642 | 3 | 10 | 1 | 10 | 28 | 28
[25 empty] | 1643 | 3 | 10 | 1 | 11 | 30 | 30
[25 empty] | 1644 | 3 | 10 | 1 | 12 | 32 | 32
[25 empty] | 1645 | 3 | 10 | 1 | 13 | 34 | 34
[25 empty] | 1646 | 3 | 10 | 1 | 14 | 35.1 | 35
[25 empty] | 1647 | 3 | 10 | 1 | 15 | 37 | 37
[25 empty] | 1648 | 3 | 10 | 1 | 16 | 37.9 | 38
[25 empty] | 1649 | 3 | 10 | 1 | 17 | 37.9 | 38
[25 empty] | 1650 | 3 | 10 | 1 | 18 | 37 | 37
[25 empty] | 1651 | 3 | 10 | 1 | 19 | 36 | 36
[25 empty] | 1652 | 3 | 10 | 1 | 20 | 35.1 | 35
[25 empty] | 1653 | 3 | 10 | 1 | 21 | 35.1 | 35
[25 empty] | 1654 | 3 | 10 | 1 | 22 | 34 | 34
[25 empty] | 1655 | 3 | 10 | 1 | 23 | 34 | 34
[25 empty] | 1656 | 3 | 11 | 2 | 0 | 34 | 34
[25 empty] | 1657 | 3 | 11 | 2 | 1 | 34 | 34
[25 empty] | 1658 | 3 | 11 | 2 | 2 | 33.1 | 33
[25 empty] | 1659 | 3 | 11 | 2 | 3 | 33.1 | 33
[25 empty] | 1660 | 3 | 11 | 2 | 4 | 32 | 32
[25 empty] | 1661 | 3 | 11 | 2 | 5 | 32 | 32
[25 empty] | 1662 | 3 | 11 | 2 | 6 | 32 | 32
[25 empty] | 1663 | 3 | 11 | 2 | 7 | 33.1 | 33
[25 empty] | 1664 | 3 | 11 | 2 | 8 | 34 | 34
[25 empty] | 1665 | 3 | 11 | 2 | 9 | 35.1 | 35
[25 empty] | 1666 | 3 | 11 | 2 | 10 | 37 | 37
[25 empty] | 1667 | 3 | 11 | 2 | 11 | 39 | 39
[25 empty] | 1668 | 3 | 11 | 2 | 12 | 39.9 | 40
[25 empty] | 1669 | 3 | 11 | 2 | 13 | 41 | 41
[25 empty] | 1670 | 3 | 11 | 2 | 14 | 43 | 43
[25 empty] | 1671 | 3 | 11 | 2 | 15 | 44.1 | 44
[25 empty] | 1672 | 3 | 11 | 2 | 16 | 42.1 | 42
[25 empty] | 1673 | 3 | 11 | 2 | 17 | 41 | 41
[25 empty] | 1674 | 3 | 11 | 2 | 18 | 39.9 | 40
[25 empty] | 1675 | 3 | 11 | 2 | 19 | 39 | 39
[25 empty] | 1676 | 3 | 11 | 2 | 20 | 39 | 39
[25 empty] | 1677 | 3 | 11 | 2 | 21 | 39 | 39
[25 empty] | 1678 | 3 | 11 | 2 | 22 | 39 | 39
[25 empty] | 1679 | 3 | 11 | 2 | 23 | 37.9 | 38
[25 empty] | 1680 | 3 | 12 | 3 | 0 | 37 | 37
[25 empty] | 1681 | 3 | 12 | 3 | 1 | 37 | 37
[25 empty] | 1682 | 3 | 12 | 3 | 2 | 37 | 37
[25 empty] | 1683 | 3 | 12 | 3 | 3 | 36 | 36
[25 empty] | 1684 | 3 | 12 | 3 | 4 | 36 | 36
[25 empty] | 1685 | 3 | 12 | 3 | 5 | 36 | 36
[25 empty] | 1686 | 3 | 12 | 3 | 6 | 35.1 | 35
[25 empty] | 1687 | 3 | 12 | 3 | 7 | 35.1 | 35
[25 empty] | 1688 | 3 | 12 | 3 | 8 | 37.9 | 38
[25 empty] | 1689 | 3 | 12 | 3 | 9 | 39.9 | 40
[25 empty] | 1690 | 3 | 12 | 3 | 10 | 42.1 | 42
[25 empty] | 1691 | 3 | 12 | 3 | 11 | 46.9 | 47
[25 empty] | 1692 | 3 | 12 | 3 | 12 | 48.9 | 49
[25 empty] | 1693 | 3 | 12 | 3 | 13 | 45 | 45
[25 empty] | 1694 | 3 | 12 | 3 | 14 | 44.1 | 44
[25 empty] | 1695 | 3 | 12 | 3 | 15 | 44.1 | 44
[25 empty] | 1696 | 3 | 12 | 3 | 16 | 42.1 | 42
[25 empty] | 1697 | 3 | 12 | 3 | 17 | 42.1 | 42
[25 empty] | 1698 | 3 | 12 | 3 | 18 | 41 | 41
[25 empty] | 1699 | 3 | 12 | 3 | 19 | 42.1 | 42
[25 empty] | 1700 | 3 | 12 | 3 | 20 | 41 | 41
[25 empty] | 1701 | 3 | 12 | 3 | 21 | 39.9 | 40
[25 empty] | 1702 | 3 | 12 | 3 | 22 | 39.9 | 40
[25 empty] | 1703 | 3 | 12 | 3 | 23 | 39 | 39
[25 empty] | 1704 | 3 | 13 | 4 | 0 | 39 | 39
[25 empty] | 1705 | 3 | 13 | 4 | 1 | 39 | 39
[25 empty] | 1706 | 3 | 13 | 4 | 2 | 37.9 | 38
[25 empty] | 1707 | 3 | 13 | 4 | 3 | 37.9 | 38
[25 empty] | 1708 | 3 | 13 | 4 | 4 | 37.9 | 38
[25 empty] | 1709 | 3 | 13 | 4 | 5 | 37.9 | 38
[25 empty] | 1710 | 3 | 13 | 4 | 6 | 39 | 39
[25 empty] | 1711 | 3 | 13 | 4 | 7 | 39 | 39
[25 empty] | 1712 | 3 | 13 | 4 | 8 | 41 | 41
[25 empty] | 1713 | 3 | 13 | 4 | 9 | 45 | 45
[25 empty] | 1714 | 3 | 13 | 4 | 10 | 48 | 48
[25 empty] | 1715 | 3 | 13 | 4 | 11 | 54 | 54
[25 empty] | 1716 | 3 | 13 | 4 | 12 | 60.1 | 60
[25 empty] | 1717 | 3 | 13 | 4 | 13 | 63 | 63
[25 empty] | 1718 | 3 | 13 | 4 | 14 | 66.9 | 67
[25 empty] | 1719 | 3 | 13 | 4 | 15 | 71.1 | 71
[25 empty] | 1720 | 3 | 13 | 4 | 16 | 72 | 72
[25 empty] | 1721 | 3 | 13 | 4 | 17 | 71.1 | 71
[25 empty] | 1722 | 3 | 13 | 4 | 18 | 68 | 68
[25 empty] | 1723 | 3 | 13 | 4 | 19 | 64 | 64
[25 empty] | 1724 | 3 | 13 | 4 | 20 | 60.1 | 60
[25 empty] | 1725 | 3 | 13 | 4 | 21 | 57.9 | 58
[25 empty] | 1726 | 3 | 13 | 4 | 22 | 60.1 | 60
[25 empty] | 1727 | 3 | 13 | 4 | 23 | 51.1 | 51
[25 empty] | 1728 | 3 | 14 | 5 | 0 | 48.9 | 49
[25 empty] | 1729 | 3 | 14 | 5 | 1 | 50 | 50
[25 empty] | 1730 | 3 | 14 | 5 | 2 | 48.9 | 49
[25 empty] | 1731 | 3 | 14 | 5 | 3 | 46.9 | 47
[25 empty] | 1732 | 3 | 14 | 5 | 4 | 44.1 | 44
[25 empty] | 1733 | 3 | 14 | 5 | 5 | 43 | 43
[25 empty] | 1734 | 3 | 14 | 5 | 6 | 42.1 | 42
[25 empty] | 1735 | 3 | 14 | 5 | 7 | 43 | 43
[25 empty] | 1736 | 3 | 14 | 5 | 8 | 46 | 46
[25 empty] | 1737 | 3 | 14 | 5 | 9 | 46.9 | 47
[25 empty] | 1738 | 3 | 14 | 5 | 10 | 48 | 48
[25 empty] | 1739 | 3 | 14 | 5 | 11 | 50 | 50
[25 empty] | 1740 | 3 | 14 | 5 | 12 | 53.1 | 53
[25 empty] | 1741 | 3 | 14 | 5 | 13 | 55.9 | 56
[25 empty] | 1742 | 3 | 14 | 5 | 14 | 59 | 59
[25 empty] | 1743 | 3 | 14 | 5 | 15 | 54 | 54
[25 empty] | 1744 | 3 | 14 | 5 | 16 | 51.1 | 51
[25 empty] | 1745 | 3 | 14 | 5 | 17 | 48.9 | 49
[25 empty] | 1746 | 3 | 14 | 5 | 18 | 45 | 45
[25 empty] | 1747 | 3 | 14 | 5 | 19 | 45 | 45
[25 empty] | 1748 | 3 | 14 | 5 | 20 | 45 | 45
[25 empty] | 1749 | 3 | 14 | 5 | 21 | 44.1 | 44
[25 empty] | 1750 | 3 | 14 | 5 | 22 | 44.1 | 44
[25 empty] | 1751 | 3 | 14 | 5 | 23 | 44.1 | 44
[25 empty] | 1752 | 3 | 15 | 6 | 0 | 45 | 45
[25 empty] | 1753 | 3 | 15 | 6 | 1 | 45 | 45
[25 empty] | 1754 | 3 | 15 | 6 | 2 | 44.1 | 44
[25 empty] | 1755 | 3 | 15 | 6 | 3 | 45 | 45
[25 empty] | 1756 | 3 | 15 | 6 | 4 | 45 | 45
[25 empty] | 1757 | 3 | 15 | 6 | 5 | 45 | 45
[25 empty] | 1758 | 3 | 15 | 6 | 6 | 45 | 45
[25 empty] | 1759 | 3 | 15 | 6 | 7 | 45 | 45
[25 empty] | 1760 | 3 | 15 | 6 | 8 | 46 | 46
[25 empty] | 1761 | 3 | 15 | 6 | 9 | 48 | 48
[25 empty] | 1762 | 3 | 15 | 6 | 10 | 52 | 52
[25 empty] | 1763 | 3 | 15 | 6 | 11 | 53.1 | 53
[25 empty] | 1764 | 3 | 15 | 6 | 12 | 59 | 59
[25 empty] | 1765 | 3 | 15 | 6 | 13 | 66 | 66
[25 empty] | 1766 | 3 | 15 | 6 | 14 | 70 | 70
[25 empty] | 1767 | 3 | 15 | 6 | 15 | 69.1 | 69
[25 empty] | 1768 | 3 | 15 | 6 | 16 | 68 | 68
[25 empty] | 1769 | 3 | 15 | 6 | 17 | 64 | 64
[25 empty] | 1770 | 3 | 15 | 6 | 18 | 55.9 | 56
[25 empty] | 1771 | 3 | 15 | 6 | 19 | 54 | 54
[25 empty] | 1772 | 3 | 15 | 6 | 20 | 53.1 | 53
[25 empty] | 1773 | 3 | 15 | 6 | 21 | 52 | 52
[25 empty] | 1774 | 3 | 15 | 6 | 22 | 50 | 50
[25 empty] | 1775 | 3 | 15 | 6 | 23 | 50 | 50
[25 empty] | 1776 | 3 | 16 | 7 | 0 | 46 | 46
[25 empty] | 1777 | 3 | 16 | 7 | 1 | 46 | 46
[25 empty] | 1778 | 3 | 16 | 7 | 2 | 45 | 45
[25 empty] | 1779 | 3 | 16 | 7 | 3 | 44.1 | 44
[25 empty] | 1780 | 3 | 16 | 7 | 4 | 43 | 43
[25 empty] | 1781 | 3 | 16 | 7 | 5 | 43 | 43
[25 empty] | 1782 | 3 | 16 | 7 | 6 | 42.1 | 42
[25 empty] | 1783 | 3 | 16 | 7 | 7 | 42.1 | 42
[25 empty] | 1784 | 3 | 16 | 7 | 8 | 45 | 45
[25 empty] | 1785 | 3 | 16 | 7 | 9 | 48 | 48
[25 empty] | 1786 | 3 | 16 | 7 | 10 | 51.1 | 51
[25 empty] | 1787 | 3 | 16 | 7 | 11 | 60.1 | 60
[25 empty] | 1788 | 3 | 16 | 7 | 12 | 59 | 59
[25 empty] | 1789 | 3 | 16 | 7 | 13 | 57 | 57
[25 empty] | 1790 | 3 | 16 | 7 | 14 | 55.9 | 56
[25 empty] | 1791 | 3 | 16 | 7 | 15 | 54 | 54
[25 empty] | 1792 | 3 | 16 | 7 | 16 | 54 | 54
[25 empty] | 1793 | 3 | 16 | 7 | 17 | 52 | 52
[25 empty] | 1794 | 3 | 16 | 7 | 18 | 52 | 52
[25 empty] | 1795 | 3 | 16 | 7 | 19 | 52 | 52
[25 empty] | 1796 | 3 | 16 | 7 | 20 | 51.1 | 51
[25 empty] | 1797 | 3 | 16 | 7 | 21 | 51.1 | 51
[25 empty] | 1798 | 3 | 16 | 7 | 22 | 51.1 | 51
[25 empty] | 1799 | 3 | 16 | 7 | 23 | 46.9 | 47
[25 empty] | 1800 | 3 | 17 | 1 | 0 | 44.1 | 44
[25 empty] | 1801 | 3 | 17 | 1 | 1 | 46 | 46
[25 empty] | 1802 | 3 | 17 | 1 | 2 | 46 | 46
[25 empty] | 1803 | 3 | 17 | 1 | 3 | 45 | 45
[25 empty] | 1804 | 3 | 17 | 1 | 4 | 44.1 | 44
[25 empty] | 1805 | 3 | 17 | 1 | 5 | 44.1 | 44
[25 empty] | 1806 | 3 | 17 | 1 | 6 | 44.1 | 44
[25 empty] | 1807 | 3 | 17 | 1 | 7 | 44.1 | 44
[25 empty] | 1808 | 3 | 17 | 1 | 8 | 45 | 45
[25 empty] | 1809 | 3 | 17 | 1 | 9 | 45 | 45
[25 empty] | 1810 | 3 | 17 | 1 | 10 | 46 | 46
[25 empty] | 1811 | 3 | 17 | 1 | 11 | 48 | 48
[25 empty] | 1812 | 3 | 17 | 1 | 12 | 51.1 | 51
[25 empty] | 1813 | 3 | 17 | 1 | 13 | 55.9 | 56
[25 empty] | 1814 | 3 | 17 | 1 | 14 | 59 | 59
[25 empty] | 1815 | 3 | 17 | 1 | 15 | 55.9 | 56
[25 empty] | 1816 | 3 | 17 | 1 | 16 | 55 | 55
[25 empty] | 1817 | 3 | 17 | 1 | 17 | 54 | 54
[25 empty] | 1818 | 3 | 17 | 1 | 18 | 55 | 55
[25 empty] | 1819 | 3 | 17 | 1 | 19 | 51.1 | 51
[25 empty] | 1820 | 3 | 17 | 1 | 20 | 54 | 54
[25 empty] | 1821 | 3 | 17 | 1 | 21 | 51.1 | 51
[25 empty] | 1822 | 3 | 17 | 1 | 22 | 48.9 | 49
[25 empty] | 1823 | 3 | 17 | 1 | 23 | 46.9 | 47
[25 empty] | 1824 | 3 | 18 | 2 | 0 | 44.1 | 44
[25 empty] | 1825 | 3 | 18 | 2 | 1 | 43 | 43
[25 empty] | 1826 | 3 | 18 | 2 | 2 | 42.1 | 42
[25 empty] | 1827 | 3 | 18 | 2 | 3 | 42.1 | 42
[25 empty] | 1828 | 3 | 18 | 2 | 4 | 42.1 | 42
[25 empty] | 1829 | 3 | 18 | 2 | 5 | 41 | 41
[25 empty] | 1830 | 3 | 18 | 2 | 6 | 41 | 41
[25 empty] | 1831 | 3 | 18 | 2 | 7 | 41 | 41
[25 empty] | 1832 | 3 | 18 | 2 | 8 | 43 | 43
[25 empty] | 1833 | 3 | 18 | 2 | 9 | 45 | 45
[25 empty] | 1834 | 3 | 18 | 2 | 10 | 46.9 | 47
[25 empty] | 1835 | 3 | 18 | 2 | 11 | 48.9 | 49
[25 empty] | 1836 | 3 | 18 | 2 | 12 | 51.1 | 51
[25 empty] | 1837 | 3 | 18 | 2 | 13 | 53.1 | 53
[25 empty] | 1838 | 3 | 18 | 2 | 14 | 55 | 55
[25 empty] | 1839 | 3 | 18 | 2 | 15 | 55 | 55
[25 empty] | 1840 | 3 | 18 | 2 | 16 | 55 | 55
[25 empty] | 1841 | 3 | 18 | 2 | 17 | 55 | 55
[25 empty] | 1842 | 3 | 18 | 2 | 18 | 54 | 54
[25 empty] | 1843 | 3 | 18 | 2 | 19 | 51.1 | 51
[25 empty] | 1844 | 3 | 18 | 2 | 20 | 50 | 50
[25 empty] | 1845 | 3 | 18 | 2 | 21 | 48 | 48
[25 empty] | 1846 | 3 | 18 | 2 | 22 | 48 | 48
[25 empty] | 1847 | 3 | 18 | 2 | 23 | 48 | 48
[25 empty] | 1848 | 3 | 19 | 3 | 0 | 46.9 | 47
[25 empty] | 1849 | 3 | 19 | 3 | 1 | 46 | 46
[25 empty] | 1850 | 3 | 19 | 3 | 2 | 45 | 45
[25 empty] | 1851 | 3 | 19 | 3 | 3 | 43 | 43
[25 empty] | 1852 | 3 | 19 | 3 | 4 | 42.1 | 42
[25 empty] | 1853 | 3 | 19 | 3 | 5 | 43 | 43
[25 empty] | 1854 | 3 | 19 | 3 | 6 | 41 | 41
[25 empty] | 1855 | 3 | 19 | 3 | 7 | 42.1 | 42
[25 empty] | 1856 | 3 | 19 | 3 | 8 | 43 | 43
[25 empty] | 1857 | 3 | 19 | 3 | 9 | 45 | 45
[25 empty] | 1858 | 3 | 19 | 3 | 10 | 46.9 | 47
[25 empty] | 1859 | 3 | 19 | 3 | 11 | 46.9 | 47
[25 empty] | 1860 | 3 | 19 | 3 | 12 | 48 | 48
[25 empty] | 1861 | 3 | 19 | 3 | 13 | 48.9 | 49
[25 empty] | 1862 | 3 | 19 | 3 | 14 | 48.9 | 49
[25 empty] | 1863 | 3 | 19 | 3 | 15 | 50 | 50
[25 empty] | 1864 | 3 | 19 | 3 | 16 | 48.9 | 49
[25 empty] | 1865 | 3 | 19 | 3 | 17 | 46.9 | 47
[25 empty] | 1866 | 3 | 19 | 3 | 18 | 45 | 45
[25 empty] | 1867 | 3 | 19 | 3 | 19 | 43 | 43
[25 empty] | 1868 | 3 | 19 | 3 | 20 | 43 | 43
[25 empty] | 1869 | 3 | 19 | 3 | 21 | 42.1 | 42
[25 empty] | 1870 | 3 | 19 | 3 | 22 | 43 | 43
[25 empty] | 1871 | 3 | 19 | 3 | 23 | 43 | 43
[25 empty] | 1872 | 3 | 20 | 4 | 0 | 42.1 | 42
[25 empty] | 1873 | 3 | 20 | 4 | 1 | 42.1 | 42
[25 empty] | 1874 | 3 | 20 | 4 | 2 | 41 | 41
[25 empty] | 1875 | 3 | 20 | 4 | 3 | 41 | 41
[25 empty] | 1876 | 3 | 20 | 4 | 4 | 39.9 | 40
[25 empty] | 1877 | 3 | 20 | 4 | 5 | 41 | 41
[25 empty] | 1878 | 3 | 20 | 4 | 6 | 42.1 | 42
[25 empty] | 1879 | 3 | 20 | 4 | 7 | 42.1 | 42
[25 empty] | 1880 | 3 | 20 | 4 | 8 | 45 | 45
[25 empty] | 1881 | 3 | 20 | 4 | 9 | 46.9 | 47
[25 empty] | 1882 | 3 | 20 | 4 | 10 | 50 | 50
[25 empty] | 1883 | 3 | 20 | 4 | 11 | 50 | 50
[25 empty] | 1884 | 3 | 20 | 4 | 12 | 51.1 | 51
[25 empty] | 1885 | 3 | 20 | 4 | 13 | 52 | 52
[25 empty] | 1886 | 3 | 20 | 4 | 14 | 52 | 52
[25 empty] | 1887 | 3 | 20 | 4 | 15 | 52 | 52
[25 empty] | 1888 | 3 | 20 | 4 | 16 | 53.1 | 53
[25 empty] | 1889 | 3 | 20 | 4 | 17 | 51.1 | 51
[25 empty] | 1890 | 3 | 20 | 4 | 18 | 50 | 50
[25 empty] | 1891 | 3 | 20 | 4 | 19 | 48.9 | 49
[25 empty] | 1892 | 3 | 20 | 4 | 20 | 48.9 | 49
[25 empty] | 1893 | 3 | 20 | 4 | 21 | 48.9 | 49
[25 empty] | 1894 | 3 | 20 | 4 | 22 | 48.9 | 49
[25 empty] | 1895 | 3 | 20 | 4 | 23 | 50 | 50
[25 empty] | 1896 | 3 | 21 | 5 | 0 | 50 | 50
[25 empty] | 1897 | 3 | 21 | 5 | 1 | 48.9 | 49
[25 empty] | 1898 | 3 | 21 | 5 | 2 | 48.9 | 49
[25 empty] | 1899 | 3 | 21 | 5 | 3 | 48.9 | 49
[25 empty] | 1900 | 3 | 21 | 5 | 4 | 48 | 48
[25 empty] | 1901 | 3 | 21 | 5 | 5 | 48.9 | 49
[25 empty] | 1902 | 3 | 21 | 5 | 6 | 48.9 | 49
[25 empty] | 1903 | 3 | 21 | 5 | 7 | 48.9 | 49
[25 empty] | 1904 | 3 | 21 | 5 | 8 | 51.1 | 51
[25 empty] | 1905 | 3 | 21 | 5 | 9 | 50 | 50
[25 empty] | 1906 | 3 | 21 | 5 | 10 | 50 | 50
[25 empty] | 1907 | 3 | 21 | 5 | 11 | 50 | 50
[25 empty] | 1908 | 3 | 21 | 5 | 12 | 51.1 | 51
[25 empty] | 1909 | 3 | 21 | 5 | 13 | 52 | 52
[25 empty] | 1910 | 3 | 21 | 5 | 14 | 55.9 | 56
[25 empty] | 1911 | 3 | 21 | 5 | 15 | 60.1 | 60
[25 empty] | 1912 | 3 | 21 | 5 | 16 | 57.9 | 58
[25 empty] | 1913 | 3 | 21 | 5 | 17 | 57.9 | 58
[25 empty] | 1914 | 3 | 21 | 5 | 18 | 57.9 | 58
[25 empty] | 1915 | 3 | 21 | 5 | 19 | 57 | 57
[25 empty] | 1916 | 3 | 21 | 5 | 20 | 55 | 55
[25 empty] | 1917 | 3 | 21 | 5 | 21 | 53.1 | 53
[25 empty] | 1918 | 3 | 21 | 5 | 22 | 51.1 | 51
[25 empty] | 1919 | 3 | 21 | 5 | 23 | 50 | 50
[25 empty] | 1920 | 3 | 22 | 6 | 0 | 50 | 50
[25 empty] | 1921 | 3 | 22 | 6 | 1 | 50 | 50
[25 empty] | 1922 | 3 | 22 | 6 | 2 | 48.9 | 49
[25 empty] | 1923 | 3 | 22 | 6 | 3 | 48 | 48
[25 empty] | 1924 | 3 | 22 | 6 | 4 | 48 | 48
[25 empty] | 1925 | 3 | 22 | 6 | 5 | 46.9 | 47
[25 empty] | 1926 | 3 | 22 | 6 | 6 | 46.9 | 47
[25 empty] | 1927 | 3 | 22 | 6 | 7 | 48 | 48
[25 empty] | 1928 | 3 | 22 | 6 | 8 | 48 | 48
[25 empty] | 1929 | 3 | 22 | 6 | 9 | 48 | 48
[25 empty] | 1930 | 3 | 22 | 6 | 10 | 48 | 48
[25 empty] | 1931 | 3 | 22 | 6 | 11 | 48 | 48
[25 empty] | 1932 | 3 | 22 | 6 | 12 | 48 | 48
[25 empty] | 1933 | 3 | 22 | 6 | 13 | 48 | 48
[25 empty] | 1934 | 3 | 22 | 6 | 14 | 48 | 48
[25 empty] | 1935 | 3 | 22 | 6 | 15 | 50 | 50
[25 empty] | 1936 | 3 | 22 | 6 | 16 | 50 | 50
[25 empty] | 1937 | 3 | 22 | 6 | 17 | 46.9 | 47
[25 empty] | 1938 | 3 | 22 | 6 | 18 | 46.9 | 47
[25 empty] | 1939 | 3 | 22 | 6 | 19 | 46 | 46
[25 empty] | 1940 | 3 | 22 | 6 | 20 | 46 | 46
[25 empty] | 1941 | 3 | 22 | 6 | 21 | 46 | 46
[25 empty] | 1942 | 3 | 22 | 6 | 22 | 45 | 45
[25 empty] | 1943 | 3 | 22 | 6 | 23 | 44.1 | 44
[25 empty] | 1944 | 3 | 23 | 7 | 0 | 44.1 | 44
[25 empty] | 1945 | 3 | 23 | 7 | 1 | 44.1 | 44
[25 empty] | 1946 | 3 | 23 | 7 | 2 | 45 | 45
[25 empty] | 1947 | 3 | 23 | 7 | 3 | 44.1 | 44
[25 empty] | 1948 | 3 | 23 | 7 | 4 | 44.1 | 44
[25 empty] | 1949 | 3 | 23 | 7 | 5 | 44.1 | 44
[25 empty] | 1950 | 3 | 23 | 7 | 6 | 44.1 | 44
[25 empty] | 1951 | 3 | 23 | 7 | 7 | 44.1 | 44
[25 empty] | 1952 | 3 | 23 | 7 | 8 | 45 | 45
[25 empty] | 1953 | 3 | 23 | 7 | 9 | 46.9 | 47
[25 empty] | 1954 | 3 | 23 | 7 | 10 | 48 | 48
[25 empty] | 1955 | 3 | 23 | 7 | 11 | 48 | 48
[25 empty] | 1956 | 3 | 23 | 7 | 12 | 48 | 48
[25 empty] | 1957 | 3 | 23 | 7 | 13 | 48 | 48
[25 empty] | 1958 | 3 | 23 | 7 | 14 | 48.9 | 49
[25 empty] | 1959 | 3 | 23 | 7 | 15 | 48.9 | 49
[25 empty] | 1960 | 3 | 23 | 7 | 16 | 48.9 | 49
[25 empty] | 1961 | 3 | 23 | 7 | 17 | 48 | 48
[25 empty] | 1962 | 3 | 23 | 7 | 18 | 48 | 48
[25 empty] | 1963 | 3 | 23 | 7 | 19 | 46.9 | 47
[25 empty] | 1964 | 3 | 23 | 7 | 20 | 46.9 | 47
[25 empty] | 1965 | 3 | 23 | 7 | 21 | 46 | 46
[25 empty] | 1966 | 3 | 23 | 7 | 22 | 45 | 45
[25 empty] | 1967 | 3 | 23 | 7 | 23 | 45 | 45
[25 empty] | 1968 | 3 | 24 | 1 | 0 | 45 | 45
[25 empty] | 1969 | 3 | 24 | 1 | 1 | 44.1 | 44
[25 empty] | 1970 | 3 | 24 | 1 | 2 | 44.1 | 44
[25 empty] | 1971 | 3 | 24 | 1 | 3 | 42.1 | 42
[25 empty] | 1972 | 3 | 24 | 1 | 4 | 41 | 41
[25 empty] | 1973 | 3 | 24 | 1 | 5 | 41 | 41
[25 empty] | 1974 | 3 | 24 | 1 | 6 | 39.9 | 40
[25 empty] | 1975 | 3 | 24 | 1 | 7 | 39.9 | 40
[25 empty] | 1976 | 3 | 24 | 1 | 8 | 42.1 | 42
[25 empty] | 1977 | 3 | 24 | 1 | 9 | 43 | 43
[25 empty] | 1978 | 3 | 24 | 1 | 10 | 45 | 45
[25 empty] | 1979 | 3 | 24 | 1 | 11 | 44.1 | 44
[25 empty] | 1980 | 3 | 24 | 1 | 12 | 44.1 | 44
[25 empty] | 1981 | 3 | 24 | 1 | 13 | 42.1 | 42
[25 empty] | 1982 | 3 | 24 | 1 | 14 | 43 | 43
[25 empty] | 1983 | 3 | 24 | 1 | 15 | 44.1 | 44
[25 empty] | 1984 | 3 | 24 | 1 | 16 | 44.1 | 44
[25 empty] | 1985 | 3 | 24 | 1 | 17 | 44.1 | 44
[25 empty] | 1986 | 3 | 24 | 1 | 18 | 43 | 43
[25 empty] | 1987 | 3 | 24 | 1 | 19 | 42.1 | 42
[25 empty] | 1988 | 3 | 24 | 1 | 20 | 41 | 41
[25 empty] | 1989 | 3 | 24 | 1 | 21 | 39.9 | 40
[25 empty] | 1990 | 3 | 24 | 1 | 22 | 39.9 | 40
[25 empty] | 1991 | 3 | 24 | 1 | 23 | 37.9 | 38
[25 empty] | 1992 | 3 | 25 | 2 | 0 | 37 | 37
[25 empty] | 1993 | 3 | 25 | 2 | 1 | 37 | 37
[25 empty] | 1994 | 3 | 25 | 2 | 2 | 36 | 36
[25 empty] | 1995 | 3 | 25 | 2 | 3 | 36 | 36
[25 empty] | 1996 | 3 | 25 | 2 | 4 | 35.1 | 35
[25 empty] | 1997 | 3 | 25 | 2 | 5 | 35.1 | 35
[25 empty] | 1998 | 3 | 25 | 2 | 6 | 35.1 | 35
[25 empty] | 1999 | 3 | 25 | 2 | 7 | 35.1 | 35
[25 empty] | 2000 | 3 | 25 | 2 | 8 | 37 | 37
[25 empty] | 2001 | 3 | 25 | 2 | 9 | 34 | 34
[25 empty] | 2002 | 3 | 25 | 2 | 10 | 41 | 41
[25 empty] | 2003 | 3 | 25 | 2 | 11 | 44.1 | 44
[25 empty] | 2004 | 3 | 25 | 2 | 12 | 46 | 46
[25 empty] | 2005 | 3 | 25 | 2 | 13 | 48.9 | 49
[25 empty] | 2006 | 3 | 25 | 2 | 14 | 51.1 | 51
[25 empty] | 2007 | 3 | 25 | 2 | 15 | 52 | 52
[25 empty] | 2008 | 3 | 25 | 2 | 16 | 53.1 | 53
[25 empty] | 2009 | 3 | 25 | 2 | 17 | 54 | 54
[25 empty] | 2010 | 3 | 25 | 2 | 18 | 52 | 52
[25 empty] | 2011 | 3 | 25 | 2 | 19 | 50 | 50
[25 empty] | 2012 | 3 | 25 | 2 | 20 | 48.9 | 49
[25 empty] | 2013 | 3 | 25 | 2 | 21 | 46.9 | 47
[25 empty] | 2014 | 3 | 25 | 2 | 22 | 46.9 | 47
[25 empty] | 2015 | 3 | 25 | 2 | 23 | 46 | 46
[25 empty] | 2016 | 3 | 26 | 3 | 0 | 45 | 45
[25 empty] | 2017 | 3 | 26 | 3 | 1 | 45 | 45
[25 empty] | 2018 | 3 | 26 | 3 | 2 | 44.1 | 44
[25 empty] | 2019 | 3 | 26 | 3 | 3 | 44.1 | 44
[25 empty] | 2020 | 3 | 26 | 3 | 4 | 43 | 43
[25 empty] | 2021 | 3 | 26 | 3 | 5 | 42.1 | 42
[25 empty] | 2022 | 3 | 26 | 3 | 6 | 41 | 41
[25 empty] | 2023 | 3 | 26 | 3 | 7 | 43 | 43
[25 empty] | 2024 | 3 | 26 | 3 | 8 | 44.1 | 44
[25 empty] | 2025 | 3 | 26 | 3 | 9 | 46 | 46
[25 empty] | 2026 | 3 | 26 | 3 | 10 | 46.9 | 47
[25 empty] | 2027 | 3 | 26 | 3 | 11 | 50 | 50
[25 empty] | 2028 | 3 | 26 | 3 | 12 | 51.1 | 51
[25 empty] | 2029 | 3 | 26 | 3 | 13 | 54 | 54
[25 empty] | 2030 | 3 | 26 | 3 | 14 | 57 | 57
[25 empty] | 2031 | 3 | 26 | 3 | 15 | 59 | 59
[25 empty] | 2032 | 3 | 26 | 3 | 16 | 59 | 59
[25 empty] | 2033 | 3 | 26 | 3 | 17 | 59 | 59
[25 empty] | 2034 | 3 | 26 | 3 | 18 | 57.9 | 58
[25 empty] | 2035 | 3 | 26 | 3 | 19 | 55.9 | 56
[25 empty] | 2036 | 3 | 26 | 3 | 20 | 54 | 54
[25 empty] | 2037 | 3 | 26 | 3 | 21 | 53.1 | 53
[25 empty] | 2038 | 3 | 26 | 3 | 22 | 51.1 | 51
[25 empty] | 2039 | 3 | 26 | 3 | 23 | 50 | 50
[25 empty] | 2040 | 3 | 27 | 4 | 0 | 48 | 48
[25 empty] | 2041 | 3 | 27 | 4 | 1 | 46 | 46
[25 empty] | 2042 | 3 | 27 | 4 | 2 | 45 | 45
[25 empty] | 2043 | 3 | 27 | 4 | 3 | 44.1 | 44
[25 empty] | 2044 | 3 | 27 | 4 | 4 | 43 | 43
[25 empty] | 2045 | 3 | 27 | 4 | 5 | 42.1 | 42
[25 empty] | 2046 | 3 | 27 | 4 | 6 | 41 | 41
[25 empty] | 2047 | 3 | 27 | 4 | 7 | 43 | 43
[25 empty] | 2048 | 3 | 27 | 4 | 8 | 44.1 | 44
[25 empty] | 2049 | 3 | 27 | 4 | 9 | 46 | 46
[25 empty] | 2050 | 3 | 27 | 4 | 10 | 46 | 46
[25 empty] | 2051 | 3 | 27 | 4 | 11 | 46.9 | 47
[25 empty] | 2052 | 3 | 27 | 4 | 12 | 48.9 | 49
[25 empty] | 2053 | 3 | 27 | 4 | 13 | 50 | 50
[25 empty] | 2054 | 3 | 27 | 4 | 14 | 52 | 52
[25 empty] | 2055 | 3 | 27 | 4 | 15 | 53.1 | 53
[25 empty] | 2056 | 3 | 27 | 4 | 16 | 53.1 | 53
[25 empty] | 2057 | 3 | 27 | 4 | 17 | 53.1 | 53
[25 empty] | 2058 | 3 | 27 | 4 | 18 | 52 | 52
[25 empty] | 2059 | 3 | 27 | 4 | 19 | 50 | 50
[25 empty] | 2060 | 3 | 27 | 4 | 20 | 50 | 50
[25 empty] | 2061 | 3 | 27 | 4 | 21 | 48.9 | 49
[25 empty] | 2062 | 3 | 27 | 4 | 22 | 48.9 | 49
[25 empty] | 2063 | 3 | 27 | 4 | 23 | 48 | 48
[25 empty] | 2064 | 3 | 28 | 5 | 0 | 46.9 | 47
[25 empty] | 2065 | 3 | 28 | 5 | 1 | 46 | 46
[25 empty] | 2066 | 3 | 28 | 5 | 2 | 44.1 | 44
[25 empty] | 2067 | 3 | 28 | 5 | 3 | 43 | 43
[25 empty] | 2068 | 3 | 28 | 5 | 4 | 42.1 | 42
[25 empty] | 2069 | 3 | 28 | 5 | 5 | 41 | 41
[25 empty] | 2070 | 3 | 28 | 5 | 6 | 39.9 | 40
[25 empty] | 2071 | 3 | 28 | 5 | 7 | 39 | 39
[25 empty] | 2072 | 3 | 28 | 5 | 8 | 43 | 43
[25 empty] | 2073 | 3 | 28 | 5 | 9 | 43 | 43
[25 empty] | 2074 | 3 | 28 | 5 | 10 | 45 | 45
[25 empty] | 2075 | 3 | 28 | 5 | 11 | 46.9 | 47
[25 empty] | 2076 | 3 | 28 | 5 | 12 | 48 | 48
[25 empty] | 2077 | 3 | 28 | 5 | 13 | 50 | 50
[25 empty] | 2078 | 3 | 28 | 5 | 14 | 52 | 52
[25 empty] | 2079 | 3 | 28 | 5 | 15 | 52 | 52
[25 empty] | 2080 | 3 | 28 | 5 | 16 | 52 | 52
[25 empty] | 2081 | 3 | 28 | 5 | 17 | 52 | 52
[25 empty] | 2082 | 3 | 28 | 5 | 18 | 51.1 | 51
[25 empty] | 2083 | 3 | 28 | 5 | 19 | 50 | 50
[25 empty] | 2084 | 3 | 28 | 5 | 20 | 50 | 50
[25 empty] | 2085 | 3 | 28 | 5 | 21 | 46.9 | 47
[25 empty] | 2086 | 3 | 28 | 5 | 22 | 46 | 46
[25 empty] | 2087 | 3 | 28 | 5 | 23 | 46.9 | 47
[25 empty] | 2088 | 3 | 29 | 6 | 0 | 46.9 | 47
[25 empty] | 2089 | 3 | 29 | 6 | 1 | 46 | 46
[25 empty] | 2090 | 3 | 29 | 6 | 2 | 45 | 45
[25 empty] | 2091 | 3 | 29 | 6 | 3 | 43 | 43
[25 empty] | 2092 | 3 | 29 | 6 | 4 | 44.1 | 44
[25 empty] | 2093 | 3 | 29 | 6 | 5 | 42.1 | 42
[25 empty] | 2094 | 3 | 29 | 6 | 6 | 41 | 41
[25 empty] | 2095 | 3 | 29 | 6 | 7 | 44.1 | 44
[25 empty] | 2096 | 3 | 29 | 6 | 8 | 46 | 46
[25 empty] | 2097 | 3 | 29 | 6 | 9 | 46.9 | 47
[25 empty] | 2098 | 3 | 29 | 6 | 10 | 48.9 | 49
[25 empty] | 2099 | 3 | 29 | 6 | 11 | 51.1 | 51
[25 empty] | 2100 | 3 | 29 | 6 | 12 | 52 | 52
[25 empty] | 2101 | 3 | 29 | 6 | 13 | 54 | 54
[25 empty] | 2102 | 3 | 29 | 6 | 14 | 57.9 | 58
[25 empty] | 2103 | 3 | 29 | 6 | 15 | 55 | 55
[25 empty] | 2104 | 3 | 29 | 6 | 16 | 54 | 54
[25 empty] | 2105 | 3 | 29 | 6 | 17 | 51.1 | 51
[25 empty] | 2106 | 3 | 29 | 6 | 18 | 48.9 | 49
[25 empty] | 2107 | 3 | 29 | 6 | 19 | 46 | 46
[25 empty] | 2108 | 3 | 29 | 6 | 20 | 46 | 46
[25 empty] | 2109 | 3 | 29 | 6 | 21 | 45 | 45
[25 empty] | 2110 | 3 | 29 | 6 | 22 | 45 | 45
[25 empty] | 2111 | 3 | 29 | 6 | 23 | 44.1 | 44
[25 empty] | 2112 | 3 | 30 | 7 | 0 | 44.1 | 44
[25 empty] | 2113 | 3 | 30 | 7 | 1 | 44.1 | 44
[25 empty] | 2114 | 3 | 30 | 7 | 2 | 45 | 45
[25 empty] | 2115 | 3 | 30 | 7 | 3 | 45 | 45
[25 empty] | 2116 | 3 | 30 | 7 | 4 | 46 | 46
[25 empty] | 2117 | 3 | 30 | 7 | 5 | 46 | 46
[25 empty] | 2118 | 3 | 30 | 7 | 6 | 46 | 46
[25 empty] | 2119 | 3 | 30 | 7 | 7 | 46.9 | 47
[25 empty] | 2120 | 3 | 30 | 7 | 8 | 48 | 48
[25 empty] | 2121 | 3 | 30 | 7 | 9 | 48 | 48
[25 empty] | 2122 | 3 | 30 | 7 | 10 | 48 | 48
[25 empty] | 2123 | 3 | 30 | 7 | 11 | 48 | 48
[25 empty] | 2124 | 3 | 30 | 7 | 12 | 48.9 | 49
[25 empty] | 2125 | 3 | 30 | 7 | 13 | 48.9 | 49
[25 empty] | 2126 | 3 | 30 | 7 | 14 | 50 | 50
[25 empty] | 2127 | 3 | 30 | 7 | 15 | 48.9 | 49
[25 empty] | 2128 | 3 | 30 | 7 | 16 | 48.9 | 49
[25 empty] | 2129 | 3 | 30 | 7 | 17 | 48.9 | 49
[25 empty] | 2130 | 3 | 30 | 7 | 18 | 48 | 48
[25 empty] | 2131 | 3 | 30 | 7 | 19 | 48 | 48
[25 empty] | 2132 | 3 | 30 | 7 | 20 | 48 | 48
[25 empty] | 2133 | 3 | 30 | 7 | 21 | 48.9 | 49
[25 empty] | 2134 | 3 | 30 | 7 | 22 | 48.9 | 49
[25 empty] | 2135 | 3 | 30 | 7 | 23 | 48.9 | 49
[25 empty] | 2136 | 3 | 31 | 1 | 0 | 48.9 | 49
[25 empty] | 2137 | 3 | 31 | 1 | 1 | 48 | 48
[25 empty] | 2138 | 3 | 31 | 1 | 2 | 46.9 | 47
[25 empty] | 2139 | 3 | 31 | 1 | 3 | 46 | 46
[25 empty] | 2140 | 3 | 31 | 1 | 4 | 45 | 45
[25 empty] | 2141 | 3 | 31 | 1 | 5 | 44.1 | 44
[25 empty] | 2142 | 3 | 31 | 1 | 6 | 44.1 | 44
[25 empty] | 2143 | 3 | 31 | 1 | 7 | 44.1 | 44
[25 empty] | 2144 | 3 | 31 | 1 | 8 | 45 | 45
[25 empty] | 2145 | 3 | 31 | 1 | 9 | 46 | 46
[25 empty] | 2146 | 3 | 31 | 1 | 10 | 46.9 | 47
[25 empty] | 2147 | 3 | 31 | 1 | 11 | 48 | 48
[25 empty] | 2148 | 3 | 31 | 1 | 12 | 50 | 50
[25 empty] | 2149 | 3 | 31 | 1 | 13 | 48.9 | 49
[25 empty] | 2150 | 3 | 31 | 1 | 14 | 50 | 50
[25 empty] | 2151 | 3 | 31 | 1 | 15 | 51.1 | 51
[25 empty] | 2152 | 3 | 31 | 1 | 16 | 51.1 | 51
[25 empty] | 2153 | 3 | 31 | 1 | 17 | 50 | 50
[25 empty] | 2154 | 3 | 31 | 1 | 18 | 50 | 50
[25 empty] | 2155 | 3 | 31 | 1 | 19 | 50 | 50
[25 empty] | 2156 | 3 | 31 | 1 | 20 | 48.9 | 49
[25 empty] | 2157 | 3 | 31 | 1 | 21 | 46.9 | 47
[25 empty] | 2158 | 3 | 31 | 1 | 22 | 46.8 | 47
[25 empty] | 2159 | 3 | 31 | 1 | 23 | 46.8 | 47
[25 empty] | 2160 | 4 | 1 | 2 | 0 | 46.6 | 47
[25 empty] | 2161 | 4 | 1 | 2 | 1 | 46.4 | 46
[25 empty] | 2162 | 4 | 1 | 2 | 2 | 46.2 | 46
[25 empty] | 2163 | 4 | 1 | 2 | 3 | 46.2 | 46
[25 empty] | 2164 | 4 | 1 | 2 | 4 | 46 | 46
[25 empty] | 2165 | 4 | 1 | 2 | 5 | 44.1 | 44
[25 empty] | 2166 | 4 | 1 | 2 | 6 | 46 | 46
[25 empty] | 2167 | 4 | 1 | 2 | 7 | 44.1 | 44
[25 empty] | 2168 | 4 | 1 | 2 | 8 | 46.9 | 47
[25 empty] | 2169 | 4 | 1 | 2 | 9 | 48.9 | 49
[25 empty] | 2170 | 4 | 1 | 2 | 10 | 51.1 | 51
[25 empty] | 2171 | 4 | 1 | 2 | 11 | 53.1 | 53
[25 empty] | 2172 | 4 | 1 | 2 | 12 | 55 | 55
[25 empty] | 2173 | 4 | 1 | 2 | 13 | 57.9 | 58
[25 empty] | 2174 | 4 | 1 | 2 | 14 | 57 | 57
[25 empty] | 2175 | 4 | 1 | 2 | 15 | 57.9 | 58
[25 empty] | 2176 | 4 | 1 | 2 | 16 | 57.9 | 58
[25 empty] | 2177 | 4 | 1 | 2 | 17 | 57.9 | 58
[25 empty] | 2178 | 4 | 1 | 2 | 18 | 55.9 | 56
[25 empty] | 2179 | 4 | 1 | 2 | 19 | 55 | 55
[25 empty] | 2180 | 4 | 1 | 2 | 20 | 54 | 54
[25 empty] | 2181 | 4 | 1 | 2 | 21 | 55.9 | 56
[25 empty] | 2182 | 4 | 1 | 2 | 22 | 55.9 | 56
[25 empty] | 2183 | 4 | 1 | 2 | 23 | 55 | 55
[25 empty] | 2184 | 4 | 2 | 3 | 0 | 54 | 54
[25 empty] | 2185 | 4 | 2 | 3 | 1 | 52 | 52
[25 empty] | 2186 | 4 | 2 | 3 | 2 | 51.1 | 51
[25 empty] | 2187 | 4 | 2 | 3 | 3 | 48.9 | 49
[25 empty] | 2188 | 4 | 2 | 3 | 4 | 45 | 45
[25 empty] | 2189 | 4 | 2 | 3 | 5 | 44.1 | 44
[25 empty] | 2190 | 4 | 2 | 3 | 6 | 43 | 43
[25 empty] | 2191 | 4 | 2 | 3 | 7 | 43 | 43
[25 empty] | 2192 | 4 | 2 | 3 | 8 | 45 | 45
[25 empty] | 2193 | 4 | 2 | 3 | 9 | 44.1 | 44
[25 empty] | 2194 | 4 | 2 | 3 | 10 | 44.1 | 44
[25 empty] | 2195 | 4 | 2 | 3 | 11 | 45 | 45
[25 empty] | 2196 | 4 | 2 | 3 | 12 | 45 | 45
[25 empty] | 2197 | 4 | 2 | 3 | 13 | 48.9 | 49
[25 empty] | 2198 | 4 | 2 | 3 | 14 | 48 | 48
[25 empty] | 2199 | 4 | 2 | 3 | 15 | 45 | 45
[25 empty] | 2200 | 4 | 2 | 3 | 16 | 45 | 45
[25 empty] | 2201 | 4 | 2 | 3 | 17 | 44.1 | 44
[25 empty] | 2202 | 4 | 2 | 3 | 18 | 43 | 43
[25 empty] | 2203 | 4 | 2 | 3 | 19 | 43 | 43
[25 empty] | 2204 | 4 | 2 | 3 | 20 | 44.1 | 44
[25 empty] | 2205 | 4 | 2 | 3 | 21 | 43 | 43
[25 empty] | 2206 | 4 | 2 | 3 | 22 | 43 | 43
[25 empty] | 2207 | 4 | 2 | 3 | 23 | 42.1 | 42
[25 empty] | 2208 | 4 | 3 | 4 | 0 | 39.9 | 40
[25 empty] | 2209 | 4 | 3 | 4 | 1 | 39.9 | 40
[25 empty] | 2210 | 4 | 3 | 4 | 2 | 40.5 | 41
[25 empty] | 2211 | 4 | 3 | 4 | 3 | 41 | 41
[25 empty] | 2212 | 4 | 3 | 4 | 4 | 46 | 46
[25 empty] | 2213 | 4 | 3 | 4 | 5 | 46 | 46
[25 empty] | 2214 | 4 | 3 | 4 | 6 | 48 | 48
[25 empty] | 2215 | 4 | 3 | 4 | 7 | 48.9 | 49
[25 empty] | 2216 | 4 | 3 | 4 | 8 | 51.1 | 51
[25 empty] | 2217 | 4 | 3 | 4 | 9 | 54 | 54
[25 empty] | 2218 | 4 | 3 | 4 | 10 | 57.9 | 58
[25 empty] | 2219 | 4 | 3 | 4 | 11 | 55 | 55
[25 empty] | 2220 | 4 | 3 | 4 | 12 | 55.9 | 56
[25 empty] | 2221 | 4 | 3 | 4 | 13 | 55.9 | 56
[25 empty] | 2222 | 4 | 3 | 4 | 14 | 55 | 55
[25 empty] | 2223 | 4 | 3 | 4 | 15 | 55 | 55
[25 empty] | 2224 | 4 | 3 | 4 | 16 | 54 | 54
[25 empty] | 2225 | 4 | 3 | 4 | 17 | 52 | 52
[25 empty] | 2226 | 4 | 3 | 4 | 18 | 52 | 52
[25 empty] | 2227 | 4 | 3 | 4 | 19 | 52 | 52
[25 empty] | 2228 | 4 | 3 | 4 | 20 | 52 | 52
[25 empty] | 2229 | 4 | 3 | 4 | 21 | 51.1 | 51
[25 empty] | 2230 | 4 | 3 | 4 | 22 | 52 | 52
[25 empty] | 2231 | 4 | 3 | 4 | 23 | 51.1 | 51
[25 empty] | 2232 | 4 | 4 | 5 | 0 | 50 | 50
[25 empty] | 2233 | 4 | 4 | 5 | 1 | 50 | 50
[25 empty] | 2234 | 4 | 4 | 5 | 2 | 48 | 48
[25 empty] | 2235 | 4 | 4 | 5 | 3 | 46.9 | 47
[25 empty] | 2236 | 4 | 4 | 5 | 4 | 45 | 45
[25 empty] | 2237 | 4 | 4 | 5 | 5 | 42.1 | 42
[25 empty] | 2238 | 4 | 4 | 5 | 6 | 39.9 | 40
[25 empty] | 2239 | 4 | 4 | 5 | 7 | 39 | 39
[25 empty] | 2240 | 4 | 4 | 5 | 8 | 39.9 | 40
[25 empty] | 2241 | 4 | 4 | 5 | 9 | 42.1 | 42
[25 empty] | 2242 | 4 | 4 | 5 | 10 | 45 | 45
[25 empty] | 2243 | 4 | 4 | 5 | 11 | 46 | 46
[25 empty] | 2244 | 4 | 4 | 5 | 12 | 48.9 | 49
[25 empty] | 2245 | 4 | 4 | 5 | 13 | 51.1 | 51
[25 empty] | 2246 | 4 | 4 | 5 | 14 | 53.1 | 53
[25 empty] | 2247 | 4 | 4 | 5 | 15 | 55.9 | 56
[25 empty] | 2248 | 4 | 4 | 5 | 16 | 59 | 59
[25 empty] | 2249 | 4 | 4 | 5 | 17 | 59 | 59
[25 empty] | 2250 | 4 | 4 | 5 | 18 | 57 | 57
[25 empty] | 2251 | 4 | 4 | 5 | 19 | 55 | 55
[25 empty] | 2252 | 4 | 4 | 5 | 20 | 55 | 55
[25 empty] | 2253 | 4 | 4 | 5 | 21 | 54 | 54
[25 empty] | 2254 | 4 | 4 | 5 | 22 | 50 | 50
[25 empty] | 2255 | 4 | 4 | 5 | 23 | 48.9 | 49
[25 empty] | 2256 | 4 | 5 | 6 | 0 | 48 | 48
[25 empty] | 2257 | 4 | 5 | 6 | 1 | 46.9 | 47
[25 empty] | 2258 | 4 | 5 | 6 | 2 | 46 | 46
[25 empty] | 2259 | 4 | 5 | 6 | 3 | 45 | 45
[25 empty] | 2260 | 4 | 5 | 6 | 4 | 44.1 | 44
[25 empty] | 2261 | 4 | 5 | 6 | 5 | 43 | 43
[25 empty] | 2262 | 4 | 5 | 6 | 6 | 44.1 | 44
[25 empty] | 2263 | 4 | 5 | 6 | 7 | 46 | 46
[25 empty] | 2264 | 4 | 5 | 6 | 8 | 52 | 52
[25 empty] | 2265 | 4 | 5 | 6 | 9 | 55 | 55
[25 empty] | 2266 | 4 | 5 | 6 | 10 | 57 | 57
[25 empty] | 2267 | 4 | 5 | 6 | 11 | 57 | 57
[25 empty] | 2268 | 4 | 5 | 6 | 12 | 57 | 57
[25 empty] | 2269 | 4 | 5 | 6 | 13 | 55.9 | 56
[25 empty] | 2270 | 4 | 5 | 6 | 14 | 55.9 | 56
[25 empty] | 2271 | 4 | 5 | 6 | 15 | 55 | 55
[25 empty] | 2272 | 4 | 5 | 6 | 16 | 54 | 54
[25 empty] | 2273 | 4 | 5 | 6 | 17 | 53.1 | 53
[25 empty] | 2274 | 4 | 5 | 6 | 18 | 51.1 | 51
[25 empty] | 2275 | 4 | 5 | 6 | 19 | 48.9 | 49
[25 empty] | 2276 | 4 | 5 | 6 | 20 | 48.9 | 49
[25 empty] | 2277 | 4 | 5 | 6 | 21 | 48.9 | 49
[25 empty] | 2278 | 4 | 5 | 6 | 22 | 50 | 50
[25 empty] | 2279 | 4 | 5 | 6 | 23 | 48.9 | 49
[25 empty] | 2280 | 4 | 6 | 7 | 0 | 48 | 48
[25 empty] | 2281 | 4 | 6 | 7 | 1 | 46.9 | 47
[25 empty] | 2282 | 4 | 6 | 7 | 2 | 46 | 46
[25 empty] | 2283 | 4 | 6 | 7 | 3 | 45 | 45
[25 empty] | 2284 | 4 | 6 | 7 | 4 | 45 | 45
[25 empty] | 2285 | 4 | 6 | 7 | 5 | 44.1 | 44
[25 empty] | 2286 | 4 | 6 | 7 | 6 | 45 | 45
[25 empty] | 2287 | 4 | 6 | 7 | 7 | 44.1 | 44
[25 empty] | 2288 | 4 | 6 | 7 | 8 | 45 | 45
[25 empty] | 2289 | 4 | 6 | 7 | 9 | 45 | 45
[25 empty] | 2290 | 4 | 6 | 7 | 10 | 45 | 45
[25 empty] | 2291 | 4 | 6 | 7 | 11 | 50 | 50
[25 empty] | 2292 | 4 | 6 | 7 | 12 | 52 | 52
[25 empty] | 2293 | 4 | 6 | 7 | 13 | 51.1 | 51
[25 empty] | 2294 | 4 | 6 | 7 | 14 | 51.1 | 51
[25 empty] | 2295 | 4 | 6 | 7 | 15 | 52 | 52
[25 empty] | 2296 | 4 | 6 | 7 | 16 | 53.1 | 53
[25 empty] | 2297 | 4 | 6 | 7 | 17 | 54 | 54
[25 empty] | 2298 | 4 | 6 | 7 | 18 | 57 | 57
[25 empty] | 2299 | 4 | 6 | 7 | 19 | 55 | 55
[25 empty] | 2300 | 4 | 6 | 7 | 20 | 54 | 54
[25 empty] | 2301 | 4 | 6 | 7 | 21 | 53.1 | 53
[25 empty] | 2302 | 4 | 6 | 7 | 22 | 52 | 52
[25 empty] | 2303 | 4 | 6 | 7 | 23 | 52 | 52
[25 empty] | 2304 | 4 | 7 | 1 | 0 | 53.1 | 53
[25 empty] | 2305 | 4 | 7 | 1 | 1 | 54 | 54
[25 empty] | 2306 | 4 | 7 | 1 | 2 | 53.1 | 53
[25 empty] | 2307 | 4 | 7 | 1 | 3 | 52 | 52
[25 empty] | 2308 | 4 | 7 | 1 | 4 | 55 | 55
[25 empty] | 2309 | 4 | 7 | 1 | 5 | 55.9 | 56
[25 empty] | 2310 | 4 | 7 | 1 | 6 | 57 | 57
[25 empty] | 2311 | 4 | 7 | 1 | 7 | 54 | 54
[25 empty] | 2312 | 4 | 7 | 1 | 8 | 55 | 55
[25 empty] | 2313 | 4 | 7 | 1 | 9 | 57.9 | 58
[25 empty] | 2314 | 4 | 7 | 1 | 10 | 52 | 52
[25 empty] | 2315 | 4 | 7 | 1 | 11 | 50 | 50
[25 empty] | 2316 | 4 | 7 | 1 | 12 | 50 | 50
[25 empty] | 2317 | 4 | 7 | 1 | 13 | 48.9 | 49
[25 empty] | 2318 | 4 | 7 | 1 | 14 | 48 | 48
[25 empty] | 2319 | 4 | 7 | 1 | 15 | 46.9 | 47
[25 empty] | 2320 | 4 | 7 | 1 | 16 | 48.9 | 49
[25 empty] | 2321 | 4 | 7 | 1 | 17 | 46.9 | 47
[25 empty] | 2322 | 4 | 7 | 1 | 18 | 46 | 46
[25 empty] | 2323 | 4 | 7 | 1 | 19 | 44.1 | 44
[25 empty] | 2324 | 4 | 7 | 1 | 20 | 44.1 | 44
[25 empty] | 2325 | 4 | 7 | 1 | 21 | 43 | 43
[25 empty] | 2326 | 4 | 7 | 1 | 22 | 41 | 41
[25 empty] | 2327 | 4 | 7 | 1 | 23 | 39.9 | 40
[25 empty] | 2328 | 4 | 8 | 2 | 0 | 39 | 39
[25 empty] | 2329 | 4 | 8 | 2 | 1 | 39 | 39
[25 empty] | 2330 | 4 | 8 | 2 | 2 | 39 | 39
[25 empty] | 2331 | 4 | 8 | 2 | 3 | 37.9 | 38
[25 empty] | 2332 | 4 | 8 | 2 | 4 | 37 | 37
[25 empty] | 2333 | 4 | 8 | 2 | 5 | 36 | 36
[25 empty] | 2334 | 4 | 8 | 2 | 6 | 36 | 36
[25 empty] | 2335 | 4 | 8 | 2 | 7 | 37 | 37
[25 empty] | 2336 | 4 | 8 | 2 | 8 | 41 | 41
[25 empty] | 2337 | 4 | 8 | 2 | 9 | 45 | 45
[25 empty] | 2338 | 4 | 8 | 2 | 10 | 48 | 48
[25 empty] | 2339 | 4 | 8 | 2 | 11 | 50 | 50
[25 empty] | 2340 | 4 | 8 | 2 | 12 | 52 | 52
[25 empty] | 2341 | 4 | 8 | 2 | 13 | 54 | 54
[25 empty] | 2342 | 4 | 8 | 2 | 14 | 55 | 55
[25 empty] | 2343 | 4 | 8 | 2 | 15 | 57 | 57
[25 empty] | 2344 | 4 | 8 | 2 | 16 | 57 | 57
[25 empty] | 2345 | 4 | 8 | 2 | 17 | 57 | 57
[25 empty] | 2346 | 4 | 8 | 2 | 18 | 51.1 | 51
[25 empty] | 2347 | 4 | 8 | 2 | 19 | 48.9 | 49
[25 empty] | 2348 | 4 | 8 | 2 | 20 | 48 | 48
[25 empty] | 2349 | 4 | 8 | 2 | 21 | 46 | 46
[25 empty] | 2350 | 4 | 8 | 2 | 22 | 45 | 45
[25 empty] | 2351 | 4 | 8 | 2 | 23 | 44.1 | 44
[25 empty] | 2352 | 4 | 9 | 3 | 0 | 44.1 | 44
[25 empty] | 2353 | 4 | 9 | 3 | 1 | 43 | 43
[25 empty] | 2354 | 4 | 9 | 3 | 2 | 43 | 43
[25 empty] | 2355 | 4 | 9 | 3 | 3 | 43 | 43
[25 empty] | 2356 | 4 | 9 | 3 | 4 | 42.1 | 42
[25 empty] | 2357 | 4 | 9 | 3 | 5 | 41 | 41
[25 empty] | 2358 | 4 | 9 | 3 | 6 | 42.1 | 42
[25 empty] | 2359 | 4 | 9 | 3 | 7 | 43 | 43
[25 empty] | 2360 | 4 | 9 | 3 | 8 | 48 | 48
[25 empty] | 2361 | 4 | 9 | 3 | 9 | 52 | 52
[25 empty] | 2362 | 4 | 9 | 3 | 10 | 52 | 52
[25 empty] | 2363 | 4 | 9 | 3 | 11 | 54 | 54
[25 empty] | 2364 | 4 | 9 | 3 | 12 | 51.1 | 51
[25 empty] | 2365 | 4 | 9 | 3 | 13 | 50 | 50
[25 empty] | 2366 | 4 | 9 | 3 | 14 | 50 | 50
[25 empty] | 2367 | 4 | 9 | 3 | 15 | 52 | 52
[25 empty] | 2368 | 4 | 9 | 3 | 16 | 53.1 | 53
[25 empty] | 2369 | 4 | 9 | 3 | 17 | 53.1 | 53
[25 empty] | 2370 | 4 | 9 | 3 | 18 | 55 | 55
[25 empty] | 2371 | 4 | 9 | 3 | 19 | 53.1 | 53
[25 empty] | 2372 | 4 | 9 | 3 | 20 | 52 | 52
[25 empty] | 2373 | 4 | 9 | 3 | 21 | 51.1 | 51
[25 empty] | 2374 | 4 | 9 | 3 | 22 | 52 | 52
[25 empty] | 2375 | 4 | 9 | 3 | 23 | 51.1 | 51
[25 empty] | 2376 | 4 | 10 | 4 | 0 | 51.1 | 51
[25 empty] | 2377 | 4 | 10 | 4 | 1 | 51.1 | 51
[25 empty] | 2378 | 4 | 10 | 4 | 2 | 50 | 50
[25 empty] | 2379 | 4 | 10 | 4 | 3 | 51.1 | 51
[25 empty] | 2380 | 4 | 10 | 4 | 4 | 52 | 52
[25 empty] | 2381 | 4 | 10 | 4 | 5 | 53.1 | 53
[25 empty] | 2382 | 4 | 10 | 4 | 6 | 55 | 55
[25 empty] | 2383 | 4 | 10 | 4 | 7 | 54 | 54
[25 empty] | 2384 | 4 | 10 | 4 | 8 | 55 | 55
[25 empty] | 2385 | 4 | 10 | 4 | 9 | 59 | 59
[25 empty] | 2386 | 4 | 10 | 4 | 10 | 63 | 63
[25 empty] | 2387 | 4 | 10 | 4 | 11 | 63 | 63
[25 empty] | 2388 | 4 | 10 | 4 | 12 | 63 | 63
[25 empty] | 2389 | 4 | 10 | 4 | 13 | 64 | 64
[25 empty] | 2390 | 4 | 10 | 4 | 14 | 61 | 61
[25 empty] | 2391 | 4 | 10 | 4 | 15 | 60.1 | 60
[25 empty] | 2392 | 4 | 10 | 4 | 16 | 60.1 | 60
[25 empty] | 2393 | 4 | 10 | 4 | 17 | 60.1 | 60
[25 empty] | 2394 | 4 | 10 | 4 | 18 | 57 | 57
[25 empty] | 2395 | 4 | 10 | 4 | 19 | 55 | 55
[25 empty] | 2396 | 4 | 10 | 4 | 20 | 55 | 55
[25 empty] | 2397 | 4 | 10 | 4 | 21 | 54 | 54
[25 empty] | 2398 | 4 | 10 | 4 | 22 | 54 | 54
[25 empty] | 2399 | 4 | 10 | 4 | 23 | 51.1 | 51
[25 empty] | 2400 | 4 | 11 | 5 | 0 | 51.1 | 51
[25 empty] | 2401 | 4 | 11 | 5 | 1 | 50 | 50
[25 empty] | 2402 | 4 | 11 | 5 | 2 | 50 | 50
[25 empty] | 2403 | 4 | 11 | 5 | 3 | 48 | 48
[25 empty] | 2404 | 4 | 11 | 5 | 4 | 46.9 | 47
[25 empty] | 2405 | 4 | 11 | 5 | 5 | 46.9 | 47
[25 empty] | 2406 | 4 | 11 | 5 | 6 | 46 | 46
[25 empty] | 2407 | 4 | 11 | 5 | 7 | 46.9 | 47
[25 empty] | 2408 | 4 | 11 | 5 | 8 | 48.9 | 49
[25 empty] | 2409 | 4 | 11 | 5 | 9 | 51.1 | 51
[25 empty] | 2410 | 4 | 11 | 5 | 10 | 54 | 54
[25 empty] | 2411 | 4 | 11 | 5 | 11 | 55.9 | 56
[25 empty] | 2412 | 4 | 11 | 5 | 12 | 59 | 59
[25 empty] | 2413 | 4 | 11 | 5 | 13 | 62.1 | 62
[25 empty] | 2414 | 4 | 11 | 5 | 14 | 63 | 63
[25 empty] | 2415 | 4 | 11 | 5 | 15 | 64 | 64
[25 empty] | 2416 | 4 | 11 | 5 | 16 | 64.9 | 65
[25 empty] | 2417 | 4 | 11 | 5 | 17 | 63 | 63
[25 empty] | 2418 | 4 | 11 | 5 | 18 | 63 | 63
[25 empty] | 2419 | 4 | 11 | 5 | 19 | 62.1 | 62
[25 empty] | 2420 | 4 | 11 | 5 | 20 | 57.9 | 58
[25 empty] | 2421 | 4 | 11 | 5 | 21 | 57.9 | 58
[25 empty] | 2422 | 4 | 11 | 5 | 22 | 55 | 55
[25 empty] | 2423 | 4 | 11 | 5 | 23 | 55.9 | 56
[25 empty] | 2424 | 4 | 12 | 6 | 0 | 55 | 55
[25 empty] | 2425 | 4 | 12 | 6 | 1 | 54 | 54
[25 empty] | 2426 | 4 | 12 | 6 | 2 | 53.1 | 53
[25 empty] | 2427 | 4 | 12 | 6 | 3 | 51.1 | 51
[25 empty] | 2428 | 4 | 12 | 6 | 4 | 48.9 | 49
[25 empty] | 2429 | 4 | 12 | 6 | 5 | 50 | 50
[25 empty] | 2430 | 4 | 12 | 6 | 6 | 50 | 50
[25 empty] | 2431 | 4 | 12 | 6 | 7 | 48.9 | 49
[25 empty] | 2432 | 4 | 12 | 6 | 8 | 50 | 50
[25 empty] | 2433 | 4 | 12 | 6 | 9 | 50 | 50
[25 empty] | 2434 | 4 | 12 | 6 | 10 | 51.1 | 51
[25 empty] | 2435 | 4 | 12 | 6 | 11 | 48.9 | 49
[25 empty] | 2436 | 4 | 12 | 6 | 12 | 48 | 48
[25 empty] | 2437 | 4 | 12 | 6 | 13 | 46 | 46
[25 empty] | 2438 | 4 | 12 | 6 | 14 | 45 | 45
[25 empty] | 2439 | 4 | 12 | 6 | 15 | 45 | 45
[25 empty] | 2440 | 4 | 12 | 6 | 16 | 46 | 46
[25 empty] | 2441 | 4 | 12 | 6 | 17 | 46 | 46
[25 empty] | 2442 | 4 | 12 | 6 | 18 | 45 | 45
[25 empty] | 2443 | 4 | 12 | 6 | 19 | 44.1 | 44
[25 empty] | 2444 | 4 | 12 | 6 | 20 | 44.1 | 44
[25 empty] | 2445 | 4 | 12 | 6 | 21 | 44.1 | 44
[25 empty] | 2446 | 4 | 12 | 6 | 22 | 44.1 | 44
[25 empty] | 2447 | 4 | 12 | 6 | 23 | 44.1 | 44
[25 empty] | 2448 | 4 | 13 | 7 | 0 | 44.1 | 44
[25 empty] | 2449 | 4 | 13 | 7 | 1 | 44.1 | 44
[25 empty] | 2450 | 4 | 13 | 7 | 2 | 43 | 43
[25 empty] | 2451 | 4 | 13 | 7 | 3 | 43 | 43
[25 empty] | 2452 | 4 | 13 | 7 | 4 | 43 | 43
[25 empty] | 2453 | 4 | 13 | 7 | 5 | 43 | 43
[25 empty] | 2454 | 4 | 13 | 7 | 6 | 44.1 | 44
[25 empty] | 2455 | 4 | 13 | 7 | 7 | 44.1 | 44
[25 empty] | 2456 | 4 | 13 | 7 | 8 | 44.1 | 44
[25 empty] | 2457 | 4 | 13 | 7 | 9 | 44.1 | 44
[25 empty] | 2458 | 4 | 13 | 7 | 10 | 45 | 45
[25 empty] | 2459 | 4 | 13 | 7 | 11 | 46 | 46
[25 empty] | 2460 | 4 | 13 | 7 | 12 | 45 | 45
[25 empty] | 2461 | 4 | 13 | 7 | 13 | 45 | 45
[25 empty] | 2462 | 4 | 13 | 7 | 14 | 46 | 46
[25 empty] | 2463 | 4 | 13 | 7 | 15 | 46.9 | 47
[25 empty] | 2464 | 4 | 13 | 7 | 16 | 55 | 55
[25 empty] | 2465 | 4 | 13 | 7 | 17 | 57 | 57
[25 empty] | 2466 | 4 | 13 | 7 | 18 | 55.9 | 56
[25 empty] | 2467 | 4 | 13 | 7 | 19 | 55 | 55
[25 empty] | 2468 | 4 | 13 | 7 | 20 | 54 | 54
[25 empty] | 2469 | 4 | 13 | 7 | 21 | 55 | 55
[25 empty] | 2470 | 4 | 13 | 7 | 22 | 54 | 54
[25 empty] | 2471 | 4 | 13 | 7 | 23 | 54 | 54
[25 empty] | 2472 | 4 | 14 | 1 | 0 | 55 | 55
[25 empty] | 2473 | 4 | 14 | 1 | 1 | 54 | 54
[25 empty] | 2474 | 4 | 14 | 1 | 2 | 55 | 55
[25 empty] | 2475 | 4 | 14 | 1 | 3 | 55 | 55
[25 empty] | 2476 | 4 | 14 | 1 | 4 | 55 | 55
[25 empty] | 2477 | 4 | 14 | 1 | 5 | 55 | 55
[25 empty] | 2478 | 4 | 14 | 1 | 6 | 55.9 | 56
[25 empty] | 2479 | 4 | 14 | 1 | 7 | 57.9 | 58
[25 empty] | 2480 | 4 | 14 | 1 | 8 | 60.1 | 60
[25 empty] | 2481 | 4 | 14 | 1 | 9 | 61 | 61
[25 empty] | 2482 | 4 | 14 | 1 | 10 | 62.1 | 62
[25 empty] | 2483 | 4 | 14 | 1 | 11 | 63 | 63
[25 empty] | 2484 | 4 | 14 | 1 | 12 | 64 | 64
[25 empty] | 2485 | 4 | 14 | 1 | 13 | 66 | 66
[25 empty] | 2486 | 4 | 14 | 1 | 14 | 66.9 | 67
[25 empty] | 2487 | 4 | 14 | 1 | 15 | 68 | 68
[25 empty] | 2488 | 4 | 14 | 1 | 16 | 69.1 | 69
[25 empty] | 2489 | 4 | 14 | 1 | 17 | 71.1 | 71
[25 empty] | 2490 | 4 | 14 | 1 | 18 | 66.9 | 67
[25 empty] | 2491 | 4 | 14 | 1 | 19 | 64.9 | 65
[25 empty] | 2492 | 4 | 14 | 1 | 20 | 63 | 63
[25 empty] | 2493 | 4 | 14 | 1 | 21 | 62.1 | 62
[25 empty] | 2494 | 4 | 14 | 1 | 22 | 63 | 63
[25 empty] | 2495 | 4 | 14 | 1 | 23 | 62.1 | 62
[25 empty] | 2496 | 4 | 15 | 2 | 0 | 57.9 | 58
[25 empty] | 2497 | 4 | 15 | 2 | 1 | 57 | 57
[25 empty] | 2498 | 4 | 15 | 2 | 2 | 53.1 | 53
[25 empty] | 2499 | 4 | 15 | 2 | 3 | 51.1 | 51
[25 empty] | 2500 | 4 | 15 | 2 | 4 | 48.9 | 49
[25 empty] | 2501 | 4 | 15 | 2 | 5 | 48.9 | 49
[25 empty] | 2502 | 4 | 15 | 2 | 6 | 48 | 48
[25 empty] | 2503 | 4 | 15 | 2 | 7 | 52 | 52
[25 empty] | 2504 | 4 | 15 | 2 | 8 | 53.1 | 53
[25 empty] | 2505 | 4 | 15 | 2 | 9 | 57 | 57
[25 empty] | 2506 | 4 | 15 | 2 | 10 | 60.1 | 60
[25 empty] | 2507 | 4 | 15 | 2 | 11 | 64.9 | 65
[25 empty] | 2508 | 4 | 15 | 2 | 12 | 64.9 | 65
[25 empty] | 2509 | 4 | 15 | 2 | 13 | 66.9 | 67
[25 empty] | 2510 | 4 | 15 | 2 | 14 | 75 | 75
[25 empty] | 2511 | 4 | 15 | 2 | 15 | 73.9 | 74
[25 empty] | 2512 | 4 | 15 | 2 | 16 | 68 | 68
[25 empty] | 2513 | 4 | 15 | 2 | 17 | 69.1 | 69
[25 empty] | 2514 | 4 | 15 | 2 | 18 | 68 | 68
[25 empty] | 2515 | 4 | 15 | 2 | 19 | 66.9 | 67
[25 empty] | 2516 | 4 | 15 | 2 | 20 | 62.1 | 62
[25 empty] | 2517 | 4 | 15 | 2 | 21 | 57.9 | 58
[25 empty] | 2518 | 4 | 15 | 2 | 22 | 57.9 | 58
[25 empty] | 2519 | 4 | 15 | 2 | 23 | 57 | 57
[25 empty] | 2520 | 4 | 16 | 3 | 0 | 57 | 57
[25 empty] | 2521 | 4 | 16 | 3 | 1 | 57.9 | 58
[25 empty] | 2522 | 4 | 16 | 3 | 2 | 57 | 57
[25 empty] | 2523 | 4 | 16 | 3 | 3 | 55 | 55
[25 empty] | 2524 | 4 | 16 | 3 | 4 | 54 | 54
[25 empty] | 2525 | 4 | 16 | 3 | 5 | 55 | 55
[25 empty] | 2526 | 4 | 16 | 3 | 6 | 57 | 57
[25 empty] | 2527 | 4 | 16 | 3 | 7 | 57 | 57
[25 empty] | 2528 | 4 | 16 | 3 | 8 | 55.9 | 56
[25 empty] | 2529 | 4 | 16 | 3 | 9 | 55.9 | 56
[25 empty] | 2530 | 4 | 16 | 3 | 10 | 54 | 54
[25 empty] | 2531 | 4 | 16 | 3 | 11 | 53.1 | 53
[25 empty] | 2532 | 4 | 16 | 3 | 12 | 55 | 55
[25 empty] | 2533 | 4 | 16 | 3 | 13 | 57 | 57
[25 empty] | 2534 | 4 | 16 | 3 | 14 | 59 | 59
[25 empty] | 2535 | 4 | 16 | 3 | 15 | 62.1 | 62
[25 empty] | 2536 | 4 | 16 | 3 | 16 | 66 | 66
[25 empty] | 2537 | 4 | 16 | 3 | 17 | 66 | 66
[25 empty] | 2538 | 4 | 16 | 3 | 18 | 63 | 63
[25 empty] | 2539 | 4 | 16 | 3 | 19 | 62.1 | 62
[25 empty] | 2540 | 4 | 16 | 3 | 20 | 61 | 61
[25 empty] | 2541 | 4 | 16 | 3 | 21 | 60.1 | 60
[25 empty] | 2542 | 4 | 16 | 3 | 22 | 59 | 59
[25 empty] | 2543 | 4 | 16 | 3 | 23 | 57 | 57
[25 empty] | 2544 | 4 | 17 | 4 | 0 | 55.9 | 56
[25 empty] | 2545 | 4 | 17 | 4 | 1 | 55 | 55
[25 empty] | 2546 | 4 | 17 | 4 | 2 | 54 | 54
[25 empty] | 2547 | 4 | 17 | 4 | 3 | 53.1 | 53
[25 empty] | 2548 | 4 | 17 | 4 | 4 | 52 | 52
[25 empty] | 2549 | 4 | 17 | 4 | 5 | 52 | 52
[25 empty] | 2550 | 4 | 17 | 4 | 6 | 50 | 50
[25 empty] | 2551 | 4 | 17 | 4 | 7 | 53.1 | 53
[25 empty] | 2552 | 4 | 17 | 4 | 8 | 55 | 55
[25 empty] | 2553 | 4 | 17 | 4 | 9 | 57.9 | 58
[25 empty] | 2554 | 4 | 17 | 4 | 10 | 57.9 | 58
[25 empty] | 2555 | 4 | 17 | 4 | 11 | 60.1 | 60
[25 empty] | 2556 | 4 | 17 | 4 | 12 | 60.1 | 60
[25 empty] | 2557 | 4 | 17 | 4 | 13 | 57.9 | 58
[25 empty] | 2558 | 4 | 17 | 4 | 14 | 57.9 | 58
[25 empty] | 2559 | 4 | 17 | 4 | 15 | 61 | 61
[25 empty] | 2560 | 4 | 17 | 4 | 16 | 59 | 59
[25 empty] | 2561 | 4 | 17 | 4 | 17 | 62.1 | 62
[25 empty] | 2562 | 4 | 17 | 4 | 18 | 60.1 | 60
[25 empty] | 2563 | 4 | 17 | 4 | 19 | 61 | 61
[25 empty] | 2564 | 4 | 17 | 4 | 20 | 60.1 | 60
[25 empty] | 2565 | 4 | 17 | 4 | 21 | 61 | 61
[25 empty] | 2566 | 4 | 17 | 4 | 22 | 55.9 | 56
[25 empty] | 2567 | 4 | 17 | 4 | 23 | 54 | 54
[25 empty] | 2568 | 4 | 18 | 5 | 0 | 54 | 54
[25 empty] | 2569 | 4 | 18 | 5 | 1 | 55 | 55
[25 empty] | 2570 | 4 | 18 | 5 | 2 | 52 | 52
[25 empty] | 2571 | 4 | 18 | 5 | 3 | 52 | 52
[25 empty] | 2572 | 4 | 18 | 5 | 4 | 52 | 52
[25 empty] | 2573 | 4 | 18 | 5 | 5 | 52 | 52
[25 empty] | 2574 | 4 | 18 | 5 | 6 | 52 | 52
[25 empty] | 2575 | 4 | 18 | 5 | 7 | 51.1 | 51
[25 empty] | 2576 | 4 | 18 | 5 | 8 | 54 | 54
[25 empty] | 2577 | 4 | 18 | 5 | 9 | 55 | 55
[25 empty] | 2578 | 4 | 18 | 5 | 10 | 55.9 | 56
[25 empty] | 2579 | 4 | 18 | 5 | 11 | 57.9 | 58
[25 empty] | 2580 | 4 | 18 | 5 | 12 | 61 | 61
[25 empty] | 2581 | 4 | 18 | 5 | 13 | 61 | 61
[25 empty] | 2582 | 4 | 18 | 5 | 14 | 63 | 63
[25 empty] | 2583 | 4 | 18 | 5 | 15 | 64 | 64
[25 empty] | 2584 | 4 | 18 | 5 | 16 | 64.9 | 65
[25 empty] | 2585 | 4 | 18 | 5 | 17 | 66 | 66
[25 empty] | 2586 | 4 | 18 | 5 | 18 | 66 | 66
[25 empty] | 2587 | 4 | 18 | 5 | 19 | 66 | 66
[25 empty] | 2588 | 4 | 18 | 5 | 20 | 64 | 64
[25 empty] | 2589 | 4 | 18 | 5 | 21 | 63 | 63
[25 empty] | 2590 | 4 | 18 | 5 | 22 | 63 | 63
[25 empty] | 2591 | 4 | 18 | 5 | 23 | 62.1 | 62
[25 empty] | 2592 | 4 | 19 | 6 | 0 | 62.1 | 62
[25 empty] | 2593 | 4 | 19 | 6 | 1 | 61 | 61
[25 empty] | 2594 | 4 | 19 | 6 | 2 | 57 | 57
[25 empty] | 2595 | 4 | 19 | 6 | 3 | 55 | 55
[25 empty] | 2596 | 4 | 19 | 6 | 4 | 54 | 54
[25 empty] | 2597 | 4 | 19 | 6 | 5 | 53.1 | 53
[25 empty] | 2598 | 4 | 19 | 6 | 6 | 52 | 52
[25 empty] | 2599 | 4 | 19 | 6 | 7 | 55.9 | 56
[25 empty] | 2600 | 4 | 19 | 6 | 8 | 62.1 | 62
[25 empty] | 2601 | 4 | 19 | 6 | 9 | 69.1 | 69
[25 empty] | 2602 | 4 | 19 | 6 | 10 | 70 | 70
[25 empty] | 2603 | 4 | 19 | 6 | 11 | 75.9 | 76
[25 empty] | 2604 | 4 | 19 | 6 | 12 | 79 | 79
[25 empty] | 2605 | 4 | 19 | 6 | 13 | 80.1 | 80
[25 empty] | 2606 | 4 | 19 | 6 | 14 | 81 | 81
[25 empty] | 2607 | 4 | 19 | 6 | 15 | 81 | 81
[25 empty] | 2608 | 4 | 19 | 6 | 16 | 80.1 | 80
[25 empty] | 2609 | 4 | 19 | 6 | 17 | 73.9 | 74
[25 empty] | 2610 | 4 | 19 | 6 | 18 | 68 | 68
[25 empty] | 2611 | 4 | 19 | 6 | 19 | 66.9 | 67
[25 empty] | 2612 | 4 | 19 | 6 | 20 | 66.9 | 67
[25 empty] | 2613 | 4 | 19 | 6 | 21 | 66.9 | 67
[25 empty] | 2614 | 4 | 19 | 6 | 22 | 66.9 | 67
[25 empty] | 2615 | 4 | 19 | 6 | 23 | 64.9 | 65
[25 empty] | 2616 | 4 | 20 | 7 | 0 | 61 | 61
[25 empty] | 2617 | 4 | 20 | 7 | 1 | 60.1 | 60
[25 empty] | 2618 | 4 | 20 | 7 | 2 | 57 | 57
[25 empty] | 2619 | 4 | 20 | 7 | 3 | 55 | 55
[25 empty] | 2620 | 4 | 20 | 7 | 4 | 54 | 54
[25 empty] | 2621 | 4 | 20 | 7 | 5 | 54 | 54
[25 empty] | 2622 | 4 | 20 | 7 | 6 | 55 | 55
[25 empty] | 2623 | 4 | 20 | 7 | 7 | 54 | 54
[25 empty] | 2624 | 4 | 20 | 7 | 8 | 55 | 55
[25 empty] | 2625 | 4 | 20 | 7 | 9 | 55.9 | 56
[25 empty] | 2626 | 4 | 20 | 7 | 10 | 57 | 57
[25 empty] | 2627 | 4 | 20 | 7 | 11 | 59 | 59
[25 empty] | 2628 | 4 | 20 | 7 | 12 | 60.1 | 60
[25 empty] | 2629 | 4 | 20 | 7 | 13 | 60.1 | 60
[25 empty] | 2630 | 4 | 20 | 7 | 14 | 60.1 | 60
[25 empty] | 2631 | 4 | 20 | 7 | 15 | 59 | 59
[25 empty] | 2632 | 4 | 20 | 7 | 16 | 60.1 | 60
[25 empty] | 2633 | 4 | 20 | 7 | 17 | 61 | 61
[25 empty] | 2634 | 4 | 20 | 7 | 18 | 59 | 59
[25 empty] | 2635 | 4 | 20 | 7 | 19 | 57 | 57
[25 empty] | 2636 | 4 | 20 | 7 | 20 | 55.9 | 56
[25 empty] | 2637 | 4 | 20 | 7 | 21 | 55 | 55
[25 empty] | 2638 | 4 | 20 | 7 | 22 | 52 | 52
[25 empty] | 2639 | 4 | 20 | 7 | 23 | 52 | 52
[25 empty] | 2640 | 4 | 21 | 1 | 0 | 51.1 | 51
[25 empty] | 2641 | 4 | 21 | 1 | 1 | 50 | 50
[25 empty] | 2642 | 4 | 21 | 1 | 2 | 50 | 50
[25 empty] | 2643 | 4 | 21 | 1 | 3 | 50 | 50
[25 empty] | 2644 | 4 | 21 | 1 | 4 | 48.9 | 49
[25 empty] | 2645 | 4 | 21 | 1 | 5 | 48 | 48
[25 empty] | 2646 | 4 | 21 | 1 | 6 | 48.9 | 49
[25 empty] | 2647 | 4 | 21 | 1 | 7 | 50 | 50
[25 empty] | 2648 | 4 | 21 | 1 | 8 | 50 | 50
[25 empty] | 2649 | 4 | 21 | 1 | 9 | 54 | 54
[25 empty] | 2650 | 4 | 21 | 1 | 10 | 55.9 | 56
[25 empty] | 2651 | 4 | 21 | 1 | 11 | 57 | 57
[25 empty] | 2652 | 4 | 21 | 1 | 12 | 59 | 59
[25 empty] | 2653 | 4 | 21 | 1 | 13 | 62.1 | 62
[25 empty] | 2654 | 4 | 21 | 1 | 14 | 61 | 61
[25 empty] | 2655 | 4 | 21 | 1 | 15 | 59 | 59
[25 empty] | 2656 | 4 | 21 | 1 | 16 | 59 | 59
[25 empty] | 2657 | 4 | 21 | 1 | 17 | 57.9 | 58
[25 empty] | 2658 | 4 | 21 | 1 | 18 | 55.9 | 56
[25 empty] | 2659 | 4 | 21 | 1 | 19 | 54 | 54
[25 empty] | 2660 | 4 | 21 | 1 | 20 | 53.1 | 53
[25 empty] | 2661 | 4 | 21 | 1 | 21 | 52 | 52
[25 empty] | 2662 | 4 | 21 | 1 | 22 | 52 | 52
[25 empty] | 2663 | 4 | 21 | 1 | 23 | 50 | 50
[25 empty] | 2664 | 4 | 22 | 2 | 0 | 48.9 | 49
[25 empty] | 2665 | 4 | 22 | 2 | 1 | 46.9 | 47
[25 empty] | 2666 | 4 | 22 | 2 | 2 | 46 | 46
[25 empty] | 2667 | 4 | 22 | 2 | 3 | 45 | 45
[25 empty] | 2668 | 4 | 22 | 2 | 4 | 44.1 | 44
[25 empty] | 2669 | 4 | 22 | 2 | 5 | 45 | 45
[25 empty] | 2670 | 4 | 22 | 2 | 6 | 46 | 46
[25 empty] | 2671 | 4 | 22 | 2 | 7 | 46.9 | 47
[25 empty] | 2672 | 4 | 22 | 2 | 8 | 48.9 | 49
[25 empty] | 2673 | 4 | 22 | 2 | 9 | 50 | 50
[25 empty] | 2674 | 4 | 22 | 2 | 10 | 51.1 | 51
[25 empty] | 2675 | 4 | 22 | 2 | 11 | 52 | 52
[25 empty] | 2676 | 4 | 22 | 2 | 12 | 54 | 54
[25 empty] | 2677 | 4 | 22 | 2 | 13 | 55.9 | 56
[25 empty] | 2678 | 4 | 22 | 2 | 14 | 57 | 57
[25 empty] | 2679 | 4 | 22 | 2 | 15 | 57 | 57
[25 empty] | 2680 | 4 | 22 | 2 | 16 | 57 | 57
[25 empty] | 2681 | 4 | 22 | 2 | 17 | 57 | 57
[25 empty] | 2682 | 4 | 22 | 2 | 18 | 55.9 | 56
[25 empty] | 2683 | 4 | 22 | 2 | 19 | 54 | 54
[25 empty] | 2684 | 4 | 22 | 2 | 20 | 53.1 | 53
[25 empty] | 2685 | 4 | 22 | 2 | 21 | 52 | 52
[25 empty] | 2686 | 4 | 22 | 2 | 22 | 51.1 | 51
[25 empty] | 2687 | 4 | 22 | 2 | 23 | 50 | 50
[25 empty] | 2688 | 4 | 23 | 3 | 0 | 48.9 | 49
[25 empty] | 2689 | 4 | 23 | 3 | 1 | 48 | 48
[25 empty] | 2690 | 4 | 23 | 3 | 2 | 46.9 | 47
[25 empty] | 2691 | 4 | 23 | 3 | 3 | 46 | 46
[25 empty] | 2692 | 4 | 23 | 3 | 4 | 46 | 46
[25 empty] | 2693 | 4 | 23 | 3 | 5 | 46 | 46
[25 empty] | 2694 | 4 | 23 | 3 | 6 | 45 | 45
[25 empty] | 2695 | 4 | 23 | 3 | 7 | 46.9 | 47
[25 empty] | 2696 | 4 | 23 | 3 | 8 | 48.9 | 49
[25 empty] | 2697 | 4 | 23 | 3 | 9 | 50 | 50
[25 empty] | 2698 | 4 | 23 | 3 | 10 | 54 | 54
[25 empty] | 2699 | 4 | 23 | 3 | 11 | 55.9 | 56
[25 empty] | 2700 | 4 | 23 | 3 | 12 | 57 | 57
[25 empty] | 2701 | 4 | 23 | 3 | 13 | 60.1 | 60
[25 empty] | 2702 | 4 | 23 | 3 | 14 | 60.1 | 60
[25 empty] | 2703 | 4 | 23 | 3 | 15 | 60.1 | 60
[25 empty] | 2704 | 4 | 23 | 3 | 16 | 57 | 57
[25 empty] | 2705 | 4 | 23 | 3 | 17 | 55.9 | 56
[25 empty] | 2706 | 4 | 23 | 3 | 18 | 53.1 | 53
[25 empty] | 2707 | 4 | 23 | 3 | 19 | 52 | 52
[25 empty] | 2708 | 4 | 23 | 3 | 20 | 53.1 | 53
[25 empty] | 2709 | 4 | 23 | 3 | 21 | 53.1 | 53
[25 empty] | 2710 | 4 | 23 | 3 | 22 | 53.1 | 53
[25 empty] | 2711 | 4 | 23 | 3 | 23 | 54 | 54
[25 empty] | 2712 | 4 | 24 | 4 | 0 | 53.1 | 53
[25 empty] | 2713 | 4 | 24 | 4 | 1 | 53.1 | 53
[25 empty] | 2714 | 4 | 24 | 4 | 2 | 53.1 | 53
[25 empty] | 2715 | 4 | 24 | 4 | 3 | 53.1 | 53
[25 empty] | 2716 | 4 | 24 | 4 | 4 | 52 | 52
[25 empty] | 2717 | 4 | 24 | 4 | 5 | 51.1 | 51
[25 empty] | 2718 | 4 | 24 | 4 | 6 | 51.1 | 51
[25 empty] | 2719 | 4 | 24 | 4 | 7 | 54 | 54
[25 empty] | 2720 | 4 | 24 | 4 | 8 | 57 | 57
[25 empty] | 2721 | 4 | 24 | 4 | 9 | 62.1 | 62
[25 empty] | 2722 | 4 | 24 | 4 | 10 | 66 | 66
[25 empty] | 2723 | 4 | 24 | 4 | 11 | 70 | 70
[25 empty] | 2724 | 4 | 24 | 4 | 12 | 73.9 | 74
[25 empty] | 2725 | 4 | 24 | 4 | 13 | 75 | 75
[25 empty] | 2726 | 4 | 24 | 4 | 14 | 77 | 77
[25 empty] | 2727 | 4 | 24 | 4 | 15 | 79 | 79
[25 empty] | 2728 | 4 | 24 | 4 | 16 | 79 | 79
[25 empty] | 2729 | 4 | 24 | 4 | 17 | 80.1 | 80
[25 empty] | 2730 | 4 | 24 | 4 | 18 | 78.1 | 78
[25 empty] | 2731 | 4 | 24 | 4 | 19 | 75 | 75
[25 empty] | 2732 | 4 | 24 | 4 | 20 | 73.9 | 74
[25 empty] | 2733 | 4 | 24 | 4 | 21 | 73 | 73
[25 empty] | 2734 | 4 | 24 | 4 | 22 | 73 | 73
[25 empty] | 2735 | 4 | 24 | 4 | 23 | 72 | 72
[25 empty] | 2736 | 4 | 25 | 5 | 0 | 71.1 | 71
[25 empty] | 2737 | 4 | 25 | 5 | 1 | 73 | 73
[25 empty] | 2738 | 4 | 25 | 5 | 2 | 72 | 72
[25 empty] | 2739 | 4 | 25 | 5 | 3 | 69.1 | 69
[25 empty] | 2740 | 4 | 25 | 5 | 4 | 64.9 | 65
[25 empty] | 2741 | 4 | 25 | 5 | 5 | 66 | 66
[25 empty] | 2742 | 4 | 25 | 5 | 6 | 66.9 | 67
[25 empty] | 2743 | 4 | 25 | 5 | 7 | 66.9 | 67
[25 empty] | 2744 | 4 | 25 | 5 | 8 | 72 | 72
[25 empty] | 2745 | 4 | 25 | 5 | 9 | 75 | 75
[25 empty] | 2746 | 4 | 25 | 5 | 10 | 71.1 | 71
[25 empty] | 2747 | 4 | 25 | 5 | 11 | 73.9 | 74
[25 empty] | 2748 | 4 | 25 | 5 | 12 | 55 | 55
[25 empty] | 2749 | 4 | 25 | 5 | 13 | 54 | 54
[25 empty] | 2750 | 4 | 25 | 5 | 14 | 55 | 55
[25 empty] | 2751 | 4 | 25 | 5 | 15 | 57 | 57
[25 empty] | 2752 | 4 | 25 | 5 | 16 | 52 | 52
[25 empty] | 2753 | 4 | 25 | 5 | 17 | 52 | 52
[25 empty] | 2754 | 4 | 25 | 5 | 18 | 55 | 55
[25 empty] | 2755 | 4 | 25 | 5 | 19 | 54 | 54
[25 empty] | 2756 | 4 | 25 | 5 | 20 | 53.1 | 53
[25 empty] | 2757 | 4 | 25 | 5 | 21 | 51.1 | 51
[25 empty] | 2758 | 4 | 25 | 5 | 22 | 50 | 50
[25 empty] | 2759 | 4 | 25 | 5 | 23 | 48 | 48
[25 empty] | 2760 | 4 | 26 | 6 | 0 | 48 | 48
[25 empty] | 2761 | 4 | 26 | 6 | 1 | 46.9 | 47
[25 empty] | 2762 | 4 | 26 | 6 | 2 | 48 | 48
[25 empty] | 2763 | 4 | 26 | 6 | 3 | 48 | 48
[25 empty] | 2764 | 4 | 26 | 6 | 4 | 48 | 48
[25 empty] | 2765 | 4 | 26 | 6 | 5 | 48 | 48
[25 empty] | 2766 | 4 | 26 | 6 | 6 | 46 | 46
[25 empty] | 2767 | 4 | 26 | 6 | 7 | 46 | 46
[25 empty] | 2768 | 4 | 26 | 6 | 8 | 46 | 46
[25 empty] | 2769 | 4 | 26 | 6 | 9 | 48 | 48
[25 empty] | 2770 | 4 | 26 | 6 | 10 | 46.9 | 47
[25 empty] | 2771 | 4 | 26 | 6 | 11 | 48 | 48
[25 empty] | 2772 | 4 | 26 | 6 | 12 | 48.9 | 49
[25 empty] | 2773 | 4 | 26 | 6 | 13 | 50 | 50
[25 empty] | 2774 | 4 | 26 | 6 | 14 | 51.1 | 51
[25 empty] | 2775 | 4 | 26 | 6 | 15 | 51.1 | 51
[25 empty] | 2776 | 4 | 26 | 6 | 16 | 51.1 | 51
[25 empty] | 2777 | 4 | 26 | 6 | 17 | 53.1 | 53
[25 empty] | 2778 | 4 | 26 | 6 | 18 | 52 | 52
[25 empty] | 2779 | 4 | 26 | 6 | 19 | 50 | 50
[25 empty] | 2780 | 4 | 26 | 6 | 20 | 48 | 48
[25 empty] | 2781 | 4 | 26 | 6 | 21 | 48 | 48
[25 empty] | 2782 | 4 | 26 | 6 | 22 | 48.9 | 49
[25 empty] | 2783 | 4 | 26 | 6 | 23 | 48 | 48
[25 empty] | 2784 | 4 | 27 | 7 | 0 | 46.9 | 47
[25 empty] | 2785 | 4 | 27 | 7 | 1 | 46.9 | 47
[25 empty] | 2786 | 4 | 27 | 7 | 2 | 48 | 48
[25 empty] | 2787 | 4 | 27 | 7 | 3 | 50 | 50
[25 empty] | 2788 | 4 | 27 | 7 | 4 | 50 | 50
[25 empty] | 2789 | 4 | 27 | 7 | 5 | 48.9 | 49
[25 empty] | 2790 | 4 | 27 | 7 | 6 | 48.9 | 49
[25 empty] | 2791 | 4 | 27 | 7 | 7 | 52 | 52
[25 empty] | 2792 | 4 | 27 | 7 | 8 | 54 | 54
[25 empty] | 2793 | 4 | 27 | 7 | 9 | 57 | 57
[25 empty] | 2794 | 4 | 27 | 7 | 10 | 63 | 63
[25 empty] | 2795 | 4 | 27 | 7 | 11 | 71.1 | 71
[25 empty] | 2796 | 4 | 27 | 7 | 12 | 75.9 | 76
[25 empty] | 2797 | 4 | 27 | 7 | 13 | 80.1 | 80
[25 empty] | 2798 | 4 | 27 | 7 | 14 | 75 | 75
[25 empty] | 2799 | 4 | 27 | 7 | 15 | 78.1 | 78
[25 empty] | 2800 | 4 | 27 | 7 | 16 | 80.1 | 80
[25 empty] | 2801 | 4 | 27 | 7 | 17 | 72 | 72
[25 empty] | 2802 | 4 | 27 | 7 | 18 | 77 | 77
[25 empty] | 2803 | 4 | 27 | 7 | 19 | 73 | 73
[25 empty] | 2804 | 4 | 27 | 7 | 20 | 71.1 | 71
[25 empty] | 2805 | 4 | 27 | 7 | 21 | 72 | 72
[25 empty] | 2806 | 4 | 27 | 7 | 22 | 72 | 72
[25 empty] | 2807 | 4 | 27 | 7 | 23 | 72 | 72
[25 empty] | 2808 | 4 | 28 | 1 | 0 | 71.1 | 71
[25 empty] | 2809 | 4 | 28 | 1 | 1 | 69.1 | 69
[25 empty] | 2810 | 4 | 28 | 1 | 2 | 66.9 | 67
[25 empty] | 2811 | 4 | 28 | 1 | 3 | 64.9 | 65
[25 empty] | 2812 | 4 | 28 | 1 | 4 | 63 | 63
[25 empty] | 2813 | 4 | 28 | 1 | 5 | 60.1 | 60
[25 empty] | 2814 | 4 | 28 | 1 | 6 | 59 | 59
[25 empty] | 2815 | 4 | 28 | 1 | 7 | 57.9 | 58
[25 empty] | 2816 | 4 | 28 | 1 | 8 | 59 | 59
[25 empty] | 2817 | 4 | 28 | 1 | 9 | 62.1 | 62
[25 empty] | 2818 | 4 | 28 | 1 | 10 | 64.9 | 65
[25 empty] | 2819 | 4 | 28 | 1 | 11 | 66 | 66
[25 empty] | 2820 | 4 | 28 | 1 | 12 | 68 | 68
[25 empty] | 2821 | 4 | 28 | 1 | 13 | 71.1 | 71
[25 empty] | 2822 | 4 | 28 | 1 | 14 | 71.1 | 71
[25 empty] | 2823 | 4 | 28 | 1 | 15 | 70 | 70
[25 empty] | 2824 | 4 | 28 | 1 | 16 | 70 | 70
[25 empty] | 2825 | 4 | 28 | 1 | 17 | 71.1 | 71
[25 empty] | 2826 | 4 | 28 | 1 | 18 | 70 | 70
[25 empty] | 2827 | 4 | 28 | 1 | 19 | 64.9 | 65
[25 empty] | 2828 | 4 | 28 | 1 | 20 | 64 | 64
[25 empty] | 2829 | 4 | 28 | 1 | 21 | 57 | 57
[25 empty] | 2830 | 4 | 28 | 1 | 22 | 55 | 55
[25 empty] | 2831 | 4 | 28 | 1 | 23 | 54 | 54
[25 empty] | 2832 | 4 | 29 | 2 | 0 | 52 | 52
[25 empty] | 2833 | 4 | 29 | 2 | 1 | 51.1 | 51
[25 empty] | 2834 | 4 | 29 | 2 | 2 | 50 | 50
[25 empty] | 2835 | 4 | 29 | 2 | 3 | 48.9 | 49
[25 empty] | 2836 | 4 | 29 | 2 | 4 | 48.9 | 49
[25 empty] | 2837 | 4 | 29 | 2 | 5 | 48 | 48
[25 empty] | 2838 | 4 | 29 | 2 | 6 | 48.9 | 49
[25 empty] | 2839 | 4 | 29 | 2 | 7 | 48.9 | 49
[25 empty] | 2840 | 4 | 29 | 2 | 8 | 48.9 | 49
[25 empty] | 2841 | 4 | 29 | 2 | 9 | 51.1 | 51
[25 empty] | 2842 | 4 | 29 | 2 | 10 | 53.1 | 53
[25 empty] | 2843 | 4 | 29 | 2 | 11 | 51.1 | 51
[25 empty] | 2844 | 4 | 29 | 2 | 12 | 52 | 52
[25 empty] | 2845 | 4 | 29 | 2 | 13 | 51.1 | 51
[25 empty] | 2846 | 4 | 29 | 2 | 14 | 52 | 52
[25 empty] | 2847 | 4 | 29 | 2 | 15 | 57 | 57
[25 empty] | 2848 | 4 | 29 | 2 | 16 | 53.1 | 53
[25 empty] | 2849 | 4 | 29 | 2 | 17 | 52 | 52
[25 empty] | 2850 | 4 | 29 | 2 | 18 | 53.1 | 53
[25 empty] | 2851 | 4 | 29 | 2 | 19 | 53.1 | 53
[25 empty] | 2852 | 4 | 29 | 2 | 20 | 54 | 54
[25 empty] | 2853 | 4 | 29 | 2 | 21 | 54 | 54
[25 empty] | 2854 | 4 | 29 | 2 | 22 | 52 | 52
[25 empty] | 2855 | 4 | 29 | 2 | 23 | 53.1 | 53
[25 empty] | 2856 | 4 | 30 | 3 | 0 | 55 | 55
[25 empty] | 2857 | 4 | 30 | 3 | 1 | 54 | 54
[25 empty] | 2858 | 4 | 30 | 3 | 2 | 55 | 55
[25 empty] | 2859 | 4 | 30 | 3 | 3 | 57.9 | 58
[25 empty] | 2860 | 4 | 30 | 3 | 4 | 60.1 | 60
[25 empty] | 2861 | 4 | 30 | 3 | 5 | 57 | 57
[25 empty] | 2862 | 4 | 30 | 3 | 6 | 59 | 59
[25 empty] | 2863 | 4 | 30 | 3 | 7 | 61 | 61
[25 empty] | 2864 | 4 | 30 | 3 | 8 | 64 | 64
[25 empty] | 2865 | 4 | 30 | 3 | 9 | 66.9 | 67
[25 empty] | 2866 | 4 | 30 | 3 | 10 | 68 | 68
[25 empty] | 2867 | 4 | 30 | 3 | 11 | 71.1 | 71
[25 empty] | 2868 | 4 | 30 | 3 | 12 | 72 | 72
[25 empty] | 2869 | 4 | 30 | 3 | 13 | 78.1 | 78
[25 empty] | 2870 | 4 | 30 | 3 | 14 | 79 | 79
[25 empty] | 2871 | 4 | 30 | 3 | 15 | 77 | 77
[25 empty] | 2872 | 4 | 30 | 3 | 16 | 75 | 75
[25 empty] | 2873 | 4 | 30 | 3 | 17 | 71.1 | 71
[25 empty] | 2874 | 4 | 30 | 3 | 18 | 69.1 | 69
[25 empty] | 2875 | 4 | 30 | 3 | 19 | 66.9 | 67
[25 empty] | 2876 | 4 | 30 | 3 | 20 | 64.9 | 65
[25 empty] | 2877 | 4 | 30 | 3 | 21 | 64 | 64
[25 empty] | 2878 | 4 | 30 | 3 | 22 | 63.5 | 64
[25 empty] | 2879 | 4 | 30 | 3 | 23 | 63 | 63
[25 empty] | 2880 | 5 | 1 | 4 | 0 | 62.4 | 62
[25 empty] | 2881 | 5 | 1 | 4 | 1 | 61.7 | 62
[25 empty] | 2882 | 5 | 1 | 4 | 2 | 61.2 | 61
[25 empty] | 2883 | 5 | 1 | 4 | 3 | 60.6 | 61
[25 empty] | 2884 | 5 | 1 | 4 | 4 | 60.1 | 60
[25 empty] | 2885 | 5 | 1 | 4 | 5 | 60.1 | 60
[25 empty] | 2886 | 5 | 1 | 4 | 6 | 60.1 | 60
[25 empty] | 2887 | 5 | 1 | 4 | 7 | 61 | 61
[25 empty] | 2888 | 5 | 1 | 4 | 8 | 64 | 64
[25 empty] | 2889 | 5 | 1 | 4 | 9 | 64 | 64
[25 empty] | 2890 | 5 | 1 | 4 | 10 | 66.9 | 67
[25 empty] | 2891 | 5 | 1 | 4 | 11 | 66.9 | 67
[25 empty] | 2892 | 5 | 1 | 4 | 12 | 68 | 68
[25 empty] | 2893 | 5 | 1 | 4 | 13 | 64.9 | 65
[25 empty] | 2894 | 5 | 1 | 4 | 14 | 71.1 | 71
[25 empty] | 2895 | 5 | 1 | 4 | 15 | 73.9 | 74
[25 empty] | 2896 | 5 | 1 | 4 | 16 | 73 | 73
[25 empty] | 2897 | 5 | 1 | 4 | 17 | 75 | 75
[25 empty] | 2898 | 5 | 1 | 4 | 18 | 70 | 70
[25 empty] | 2899 | 5 | 1 | 4 | 19 | 64.9 | 65
[25 empty] | 2900 | 5 | 1 | 4 | 20 | 60.1 | 60
[25 empty] | 2901 | 5 | 1 | 4 | 21 | 57.9 | 58
[25 empty] | 2902 | 5 | 1 | 4 | 22 | 55.9 | 56
[25 empty] | 2903 | 5 | 1 | 4 | 23 | 54 | 54
[25 empty] | 2904 | 5 | 2 | 5 | 0 | 51.1 | 51
[25 empty] | 2905 | 5 | 2 | 5 | 1 | 50 | 50
[25 empty] | 2906 | 5 | 2 | 5 | 2 | 48.9 | 49
[25 empty] | 2907 | 5 | 2 | 5 | 3 | 48 | 48
[25 empty] | 2908 | 5 | 2 | 5 | 4 | 46.9 | 47
[25 empty] | 2909 | 5 | 2 | 5 | 5 | 46.9 | 47
[25 empty] | 2910 | 5 | 2 | 5 | 6 | 46.9 | 47
[25 empty] | 2911 | 5 | 2 | 5 | 7 | 48 | 48
[25 empty] | 2912 | 5 | 2 | 5 | 8 | 48.9 | 49
[25 empty] | 2913 | 5 | 2 | 5 | 9 | 52 | 52
[25 empty] | 2914 | 5 | 2 | 5 | 10 | 53.1 | 53
[25 empty] | 2915 | 5 | 2 | 5 | 11 | 55 | 55
[25 empty] | 2916 | 5 | 2 | 5 | 12 | 57 | 57
[25 empty] | 2917 | 5 | 2 | 5 | 13 | 59 | 59
[25 empty] | 2918 | 5 | 2 | 5 | 14 | 60.1 | 60
[25 empty] | 2919 | 5 | 2 | 5 | 15 | 61 | 61
[25 empty] | 2920 | 5 | 2 | 5 | 16 | 62.1 | 62
[25 empty] | 2921 | 5 | 2 | 5 | 17 | 61 | 61
[25 empty] | 2922 | 5 | 2 | 5 | 18 | 60.1 | 60
[25 empty] | 2923 | 5 | 2 | 5 | 19 | 59 | 59
[25 empty] | 2924 | 5 | 2 | 5 | 20 | 57.9 | 58
[25 empty] | 2925 | 5 | 2 | 5 | 21 | 57 | 57
[25 empty] | 2926 | 5 | 2 | 5 | 22 | 55 | 55
[25 empty] | 2927 | 5 | 2 | 5 | 23 | 54 | 54
[25 empty] | 2928 | 5 | 3 | 6 | 0 | 53.1 | 53
[25 empty] | 2929 | 5 | 3 | 6 | 1 | 52 | 52
[25 empty] | 2930 | 5 | 3 | 6 | 2 | 51.1 | 51
[25 empty] | 2931 | 5 | 3 | 6 | 3 | 50 | 50
[25 empty] | 2932 | 5 | 3 | 6 | 4 | 50 | 50
[25 empty] | 2933 | 5 | 3 | 6 | 5 | 48.9 | 49
[25 empty] | 2934 | 5 | 3 | 6 | 6 | 50 | 50
[25 empty] | 2935 | 5 | 3 | 6 | 7 | 52 | 52
[25 empty] | 2936 | 5 | 3 | 6 | 8 | 54 | 54
[25 empty] | 2937 | 5 | 3 | 6 | 9 | 55 | 55
[25 empty] | 2938 | 5 | 3 | 6 | 10 | 57.9 | 58
[25 empty] | 2939 | 5 | 3 | 6 | 11 | 59 | 59
[25 empty] | 2940 | 5 | 3 | 6 | 12 | 60.1 | 60
[25 empty] | 2941 | 5 | 3 | 6 | 13 | 61 | 61
[25 empty] | 2942 | 5 | 3 | 6 | 14 | 63 | 63
[25 empty] | 2943 | 5 | 3 | 6 | 15 | 63 | 63
[25 empty] | 2944 | 5 | 3 | 6 | 16 | 62.1 | 62
[25 empty] | 2945 | 5 | 3 | 6 | 17 | 59 | 59
[25 empty] | 2946 | 5 | 3 | 6 | 18 | 57 | 57
[25 empty] | 2947 | 5 | 3 | 6 | 19 | 57 | 57
[25 empty] | 2948 | 5 | 3 | 6 | 20 | 57 | 57
[25 empty] | 2949 | 5 | 3 | 6 | 21 | 57 | 57
[25 empty] | 2950 | 5 | 3 | 6 | 22 | 55.9 | 56
[25 empty] | 2951 | 5 | 3 | 6 | 23 | 55 | 55
[25 empty] | 2952 | 5 | 4 | 7 | 0 | 55 | 55
[25 empty] | 2953 | 5 | 4 | 7 | 1 | 55 | 55
[25 empty] | 2954 | 5 | 4 | 7 | 2 | 55 | 55
[25 empty] | 2955 | 5 | 4 | 7 | 3 | 55 | 55
[25 empty] | 2956 | 5 | 4 | 7 | 4 | 52 | 52
[25 empty] | 2957 | 5 | 4 | 7 | 5 | 51.1 | 51
[25 empty] | 2958 | 5 | 4 | 7 | 6 | 51.1 | 51
[25 empty] | 2959 | 5 | 4 | 7 | 7 | 54 | 54
[25 empty] | 2960 | 5 | 4 | 7 | 8 | 57.9 | 58
[25 empty] | 2961 | 5 | 4 | 7 | 9 | 60.1 | 60
[25 empty] | 2962 | 5 | 4 | 7 | 10 | 61 | 61
[25 empty] | 2963 | 5 | 4 | 7 | 11 | 62.1 | 62
[25 empty] | 2964 | 5 | 4 | 7 | 12 | 60.1 | 60
[25 empty] | 2965 | 5 | 4 | 7 | 13 | 61 | 61
[25 empty] | 2966 | 5 | 4 | 7 | 14 | 57.9 | 58
[25 empty] | 2967 | 5 | 4 | 7 | 15 | 57 | 57
[25 empty] | 2968 | 5 | 4 | 7 | 16 | 55 | 55
[25 empty] | 2969 | 5 | 4 | 7 | 17 | 55 | 55
[25 empty] | 2970 | 5 | 4 | 7 | 18 | 55 | 55
[25 empty] | 2971 | 5 | 4 | 7 | 19 | 53.1 | 53
[25 empty] | 2972 | 5 | 4 | 7 | 20 | 52 | 52
[25 empty] | 2973 | 5 | 4 | 7 | 21 | 51.1 | 51
[25 empty] | 2974 | 5 | 4 | 7 | 22 | 51.1 | 51
[25 empty] | 2975 | 5 | 4 | 7 | 23 | 51.1 | 51
[25 empty] | 2976 | 5 | 5 | 1 | 0 | 51.1 | 51
[25 empty] | 2977 | 5 | 5 | 1 | 1 | 51.1 | 51
[25 empty] | 2978 | 5 | 5 | 1 | 2 | 52 | 52
[25 empty] | 2979 | 5 | 5 | 1 | 3 | 52 | 52
[25 empty] | 2980 | 5 | 5 | 1 | 4 | 52 | 52
[25 empty] | 2981 | 5 | 5 | 1 | 5 | 53.1 | 53
[25 empty] | 2982 | 5 | 5 | 1 | 6 | 54 | 54
[25 empty] | 2983 | 5 | 5 | 1 | 7 | 55.9 | 56
[25 empty] | 2984 | 5 | 5 | 1 | 8 | 55.9 | 56
[25 empty] | 2985 | 5 | 5 | 1 | 9 | 57.9 | 58
[25 empty] | 2986 | 5 | 5 | 1 | 10 | 61 | 61
[25 empty] | 2987 | 5 | 5 | 1 | 11 | 63 | 63
[25 empty] | 2988 | 5 | 5 | 1 | 12 | 64 | 64
[25 empty] | 2989 | 5 | 5 | 1 | 13 | 66 | 66
[25 empty] | 2990 | 5 | 5 | 1 | 14 | 68 | 68
[25 empty] | 2991 | 5 | 5 | 1 | 15 | 69.1 | 69
[25 empty] | 2992 | 5 | 5 | 1 | 16 | 71.1 | 71
[25 empty] | 2993 | 5 | 5 | 1 | 17 | 72 | 72
[25 empty] | 2994 | 5 | 5 | 1 | 18 | 71.1 | 71
[25 empty] | 2995 | 5 | 5 | 1 | 19 | 66 | 66
[25 empty] | 2996 | 5 | 5 | 1 | 20 | 62.1 | 62
[25 empty] | 2997 | 5 | 5 | 1 | 21 | 60.1 | 60
[25 empty] | 2998 | 5 | 5 | 1 | 22 | 59 | 59
[25 empty] | 2999 | 5 | 5 | 1 | 23 | 57 | 57
[25 empty] | 3000 | 5 | 6 | 2 | 0 | 55.9 | 56
[25 empty] | 3001 | 5 | 6 | 2 | 1 | 57.9 | 58
[25 empty] | 3002 | 5 | 6 | 2 | 2 | 60.1 | 60
[25 empty] | 3003 | 5 | 6 | 2 | 3 | 57.9 | 58
[25 empty] | 3004 | 5 | 6 | 2 | 4 | 59 | 59
[25 empty] | 3005 | 5 | 6 | 2 | 5 | 60.1 | 60
[25 empty] | 3006 | 5 | 6 | 2 | 6 | 61 | 61
[25 empty] | 3007 | 5 | 6 | 2 | 7 | 59 | 59
[25 empty] | 3008 | 5 | 6 | 2 | 8 | 55.9 | 56
[25 empty] | 3009 | 5 | 6 | 2 | 9 | 55.9 | 56
[25 empty] | 3010 | 5 | 6 | 2 | 10 | 57.9 | 58
[25 empty] | 3011 | 5 | 6 | 2 | 11 | 61 | 61
[25 empty] | 3012 | 5 | 6 | 2 | 12 | 63 | 63
[25 empty] | 3013 | 5 | 6 | 2 | 13 | 57.9 | 58
[25 empty] | 3014 | 5 | 6 | 2 | 14 | 62.1 | 62
[25 empty] | 3015 | 5 | 6 | 2 | 15 | 61 | 61
[25 empty] | 3016 | 5 | 6 | 2 | 16 | 60.1 | 60
[25 empty] | 3017 | 5 | 6 | 2 | 17 | 59 | 59
[25 empty] | 3018 | 5 | 6 | 2 | 18 | 57.9 | 58
[25 empty] | 3019 | 5 | 6 | 2 | 19 | 55.9 | 56
[25 empty] | 3020 | 5 | 6 | 2 | 20 | 54 | 54
[25 empty] | 3021 | 5 | 6 | 2 | 21 | 53.1 | 53
[25 empty] | 3022 | 5 | 6 | 2 | 22 | 52 | 52
[25 empty] | 3023 | 5 | 6 | 2 | 23 | 51.1 | 51
[25 empty] | 3024 | 5 | 7 | 3 | 0 | 51.1 | 51
[25 empty] | 3025 | 5 | 7 | 3 | 1 | 51.1 | 51
[25 empty] | 3026 | 5 | 7 | 3 | 2 | 50 | 50
[25 empty] | 3027 | 5 | 7 | 3 | 3 | 51.1 | 51
[25 empty] | 3028 | 5 | 7 | 3 | 4 | 50 | 50
[25 empty] | 3029 | 5 | 7 | 3 | 5 | 48.9 | 49
[25 empty] | 3030 | 5 | 7 | 3 | 6 | 50 | 50
[25 empty] | 3031 | 5 | 7 | 3 | 7 | 53.1 | 53
[25 empty] | 3032 | 5 | 7 | 3 | 8 | 57 | 57
[25 empty] | 3033 | 5 | 7 | 3 | 9 | 60.1 | 60
[25 empty] | 3034 | 5 | 7 | 3 | 10 | 62.1 | 62
[25 empty] | 3035 | 5 | 7 | 3 | 11 | 63 | 63
[25 empty] | 3036 | 5 | 7 | 3 | 12 | 66.9 | 67
[25 empty] | 3037 | 5 | 7 | 3 | 13 | 68 | 68
[25 empty] | 3038 | 5 | 7 | 3 | 14 | 64.9 | 65
[25 empty] | 3039 | 5 | 7 | 3 | 15 | 62.1 | 62
[25 empty] | 3040 | 5 | 7 | 3 | 16 | 60.1 | 60
[25 empty] | 3041 | 5 | 7 | 3 | 17 | 57.9 | 58
[25 empty] | 3042 | 5 | 7 | 3 | 18 | 57 | 57
[25 empty] | 3043 | 5 | 7 | 3 | 19 | 55.9 | 56
[25 empty] | 3044 | 5 | 7 | 3 | 20 | 53.1 | 53
[25 empty] | 3045 | 5 | 7 | 3 | 21 | 52 | 52
[25 empty] | 3046 | 5 | 7 | 3 | 22 | 51.1 | 51
[25 empty] | 3047 | 5 | 7 | 3 | 23 | 51.1 | 51
[25 empty] | 3048 | 5 | 8 | 4 | 0 | 52 | 52
[25 empty] | 3049 | 5 | 8 | 4 | 1 | 52 | 52
[25 empty] | 3050 | 5 | 8 | 4 | 2 | 53.1 | 53
[25 empty] | 3051 | 5 | 8 | 4 | 3 | 55 | 55
[25 empty] | 3052 | 5 | 8 | 4 | 4 | 54 | 54
[25 empty] | 3053 | 5 | 8 | 4 | 5 | 53.1 | 53
[25 empty] | 3054 | 5 | 8 | 4 | 6 | 54 | 54
[25 empty] | 3055 | 5 | 8 | 4 | 7 | 54 | 54
[25 empty] | 3056 | 5 | 8 | 4 | 8 | 55 | 55
[25 empty] | 3057 | 5 | 8 | 4 | 9 | 57 | 57
[25 empty] | 3058 | 5 | 8 | 4 | 10 | 59 | 59
[25 empty] | 3059 | 5 | 8 | 4 | 11 | 59 | 59
[25 empty] | 3060 | 5 | 8 | 4 | 12 | 61 | 61
[25 empty] | 3061 | 5 | 8 | 4 | 13 | 62.1 | 62
[25 empty] | 3062 | 5 | 8 | 4 | 14 | 61 | 61
[25 empty] | 3063 | 5 | 8 | 4 | 15 | 61 | 61
[25 empty] | 3064 | 5 | 8 | 4 | 16 | 59 | 59
[25 empty] | 3065 | 5 | 8 | 4 | 17 | 57 | 57
[25 empty] | 3066 | 5 | 8 | 4 | 18 | 59 | 59
[25 empty] | 3067 | 5 | 8 | 4 | 19 | 57.9 | 58
[25 empty] | 3068 | 5 | 8 | 4 | 20 | 57.9 | 58
[25 empty] | 3069 | 5 | 8 | 4 | 21 | 57 | 57
[25 empty] | 3070 | 5 | 8 | 4 | 22 | 57 | 57
[25 empty] | 3071 | 5 | 8 | 4 | 23 | 55.9 | 56
[25 empty] | 3072 | 5 | 9 | 5 | 0 | 55.9 | 56
[25 empty] | 3073 | 5 | 9 | 5 | 1 | 55 | 55
[25 empty] | 3074 | 5 | 9 | 5 | 2 | 54 | 54
[25 empty] | 3075 | 5 | 9 | 5 | 3 | 54 | 54
[25 empty] | 3076 | 5 | 9 | 5 | 4 | 52 | 52
[25 empty] | 3077 | 5 | 9 | 5 | 5 | 51.1 | 51
[25 empty] | 3078 | 5 | 9 | 5 | 6 | 54 | 54
[25 empty] | 3079 | 5 | 9 | 5 | 7 | 57 | 57
[25 empty] | 3080 | 5 | 9 | 5 | 8 | 60.1 | 60
[25 empty] | 3081 | 5 | 9 | 5 | 9 | 64 | 64
[25 empty] | 3082 | 5 | 9 | 5 | 10 | 68 | 68
[25 empty] | 3083 | 5 | 9 | 5 | 11 | 70 | 70
[25 empty] | 3084 | 5 | 9 | 5 | 12 | 73 | 73
[25 empty] | 3085 | 5 | 9 | 5 | 13 | 75 | 75
[25 empty] | 3086 | 5 | 9 | 5 | 14 | 73.9 | 74
[25 empty] | 3087 | 5 | 9 | 5 | 15 | 75 | 75
[25 empty] | 3088 | 5 | 9 | 5 | 16 | 75 | 75
[25 empty] | 3089 | 5 | 9 | 5 | 17 | 73.9 | 74
[25 empty] | 3090 | 5 | 9 | 5 | 18 | 73 | 73
[25 empty] | 3091 | 5 | 9 | 5 | 19 | 71.1 | 71
[25 empty] | 3092 | 5 | 9 | 5 | 20 | 70 | 70
[25 empty] | 3093 | 5 | 9 | 5 | 21 | 66.9 | 67
[25 empty] | 3094 | 5 | 9 | 5 | 22 | 66 | 66
[25 empty] | 3095 | 5 | 9 | 5 | 23 | 64.9 | 65
[25 empty] | 3096 | 5 | 10 | 6 | 0 | 64 | 64
[25 empty] | 3097 | 5 | 10 | 6 | 1 | 62.1 | 62
[25 empty] | 3098 | 5 | 10 | 6 | 2 | 62.1 | 62
[25 empty] | 3099 | 5 | 10 | 6 | 3 | 62.1 | 62
[25 empty] | 3100 | 5 | 10 | 6 | 4 | 60.1 | 60
[25 empty] | 3101 | 5 | 10 | 6 | 5 | 59 | 59
[25 empty] | 3102 | 5 | 10 | 6 | 6 | 57.9 | 58
[25 empty] | 3103 | 5 | 10 | 6 | 7 | 60.1 | 60
[25 empty] | 3104 | 5 | 10 | 6 | 8 | 61 | 61
[25 empty] | 3105 | 5 | 10 | 6 | 9 | 64 | 64
[25 empty] | 3106 | 5 | 10 | 6 | 10 | 66 | 66
[25 empty] | 3107 | 5 | 10 | 6 | 11 | 68 | 68
[25 empty] | 3108 | 5 | 10 | 6 | 12 | 70 | 70
[25 empty] | 3109 | 5 | 10 | 6 | 13 | 66 | 66
[25 empty] | 3110 | 5 | 10 | 6 | 14 | 70 | 70
[25 empty] | 3111 | 5 | 10 | 6 | 15 | 71.1 | 71
[25 empty] | 3112 | 5 | 10 | 6 | 16 | 64 | 64
[25 empty] | 3113 | 5 | 10 | 6 | 17 | 63 | 63
[25 empty] | 3114 | 5 | 10 | 6 | 18 | 64 | 64
[25 empty] | 3115 | 5 | 10 | 6 | 19 | 63 | 63
[25 empty] | 3116 | 5 | 10 | 6 | 20 | 60.1 | 60
[25 empty] | 3117 | 5 | 10 | 6 | 21 | 59 | 59
[25 empty] | 3118 | 5 | 10 | 6 | 22 | 59 | 59
[25 empty] | 3119 | 5 | 10 | 6 | 23 | 57 | 57
[25 empty] | 3120 | 5 | 11 | 7 | 0 | 55.9 | 56
[25 empty] | 3121 | 5 | 11 | 7 | 1 | 55 | 55
[25 empty] | 3122 | 5 | 11 | 7 | 2 | 55 | 55
[25 empty] | 3123 | 5 | 11 | 7 | 3 | 54 | 54
[25 empty] | 3124 | 5 | 11 | 7 | 4 | 52 | 52
[25 empty] | 3125 | 5 | 11 | 7 | 5 | 50 | 50
[25 empty] | 3126 | 5 | 11 | 7 | 6 | 54 | 54
[25 empty] | 3127 | 5 | 11 | 7 | 7 | 60.1 | 60
[25 empty] | 3128 | 5 | 11 | 7 | 8 | 62.1 | 62
[25 empty] | 3129 | 5 | 11 | 7 | 9 | 64.9 | 65
[25 empty] | 3130 | 5 | 11 | 7 | 10 | 68 | 68
[25 empty] | 3131 | 5 | 11 | 7 | 11 | 69.1 | 69
[25 empty] | 3132 | 5 | 11 | 7 | 12 | 71.1 | 71
[25 empty] | 3133 | 5 | 11 | 7 | 13 | 69.1 | 69
[25 empty] | 3134 | 5 | 11 | 7 | 14 | 66.9 | 67
[25 empty] | 3135 | 5 | 11 | 7 | 15 | 66 | 66
[25 empty] | 3136 | 5 | 11 | 7 | 16 | 64 | 64
[25 empty] | 3137 | 5 | 11 | 7 | 17 | 62.1 | 62
[25 empty] | 3138 | 5 | 11 | 7 | 18 | 61 | 61
[25 empty] | 3139 | 5 | 11 | 7 | 19 | 60.1 | 60
[25 empty] | 3140 | 5 | 11 | 7 | 20 | 62.1 | 62
[25 empty] | 3141 | 5 | 11 | 7 | 21 | 62.1 | 62
[25 empty] | 3142 | 5 | 11 | 7 | 22 | 60.1 | 60
[25 empty] | 3143 | 5 | 11 | 7 | 23 | 60.1 | 60
[25 empty] | 3144 | 5 | 12 | 1 | 0 | 59 | 59
[25 empty] | 3145 | 5 | 12 | 1 | 1 | 57.9 | 58
[25 empty] | 3146 | 5 | 12 | 1 | 2 | 57.9 | 58
[25 empty] | 3147 | 5 | 12 | 1 | 3 | 59 | 59
[25 empty] | 3148 | 5 | 12 | 1 | 4 | 62.1 | 62
[25 empty] | 3149 | 5 | 12 | 1 | 5 | 62.1 | 62
[25 empty] | 3150 | 5 | 12 | 1 | 6 | 63 | 63
[25 empty] | 3151 | 5 | 12 | 1 | 7 | 63 | 63
[25 empty] | 3152 | 5 | 12 | 1 | 8 | 63 | 63
[25 empty] | 3153 | 5 | 12 | 1 | 9 | 64 | 64
[25 empty] | 3154 | 5 | 12 | 1 | 10 | 60.1 | 60
[25 empty] | 3155 | 5 | 12 | 1 | 11 | 64 | 64
[25 empty] | 3156 | 5 | 12 | 1 | 12 | 66.9 | 67
[25 empty] | 3157 | 5 | 12 | 1 | 13 | 70 | 70
[25 empty] | 3158 | 5 | 12 | 1 | 14 | 59 | 59
[25 empty] | 3159 | 5 | 12 | 1 | 15 | 63 | 63
[25 empty] | 3160 | 5 | 12 | 1 | 16 | 62.1 | 62
[25 empty] | 3161 | 5 | 12 | 1 | 17 | 61 | 61
[25 empty] | 3162 | 5 | 12 | 1 | 18 | 57 | 57
[25 empty] | 3163 | 5 | 12 | 1 | 19 | 55.9 | 56
[25 empty] | 3164 | 5 | 12 | 1 | 20 | 54 | 54
[25 empty] | 3165 | 5 | 12 | 1 | 21 | 54 | 54
[25 empty] | 3166 | 5 | 12 | 1 | 22 | 53.1 | 53
[25 empty] | 3167 | 5 | 12 | 1 | 23 | 52 | 52
[25 empty] | 3168 | 5 | 13 | 2 | 0 | 50 | 50
[25 empty] | 3169 | 5 | 13 | 2 | 1 | 51.1 | 51
[25 empty] | 3170 | 5 | 13 | 2 | 2 | 50 | 50
[25 empty] | 3171 | 5 | 13 | 2 | 3 | 48.9 | 49
[25 empty] | 3172 | 5 | 13 | 2 | 4 | 48 | 48
[25 empty] | 3173 | 5 | 13 | 2 | 5 | 48 | 48
[25 empty] | 3174 | 5 | 13 | 2 | 6 | 48 | 48
[25 empty] | 3175 | 5 | 13 | 2 | 7 | 48.9 | 49
[25 empty] | 3176 | 5 | 13 | 2 | 8 | 51.1 | 51
[25 empty] | 3177 | 5 | 13 | 2 | 9 | 53.1 | 53
[25 empty] | 3178 | 5 | 13 | 2 | 10 | 55 | 55
[25 empty] | 3179 | 5 | 13 | 2 | 11 | 57 | 57
[25 empty] | 3180 | 5 | 13 | 2 | 12 | 60.1 | 60
[25 empty] | 3181 | 5 | 13 | 2 | 13 | 61 | 61
[25 empty] | 3182 | 5 | 13 | 2 | 14 | 63 | 63
[25 empty] | 3183 | 5 | 13 | 2 | 15 | 63 | 63
[25 empty] | 3184 | 5 | 13 | 2 | 16 | 63 | 63
[25 empty] | 3185 | 5 | 13 | 2 | 17 | 62.1 | 62
[25 empty] | 3186 | 5 | 13 | 2 | 18 | 61 | 61
[25 empty] | 3187 | 5 | 13 | 2 | 19 | 57.9 | 58
[25 empty] | 3188 | 5 | 13 | 2 | 20 | 55.9 | 56
[25 empty] | 3189 | 5 | 13 | 2 | 21 | 55 | 55
[25 empty] | 3190 | 5 | 13 | 2 | 22 | 54 | 54
[25 empty] | 3191 | 5 | 13 | 2 | 23 | 54 | 54
[25 empty] | 3192 | 5 | 14 | 3 | 0 | 53.1 | 53
[25 empty] | 3193 | 5 | 14 | 3 | 1 | 53.1 | 53
[25 empty] | 3194 | 5 | 14 | 3 | 2 | 52 | 52
[25 empty] | 3195 | 5 | 14 | 3 | 3 | 51.1 | 51
[25 empty] | 3196 | 5 | 14 | 3 | 4 | 51.1 | 51
[25 empty] | 3197 | 5 | 14 | 3 | 5 | 51.1 | 51
[25 empty] | 3198 | 5 | 14 | 3 | 6 | 51.1 | 51
[25 empty] | 3199 | 5 | 14 | 3 | 7 | 52 | 52
[25 empty] | 3200 | 5 | 14 | 3 | 8 | 55 | 55
[25 empty] | 3201 | 5 | 14 | 3 | 9 | 57.9 | 58
[25 empty] | 3202 | 5 | 14 | 3 | 10 | 62.1 | 62
[25 empty] | 3203 | 5 | 14 | 3 | 11 | 63 | 63
[25 empty] | 3204 | 5 | 14 | 3 | 12 | 66 | 66
[25 empty] | 3205 | 5 | 14 | 3 | 13 | 69.1 | 69
[25 empty] | 3206 | 5 | 14 | 3 | 14 | 71.1 | 71
[25 empty] | 3207 | 5 | 14 | 3 | 15 | 73.9 | 74
[25 empty] | 3208 | 5 | 14 | 3 | 16 | 73.9 | 74
[25 empty] | 3209 | 5 | 14 | 3 | 17 | 75.9 | 76
[25 empty] | 3210 | 5 | 14 | 3 | 18 | 75.9 | 76
[25 empty] | 3211 | 5 | 14 | 3 | 19 | 73.9 | 74
[25 empty] | 3212 | 5 | 14 | 3 | 20 | 71.1 | 71
[25 empty] | 3213 | 5 | 14 | 3 | 21 | 70 | 70
[25 empty] | 3214 | 5 | 14 | 3 | 22 | 69.1 | 69
[25 empty] | 3215 | 5 | 14 | 3 | 23 | 68 | 68
[25 empty] | 3216 | 5 | 15 | 4 | 0 | 64 | 64
[25 empty] | 3217 | 5 | 15 | 4 | 1 | 62.1 | 62
[25 empty] | 3218 | 5 | 15 | 4 | 2 | 60.1 | 60
[25 empty] | 3219 | 5 | 15 | 4 | 3 | 59 | 59
[25 empty] | 3220 | 5 | 15 | 4 | 4 | 57.9 | 58
[25 empty] | 3221 | 5 | 15 | 4 | 5 | 57.9 | 58
[25 empty] | 3222 | 5 | 15 | 4 | 6 | 59 | 59
[25 empty] | 3223 | 5 | 15 | 4 | 7 | 63 | 63
[25 empty] | 3224 | 5 | 15 | 4 | 8 | 69.1 | 69
[25 empty] | 3225 | 5 | 15 | 4 | 9 | 66.9 | 67
[25 empty] | 3226 | 5 | 15 | 4 | 10 | 73 | 73
[25 empty] | 3227 | 5 | 15 | 4 | 11 | 73.9 | 74
[25 empty] | 3228 | 5 | 15 | 4 | 12 | 73 | 73
[25 empty] | 3229 | 5 | 15 | 4 | 13 | 71.1 | 71
[25 empty] | 3230 | 5 | 15 | 4 | 14 | 70 | 70
[25 empty] | 3231 | 5 | 15 | 4 | 15 | 70 | 70
[25 empty] | 3232 | 5 | 15 | 4 | 16 | 70 | 70
[25 empty] | 3233 | 5 | 15 | 4 | 17 | 64.9 | 65
[25 empty] | 3234 | 5 | 15 | 4 | 18 | 66 | 66
[25 empty] | 3235 | 5 | 15 | 4 | 19 | 64 | 64
[25 empty] | 3236 | 5 | 15 | 4 | 20 | 63 | 63
[25 empty] | 3237 | 5 | 15 | 4 | 21 | 62.1 | 62
[25 empty] | 3238 | 5 | 15 | 4 | 22 | 59 | 59
[25 empty] | 3239 | 5 | 15 | 4 | 23 | 57 | 57
[25 empty] | 3240 | 5 | 16 | 5 | 0 | 57 | 57
[25 empty] | 3241 | 5 | 16 | 5 | 1 | 55 | 55
[25 empty] | 3242 | 5 | 16 | 5 | 2 | 55 | 55
[25 empty] | 3243 | 5 | 16 | 5 | 3 | 55 | 55
[25 empty] | 3244 | 5 | 16 | 5 | 4 | 55 | 55
[25 empty] | 3245 | 5 | 16 | 5 | 5 | 55.9 | 56
[25 empty] | 3246 | 5 | 16 | 5 | 6 | 55.9 | 56
[25 empty] | 3247 | 5 | 16 | 5 | 7 | 55 | 55
[25 empty] | 3248 | 5 | 16 | 5 | 8 | 57 | 57
[25 empty] | 3249 | 5 | 16 | 5 | 9 | 59 | 59
[25 empty] | 3250 | 5 | 16 | 5 | 10 | 64 | 64
[25 empty] | 3251 | 5 | 16 | 5 | 11 | 68 | 68
[25 empty] | 3252 | 5 | 16 | 5 | 12 | 73 | 73
[25 empty] | 3253 | 5 | 16 | 5 | 13 | 68 | 68
[25 empty] | 3254 | 5 | 16 | 5 | 14 | 68 | 68
[25 empty] | 3255 | 5 | 16 | 5 | 15 | 70 | 70
[25 empty] | 3256 | 5 | 16 | 5 | 16 | 71.1 | 71
[25 empty] | 3257 | 5 | 16 | 5 | 17 | 69.1 | 69
[25 empty] | 3258 | 5 | 16 | 5 | 18 | 63 | 63
[25 empty] | 3259 | 5 | 16 | 5 | 19 | 62.1 | 62
[25 empty] | 3260 | 5 | 16 | 5 | 20 | 57.9 | 58
[25 empty] | 3261 | 5 | 16 | 5 | 21 | 57 | 57
[25 empty] | 3262 | 5 | 16 | 5 | 22 | 55.9 | 56
[25 empty] | 3263 | 5 | 16 | 5 | 23 | 54 | 54
[25 empty] | 3264 | 5 | 17 | 6 | 0 | 54 | 54
[25 empty] | 3265 | 5 | 17 | 6 | 1 | 53.1 | 53
[25 empty] | 3266 | 5 | 17 | 6 | 2 | 53.1 | 53
[25 empty] | 3267 | 5 | 17 | 6 | 3 | 52 | 52
[25 empty] | 3268 | 5 | 17 | 6 | 4 | 51.1 | 51
[25 empty] | 3269 | 5 | 17 | 6 | 5 | 50 | 50
[25 empty] | 3270 | 5 | 17 | 6 | 6 | 51.1 | 51
[25 empty] | 3271 | 5 | 17 | 6 | 7 | 51.1 | 51
[25 empty] | 3272 | 5 | 17 | 6 | 8 | 52 | 52
[25 empty] | 3273 | 5 | 17 | 6 | 9 | 52 | 52
[25 empty] | 3274 | 5 | 17 | 6 | 10 | 52 | 52
[25 empty] | 3275 | 5 | 17 | 6 | 11 | 54 | 54
[25 empty] | 3276 | 5 | 17 | 6 | 12 | 57 | 57
[25 empty] | 3277 | 5 | 17 | 6 | 13 | 57.9 | 58
[25 empty] | 3278 | 5 | 17 | 6 | 14 | 57.9 | 58
[25 empty] | 3279 | 5 | 17 | 6 | 15 | 57.9 | 58
[25 empty] | 3280 | 5 | 17 | 6 | 16 | 59 | 59
[25 empty] | 3281 | 5 | 17 | 6 | 17 | 59 | 59
[25 empty] | 3282 | 5 | 17 | 6 | 18 | 59 | 59
[25 empty] | 3283 | 5 | 17 | 6 | 19 | 57.9 | 58
[25 empty] | 3284 | 5 | 17 | 6 | 20 | 57.9 | 58
[25 empty] | 3285 | 5 | 17 | 6 | 21 | 57.9 | 58
[25 empty] | 3286 | 5 | 17 | 6 | 22 | 57 | 57
[25 empty] | 3287 | 5 | 17 | 6 | 23 | 55.9 | 56
[25 empty] | 3288 | 5 | 18 | 7 | 0 | 55.9 | 56
[25 empty] | 3289 | 5 | 18 | 7 | 1 | 53.1 | 53
[25 empty] | 3290 | 5 | 18 | 7 | 2 | 52 | 52
[25 empty] | 3291 | 5 | 18 | 7 | 3 | 52 | 52
[25 empty] | 3292 | 5 | 18 | 7 | 4 | 54 | 54
[25 empty] | 3293 | 5 | 18 | 7 | 5 | 54 | 54
[25 empty] | 3294 | 5 | 18 | 7 | 6 | 53.1 | 53
[25 empty] | 3295 | 5 | 18 | 7 | 7 | 55 | 55
[25 empty] | 3296 | 5 | 18 | 7 | 8 | 57 | 57
[25 empty] | 3297 | 5 | 18 | 7 | 9 | 59 | 59
[25 empty] | 3298 | 5 | 18 | 7 | 10 | 61 | 61
[25 empty] | 3299 | 5 | 18 | 7 | 11 | 61 | 61
[25 empty] | 3300 | 5 | 18 | 7 | 12 | 60.1 | 60
[25 empty] | 3301 | 5 | 18 | 7 | 13 | 61 | 61
[25 empty] | 3302 | 5 | 18 | 7 | 14 | 62.1 | 62
[25 empty] | 3303 | 5 | 18 | 7 | 15 | 60.1 | 60
[25 empty] | 3304 | 5 | 18 | 7 | 16 | 63 | 63
[25 empty] | 3305 | 5 | 18 | 7 | 17 | 61 | 61
[25 empty] | 3306 | 5 | 18 | 7 | 18 | 55 | 55
[25 empty] | 3307 | 5 | 18 | 7 | 19 | 55 | 55
[25 empty] | 3308 | 5 | 18 | 7 | 20 | 55 | 55
[25 empty] | 3309 | 5 | 18 | 7 | 21 | 53.1 | 53
[25 empty] | 3310 | 5 | 18 | 7 | 22 | 53.1 | 53
[25 empty] | 3311 | 5 | 18 | 7 | 23 | 54 | 54
[25 empty] | 3312 | 5 | 19 | 1 | 0 | 53.1 | 53
[25 empty] | 3313 | 5 | 19 | 1 | 1 | 54 | 54
[25 empty] | 3314 | 5 | 19 | 1 | 2 | 51.1 | 51
[25 empty] | 3315 | 5 | 19 | 1 | 3 | 50 | 50
[25 empty] | 3316 | 5 | 19 | 1 | 4 | 51.1 | 51
[25 empty] | 3317 | 5 | 19 | 1 | 5 | 50 | 50
[25 empty] | 3318 | 5 | 19 | 1 | 6 | 51.1 | 51
[25 empty] | 3319 | 5 | 19 | 1 | 7 | 52 | 52
[25 empty] | 3320 | 5 | 19 | 1 | 8 | 52 | 52
[25 empty] | 3321 | 5 | 19 | 1 | 9 | 53.1 | 53
[25 empty] | 3322 | 5 | 19 | 1 | 10 | 53.1 | 53
[25 empty] | 3323 | 5 | 19 | 1 | 11 | 53.1 | 53
[25 empty] | 3324 | 5 | 19 | 1 | 12 | 53.1 | 53
[25 empty] | 3325 | 5 | 19 | 1 | 13 | 54 | 54
[25 empty] | 3326 | 5 | 19 | 1 | 14 | 54 | 54
[25 empty] | 3327 | 5 | 19 | 1 | 15 | 53.1 | 53
[25 empty] | 3328 | 5 | 19 | 1 | 16 | 52 | 52
[25 empty] | 3329 | 5 | 19 | 1 | 17 | 52 | 52
[25 empty] | 3330 | 5 | 19 | 1 | 18 | 51.1 | 51
[25 empty] | 3331 | 5 | 19 | 1 | 19 | 51.1 | 51
[25 empty] | 3332 | 5 | 19 | 1 | 20 | 51.1 | 51
[25 empty] | 3333 | 5 | 19 | 1 | 21 | 50 | 50
[25 empty] | 3334 | 5 | 19 | 1 | 22 | 50 | 50
[25 empty] | 3335 | 5 | 19 | 1 | 23 | 48.9 | 49
[25 empty] | 3336 | 5 | 20 | 2 | 0 | 48.9 | 49
[25 empty] | 3337 | 5 | 20 | 2 | 1 | 48.9 | 49
[25 empty] | 3338 | 5 | 20 | 2 | 2 | 48 | 48
[25 empty] | 3339 | 5 | 20 | 2 | 3 | 46.9 | 47
[25 empty] | 3340 | 5 | 20 | 2 | 4 | 48 | 48
[25 empty] | 3341 | 5 | 20 | 2 | 5 | 48.9 | 49
[25 empty] | 3342 | 5 | 20 | 2 | 6 | 48 | 48
[25 empty] | 3343 | 5 | 20 | 2 | 7 | 48 | 48
[25 empty] | 3344 | 5 | 20 | 2 | 8 | 48.9 | 49
[25 empty] | 3345 | 5 | 20 | 2 | 9 | 51.1 | 51
[25 empty] | 3346 | 5 | 20 | 2 | 10 | 52 | 52
[25 empty] | 3347 | 5 | 20 | 2 | 11 | 54 | 54
[25 empty] | 3348 | 5 | 20 | 2 | 12 | 55 | 55
[25 empty] | 3349 | 5 | 20 | 2 | 13 | 55.9 | 56
[25 empty] | 3350 | 5 | 20 | 2 | 14 | 57 | 57
[25 empty] | 3351 | 5 | 20 | 2 | 15 | 60.1 | 60
[25 empty] | 3352 | 5 | 20 | 2 | 16 | 60.1 | 60
[25 empty] | 3353 | 5 | 20 | 2 | 17 | 61 | 61
[25 empty] | 3354 | 5 | 20 | 2 | 18 | 55.9 | 56
[25 empty] | 3355 | 5 | 20 | 2 | 19 | 54 | 54
[25 empty] | 3356 | 5 | 20 | 2 | 20 | 52 | 52
[25 empty] | 3357 | 5 | 20 | 2 | 21 | 51.1 | 51
[25 empty] | 3358 | 5 | 20 | 2 | 22 | 50 | 50
[25 empty] | 3359 | 5 | 20 | 2 | 23 | 50 | 50
[25 empty] | 3360 | 5 | 21 | 3 | 0 | 50 | 50
[25 empty] | 3361 | 5 | 21 | 3 | 1 | 48.9 | 49
[25 empty] | 3362 | 5 | 21 | 3 | 2 | 48.9 | 49
[25 empty] | 3363 | 5 | 21 | 3 | 3 | 48.9 | 49
[25 empty] | 3364 | 5 | 21 | 3 | 4 | 48 | 48
[25 empty] | 3365 | 5 | 21 | 3 | 5 | 50 | 50
[25 empty] | 3366 | 5 | 21 | 3 | 6 | 52 | 52
[25 empty] | 3367 | 5 | 21 | 3 | 7 | 55 | 55
[25 empty] | 3368 | 5 | 21 | 3 | 8 | 57 | 57
[25 empty] | 3369 | 5 | 21 | 3 | 9 | 60.1 | 60
[25 empty] | 3370 | 5 | 21 | 3 | 10 | 62.1 | 62
[25 empty] | 3371 | 5 | 21 | 3 | 11 | 64 | 64
[25 empty] | 3372 | 5 | 21 | 3 | 12 | 66.9 | 67
[25 empty] | 3373 | 5 | 21 | 3 | 13 | 70 | 70
[25 empty] | 3374 | 5 | 21 | 3 | 14 | 71.1 | 71
[25 empty] | 3375 | 5 | 21 | 3 | 15 | 69.1 | 69
[25 empty] | 3376 | 5 | 21 | 3 | 16 | 69.1 | 69
[25 empty] | 3377 | 5 | 21 | 3 | 17 | 66.9 | 67
[25 empty] | 3378 | 5 | 21 | 3 | 18 | 64 | 64
[25 empty] | 3379 | 5 | 21 | 3 | 19 | 60.1 | 60
[25 empty] | 3380 | 5 | 21 | 3 | 20 | 57.9 | 58
[25 empty] | 3381 | 5 | 21 | 3 | 21 | 57 | 57
[25 empty] | 3382 | 5 | 21 | 3 | 22 | 55.9 | 56
[25 empty] | 3383 | 5 | 21 | 3 | 23 | 55 | 55
[25 empty] | 3384 | 5 | 22 | 4 | 0 | 55 | 55
[25 empty] | 3385 | 5 | 22 | 4 | 1 | 55 | 55
[25 empty] | 3386 | 5 | 22 | 4 | 2 | 55 | 55
[25 empty] | 3387 | 5 | 22 | 4 | 3 | 55 | 55
[25 empty] | 3388 | 5 | 22 | 4 | 4 | 54 | 54
[25 empty] | 3389 | 5 | 22 | 4 | 5 | 54 | 54
[25 empty] | 3390 | 5 | 22 | 4 | 6 | 57.9 | 58
[25 empty] | 3391 | 5 | 22 | 4 | 7 | 60.1 | 60
[25 empty] | 3392 | 5 | 22 | 4 | 8 | 66.9 | 67
[25 empty] | 3393 | 5 | 22 | 4 | 9 | 73 | 73
[25 empty] | 3394 | 5 | 22 | 4 | 10 | 75 | 75
[25 empty] | 3395 | 5 | 22 | 4 | 11 | 75 | 75
[25 empty] | 3396 | 5 | 22 | 4 | 12 | 75.9 | 76
[25 empty] | 3397 | 5 | 22 | 4 | 13 | 78.1 | 78
[25 empty] | 3398 | 5 | 22 | 4 | 14 | 73.9 | 74
[25 empty] | 3399 | 5 | 22 | 4 | 15 | 75 | 75
[25 empty] | 3400 | 5 | 22 | 4 | 16 | 73.9 | 74
[25 empty] | 3401 | 5 | 22 | 4 | 17 | 75 | 75
[25 empty] | 3402 | 5 | 22 | 4 | 18 | 73 | 73
[25 empty] | 3403 | 5 | 22 | 4 | 19 | 66.9 | 67
[25 empty] | 3404 | 5 | 22 | 4 | 20 | 64 | 64
[25 empty] | 3405 | 5 | 22 | 4 | 21 | 64 | 64
[25 empty] | 3406 | 5 | 22 | 4 | 22 | 63 | 63
[25 empty] | 3407 | 5 | 22 | 4 | 23 | 63 | 63
[25 empty] | 3408 | 5 | 23 | 5 | 0 | 61 | 61
[25 empty] | 3409 | 5 | 23 | 5 | 1 | 60.1 | 60
[25 empty] | 3410 | 5 | 23 | 5 | 2 | 60.1 | 60
[25 empty] | 3411 | 5 | 23 | 5 | 3 | 59 | 59
[25 empty] | 3412 | 5 | 23 | 5 | 4 | 57.9 | 58
[25 empty] | 3413 | 5 | 23 | 5 | 5 | 57.9 | 58
[25 empty] | 3414 | 5 | 23 | 5 | 6 | 61 | 61
[25 empty] | 3415 | 5 | 23 | 5 | 7 | 64.9 | 65
[25 empty] | 3416 | 5 | 23 | 5 | 8 | 69.1 | 69
[25 empty] | 3417 | 5 | 23 | 5 | 9 | 72 | 72
[25 empty] | 3418 | 5 | 23 | 5 | 10 | 77 | 77
[25 empty] | 3419 | 5 | 23 | 5 | 11 | 81 | 81
[25 empty] | 3420 | 5 | 23 | 5 | 12 | 84.9 | 85
[25 empty] | 3421 | 5 | 23 | 5 | 13 | 89.1 | 89
[25 empty] | 3422 | 5 | 23 | 5 | 14 | 89.1 | 89
[25 empty] | 3423 | 5 | 23 | 5 | 15 | 82 | 82
[25 empty] | 3424 | 5 | 23 | 5 | 16 | 81 | 81
[25 empty] | 3425 | 5 | 23 | 5 | 17 | 84 | 84
[25 empty] | 3426 | 5 | 23 | 5 | 18 | 80.1 | 80
[25 empty] | 3427 | 5 | 23 | 5 | 19 | 78.1 | 78
[25 empty] | 3428 | 5 | 23 | 5 | 20 | 75.9 | 76
[25 empty] | 3429 | 5 | 23 | 5 | 21 | 75 | 75
[25 empty] | 3430 | 5 | 23 | 5 | 22 | 75.9 | 76
[25 empty] | 3431 | 5 | 23 | 5 | 23 | 73.9 | 74
[25 empty] | 3432 | 5 | 24 | 6 | 0 | 70 | 70
[25 empty] | 3433 | 5 | 24 | 6 | 1 | 70 | 70
[25 empty] | 3434 | 5 | 24 | 6 | 2 | 66.9 | 67
[25 empty] | 3435 | 5 | 24 | 6 | 3 | 66.9 | 67
[25 empty] | 3436 | 5 | 24 | 6 | 4 | 64 | 64
[25 empty] | 3437 | 5 | 24 | 6 | 5 | 64.9 | 65
[25 empty] | 3438 | 5 | 24 | 6 | 6 | 66 | 66
[25 empty] | 3439 | 5 | 24 | 6 | 7 | 69.1 | 69
[25 empty] | 3440 | 5 | 24 | 6 | 8 | 71.1 | 71
[25 empty] | 3441 | 5 | 24 | 6 | 9 | 73.9 | 74
[25 empty] | 3442 | 5 | 24 | 6 | 10 | 75 | 75
[25 empty] | 3443 | 5 | 24 | 6 | 11 | 75.9 | 76
[25 empty] | 3444 | 5 | 24 | 6 | 12 | 78.1 | 78
[25 empty] | 3445 | 5 | 24 | 6 | 13 | 80.1 | 80
[25 empty] | 3446 | 5 | 24 | 6 | 14 | 82 | 82
[25 empty] | 3447 | 5 | 24 | 6 | 15 | 79 | 79
[25 empty] | 3448 | 5 | 24 | 6 | 16 | 78.1 | 78
[25 empty] | 3449 | 5 | 24 | 6 | 17 | 75.9 | 76
[25 empty] | 3450 | 5 | 24 | 6 | 18 | 73.9 | 74
[25 empty] | 3451 | 5 | 24 | 6 | 19 | 70 | 70
[25 empty] | 3452 | 5 | 24 | 6 | 20 | 68 | 68
[25 empty] | 3453 | 5 | 24 | 6 | 21 | 66.9 | 67
[25 empty] | 3454 | 5 | 24 | 6 | 22 | 66 | 66
[25 empty] | 3455 | 5 | 24 | 6 | 23 | 63 | 63
[25 empty] | 3456 | 5 | 25 | 7 | 0 | 63 | 63
[25 empty] | 3457 | 5 | 25 | 7 | 1 | 62.1 | 62
[25 empty] | 3458 | 5 | 25 | 7 | 2 | 63 | 63
[25 empty] | 3459 | 5 | 25 | 7 | 3 | 64 | 64
[25 empty] | 3460 | 5 | 25 | 7 | 4 | 66.9 | 67
[25 empty] | 3461 | 5 | 25 | 7 | 5 | 66.9 | 67
[25 empty] | 3462 | 5 | 25 | 7 | 6 | 68 | 68
[25 empty] | 3463 | 5 | 25 | 7 | 7 | 71.1 | 71
[25 empty] | 3464 | 5 | 25 | 7 | 8 | 75 | 75
[25 empty] | 3465 | 5 | 25 | 7 | 9 | 75 | 75
[25 empty] | 3466 | 5 | 25 | 7 | 10 | 75.9 | 76
[25 empty] | 3467 | 5 | 25 | 7 | 11 | 80.1 | 80
[25 empty] | 3468 | 5 | 25 | 7 | 12 | 82 | 82
[25 empty] | 3469 | 5 | 25 | 7 | 13 | 84.9 | 85
[25 empty] | 3470 | 5 | 25 | 7 | 14 | 84.9 | 85
[25 empty] | 3471 | 5 | 25 | 7 | 15 | 84 | 84
[25 empty] | 3472 | 5 | 25 | 7 | 16 | 82.9 | 83
[25 empty] | 3473 | 5 | 25 | 7 | 17 | 72 | 72
[25 empty] | 3474 | 5 | 25 | 7 | 18 | 71.1 | 71
[25 empty] | 3475 | 5 | 25 | 7 | 19 | 72 | 72
[25 empty] | 3476 | 5 | 25 | 7 | 20 | 66.9 | 67
[25 empty] | 3477 | 5 | 25 | 7 | 21 | 66.9 | 67
[25 empty] | 3478 | 5 | 25 | 7 | 22 | 64.9 | 65
[25 empty] | 3479 | 5 | 25 | 7 | 23 | 66 | 66
[25 empty] | 3480 | 5 | 26 | 1 | 0 | 66 | 66
[25 empty] | 3481 | 5 | 26 | 1 | 1 | 64.9 | 65
[25 empty] | 3482 | 5 | 26 | 1 | 2 | 64.9 | 65
[25 empty] | 3483 | 5 | 26 | 1 | 3 | 64.9 | 65
[25 empty] | 3484 | 5 | 26 | 1 | 4 | 64 | 64
[25 empty] | 3485 | 5 | 26 | 1 | 5 | 64 | 64
[25 empty] | 3486 | 5 | 26 | 1 | 6 | 64.9 | 65
[25 empty] | 3487 | 5 | 26 | 1 | 7 | 64.9 | 65
[25 empty] | 3488 | 5 | 26 | 1 | 8 | 69.1 | 69
[25 empty] | 3489 | 5 | 26 | 1 | 9 | 72 | 72
[25 empty] | 3490 | 5 | 26 | 1 | 10 | 72 | 72
[25 empty] | 3491 | 5 | 26 | 1 | 11 | 69.1 | 69
[25 empty] | 3492 | 5 | 26 | 1 | 12 | 70 | 70
[25 empty] | 3493 | 5 | 26 | 1 | 13 | 68 | 68
[25 empty] | 3494 | 5 | 26 | 1 | 14 | 71.1 | 71
[25 empty] | 3495 | 5 | 26 | 1 | 15 | 72 | 72
[25 empty] | 3496 | 5 | 26 | 1 | 16 | 73 | 73
[25 empty] | 3497 | 5 | 26 | 1 | 17 | 73.9 | 74
[25 empty] | 3498 | 5 | 26 | 1 | 18 | 75.9 | 76
[25 empty] | 3499 | 5 | 26 | 1 | 19 | 68 | 68
[25 empty] | 3500 | 5 | 26 | 1 | 20 | 68 | 68
[25 empty] | 3501 | 5 | 26 | 1 | 21 | 66.9 | 67
[25 empty] | 3502 | 5 | 26 | 1 | 22 | 66 | 66
[25 empty] | 3503 | 5 | 26 | 1 | 23 | 66 | 66
[25 empty] | 3504 | 5 | 27 | 2 | 0 | 66 | 66
[25 empty] | 3505 | 5 | 27 | 2 | 1 | 66 | 66
[25 empty] | 3506 | 5 | 27 | 2 | 2 | 64 | 64
[25 empty] | 3507 | 5 | 27 | 2 | 3 | 60.1 | 60
[25 empty] | 3508 | 5 | 27 | 2 | 4 | 55.9 | 56
[25 empty] | 3509 | 5 | 27 | 2 | 5 | 52 | 52
[25 empty] | 3510 | 5 | 27 | 2 | 6 | 51.1 | 51
[25 empty] | 3511 | 5 | 27 | 2 | 7 | 50 | 50
[25 empty] | 3512 | 5 | 27 | 2 | 8 | 50 | 50
[25 empty] | 3513 | 5 | 27 | 2 | 9 | 52 | 52
[25 empty] | 3514 | 5 | 27 | 2 | 10 | 55 | 55
[25 empty] | 3515 | 5 | 27 | 2 | 11 | 55.9 | 56
[25 empty] | 3516 | 5 | 27 | 2 | 12 | 59 | 59
[25 empty] | 3517 | 5 | 27 | 2 | 13 | 60.1 | 60
[25 empty] | 3518 | 5 | 27 | 2 | 14 | 61 | 61
[25 empty] | 3519 | 5 | 27 | 2 | 15 | 63 | 63
[25 empty] | 3520 | 5 | 27 | 2 | 16 | 64 | 64
[25 empty] | 3521 | 5 | 27 | 2 | 17 | 64 | 64
[25 empty] | 3522 | 5 | 27 | 2 | 18 | 64.9 | 65
[25 empty] | 3523 | 5 | 27 | 2 | 19 | 63 | 63
[25 empty] | 3524 | 5 | 27 | 2 | 20 | 62.1 | 62
[25 empty] | 3525 | 5 | 27 | 2 | 21 | 60.1 | 60
[25 empty] | 3526 | 5 | 27 | 2 | 22 | 57.9 | 58
[25 empty] | 3527 | 5 | 27 | 2 | 23 | 57 | 57
[25 empty] | 3528 | 5 | 28 | 3 | 0 | 55.9 | 56
[25 empty] | 3529 | 5 | 28 | 3 | 1 | 55 | 55
[25 empty] | 3530 | 5 | 28 | 3 | 2 | 54 | 54
[25 empty] | 3531 | 5 | 28 | 3 | 3 | 53.1 | 53
[25 empty] | 3532 | 5 | 28 | 3 | 4 | 52 | 52
[25 empty] | 3533 | 5 | 28 | 3 | 5 | 51.1 | 51
[25 empty] | 3534 | 5 | 28 | 3 | 6 | 52 | 52
[25 empty] | 3535 | 5 | 28 | 3 | 7 | 55.9 | 56
[25 empty] | 3536 | 5 | 28 | 3 | 8 | 59 | 59
[25 empty] | 3537 | 5 | 28 | 3 | 9 | 61 | 61
[25 empty] | 3538 | 5 | 28 | 3 | 10 | 63 | 63
[25 empty] | 3539 | 5 | 28 | 3 | 11 | 64.9 | 65
[25 empty] | 3540 | 5 | 28 | 3 | 12 | 66 | 66
[25 empty] | 3541 | 5 | 28 | 3 | 13 | 68 | 68
[25 empty] | 3542 | 5 | 28 | 3 | 14 | 70 | 70
[25 empty] | 3543 | 5 | 28 | 3 | 15 | 70 | 70
[25 empty] | 3544 | 5 | 28 | 3 | 16 | 69.1 | 69
[25 empty] | 3545 | 5 | 28 | 3 | 17 | 72 | 72
[25 empty] | 3546 | 5 | 28 | 3 | 18 | 70 | 70
[25 empty] | 3547 | 5 | 28 | 3 | 19 | 69.1 | 69
[25 empty] | 3548 | 5 | 28 | 3 | 20 | 66.9 | 67
[25 empty] | 3549 | 5 | 28 | 3 | 21 | 64.9 | 65
[25 empty] | 3550 | 5 | 28 | 3 | 22 | 64 | 64
[25 empty] | 3551 | 5 | 28 | 3 | 23 | 63 | 63
[25 empty] | 3552 | 5 | 29 | 4 | 0 | 62.1 | 62
[25 empty] | 3553 | 5 | 29 | 4 | 1 | 62.1 | 62
[25 empty] | 3554 | 5 | 29 | 4 | 2 | 60.1 | 60
[25 empty] | 3555 | 5 | 29 | 4 | 3 | 61 | 61
[25 empty] | 3556 | 5 | 29 | 4 | 4 | 59 | 59
[25 empty] | 3557 | 5 | 29 | 4 | 5 | 57.9 | 58
[25 empty] | 3558 | 5 | 29 | 4 | 6 | 60.1 | 60
[25 empty] | 3559 | 5 | 29 | 4 | 7 | 64 | 64
[25 empty] | 3560 | 5 | 29 | 4 | 8 | 66 | 66
[25 empty] | 3561 | 5 | 29 | 4 | 9 | 69.1 | 69
[25 empty] | 3562 | 5 | 29 | 4 | 10 | 73 | 73
[25 empty] | 3563 | 5 | 29 | 4 | 11 | 75.9 | 76
[25 empty] | 3564 | 5 | 29 | 4 | 12 | 77 | 77
[25 empty] | 3565 | 5 | 29 | 4 | 13 | 78.1 | 78
[25 empty] | 3566 | 5 | 29 | 4 | 14 | 77 | 77
[25 empty] | 3567 | 5 | 29 | 4 | 15 | 75.9 | 76
[25 empty] | 3568 | 5 | 29 | 4 | 16 | 75.9 | 76
[25 empty] | 3569 | 5 | 29 | 4 | 17 | 73.9 | 74
[25 empty] | 3570 | 5 | 29 | 4 | 18 | 70 | 70
[25 empty] | 3571 | 5 | 29 | 4 | 19 | 68 | 68
[25 empty] | 3572 | 5 | 29 | 4 | 20 | 68 | 68
[25 empty] | 3573 | 5 | 29 | 4 | 21 | 69.1 | 69
[25 empty] | 3574 | 5 | 29 | 4 | 22 | 68 | 68
[25 empty] | 3575 | 5 | 29 | 4 | 23 | 66.9 | 67
[25 empty] | 3576 | 5 | 30 | 5 | 0 | 66 | 66
[25 empty] | 3577 | 5 | 30 | 5 | 1 | 64.9 | 65
[25 empty] | 3578 | 5 | 30 | 5 | 2 | 64 | 64
[25 empty] | 3579 | 5 | 30 | 5 | 3 | 64 | 64
[25 empty] | 3580 | 5 | 30 | 5 | 4 | 63 | 63
[25 empty] | 3581 | 5 | 30 | 5 | 5 | 61 | 61
[25 empty] | 3582 | 5 | 30 | 5 | 6 | 63 | 63
[25 empty] | 3583 | 5 | 30 | 5 | 7 | 66.9 | 67
[25 empty] | 3584 | 5 | 30 | 5 | 8 | 69.1 | 69
[25 empty] | 3585 | 5 | 30 | 5 | 9 | 73 | 73
[25 empty] | 3586 | 5 | 30 | 5 | 10 | 75.9 | 76
[25 empty] | 3587 | 5 | 30 | 5 | 11 | 79 | 79
[25 empty] | 3588 | 5 | 30 | 5 | 12 | 80.1 | 80
[25 empty] | 3589 | 5 | 30 | 5 | 13 | 81 | 81
[25 empty] | 3590 | 5 | 30 | 5 | 14 | 80.1 | 80
[25 empty] | 3591 | 5 | 30 | 5 | 15 | 77 | 77
[25 empty] | 3592 | 5 | 30 | 5 | 16 | 77 | 77
[25 empty] | 3593 | 5 | 30 | 5 | 17 | 70 | 70
[25 empty] | 3594 | 5 | 30 | 5 | 18 | 73 | 73
[25 empty] | 3595 | 5 | 30 | 5 | 19 | 72 | 72
[25 empty] | 3596 | 5 | 30 | 5 | 20 | 72 | 72
[25 empty] | 3597 | 5 | 30 | 5 | 21 | 71.1 | 71
[25 empty] | 3598 | 5 | 30 | 5 | 22 | 70 | 70
[25 empty] | 3599 | 5 | 30 | 5 | 23 | 69.1 | 69
[25 empty] | 3600 | 5 | 31 | 6 | 0 | 68 | 68
[25 empty] | 3601 | 5 | 31 | 6 | 1 | 66.9 | 67
[25 empty] | 3602 | 5 | 31 | 6 | 2 | 66 | 66
[25 empty] | 3603 | 5 | 31 | 6 | 3 | 66 | 66
[25 empty] | 3604 | 5 | 31 | 6 | 4 | 64.9 | 65
[25 empty] | 3605 | 5 | 31 | 6 | 5 | 64 | 64
[25 empty] | 3606 | 5 | 31 | 6 | 6 | 64.9 | 65
[25 empty] | 3607 | 5 | 31 | 6 | 7 | 68 | 68
[25 empty] | 3608 | 5 | 31 | 6 | 8 | 70 | 70
[25 empty] | 3609 | 5 | 31 | 6 | 9 | 73.9 | 74
[25 empty] | 3610 | 5 | 31 | 6 | 10 | 75.9 | 76
[25 empty] | 3611 | 5 | 31 | 6 | 11 | 79 | 79
[25 empty] | 3612 | 5 | 31 | 6 | 12 | 75.9 | 76
[25 empty] | 3613 | 5 | 31 | 6 | 13 | 78.1 | 78
[25 empty] | 3614 | 5 | 31 | 6 | 14 | 79 | 79
[25 empty] | 3615 | 5 | 31 | 6 | 15 | 78.1 | 78
[25 empty] | 3616 | 5 | 31 | 6 | 16 | 78.1 | 78
[25 empty] | 3617 | 5 | 31 | 6 | 17 | 75.9 | 76
[25 empty] | 3618 | 5 | 31 | 6 | 18 | 73.9 | 74
[25 empty] | 3619 | 5 | 31 | 6 | 19 | 72 | 72
[25 empty] | 3620 | 5 | 31 | 6 | 20 | 71.1 | 71
[25 empty] | 3621 | 5 | 31 | 6 | 21 | 70 | 70
[25 empty] | 3622 | 5 | 31 | 6 | 22 | 68.2 | 68
[25 empty] | 3623 | 5 | 31 | 6 | 23 | 66.2 | 66
[25 empty] | 6552 | 10 | 1 | 3 | 0 | 51.1 | 51
[25 empty] | 6553 | 10 | 1 | 3 | 1 | 50.9 | 51
[25 empty] | 6554 | 10 | 1 | 3 | 2 | 50.5 | 51
[25 empty] | 6555 | 10 | 1 | 3 | 3 | 50.4 | 50
[25 empty] | 6556 | 10 | 1 | 3 | 4 | 50 | 50
[25 empty] | 6557 | 10 | 1 | 3 | 5 | 51.1 | 51
[25 empty] | 6558 | 10 | 1 | 3 | 6 | 52 | 52
[25 empty] | 6559 | 10 | 1 | 3 | 7 | 53.1 | 53
[25 empty] | 6560 | 10 | 1 | 3 | 8 | 55.6 | 56
[25 empty] | 6561 | 10 | 1 | 3 | 9 | 55 | 55
[25 empty] | 6562 | 10 | 1 | 3 | 10 | 56.5 | 57
[25 empty] | 6563 | 10 | 1 | 3 | 11 | 56.3 | 56
[25 empty] | 6564 | 10 | 1 | 3 | 12 | 56.7 | 57
[25 empty] | 6565 | 10 | 1 | 3 | 13 | 56.7 | 57
[25 empty] | 6566 | 10 | 1 | 3 | 14 | 57 | 57
[25 empty] | 6567 | 10 | 1 | 3 | 15 | 57 | 57
[25 empty] | 6568 | 10 | 1 | 3 | 16 | 57.9 | 58
[25 empty] | 6569 | 10 | 1 | 3 | 17 | 55.6 | 56
[25 empty] | 6570 | 10 | 1 | 3 | 18 | 57.9 | 58
[25 empty] | 6571 | 10 | 1 | 3 | 19 | 59 | 59
[25 empty] | 6572 | 10 | 1 | 3 | 20 | 59 | 59
[25 empty] | 6573 | 10 | 1 | 3 | 21 | 57 | 57
[25 empty] | 6574 | 10 | 1 | 3 | 22 | 57 | 57
[25 empty] | 6575 | 10 | 1 | 3 | 23 | 55.9 | 56
[25 empty] | 6576 | 10 | 2 | 4 | 0 | 55 | 55
[25 empty] | 6577 | 10 | 2 | 4 | 1 | 54 | 54
[25 empty] | 6578 | 10 | 2 | 4 | 2 | 53.1 | 53
[25 empty] | 6579 | 10 | 2 | 4 | 3 | 55.9 | 56
[25 empty] | 6580 | 10 | 2 | 4 | 4 | 55 | 55
[25 empty] | 6581 | 10 | 2 | 4 | 5 | 55.9 | 56
[25 empty] | 6582 | 10 | 2 | 4 | 6 | 57 | 57
[25 empty] | 6583 | 10 | 2 | 4 | 7 | 57 | 57
[25 empty] | 6584 | 10 | 2 | 4 | 8 | 60.1 | 60
[25 empty] | 6585 | 10 | 2 | 4 | 9 | 63 | 63
[25 empty] | 6586 | 10 | 2 | 4 | 10 | 64 | 64
[25 empty] | 6587 | 10 | 2 | 4 | 11 | 69.1 | 69
[25 empty] | 6588 | 10 | 2 | 4 | 12 | 72 | 72
[25 empty] | 6589 | 10 | 2 | 4 | 13 | 72 | 72
[25 empty] | 6590 | 10 | 2 | 4 | 14 | 73.9 | 74
[25 empty] | 6591 | 10 | 2 | 4 | 15 | 75 | 75
[25 empty] | 6592 | 10 | 2 | 4 | 16 | 75 | 75
[25 empty] | 6593 | 10 | 2 | 4 | 17 | 75 | 75
[25 empty] | 6594 | 10 | 2 | 4 | 18 | 73 | 73
[25 empty] | 6595 | 10 | 2 | 4 | 19 | 71.1 | 71
[25 empty] | 6596 | 10 | 2 | 4 | 20 | 70 | 70
[25 empty] | 6597 | 10 | 2 | 4 | 21 | 69.1 | 69
[25 empty] | 6598 | 10 | 2 | 4 | 22 | 68 | 68
[25 empty] | 6599 | 10 | 2 | 4 | 23 | 68 | 68
[25 empty] | 6600 | 10 | 3 | 5 | 0 | 66.9 | 67
[25 empty] | 6601 | 10 | 3 | 5 | 1 | 64 | 64
[25 empty] | 6602 | 10 | 3 | 5 | 2 | 63 | 63
[25 empty] | 6603 | 10 | 3 | 5 | 3 | 62.1 | 62
[25 empty] | 6604 | 10 | 3 | 5 | 4 | 62.1 | 62
[25 empty] | 6605 | 10 | 3 | 5 | 5 | 62.1 | 62
[25 empty] | 6606 | 10 | 3 | 5 | 6 | 62.1 | 62
[25 empty] | 6607 | 10 | 3 | 5 | 7 | 63 | 63
[25 empty] | 6608 | 10 | 3 | 5 | 8 | 66 | 66
[25 empty] | 6609 | 10 | 3 | 5 | 9 | 69.1 | 69
[25 empty] | 6610 | 10 | 3 | 5 | 10 | 73 | 73
[25 empty] | 6611 | 10 | 3 | 5 | 11 | 75.9 | 76
[25 empty] | 6612 | 10 | 3 | 5 | 12 | 79 | 79
[25 empty] | 6613 | 10 | 3 | 5 | 13 | 80.1 | 80
[25 empty] | 6614 | 10 | 3 | 5 | 14 | 81 | 81
[25 empty] | 6615 | 10 | 3 | 5 | 15 | 82 | 82
[25 empty] | 6616 | 10 | 3 | 5 | 16 | 81 | 81
[25 empty] | 6617 | 10 | 3 | 5 | 17 | 80.1 | 80
[25 empty] | 6618 | 10 | 3 | 5 | 18 | 77 | 77
[25 empty] | 6619 | 10 | 3 | 5 | 19 | 75.9 | 76
[25 empty] | 6620 | 10 | 3 | 5 | 20 | 75 | 75
[25 empty] | 6621 | 10 | 3 | 5 | 21 | 73.9 | 74
[25 empty] | 6622 | 10 | 3 | 5 | 22 | 73 | 73
[25 empty] | 6623 | 10 | 3 | 5 | 23 | 72 | 72
[25 empty] | 6624 | 10 | 4 | 6 | 0 | 70 | 70
[25 empty] | 6625 | 10 | 4 | 6 | 1 | 69.1 | 69
[25 empty] | 6626 | 10 | 4 | 6 | 2 | 69.1 | 69
[25 empty] | 6627 | 10 | 4 | 6 | 3 | 68 | 68
[25 empty] | 6628 | 10 | 4 | 6 | 4 | 66.9 | 67
[25 empty] | 6629 | 10 | 4 | 6 | 5 | 66 | 66
[25 empty] | 6630 | 10 | 4 | 6 | 6 | 64.9 | 65
[25 empty] | 6631 | 10 | 4 | 6 | 7 | 66 | 66
[25 empty] | 6632 | 10 | 4 | 6 | 8 | 69.1 | 69
[25 empty] | 6633 | 10 | 4 | 6 | 9 | 72 | 72
[25 empty] | 6634 | 10 | 4 | 6 | 10 | 75 | 75
[25 empty] | 6635 | 10 | 4 | 6 | 11 | 77 | 77
[25 empty] | 6636 | 10 | 4 | 6 | 12 | 79 | 79
[25 empty] | 6637 | 10 | 4 | 6 | 13 | 80.1 | 80
[25 empty] | 6638 | 10 | 4 | 6 | 14 | 81 | 81
[25 empty] | 6639 | 10 | 4 | 6 | 15 | 82 | 82
[25 empty] | 6640 | 10 | 4 | 6 | 16 | 81 | 81
[25 empty] | 6641 | 10 | 4 | 6 | 17 | 80.1 | 80
[25 empty] | 6642 | 10 | 4 | 6 | 18 | 78.1 | 78
[25 empty] | 6643 | 10 | 4 | 6 | 19 | 77 | 77
[25 empty] | 6644 | 10 | 4 | 6 | 20 | 75.9 | 76
[25 empty] | 6645 | 10 | 4 | 6 | 21 | 73.9 | 74
[25 empty] | 6646 | 10 | 4 | 6 | 22 | 73.9 | 74
[25 empty] | 6647 | 10 | 4 | 6 | 23 | 71.1 | 71
[25 empty] | 6648 | 10 | 5 | 7 | 0 | 70 | 70
[25 empty] | 6649 | 10 | 5 | 7 | 1 | 71.1 | 71
[25 empty] | 6650 | 10 | 5 | 7 | 2 | 69.1 | 69
[25 empty] | 6651 | 10 | 5 | 7 | 3 | 66.9 | 67
[25 empty] | 6652 | 10 | 5 | 7 | 4 | 66.9 | 67
[25 empty] | 6653 | 10 | 5 | 7 | 5 | 64.9 | 65
[25 empty] | 6654 | 10 | 5 | 7 | 6 | 64.9 | 65
[25 empty] | 6655 | 10 | 5 | 7 | 7 | 64.9 | 65
[25 empty] | 6656 | 10 | 5 | 7 | 8 | 68 | 68
[25 empty] | 6657 | 10 | 5 | 7 | 9 | 70 | 70
[25 empty] | 6658 | 10 | 5 | 7 | 10 | 73 | 73
[25 empty] | 6659 | 10 | 5 | 7 | 11 | 75.9 | 76
[25 empty] | 6660 | 10 | 5 | 7 | 12 | 78.1 | 78
[25 empty] | 6661 | 10 | 5 | 7 | 13 | 79 | 79
[25 empty] | 6662 | 10 | 5 | 7 | 14 | 80.1 | 80
[25 empty] | 6663 | 10 | 5 | 7 | 15 | 79 | 79
[25 empty] | 6664 | 10 | 5 | 7 | 16 | 77 | 77
[25 empty] | 6665 | 10 | 5 | 7 | 17 | 75 | 75
[25 empty] | 6666 | 10 | 5 | 7 | 18 | 73 | 73
[25 empty] | 6667 | 10 | 5 | 7 | 19 | 72 | 72
[25 empty] | 6668 | 10 | 5 | 7 | 20 | 71.1 | 71
[25 empty] | 6669 | 10 | 5 | 7 | 21 | 72 | 72
[25 empty] | 6670 | 10 | 5 | 7 | 22 | 72 | 72
[25 empty] | 6671 | 10 | 5 | 7 | 23 | 70 | 70
[25 empty] | 6672 | 10 | 6 | 1 | 0 | 70 | 70
[25 empty] | 6673 | 10 | 6 | 1 | 1 | 71.1 | 71
[25 empty] | 6674 | 10 | 6 | 1 | 2 | 69.1 | 69
[25 empty] | 6675 | 10 | 6 | 1 | 3 | 70 | 70
[25 empty] | 6676 | 10 | 6 | 1 | 4 | 70 | 70
[25 empty] | 6677 | 10 | 6 | 1 | 5 | 70 | 70
[25 empty] | 6678 | 10 | 6 | 1 | 6 | 71.1 | 71
[25 empty] | 6679 | 10 | 6 | 1 | 7 | 71.1 | 71
[25 empty] | 6680 | 10 | 6 | 1 | 8 | 69.1 | 69
[25 empty] | 6681 | 10 | 6 | 1 | 9 | 68 | 68
[25 empty] | 6682 | 10 | 6 | 1 | 10 | 63 | 63
[25 empty] | 6683 | 10 | 6 | 1 | 11 | 57.9 | 58
[25 empty] | 6684 | 10 | 6 | 1 | 12 | 57 | 57
[25 empty] | 6685 | 10 | 6 | 1 | 13 | 61 | 61
[25 empty] | 6686 | 10 | 6 | 1 | 14 | 62.1 | 62
[25 empty] | 6687 | 10 | 6 | 1 | 15 | 63 | 63
[25 empty] | 6688 | 10 | 6 | 1 | 16 | 62.1 | 62
[25 empty] | 6689 | 10 | 6 | 1 | 17 | 61 | 61
[25 empty] | 6690 | 10 | 6 | 1 | 18 | 60.1 | 60
[25 empty] | 6691 | 10 | 6 | 1 | 19 | 60.1 | 60
[25 empty] | 6692 | 10 | 6 | 1 | 20 | 59 | 59
[25 empty] | 6693 | 10 | 6 | 1 | 21 | 57.9 | 58
[25 empty] | 6694 | 10 | 6 | 1 | 22 | 57.9 | 58
[25 empty] | 6695 | 10 | 6 | 1 | 23 | 55.9 | 56
[25 empty] | 6696 | 10 | 7 | 2 | 0 | 54 | 54
[25 empty] | 6697 | 10 | 7 | 2 | 1 | 53.1 | 53
[25 empty] | 6698 | 10 | 7 | 2 | 2 | 52 | 52
[25 empty] | 6699 | 10 | 7 | 2 | 3 | 50 | 50
[25 empty] | 6700 | 10 | 7 | 2 | 4 | 50 | 50
[25 empty] | 6701 | 10 | 7 | 2 | 5 | 48.9 | 49
[25 empty] | 6702 | 10 | 7 | 2 | 6 | 48 | 48
[25 empty] | 6703 | 10 | 7 | 2 | 7 | 48 | 48
[25 empty] | 6704 | 10 | 7 | 2 | 8 | 48.9 | 49
[25 empty] | 6705 | 10 | 7 | 2 | 9 | 50 | 50
[25 empty] | 6706 | 10 | 7 | 2 | 10 | 52 | 52
[25 empty] | 6707 | 10 | 7 | 2 | 11 | 54 | 54
[25 empty] | 6708 | 10 | 7 | 2 | 12 | 55.9 | 56
[25 empty] | 6709 | 10 | 7 | 2 | 13 | 55.9 | 56
[25 empty] | 6710 | 10 | 7 | 2 | 14 | 55.9 | 56
[25 empty] | 6711 | 10 | 7 | 2 | 15 | 55 | 55
[25 empty] | 6712 | 10 | 7 | 2 | 16 | 55 | 55
[25 empty] | 6713 | 10 | 7 | 2 | 17 | 54 | 54
[25 empty] | 6714 | 10 | 7 | 2 | 18 | 53.1 | 53
[25 empty] | 6715 | 10 | 7 | 2 | 19 | 51.1 | 51
[25 empty] | 6716 | 10 | 7 | 2 | 20 | 50 | 50
[25 empty] | 6717 | 10 | 7 | 2 | 21 | 50 | 50
[25 empty] | 6718 | 10 | 7 | 2 | 22 | 48 | 48
[25 empty] | 6719 | 10 | 7 | 2 | 23 | 46.9 | 47
[25 empty] | 6720 | 10 | 8 | 3 | 0 | 46.9 | 47
[25 empty] | 6721 | 10 | 8 | 3 | 1 | 45 | 45
[25 empty] | 6722 | 10 | 8 | 3 | 2 | 44.1 | 44
[25 empty] | 6723 | 10 | 8 | 3 | 3 | 43 | 43
[25 empty] | 6724 | 10 | 8 | 3 | 4 | 43 | 43
[25 empty] | 6725 | 10 | 8 | 3 | 5 | 43 | 43
[25 empty] | 6726 | 10 | 8 | 3 | 6 | 42.1 | 42
[25 empty] | 6727 | 10 | 8 | 3 | 7 | 42.1 | 42
[25 empty] | 6728 | 10 | 8 | 3 | 8 | 43 | 43
[25 empty] | 6729 | 10 | 8 | 3 | 9 | 45 | 45
[25 empty] | 6730 | 10 | 8 | 3 | 10 | 46 | 46
[25 empty] | 6731 | 10 | 8 | 3 | 11 | 48 | 48
[25 empty] | 6732 | 10 | 8 | 3 | 12 | 50 | 50
[25 empty] | 6733 | 10 | 8 | 3 | 13 | 52 | 52
[25 empty] | 6734 | 10 | 8 | 3 | 14 | 53.1 | 53
[25 empty] | 6735 | 10 | 8 | 3 | 15 | 54 | 54
[25 empty] | 6736 | 10 | 8 | 3 | 16 | 53.1 | 53
[25 empty] | 6737 | 10 | 8 | 3 | 17 | 54 | 54
[25 empty] | 6738 | 10 | 8 | 3 | 18 | 52 | 52
[25 empty] | 6739 | 10 | 8 | 3 | 19 | 52 | 52
[25 empty] | 6740 | 10 | 8 | 3 | 20 | 51.1 | 51
[25 empty] | 6741 | 10 | 8 | 3 | 21 | 50 | 50
[25 empty] | 6742 | 10 | 8 | 3 | 22 | 48.9 | 49
[25 empty] | 6743 | 10 | 8 | 3 | 23 | 48.9 | 49
[25 empty] | 6744 | 10 | 9 | 4 | 0 | 48 | 48
[25 empty] | 6745 | 10 | 9 | 4 | 1 | 48 | 48
[25 empty] | 6746 | 10 | 9 | 4 | 2 | 46.9 | 47
[25 empty] | 6747 | 10 | 9 | 4 | 3 | 44.1 | 44
[25 empty] | 6748 | 10 | 9 | 4 | 4 | 46 | 46
[25 empty] | 6749 | 10 | 9 | 4 | 5 | 46 | 46
[25 empty] | 6750 | 10 | 9 | 4 | 6 | 45 | 45
[25 empty] | 6751 | 10 | 9 | 4 | 7 | 46 | 46
[25 empty] | 6752 | 10 | 9 | 4 | 8 | 48.9 | 49
[25 empty] | 6753 | 10 | 9 | 4 | 9 | 52 | 52
[25 empty] | 6754 | 10 | 9 | 4 | 10 | 53.1 | 53
[25 empty] | 6755 | 10 | 9 | 4 | 11 | 55 | 55
[25 empty] | 6756 | 10 | 9 | 4 | 12 | 57 | 57
[25 empty] | 6757 | 10 | 9 | 4 | 13 | 59 | 59
[25 empty] | 6758 | 10 | 9 | 4 | 14 | 60.1 | 60
[25 empty] | 6759 | 10 | 9 | 4 | 15 | 60.1 | 60
[25 empty] | 6760 | 10 | 9 | 4 | 16 | 59 | 59
[25 empty] | 6761 | 10 | 9 | 4 | 17 | 57.9 | 58
[25 empty] | 6762 | 10 | 9 | 4 | 18 | 57.9 | 58
[25 empty] | 6763 | 10 | 9 | 4 | 19 | 57.9 | 58
[25 empty] | 6764 | 10 | 9 | 4 | 20 | 57.9 | 58
[25 empty] | 6765 | 10 | 9 | 4 | 21 | 55.9 | 56
[25 empty] | 6766 | 10 | 9 | 4 | 22 | 55.9 | 56
[25 empty] | 6767 | 10 | 9 | 4 | 23 | 54 | 54
[25 empty] | 6768 | 10 | 10 | 5 | 0 | 54 | 54
[25 empty] | 6769 | 10 | 10 | 5 | 1 | 53.1 | 53
[25 empty] | 6770 | 10 | 10 | 5 | 2 | 54 | 54
[25 empty] | 6771 | 10 | 10 | 5 | 3 | 53.1 | 53
[25 empty] | 6772 | 10 | 10 | 5 | 4 | 52 | 52
[25 empty] | 6773 | 10 | 10 | 5 | 5 | 51.1 | 51
[25 empty] | 6774 | 10 | 10 | 5 | 6 | 51.1 | 51
[25 empty] | 6775 | 10 | 10 | 5 | 7 | 52 | 52
[25 empty] | 6776 | 10 | 10 | 5 | 8 | 55 | 55
[25 empty] | 6777 | 10 | 10 | 5 | 9 | 57 | 57
[25 empty] | 6778 | 10 | 10 | 5 | 10 | 59 | 59
[25 empty] | 6779 | 10 | 10 | 5 | 11 | 62.1 | 62
[25 empty] | 6780 | 10 | 10 | 5 | 12 | 64 | 64
[25 empty] | 6781 | 10 | 10 | 5 | 13 | 66 | 66
[25 empty] | 6782 | 10 | 10 | 5 | 14 | 68 | 68
[25 empty] | 6783 | 10 | 10 | 5 | 15 | 68 | 68
[25 empty] | 6784 | 10 | 10 | 5 | 16 | 69.1 | 69
[25 empty] | 6785 | 10 | 10 | 5 | 17 | 68 | 68
[25 empty] | 6786 | 10 | 10 | 5 | 18 | 64.9 | 65
[25 empty] | 6787 | 10 | 10 | 5 | 19 | 64.9 | 65
[25 empty] | 6788 | 10 | 10 | 5 | 20 | 64 | 64
[25 empty] | 6789 | 10 | 10 | 5 | 21 | 62.1 | 62
[25 empty] | 6790 | 10 | 10 | 5 | 22 | 61 | 61
[25 empty] | 6791 | 10 | 10 | 5 | 23 | 60.1 | 60
[25 empty] | 6792 | 10 | 11 | 6 | 0 | 59 | 59
[25 empty] | 6793 | 10 | 11 | 6 | 1 | 59 | 59
[25 empty] | 6794 | 10 | 11 | 6 | 2 | 59 | 59
[25 empty] | 6795 | 10 | 11 | 6 | 3 | 59 | 59
[25 empty] | 6796 | 10 | 11 | 6 | 4 | 57.9 | 58
[25 empty] | 6797 | 10 | 11 | 6 | 5 | 57 | 57
[25 empty] | 6798 | 10 | 11 | 6 | 6 | 57 | 57
[25 empty] | 6799 | 10 | 11 | 6 | 7 | 57.9 | 58
[25 empty] | 6800 | 10 | 11 | 6 | 8 | 60.1 | 60
[25 empty] | 6801 | 10 | 11 | 6 | 9 | 62.1 | 62
[25 empty] | 6802 | 10 | 11 | 6 | 10 | 64.9 | 65
[25 empty] | 6803 | 10 | 11 | 6 | 11 | 68 | 68
[25 empty] | 6804 | 10 | 11 | 6 | 12 | 70 | 70
[25 empty] | 6805 | 10 | 11 | 6 | 13 | 72 | 72
[25 empty] | 6806 | 10 | 11 | 6 | 14 | 73.9 | 74
[25 empty] | 6807 | 10 | 11 | 6 | 15 | 71.1 | 71
[25 empty] | 6808 | 10 | 11 | 6 | 16 | 71.1 | 71
[25 empty] | 6809 | 10 | 11 | 6 | 17 | 68 | 68
[25 empty] | 6810 | 10 | 11 | 6 | 18 | 66.9 | 67
[25 empty] | 6811 | 10 | 11 | 6 | 19 | 66 | 66
[25 empty] | 6812 | 10 | 11 | 6 | 20 | 66.9 | 67
[25 empty] | 6813 | 10 | 11 | 6 | 21 | 66 | 66
[25 empty] | 6814 | 10 | 11 | 6 | 22 | 66 | 66
[25 empty] | 6815 | 10 | 11 | 6 | 23 | 64.9 | 65
[25 empty] | 6816 | 10 | 12 | 7 | 0 | 63 | 63
[25 empty] | 6817 | 10 | 12 | 7 | 1 | 62.1 | 62
[25 empty] | 6818 | 10 | 12 | 7 | 2 | 62.1 | 62
[25 empty] | 6819 | 10 | 12 | 7 | 3 | 62.1 | 62
[25 empty] | 6820 | 10 | 12 | 7 | 4 | 60.1 | 60
[25 empty] | 6821 | 10 | 12 | 7 | 5 | 60.1 | 60
[25 empty] | 6822 | 10 | 12 | 7 | 6 | 60.1 | 60
[25 empty] | 6823 | 10 | 12 | 7 | 7 | 60.1 | 60
[25 empty] | 6824 | 10 | 12 | 7 | 8 | 63 | 63
[25 empty] | 6825 | 10 | 12 | 7 | 9 | 66 | 66
[25 empty] | 6826 | 10 | 12 | 7 | 10 | 68 | 68
[25 empty] | 6827 | 10 | 12 | 7 | 11 | 71.1 | 71
[25 empty] | 6828 | 10 | 12 | 7 | 12 | 73.9 | 74
[25 empty] | 6829 | 10 | 12 | 7 | 13 | 75 | 75
[25 empty] | 6830 | 10 | 12 | 7 | 14 | 75 | 75
[25 empty] | 6831 | 10 | 12 | 7 | 15 | 75.9 | 76
[25 empty] | 6832 | 10 | 12 | 7 | 16 | 71.1 | 71
[25 empty] | 6833 | 10 | 12 | 7 | 17 | 69.1 | 69
[25 empty] | 6834 | 10 | 12 | 7 | 18 | 66.9 | 67
[25 empty] | 6835 | 10 | 12 | 7 | 19 | 66.9 | 67
[25 empty] | 6836 | 10 | 12 | 7 | 20 | 66.9 | 67
[25 empty] | 6837 | 10 | 12 | 7 | 21 | 66 | 66
[25 empty] | 6838 | 10 | 12 | 7 | 22 | 64.9 | 65
[25 empty] | 6839 | 10 | 12 | 7 | 23 | 64.9 | 65
[25 empty] | 6840 | 10 | 13 | 1 | 0 | 66 | 66
[25 empty] | 6841 | 10 | 13 | 1 | 1 | 66 | 66
[25 empty] | 6842 | 10 | 13 | 1 | 2 | 64.9 | 65
[25 empty] | 6843 | 10 | 13 | 1 | 3 | 64 | 64
[25 empty] | 6844 | 10 | 13 | 1 | 4 | 63 | 63
[25 empty] | 6845 | 10 | 13 | 1 | 5 | 64 | 64
[25 empty] | 6846 | 10 | 13 | 1 | 6 | 63 | 63
[25 empty] | 6847 | 10 | 13 | 1 | 7 | 63 | 63
[25 empty] | 6848 | 10 | 13 | 1 | 8 | 64.9 | 65
[25 empty] | 6849 | 10 | 13 | 1 | 9 | 64.9 | 65
[25 empty] | 6850 | 10 | 13 | 1 | 10 | 66.9 | 67
[25 empty] | 6851 | 10 | 13 | 1 | 11 | 69.1 | 69
[25 empty] | 6852 | 10 | 13 | 1 | 12 | 70 | 70
[25 empty] | 6853 | 10 | 13 | 1 | 13 | 72 | 72
[25 empty] | 6854 | 10 | 13 | 1 | 14 | 73 | 73
[25 empty] | 6855 | 10 | 13 | 1 | 15 | 73.9 | 74
[25 empty] | 6856 | 10 | 13 | 1 | 16 | 72 | 72
[25 empty] | 6857 | 10 | 13 | 1 | 17 | 69.1 | 69
[25 empty] | 6858 | 10 | 13 | 1 | 18 | 66 | 66
[25 empty] | 6859 | 10 | 13 | 1 | 19 | 63 | 63
[25 empty] | 6860 | 10 | 13 | 1 | 20 | 62.6 | 63
[25 empty] | 6861 | 10 | 13 | 1 | 21 | 62.1 | 62
[25 empty] | 6862 | 10 | 13 | 1 | 22 | 61 | 61
[25 empty] | 6863 | 10 | 13 | 1 | 23 | 61 | 61
[25 empty] | 6864 | 10 | 14 | 2 | 0 | 61 | 61
[25 empty] | 6865 | 10 | 14 | 2 | 1 | 61 | 61
[25 empty] | 6866 | 10 | 14 | 2 | 2 | 60.1 | 60
[25 empty] | 6867 | 10 | 14 | 2 | 3 | 60.1 | 60
[25 empty] | 6868 | 10 | 14 | 2 | 4 | 59 | 59
[25 empty] | 6869 | 10 | 14 | 2 | 5 | 57.9 | 58
[25 empty] | 6870 | 10 | 14 | 2 | 6 | 57.9 | 58
[25 empty] | 6871 | 10 | 14 | 2 | 7 | 57.9 | 58
[25 empty] | 6872 | 10 | 14 | 2 | 8 | 57.9 | 58
[25 empty] | 6873 | 10 | 14 | 2 | 9 | 59 | 59
[25 empty] | 6874 | 10 | 14 | 2 | 10 | 61 | 61
[25 empty] | 6875 | 10 | 14 | 2 | 11 | 63 | 63
[25 empty] | 6876 | 10 | 14 | 2 | 12 | 64 | 64
[25 empty] | 6877 | 10 | 14 | 2 | 13 | 64.9 | 65
[25 empty] | 6878 | 10 | 14 | 2 | 14 | 66 | 66
[25 empty] | 6879 | 10 | 14 | 2 | 15 | 66.9 | 67
[25 empty] | 6880 | 10 | 14 | 2 | 16 | 64.4 | 64
[25 empty] | 6881 | 10 | 14 | 2 | 17 | 64 | 64
[25 empty] | 6882 | 10 | 14 | 2 | 18 | 63 | 63
[25 empty] | 6883 | 10 | 14 | 2 | 19 | 63 | 63
[25 empty] | 6884 | 10 | 14 | 2 | 20 | 62.6 | 63
[25 empty] | 6885 | 10 | 14 | 2 | 21 | 63 | 63
[25 empty] | 6886 | 10 | 14 | 2 | 22 | 64 | 64
[25 empty] | 6887 | 10 | 14 | 2 | 23 | 64 | 64
[25 empty] | 6888 | 10 | 15 | 3 | 0 | 64 | 64
[25 empty] | 6889 | 10 | 15 | 3 | 1 | 64.9 | 65
[25 empty] | 6890 | 10 | 15 | 3 | 2 | 66 | 66
[25 empty] | 6891 | 10 | 15 | 3 | 3 | 66 | 66
[25 empty] | 6892 | 10 | 15 | 3 | 4 | 62.1 | 62
[25 empty] | 6893 | 10 | 15 | 3 | 5 | 62.1 | 62
[25 empty] | 6894 | 10 | 15 | 3 | 6 | 61 | 61
[25 empty] | 6895 | 10 | 15 | 3 | 7 | 60.1 | 60
[25 empty] | 6896 | 10 | 15 | 3 | 8 | 60.1 | 60
[25 empty] | 6897 | 10 | 15 | 3 | 9 | 62.1 | 62
[25 empty] | 6898 | 10 | 15 | 3 | 10 | 64 | 64
[25 empty] | 6899 | 10 | 15 | 3 | 11 | 66 | 66
[25 empty] | 6900 | 10 | 15 | 3 | 12 | 68 | 68
[25 empty] | 6901 | 10 | 15 | 3 | 13 | 68 | 68
[25 empty] | 6902 | 10 | 15 | 3 | 14 | 69.1 | 69
[25 empty] | 6903 | 10 | 15 | 3 | 15 | 69.1 | 69
[25 empty] | 6904 | 10 | 15 | 3 | 16 | 68 | 68
[25 empty] | 6905 | 10 | 15 | 3 | 17 | 66.9 | 67
[25 empty] | 6906 | 10 | 15 | 3 | 18 | 66 | 66
[25 empty] | 6907 | 10 | 15 | 3 | 19 | 64.9 | 65
[25 empty] | 6908 | 10 | 15 | 3 | 20 | 64 | 64
[25 empty] | 6909 | 10 | 15 | 3 | 21 | 63 | 63
[25 empty] | 6910 | 10 | 15 | 3 | 22 | 62.1 | 62
[25 empty] | 6911 | 10 | 15 | 3 | 23 | 61 | 61
[25 empty] | 6912 | 10 | 16 | 4 | 0 | 60.1 | 60
[25 empty] | 6913 | 10 | 16 | 4 | 1 | 59 | 59
[25 empty] | 6914 | 10 | 16 | 4 | 2 | 57 | 57
[25 empty] | 6915 | 10 | 16 | 4 | 3 | 55.9 | 56
[25 empty] | 6916 | 10 | 16 | 4 | 4 | 55.9 | 56
[25 empty] | 6917 | 10 | 16 | 4 | 5 | 55 | 55
[25 empty] | 6918 | 10 | 16 | 4 | 6 | 55.9 | 56
[25 empty] | 6919 | 10 | 16 | 4 | 7 | 55.9 | 56
[25 empty] | 6920 | 10 | 16 | 4 | 8 | 59 | 59
[25 empty] | 6921 | 10 | 16 | 4 | 9 | 63 | 63
[25 empty] | 6922 | 10 | 16 | 4 | 10 | 64.9 | 65
[25 empty] | 6923 | 10 | 16 | 4 | 11 | 64.9 | 65
[25 empty] | 6924 | 10 | 16 | 4 | 12 | 66.9 | 67
[25 empty] | 6925 | 10 | 16 | 4 | 13 | 68 | 68
[25 empty] | 6926 | 10 | 16 | 4 | 14 | 68 | 68
[25 empty] | 6927 | 10 | 16 | 4 | 15 | 68 | 68
[25 empty] | 6928 | 10 | 16 | 4 | 16 | 68 | 68
[25 empty] | 6929 | 10 | 16 | 4 | 17 | 66 | 66
[25 empty] | 6930 | 10 | 16 | 4 | 18 | 64 | 64
[25 empty] | 6931 | 10 | 16 | 4 | 19 | 64 | 64
[25 empty] | 6932 | 10 | 16 | 4 | 20 | 63 | 63
[25 empty] | 6933 | 10 | 16 | 4 | 21 | 63 | 63
[25 empty] | 6934 | 10 | 16 | 4 | 22 | 57 | 57
[25 empty] | 6935 | 10 | 16 | 4 | 23 | 53.1 | 53
[25 empty] | 6936 | 10 | 17 | 5 | 0 | 52 | 52
[25 empty] | 6937 | 10 | 17 | 5 | 1 | 52 | 52
[25 empty] | 6938 | 10 | 17 | 5 | 2 | 52 | 52
[25 empty] | 6939 | 10 | 17 | 5 | 3 | 52 | 52
[25 empty] | 6940 | 10 | 17 | 5 | 4 | 50 | 50
[25 empty] | 6941 | 10 | 17 | 5 | 5 | 50 | 50
[25 empty] | 6942 | 10 | 17 | 5 | 6 | 51.1 | 51
[25 empty] | 6943 | 10 | 17 | 5 | 7 | 51.1 | 51
[25 empty] | 6944 | 10 | 17 | 5 | 8 | 52 | 52
[25 empty] | 6945 | 10 | 17 | 5 | 9 | 53.1 | 53
[25 empty] | 6946 | 10 | 17 | 5 | 10 | 55.9 | 56
[25 empty] | 6947 | 10 | 17 | 5 | 11 | 57 | 57
[25 empty] | 6948 | 10 | 17 | 5 | 12 | 57 | 57
[25 empty] | 6949 | 10 | 17 | 5 | 13 | 57.9 | 58
[25 empty] | 6950 | 10 | 17 | 5 | 14 | 57.9 | 58
[25 empty] | 6951 | 10 | 17 | 5 | 15 | 57 | 57
[25 empty] | 6952 | 10 | 17 | 5 | 16 | 55.9 | 56
[25 empty] | 6953 | 10 | 17 | 5 | 17 | 55 | 55
[25 empty] | 6954 | 10 | 17 | 5 | 18 | 54 | 54
[25 empty] | 6955 | 10 | 17 | 5 | 19 | 52 | 52
[25 empty] | 6956 | 10 | 17 | 5 | 20 | 52 | 52
[25 empty] | 6957 | 10 | 17 | 5 | 21 | 51.1 | 51
[25 empty] | 6958 | 10 | 17 | 5 | 22 | 50 | 50
[25 empty] | 6959 | 10 | 17 | 5 | 23 | 50 | 50
[25 empty] | 6960 | 10 | 18 | 6 | 0 | 48 | 48
[25 empty] | 6961 | 10 | 18 | 6 | 1 | 46.9 | 47
[25 empty] | 6962 | 10 | 18 | 6 | 2 | 46.9 | 47
[25 empty] | 6963 | 10 | 18 | 6 | 3 | 46 | 46
[25 empty] | 6964 | 10 | 18 | 6 | 4 | 45 | 45
[25 empty] | 6965 | 10 | 18 | 6 | 5 | 45 | 45
[25 empty] | 6966 | 10 | 18 | 6 | 6 | 44.1 | 44
[25 empty] | 6967 | 10 | 18 | 6 | 7 | 44.1 | 44
[25 empty] | 6968 | 10 | 18 | 6 | 8 | 45 | 45
[25 empty] | 6969 | 10 | 18 | 6 | 9 | 46.9 | 47
[25 empty] | 6970 | 10 | 18 | 6 | 10 | 50 | 50
[25 empty] | 6971 | 10 | 18 | 6 | 11 | 51.1 | 51
[25 empty] | 6972 | 10 | 18 | 6 | 12 | 52 | 52
[25 empty] | 6973 | 10 | 18 | 6 | 13 | 55 | 55
[25 empty] | 6974 | 10 | 18 | 6 | 14 | 55.9 | 56
[25 empty] | 6975 | 10 | 18 | 6 | 15 | 57 | 57
[25 empty] | 6976 | 10 | 18 | 6 | 16 | 57 | 57
[25 empty] | 6977 | 10 | 18 | 6 | 17 | 57 | 57
[25 empty] | 6978 | 10 | 18 | 6 | 18 | 55.9 | 56
[25 empty] | 6979 | 10 | 18 | 6 | 19 | 55 | 55
[25 empty] | 6980 | 10 | 18 | 6 | 20 | 54 | 54
[25 empty] | 6981 | 10 | 18 | 6 | 21 | 53.1 | 53
[25 empty] | 6982 | 10 | 18 | 6 | 22 | 53.1 | 53
[25 empty] | 6983 | 10 | 18 | 6 | 23 | 51.1 | 51
[25 empty] | 6984 | 10 | 19 | 7 | 0 | 50 | 50
[25 empty] | 6985 | 10 | 19 | 7 | 1 | 50 | 50
[25 empty] | 6986 | 10 | 19 | 7 | 2 | 46.9 | 47
[25 empty] | 6987 | 10 | 19 | 7 | 3 | 48 | 48
[25 empty] | 6988 | 10 | 19 | 7 | 4 | 46.9 | 47
[25 empty] | 6989 | 10 | 19 | 7 | 5 | 48 | 48
[25 empty] | 6990 | 10 | 19 | 7 | 6 | 48 | 48
[25 empty] | 6991 | 10 | 19 | 7 | 7 | 48.9 | 49
[25 empty] | 6992 | 10 | 19 | 7 | 8 | 51.1 | 51
[25 empty] | 6993 | 10 | 19 | 7 | 9 | 55 | 55
[25 empty] | 6994 | 10 | 19 | 7 | 10 | 55.9 | 56
[25 empty] | 6995 | 10 | 19 | 7 | 11 | 57.9 | 58
[25 empty] | 6996 | 10 | 19 | 7 | 12 | 60.1 | 60
[25 empty] | 6997 | 10 | 19 | 7 | 13 | 62.1 | 62
[25 empty] | 6998 | 10 | 19 | 7 | 14 | 62.1 | 62
[25 empty] | 6999 | 10 | 19 | 7 | 15 | 61 | 61
[25 empty] | 7000 | 10 | 19 | 7 | 16 | 60.1 | 60
[25 empty] | 7001 | 10 | 19 | 7 | 17 | 59 | 59
[25 empty] | 7002 | 10 | 19 | 7 | 18 | 59 | 59
[25 empty] | 7003 | 10 | 19 | 7 | 19 | 57.9 | 58
[25 empty] | 7004 | 10 | 19 | 7 | 20 | 57 | 57
[25 empty] | 7005 | 10 | 19 | 7 | 21 | 57 | 57
[25 empty] | 7006 | 10 | 19 | 7 | 22 | 57 | 57
[25 empty] | 7007 | 10 | 19 | 7 | 23 | 55.9 | 56
[25 empty] | 7008 | 10 | 20 | 1 | 0 | 55.9 | 56
[25 empty] | 7009 | 10 | 20 | 1 | 1 | 55 | 55
[25 empty] | 7010 | 10 | 20 | 1 | 2 | 55 | 55
[25 empty] | 7011 | 10 | 20 | 1 | 3 | 55 | 55
[25 empty] | 7012 | 10 | 20 | 1 | 4 | 54 | 54
[25 empty] | 7013 | 10 | 20 | 1 | 5 | 53.1 | 53
[25 empty] | 7014 | 10 | 20 | 1 | 6 | 53.1 | 53
[25 empty] | 7015 | 10 | 20 | 1 | 7 | 53.1 | 53
[25 empty] | 7016 | 10 | 20 | 1 | 8 | 55.9 | 56
[25 empty] | 7017 | 10 | 20 | 1 | 9 | 57 | 57
[25 empty] | 7018 | 10 | 20 | 1 | 10 | 59 | 59
[25 empty] | 7019 | 10 | 20 | 1 | 11 | 62.1 | 62
[25 empty] | 7020 | 10 | 20 | 1 | 12 | 66 | 66
[25 empty] | 7021 | 10 | 20 | 1 | 13 | 68 | 68
[25 empty] | 7022 | 10 | 20 | 1 | 14 | 70 | 70
[25 empty] | 7023 | 10 | 20 | 1 | 15 | 71.1 | 71
[25 empty] | 7024 | 10 | 20 | 1 | 16 | 70 | 70
[25 empty] | 7025 | 10 | 20 | 1 | 17 | 69.1 | 69
[25 empty] | 7026 | 10 | 20 | 1 | 18 | 69.1 | 69
[25 empty] | 7027 | 10 | 20 | 1 | 19 | 68 | 68
[25 empty] | 7028 | 10 | 20 | 1 | 20 | 66 | 66
[25 empty] | 7029 | 10 | 20 | 1 | 21 | 64 | 64
[25 empty] | 7030 | 10 | 20 | 1 | 22 | 62.1 | 62
[25 empty] | 7031 | 10 | 20 | 1 | 23 | 60.1 | 60
[25 empty] | 7032 | 10 | 21 | 2 | 0 | 60.1 | 60
[25 empty] | 7033 | 10 | 21 | 2 | 1 | 60.1 | 60
[25 empty] | 7034 | 10 | 21 | 2 | 2 | 60.1 | 60
[25 empty] | 7035 | 10 | 21 | 2 | 3 | 59 | 59
[25 empty] | 7036 | 10 | 21 | 2 | 4 | 57.9 | 58
[25 empty] | 7037 | 10 | 21 | 2 | 5 | 57 | 57
[25 empty] | 7038 | 10 | 21 | 2 | 6 | 55.9 | 56
[25 empty] | 7039 | 10 | 21 | 2 | 7 | 57 | 57
[25 empty] | 7040 | 10 | 21 | 2 | 8 | 59 | 59
[25 empty] | 7041 | 10 | 21 | 2 | 9 | 63 | 63
[25 empty] | 7042 | 10 | 21 | 2 | 10 | 66.9 | 67
[25 empty] | 7043 | 10 | 21 | 2 | 11 | 70 | 70
[25 empty] | 7044 | 10 | 21 | 2 | 12 | 71.1 | 71
[25 empty] | 7045 | 10 | 21 | 2 | 13 | 70 | 70
[25 empty] | 7046 | 10 | 21 | 2 | 14 | 71.1 | 71
[25 empty] | 7047 | 10 | 21 | 2 | 15 | 70 | 70
[25 empty] | 7048 | 10 | 21 | 2 | 16 | 70 | 70
[25 empty] | 7049 | 10 | 21 | 2 | 17 | 69.1 | 69
[25 empty] | 7050 | 10 | 21 | 2 | 18 | 66.9 | 67
[25 empty] | 7051 | 10 | 21 | 2 | 19 | 68 | 68
[25 empty] | 7052 | 10 | 21 | 2 | 20 | 66.9 | 67
[25 empty] | 7053 | 10 | 21 | 2 | 21 | 66 | 66
[25 empty] | 7054 | 10 | 21 | 2 | 22 | 64 | 64
[25 empty] | 7055 | 10 | 21 | 2 | 23 | 64 | 64
[25 empty] | 7056 | 10 | 22 | 3 | 0 | 64 | 64
[25 empty] | 7057 | 10 | 22 | 3 | 1 | 63 | 63
[25 empty] | 7058 | 10 | 22 | 3 | 2 | 63 | 63
[25 empty] | 7059 | 10 | 22 | 3 | 3 | 62.1 | 62
[25 empty] | 7060 | 10 | 22 | 3 | 4 | 62.1 | 62
[25 empty] | 7061 | 10 | 22 | 3 | 5 | 61 | 61
[25 empty] | 7062 | 10 | 22 | 3 | 6 | 60.1 | 60
[25 empty] | 7063 | 10 | 22 | 3 | 7 | 62.1 | 62
[25 empty] | 7064 | 10 | 22 | 3 | 8 | 62.1 | 62
[25 empty] | 7065 | 10 | 22 | 3 | 9 | 64 | 64
[25 empty] | 7066 | 10 | 22 | 3 | 10 | 64.9 | 65
[25 empty] | 7067 | 10 | 22 | 3 | 11 | 66 | 66
[25 empty] | 7068 | 10 | 22 | 3 | 12 | 68 | 68
[25 empty] | 7069 | 10 | 22 | 3 | 13 | 69.1 | 69
[25 empty] | 7070 | 10 | 22 | 3 | 14 | 70 | 70
[25 empty] | 7071 | 10 | 22 | 3 | 15 | 70 | 70
[25 empty] | 7072 | 10 | 22 | 3 | 16 | 69.1 | 69
[25 empty] | 7073 | 10 | 22 | 3 | 17 | 69.1 | 69
[25 empty] | 7074 | 10 | 22 | 3 | 18 | 66.9 | 67
[25 empty] | 7075 | 10 | 22 | 3 | 19 | 64 | 64
[25 empty] | 7076 | 10 | 22 | 3 | 20 | 63 | 63
[25 empty] | 7077 | 10 | 22 | 3 | 21 | 62.1 | 62
[25 empty] | 7078 | 10 | 22 | 3 | 22 | 61 | 61
[25 empty] | 7079 | 10 | 22 | 3 | 23 | 61 | 61
[25 empty] | 7080 | 10 | 23 | 4 | 0 | 60.1 | 60
[25 empty] | 7081 | 10 | 23 | 4 | 1 | 59 | 59
[25 empty] | 7082 | 10 | 23 | 4 | 2 | 59 | 59
[25 empty] | 7083 | 10 | 23 | 4 | 3 | 57.9 | 58
[25 empty] | 7084 | 10 | 23 | 4 | 4 | 57.9 | 58
[25 empty] | 7085 | 10 | 23 | 4 | 5 | 59 | 59
[25 empty] | 7086 | 10 | 23 | 4 | 6 | 57.9 | 58
[25 empty] | 7087 | 10 | 23 | 4 | 7 | 59 | 59
[25 empty] | 7088 | 10 | 23 | 4 | 8 | 61 | 61
[25 empty] | 7089 | 10 | 23 | 4 | 9 | 62.1 | 62
[25 empty] | 7090 | 10 | 23 | 4 | 10 | 63 | 63
[25 empty] | 7091 | 10 | 23 | 4 | 11 | 64.4 | 64
[25 empty] | 7092 | 10 | 23 | 4 | 12 | 64.9 | 65
[25 empty] | 7093 | 10 | 23 | 4 | 13 | 66 | 66
[25 empty] | 7094 | 10 | 23 | 4 | 14 | 66.9 | 67
[25 empty] | 7095 | 10 | 23 | 4 | 15 | 66.9 | 67
[25 empty] | 7096 | 10 | 23 | 4 | 16 | 66 | 66
[25 empty] | 7097 | 10 | 23 | 4 | 17 | 64.9 | 65
[25 empty] | 7098 | 10 | 23 | 4 | 18 | 64.4 | 64
[25 empty] | 7099 | 10 | 23 | 4 | 19 | 64 | 64
[25 empty] | 7100 | 10 | 23 | 4 | 20 | 64.4 | 64
[25 empty] | 7101 | 10 | 23 | 4 | 21 | 64.9 | 65
[25 empty] | 7102 | 10 | 23 | 4 | 22 | 66 | 66
[25 empty] | 7103 | 10 | 23 | 4 | 23 | 66 | 66
[25 empty] | 7104 | 10 | 24 | 5 | 0 | 64.9 | 65
[25 empty] | 7105 | 10 | 24 | 5 | 1 | 64 | 64
[25 empty] | 7106 | 10 | 24 | 5 | 2 | 64 | 64
[25 empty] | 7107 | 10 | 24 | 5 | 3 | 64.9 | 65
[25 empty] | 7108 | 10 | 24 | 5 | 4 | 66 | 66
[25 empty] | 7109 | 10 | 24 | 5 | 5 | 64.9 | 65
[25 empty] | 7110 | 10 | 24 | 5 | 6 | 64 | 64
[25 empty] | 7111 | 10 | 24 | 5 | 7 | 64 | 64
[25 empty] | 7112 | 10 | 24 | 5 | 8 | 66 | 66
[25 empty] | 7113 | 10 | 24 | 5 | 9 | 69.1 | 69
[25 empty] | 7114 | 10 | 24 | 5 | 10 | 71.1 | 71
[25 empty] | 7115 | 10 | 24 | 5 | 11 | 73.9 | 74
[25 empty] | 7116 | 10 | 24 | 5 | 12 | 75.9 | 76
[25 empty] | 7117 | 10 | 24 | 5 | 13 | 78.1 | 78
[25 empty] | 7118 | 10 | 24 | 5 | 14 | 79 | 79
[25 empty] | 7119 | 10 | 24 | 5 | 15 | 77 | 77
[25 empty] | 7120 | 10 | 24 | 5 | 16 | 75 | 75
[25 empty] | 7121 | 10 | 24 | 5 | 17 | 72 | 72
[25 empty] | 7122 | 10 | 24 | 5 | 18 | 69.1 | 69
[25 empty] | 7123 | 10 | 24 | 5 | 19 | 68 | 68
[25 empty] | 7124 | 10 | 24 | 5 | 20 | 69.1 | 69
[25 empty] | 7125 | 10 | 24 | 5 | 21 | 68 | 68
[25 empty] | 7126 | 10 | 24 | 5 | 22 | 68 | 68
[25 empty] | 7127 | 10 | 24 | 5 | 23 | 66.9 | 67
[25 empty] | 7128 | 10 | 25 | 6 | 0 | 66 | 66
[25 empty] | 7129 | 10 | 25 | 6 | 1 | 66 | 66
[25 empty] | 7130 | 10 | 25 | 6 | 2 | 64.4 | 64
[25 empty] | 7131 | 10 | 25 | 6 | 3 | 64 | 64
[25 empty] | 7132 | 10 | 25 | 6 | 4 | 63 | 63
[25 empty] | 7133 | 10 | 25 | 6 | 5 | 64 | 64
[25 empty] | 7134 | 10 | 25 | 6 | 6 | 64.4 | 64
[25 empty] | 7135 | 10 | 25 | 6 | 7 | 64.9 | 65
[25 empty] | 7136 | 10 | 25 | 6 | 8 | 68 | 68
[25 empty] | 7137 | 10 | 25 | 6 | 9 | 73 | 73
[25 empty] | 7138 | 10 | 25 | 6 | 10 | 75.9 | 76
[25 empty] | 7139 | 10 | 25 | 6 | 11 | 78.1 | 78
[25 empty] | 7140 | 10 | 25 | 6 | 12 | 75 | 75
[25 empty] | 7141 | 10 | 25 | 6 | 13 | 73.9 | 74
[25 empty] | 7142 | 10 | 25 | 6 | 14 | 75 | 75
[25 empty] | 7143 | 10 | 25 | 6 | 15 | 73.9 | 74
[25 empty] | 7144 | 10 | 25 | 6 | 16 | 72 | 72
[25 empty] | 7145 | 10 | 25 | 6 | 17 | 69.1 | 69
[25 empty] | 7146 | 10 | 25 | 6 | 18 | 68 | 68
[25 empty] | 7147 | 10 | 25 | 6 | 19 | 66.9 | 67
[25 empty] | 7148 | 10 | 25 | 6 | 20 | 66 | 66
[25 empty] | 7149 | 10 | 25 | 6 | 21 | 64 | 64
[25 empty] | 7150 | 10 | 25 | 6 | 22 | 63 | 63
[25 empty] | 7151 | 10 | 25 | 6 | 23 | 61 | 61
[25 empty] | 7152 | 10 | 26 | 7 | 0 | 60.1 | 60
[25 empty] | 7153 | 10 | 26 | 7 | 1 | 60.1 | 60
[25 empty] | 7154 | 10 | 26 | 7 | 2 | 57.9 | 58
[25 empty] | 7155 | 10 | 26 | 7 | 3 | 57.9 | 58
[25 empty] | 7156 | 10 | 26 | 7 | 4 | 55.9 | 56
[25 empty] | 7157 | 10 | 26 | 7 | 5 | 55 | 55
[25 empty] | 7158 | 10 | 26 | 7 | 6 | 54 | 54
[25 empty] | 7159 | 10 | 26 | 7 | 7 | 54 | 54
[25 empty] | 7160 | 10 | 26 | 7 | 8 | 54 | 54
[25 empty] | 7161 | 10 | 26 | 7 | 9 | 55 | 55
[25 empty] | 7162 | 10 | 26 | 7 | 10 | 55.9 | 56
[25 empty] | 7163 | 10 | 26 | 7 | 11 | 57 | 57
[25 empty] | 7164 | 10 | 26 | 7 | 12 | 55.9 | 56
[25 empty] | 7165 | 10 | 26 | 7 | 13 | 55 | 55
[25 empty] | 7166 | 10 | 26 | 7 | 14 | 55.9 | 56
[25 empty] | 7167 | 10 | 26 | 7 | 15 | 55 | 55
[25 empty] | 7168 | 10 | 26 | 7 | 16 | 54 | 54
[25 empty] | 7169 | 10 | 26 | 7 | 17 | 52 | 52
[25 empty] | 7170 | 10 | 26 | 7 | 18 | 51.1 | 51
[25 empty] | 7171 | 10 | 26 | 7 | 19 | 50 | 50
[25 empty] | 7172 | 10 | 26 | 7 | 20 | 48.9 | 49
[25 empty] | 7173 | 10 | 26 | 7 | 21 | 46.9 | 47
[25 empty] | 7174 | 10 | 26 | 7 | 22 | 46 | 46
[25 empty] | 7175 | 10 | 26 | 7 | 23 | 45 | 45
[25 empty] | 7176 | 10 | 27 | 1 | 0 | 45 | 45
[25 empty] | 7177 | 10 | 27 | 1 | 1 | 44.1 | 44
[25 empty] | 7178 | 10 | 27 | 1 | 2 | 44.1 | 44
[25 empty] | 7179 | 10 | 27 | 1 | 3 | 44.1 | 44
[25 empty] | 7180 | 10 | 27 | 1 | 4 | 44.1 | 44
[25 empty] | 7181 | 10 | 27 | 1 | 5 | 44.1 | 44
[25 empty] | 7182 | 10 | 27 | 1 | 6 | 44.1 | 44
[25 empty] | 7183 | 10 | 27 | 1 | 7 | 44.1 | 44
[25 empty] | 7184 | 10 | 27 | 1 | 8 | 45 | 45
[25 empty] | 7185 | 10 | 27 | 1 | 9 | 46.9 | 47
[25 empty] | 7186 | 10 | 27 | 1 | 10 | 48.9 | 49
[25 empty] | 7187 | 10 | 27 | 1 | 11 | 50 | 50
[25 empty] | 7188 | 10 | 27 | 1 | 12 | 51.1 | 51
[25 empty] | 7189 | 10 | 27 | 1 | 13 | 51.1 | 51
[25 empty] | 7190 | 10 | 27 | 1 | 14 | 52 | 52
[25 empty] | 7191 | 10 | 27 | 1 | 15 | 51.1 | 51
[25 empty] | 7192 | 10 | 27 | 1 | 16 | 51.1 | 51
[25 empty] | 7193 | 10 | 27 | 1 | 17 | 48.9 | 49
[25 empty] | 7194 | 10 | 27 | 1 | 18 | 48 | 48
[25 empty] | 7195 | 10 | 27 | 1 | 19 | 46.9 | 47
[25 empty] | 7196 | 10 | 27 | 1 | 20 | 46 | 46
[25 empty] | 7197 | 10 | 27 | 1 | 21 | 46.2 | 46
[25 empty] | 7198 | 10 | 27 | 1 | 22 | 46 | 46
[25 empty] | 7199 | 10 | 27 | 1 | 23 | 45 | 45
[25 empty] | 7200 | 10 | 28 | 2 | 0 | 45 | 45
[25 empty] | 7201 | 10 | 28 | 2 | 1 | 44.1 | 44
[25 empty] | 7202 | 10 | 28 | 2 | 2 | 43 | 43
[25 empty] | 7203 | 10 | 28 | 2 | 3 | 42.1 | 42
[25 empty] | 7204 | 10 | 28 | 2 | 4 | 42.1 | 42
[25 empty] | 7205 | 10 | 28 | 2 | 5 | 41 | 41
[25 empty] | 7206 | 10 | 28 | 2 | 6 | 41 | 41
[25 empty] | 7207 | 10 | 28 | 2 | 7 | 41 | 41
[25 empty] | 7208 | 10 | 28 | 2 | 8 | 42.1 | 42
[25 empty] | 7209 | 10 | 28 | 2 | 9 | 44.1 | 44
[25 empty] | 7210 | 10 | 28 | 2 | 10 | 45 | 45
[25 empty] | 7211 | 10 | 28 | 2 | 11 | 46 | 46
[25 empty] | 7212 | 10 | 28 | 2 | 12 | 48 | 48
[25 empty] | 7213 | 10 | 28 | 2 | 13 | 50 | 50
[25 empty] | 7214 | 10 | 28 | 2 | 14 | 51.1 | 51
[25 empty] | 7215 | 10 | 28 | 2 | 15 | 51.1 | 51
[25 empty] | 7216 | 10 | 28 | 2 | 16 | 51.1 | 51
[25 empty] | 7217 | 10 | 28 | 2 | 17 | 50 | 50
[25 empty] | 7218 | 10 | 28 | 2 | 18 | 50 | 50
[25 empty] | 7219 | 10 | 28 | 2 | 19 | 48.9 | 49
[25 empty] | 7220 | 10 | 28 | 2 | 20 | 48 | 48
[25 empty] | 7221 | 10 | 28 | 2 | 21 | 46.9 | 47
[25 empty] | 7222 | 10 | 28 | 2 | 22 | 46.9 | 47
[25 empty] | 7223 | 10 | 28 | 2 | 23 | 45 | 45
[25 empty] | 7224 | 10 | 29 | 3 | 0 | 45 | 45
[25 empty] | 7225 | 10 | 29 | 3 | 1 | 44.1 | 44
[25 empty] | 7226 | 10 | 29 | 3 | 2 | 43 | 43
[25 empty] | 7227 | 10 | 29 | 3 | 3 | 42.1 | 42
[25 empty] | 7228 | 10 | 29 | 3 | 4 | 42.1 | 42
[25 empty] | 7229 | 10 | 29 | 3 | 5 | 42.1 | 42
[25 empty] | 7230 | 10 | 29 | 3 | 6 | 42.1 | 42
[25 empty] | 7231 | 10 | 29 | 3 | 7 | 42.1 | 42
[25 empty] | 7232 | 10 | 29 | 3 | 8 | 43 | 43
[25 empty] | 7233 | 10 | 29 | 3 | 9 | 46 | 46
[25 empty] | 7234 | 10 | 29 | 3 | 10 | 48 | 48
[25 empty] | 7235 | 10 | 29 | 3 | 11 | 50 | 50
[25 empty] | 7236 | 10 | 29 | 3 | 12 | 52 | 52
[25 empty] | 7237 | 10 | 29 | 3 | 13 | 54 | 54
[25 empty] | 7238 | 10 | 29 | 3 | 14 | 55.9 | 56
[25 empty] | 7239 | 10 | 29 | 3 | 15 | 57.9 | 58
[25 empty] | 7240 | 10 | 29 | 3 | 16 | 59 | 59
[25 empty] | 7241 | 10 | 29 | 3 | 17 | 57.9 | 58
[25 empty] | 7242 | 10 | 29 | 3 | 18 | 57.9 | 58
[25 empty] | 7243 | 10 | 29 | 3 | 19 | 57 | 57
[25 empty] | 7244 | 10 | 29 | 3 | 20 | 57 | 57
[25 empty] | 7245 | 10 | 29 | 3 | 21 | 57 | 57
[25 empty] | 7246 | 10 | 29 | 3 | 22 | 55.9 | 56
[25 empty] | 7247 | 10 | 29 | 3 | 23 | 55.9 | 56
[25 empty] | 7248 | 10 | 30 | 4 | 0 | 55.9 | 56
[25 empty] | 7249 | 10 | 30 | 4 | 1 | 55.9 | 56
[25 empty] | 7250 | 10 | 30 | 4 | 2 | 55 | 55
[25 empty] | 7251 | 10 | 30 | 4 | 3 | 55 | 55
[25 empty] | 7252 | 10 | 30 | 4 | 4 | 54 | 54
[25 empty] | 7253 | 10 | 30 | 4 | 5 | 54 | 54
[25 empty] | 7254 | 10 | 30 | 4 | 6 | 53.1 | 53
[25 empty] | 7255 | 10 | 30 | 4 | 7 | 53.1 | 53
[25 empty] | 7256 | 10 | 30 | 4 | 8 | 53.1 | 53
[25 empty] | 7257 | 10 | 30 | 4 | 9 | 54 | 54
[25 empty] | 7258 | 10 | 30 | 4 | 10 | 55.9 | 56
[25 empty] | 7259 | 10 | 30 | 4 | 11 | 57 | 57
[25 empty] | 7260 | 10 | 30 | 4 | 12 | 57.9 | 58
[25 empty] | 7261 | 10 | 30 | 4 | 13 | 59 | 59
[25 empty] | 7262 | 10 | 30 | 4 | 14 | 61 | 61
[25 empty] | 7263 | 10 | 30 | 4 | 15 | 60.1 | 60
[25 empty] | 7264 | 10 | 30 | 4 | 16 | 60.1 | 60
[25 empty] | 7265 | 10 | 30 | 4 | 17 | 57.9 | 58
[25 empty] | 7266 | 10 | 30 | 4 | 18 | 55.9 | 56
[25 empty] | 7267 | 10 | 30 | 4 | 19 | 54 | 54
[25 empty] | 7268 | 10 | 30 | 4 | 20 | 53.1 | 53
[25 empty] | 7269 | 10 | 30 | 4 | 21 | 52 | 52
[25 empty] | 7270 | 10 | 30 | 4 | 22 | 50 | 50
[25 empty] | 7271 | 10 | 30 | 4 | 23 | 48.9 | 49
[25 empty] | 7272 | 10 | 31 | 5 | 0 | 48 | 48
[25 empty] | 7273 | 10 | 31 | 5 | 1 | 46.9 | 47
[25 empty] | 7274 | 10 | 31 | 5 | 2 | 46 | 46
[25 empty] | 7275 | 10 | 31 | 5 | 3 | 45 | 45
[25 empty] | 7276 | 10 | 31 | 5 | 4 | 44.1 | 44
[25 empty] | 7277 | 10 | 31 | 5 | 5 | 44.1 | 44
[25 empty] | 7278 | 10 | 31 | 5 | 6 | 45 | 45
[25 empty] | 7279 | 10 | 31 | 5 | 7 | 46 | 46
[25 empty] | 7280 | 10 | 31 | 5 | 8 | 45 | 45
[25 empty] | 7281 | 10 | 31 | 5 | 9 | 46 | 46
[25 empty] | 7282 | 10 | 31 | 5 | 10 | 48 | 48
[25 empty] | 7283 | 10 | 31 | 5 | 11 | 48.9 | 49
[25 empty] | 7284 | 10 | 31 | 5 | 12 | 50 | 50
[25 empty] | 7285 | 10 | 31 | 5 | 13 | 51.1 | 51
[25 empty] | 7286 | 10 | 31 | 5 | 14 | 52 | 52
[25 empty] | 7287 | 10 | 31 | 5 | 15 | 55 | 55
[25 empty] | 7288 | 10 | 31 | 5 | 16 | 55.9 | 56
[25 empty] | 7289 | 10 | 31 | 5 | 17 | 55.9 | 56
[25 empty] | 7290 | 10 | 31 | 5 | 18 | 57 | 57
[25 empty] | 7291 | 10 | 31 | 5 | 19 | 57 | 57
[25 empty] | 7292 | 10 | 31 | 5 | 20 | 57.9 | 58
[25 empty] | 7293 | 10 | 31 | 5 | 21 | 57.9 | 58
[25 empty] | 7294 | 10 | 31 | 5 | 22 | 58.6 | 59
[25 empty] | 7295 | 10 | 31 | 5 | 23 | 59.4 | 59
[25 empty] | 7296 | 11 | 1 | 6 | 0 | 60.1 | 60
[25 empty] | 7297 | 11 | 1 | 6 | 1 | 60.8 | 61
[25 empty] | 7298 | 11 | 1 | 6 | 2 | 61.5 | 62
[25 empty] | 7299 | 11 | 1 | 6 | 3 | 62.2 | 62
[25 empty] | 7300 | 11 | 1 | 6 | 4 | 63 | 63
[25 empty] | 7301 | 11 | 1 | 6 | 5 | 64 | 64
[25 empty] | 7302 | 11 | 1 | 6 | 6 | 63 | 63
[25 empty] | 7303 | 11 | 1 | 6 | 7 | 63 | 63
[25 empty] | 7304 | 11 | 1 | 6 | 8 | 63 | 63
[25 empty] | 7305 | 11 | 1 | 6 | 9 | 64.9 | 65
[25 empty] | 7306 | 11 | 1 | 6 | 10 | 64.9 | 65
[25 empty] | 7307 | 11 | 1 | 6 | 11 | 64 | 64
[25 empty] | 7308 | 11 | 1 | 6 | 12 | 64 | 64
[25 empty] | 7309 | 11 | 1 | 6 | 13 | 63 | 63
[25 empty] | 7310 | 11 | 1 | 6 | 14 | 64.9 | 65
[25 empty] | 7311 | 11 | 1 | 6 | 15 | 64.9 | 65
[25 empty] | 7312 | 11 | 1 | 6 | 16 | 64.9 | 65
[25 empty] | 7313 | 11 | 1 | 6 | 17 | 66 | 66
[25 empty] | 7314 | 11 | 1 | 6 | 18 | 64.9 | 65
[25 empty] | 7315 | 11 | 1 | 6 | 19 | 64.9 | 65
[25 empty] | 7316 | 11 | 1 | 6 | 20 | 55.9 | 56
[25 empty] | 7317 | 11 | 1 | 6 | 21 | 57 | 57
[25 empty] | 7318 | 11 | 1 | 6 | 22 | 55 | 55
[25 empty] | 7319 | 11 | 1 | 6 | 23 | 54 | 54
[25 empty] | 7320 | 11 | 2 | 7 | 0 | 53.1 | 53
[25 empty] | 7321 | 11 | 2 | 7 | 1 | 51.1 | 51
[25 empty] | 7322 | 11 | 2 | 7 | 2 | 48.9 | 49
[25 empty] | 7323 | 11 | 2 | 7 | 3 | 48 | 48
[25 empty] | 7324 | 11 | 2 | 7 | 4 | 48.9 | 49
[25 empty] | 7325 | 11 | 2 | 7 | 5 | 48 | 48
[25 empty] | 7326 | 11 | 2 | 7 | 6 | 46.9 | 47
[25 empty] | 7327 | 11 | 2 | 7 | 7 | 46.9 | 47
[25 empty] | 7328 | 11 | 2 | 7 | 8 | 48.9 | 49
[25 empty] | 7329 | 11 | 2 | 7 | 9 | 51.1 | 51
[25 empty] | 7330 | 11 | 2 | 7 | 10 | 51.1 | 51
[25 empty] | 7331 | 11 | 2 | 7 | 11 | 50 | 50
[25 empty] | 7332 | 11 | 2 | 7 | 12 | 51.1 | 51
[25 empty] | 7333 | 11 | 2 | 7 | 13 | 54 | 54
[25 empty] | 7334 | 11 | 2 | 7 | 14 | 55 | 55
[25 empty] | 7335 | 11 | 2 | 7 | 15 | 57 | 57
[25 empty] | 7336 | 11 | 2 | 7 | 16 | 57.9 | 58
[25 empty] | 7337 | 11 | 2 | 7 | 17 | 57 | 57
[25 empty] | 7338 | 11 | 2 | 7 | 18 | 57 | 57
[25 empty] | 7339 | 11 | 2 | 7 | 19 | 55.9 | 56
[25 empty] | 7340 | 11 | 2 | 7 | 20 | 55 | 55
[25 empty] | 7341 | 11 | 2 | 7 | 21 | 54 | 54
[25 empty] | 7342 | 11 | 2 | 7 | 22 | 54 | 54
[25 empty] | 7343 | 11 | 2 | 7 | 23 | 52 | 52
[25 empty] | 7344 | 11 | 3 | 1 | 0 | 52 | 52
[25 empty] | 7345 | 11 | 3 | 1 | 1 | 51.1 | 51
[25 empty] | 7346 | 11 | 3 | 1 | 2 | 50 | 50
[25 empty] | 7347 | 11 | 3 | 1 | 3 | 48.9 | 49
[25 empty] | 7348 | 11 | 3 | 1 | 4 | 48.9 | 49
[25 empty] | 7349 | 11 | 3 | 1 | 5 | 46.9 | 47
[25 empty] | 7350 | 11 | 3 | 1 | 6 | 46.9 | 47
[25 empty] | 7351 | 11 | 3 | 1 | 7 | 46.9 | 47
[25 empty] | 7352 | 11 | 3 | 1 | 8 | 48.9 | 49
[25 empty] | 7353 | 11 | 3 | 1 | 9 | 51.1 | 51
[25 empty] | 7354 | 11 | 3 | 1 | 10 | 54 | 54
[25 empty] | 7355 | 11 | 3 | 1 | 11 | 59 | 59
[25 empty] | 7356 | 11 | 3 | 1 | 12 | 62.1 | 62
[25 empty] | 7357 | 11 | 3 | 1 | 13 | 64 | 64
[25 empty] | 7358 | 11 | 3 | 1 | 14 | 68 | 68
[25 empty] | 7359 | 11 | 3 | 1 | 15 | 69.1 | 69
[25 empty] | 7360 | 11 | 3 | 1 | 16 | 68 | 68
[25 empty] | 7361 | 11 | 3 | 1 | 17 | 60.1 | 60
[25 empty] | 7362 | 11 | 3 | 1 | 18 | 57.9 | 58
[25 empty] | 7363 | 11 | 3 | 1 | 19 | 59 | 59
[25 empty] | 7364 | 11 | 3 | 1 | 20 | 63 | 63
[25 empty] | 7365 | 11 | 3 | 1 | 21 | 63 | 63
[25 empty] | 7366 | 11 | 3 | 1 | 22 | 63 | 63
[25 empty] | 7367 | 11 | 3 | 1 | 23 | 62.1 | 62
[25 empty] | 7368 | 11 | 4 | 2 | 0 | 62.1 | 62
[25 empty] | 7369 | 11 | 4 | 2 | 1 | 61 | 61
[25 empty] | 7370 | 11 | 4 | 2 | 2 | 61 | 61
[25 empty] | 7371 | 11 | 4 | 2 | 3 | 60.1 | 60
[25 empty] | 7372 | 11 | 4 | 2 | 4 | 59 | 59
[25 empty] | 7373 | 11 | 4 | 2 | 5 | 57.9 | 58
[25 empty] | 7374 | 11 | 4 | 2 | 6 | 57.9 | 58
[25 empty] | 7375 | 11 | 4 | 2 | 7 | 60.1 | 60
[25 empty] | 7376 | 11 | 4 | 2 | 8 | 61 | 61
[25 empty] | 7377 | 11 | 4 | 2 | 9 | 64 | 64
[25 empty] | 7378 | 11 | 4 | 2 | 10 | 66.9 | 67
[25 empty] | 7379 | 11 | 4 | 2 | 11 | 70 | 70
[25 empty] | 7380 | 11 | 4 | 2 | 12 | 70 | 70
[25 empty] | 7381 | 11 | 4 | 2 | 13 | 70 | 70
[25 empty] | 7382 | 11 | 4 | 2 | 14 | 70 | 70
[25 empty] | 7383 | 11 | 4 | 2 | 15 | 70 | 70
[25 empty] | 7384 | 11 | 4 | 2 | 16 | 69.1 | 69
[25 empty] | 7385 | 11 | 4 | 2 | 17 | 66 | 66
[25 empty] | 7386 | 11 | 4 | 2 | 18 | 64 | 64
[25 empty] | 7387 | 11 | 4 | 2 | 19 | 66 | 66
[25 empty] | 7388 | 11 | 4 | 2 | 20 | 64 | 64
[25 empty] | 7389 | 11 | 4 | 2 | 21 | 64.9 | 65
[25 empty] | 7390 | 11 | 4 | 2 | 22 | 64 | 64
[25 empty] | 7391 | 11 | 4 | 2 | 23 | 64 | 64
[25 empty] | 7392 | 11 | 5 | 3 | 0 | 64 | 64
[25 empty] | 7393 | 11 | 5 | 3 | 1 | 63 | 63
[25 empty] | 7394 | 11 | 5 | 3 | 2 | 61 | 61
[25 empty] | 7395 | 11 | 5 | 3 | 3 | 60.1 | 60
[25 empty] | 7396 | 11 | 5 | 3 | 4 | 59 | 59
[25 empty] | 7397 | 11 | 5 | 3 | 5 | 57.9 | 58
[25 empty] | 7398 | 11 | 5 | 3 | 6 | 57.9 | 58
[25 empty] | 7399 | 11 | 5 | 3 | 7 | 59 | 59
[25 empty] | 7400 | 11 | 5 | 3 | 8 | 61 | 61
[25 empty] | 7401 | 11 | 5 | 3 | 9 | 61 | 61
[25 empty] | 7402 | 11 | 5 | 3 | 10 | 64 | 64
[25 empty] | 7403 | 11 | 5 | 3 | 11 | 64.9 | 65
[25 empty] | 7404 | 11 | 5 | 3 | 12 | 66.9 | 67
[25 empty] | 7405 | 11 | 5 | 3 | 13 | 68 | 68
[25 empty] | 7406 | 11 | 5 | 3 | 14 | 70 | 70
[25 empty] | 7407 | 11 | 5 | 3 | 15 | 72 | 72
[25 empty] | 7408 | 11 | 5 | 3 | 16 | 73 | 73
[25 empty] | 7409 | 11 | 5 | 3 | 17 | 70 | 70
[25 empty] | 7410 | 11 | 5 | 3 | 18 | 64.9 | 65
[25 empty] | 7411 | 11 | 5 | 3 | 19 | 66 | 66
[25 empty] | 7412 | 11 | 5 | 3 | 20 | 66 | 66
[25 empty] | 7413 | 11 | 5 | 3 | 21 | 66 | 66
[25 empty] | 7414 | 11 | 5 | 3 | 22 | 66 | 66
[25 empty] | 7415 | 11 | 5 | 3 | 23 | 64.9 | 65
[25 empty] | 7416 | 11 | 6 | 4 | 0 | 64 | 64
[25 empty] | 7417 | 11 | 6 | 4 | 1 | 64 | 64
[25 empty] | 7418 | 11 | 6 | 4 | 2 | 62.1 | 62
[25 empty] | 7419 | 11 | 6 | 4 | 3 | 61 | 61
[25 empty] | 7420 | 11 | 6 | 4 | 4 | 60.1 | 60
[25 empty] | 7421 | 11 | 6 | 4 | 5 | 59 | 59
[25 empty] | 7422 | 11 | 6 | 4 | 6 | 57.9 | 58
[25 empty] | 7423 | 11 | 6 | 4 | 7 | 60.1 | 60
[25 empty] | 7424 | 11 | 6 | 4 | 8 | 62.1 | 62
[25 empty] | 7425 | 11 | 6 | 4 | 9 | 66 | 66
[25 empty] | 7426 | 11 | 6 | 4 | 10 | 66 | 66
[25 empty] | 7427 | 11 | 6 | 4 | 11 | 66.9 | 67
[25 empty] | 7428 | 11 | 6 | 4 | 12 | 68 | 68
[25 empty] | 7429 | 11 | 6 | 4 | 13 | 66.9 | 67
[25 empty] | 7430 | 11 | 6 | 4 | 14 | 69.1 | 69
[25 empty] | 7431 | 11 | 6 | 4 | 15 | 68 | 68
[25 empty] | 7432 | 11 | 6 | 4 | 16 | 68 | 68
[25 empty] | 7433 | 11 | 6 | 4 | 17 | 66.9 | 67
[25 empty] | 7434 | 11 | 6 | 4 | 18 | 66.9 | 67
[25 empty] | 7435 | 11 | 6 | 4 | 19 | 66.9 | 67
[25 empty] | 7436 | 11 | 6 | 4 | 20 | 68 | 68
[25 empty] | 7437 | 11 | 6 | 4 | 21 | 66 | 66
[25 empty] | 7438 | 11 | 6 | 4 | 22 | 64 | 64
[25 empty] | 7439 | 11 | 6 | 4 | 23 | 63 | 63
[25 empty] | 7440 | 11 | 7 | 5 | 0 | 61 | 61
[25 empty] | 7441 | 11 | 7 | 5 | 1 | 59 | 59
[25 empty] | 7442 | 11 | 7 | 5 | 2 | 55.9 | 56
[25 empty] | 7443 | 11 | 7 | 5 | 3 | 54 | 54
[25 empty] | 7444 | 11 | 7 | 5 | 4 | 53.1 | 53
[25 empty] | 7445 | 11 | 7 | 5 | 5 | 52 | 52
[25 empty] | 7446 | 11 | 7 | 5 | 6 | 50 | 50
[25 empty] | 7447 | 11 | 7 | 5 | 7 | 48 | 48
[25 empty] | 7448 | 11 | 7 | 5 | 8 | 48.9 | 49
[25 empty] | 7449 | 11 | 7 | 5 | 9 | 50 | 50
[25 empty] | 7450 | 11 | 7 | 5 | 10 | 51.1 | 51
[25 empty] | 7451 | 11 | 7 | 5 | 11 | 53.1 | 53
[25 empty] | 7452 | 11 | 7 | 5 | 12 | 55 | 55
[25 empty] | 7453 | 11 | 7 | 5 | 13 | 57 | 57
[25 empty] | 7454 | 11 | 7 | 5 | 14 | 57 | 57
[25 empty] | 7455 | 11 | 7 | 5 | 15 | 57.9 | 58
[25 empty] | 7456 | 11 | 7 | 5 | 16 | 57.9 | 58
[25 empty] | 7457 | 11 | 7 | 5 | 17 | 57 | 57
[25 empty] | 7458 | 11 | 7 | 5 | 18 | 55.9 | 56
[25 empty] | 7459 | 11 | 7 | 5 | 19 | 55 | 55
[25 empty] | 7460 | 11 | 7 | 5 | 20 | 54 | 54
[25 empty] | 7461 | 11 | 7 | 5 | 21 | 53.1 | 53
[25 empty] | 7462 | 11 | 7 | 5 | 22 | 53.1 | 53
[25 empty] | 7463 | 11 | 7 | 5 | 23 | 52 | 52
[25 empty] | 7464 | 11 | 8 | 6 | 0 | 51.1 | 51
[25 empty] | 7465 | 11 | 8 | 6 | 1 | 51.1 | 51
[25 empty] | 7466 | 11 | 8 | 6 | 2 | 51.1 | 51
[25 empty] | 7467 | 11 | 8 | 6 | 3 | 51.1 | 51
[25 empty] | 7468 | 11 | 8 | 6 | 4 | 51.1 | 51
[25 empty] | 7469 | 11 | 8 | 6 | 5 | 48.9 | 49
[25 empty] | 7470 | 11 | 8 | 6 | 6 | 48.9 | 49
[25 empty] | 7471 | 11 | 8 | 6 | 7 | 48.9 | 49
[25 empty] | 7472 | 11 | 8 | 6 | 8 | 52 | 52
[25 empty] | 7473 | 11 | 8 | 6 | 9 | 54 | 54
[25 empty] | 7474 | 11 | 8 | 6 | 10 | 57 | 57
[25 empty] | 7475 | 11 | 8 | 6 | 11 | 59 | 59
[25 empty] | 7476 | 11 | 8 | 6 | 12 | 62.1 | 62
[25 empty] | 7477 | 11 | 8 | 6 | 13 | 66 | 66
[25 empty] | 7478 | 11 | 8 | 6 | 14 | 68 | 68
[25 empty] | 7479 | 11 | 8 | 6 | 15 | 69.1 | 69
[25 empty] | 7480 | 11 | 8 | 6 | 16 | 66.9 | 67
[25 empty] | 7481 | 11 | 8 | 6 | 17 | 68 | 68
[25 empty] | 7482 | 11 | 8 | 6 | 18 | 66 | 66
[25 empty] | 7483 | 11 | 8 | 6 | 19 | 64.9 | 65
[25 empty] | 7484 | 11 | 8 | 6 | 20 | 63 | 63
[25 empty] | 7485 | 11 | 8 | 6 | 21 | 62.1 | 62
[25 empty] | 7486 | 11 | 8 | 6 | 22 | 62.1 | 62
[25 empty] | 7487 | 11 | 8 | 6 | 23 | 62.1 | 62
[25 empty] | 7488 | 11 | 9 | 7 | 0 | 62.1 | 62
[25 empty] | 7489 | 11 | 9 | 7 | 1 | 61 | 61
[25 empty] | 7490 | 11 | 9 | 7 | 2 | 62.1 | 62
[25 empty] | 7491 | 11 | 9 | 7 | 3 | 62.1 | 62
[25 empty] | 7492 | 11 | 9 | 7 | 4 | 61 | 61
[25 empty] | 7493 | 11 | 9 | 7 | 5 | 61 | 61
[25 empty] | 7494 | 11 | 9 | 7 | 6 | 60.1 | 60
[25 empty] | 7495 | 11 | 9 | 7 | 7 | 61 | 61
[25 empty] | 7496 | 11 | 9 | 7 | 8 | 63 | 63
[25 empty] | 7497 | 11 | 9 | 7 | 9 | 64.9 | 65
[25 empty] | 7498 | 11 | 9 | 7 | 10 | 66.9 | 67
[25 empty] | 7499 | 11 | 9 | 7 | 11 | 68 | 68
[25 empty] | 7500 | 11 | 9 | 7 | 12 | 70 | 70
[25 empty] | 7501 | 11 | 9 | 7 | 13 | 69.1 | 69
[25 empty] | 7502 | 11 | 9 | 7 | 14 | 68 | 68
[25 empty] | 7503 | 11 | 9 | 7 | 15 | 66.9 | 67
[25 empty] | 7504 | 11 | 9 | 7 | 16 | 64.9 | 65
[25 empty] | 7505 | 11 | 9 | 7 | 17 | 64 | 64
[25 empty] | 7506 | 11 | 9 | 7 | 18 | 63 | 63
[25 empty] | 7507 | 11 | 9 | 7 | 19 | 61 | 61
[25 empty] | 7508 | 11 | 9 | 7 | 20 | 60.1 | 60
[25 empty] | 7509 | 11 | 9 | 7 | 21 | 59 | 59
[25 empty] | 7510 | 11 | 9 | 7 | 22 | 55.9 | 56
[25 empty] | 7511 | 11 | 9 | 7 | 23 | 53.1 | 53
[25 empty] | 7512 | 11 | 10 | 1 | 0 | 53.1 | 53
[25 empty] | 7513 | 11 | 10 | 1 | 1 | 52 | 52
[25 empty] | 7514 | 11 | 10 | 1 | 2 | 50 | 50
[25 empty] | 7515 | 11 | 10 | 1 | 3 | 46.9 | 47
[25 empty] | 7516 | 11 | 10 | 1 | 4 | 43 | 43
[25 empty] | 7517 | 11 | 10 | 1 | 5 | 43 | 43
[25 empty] | 7518 | 11 | 10 | 1 | 6 | 43 | 43
[25 empty] | 7519 | 11 | 10 | 1 | 7 | 43 | 43
[25 empty] | 7520 | 11 | 10 | 1 | 8 | 44.1 | 44
[25 empty] | 7521 | 11 | 10 | 1 | 9 | 45 | 45
[25 empty] | 7522 | 11 | 10 | 1 | 10 | 46 | 46
[25 empty] | 7523 | 11 | 10 | 1 | 11 | 48 | 48
[25 empty] | 7524 | 11 | 10 | 1 | 12 | 50 | 50
[25 empty] | 7525 | 11 | 10 | 1 | 13 | 53.1 | 53
[25 empty] | 7526 | 11 | 10 | 1 | 14 | 54 | 54
[25 empty] | 7527 | 11 | 10 | 1 | 15 | 55 | 55
[25 empty] | 7528 | 11 | 10 | 1 | 16 | 54 | 54
[25 empty] | 7529 | 11 | 10 | 1 | 17 | 52 | 52
[25 empty] | 7530 | 11 | 10 | 1 | 18 | 51.1 | 51
[25 empty] | 7531 | 11 | 10 | 1 | 19 | 50 | 50
[25 empty] | 7532 | 11 | 10 | 1 | 20 | 48 | 48
[25 empty] | 7533 | 11 | 10 | 1 | 21 | 46 | 46
[25 empty] | 7534 | 11 | 10 | 1 | 22 | 44.1 | 44
[25 empty] | 7535 | 11 | 10 | 1 | 23 | 42.1 | 42
[25 empty] | 7536 | 11 | 11 | 2 | 0 | 43 | 43
[25 empty] | 7537 | 11 | 11 | 2 | 1 | 42.1 | 42
[25 empty] | 7538 | 11 | 11 | 2 | 2 | 42.1 | 42
[25 empty] | 7539 | 11 | 11 | 2 | 3 | 42.1 | 42
[25 empty] | 7540 | 11 | 11 | 2 | 4 | 41 | 41
[25 empty] | 7541 | 11 | 11 | 2 | 5 | 39.9 | 40
[25 empty] | 7542 | 11 | 11 | 2 | 6 | 39 | 39
[25 empty] | 7543 | 11 | 11 | 2 | 7 | 39 | 39
[25 empty] | 7544 | 11 | 11 | 2 | 8 | 39 | 39
[25 empty] | 7545 | 11 | 11 | 2 | 9 | 41 | 41
[25 empty] | 7546 | 11 | 11 | 2 | 10 | 42.1 | 42
[25 empty] | 7547 | 11 | 11 | 2 | 11 | 44.1 | 44
[25 empty] | 7548 | 11 | 11 | 2 | 12 | 46.9 | 47
[25 empty] | 7549 | 11 | 11 | 2 | 13 | 48 | 48
[25 empty] | 7550 | 11 | 11 | 2 | 14 | 50 | 50
[25 empty] | 7551 | 11 | 11 | 2 | 15 | 50 | 50
[25 empty] | 7552 | 11 | 11 | 2 | 16 | 50 | 50
[25 empty] | 7553 | 11 | 11 | 2 | 17 | 50 | 50
[25 empty] | 7554 | 11 | 11 | 2 | 18 | 48.9 | 49
[25 empty] | 7555 | 11 | 11 | 2 | 19 | 48 | 48
[25 empty] | 7556 | 11 | 11 | 2 | 20 | 48 | 48
[25 empty] | 7557 | 11 | 11 | 2 | 21 | 46 | 46
[25 empty] | 7558 | 11 | 11 | 2 | 22 | 45 | 45
[25 empty] | 7559 | 11 | 11 | 2 | 23 | 44.1 | 44
[25 empty] | 7560 | 11 | 12 | 3 | 0 | 43 | 43
[25 empty] | 7561 | 11 | 12 | 3 | 1 | 42.1 | 42
[25 empty] | 7562 | 11 | 12 | 3 | 2 | 42.1 | 42
[25 empty] | 7563 | 11 | 12 | 3 | 3 | 41 | 41
[25 empty] | 7564 | 11 | 12 | 3 | 4 | 39.9 | 40
[25 empty] | 7565 | 11 | 12 | 3 | 5 | 37.9 | 38
[25 empty] | 7566 | 11 | 12 | 3 | 6 | 37.9 | 38
[25 empty] | 7567 | 11 | 12 | 3 | 7 | 37.9 | 38
[25 empty] | 7568 | 11 | 12 | 3 | 8 | 39.9 | 40
[25 empty] | 7569 | 11 | 12 | 3 | 9 | 43 | 43
[25 empty] | 7570 | 11 | 12 | 3 | 10 | 44.1 | 44
[25 empty] | 7571 | 11 | 12 | 3 | 11 | 48 | 48
[25 empty] | 7572 | 11 | 12 | 3 | 12 | 44.1 | 44
[25 empty] | 7573 | 11 | 12 | 3 | 13 | 51.1 | 51
[25 empty] | 7574 | 11 | 12 | 3 | 14 | 52 | 52
[25 empty] | 7575 | 11 | 12 | 3 | 15 | 52 | 52
[25 empty] | 7576 | 11 | 12 | 3 | 16 | 51.1 | 51
[25 empty] | 7577 | 11 | 12 | 3 | 17 | 51.1 | 51
[25 empty] | 7578 | 11 | 12 | 3 | 18 | 50 | 50
[25 empty] | 7579 | 11 | 12 | 3 | 19 | 48.9 | 49
[25 empty] | 7580 | 11 | 12 | 3 | 20 | 48.9 | 49
[25 empty] | 7581 | 11 | 12 | 3 | 21 | 48.9 | 49
[25 empty] | 7582 | 11 | 12 | 3 | 22 | 48.9 | 49
[25 empty] | 7583 | 11 | 12 | 3 | 23 | 48.9 | 49
[25 empty] | 7584 | 11 | 13 | 4 | 0 | 48.9 | 49
[25 empty] | 7585 | 11 | 13 | 4 | 1 | 48.9 | 49
[25 empty] | 7586 | 11 | 13 | 4 | 2 | 48.9 | 49
[25 empty] | 7587 | 11 | 13 | 4 | 3 | 48.9 | 49
[25 empty] | 7588 | 11 | 13 | 4 | 4 | 48.9 | 49
[25 empty] | 7589 | 11 | 13 | 4 | 5 | 50 | 50
[25 empty] | 7590 | 11 | 13 | 4 | 6 | 50 | 50
[25 empty] | 7591 | 11 | 13 | 4 | 7 | 52 | 52
[25 empty] | 7592 | 11 | 13 | 4 | 8 | 52 | 52
[25 empty] | 7593 | 11 | 13 | 4 | 9 | 53.1 | 53
[25 empty] | 7594 | 11 | 13 | 4 | 10 | 54 | 54
[25 empty] | 7595 | 11 | 13 | 4 | 11 | 55 | 55
[25 empty] | 7596 | 11 | 13 | 4 | 12 | 55.9 | 56
[25 empty] | 7597 | 11 | 13 | 4 | 13 | 57 | 57
[25 empty] | 7598 | 11 | 13 | 4 | 14 | 57.9 | 58
[25 empty] | 7599 | 11 | 13 | 4 | 15 | 57.9 | 58
[25 empty] | 7600 | 11 | 13 | 4 | 16 | 57.9 | 58
[25 empty] | 7601 | 11 | 13 | 4 | 17 | 57 | 57
[25 empty] | 7602 | 11 | 13 | 4 | 18 | 55 | 55
[25 empty] | 7603 | 11 | 13 | 4 | 19 | 55 | 55
[25 empty] | 7604 | 11 | 13 | 4 | 20 | 53.1 | 53
[25 empty] | 7605 | 11 | 13 | 4 | 21 | 54 | 54
[25 empty] | 7606 | 11 | 13 | 4 | 22 | 52 | 52
[25 empty] | 7607 | 11 | 13 | 4 | 23 | 51.1 | 51
[25 empty] | 7608 | 11 | 14 | 5 | 0 | 51.1 | 51
[25 empty] | 7609 | 11 | 14 | 5 | 1 | 50 | 50
[25 empty] | 7610 | 11 | 14 | 5 | 2 | 48.9 | 49
[25 empty] | 7611 | 11 | 14 | 5 | 3 | 50 | 50
[25 empty] | 7612 | 11 | 14 | 5 | 4 | 50 | 50
[25 empty] | 7613 | 11 | 14 | 5 | 5 | 50 | 50
[25 empty] | 7614 | 11 | 14 | 5 | 6 | 48.9 | 49
[25 empty] | 7615 | 11 | 14 | 5 | 7 | 50 | 50
[25 empty] | 7616 | 11 | 14 | 5 | 8 | 51.1 | 51
[25 empty] | 7617 | 11 | 14 | 5 | 9 | 52 | 52
[25 empty] | 7618 | 11 | 14 | 5 | 10 | 55 | 55
[25 empty] | 7619 | 11 | 14 | 5 | 11 | 61 | 61
[25 empty] | 7620 | 11 | 14 | 5 | 12 | 62.1 | 62
[25 empty] | 7621 | 11 | 14 | 5 | 13 | 61 | 61
[25 empty] | 7622 | 11 | 14 | 5 | 14 | 61 | 61
[25 empty] | 7623 | 11 | 14 | 5 | 15 | 61 | 61
[25 empty] | 7624 | 11 | 14 | 5 | 16 | 59 | 59
[25 empty] | 7625 | 11 | 14 | 5 | 17 | 57 | 57
[25 empty] | 7626 | 11 | 14 | 5 | 18 | 57 | 57
[25 empty] | 7627 | 11 | 14 | 5 | 19 | 57 | 57
[25 empty] | 7628 | 11 | 14 | 5 | 20 | 57 | 57
[25 empty] | 7629 | 11 | 14 | 5 | 21 | 57 | 57
[25 empty] | 7630 | 11 | 14 | 5 | 22 | 55.9 | 56
[25 empty] | 7631 | 11 | 14 | 5 | 23 | 55.9 | 56
[25 empty] | 7632 | 11 | 15 | 6 | 0 | 55.9 | 56
[25 empty] | 7633 | 11 | 15 | 6 | 1 | 55 | 55
[25 empty] | 7634 | 11 | 15 | 6 | 2 | 55 | 55
[25 empty] | 7635 | 11 | 15 | 6 | 3 | 55.9 | 56
[25 empty] | 7636 | 11 | 15 | 6 | 4 | 55.9 | 56
[25 empty] | 7637 | 11 | 15 | 6 | 5 | 55.9 | 56
[25 empty] | 7638 | 11 | 15 | 6 | 6 | 57 | 57
[25 empty] | 7639 | 11 | 15 | 6 | 7 | 55.9 | 56
[25 empty] | 7640 | 11 | 15 | 6 | 8 | 55.9 | 56
[25 empty] | 7641 | 11 | 15 | 6 | 9 | 59 | 59
[25 empty] | 7642 | 11 | 15 | 6 | 10 | 63 | 63
[25 empty] | 7643 | 11 | 15 | 6 | 11 | 64 | 64
[25 empty] | 7644 | 11 | 15 | 6 | 12 | 64.9 | 65
[25 empty] | 7645 | 11 | 15 | 6 | 13 | 68 | 68
[25 empty] | 7646 | 11 | 15 | 6 | 14 | 68 | 68
[25 empty] | 7647 | 11 | 15 | 6 | 15 | 68 | 68
[25 empty] | 7648 | 11 | 15 | 6 | 16 | 66 | 66
[25 empty] | 7649 | 11 | 15 | 6 | 17 | 66 | 66
[25 empty] | 7650 | 11 | 15 | 6 | 18 | 61 | 61
[25 empty] | 7651 | 11 | 15 | 6 | 19 | 59 | 59
[25 empty] | 7652 | 11 | 15 | 6 | 20 | 57.9 | 58
[25 empty] | 7653 | 11 | 15 | 6 | 21 | 57 | 57
[25 empty] | 7654 | 11 | 15 | 6 | 22 | 55 | 55
[25 empty] | 7655 | 11 | 15 | 6 | 23 | 54 | 54
[25 empty] | 7656 | 11 | 16 | 7 | 0 | 53.1 | 53
[25 empty] | 7657 | 11 | 16 | 7 | 1 | 52 | 52
[25 empty] | 7658 | 11 | 16 | 7 | 2 | 51.1 | 51
[25 empty] | 7659 | 11 | 16 | 7 | 3 | 50 | 50
[25 empty] | 7660 | 11 | 16 | 7 | 4 | 48.9 | 49
[25 empty] | 7661 | 11 | 16 | 7 | 5 | 50 | 50
[25 empty] | 7662 | 11 | 16 | 7 | 6 | 50 | 50
[25 empty] | 7663 | 11 | 16 | 7 | 7 | 50 | 50
[25 empty] | 7664 | 11 | 16 | 7 | 8 | 48.9 | 49
[25 empty] | 7665 | 11 | 16 | 7 | 9 | 50 | 50
[25 empty] | 7666 | 11 | 16 | 7 | 10 | 50 | 50
[25 empty] | 7667 | 11 | 16 | 7 | 11 | 51.1 | 51
[25 empty] | 7668 | 11 | 16 | 7 | 12 | 51.1 | 51
[25 empty] | 7669 | 11 | 16 | 7 | 13 | 51.1 | 51
[25 empty] | 7670 | 11 | 16 | 7 | 14 | 50 | 50
[25 empty] | 7671 | 11 | 16 | 7 | 15 | 50 | 50
[25 empty] | 7672 | 11 | 16 | 7 | 16 | 50 | 50
[25 empty] | 7673 | 11 | 16 | 7 | 17 | 50 | 50
[25 empty] | 7674 | 11 | 16 | 7 | 18 | 50 | 50
[25 empty] | 7675 | 11 | 16 | 7 | 19 | 50 | 50
[25 empty] | 7676 | 11 | 16 | 7 | 20 | 52 | 52
[25 empty] | 7677 | 11 | 16 | 7 | 21 | 51.1 | 51
[25 empty] | 7678 | 11 | 16 | 7 | 22 | 50 | 50
[25 empty] | 7679 | 11 | 16 | 7 | 23 | 48.9 | 49
[25 empty] | 7680 | 11 | 17 | 1 | 0 | 48 | 48
[25 empty] | 7681 | 11 | 17 | 1 | 1 | 48.9 | 49
[25 empty] | 7682 | 11 | 17 | 1 | 2 | 48.9 | 49
[25 empty] | 7683 | 11 | 17 | 1 | 3 | 48.9 | 49
[25 empty] | 7684 | 11 | 17 | 1 | 4 | 48 | 48
[25 empty] | 7685 | 11 | 17 | 1 | 5 | 48 | 48
[25 empty] | 7686 | 11 | 17 | 1 | 6 | 48 | 48
[25 empty] | 7687 | 11 | 17 | 1 | 7 | 46 | 46
[25 empty] | 7688 | 11 | 17 | 1 | 8 | 46 | 46
[25 empty] | 7689 | 11 | 17 | 1 | 9 | 46.9 | 47
[25 empty] | 7690 | 11 | 17 | 1 | 10 | 50 | 50
[25 empty] | 7691 | 11 | 17 | 1 | 11 | 50 | 50
[25 empty] | 7692 | 11 | 17 | 1 | 12 | 52 | 52
[25 empty] | 7693 | 11 | 17 | 1 | 13 | 53.1 | 53
[25 empty] | 7694 | 11 | 17 | 1 | 14 | 55 | 55
[25 empty] | 7695 | 11 | 17 | 1 | 15 | 54 | 54
[25 empty] | 7696 | 11 | 17 | 1 | 16 | 54 | 54
[25 empty] | 7697 | 11 | 17 | 1 | 17 | 55 | 55
[25 empty] | 7698 | 11 | 17 | 1 | 18 | 54 | 54
[25 empty] | 7699 | 11 | 17 | 1 | 19 | 55 | 55
[25 empty] | 7700 | 11 | 17 | 1 | 20 | 55.9 | 56
[25 empty] | 7701 | 11 | 17 | 1 | 21 | 55 | 55
[25 empty] | 7702 | 11 | 17 | 1 | 22 | 54 | 54
[25 empty] | 7703 | 11 | 17 | 1 | 23 | 53.1 | 53
[25 empty] | 7704 | 11 | 18 | 2 | 0 | 53.1 | 53
[25 empty] | 7705 | 11 | 18 | 2 | 1 | 53.1 | 53
[25 empty] | 7706 | 11 | 18 | 2 | 2 | 52 | 52
[25 empty] | 7707 | 11 | 18 | 2 | 3 | 52 | 52
[25 empty] | 7708 | 11 | 18 | 2 | 4 | 52 | 52
[25 empty] | 7709 | 11 | 18 | 2 | 5 | 51.1 | 51
[25 empty] | 7710 | 11 | 18 | 2 | 6 | 51.1 | 51
[25 empty] | 7711 | 11 | 18 | 2 | 7 | 53.1 | 53
[25 empty] | 7712 | 11 | 18 | 2 | 8 | 53.1 | 53
[25 empty] | 7713 | 11 | 18 | 2 | 9 | 54 | 54
[25 empty] | 7714 | 11 | 18 | 2 | 10 | 54 | 54
[25 empty] | 7715 | 11 | 18 | 2 | 11 | 55 | 55
[25 empty] | 7716 | 11 | 18 | 2 | 12 | 55.9 | 56
[25 empty] | 7717 | 11 | 18 | 2 | 13 | 55 | 55
[25 empty] | 7718 | 11 | 18 | 2 | 14 | 55 | 55
[25 empty] | 7719 | 11 | 18 | 2 | 15 | 55.9 | 56
[25 empty] | 7720 | 11 | 18 | 2 | 16 | 57 | 57
[25 empty] | 7721 | 11 | 18 | 2 | 17 | 57 | 57
[25 empty] | 7722 | 11 | 18 | 2 | 18 | 57.9 | 58
[25 empty] | 7723 | 11 | 18 | 2 | 19 | 57 | 57
[25 empty] | 7724 | 11 | 18 | 2 | 20 | 60.1 | 60
[25 empty] | 7725 | 11 | 18 | 2 | 21 | 59 | 59
[25 empty] | 7726 | 11 | 18 | 2 | 22 | 60.1 | 60
[25 empty] | 7727 | 11 | 18 | 2 | 23 | 59 | 59
[25 empty] | 7728 | 11 | 19 | 3 | 0 | 57.9 | 58
[25 empty] | 7729 | 11 | 19 | 3 | 1 | 57.9 | 58
[25 empty] | 7730 | 11 | 19 | 3 | 2 | 59 | 59
[25 empty] | 7731 | 11 | 19 | 3 | 3 | 59 | 59
[25 empty] | 7732 | 11 | 19 | 3 | 4 | 59 | 59
[25 empty] | 7733 | 11 | 19 | 3 | 5 | 57.9 | 58
[25 empty] | 7734 | 11 | 19 | 3 | 6 | 57 | 57
[25 empty] | 7735 | 11 | 19 | 3 | 7 | 55.9 | 56
[25 empty] | 7736 | 11 | 19 | 3 | 8 | 55.9 | 56
[25 empty] | 7737 | 11 | 19 | 3 | 9 | 55.9 | 56
[25 empty] | 7738 | 11 | 19 | 3 | 10 | 57 | 57
[25 empty] | 7739 | 11 | 19 | 3 | 11 | 57 | 57
[25 empty] | 7740 | 11 | 19 | 3 | 12 | 57.9 | 58
[25 empty] | 7741 | 11 | 19 | 3 | 13 | 60.1 | 60
[25 empty] | 7742 | 11 | 19 | 3 | 14 | 60.1 | 60
[25 empty] | 7743 | 11 | 19 | 3 | 15 | 60.1 | 60
[25 empty] | 7744 | 11 | 19 | 3 | 16 | 60.1 | 60
[25 empty] | 7745 | 11 | 19 | 3 | 17 | 59 | 59
[25 empty] | 7746 | 11 | 19 | 3 | 18 | 57 | 57
[25 empty] | 7747 | 11 | 19 | 3 | 19 | 55.9 | 56
[25 empty] | 7748 | 11 | 19 | 3 | 20 | 54 | 54
[25 empty] | 7749 | 11 | 19 | 3 | 21 | 53.1 | 53
[25 empty] | 7750 | 11 | 19 | 3 | 22 | 52 | 52
[25 empty] | 7751 | 11 | 19 | 3 | 23 | 51.1 | 51
[25 empty] | 7752 | 11 | 20 | 4 | 0 | 50 | 50
[25 empty] | 7753 | 11 | 20 | 4 | 1 | 48.9 | 49
[25 empty] | 7754 | 11 | 20 | 4 | 2 | 48 | 48
[25 empty] | 7755 | 11 | 20 | 4 | 3 | 46.9 | 47
[25 empty] | 7756 | 11 | 20 | 4 | 4 | 46.9 | 47
[25 empty] | 7757 | 11 | 20 | 4 | 5 | 46.9 | 47
[25 empty] | 7758 | 11 | 20 | 4 | 6 | 46.9 | 47
[25 empty] | 7759 | 11 | 20 | 4 | 7 | 46 | 46
[25 empty] | 7760 | 11 | 20 | 4 | 8 | 46 | 46
[25 empty] | 7761 | 11 | 20 | 4 | 9 | 46.9 | 47
[25 empty] | 7762 | 11 | 20 | 4 | 10 | 48 | 48
[25 empty] | 7763 | 11 | 20 | 4 | 11 | 48 | 48
[25 empty] | 7764 | 11 | 20 | 4 | 12 | 48.9 | 49
[25 empty] | 7765 | 11 | 20 | 4 | 13 | 50 | 50
[25 empty] | 7766 | 11 | 20 | 4 | 14 | 51.1 | 51
[25 empty] | 7767 | 11 | 20 | 4 | 15 | 51.1 | 51
[25 empty] | 7768 | 11 | 20 | 4 | 16 | 51.1 | 51
[25 empty] | 7769 | 11 | 20 | 4 | 17 | 51.1 | 51
[25 empty] | 7770 | 11 | 20 | 4 | 18 | 51.1 | 51
[25 empty] | 7771 | 11 | 20 | 4 | 19 | 51.1 | 51
[25 empty] | 7772 | 11 | 20 | 4 | 20 | 51.1 | 51
[25 empty] | 7773 | 11 | 20 | 4 | 21 | 50 | 50
[25 empty] | 7774 | 11 | 20 | 4 | 22 | 48 | 48
[25 empty] | 7775 | 11 | 20 | 4 | 23 | 48.9 | 49
[25 empty] | 7776 | 11 | 21 | 5 | 0 | 48 | 48
[25 empty] | 7777 | 11 | 21 | 5 | 1 | 46.9 | 47
[25 empty] | 7778 | 11 | 21 | 5 | 2 | 46.9 | 47
[25 empty] | 7779 | 11 | 21 | 5 | 3 | 46 | 46
[25 empty] | 7780 | 11 | 21 | 5 | 4 | 46 | 46
[25 empty] | 7781 | 11 | 21 | 5 | 5 | 46.9 | 47
[25 empty] | 7782 | 11 | 21 | 5 | 6 | 48 | 48
[25 empty] | 7783 | 11 | 21 | 5 | 7 | 48 | 48
[25 empty] | 7784 | 11 | 21 | 5 | 8 | 53.1 | 53
[25 empty] | 7785 | 11 | 21 | 5 | 9 | 54 | 54
[25 empty] | 7786 | 11 | 21 | 5 | 10 | 55.9 | 56
[25 empty] | 7787 | 11 | 21 | 5 | 11 | 57 | 57
[25 empty] | 7788 | 11 | 21 | 5 | 12 | 57.9 | 58
[25 empty] | 7789 | 11 | 21 | 5 | 13 | 57.9 | 58
[25 empty] | 7790 | 11 | 21 | 5 | 14 | 57.9 | 58
[25 empty] | 7791 | 11 | 21 | 5 | 15 | 57.9 | 58
[25 empty] | 7792 | 11 | 21 | 5 | 16 | 59 | 59
[25 empty] | 7793 | 11 | 21 | 5 | 17 | 60.1 | 60
[25 empty] | 7794 | 11 | 21 | 5 | 18 | 61 | 61
[25 empty] | 7795 | 11 | 21 | 5 | 19 | 60.1 | 60
[25 empty] | 7796 | 11 | 21 | 5 | 20 | 61 | 61
[25 empty] | 7797 | 11 | 21 | 5 | 21 | 61 | 61
[25 empty] | 7798 | 11 | 21 | 5 | 22 | 61 | 61
[25 empty] | 7799 | 11 | 21 | 5 | 23 | 61 | 61
[25 empty] | 7800 | 11 | 22 | 6 | 0 | 62.1 | 62
[25 empty] | 7801 | 11 | 22 | 6 | 1 | 62.1 | 62
[25 empty] | 7802 | 11 | 22 | 6 | 2 | 62.1 | 62
[25 empty] | 7803 | 11 | 22 | 6 | 3 | 60.1 | 60
[25 empty] | 7804 | 11 | 22 | 6 | 4 | 57.9 | 58
[25 empty] | 7805 | 11 | 22 | 6 | 5 | 55.9 | 56
[25 empty] | 7806 | 11 | 22 | 6 | 6 | 55 | 55
[25 empty] | 7807 | 11 | 22 | 6 | 7 | 54 | 54
[25 empty] | 7808 | 11 | 22 | 6 | 8 | 53.1 | 53
[25 empty] | 7809 | 11 | 22 | 6 | 9 | 54 | 54
[25 empty] | 7810 | 11 | 22 | 6 | 10 | 55 | 55
[25 empty] | 7811 | 11 | 22 | 6 | 11 | 55 | 55
[25 empty] | 7812 | 11 | 22 | 6 | 12 | 55 | 55
[25 empty] | 7813 | 11 | 22 | 6 | 13 | 55.9 | 56
[25 empty] | 7814 | 11 | 22 | 6 | 14 | 55.9 | 56
[25 empty] | 7815 | 11 | 22 | 6 | 15 | 55 | 55
[25 empty] | 7816 | 11 | 22 | 6 | 16 | 54 | 54
[25 empty] | 7817 | 11 | 22 | 6 | 17 | 51.1 | 51
[25 empty] | 7818 | 11 | 22 | 6 | 18 | 50 | 50
[25 empty] | 7819 | 11 | 22 | 6 | 19 | 48 | 48
[25 empty] | 7820 | 11 | 22 | 6 | 20 | 46 | 46
[25 empty] | 7821 | 11 | 22 | 6 | 21 | 43 | 43
[25 empty] | 7822 | 11 | 22 | 6 | 22 | 42.1 | 42
[25 empty] | 7823 | 11 | 22 | 6 | 23 | 41 | 41
[25 empty] | 7824 | 11 | 23 | 7 | 0 | 39.9 | 40
[25 empty] | 7825 | 11 | 23 | 7 | 1 | 39 | 39
[25 empty] | 7826 | 11 | 23 | 7 | 2 | 37.9 | 38
[25 empty] | 7827 | 11 | 23 | 7 | 3 | 37 | 37
[25 empty] | 7828 | 11 | 23 | 7 | 4 | 37 | 37
[25 empty] | 7829 | 11 | 23 | 7 | 5 | 36 | 36
[25 empty] | 7830 | 11 | 23 | 7 | 6 | 36 | 36
[25 empty] | 7831 | 11 | 23 | 7 | 7 | 37 | 37
[25 empty] | 7832 | 11 | 23 | 7 | 8 | 37 | 37
[25 empty] | 7833 | 11 | 23 | 7 | 9 | 37.9 | 38
[25 empty] | 7834 | 11 | 23 | 7 | 10 | 41 | 41
[25 empty] | 7835 | 11 | 23 | 7 | 11 | 43 | 43
[25 empty] | 7836 | 11 | 23 | 7 | 12 | 45 | 45
[25 empty] | 7837 | 11 | 23 | 7 | 13 | 46 | 46
[25 empty] | 7838 | 11 | 23 | 7 | 14 | 46 | 46
[25 empty] | 7839 | 11 | 23 | 7 | 15 | 46 | 46
[25 empty] | 7840 | 11 | 23 | 7 | 16 | 44.1 | 44
[25 empty] | 7841 | 11 | 23 | 7 | 17 | 37.9 | 38
[25 empty] | 7842 | 11 | 23 | 7 | 18 | 37.9 | 38
[25 empty] | 7843 | 11 | 23 | 7 | 19 | 36 | 36
[25 empty] | 7844 | 11 | 23 | 7 | 20 | 34 | 34
[25 empty] | 7845 | 11 | 23 | 7 | 21 | 32 | 32
[25 empty] | 7846 | 11 | 23 | 7 | 22 | 30 | 30
[25 empty] | 7847 | 11 | 23 | 7 | 23 | 28.9 | 29
[25 empty] | 7848 | 11 | 24 | 1 | 0 | 28 | 28
[25 empty] | 7849 | 11 | 24 | 1 | 1 | 27 | 27
[25 empty] | 7850 | 11 | 24 | 1 | 2 | 26.1 | 26
[25 empty] | 7851 | 11 | 24 | 1 | 3 | 26.1 | 26
[25 empty] | 7852 | 11 | 24 | 1 | 4 | 27 | 27
[25 empty] | 7853 | 11 | 24 | 1 | 5 | 26.1 | 26
[25 empty] | 7854 | 11 | 24 | 1 | 6 | 26.1 | 26
[25 empty] | 7855 | 11 | 24 | 1 | 7 | 27 | 27
[25 empty] | 7856 | 11 | 24 | 1 | 8 | 28 | 28
[25 empty] | 7857 | 11 | 24 | 1 | 9 | 28.9 | 29
[25 empty] | 7858 | 11 | 24 | 1 | 10 | 30 | 30
[25 empty] | 7859 | 11 | 24 | 1 | 11 | 32 | 32
[25 empty] | 7860 | 11 | 24 | 1 | 12 | 35.1 | 35
[25 empty] | 7861 | 11 | 24 | 1 | 13 | 36 | 36
[25 empty] | 7862 | 11 | 24 | 1 | 14 | 37 | 37
[25 empty] | 7863 | 11 | 24 | 1 | 15 | 37.9 | 38
[25 empty] | 7864 | 11 | 24 | 1 | 16 | 39 | 39
[25 empty] | 7865 | 11 | 24 | 1 | 17 | 37.9 | 38
[25 empty] | 7866 | 11 | 24 | 1 | 18 | 37 | 37
[25 empty] | 7867 | 11 | 24 | 1 | 19 | 37 | 37
[25 empty] | 7868 | 11 | 24 | 1 | 20 | 37 | 37
[25 empty] | 7869 | 11 | 24 | 1 | 21 | 37.9 | 38
[25 empty] | 7870 | 11 | 24 | 1 | 22 | 37.9 | 38
[25 empty] | 7871 | 11 | 24 | 1 | 23 | 37.9 | 38
[25 empty] | 7872 | 11 | 25 | 2 | 0 | 37.9 | 38
[25 empty] | 7873 | 11 | 25 | 2 | 1 | 37.9 | 38
[25 empty] | 7874 | 11 | 25 | 2 | 2 | 39 | 39
[25 empty] | 7875 | 11 | 25 | 2 | 3 | 39 | 39
[25 empty] | 7876 | 11 | 25 | 2 | 4 | 39 | 39
[25 empty] | 7877 | 11 | 25 | 2 | 5 | 39.9 | 40
[25 empty] | 7878 | 11 | 25 | 2 | 6 | 39.9 | 40
[25 empty] | 7879 | 11 | 25 | 2 | 7 | 41 | 41
[25 empty] | 7880 | 11 | 25 | 2 | 8 | 42.1 | 42
[25 empty] | 7881 | 11 | 25 | 2 | 9 | 42.1 | 42
[25 empty] | 7882 | 11 | 25 | 2 | 10 | 44.1 | 44
[25 empty] | 7883 | 11 | 25 | 2 | 11 | 46 | 46
[25 empty] | 7884 | 11 | 25 | 2 | 12 | 48.9 | 49
[25 empty] | 7885 | 11 | 25 | 2 | 13 | 50 | 50
[25 empty] | 7886 | 11 | 25 | 2 | 14 | 51.1 | 51
[25 empty] | 7887 | 11 | 25 | 2 | 15 | 51.1 | 51
[25 empty] | 7888 | 11 | 25 | 2 | 16 | 52 | 52
[25 empty] | 7889 | 11 | 25 | 2 | 17 | 51.1 | 51
[25 empty] | 7890 | 11 | 25 | 2 | 18 | 50 | 50
[25 empty] | 7891 | 11 | 25 | 2 | 19 | 48.9 | 49
[25 empty] | 7892 | 11 | 25 | 2 | 20 | 48.9 | 49
[25 empty] | 7893 | 11 | 25 | 2 | 21 | 48 | 48
[25 empty] | 7894 | 11 | 25 | 2 | 22 | 46.9 | 47
[25 empty] | 7895 | 11 | 25 | 2 | 23 | 46 | 46
[25 empty] | 7896 | 11 | 26 | 3 | 0 | 46 | 46
[25 empty] | 7897 | 11 | 26 | 3 | 1 | 46.9 | 47
[25 empty] | 7898 | 11 | 26 | 3 | 2 | 46 | 46
[25 empty] | 7899 | 11 | 26 | 3 | 3 | 45 | 45
[25 empty] | 7900 | 11 | 26 | 3 | 4 | 43 | 43
[25 empty] | 7901 | 11 | 26 | 3 | 5 | 43 | 43
[25 empty] | 7902 | 11 | 26 | 3 | 6 | 43 | 43
[25 empty] | 7903 | 11 | 26 | 3 | 7 | 42.1 | 42
[25 empty] | 7904 | 11 | 26 | 3 | 8 | 42.1 | 42
[25 empty] | 7905 | 11 | 26 | 3 | 9 | 43 | 43
[25 empty] | 7906 | 11 | 26 | 3 | 10 | 44.1 | 44
[25 empty] | 7907 | 11 | 26 | 3 | 11 | 45 | 45
[25 empty] | 7908 | 11 | 26 | 3 | 12 | 45 | 45
[25 empty] | 7909 | 11 | 26 | 3 | 13 | 44.1 | 44
[25 empty] | 7910 | 11 | 26 | 3 | 14 | 45 | 45
[25 empty] | 7911 | 11 | 26 | 3 | 15 | 44.1 | 44
[25 empty] | 7912 | 11 | 26 | 3 | 16 | 44.1 | 44
[25 empty] | 7913 | 11 | 26 | 3 | 17 | 42.1 | 42
[25 empty] | 7914 | 11 | 26 | 3 | 18 | 41 | 41
[25 empty] | 7915 | 11 | 26 | 3 | 19 | 39 | 39
[25 empty] | 7916 | 11 | 26 | 3 | 20 | 37.9 | 38
[25 empty] | 7917 | 11 | 26 | 3 | 21 | 36 | 36
[25 empty] | 7918 | 11 | 26 | 3 | 22 | 35.1 | 35
[25 empty] | 7919 | 11 | 26 | 3 | 23 | 34 | 34
[25 empty] | 7920 | 11 | 27 | 4 | 0 | 33.1 | 33
[25 empty] | 7921 | 11 | 27 | 4 | 1 | 32 | 32
[25 empty] | 7922 | 11 | 27 | 4 | 2 | 30.9 | 31
[25 empty] | 7923 | 11 | 27 | 4 | 3 | 30 | 30
[25 empty] | 7924 | 11 | 27 | 4 | 4 | 28 | 28
[25 empty] | 7925 | 11 | 27 | 4 | 5 | 28 | 28
[25 empty] | 7926 | 11 | 27 | 4 | 6 | 27 | 27
[25 empty] | 7927 | 11 | 27 | 4 | 7 | 27 | 27
[25 empty] | 7928 | 11 | 27 | 4 | 8 | 27 | 27
[25 empty] | 7929 | 11 | 27 | 4 | 9 | 28 | 28
[25 empty] | 7930 | 11 | 27 | 4 | 10 | 30 | 30
[25 empty] | 7931 | 11 | 27 | 4 | 11 | 30.9 | 31
[25 empty] | 7932 | 11 | 27 | 4 | 12 | 33.1 | 33
[25 empty] | 7933 | 11 | 27 | 4 | 13 | 34 | 34
[25 empty] | 7934 | 11 | 27 | 4 | 14 | 35.1 | 35
[25 empty] | 7935 | 11 | 27 | 4 | 15 | 36 | 36
[25 empty] | 7936 | 11 | 27 | 4 | 16 | 37 | 37
[25 empty] | 7937 | 11 | 27 | 4 | 17 | 37.9 | 38
[25 empty] | 7938 | 11 | 27 | 4 | 18 | 39 | 39
[25 empty] | 7939 | 11 | 27 | 4 | 19 | 41 | 41
[25 empty] | 7940 | 11 | 27 | 4 | 20 | 41 | 41
[25 empty] | 7941 | 11 | 27 | 4 | 21 | 41 | 41
[25 empty] | 7942 | 11 | 27 | 4 | 22 | 44.1 | 44
[25 empty] | 7943 | 11 | 27 | 4 | 23 | 44.1 | 44
[25 empty] | 7944 | 11 | 28 | 5 | 0 | 44.1 | 44
[25 empty] | 7945 | 11 | 28 | 5 | 1 | 44.1 | 44
[25 empty] | 7946 | 11 | 28 | 5 | 2 | 43 | 43
[25 empty] | 7947 | 11 | 28 | 5 | 3 | 45 | 45
[25 empty] | 7948 | 11 | 28 | 5 | 4 | 46 | 46
[25 empty] | 7949 | 11 | 28 | 5 | 5 | 46.9 | 47
[25 empty] | 7950 | 11 | 28 | 5 | 6 | 48 | 48
[25 empty] | 7951 | 11 | 28 | 5 | 7 | 48.9 | 49
[25 empty] | 7952 | 11 | 28 | 5 | 8 | 48.9 | 49
[25 empty] | 7953 | 11 | 28 | 5 | 9 | 50 | 50
[25 empty] | 7954 | 11 | 28 | 5 | 10 | 53.1 | 53
[25 empty] | 7955 | 11 | 28 | 5 | 11 | 57.9 | 58
[25 empty] | 7956 | 11 | 28 | 5 | 12 | 57.9 | 58
[25 empty] | 7957 | 11 | 28 | 5 | 13 | 59 | 59
[25 empty] | 7958 | 11 | 28 | 5 | 14 | 62.1 | 62
[25 empty] | 7959 | 11 | 28 | 5 | 15 | 61 | 61
[25 empty] | 7960 | 11 | 28 | 5 | 16 | 62.1 | 62
[25 empty] | 7961 | 11 | 28 | 5 | 17 | 63 | 63
[25 empty] | 7962 | 11 | 28 | 5 | 18 | 64.9 | 65
[25 empty] | 7963 | 11 | 28 | 5 | 19 | 59 | 59
[25 empty] | 7964 | 11 | 28 | 5 | 20 | 57.9 | 58
[25 empty] | 7965 | 11 | 28 | 5 | 21 | 57 | 57
[25 empty] | 7966 | 11 | 28 | 5 | 22 | 55.9 | 56
[25 empty] | 7967 | 11 | 28 | 5 | 23 | 55 | 55
[25 empty] | 7968 | 11 | 29 | 6 | 0 | 55 | 55
[25 empty] | 7969 | 11 | 29 | 6 | 1 | 55 | 55
[25 empty] | 7970 | 11 | 29 | 6 | 2 | 53.1 | 53
[25 empty] | 7971 | 11 | 29 | 6 | 3 | 52 | 52
[25 empty] | 7972 | 11 | 29 | 6 | 4 | 51.1 | 51
[25 empty] | 7973 | 11 | 29 | 6 | 5 | 50 | 50
[25 empty] | 7974 | 11 | 29 | 6 | 6 | 50 | 50
[25 empty] | 7975 | 11 | 29 | 6 | 7 | 48 | 48
[25 empty] | 7976 | 11 | 29 | 6 | 8 | 48.9 | 49
[25 empty] | 7977 | 11 | 29 | 6 | 9 | 50 | 50
[25 empty] | 7978 | 11 | 29 | 6 | 10 | 53.1 | 53
[25 empty] | 7979 | 11 | 29 | 6 | 11 | 54 | 54
[25 empty] | 7980 | 11 | 29 | 6 | 12 | 55 | 55
[25 empty] | 7981 | 11 | 29 | 6 | 13 | 55 | 55
[25 empty] | 7982 | 11 | 29 | 6 | 14 | 55.9 | 56
[25 empty] | 7983 | 11 | 29 | 6 | 15 | 55 | 55
[25 empty] | 7984 | 11 | 29 | 6 | 16 | 55 | 55
[25 empty] | 7985 | 11 | 29 | 6 | 17 | 54 | 54
[25 empty] | 7986 | 11 | 29 | 6 | 18 | 53.1 | 53
[25 empty] | 7987 | 11 | 29 | 6 | 19 | 53.1 | 53
[25 empty] | 7988 | 11 | 29 | 6 | 20 | 53.1 | 53
[25 empty] | 7989 | 11 | 29 | 6 | 21 | 52 | 52
[25 empty] | 7990 | 11 | 29 | 6 | 22 | 52 | 52
[25 empty] | 7991 | 11 | 29 | 6 | 23 | 52 | 52
[25 empty] | 7992 | 11 | 30 | 7 | 0 | 51.1 | 51
[25 empty] | 7993 | 11 | 30 | 7 | 1 | 50 | 50
[25 empty] | 7994 | 11 | 30 | 7 | 2 | 48.9 | 49
[25 empty] | 7995 | 11 | 30 | 7 | 3 | 48 | 48
[25 empty] | 7996 | 11 | 30 | 7 | 4 | 46.9 | 47
[25 empty] | 7997 | 11 | 30 | 7 | 5 | 46.9 | 47
[25 empty] | 7998 | 11 | 30 | 7 | 6 | 48 | 48
[25 empty] | 7999 | 11 | 30 | 7 | 7 | 48 | 48
[25 empty] | 8000 | 11 | 30 | 7 | 8 | 48 | 48
[25 empty] | 8001 | 11 | 30 | 7 | 9 | 48 | 48
[25 empty] | 8002 | 11 | 30 | 7 | 10 | 48.9 | 49
[25 empty] | 8003 | 11 | 30 | 7 | 11 | 50 | 50
[25 empty] | 8004 | 11 | 30 | 7 | 12 | 51.1 | 51
[25 empty] | 8005 | 11 | 30 | 7 | 13 | 51.1 | 51
[25 empty] | 8006 | 11 | 30 | 7 | 14 | 51.1 | 51
[25 empty] | 8007 | 11 | 30 | 7 | 15 | 51.1 | 51
[25 empty] | 8008 | 11 | 30 | 7 | 16 | 50 | 50
[25 empty] | 8009 | 11 | 30 | 7 | 17 | 48 | 48
[25 empty] | 8010 | 11 | 30 | 7 | 18 | 48 | 48
[25 empty] | 8011 | 11 | 30 | 7 | 19 | 46 | 46
[25 empty] | 8012 | 11 | 30 | 7 | 20 | 44.1 | 44
[25 empty] | 8013 | 11 | 30 | 7 | 21 | 42.1 | 42
[25 empty] | 8014 | 11 | 30 | 7 | 22 | 42.6 | 43
[25 empty] | 8015 | 11 | 30 | 7 | 23 | 43.2 | 43
[25 empty] | 8016 | 12 | 1 | 1 | 0 | 43.7 | 44
[25 empty] | 8017 | 12 | 1 | 1 | 1 | 44.4 | 44
[25 empty] | 8018 | 12 | 1 | 1 | 2 | 45 | 45
[25 empty] | 8019 | 12 | 1 | 1 | 3 | 45.5 | 46
[25 empty] | 8020 | 12 | 1 | 1 | 4 | 46 | 46
[25 empty] | 8021 | 12 | 1 | 1 | 5 | 46.9 | 47
[25 empty] | 8022 | 12 | 1 | 1 | 6 | 48 | 48
[25 empty] | 8023 | 12 | 1 | 1 | 7 | 48 | 48
[25 empty] | 8024 | 12 | 1 | 1 | 8 | 50 | 50
[25 empty] | 8025 | 12 | 1 | 1 | 9 | 50 | 50
[25 empty] | 8026 | 12 | 1 | 1 | 10 | 51.1 | 51
[25 empty] | 8027 | 12 | 1 | 1 | 11 | 46.9 | 47
[25 empty] | 8028 | 12 | 1 | 1 | 12 | 46.9 | 47
[25 empty] | 8029 | 12 | 1 | 1 | 13 | 50 | 50
[25 empty] | 8030 | 12 | 1 | 1 | 14 | 48.9 | 49
[25 empty] | 8031 | 12 | 1 | 1 | 15 | 43 | 43
[25 empty] | 8032 | 12 | 1 | 1 | 16 | 43 | 43
[25 empty] | 8033 | 12 | 1 | 1 | 17 | 42.1 | 42
[25 empty] | 8034 | 12 | 1 | 1 | 18 | 39.9 | 40
[25 empty] | 8035 | 12 | 1 | 1 | 19 | 39.9 | 40
[25 empty] | 8036 | 12 | 1 | 1 | 20 | 39.9 | 40
[25 empty] | 8037 | 12 | 1 | 1 | 21 | 37.9 | 38
[25 empty] | 8038 | 12 | 1 | 1 | 22 | 37.9 | 38
[25 empty] | 8039 | 12 | 1 | 1 | 23 | 37 | 37
[25 empty] | 8040 | 12 | 2 | 2 | 0 | 37 | 37
[25 empty] | 8041 | 12 | 2 | 2 | 1 | 37 | 37
[25 empty] | 8042 | 12 | 2 | 2 | 2 | 37 | 37
[25 empty] | 8043 | 12 | 2 | 2 | 3 | 36 | 36
[25 empty] | 8044 | 12 | 2 | 2 | 4 | 36 | 36
[25 empty] | 8045 | 12 | 2 | 2 | 5 | 35.1 | 35
[25 empty] | 8046 | 12 | 2 | 2 | 6 | 35.1 | 35
[25 empty] | 8047 | 12 | 2 | 2 | 7 | 35.1 | 35
[25 empty] | 8048 | 12 | 2 | 2 | 8 | 30.9 | 31
[25 empty] | 8049 | 12 | 2 | 2 | 9 | 34 | 34
[25 empty] | 8050 | 12 | 2 | 2 | 10 | 35.1 | 35
[25 empty] | 8051 | 12 | 2 | 2 | 11 | 36 | 36
[25 empty] | 8052 | 12 | 2 | 2 | 12 | 34 | 34
[25 empty] | 8053 | 12 | 2 | 2 | 13 | 36 | 36
[25 empty] | 8054 | 12 | 2 | 2 | 14 | 33.1 | 33
[25 empty] | 8055 | 12 | 2 | 2 | 15 | 34 | 34
[25 empty] | 8056 | 12 | 2 | 2 | 16 | 32 | 32
[25 empty] | 8057 | 12 | 2 | 2 | 17 | 30.9 | 31
[25 empty] | 8058 | 12 | 2 | 2 | 18 | 30 | 30
[25 empty] | 8059 | 12 | 2 | 2 | 19 | 28.9 | 29
[25 empty] | 8060 | 12 | 2 | 2 | 20 | 28 | 28
[25 empty] | 8061 | 12 | 2 | 2 | 21 | 26.1 | 26
[25 empty] | 8062 | 12 | 2 | 2 | 22 | 26.1 | 26
[25 empty] | 8063 | 12 | 2 | 2 | 23 | 25 | 25
[25 empty] | 8064 | 12 | 3 | 3 | 0 | 24.1 | 24
[25 empty] | 8065 | 12 | 3 | 3 | 1 | 24.1 | 24
[25 empty] | 8066 | 12 | 3 | 3 | 2 | 24.1 | 24
[25 empty] | 8067 | 12 | 3 | 3 | 3 | 23 | 23
[25 empty] | 8068 | 12 | 3 | 3 | 4 | 23 | 23
[25 empty] | 8069 | 12 | 3 | 3 | 5 | 23 | 23
[25 empty] | 8070 | 12 | 3 | 3 | 6 | 23 | 23
[25 empty] | 8071 | 12 | 3 | 3 | 7 | 23 | 23
[25 empty] | 8072 | 12 | 3 | 3 | 8 | 23 | 23
[25 empty] | 8073 | 12 | 3 | 3 | 9 | 24.1 | 24
[25 empty] | 8074 | 12 | 3 | 3 | 10 | 25 | 25
[25 empty] | 8075 | 12 | 3 | 3 | 11 | 26.1 | 26
[25 empty] | 8076 | 12 | 3 | 3 | 12 | 28 | 28
[25 empty] | 8077 | 12 | 3 | 3 | 13 | 30 | 30
[25 empty] | 8078 | 12 | 3 | 3 | 14 | 30.9 | 31
[25 empty] | 8079 | 12 | 3 | 3 | 15 | 32 | 32
[25 empty] | 8080 | 12 | 3 | 3 | 16 | 32 | 32
[25 empty] | 8081 | 12 | 3 | 3 | 17 | 32 | 32
[25 empty] | 8082 | 12 | 3 | 3 | 18 | 30.9 | 31
[25 empty] | 8083 | 12 | 3 | 3 | 19 | 30.9 | 31
[25 empty] | 8084 | 12 | 3 | 3 | 20 | 30.9 | 31
[25 empty] | 8085 | 12 | 3 | 3 | 21 | 30 | 30
[25 empty] | 8086 | 12 | 3 | 3 | 22 | 28.9 | 29
[25 empty] | 8087 | 12 | 3 | 3 | 23 | 28.9 | 29
[25 empty] | 8088 | 12 | 4 | 4 | 0 | 28.9 | 29
[25 empty] | 8089 | 12 | 4 | 4 | 1 | 28.9 | 29
[25 empty] | 8090 | 12 | 4 | 4 | 2 | 28.9 | 29
[25 empty] | 8091 | 12 | 4 | 4 | 3 | 28.9 | 29
[25 empty] | 8092 | 12 | 4 | 4 | 4 | 30 | 30
[25 empty] | 8093 | 12 | 4 | 4 | 5 | 30 | 30
[25 empty] | 8094 | 12 | 4 | 4 | 6 | 30 | 30
[25 empty] | 8095 | 12 | 4 | 4 | 7 | 30 | 30
[25 empty] | 8096 | 12 | 4 | 4 | 8 | 32 | 32
[25 empty] | 8097 | 12 | 4 | 4 | 9 | 34 | 34
[25 empty] | 8098 | 12 | 4 | 4 | 10 | 35.1 | 35
[25 empty] | 8099 | 12 | 4 | 4 | 11 | 36 | 36
[25 empty] | 8100 | 12 | 4 | 4 | 12 | 37.9 | 38
[25 empty] | 8101 | 12 | 4 | 4 | 13 | 39.9 | 40
[25 empty] | 8102 | 12 | 4 | 4 | 14 | 41 | 41
[25 empty] | 8103 | 12 | 4 | 4 | 15 | 42.1 | 42
[25 empty] | 8104 | 12 | 4 | 4 | 16 | 41 | 41
[25 empty] | 8105 | 12 | 4 | 4 | 17 | 41 | 41
[25 empty] | 8106 | 12 | 4 | 4 | 18 | 39.9 | 40
[25 empty] | 8107 | 12 | 4 | 4 | 19 | 39 | 39
[25 empty] | 8108 | 12 | 4 | 4 | 20 | 37 | 37
[25 empty] | 8109 | 12 | 4 | 4 | 21 | 37.9 | 38
[25 empty] | 8110 | 12 | 4 | 4 | 22 | 37.9 | 38
[25 empty] | 8111 | 12 | 4 | 4 | 23 | 37 | 37
[25 empty] | 8112 | 12 | 5 | 5 | 0 | 36 | 36
[25 empty] | 8113 | 12 | 5 | 5 | 1 | 37 | 37
[25 empty] | 8114 | 12 | 5 | 5 | 2 | 35.1 | 35
[25 empty] | 8115 | 12 | 5 | 5 | 3 | 35.1 | 35
[25 empty] | 8116 | 12 | 5 | 5 | 4 | 34 | 34
[25 empty] | 8117 | 12 | 5 | 5 | 5 | 34 | 34
[25 empty] | 8118 | 12 | 5 | 5 | 6 | 34 | 34
[25 empty] | 8119 | 12 | 5 | 5 | 7 | 35.1 | 35
[25 empty] | 8120 | 12 | 5 | 5 | 8 | 34 | 34
[25 empty] | 8121 | 12 | 5 | 5 | 9 | 34 | 34
[25 empty] | 8122 | 12 | 5 | 5 | 10 | 34 | 34
[25 empty] | 8123 | 12 | 5 | 5 | 11 | 33.1 | 33
[25 empty] | 8124 | 12 | 5 | 5 | 12 | 32 | 32
[25 empty] | 8125 | 12 | 5 | 5 | 13 | 30 | 30
[25 empty] | 8126 | 12 | 5 | 5 | 14 | 28.9 | 29
[25 empty] | 8127 | 12 | 5 | 5 | 15 | 28.9 | 29
[25 empty] | 8128 | 12 | 5 | 5 | 16 | 28.9 | 29
[25 empty] | 8129 | 12 | 5 | 5 | 17 | 28 | 28
[25 empty] | 8130 | 12 | 5 | 5 | 18 | 28.9 | 29
[25 empty] | 8131 | 12 | 5 | 5 | 19 | 27 | 27
[25 empty] | 8132 | 12 | 5 | 5 | 20 | 28 | 28
[25 empty] | 8133 | 12 | 5 | 5 | 21 | 30 | 30
[25 empty] | 8134 | 12 | 5 | 5 | 22 | 32 | 32
[25 empty] | 8135 | 12 | 5 | 5 | 23 | 30.9 | 31
[25 empty] | 8136 | 12 | 6 | 6 | 0 | 30 | 30
[25 empty] | 8137 | 12 | 6 | 6 | 1 | 30 | 30
[25 empty] | 8138 | 12 | 6 | 6 | 2 | 28.9 | 29
[25 empty] | 8139 | 12 | 6 | 6 | 3 | 28.9 | 29
[25 empty] | 8140 | 12 | 6 | 6 | 4 | 28.9 | 29
[25 empty] | 8141 | 12 | 6 | 6 | 5 | 28.9 | 29
[25 empty] | 8142 | 12 | 6 | 6 | 6 | 28 | 28
[25 empty] | 8143 | 12 | 6 | 6 | 7 | 28 | 28
[25 empty] | 8144 | 12 | 6 | 6 | 8 | 28 | 28
[25 empty] | 8145 | 12 | 6 | 6 | 9 | 26.1 | 26
[25 empty] | 8146 | 12 | 6 | 6 | 10 | 25 | 25
[25 empty] | 8147 | 12 | 6 | 6 | 11 | 25 | 25
[25 empty] | 8148 | 12 | 6 | 6 | 12 | 26.1 | 26
[25 empty] | 8149 | 12 | 6 | 6 | 13 | 25 | 25
[25 empty] | 8150 | 12 | 6 | 6 | 14 | 26.1 | 26
[25 empty] | 8151 | 12 | 6 | 6 | 15 | 26.1 | 26
[25 empty] | 8152 | 12 | 6 | 6 | 16 | 26.1 | 26
[25 empty] | 8153 | 12 | 6 | 6 | 17 | 27 | 27
[25 empty] | 8154 | 12 | 6 | 6 | 18 | 27 | 27
[25 empty] | 8155 | 12 | 6 | 6 | 19 | 28 | 28
[25 empty] | 8156 | 12 | 6 | 6 | 20 | 27 | 27
[25 empty] | 8157 | 12 | 6 | 6 | 21 | 27 | 27
[25 empty] | 8158 | 12 | 6 | 6 | 22 | 27 | 27
[25 empty] | 8159 | 12 | 6 | 6 | 23 | 28 | 28
[25 empty] | 8160 | 12 | 7 | 7 | 0 | 28 | 28
[25 empty] | 8161 | 12 | 7 | 7 | 1 | 28 | 28
[25 empty] | 8162 | 12 | 7 | 7 | 2 | 28 | 28
[25 empty] | 8163 | 12 | 7 | 7 | 3 | 27 | 27
[25 empty] | 8164 | 12 | 7 | 7 | 4 | 26.1 | 26
[25 empty] | 8165 | 12 | 7 | 7 | 5 | 27 | 27
[25 empty] | 8166 | 12 | 7 | 7 | 6 | 26.1 | 26
[25 empty] | 8167 | 12 | 7 | 7 | 7 | 26.1 | 26
[25 empty] | 8168 | 12 | 7 | 7 | 8 | 26.1 | 26
[25 empty] | 8169 | 12 | 7 | 7 | 9 | 24.1 | 24
[25 empty] | 8170 | 12 | 7 | 7 | 10 | 26.1 | 26
[25 empty] | 8171 | 12 | 7 | 7 | 11 | 27 | 27
[25 empty] | 8172 | 12 | 7 | 7 | 12 | 28.9 | 29
[25 empty] | 8173 | 12 | 7 | 7 | 13 | 30 | 30
[25 empty] | 8174 | 12 | 7 | 7 | 14 | 30.9 | 31
[25 empty] | 8175 | 12 | 7 | 7 | 15 | 30.9 | 31
[25 empty] | 8176 | 12 | 7 | 7 | 16 | 30.9 | 31
[25 empty] | 8177 | 12 | 7 | 7 | 17 | 30 | 30
[25 empty] | 8178 | 12 | 7 | 7 | 18 | 30 | 30
[25 empty] | 8179 | 12 | 7 | 7 | 19 | 30 | 30
[25 empty] | 8180 | 12 | 7 | 7 | 20 | 28 | 28
[25 empty] | 8181 | 12 | 7 | 7 | 21 | 28 | 28
[25 empty] | 8182 | 12 | 7 | 7 | 22 | 27 | 27
[25 empty] | 8183 | 12 | 7 | 7 | 23 | 27 | 27
[25 empty] | 8184 | 12 | 8 | 1 | 0 | 27 | 27
[25 empty] | 8185 | 12 | 8 | 1 | 1 | 26.1 | 26
[25 empty] | 8186 | 12 | 8 | 1 | 2 | 26.1 | 26
[25 empty] | 8187 | 12 | 8 | 1 | 3 | 25 | 25
[25 empty] | 8188 | 12 | 8 | 1 | 4 | 25 | 25
[25 empty] | 8189 | 12 | 8 | 1 | 5 | 25 | 25
[25 empty] | 8190 | 12 | 8 | 1 | 6 | 26.1 | 26
[25 empty] | 8191 | 12 | 8 | 1 | 7 | 26.1 | 26
[25 empty] | 8192 | 12 | 8 | 1 | 8 | 26.1 | 26
[25 empty] | 8193 | 12 | 8 | 1 | 9 | 28 | 28
[25 empty] | 8194 | 12 | 8 | 1 | 10 | 28.9 | 29
[25 empty] | 8195 | 12 | 8 | 1 | 11 | 32 | 32
[25 empty] | 8196 | 12 | 8 | 1 | 12 | 34 | 34
[25 empty] | 8197 | 12 | 8 | 1 | 13 | 35.1 | 35
[25 empty] | 8198 | 12 | 8 | 1 | 14 | 37 | 37
[25 empty] | 8199 | 12 | 8 | 1 | 15 | 37 | 37
[25 empty] | 8200 | 12 | 8 | 1 | 16 | 37 | 37
[25 empty] | 8201 | 12 | 8 | 1 | 17 | 37 | 37
[25 empty] | 8202 | 12 | 8 | 1 | 18 | 36 | 36
[25 empty] | 8203 | 12 | 8 | 1 | 19 | 36 | 36
[25 empty] | 8204 | 12 | 8 | 1 | 20 | 35.1 | 35
[25 empty] | 8205 | 12 | 8 | 1 | 21 | 37 | 37
[25 empty] | 8206 | 12 | 8 | 1 | 22 | 36 | 36
[25 empty] | 8207 | 12 | 8 | 1 | 23 | 35.1 | 35
[25 empty] | 8208 | 12 | 9 | 2 | 0 | 34 | 34
[25 empty] | 8209 | 12 | 9 | 2 | 1 | 33.1 | 33
[25 empty] | 8210 | 12 | 9 | 2 | 2 | 33.1 | 33
[25 empty] | 8211 | 12 | 9 | 2 | 3 | 33.1 | 33
[25 empty] | 8212 | 12 | 9 | 2 | 4 | 33.1 | 33
[25 empty] | 8213 | 12 | 9 | 2 | 5 | 32 | 32
[25 empty] | 8214 | 12 | 9 | 2 | 6 | 32 | 32
[25 empty] | 8215 | 12 | 9 | 2 | 7 | 32 | 32
[25 empty] | 8216 | 12 | 9 | 2 | 8 | 32 | 32
[25 empty] | 8217 | 12 | 9 | 2 | 9 | 33.1 | 33
[25 empty] | 8218 | 12 | 9 | 2 | 10 | 33.1 | 33
[25 empty] | 8219 | 12 | 9 | 2 | 11 | 34 | 34
[25 empty] | 8220 | 12 | 9 | 2 | 12 | 34 | 34
[25 empty] | 8221 | 12 | 9 | 2 | 13 | 35.1 | 35
[25 empty] | 8222 | 12 | 9 | 2 | 14 | 36 | 36
[25 empty] | 8223 | 12 | 9 | 2 | 15 | 36 | 36
[25 empty] | 8224 | 12 | 9 | 2 | 16 | 36 | 36
[25 empty] | 8225 | 12 | 9 | 2 | 17 | 37 | 37
[25 empty] | 8226 | 12 | 9 | 2 | 18 | 37.9 | 38
[25 empty] | 8227 | 12 | 9 | 2 | 19 | 37 | 37
[25 empty] | 8228 | 12 | 9 | 2 | 20 | 37 | 37
[25 empty] | 8229 | 12 | 9 | 2 | 21 | 37 | 37
[25 empty] | 8230 | 12 | 9 | 2 | 22 | 37 | 37
[25 empty] | 8231 | 12 | 9 | 2 | 23 | 37 | 37
[25 empty] | 8232 | 12 | 10 | 3 | 0 | 36 | 36
[25 empty] | 8233 | 12 | 10 | 3 | 1 | 37 | 37
[25 empty] | 8234 | 12 | 10 | 3 | 2 | 37 | 37
[25 empty] | 8235 | 12 | 10 | 3 | 3 | 37 | 37
[25 empty] | 8236 | 12 | 10 | 3 | 4 | 37 | 37
[25 empty] | 8237 | 12 | 10 | 3 | 5 | 36 | 36
[25 empty] | 8238 | 12 | 10 | 3 | 6 | 37 | 37
[25 empty] | 8239 | 12 | 10 | 3 | 7 | 37.9 | 38
[25 empty] | 8240 | 12 | 10 | 3 | 8 | 37.9 | 38
[25 empty] | 8241 | 12 | 10 | 3 | 9 | 39.9 | 40
[25 empty] | 8242 | 12 | 10 | 3 | 10 | 41 | 41
[25 empty] | 8243 | 12 | 10 | 3 | 11 | 43 | 43
[25 empty] | 8244 | 12 | 10 | 3 | 12 | 43 | 43
[25 empty] | 8245 | 12 | 10 | 3 | 13 | 44.1 | 44
[25 empty] | 8246 | 12 | 10 | 3 | 14 | 46.9 | 47
[25 empty] | 8247 | 12 | 10 | 3 | 15 | 48.9 | 49
[25 empty] | 8248 | 12 | 10 | 3 | 16 | 50 | 50
[25 empty] | 8249 | 12 | 10 | 3 | 17 | 50 | 50
[25 empty] | 8250 | 12 | 10 | 3 | 18 | 48 | 48
[25 empty] | 8251 | 12 | 10 | 3 | 19 | 48.9 | 49
[25 empty] | 8252 | 12 | 10 | 3 | 20 | 50 | 50
[25 empty] | 8253 | 12 | 10 | 3 | 21 | 50 | 50
[25 empty] | 8254 | 12 | 10 | 3 | 22 | 51.1 | 51
[25 empty] | 8255 | 12 | 10 | 3 | 23 | 52 | 52
[25 empty] | 8256 | 12 | 11 | 4 | 0 | 52 | 52
[25 empty] | 8257 | 12 | 11 | 4 | 1 | 52 | 52
[25 empty] | 8258 | 12 | 11 | 4 | 2 | 53.1 | 53
[25 empty] | 8259 | 12 | 11 | 4 | 3 | 53.1 | 53
[25 empty] | 8260 | 12 | 11 | 4 | 4 | 53.1 | 53
[25 empty] | 8261 | 12 | 11 | 4 | 5 | 54 | 54
[25 empty] | 8262 | 12 | 11 | 4 | 6 | 55 | 55
[25 empty] | 8263 | 12 | 11 | 4 | 7 | 55.9 | 56
[25 empty] | 8264 | 12 | 11 | 4 | 8 | 57 | 57
[25 empty] | 8265 | 12 | 11 | 4 | 9 | 57.9 | 58
[25 empty] | 8266 | 12 | 11 | 4 | 10 | 59 | 59
[25 empty] | 8267 | 12 | 11 | 4 | 11 | 57.9 | 58
[25 empty] | 8268 | 12 | 11 | 4 | 12 | 57 | 57
[25 empty] | 8269 | 12 | 11 | 4 | 13 | 53.1 | 53
[25 empty] | 8270 | 12 | 11 | 4 | 14 | 53.1 | 53
[25 empty] | 8271 | 12 | 11 | 4 | 15 | 55.9 | 56
[25 empty] | 8272 | 12 | 11 | 4 | 16 | 54 | 54
[25 empty] | 8273 | 12 | 11 | 4 | 17 | 53.1 | 53
[25 empty] | 8274 | 12 | 11 | 4 | 18 | 52 | 52
[25 empty] | 8275 | 12 | 11 | 4 | 19 | 48.9 | 49
[25 empty] | 8276 | 12 | 11 | 4 | 20 | 46.9 | 47
[25 empty] | 8277 | 12 | 11 | 4 | 21 | 44.1 | 44
[25 empty] | 8278 | 12 | 11 | 4 | 22 | 43 | 43
[25 empty] | 8279 | 12 | 11 | 4 | 23 | 42.1 | 42
[25 empty] | 8280 | 12 | 12 | 5 | 0 | 41 | 41
[25 empty] | 8281 | 12 | 12 | 5 | 1 | 41 | 41
[25 empty] | 8282 | 12 | 12 | 5 | 2 | 41 | 41
[25 empty] | 8283 | 12 | 12 | 5 | 3 | 39.9 | 40
[25 empty] | 8284 | 12 | 12 | 5 | 4 | 39 | 39
[25 empty] | 8285 | 12 | 12 | 5 | 5 | 39 | 39
[25 empty] | 8286 | 12 | 12 | 5 | 6 | 39 | 39
[25 empty] | 8287 | 12 | 12 | 5 | 7 | 37.9 | 38
[25 empty] | 8288 | 12 | 12 | 5 | 8 | 37.9 | 38
[25 empty] | 8289 | 12 | 12 | 5 | 9 | 37.9 | 38
[25 empty] | 8290 | 12 | 12 | 5 | 10 | 39 | 39
[25 empty] | 8291 | 12 | 12 | 5 | 11 | 39.9 | 40
[25 empty] | 8292 | 12 | 12 | 5 | 12 | 41 | 41
[25 empty] | 8293 | 12 | 12 | 5 | 13 | 41 | 41
[25 empty] | 8294 | 12 | 12 | 5 | 14 | 41 | 41
[25 empty] | 8295 | 12 | 12 | 5 | 15 | 41 | 41
[25 empty] | 8296 | 12 | 12 | 5 | 16 | 41 | 41
[25 empty] | 8297 | 12 | 12 | 5 | 17 | 39 | 39
[25 empty] | 8298 | 12 | 12 | 5 | 18 | 39 | 39
[25 empty] | 8299 | 12 | 12 | 5 | 19 | 37.9 | 38
[25 empty] | 8300 | 12 | 12 | 5 | 20 | 37.9 | 38
[25 empty] | 8301 | 12 | 12 | 5 | 21 | 37.9 | 38
[25 empty] | 8302 | 12 | 12 | 5 | 22 | 37 | 37
[25 empty] | 8303 | 12 | 12 | 5 | 23 | 36 | 36
[25 empty] | 8304 | 12 | 13 | 6 | 0 | 36 | 36
[25 empty] | 8305 | 12 | 13 | 6 | 1 | 34 | 34
[25 empty] | 8306 | 12 | 13 | 6 | 2 | 34 | 34
[25 empty] | 8307 | 12 | 13 | 6 | 3 | 33.1 | 33
[25 empty] | 8308 | 12 | 13 | 6 | 4 | 32 | 32
[25 empty] | 8309 | 12 | 13 | 6 | 5 | 32 | 32
[25 empty] | 8310 | 12 | 13 | 6 | 6 | 30.9 | 31
[25 empty] | 8311 | 12 | 13 | 6 | 7 | 30.9 | 31
[25 empty] | 8312 | 12 | 13 | 6 | 8 | 30.9 | 31
[25 empty] | 8313 | 12 | 13 | 6 | 9 | 30.9 | 31
[25 empty] | 8314 | 12 | 13 | 6 | 10 | 32 | 32
[25 empty] | 8315 | 12 | 13 | 6 | 11 | 32 | 32
[25 empty] | 8316 | 12 | 13 | 6 | 12 | 33.1 | 33
[25 empty] | 8317 | 12 | 13 | 6 | 13 | 33.1 | 33
[25 empty] | 8318 | 12 | 13 | 6 | 14 | 33.1 | 33
[25 empty] | 8319 | 12 | 13 | 6 | 15 | 33.1 | 33
[25 empty] | 8320 | 12 | 13 | 6 | 16 | 33.1 | 33
[25 empty] | 8321 | 12 | 13 | 6 | 17 | 33.1 | 33
[25 empty] | 8322 | 12 | 13 | 6 | 18 | 32 | 32
[25 empty] | 8323 | 12 | 13 | 6 | 19 | 32 | 32
[25 empty] | 8324 | 12 | 13 | 6 | 20 | 30.9 | 31
[25 empty] | 8325 | 12 | 13 | 6 | 21 | 30.9 | 31
[25 empty] | 8326 | 12 | 13 | 6 | 22 | 30.9 | 31
[25 empty] | 8327 | 12 | 13 | 6 | 23 | 30.9 | 31
[25 empty] | 8328 | 12 | 14 | 7 | 0 | 30 | 30
[25 empty] | 8329 | 12 | 14 | 7 | 1 | 30 | 30
[25 empty] | 8330 | 12 | 14 | 7 | 2 | 28.9 | 29
[25 empty] | 8331 | 12 | 14 | 7 | 3 | 28.9 | 29
[25 empty] | 8332 | 12 | 14 | 7 | 4 | 28 | 28
[25 empty] | 8333 | 12 | 14 | 7 | 5 | 28.9 | 29
[25 empty] | 8334 | 12 | 14 | 7 | 6 | 28.9 | 29
[25 empty] | 8335 | 12 | 14 | 7 | 7 | 30 | 30
[25 empty] | 8336 | 12 | 14 | 7 | 8 | 30.9 | 31
[25 empty] | 8337 | 12 | 14 | 7 | 9 | 28.9 | 29
[25 empty] | 8338 | 12 | 14 | 7 | 10 | 28.9 | 29
[25 empty] | 8339 | 12 | 14 | 7 | 11 | 28.9 | 29
[25 empty] | 8340 | 12 | 14 | 7 | 12 | 28.9 | 29
[25 empty] | 8341 | 12 | 14 | 7 | 13 | 30 | 30
[25 empty] | 8342 | 12 | 14 | 7 | 14 | 32 | 32
[25 empty] | 8343 | 12 | 14 | 7 | 15 | 34 | 34
[25 empty] | 8344 | 12 | 14 | 7 | 16 | 35.1 | 35
[25 empty] | 8345 | 12 | 14 | 7 | 17 | 35.1 | 35
[25 empty] | 8346 | 12 | 14 | 7 | 18 | 37 | 37
[25 empty] | 8347 | 12 | 14 | 7 | 19 | 39 | 39
[25 empty] | 8348 | 12 | 14 | 7 | 20 | 42.1 | 42
[25 empty] | 8349 | 12 | 14 | 7 | 21 | 41 | 41
[25 empty] | 8350 | 12 | 14 | 7 | 22 | 41 | 41
[25 empty] | 8351 | 12 | 14 | 7 | 23 | 39.9 | 40
[25 empty] | 8352 | 12 | 15 | 1 | 0 | 39.9 | 40
[25 empty] | 8353 | 12 | 15 | 1 | 1 | 41 | 41
[25 empty] | 8354 | 12 | 15 | 1 | 2 | 37 | 37
[25 empty] | 8355 | 12 | 15 | 1 | 3 | 33.1 | 33
[25 empty] | 8356 | 12 | 15 | 1 | 4 | 32 | 32
[25 empty] | 8357 | 12 | 15 | 1 | 5 | 32 | 32
[25 empty] | 8358 | 12 | 15 | 1 | 6 | 32 | 32
[25 empty] | 8359 | 12 | 15 | 1 | 7 | 32 | 32
[25 empty] | 8360 | 12 | 15 | 1 | 8 | 32 | 32
[25 empty] | 8361 | 12 | 15 | 1 | 9 | 32 | 32
[25 empty] | 8362 | 12 | 15 | 1 | 10 | 34 | 34
[25 empty] | 8363 | 12 | 15 | 1 | 11 | 36 | 36
[25 empty] | 8364 | 12 | 15 | 1 | 12 | 37 | 37
[25 empty] | 8365 | 12 | 15 | 1 | 13 | 37.9 | 38
[25 empty] | 8366 | 12 | 15 | 1 | 14 | 37.9 | 38
[25 empty] | 8367 | 12 | 15 | 1 | 15 | 39 | 39
[25 empty] | 8368 | 12 | 15 | 1 | 16 | 37.9 | 38
[25 empty] | 8369 | 12 | 15 | 1 | 17 | 37.9 | 38
[25 empty] | 8370 | 12 | 15 | 1 | 18 | 37 | 37
[25 empty] | 8371 | 12 | 15 | 1 | 19 | 37 | 37
[25 empty] | 8372 | 12 | 15 | 1 | 20 | 36 | 36
[25 empty] | 8373 | 12 | 15 | 1 | 21 | 36 | 36
[25 empty] | 8374 | 12 | 15 | 1 | 22 | 36 | 36
[25 empty] | 8375 | 12 | 15 | 1 | 23 | 35.1 | 35
[25 empty] | 8376 | 12 | 16 | 2 | 0 | 35.1 | 35
[25 empty] | 8377 | 12 | 16 | 2 | 1 | 35.1 | 35
[25 empty] | 8378 | 12 | 16 | 2 | 2 | 34 | 34
[25 empty] | 8379 | 12 | 16 | 2 | 3 | 34 | 34
[25 empty] | 8380 | 12 | 16 | 2 | 4 | 34 | 34
[25 empty] | 8381 | 12 | 16 | 2 | 5 | 34 | 34
[25 empty] | 8382 | 12 | 16 | 2 | 6 | 35.1 | 35
[25 empty] | 8383 | 12 | 16 | 2 | 7 | 34 | 34
[25 empty] | 8384 | 12 | 16 | 2 | 8 | 34 | 34
[25 empty] | 8385 | 12 | 16 | 2 | 9 | 36 | 36
[25 empty] | 8386 | 12 | 16 | 2 | 10 | 37.9 | 38
[25 empty] | 8387 | 12 | 16 | 2 | 11 | 41 | 41
[25 empty] | 8388 | 12 | 16 | 2 | 12 | 43 | 43
[25 empty] | 8389 | 12 | 16 | 2 | 13 | 46 | 46
[25 empty] | 8390 | 12 | 16 | 2 | 14 | 46.9 | 47
[25 empty] | 8391 | 12 | 16 | 2 | 15 | 46 | 46
[25 empty] | 8392 | 12 | 16 | 2 | 16 | 42.1 | 42
[25 empty] | 8393 | 12 | 16 | 2 | 17 | 42.1 | 42
[25 empty] | 8394 | 12 | 16 | 2 | 18 | 43 | 43
[25 empty] | 8395 | 12 | 16 | 2 | 19 | 43 | 43
[25 empty] | 8396 | 12 | 16 | 2 | 20 | 44.1 | 44
[25 empty] | 8397 | 12 | 16 | 2 | 21 | 44.1 | 44
[25 empty] | 8398 | 12 | 16 | 2 | 22 | 44.1 | 44
[25 empty] | 8399 | 12 | 16 | 2 | 23 | 45 | 45
[25 empty] | 8400 | 12 | 17 | 3 | 0 | 45 | 45
[25 empty] | 8401 | 12 | 17 | 3 | 1 | 44.1 | 44
[25 empty] | 8402 | 12 | 17 | 3 | 2 | 44.1 | 44
[25 empty] | 8403 | 12 | 17 | 3 | 3 | 44.1 | 44
[25 empty] | 8404 | 12 | 17 | 3 | 4 | 45 | 45
[25 empty] | 8405 | 12 | 17 | 3 | 5 | 45 | 45
[25 empty] | 8406 | 12 | 17 | 3 | 6 | 48.9 | 49
[25 empty] | 8407 | 12 | 17 | 3 | 7 | 48 | 48
[25 empty] | 8408 | 12 | 17 | 3 | 8 | 50 | 50
[25 empty] | 8409 | 12 | 17 | 3 | 9 | 51.1 | 51
[25 empty] | 8410 | 12 | 17 | 3 | 10 | 54 | 54
[25 empty] | 8411 | 12 | 17 | 3 | 11 | 55 | 55
[25 empty] | 8412 | 12 | 17 | 3 | 12 | 54 | 54
[25 empty] | 8413 | 12 | 17 | 3 | 13 | 53.1 | 53
[25 empty] | 8414 | 12 | 17 | 3 | 14 | 54 | 54
[25 empty] | 8415 | 12 | 17 | 3 | 15 | 51.1 | 51
[25 empty] | 8416 | 12 | 17 | 3 | 16 | 46 | 46
[25 empty] | 8417 | 12 | 17 | 3 | 17 | 43 | 43
[25 empty] | 8418 | 12 | 17 | 3 | 18 | 42.1 | 42
[25 empty] | 8419 | 12 | 17 | 3 | 19 | 42.1 | 42
[25 empty] | 8420 | 12 | 17 | 3 | 20 | 37.9 | 38
[25 empty] | 8421 | 12 | 17 | 3 | 21 | 37 | 37
[25 empty] | 8422 | 12 | 17 | 3 | 22 | 37.9 | 38
[25 empty] | 8423 | 12 | 17 | 3 | 23 | 37.9 | 38
[25 empty] | 8424 | 12 | 18 | 4 | 0 | 36 | 36
[25 empty] | 8425 | 12 | 18 | 4 | 1 | 35.1 | 35
[25 empty] | 8426 | 12 | 18 | 4 | 2 | 34 | 34
[25 empty] | 8427 | 12 | 18 | 4 | 3 | 34 | 34
[25 empty] | 8428 | 12 | 18 | 4 | 4 | 34 | 34
[25 empty] | 8429 | 12 | 18 | 4 | 5 | 34 | 34
[25 empty] | 8430 | 12 | 18 | 4 | 6 | 33.1 | 33
[25 empty] | 8431 | 12 | 18 | 4 | 7 | 33.1 | 33
[25 empty] | 8432 | 12 | 18 | 4 | 8 | 33.1 | 33
[25 empty] | 8433 | 12 | 18 | 4 | 9 | 34 | 34
[25 empty] | 8434 | 12 | 18 | 4 | 10 | 35.1 | 35
[25 empty] | 8435 | 12 | 18 | 4 | 11 | 36 | 36
[25 empty] | 8436 | 12 | 18 | 4 | 12 | 36 | 36
[25 empty] | 8437 | 12 | 18 | 4 | 13 | 36 | 36
[25 empty] | 8438 | 12 | 18 | 4 | 14 | 36 | 36
[25 empty] | 8439 | 12 | 18 | 4 | 15 | 36 | 36
[25 empty] | 8440 | 12 | 18 | 4 | 16 | 36 | 36
[25 empty] | 8441 | 12 | 18 | 4 | 17 | 35.1 | 35
[25 empty] | 8442 | 12 | 18 | 4 | 18 | 36 | 36
[25 empty] | 8443 | 12 | 18 | 4 | 19 | 35.1 | 35
[25 empty] | 8444 | 12 | 18 | 4 | 20 | 35.1 | 35
[25 empty] | 8445 | 12 | 18 | 4 | 21 | 35.1 | 35
[25 empty] | 8446 | 12 | 18 | 4 | 22 | 35.1 | 35
[25 empty] | 8447 | 12 | 18 | 4 | 23 | 35.1 | 35
[25 empty] | 8448 | 12 | 19 | 5 | 0 | 35.1 | 35
[25 empty] | 8449 | 12 | 19 | 5 | 1 | 34 | 34
[25 empty] | 8450 | 12 | 19 | 5 | 2 | 34 | 34
[25 empty] | 8451 | 12 | 19 | 5 | 3 | 33.1 | 33
[25 empty] | 8452 | 12 | 19 | 5 | 4 | 33.1 | 33
[25 empty] | 8453 | 12 | 19 | 5 | 5 | 32 | 32
[25 empty] | 8454 | 12 | 19 | 5 | 6 | 32 | 32
[25 empty] | 8455 | 12 | 19 | 5 | 7 | 32 | 32
[25 empty] | 8456 | 12 | 19 | 5 | 8 | 30.9 | 31
[25 empty] | 8457 | 12 | 19 | 5 | 9 | 32 | 32
[25 empty] | 8458 | 12 | 19 | 5 | 10 | 32 | 32
[25 empty] | 8459 | 12 | 19 | 5 | 11 | 33.1 | 33
[25 empty] | 8460 | 12 | 19 | 5 | 12 | 34 | 34
[25 empty] | 8461 | 12 | 19 | 5 | 13 | 34 | 34
[25 empty] | 8462 | 12 | 19 | 5 | 14 | 34 | 34
[25 empty] | 8463 | 12 | 19 | 5 | 15 | 35.1 | 35
[25 empty] | 8464 | 12 | 19 | 5 | 16 | 36 | 36
[25 empty] | 8465 | 12 | 19 | 5 | 17 | 36 | 36
[25 empty] | 8466 | 12 | 19 | 5 | 18 | 36 | 36
[25 empty] | 8467 | 12 | 19 | 5 | 19 | 36 | 36
[25 empty] | 8468 | 12 | 19 | 5 | 20 | 36 | 36
[25 empty] | 8469 | 12 | 19 | 5 | 21 | 35.1 | 35
[25 empty] | 8470 | 12 | 19 | 5 | 22 | 35.1 | 35
[25 empty] | 8471 | 12 | 19 | 5 | 23 | 35.1 | 35
[25 empty] | 8472 | 12 | 20 | 6 | 0 | 35.1 | 35
[25 empty] | 8473 | 12 | 20 | 6 | 1 | 35.1 | 35
[25 empty] | 8474 | 12 | 20 | 6 | 2 | 34 | 34
[25 empty] | 8475 | 12 | 20 | 6 | 3 | 34 | 34
[25 empty] | 8476 | 12 | 20 | 6 | 4 | 33.1 | 33
[25 empty] | 8477 | 12 | 20 | 6 | 5 | 33.1 | 33
[25 empty] | 8478 | 12 | 20 | 6 | 6 | 33.1 | 33
[25 empty] | 8479 | 12 | 20 | 6 | 7 | 32 | 32
[25 empty] | 8480 | 12 | 20 | 6 | 8 | 32 | 32
[25 empty] | 8481 | 12 | 20 | 6 | 9 | 33.1 | 33
[25 empty] | 8482 | 12 | 20 | 6 | 10 | 34 | 34
[25 empty] | 8483 | 12 | 20 | 6 | 11 | 36 | 36
[25 empty] | 8484 | 12 | 20 | 6 | 12 | 37 | 37
[25 empty] | 8485 | 12 | 20 | 6 | 13 | 37.9 | 38
[25 empty] | 8486 | 12 | 20 | 6 | 14 | 37.9 | 38
[25 empty] | 8487 | 12 | 20 | 6 | 15 | 37 | 37
[25 empty] | 8488 | 12 | 20 | 6 | 16 | 37 | 37
[25 empty] | 8489 | 12 | 20 | 6 | 17 | 36 | 36
[25 empty] | 8490 | 12 | 20 | 6 | 18 | 35.1 | 35
[25 empty] | 8491 | 12 | 20 | 6 | 19 | 34 | 34
[25 empty] | 8492 | 12 | 20 | 6 | 20 | 32 | 32
[25 empty] | 8493 | 12 | 20 | 6 | 21 | 30.9 | 31
[25 empty] | 8494 | 12 | 20 | 6 | 22 | 30 | 30
[25 empty] | 8495 | 12 | 20 | 6 | 23 | 30 | 30
[25 empty] | 8496 | 12 | 21 | 7 | 0 | 28 | 28
[25 empty] | 8497 | 12 | 21 | 7 | 1 | 27 | 27
[25 empty] | 8498 | 12 | 21 | 7 | 2 | 27 | 27
[25 empty] | 8499 | 12 | 21 | 7 | 3 | 26.1 | 26
[25 empty] | 8500 | 12 | 21 | 7 | 4 | 26.1 | 26
[25 empty] | 8501 | 12 | 21 | 7 | 5 | 26.1 | 26
[25 empty] | 8502 | 12 | 21 | 7 | 6 | 27 | 27
[25 empty] | 8503 | 12 | 21 | 7 | 7 | 28 | 28
[25 empty] | 8504 | 12 | 21 | 7 | 8 | 28.9 | 29
[25 empty] | 8505 | 12 | 21 | 7 | 9 | 30.9 | 31
[25 empty] | 8506 | 12 | 21 | 7 | 10 | 30.9 | 31
[25 empty] | 8507 | 12 | 21 | 7 | 11 | 34 | 34
[25 empty] | 8508 | 12 | 21 | 7 | 12 | 35.1 | 35
[25 empty] | 8509 | 12 | 21 | 7 | 13 | 36 | 36
[25 empty] | 8510 | 12 | 21 | 7 | 14 | 37.9 | 38
[25 empty] | 8511 | 12 | 21 | 7 | 15 | 39 | 39
[25 empty] | 8512 | 12 | 21 | 7 | 16 | 39 | 39
[25 empty] | 8513 | 12 | 21 | 7 | 17 | 37.9 | 38
[25 empty] | 8514 | 12 | 21 | 7 | 18 | 37.9 | 38
[25 empty] | 8515 | 12 | 21 | 7 | 19 | 37.9 | 38
[25 empty] | 8516 | 12 | 21 | 7 | 20 | 37.9 | 38
[25 empty] | 8517 | 12 | 21 | 7 | 21 | 37.9 | 38
[25 empty] | 8518 | 12 | 21 | 7 | 22 | 37.9 | 38
[25 empty] | 8519 | 12 | 21 | 7 | 23 | 37.9 | 38
[25 empty] | 8520 | 12 | 22 | 1 | 0 | 37.9 | 38
[25 empty] | 8521 | 12 | 22 | 1 | 1 | 39 | 39
[25 empty] | 8522 | 12 | 22 | 1 | 2 | 37.9 | 38
[25 empty] | 8523 | 12 | 22 | 1 | 3 | 39 | 39
[25 empty] | 8524 | 12 | 22 | 1 | 4 | 37.9 | 38
[25 empty] | 8525 | 12 | 22 | 1 | 5 | 37.9 | 38
[25 empty] | 8526 | 12 | 22 | 1 | 6 | 37 | 37
[25 empty] | 8527 | 12 | 22 | 1 | 7 | 37 | 37
[25 empty] | 8528 | 12 | 22 | 1 | 8 | 37 | 37
[25 empty] | 8529 | 12 | 22 | 1 | 9 | 39.9 | 40
[25 empty] | 8530 | 12 | 22 | 1 | 10 | 41 | 41
[25 empty] | 8531 | 12 | 22 | 1 | 11 | 45 | 45
[25 empty] | 8532 | 12 | 22 | 1 | 12 | 45 | 45
[25 empty] | 8533 | 12 | 22 | 1 | 13 | 46.9 | 47
[25 empty] | 8534 | 12 | 22 | 1 | 14 | 48.9 | 49
[25 empty] | 8535 | 12 | 22 | 1 | 15 | 50 | 50
[25 empty] | 8536 | 12 | 22 | 1 | 16 | 50 | 50
[25 empty] | 8537 | 12 | 22 | 1 | 17 | 50 | 50
[25 empty] | 8538 | 12 | 22 | 1 | 18 | 50 | 50
[25 empty] | 8539 | 12 | 22 | 1 | 19 | 48.9 | 49
[25 empty] | 8540 | 12 | 22 | 1 | 20 | 48.9 | 49
[25 empty] | 8541 | 12 | 22 | 1 | 21 | 48.9 | 49
[25 empty] | 8542 | 12 | 22 | 1 | 22 | 48 | 48
[25 empty] | 8543 | 12 | 22 | 1 | 23 | 48 | 48
[25 empty] | 8544 | 12 | 23 | 2 | 0 | 48 | 48
[25 empty] | 8545 | 12 | 23 | 2 | 1 | 46.9 | 47
[25 empty] | 8546 | 12 | 23 | 2 | 2 | 46.9 | 47
[25 empty] | 8547 | 12 | 23 | 2 | 3 | 46.9 | 47
[25 empty] | 8548 | 12 | 23 | 2 | 4 | 46.9 | 47
[25 empty] | 8549 | 12 | 23 | 2 | 5 | 46.9 | 47
[25 empty] | 8550 | 12 | 23 | 2 | 6 | 48 | 48
[25 empty] | 8551 | 12 | 23 | 2 | 7 | 46 | 46
[25 empty] | 8552 | 12 | 23 | 2 | 8 | 46 | 46
[25 empty] | 8553 | 12 | 23 | 2 | 9 | 46.9 | 47
[25 empty] | 8554 | 12 | 23 | 2 | 10 | 48.9 | 49
[25 empty] | 8555 | 12 | 23 | 2 | 11 | 51.1 | 51
[25 empty] | 8556 | 12 | 23 | 2 | 12 | 51.1 | 51
[25 empty] | 8557 | 12 | 23 | 2 | 13 | 53.1 | 53
[25 empty] | 8558 | 12 | 23 | 2 | 14 | 53.1 | 53
[25 empty] | 8559 | 12 | 23 | 2 | 15 | 52 | 52
[25 empty] | 8560 | 12 | 23 | 2 | 16 | 51.1 | 51
[25 empty] | 8561 | 12 | 23 | 2 | 17 | 48.9 | 49
[25 empty] | 8562 | 12 | 23 | 2 | 18 | 48.9 | 49
[25 empty] | 8563 | 12 | 23 | 2 | 19 | 48 | 48
[25 empty] | 8564 | 12 | 23 | 2 | 20 | 48 | 48
[25 empty] | 8565 | 12 | 23 | 2 | 21 | 48 | 48
[25 empty] | 8566 | 12 | 23 | 2 | 22 | 48 | 48
[25 empty] | 8567 | 12 | 23 | 2 | 23 | 48.9 | 49
[25 empty] | 8568 | 12 | 24 | 3 | 0 | 50 | 50
[25 empty] | 8569 | 12 | 24 | 3 | 1 | 50 | 50
[25 empty] | 8570 | 12 | 24 | 3 | 2 | 50 | 50
[25 empty] | 8571 | 12 | 24 | 3 | 3 | 50 | 50
[25 empty] | 8572 | 12 | 24 | 3 | 4 | 52 | 52
[25 empty] | 8573 | 12 | 24 | 3 | 5 | 52 | 52
[25 empty] | 8574 | 12 | 24 | 3 | 6 | 53.1 | 53
[25 empty] | 8575 | 12 | 24 | 3 | 7 | 54 | 54
[25 empty] | 8576 | 12 | 24 | 3 | 8 | 55.9 | 56
[25 empty] | 8577 | 12 | 24 | 3 | 9 | 54 | 54
[25 empty] | 8578 | 12 | 24 | 3 | 10 | 54 | 54
[25 empty] | 8579 | 12 | 24 | 3 | 11 | 53.1 | 53
[25 empty] | 8580 | 12 | 24 | 3 | 12 | 55.9 | 56
[25 empty] | 8581 | 12 | 24 | 3 | 13 | 57 | 57
[25 empty] | 8582 | 12 | 24 | 3 | 14 | 54 | 54
[25 empty] | 8583 | 12 | 24 | 3 | 15 | 53.1 | 53
[25 empty] | 8584 | 12 | 24 | 3 | 16 | 53.1 | 53
[25 empty] | 8585 | 12 | 24 | 3 | 17 | 53.1 | 53
[25 empty] | 8586 | 12 | 24 | 3 | 18 | 52 | 52
[25 empty] | 8587 | 12 | 24 | 3 | 19 | 52 | 52
[25 empty] | 8588 | 12 | 24 | 3 | 20 | 54 | 54
[25 empty] | 8589 | 12 | 24 | 3 | 21 | 52 | 52
[25 empty] | 8590 | 12 | 24 | 3 | 22 | 50 | 50
[25 empty] | 8591 | 12 | 24 | 3 | 23 | 48.9 | 49
[25 empty] | 8592 | 12 | 25 | 4 | 0 | 46.9 | 47
[25 empty] | 8593 | 12 | 25 | 4 | 1 | 46 | 46
[25 empty] | 8594 | 12 | 25 | 4 | 2 | 45 | 45
[25 empty] | 8595 | 12 | 25 | 4 | 3 | 44.1 | 44
[25 empty] | 8596 | 12 | 25 | 4 | 4 | 43 | 43
[25 empty] | 8597 | 12 | 25 | 4 | 5 | 42.1 | 42
[25 empty] | 8598 | 12 | 25 | 4 | 6 | 42.1 | 42
[25 empty] | 8599 | 12 | 25 | 4 | 7 | 42.1 | 42
[25 empty] | 8600 | 12 | 25 | 4 | 8 | 42.1 | 42
[25 empty] | 8601 | 12 | 25 | 4 | 9 | 42.1 | 42
[25 empty] | 8602 | 12 | 25 | 4 | 10 | 41 | 41
[25 empty] | 8603 | 12 | 25 | 4 | 11 | 42.1 | 42
[25 empty] | 8604 | 12 | 25 | 4 | 12 | 42.1 | 42
[25 empty] | 8605 | 12 | 25 | 4 | 13 | 42.1 | 42
[25 empty] | 8606 | 12 | 25 | 4 | 14 | 42.1 | 42
[25 empty] | 8607 | 12 | 25 | 4 | 15 | 42.1 | 42
[25 empty] | 8608 | 12 | 25 | 4 | 16 | 41 | 41
[25 empty] | 8609 | 12 | 25 | 4 | 17 | 39 | 39
[25 empty] | 8610 | 12 | 25 | 4 | 18 | 39 | 39
[25 empty] | 8611 | 12 | 25 | 4 | 19 | 39 | 39
[25 empty] | 8612 | 12 | 25 | 4 | 20 | 37 | 37
[25 empty] | 8613 | 12 | 25 | 4 | 21 | 37 | 37
[25 empty] | 8614 | 12 | 25 | 4 | 22 | 36 | 36
[25 empty] | 8615 | 12 | 25 | 4 | 23 | 35.1 | 35
[25 empty] | 8616 | 12 | 26 | 5 | 0 | 35.1 | 35
[25 empty] | 8617 | 12 | 26 | 5 | 1 | 34 | 34
[25 empty] | 8618 | 12 | 26 | 5 | 2 | 34 | 34
[25 empty] | 8619 | 12 | 26 | 5 | 3 | 34 | 34
[25 empty] | 8620 | 12 | 26 | 5 | 4 | 34 | 34
[25 empty] | 8621 | 12 | 26 | 5 | 5 | 33.1 | 33
[25 empty] | 8622 | 12 | 26 | 5 | 6 | 32 | 32
[25 empty] | 8623 | 12 | 26 | 5 | 7 | 33.1 | 33
[25 empty] | 8624 | 12 | 26 | 5 | 8 | 33.1 | 33
[25 empty] | 8625 | 12 | 26 | 5 | 9 | 34 | 34
[25 empty] | 8626 | 12 | 26 | 5 | 10 | 36 | 36
[25 empty] | 8627 | 12 | 26 | 5 | 11 | 37 | 37
[25 empty] | 8628 | 12 | 26 | 5 | 12 | 37.9 | 38
[25 empty] | 8629 | 12 | 26 | 5 | 13 | 39 | 39
[25 empty] | 8630 | 12 | 26 | 5 | 14 | 39.9 | 40
[25 empty] | 8631 | 12 | 26 | 5 | 15 | 42.1 | 42
[25 empty] | 8632 | 12 | 26 | 5 | 16 | 42.1 | 42
[25 empty] | 8633 | 12 | 26 | 5 | 17 | 42.1 | 42
[25 empty] | 8634 | 12 | 26 | 5 | 18 | 42.1 | 42
[25 empty] | 8635 | 12 | 26 | 5 | 19 | 42.1 | 42
[25 empty] | 8636 | 12 | 26 | 5 | 20 | 42.1 | 42
[25 empty] | 8637 | 12 | 26 | 5 | 21 | 42.1 | 42
[25 empty] | 8638 | 12 | 26 | 5 | 22 | 42.1 | 42
[25 empty] | 8639 | 12 | 26 | 5 | 23 | 41 | 41
[25 empty] | 8640 | 12 | 27 | 6 | 0 | 41 | 41
[25 empty] | 8641 | 12 | 27 | 6 | 1 | 39.9 | 40
[25 empty] | 8642 | 12 | 27 | 6 | 2 | 39 | 39
[25 empty] | 8643 | 12 | 27 | 6 | 3 | 39.9 | 40
[25 empty] | 8644 | 12 | 27 | 6 | 4 | 39.9 | 40
[25 empty] | 8645 | 12 | 27 | 6 | 5 | 39.9 | 40
[25 empty] | 8646 | 12 | 27 | 6 | 6 | 39.9 | 40
[25 empty] | 8647 | 12 | 27 | 6 | 7 | 39.9 | 40
[25 empty] | 8648 | 12 | 27 | 6 | 8 | 39.9 | 40
[25 empty] | 8649 | 12 | 27 | 6 | 9 | 41 | 41
[25 empty] | 8650 | 12 | 27 | 6 | 10 | 43 | 43
[25 empty] | 8651 | 12 | 27 | 6 | 11 | 46 | 46
[25 empty] | 8652 | 12 | 27 | 6 | 12 | 48 | 48
[25 empty] | 8653 | 12 | 27 | 6 | 13 | 50 | 50
[25 empty] | 8654 | 12 | 27 | 6 | 14 | 51.1 | 51
[25 empty] | 8655 | 12 | 27 | 6 | 15 | 52 | 52
[25 empty] | 8656 | 12 | 27 | 6 | 16 | 51.1 | 51
[25 empty] | 8657 | 12 | 27 | 6 | 17 | 50 | 50
[25 empty] | 8658 | 12 | 27 | 6 | 18 | 48 | 48
[25 empty] | 8659 | 12 | 27 | 6 | 19 | 46 | 46
[25 empty] | 8660 | 12 | 27 | 6 | 20 | 45 | 45
[25 empty] | 8661 | 12 | 27 | 6 | 21 | 43 | 43
[25 empty] | 8662 | 12 | 27 | 6 | 22 | 41 | 41
[25 empty] | 8663 | 12 | 27 | 6 | 23 | 41 | 41
[25 empty] | 8664 | 12 | 28 | 7 | 0 | 39.9 | 40
[25 empty] | 8665 | 12 | 28 | 7 | 1 | 39 | 39
[25 empty] | 8666 | 12 | 28 | 7 | 2 | 37.9 | 38
[25 empty] | 8667 | 12 | 28 | 7 | 3 | 39 | 39
[25 empty] | 8668 | 12 | 28 | 7 | 4 | 37.9 | 38
[25 empty] | 8669 | 12 | 28 | 7 | 5 | 37 | 37
[25 empty] | 8670 | 12 | 28 | 7 | 6 | 36 | 36
[25 empty] | 8671 | 12 | 28 | 7 | 7 | 37 | 37
[25 empty] | 8672 | 12 | 28 | 7 | 8 | 37 | 37
[25 empty] | 8673 | 12 | 28 | 7 | 9 | 37.9 | 38
[25 empty] | 8674 | 12 | 28 | 7 | 10 | 39.9 | 40
[25 empty] | 8675 | 12 | 28 | 7 | 11 | 44.1 | 44
[25 empty] | 8676 | 12 | 28 | 7 | 12 | 46 | 46
[25 empty] | 8677 | 12 | 28 | 7 | 13 | 48.9 | 49
[25 empty] | 8678 | 12 | 28 | 7 | 14 | 51.1 | 51
[25 empty] | 8679 | 12 | 28 | 7 | 15 | 51.1 | 51
[25 empty] | 8680 | 12 | 28 | 7 | 16 | 51.1 | 51
[25 empty] | 8681 | 12 | 28 | 7 | 17 | 46.9 | 47
[25 empty] | 8682 | 12 | 28 | 7 | 18 | 45 | 45
[25 empty] | 8683 | 12 | 28 | 7 | 19 | 44.1 | 44
[25 empty] | 8684 | 12 | 28 | 7 | 20 | 42.1 | 42
[25 empty] | 8685 | 12 | 28 | 7 | 21 | 43 | 43
[25 empty] | 8686 | 12 | 28 | 7 | 22 | 42.1 | 42
[25 empty] | 8687 | 12 | 28 | 7 | 23 | 42.1 | 42
[25 empty] | 8688 | 12 | 29 | 1 | 0 | 42.1 | 42
[25 empty] | 8689 | 12 | 29 | 1 | 1 | 41 | 41
[25 empty] | 8690 | 12 | 29 | 1 | 2 | 41 | 41
[25 empty] | 8691 | 12 | 29 | 1 | 3 | 39 | 39
[25 empty] | 8692 | 12 | 29 | 1 | 4 | 39 | 39
[25 empty] | 8693 | 12 | 29 | 1 | 5 | 37.9 | 38
[25 empty] | 8694 | 12 | 29 | 1 | 6 | 39 | 39
[25 empty] | 8695 | 12 | 29 | 1 | 7 | 39 | 39
[25 empty] | 8696 | 12 | 29 | 1 | 8 | 39 | 39
[25 empty] | 8697 | 12 | 29 | 1 | 9 | 41 | 41
[25 empty] | 8698 | 12 | 29 | 1 | 10 | 44.1 | 44
[25 empty] | 8699 | 12 | 29 | 1 | 11 | 46 | 46
[25 empty] | 8700 | 12 | 29 | 1 | 12 | 50 | 50
[25 empty] | 8701 | 12 | 29 | 1 | 13 | 52 | 52
[25 empty] | 8702 | 12 | 29 | 1 | 14 | 54 | 54
[25 empty] | 8703 | 12 | 29 | 1 | 15 | 55 | 55
[25 empty] | 8704 | 12 | 29 | 1 | 16 | 51.1 | 51
[25 empty] | 8705 | 12 | 29 | 1 | 17 | 48 | 48
[25 empty] | 8706 | 12 | 29 | 1 | 18 | 46 | 46
[25 empty] | 8707 | 12 | 29 | 1 | 19 | 46 | 46
[25 empty] | 8708 | 12 | 29 | 1 | 20 | 46 | 46
[25 empty] | 8709 | 12 | 29 | 1 | 21 | 46.9 | 47
[25 empty] | 8710 | 12 | 29 | 1 | 22 | 46.9 | 47
[25 empty] | 8711 | 12 | 29 | 1 | 23 | 46.9 | 47
[25 empty] | 8712 | 12 | 30 | 2 | 0 | 45 | 45
[25 empty] | 8713 | 12 | 30 | 2 | 1 | 44.1 | 44
[25 empty] | 8714 | 12 | 30 | 2 | 2 | 44.1 | 44
[25 empty] | 8715 | 12 | 30 | 2 | 3 | 44.1 | 44
[25 empty] | 8716 | 12 | 30 | 2 | 4 | 45 | 45
[25 empty] | 8717 | 12 | 30 | 2 | 5 | 46 | 46
[25 empty] | 8718 | 12 | 30 | 2 | 6 | 46 | 46
[25 empty] | 8719 | 12 | 30 | 2 | 7 | 46.9 | 47
[25 empty] | 8720 | 12 | 30 | 2 | 8 | 48.9 | 49
[25 empty] | 8721 | 12 | 30 | 2 | 9 | 50 | 50
[25 empty] | 8722 | 12 | 30 | 2 | 10 | 51.1 | 51
[25 empty] | 8723 | 12 | 30 | 2 | 11 | 52 | 52
[25 empty] | 8724 | 12 | 30 | 2 | 12 | 52 | 52
[25 empty] | 8725 | 12 | 30 | 2 | 13 | 51.1 | 51
[25 empty] | 8726 | 12 | 30 | 2 | 14 | 50 | 50
[25 empty] | 8727 | 12 | 30 | 2 | 15 | 48.9 | 49
[25 empty] | 8728 | 12 | 30 | 2 | 16 | 46.9 | 47
[25 empty] | 8729 | 12 | 30 | 2 | 17 | 46 | 46
[25 empty] | 8730 | 12 | 30 | 2 | 18 | 45 | 45
[25 empty] | 8731 | 12 | 30 | 2 | 19 | 44.1 | 44
[25 empty] | 8732 | 12 | 30 | 2 | 20 | 43 | 43
[25 empty] | 8733 | 12 | 30 | 2 | 21 | 42.1 | 42
[25 empty] | 8734 | 12 | 30 | 2 | 22 | 42.1 | 42
[25 empty] | 8735 | 12 | 30 | 2 | 23 | 41 | 41
[25 empty] | 8736 | 12 | 31 | 3 | 0 | 41 | 41
[25 empty] | 8737 | 12 | 31 | 3 | 1 | 41 | 41
[25 empty] | 8738 | 12 | 31 | 3 | 2 | 41 | 41
[25 empty] | 8739 | 12 | 31 | 3 | 3 | 39.9 | 40
[25 empty] | 8740 | 12 | 31 | 3 | 4 | 39.9 | 40
[25 empty] | 8741 | 12 | 31 | 3 | 5 | 39.9 | 40
[25 empty] | 8742 | 12 | 31 | 3 | 6 | 39 | 39
[25 empty] | 8743 | 12 | 31 | 3 | 7 | 39 | 39
[25 empty] | 8744 | 12 | 31 | 3 | 8 | 39 | 39
[25 empty] | 8745 | 12 | 31 | 3 | 9 | 39 | 39
[25 empty] | 8746 | 12 | 31 | 3 | 10 | 39 | 39
[25 empty] | 8747 | 12 | 31 | 3 | 11 | 41 | 41
[25 empty] | 8748 | 12 | 31 | 3 | 12 | 42.1 | 42
[25 empty] | 8749 | 12 | 31 | 3 | 13 | 43 | 43
[25 empty] | 8750 | 12 | 31 | 3 | 14 | 45 | 45
[25 empty] | 8751 | 12 | 31 | 3 | 15 | 46 | 46
[25 empty] | 8752 | 12 | 31 | 3 | 16 | 46 | 46
[25 empty] | 8753 | 12 | 31 | 3 | 17 | 45 | 45
[25 empty] | 8754 | 12 | 31 | 3 | 18 | 45 | 45
[25 empty] | 8755 | 12 | 31 | 3 | 19 | 45 | 45
[25 empty] | 8756 | 12 | 31 | 3 | 20 | 44.1 | 44
[25 empty] | 8757 | 12 | 31 | 3 | 21 | 43 | 43
[25 empty] | 8758 | 12 | 31 | 3 | 22 | 43 | 43
[25 empty] | 8759 | 12 | 31 | 3 | 23 | 43 | 43
[25 empty] | 8760 | 1 | 1 | 4 | 0 | 43 | 43
Note on BF53: Madnick, Philip: (Establish Heat time + Cycle On time)
Note on BH53: Madnick, Philip: (Establish Heat time + Cycle On time)
Note on FD5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copied numbers from 10 degF Col

## Orifice Plates
Orifice Plates |  |  |  | Click to go to Summary of Savings
Existing Steam Usage
| Factor | Input | Units
| Grashof's Equation Constant | 60 | lbm/in0.06-lb0.97-hr
| Orifice area development factor | 0.7854
| Grashof's Equation Constant | 0.97
| Diameter of hand valve orifice | 0.5 | in
| psig |  | Steam gage pressure
| patm | 14.7 | Atmospheric pressure
| Number of Radiators | 0
| Steam through hand valves | 0 | lbm/hr
Proposed Steam Usage
| Factor | Input | Units
| Grashof's Equation Constant | 60 | lbm/in0.06-lb0.97-hr
| Orifice area development factor | 0.7854
| Grashof's Equation Constant | 0.97
| Orifice Plate Diameter | 0.48 | in
| psig | 5 | Steam gage pressure
| patm | 14.7 | Atmospheric pressure
| Number of Radiators | 0
| Steam through orifice plates | 0 | lbm/hr | 0
Annual Fuel Savings
| Factor | Input | Units
| Boiler efficiency | 0.8
| Heat of vaporization | 961 | BTU/lbm
| Annual hours system pressurized | 800 | hrs
| Conversion factor - Btu to MMBTU | 1000000 | Btu to MMBTU
| Steam through hand valves | 0
| Steam through orifice plates | 0
| Steam Savings | 0 | MMbtu
| Steam Savings | 0 | Therms
Steam passing through non orifice plated hand valves - steam passing through orifice plates = steam savings
Steam through one hand valve = 60 * pi/4 * dia^2 * (psig+psi atm)^0.97

## Steam Traps
Steam Traps | [6 empty] | Click to go to Summary of Savings |  |  | Post-Inspection Type
# | Location | # of Steam Traps | # of Tested Traps | # of Failed Open Steam Traps | Failed Open Failure Rate | Pressure | Heat of Vaporization | EFLH | Reduced ELFH | Orifice Diameter | FCR | Steam Losses | Savings without Interactivity (therms) | Savings with Interactivity (therms) |  |  | 0 | 4
1 | [6 empty] | 970 | 1700 | 1700 |  | 0.36 | 0 |  |  | Vlookup | Building_Age | Low-Rise | High-Rise | Post-Inspection Type | Savings Factor
2 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 0 | 1940 & Prior | 999 | 1012 | Visual | 0.95
3 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 1941 | 1941-1978 | 757 | 724 | Functional | 1
4 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 1979 | 1979-2006 | 723 | 395
5 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 2007 | 2007-Now | 503 | 219
6 | [6 empty] | 970 | 1700 | 1700 |  | 0.36 | 0
7 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0
8 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0
9 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0
10 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0
11 | [6 empty] | 970 | 1700 | 1700 |  | 0.36 | 0
12 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0
13 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | Steam gage pressure (psig) | Heat of vaporization (latent heat), in Btu/lb
14 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 0 | 970
15 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 1 | 968
16 | [6 empty] | 970 | 1700 | 1700 |  | 0.36 | 0 |  |  | 2 | 966
17 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 3 | 964
18 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 4 | 962
19 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 5 | 961
20 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 6 | 959
21 | [6 empty] | 970 | 1700 | 1700 |  | 0.36 | 0 |  |  | 7 | 957
22 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 8 | 956
23 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 9 | 954
24 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 10 | 953
25 | [6 empty] | #N/A | 1700 | 1700 |  | 0.36 | 0 |  |  | 11 | 951
[13 empty] | 0 | 0 | 12 | 950
[15 empty] | 13 | 948
[15 empty] | 14 | 947
[15 empty] | 15 | 946
[15 empty] | 20 | 940
[15 empty] | 25 | 934
[15 empty] | 30 | 929
[15 empty] | 35 | 924
[15 empty] | 40 | 920
[15 empty] | 45 | 916
[15 empty] | 50 | 912
[15 empty] | 55 | 908
[15 empty] | 60 | 905
[15 empty] | 65 | 901
[15 empty] | 70 | 898
[15 empty] | 75 | 895
[15 empty] | 80 | 892
[15 empty] | 85 | 889
[15 empty] | 90 | 886
[15 empty] | 95 | 884
[15 empty] | 100 | 881
[15 empty] | 110 | 876
[15 empty] | 120 | 871
[15 empty] | 130 | 866
[15 empty] | 140 | 862
[15 empty] | 150 | 857
[15 empty] | 160 | 853
[15 empty] | 170 | 849
[15 empty] | 180 | 845
[15 empty] | 190 | 842
[15 empty] | 200 | 838
[15 empty] | 250 | 821
[15 empty] | 300 | 805
[15 empty] | 350 | 791
[15 empty] | 400 | 777
[15 empty] | 450 | 764
[15 empty] | 500 | 752
[15 empty] | 550 | 740
[15 empty] | 600 | 729
[15 empty] | 700 | 707
[15 empty] | 800 | 686
[15 empty] | 900 | 667
[15 empty] | 1000 | 647
[15 empty] | 1100 | 584
[15 empty] | 1200 | 354
[15 empty] | 1300 | 591
[15 empty] | 1400 | 573
[15 empty] | 1500 | 555
[15 empty] | 1600 | 536
[15 empty] | 1700 | 518
[15 empty] | 1800 | 500
[15 empty] | 1900 | 481
[15 empty] | 2000 | 462
[15 empty] | 2250 | 412
[15 empty] | 2500 | 357
[15 empty] | 2750 | 293
[15 empty] | 3000 | 209

## TRVs
Thermostatic Radiator Valve (TRV) | [9 empty] | Click to go to Summary of Savings
| Location(s) | Boiler Input (MBH) | Number of Apartments | Number of TRVs installed | Does the TRV SOW include Hydronic System Balancing? | Total Number of Radiators | Total Number of Radiators | EFLHheating | Reduced EFLHheating | Annual Energy Savings (Therms) | Adjusted Annual Energy Savings (Therms)
0
0
0
0
0
0
0
0
0
0
[10 empty] | 0 | 0
*adjusted to account for interactive effects with other measures
[14 empty] | Does the TRV SOW include Hydronic System Balancing? | ESF |  |  | Heating EFLH
[12 empty] | Conversion kbtu/therm | 100 | Yes | 0.191 |  |  | 0 | 4
[14 empty] | No | 0.095 | Lookup | Building age | Low-Rise | High-Rise
[16 empty] | 0 | 1940 & Prior | 974 | 987
[16 empty] | 1941 | 1941-1978 | 738 | 513
[16 empty] | 1979 | 1979-2006 | 705 | 385
[16 empty] | 2007 | 2007-Now | 491 | 214
HEI
SF
HDD
ESF
Note on B3: Location(s) where TRVs are installed for this line item. For Example: Apartment Number(s), Room(s), Floor Number and number of apartments.
Note on C3: Boiler Input Capacity Enter the sum of input capacities of all boilers that are run simultaneously in the boiler plant. For Example: If only 1 boiler of a 2 boiler plant is used at a time (lead lag configuration). Enter the input capacity of only 1 boiler or 1/2 of the sum of the 2 boilers.
Note on D3: Number of Apartments where TRVs are being installed in this line item. The Location(s) input should describe all the apartments for this line item. Apartments can be grouped by floor, apartment line, or other methods.
Note on E3: Number of TRVs installed in the apartments for this line item.
Note on F3: Only applicable to Hydronic Distribution Systems.
Note on G3: Total Number of Radiators in the Building, Common Area and In-Unit Radiators.

## Steam Balancing (hidden)
Steam Balancing - Master & Riser Venting
[9 empty] | Main 1 |  | Main 2
[9 empty] | Diameter (in) | Length (ft) | Diameter (in) | Length (ft)
|  |  | Input | [5 empty] | 5 | 3 | 5 | 3
| Operating Pressure |  | 5 | psi |  | Estimated Boiler Cycles Per Year |  | 1800 | 3 | 63 | 4 | 28
| # of Floors |  | 0 | floors |  | Runtime Hours Reduced |  | 70.0313
| Boiler Input |  | 0 | MBH |  | Savings (therms) |  | 0
| Existing System Vent Time (min) |  | 3.5016 |  | Proposed System Vent Time (min) | 1.1672 | Cycle Time Reduction (min) | 2.3344 | Volume (CF) | 3.5016 | Volume (CF) | 2.8525
| Mains |  | Volume (ft^3) |  | Existing Venting Capacity (CFM) | Existing Vent Time (min) | Proposed Venting Capacity (CFM) | Proposed Vent Time (min)
| 1 |  | 3.5016 |  | 1 | 3.5016 | 3 | 1.1672 | Main 3 |  | Main 4
| 2 |  | 2.8525 |  | 1 | 2.8525 | 3 | 0.95084 | Diameter (in) | Length (ft) | Diameter (in) | Length (ft)
| 3 |  | 0.79631 |  | 1 | 0.79631 | 3 | 0.26544 | 5 | 2
| 4 |  | 0 |  | 1 | 0 | 3 | 0 | 4 | 6
| 5 |  | 0
| 6 |  | 0
| Risers | Diameter (in) | Length (ft) | Volume (ft^3) | Existing Venting Capacity (CFM) | Existing Vent Time (min) | Proposed Venting Capacity (CFM) | Proposed Vent Time (min)
| 1 | 2.5 | 0 | 0 | 1 | 0 | 2 | 0 | Volume (CF) | 0.79631 | Volume (CF) | 0
| 2 | 2 | 0 | 0 | 1 | 0 | 2 | 0
| 3 | 1.5 | 0 | 0 | 1 | 0 | 2 | 0 | Main 5 |  | Main 6
| 4 |  |  | 0 |  |  |  |  | Diameter (in) | Length (ft) | Diameter (in) | Length (ft)
| 5 |  |  | 0
[9 empty] | Volume (CF) | 0 | Volume (CF) | 0
Note on F11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: source?
Note on H11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source?

## Radiant Barriers (hidden)
Insulation Barrier
Item | Radiator 1 | Radiator 2 | Radiator 3 | Radiator 4 | Unit
Convector Height | 24 | 24 | 24 | 24 | in
Convector Width | 22 | 30 | 34 | 48 | in
Convector Depth | 6 | 6 | 6 | 6 | in
# of Convectors | 283 | 542 | 885 | 705 | Check # of convectors
Penetration Rate | 50% | 50% | 50% | 50%
Insulated Convector Area | 648.5417 | 1693.75 | 3134.375 | 3525 | ft^2
Convector Temperature | 220 | 220 | 220 | 220 | deg F
Back of Cabinet Temp | 180 | 180 | 180 | 180 | deg F
Existing Wall R-Value (behind cabinet) | 6 | 6 | 6 | 6 | ft2·°F·hr/BTU
Existing Wall U-value (behind cabinet) | 0.16667 | 0.16667 | 0.16667 | 0.16667 | BTU/(ft2·°F·h)
Insulated back of cabinet Temp | 100 | 100 | 100 | 100 | deg F
Existing Wall U-A | 108.0903 | 282.2917 | 522.3958 | 587.5 | °F·hr/BTU
Existing Heat Loss | 38293.6832 | 100008.8802 | 185071.7839 | 208136.5625 | kbtu
Proposed Heat Loss | 16347.0332 | 42692.3802 | 79004.5339 | 88850.5625 | kbtu
Heat Plant Efficiency | 0% | 0% | 0% | 0% | %
Energy Savings | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | kbtu
Therms Saved | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | therms
Bin Temperature | Enthalpy (BTU/lbda) | Hours | Existing Heat Transfer (Q) Convector 1 | Existing Heat Transfer (Q) Convector 2 | Existing Heat Transfer (Q) Convector 3 | Existing Heat Transfer (Q) Convector 4 | Proposed Heat Transfer (Q) Convector 1 | Proposed Heat Transfer (Q) Convector 2 | Proposed Heat Transfer (Q) Convector 3 | Proposed Heat Transfer (Q) Convector 4
(Range is +/- 2.5 °F) |  |  | KBTU | KBTU | KBTU | KBTU | KBTU | KBTU | KBTU | KBTU
107.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87.5 | 32.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82.5 | 29.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77.5 | 27.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72.5 | 26.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67.5 | 24.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62.5 | 22.3016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57.5 | 19.5684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52.5 | 17.9623 | 439 | 6050.0831 | 15800.5703 | 29239.8008 | 32883.8438 | 2253.9525 | 5886.487 | 10893.2591 | 12250.8438
47.5 | 15.8297 | 497 | 7118.015 | 18589.612 | 34401.0716 | 38688.3438 | 2820.3456 | 7365.6953 | 13630.6133 | 15329.3438
42.5 | 14.0992 | 434 | 6450.2873 | 16845.7552 | 31173.9714 | 35059.0625 | 2697.3929 | 7044.5885 | 13036.388 | 14661.0625
37.5 | 11.7667 | 527 | 8117.3096 | 21199.3984 | 39230.6211 | 44119.7812 | 3560.2235 | 9297.9818 | 17206.4128 | 19350.7812
32.5 | 9.9661 | 313 | 4990.2579 | 13032.7005 | 24117.7096 | 27123.4062 | 2283.6773 | 5964.1172 | 11036.918 | 12412.4062
27.5 | 8.5693 | 138 | 2274.7599 | 5940.8281 | 10993.8203 | 12363.9375 | 1081.4432 | 2824.3281 | 5226.5703 | 5877.9375
22.5 | 6.9471 | 107 | 1821.5914 | 4757.3203 | 8803.6758 | 9900.8438 | 896.3386 | 2340.9036 | 4331.9674 | 4871.8438
17.5 | 5.3871 | 62 | 1089.0095 | 2844.0885 | 5263.138 | 5919.0625 | 552.8818 | 1443.9219 | 2672.0547 | 3005.0625
12.5 | 3.5984 | 17 | 307.7871 | 803.8255 | 1487.5221 | 1672.9062 | 160.7843 | 419.9089 | 777.0638 | 873.9062
7.5 | 2.3057 | 4 | 74.5823 | 194.7812 | 360.4531 | 405.375 | 39.9934 | 104.4479 | 193.2865 | 217.375
2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Temperature Reduction (hidden)
|  | Savings | Amount | Units
|  | Pre-retrofit Space Temperature | 76 | deg F
|  | Temperature Reduction | 8 | deg F
|  | Post-retrofit Space Temperature | 68 | deg F
|  | Boiler Efficiency | 0%
|  | Savings | #DIV/0! | kbtu
|  | Savings | #DIV/0! | therms
|  | Percentage of Heating Usage | #DIV/0!
|  | Usage allocated to space heat | 5124.9561
|  | % Savings of space heat usage | #DIV/0!
Bin Temperature | Enthalpy (BTU/lbda) | Hours | Slab | Envelope | Ventilation
(Range is +/- 2.5 °F)
107.5 | 0 | 0 | 0 | 0 | 0
102.5 | 0 | 0 | 0 | 0 | 0
97.5 | 0 | 0 | 0 | 0 | 0
92.5 | 0 | 0 | 0 | 0 | 0
87.5 | 32.7808 | 0 | 0 | 0 | 0
82.5 | 29.805 | 0 | 0 | 0 | 0
77.5 | 27.7572 | 0 | 0 | 0 | 0
72.5 | 26.4938 | 0 | 0 | 0 | 0
67.5 | 24.7099 | 0 | 0 | 0 | 0
62.5 | 22.3016 | 0 | 0 | 0 | 0
57.5 | 19.5684 | 0 | 0 | 0 | 0
52.5 | 17.9623 | 439 | 30708.928 | 1806.4075 | 0
47.5 | 15.8297 | 497 | 34766.144 | 2045.0673 | 0
42.5 | 14.0992 | 434 | 30359.168 | 1785.8334 | 0
37.5 | 11.7667 | 527 | 36864.704 | 2168.512 | 0
32.5 | 9.9661 | 313 | 21894.976 | 1287.9398 | 0
27.5 | 8.5693 | 138 | 9653.376 | 567.8456 | 0
22.5 | 6.9471 | 107 | 7484.864 | 440.2861 | 0
17.5 | 5.3871 | 62 | 4337.024 | 255.1191 | 0
12.5 | 3.5984 | 17 | 1189.184 | 69.952 | 0
7.5 | 2.3057 | 4 | 279.808 | 16.4593 | 0
2.5 | 0 | 0 | 0 | 0 | 0
-2.5 | 0 | 0 | 0 | 0 | 0
-7.5 | 0 | 0 | 0 | 0 | 0

## Leak Calc (hidden)
Excess usage after energy model | -474635.5967
-4746.356
Lost water temp | 205 | °F
Make-up water temp | 61.4 | °F
Leak rate | 40 | GPM
Additional leaking during heating | 12 | GPM
Time duration of leak | 8760 | hrs/year
Time for heating leaks | 4560 | hrs/year
Annual gallons lost | 24307200 | gal/year
Savings | 181724.881 | therms

## Air Sealing (custom) (hidden)
Air Sealing | Inputs in Yellow
Measured Average Indoor Space Temperature | 77 | ⁰F
Adjusted Space Temperature | #VALUE! | ⁰F
Efficiency of the heating plant | 0% | %
Volume of the Building | 0 | ft^3
Height of the Building | 0 | ft
Height of Neutral Pressure Line | 0 | ft
Number of Basement Penetrations | 20
Average Gap Area per Penetration | 5 | sq in/penetration
Total Basement Penetration Gap Area | 0.69444 | Sq Ft
Number of Exterior Doors Sealed | 6
Average Gap Area per Door | 50 | sq in/door
Total Exterior Door Gap Area | 2.0833 | Sq Ft
Number of Windows Sealed | 15
Average Gap Area per Window | 9 | sq in/window
Total Exterior Door Gap Area | 0.9375 | Sq Ft
Length of Additional Sealed Gaps | 0 | ft
Average Gap Width | 0.25 | in
Total Gap Area | 0 | Sq Ft
Total Gap | 3.7153 | Sq Ft |  |  |  | 2
CFM Prevented | #VALUE! | CFM
Savings | #VALUE! | kBTU
| #VALUE! | therms
| #VALUE! | dTherms
Bin Temperature | Enthalpy (BTU/lbda) | Hours | Co-Efficient of Discharge (Cd) | ΔCFM | Q (ventilation) - (Btus)
(Range is +/- 2.5 °F)
107.5 | 0 | 0 | 0 | 0 | #VALUE!
102.5 | 0 | 0 | 0 | 0 | #VALUE!
97.5 | 0 | 0 | 0 | 0 | #VALUE!
92.5 | 0 | 0 | 0 | 0 | #VALUE!
87.5 | 32.7808 | 0 | 0 | 0 | #VALUE!
82.5 | 29.805 | 0 | 0 | 0 | #VALUE!
77.5 | 27.7572 | 0 | 0 | 0 | #VALUE!
72.5 | 26.4938 | 0 | 0 | 0 | #VALUE!
67.5 | 24.7099 | 0 | 0 | 0 | #VALUE!
62.5 | 22.3016 | 0 | 0 | 0 | #VALUE!
57.5 | 19.5684 | 0 | 0 | 0 | #VALUE!
52.5 | 17.9623 | 439 | #VALUE! | #VALUE! | #VALUE!
47.5 | 15.8297 | 497 | #VALUE! | #VALUE! | #VALUE!
42.5 | 14.0992 | 434 | #VALUE! | #VALUE! | #VALUE!
37.5 | 11.7667 | 527 | #VALUE! | #VALUE! | #VALUE!
32.5 | 9.9661 | 313 | #VALUE! | #VALUE! | #VALUE!
27.5 | 8.5693 | 138 | #VALUE! | #VALUE! | #VALUE!
22.5 | 6.9471 | 107 | #VALUE! | #VALUE! | #VALUE!
17.5 | 5.3871 | 62 | #VALUE! | #VALUE! | #VALUE!
12.5 | 3.5984 | 17 | #VALUE! | #VALUE! | #VALUE!
7.5 | 2.3057 | 4 | #VALUE! | #VALUE! | #VALUE!
2.5 | 0 | 0 | 0 | 0 | #VALUE!
-2.5 | 0 | 0 | 0 | 0 | #VALUE!
-7.5 | 0 | 0 | 0 | 0 | #VALUE!

## BMS (hidden)
BMS Systems | Usage | Units | Source |  | Explanation
Steam Boiler | #VALUE! | Therms | Heating and DHW Usage
Chiller/Cooling Tower | #DIV/0! | kWh | Utility analysis |  | Chiller and Cooling Tower only run during cooling season. Pumps, air handlers, and fan coil units run in both heating and cooling season which show as electric baseload.
Dual Temp Loop Pumps | 134379.378 | kWh | Quantity*kW*Efficiency*Annual Runtime*Load Factor |  | Dual Temp Loop pumps assumer to run 8,760 hours
Air Handlers | 268758.756 | kWh | Quantity*kW*Efficiency*Annual Runtime*Load Factor |  | Four air handlers each with a supply and return air fan, assumed to run 8,760 hours.
Fan Coil Units | #VALUE! |  | Estimate from remaining usage
SAVINGS
Utility | Existing Consumption | % Savings | Savings
Electricity (kWh) | #DIV/0! | 5% | #DIV/0! | kWh
Gas (therms) | #VALUE! | 5% | #VALUE! | Therms
Usage excluded from total
Electric | #VALUE! | kWh
Gas | #VALUE! | Therms
Systems Excluded |  |  | Source
Lighting | 45016.764 | kWh | 0.2 W per sqft
Elevator | 27269.3858 | kWh | Quantity*kW*Efficiency*Annual Runtime*Load Factor

## Roof Insulation (custom) (hidden)
Roof Insulation
Air-sealing savings will vary highly from one building to the next (therefore not included here), but will likely represent significant savings thus lowering the payback
Input value in the yellow cells (suggestion next to it)
|  | Item | Value | Unit |  | R existing | $/ft² | Suggestion | Linear interpolation
|  | HDD | 4884 | days.F/yr |  | 3 | 2.5 | 2.5 - 4 | Slope | -0.042857
|  | CDD | 1374.01 | days.F/yr |  | 38 | 1 | 1 | Intercept | 2.6286
|  | Cost of fuel | 1.1 | $/therms
|  | Total Heating System Efficiency | 0.75
|  | Cost of insulating from R-existing to R-38 | 3 | $/sqft
|  | Output | Value | Unit
|  | Annual Fuel Savings | 19059.4831 | Therm
|  | Annual Fuel Savings | 1905.9483 | mmBTU
Savings bringing it to R-38
| Existing R-Value | Losses BTU/sqft | Losses, Therms/sqft | Therms/sqft output | Therms/sqft, Input (with heating system eff) | Cost per sqft | Savings per sqft | Payback
| 1 | 150192.24 | 1.5019 | 1.4624 | 1.9499 | 2.5857 | 2.1449 | 1.2055
| 2 | 75096.12 | 0.75096 | 0.71144 | 0.94858 | 2.5429 | 1.0434 | 2.437
| 3 | 50064.08 | 0.50064 | 0.46112 | 0.61482 | 2.5 | 0.6763 | 3.6966
| 4 | 37548.06 | 0.37548 | 0.33596 | 0.44794 | 2.4571 | 0.49274 | 4.9867
| 5 | 30038.448 | 0.30038 | 0.26086 | 0.34781 | 2.4143 | 0.38259 | 6.3103
| 6 | 25032.04 | 0.25032 | 0.2108 | 0.28106 | 2.3714 | 0.30917 | 7.6704
| 7 | 21456.0343 | 0.21456 | 0.17504 | 0.23338 | 2.3286 | 0.25672 | 9.0705
| 8 | 18774.03 | 0.18774 | 0.14822 | 0.19762 | 2.2857 | 0.21738 | 10.5147
| 9 | 16688.0267 | 0.16688 | 0.12736 | 0.16981 | 2.2429 | 0.18679 | 12.0075
| 10 | 15019.224 | 0.15019 | 0.11067 | 0.14756 | 2.2 | 0.16231 | 13.5541
| 11 | 13653.84 | 0.13654 | 0.097014 | 0.12935 | 2.1571 | 0.14229 | 15.1605
| 12 | 12516.02 | 0.12516 | 0.085636 | 0.11418 | 2.1143 | 0.1256 | 16.8336
| 13 | 11553.2492 | 0.11553 | 0.076008 | 0.10134 | 2.0714 | 0.11148 | 18.5814
| 14 | 10728.0171 | 0.10728 | 0.067756 | 0.090341 | 2.0286 | 0.099375 | 20.4132
| 15 | 10012.816 | 0.10013 | 0.060604 | 0.080805 | 1.9857 | 0.088886 | 22.3401
| 16 | 9387.015 | 0.09387 | 0.054346 | 0.072461 | 1.9429 | 0.079707 | 24.3749
| 17 | 8834.8376 | 0.088348 | 0.048824 | 0.065099 | 1.9 | 0.071609 | 26.5331
| 18 | 8344.0133 | 0.08344 | 0.043916 | 0.058554 | 1.8571 | 0.06441 | 28.8332
| 19 | 7904.8547 | 0.079049 | 0.039524 | 0.052699 | 1.8143 | 0.057969 | 31.2976
| 20 | 7509.612 | 0.075096 | 0.035572 | 0.047429 | 1.7714 | 0.052172 | 33.9536
| 21 | 7152.0114 | 0.07152 | 0.031996 | 0.042661 | 1.7286 | 0.046927 | 36.8351
| 22 | 6826.92 | 0.068269 | 0.028745 | 0.038327 | 1.6857 | 0.042159 | 39.9845
| 23 | 6530.0974 | 0.065301 | 0.025777 | 0.034369 | 1.6429 | 0.037806 | 43.4551
| 24 | 6258.01 | 0.06258 | 0.023056 | 0.030741 | 1.6 | 0.033815 | 47.316
| 25 | 6007.6896 | 0.060077 | 0.020553 | 0.027403 | 1.5571 | 0.030144 | 51.6571
| 26 | 5776.6246 | 0.057766 | 0.018242 | 0.024323 | 1.5143 | 0.026755 | 56.5985
| 27 | 5562.6756 | 0.055627 | 0.016102 | 0.02147 | 1.4714 | 0.023617 | 62.3039
| 28 | 5364.0086 | 0.05364 | 0.014116 | 0.018821 | 1.4286 | 0.020703 | 69.0025
| 29 | 5179.0428 | 0.05179 | 0.012266 | 0.016355 | 1.3857 | 0.01799 | 77.0254
| 30 | 5006.408 | 0.050064 | 0.01054 | 0.014053 | 1.3429 | 0.015458 | 86.8692
| 31 | 4844.911 | 0.048449 | 0.0089248 | 0.0119 | 1.3 | 0.01309 | 99.3143
| 32 | 4693.5075 | 0.046935 | 0.0074108 | 0.0098811 | 1.2571 | 0.010869 | 115.6613
| 33 | 4551.28 | 0.045513 | 0.0059885 | 0.0079847 | 1.2143 | 0.0087832 | 138.2514
| 34 | 4417.4188 | 0.044174 | 0.0046499 | 0.0061999 | 1.1714 | 0.0068199 | 171.7669
| 35 | 4291.2069 | 0.042912 | 0.0033878 | 0.0045171 | 1.1286 | 0.0049688 | 227.1331
| 36 | 4172.0067 | 0.04172 | 0.0021958 | 0.0029277 | 1.0857 | 0.0032205 | 337.1264
| 37 | 4059.2497 | 0.040592 | 0.0010682 | 0.0014243 | 1.0429 | 0.0015667 | 665.6275
| 38 | 3952.4274 | 0.039524 | 0 | 0 | 1 | 0 | #DIV/0!

## Boiler Clean & Tune (TRM) (hidden)
Boiler Clean & Tune Savings
| Building Vintage | Prior to 1979 |  | Multifamily High-Rise Heating ELFH
| Boiler Make/Model | A.L. Eastmond/ESP-125 |  | Pre-war uninsulated brick | 1012
| # of Boilers | 1 |  | Prior to 1979 | 526
|  |  |  | 1979 to 2006 | 395
| Annual Gas Energy Savings |  |  | 2007 to present | 219
|  | Value | Units
| Boiler Input | 0 | kbtu/in
| Load Factor (LF) | 1.3
| Ec,baseline | 0%
| Ec,ee | 80%
| EFLHheating | 0 | hrs
| Reduced EFLHheating | -35.0157 | hrs
| Δtherms | 0 | therms

## EMS Controls (TRM-conEd) (hidden)
EMS Control
Advanced Boiler Control
| Inputs |  | Explanation
| units | 0 | Number of measures being installed
| Boiler Input (MBH) | 0 | Boiler input rating (MBH)
| BTU/h-in | 0 | Boiler input rating (BTU/h)
| EFLH-heating | 999 | Heating equivalent full-load hours
| Reduced EFLH | 999 | Reduced heating equivalent full-load hours
| ESF | 0.1 | Energy Savings Factor for boiler control systems
| Savings | 0 | therms
[6 empty] | 0 | 4
|  |  |  | Vlookup | Building_Age | Low-Rise | High-Rise
|  |  |  | 0 | 1940 & Prior | 999 | 724
|  |  |  | 1941 | 1941-1978 | 757 | 724
|  |  |  | 1979 | 1979-2006 | 723 | 395
|  |  |  | 2007 | 2007-Now | 503 | 219
*The hours are determined conEd Evalulation of EMS measure
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4389 = heating run hours, hours at temp. 55F & below.

## Central DHW Control
Central DHW Control |  |  |  | Is DHW heated by the Space Heating Boiler? |  |  | Click to go to Summary of Savings
hp | Type of pump | Proposed Control Type | hrsrecirc, baseline | Fuel used to heat DHW | Tdel | Effpump | FDHW, elec | FDHW, fuel | Et, elec | Et, fuel | Et, fuel, w/Interactivity | ESFpump | ESFHW | GPD | ΔTmain | LF | CF | ΔkWhpump | ΔkWhHW | ΔkWh | ΔkW | Δtherms | Δtherms w/Interactivity
[12 empty] | 0.87 |  | 0 | 64.3 | 0.9 | 0.8
[12 empty] | 0.87 |  | 0 | 64.3 | 0.9 | 0.8
[12 empty] | 0.87 |  | 0 | 64.3 | 0.9 | 0.8
[12 empty] | 0.87 |  | 0 | 64.3 | 0.9 | 0.8
[12 empty] | 0.87 |  | 0 | 64.3 | 0.9 | 0.8
[18 empty] | 0 | 0 | 0 | 0 | 0 | 0
[24 empty] | Pump Motor Type | Efficiency
[24 empty] | PSC Pump | 0.6
[24 empty] | ECM Pump | 0.8
[24 empty] | Unknown | 0.8
[25 empty] | FDHW, elec | FDHW, fuel | Et, elec | Et, fuel
[24 empty] | Electricity | 1 | 0 | 0.98
[24 empty] | Gas | 0 | 1 |  | 0.8
[24 empty] | Control Type | ESFHW
[24 empty] | Demand Control | 0.07
[24 empty] | Temperature Modulation | 0.02
[24 empty] | Demand Control and Temperature Modulation | 0.15

## EMS Controls
EMS Control |  |  |  | Click to go to Summary of Savings
Advanced Boiler Control
| Inputs |  | Explanation
Is DHW heated by the Space Heating Boiler?
| Baseline Gas Usage | 0 | therms
| Reduction in Gas Load | 0 | therms
| Reduced Baseline Gas Usage | 0 | therms
| ESF | 0 | Energy Savings Factor for boiler control systems
| Savings without Interactivity (therms) | 0 | therms
| Savings with Interactivity (therms) | 0 | therms
[5 empty] | ConEd |  | Heating |  | Utility
[7 empty] | 0 | 4 | ConEd
[5 empty] | Lookup | Building age | Low-Rise | High-Rise | National Grid
[5 empty] | 0 | 1940 & Prior | 999 | 724
[5 empty] | 1941 | 1941-1978 | 757 | 724 |  | 41 | 50% | 50% | 100%
[5 empty] | 1979 | 1979-2006 | 723 | 395
[5 empty] | 2007 | 2007-Now | 503 | 219
*The hours are determined conEd Evalulation of EMS measure
[5 empty] | National Grid |  | Heating
[7 empty] | 0 | 4
[5 empty] | Lookup | Building age | Low-Rise | High-Rise
[5 empty] | 0 | 1940 & Prior | 974 | 987
[5 empty] | 1941 | 1941-1978 | 738 | 513
[5 empty] | 1979 | 1979-2006 | 705 | 385
[5 empty] | 2007 | 2007-Now | 491 | 214
*TRM v10 Heating EFLH
**Niether EFLH table is used for this calculation

## Smart TRE
Smart Thermostatic Radiator Enclosure | [5 empty] | Click to go to Summary of Savings
[9 empty] | Savings without Interactivity |  | Savings with Interactivity
# of Units | Space Heating Consumption (BTU) | Heatingannual (MMBTU) | Building Area (ft2) | Heating Energy Intensity (HEI) | HDD with Interactivity | Space Heating Consumption (BTU) | Heatingannual with Interactivity (MMBTU) | Heating Energy Intensity (HEI) with Interactivity | ∆kWh | ∆Therms | ∆kWh | ∆Therms
| #DIV/0! | #DIV/0! | 0 | #DIV/0! | 4901 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0
[13 empty] | HDD | F_ratio | F_lower bound | kWhTRE
[13 empty] | 4900 | 0.018 | 0.02 | 7

## Pipe Insulation
Pipe Insulation |  |  |  | Click to go to Summary of Savings |  |  | Space Heating Equipment Efficiency |  | 0% |  | Space Heating Equipment Efficiency with Interactivity |  | 0% |  | EFLHHeating
|  |  |  | Is DHW heated by the Space Heating Boiler? |  |  | DHW Equipment Efficiency |  |  |  | DHW Equipment Efficiency with Interactivity |  |  |  | EFLHHeating with Interactivity
No. | Location | Pipe Type | Insulation Type | Pipe Material | Pipe Diameter (in) | Pipe Length (ft) | Insulation Thickness (in) | Minimun Insulation Thickness (in) | Pipe Temperature (°F) | Ambient Temp (°F) | Boiler Efficiency | Boiler Efficiency with Interactivity | (UA/L)Baseline | (UA/L)ee | Heating EFLH (hours) | Heating EFLH with Interactivity (hours) | Annual Gas Energy Savings (therms) | Annual Electric Energy Savings (kWh) | Summer Peak Coincident Demand Savings (kW) | Annual Gas Energy Savings with Interactivity (therms) | Annual Electric Energy Savings with Interactivity (kWh) | Summer Peak Coincident Demand Savings with Interactivity (kW)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | UA/L Baseline | [12 empty] | UA/L EE | [12 empty] | Minimun Required Insulation Thickness |  |  |  | Pipe Diameter
[24 empty] | Copper |  |  | Steel |  |  | CPVC |  | PEX |  |  |  |  | Fiberglass | [5 empty] | Rigid Foam/Cellular Glass | [5 empty] | Application | (CE) Ambient Temp (°F) | (NG) Ambient Temp (°F) | Pipe Temperature (°F) | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5 | 6 | 8 | 10 | 12 | 14 | 16 |  |  | Heating EFLH
[23 empty] | Pipe Diameter (in) | DHW | Hot Water Heating | Steam Heating | DHW | Hot Water Heating | Steam Heating | DHW | Hot Water Heating | DHW | Hot Water Heating |  |  | Pipe Diameter (in) | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | Hot Water Heating | 50 | 70 | 160 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 0 | 4
[23 empty] | - | CopperDHW | CopperHot Water Heating | CopperSteam Heating | SteelDHW | SteelHot Water Heating | SteelSteam Heating | CPVCDHW | CPVCHot Water Heating | PEXDHW | PEXHot Water Heating |  |  | - | Fiberglass0.5 | Fiberglass1 | Fiberglass1.5 | Fiberglass2 | Fiberglass2.5 | Fiberglass3 | Rigid Foam/Cellular Glass0.5 | Rigid Foam/Cellular Glass1 | Rigid Foam/Cellular Glass1.5 | Rigid Foam/Cellular Glass2 | Rigid Foam/Cellular Glass2.5 | Rigid Foam/Cellular Glass3 | Steam Heating | 50 | 70 | 212 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Lookup | Building age | Low-Rise | High-Rise
[23 empty] | 0.5 | 0.44 | 0.48 | 0.53 | Invalid Selection Combination | 0.53 | 0.59 | 0.39 | 0.41 | 0.39 | 0.41 |  |  | 0.5 | 0.12 | 0.09 | 0.08 | 0.07 | 0.06 | 0.06 | 0.16 | 0.12 | 0.1 | 0.09 | 0.09 | 0.08 | DHW | 70 | 70 | 125 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 0 | 1940 & Prior | 974 | 987
[23 empty] | 0.75 | 0.54 | 0.58 | 0.64 | Invalid Selection Combination | 0.65 | 0.72 | 0.48 | 0.5 | 0.48 | 0.5 |  |  | 0.75 | 0.14 | 0.1 | 0.09 | 0.08 | 0.07 | 0.07 | 0.18 | 0.14 | 0.12 | 0.11 | 0.1 | 0.09 | [21 empty] | 1941 | 1941-1978 | 738 | 513
[23 empty] | 1 | 0.65 | 0.7 | 0.78 | Invalid Selection Combination | 0.79 | 0.88 | 0.56 | 0.58 | 0.56 | 0.58 |  |  | 1 | 0.16 | 0.12 | 0.1 | 0.09 | 0.08 | 0.07 | 0.21 | 0.16 | 0.13 | 0.12 | 0.11 | 0.1 | [21 empty] | 1979 | 1979-2006 | 705 | 385
[23 empty] | 1.25 | 0.8 | 0.86 | 0.96 | Invalid Selection Combination | 0.97 | 1.09 | 0.69 | 0.72 | 0.69 | 0.72 |  |  | 1.25 | 0.19 | 0.14 | 0.11 | 0.1 | 0.09 | 0.08 | 0.24 | 0.18 | 0.15 | 0.13 | 0.12 | 0.11 | Utility | DHW Efficiency | [19 empty] | 2007 | 2007-Now | 491 | 214
[23 empty] | 1.5 | 0.9 | 0.97 | 1.09 | Invalid Selection Combination | 1.1 | 1.23 | 0.78 | 0.81 | 0.78 | 0.81 |  |  | 1.5 | 0.21 | 0.15 | 0.12 | 0.1 | 0.09 | 0.09 | 0.27 | 0.2 | 0.16 | 0.14 | 0.13 | 0.12 | ConEd | 0.8
[23 empty] | 2 | 1.1 | 1.19 | 1.33 | Invalid Selection Combination | 1.34 | 1.51 | 0.95 | 0.98 | 0.95 | 0.98 |  |  | 2 | 0.25 | 0.17 | 0.14 | 0.12 | 0.11 | 0.1 | 0.32 | 0.23 | 0.19 | 0.16 | 0.15 | 0.13 | National Grid | 0.75
[23 empty] | 2.5 | 1.31 | 1.42 | 1.58 | Invalid Selection Combination | 1.6 | 1.8 | 1.07 | 1.11 | 1.07 | 1.11 |  |  | 2.5 | 0.29 | 0.2 | 0.16 | 0.13 | 0.12 | 0.11 | 0.37 | 0.26 | 0.21 | 0.18 | 0.16 | 0.15
[23 empty] | 3 | 1.57 | 1.7 | 1.9 | Invalid Selection Combination | 1.92 | 2.16 | 1.23 | 1.27 | 1.23 | 1.27 |  |  | 3 | 0.34 | 0.23 | 0.18 | 0.15 | 0.13 | 0.12 | 0.43 | 0.3 | 0.24 | 0.21 | 0.18 | 0.17
[23 empty] | 3.5 | 1.77 | 1.92 | 2.15 | Invalid Selection Combination | 2.18 | 2.45 | 1.38 | 1.42 | 1.38 | 1.42 |  |  | 3.5 | 0.38 | 0.26 | 0.2 | 0.17 | 0.15 | 0.13 | 0.47 | 0.33 | 0.27 | 0.23 | 0.2 | 0.18
[23 empty] | 4 | 1.98 | 2.14 | 2.4 | Invalid Selection Combination | 2.43 | 2.73 | 1.52 | 1.57 | 1.52 | 1.57 |  |  | 4 | 0.42 | 0.28 | 0.22 | 0.18 | 0.16 | 0.14 | 0.52 | 0.36 | 0.29 | 0.25 | 0.22 | 0.2
[23 empty] | 5 | 2.41 | 2.61 | 2.92 | Invalid Selection Combination | 2.97 | 3.34 | 1.82 | 1.87 | 1.82 | 1.87 |  |  | 5 | 0.51 | 0.33 | 0.26 | 0.21 | 0.18 | 0.16 | 0.63 | 0.43 | 0.34 | 0.29 | 0.25 | 0.23
[23 empty] | 6 | 2.84 | 3.07 | 3.45 | Invalid Selection Combination | 3.5 | 3.94 | 2.09 | 2.15 | 2.09 | 2.15 |  |  | 6 | 0.59 | 0.38 | 0.29 | 0.24 | 0.21 | 0.19 | 0.73 | 0.5 | 0.39 | 0.33 | 0.28 | 0.25
[23 empty] | 8 | 3.64 | 3.94 | 4.42 | Invalid Selection Combination | 4.5 | 5.06 | 2.56 | 2.62 | 2.56 | 2.62 |  |  | 8 | 0.75 | 0.48 | 0.36 | 0.3 | 0.26 | 0.23 | 0.91 | 0.62 | 0.48 | 0.4 | 0.35 | 0.31
[23 empty] | 10 | 4.26 | 4.86 | 5.46 | Invalid Selection Combination | 5.55 | 6.25 | [6 empty] | 10 | 0.93297 | 0.59075 | 0.44293 | 0.35997 | 0.30658 | 0.26927 | 1.1438 | 0.76246 | 0.58576 | 0.48291 | 0.4153 | 0.36725
[23 empty] | 12 | 5.01 | 5.72 | 6.43 | Invalid Selection Combination | 6.54 | 7.37 | [6 empty] | 12 | 1.0918 | 0.68826 | 0.51365 | 0.41567 | 0.35268 | 0.30863 | 1.3365 | 0.88694 | 0.67829 | 0.5569 | 0.47714 | 0.42047
[23 empty] | 14 | 5.48 | 6.26 | 7.03 | Invalid Selection Combination | 7.16 | 8.07 | [6 empty] | 14 | 1.191 | 0.74904 | 0.55778 | 0.45038 | 0.38136 | 0.33314 | 1.4567 | 0.96467 | 0.73606 | 0.60311 | 0.51561 | 0.45358
[23 empty] | 16 | 6.23 | 7.12 | 8 | Invalid Selection Combination | 8.15 | 9.19 | [6 empty] | 16 | 1.3491 | 0.84593 | 0.62816 | 0.50585 | 0.42716 | 0.37223 | 1.6484 | 1.0885 | 0.82829 | 0.67668 | 0.57711 | 0.50644
*Data for Diameters 10-16 are from NG
[23 empty] | Gas Utility | Heating System Type | Heating System Size Range | Existing Pipe Condition | Pipe Diameter (in) | Copper Pipe Usage | Steel Pipe Usage | Insulation Type | Insulation Thickness | UA/L Baseline | UA/L EE | Heating System Inputs | DHW Source
[23 empty] | ConEd | Boiler, Hot Water, Gas Fired | < 300 kBTU/h | Steel | 0.5 | Domestic Hot Water | Hot Water Heating | Fiberglass | 0.5 | CopperDomestic Hot Water | Fiberglass0.5 | Hot Water Space Heating System | Gas
[23 empty] | National Grid | Boiler, Steam, Gas Fired, All Except Natural Draft | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Copper | 0.75 | Hot Water Heating | Steam Heating | Rigid Foam/Cellular Glass | 1 | CopperHot Water Heating | Fiberglass1 | Steam Heating System | Electric
[24 empty] | Boiler, Steam, Gas Fired, Natural Draft | > 2,500 kBTU/h | CPVC | 1 | Steam Heating |  |  | 1.5 | CopperSteam Heating | Fiberglass1.5 | DHW System
[26 empty] | PEX | 1.25 |  |  |  | 2 | SteelHot Water Heating | Fiberglass2 |  | DHW Heating Source
[27 empty] | 1.5 |  |  |  | 2.5 | SteelSteam Heating | Fiberglass2.5 |  | Gas
[27 empty] | 2 |  |  |  | 3 |  | Fiberglass3
[27 empty] | 2.5 | [5 empty] | Rigid Foam/Cellular Glass0.5
[27 empty] | 3 | [5 empty] | Rigid Foam/Cellular Glass1
[27 empty] | 3.5 | [5 empty] | Rigid Foam/Cellular Glass1.5
[27 empty] | 4 | [5 empty] | Rigid Foam/Cellular Glass2
[27 empty] | 5 | [5 empty] | Rigid Foam/Cellular Glass2.5
[27 empty] | 6 | [5 empty] | Rigid Foam/Cellular Glass3
8
10
12
14
16

## Pipe Insulation (OLD) (hidden)
Pipe Insulation |  |  |  | Supply Pipe Survey |  |  |  |  | Estimated Linear Equivalent Length (in) |  |  | Total Length (in) | [9 empty] | Click to go to Summary of Savings | [6 empty] | Row | Building | Floor | Room | Pipe Location | Pipe Elevation (FT) | System Application | Length of Bare Pipe (ft) | Pipe Type | Diameter of Pipe (") | Insulation Required by Code (") | Insulation to be Added (") | Insulation Type | 725033 | NEW YORK CENTRAL PRK OBS BELV
Input | Value | Unit | Explanation | Diameter | Linear (ft) | 90° Elbows | 45° Elbows | Tees | 90° Elbows | 45° Elbows | Tees | 90° Elbows | 45° Elbows | Tees | Sum (in) | ft | UA/L Baseline | UA/L ee | Savings Without Interactivity (therms) | Savings With Interactivity (therms) | [8 empty] | 0 | [12 empty] | Date (MM/DD/YYYY) | Time (HH:MM) | Dry-bulb (C)
Insulation Thickness | 2" | in | Thickness to install (defaults to 2" if nothing selected) | 0.5 |  |  |  |  | 2.35 | 0.98948 | 2.4606 | 0 | 0 | 0 | 0 | 0 | 0.69074 | 0.077322 | #DIV/0! | #DIV/0! | [8 empty] | 1 | [12 empty] | 1976-01-01 | 1:00 | 2.2 | Hot Pipe Hours | Temp (°F) | Temp (°C)
T pipe - supply | 212 | °F | Temperature of pipe - steam | 0.75 |  |  |  |  | 2.35 | 1.175 | 2.8543 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0.08 | #DIV/0! | #DIV/0! | [8 empty] | 2 | [12 empty] | 1976-01-01 | 2:00 | 2.2 | 2937 | 45 | 7.2222
T pipe - return | 180 | °F |  | 1 |  |  |  |  | 2.35 | 1.3605 | 3.7402 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0.09 | #DIV/0! | #DIV/0! | [8 empty] | 3 | [12 empty] | 1976-01-01 | 3:00 | 1.7
T amb | 70 | °F | Ambient Temperature | 1.25 |  |  |  |  | 2.9684 | 1.5461 | 4.7244 | 0 | 0 | 0 | 0 | 0 | 1.09 | 0.1 | #DIV/0! | #DIV/0! | [8 empty] | 4 | [12 empty] | 1976-01-01 | 4:00 | 1.1
Delta T - Steam supply | 142 | °F | Temperature difference between ambient air and steam | 1.5 |  |  |  |  | 3.525 | 1.7934 | 5.6102 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0.11 | #DIV/0! | #DIV/0! | [8 empty] | 5 | [12 empty] | 1976-01-01 | 5:00 | 1.1
Delta T - Condensate Return | 110 | °F | Temperature difference between ambient air and return | 2 |  |  |  |  | 4.7 | 2.1645 | 6.3976 | 0 | 0 | 0 | 0 | 0 | 1.51 | 0.12 | #DIV/0! | #DIV/0! | [8 empty] | 6 | [12 empty] | 1976-01-01 | 6:00 | 0.6
hrs | 2937 | hrs | Annual operating hours | 2.5 |  |  |  |  | 5.875 | 2.7211 | 7.4803 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0.14 | #DIV/0! | #DIV/0! | [8 empty] | 7 | [12 empty] | 1976-01-01 | 7:00 | 1.1
Reduced hrs | 2937 | hrs | Reduced annual operating hours | 3 |  |  |  |  | 7.05 | 3.154 | 8.4646 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0.16 | #DIV/0! | #DIV/0! | [8 empty] | 8 | [12 empty] | 1976-01-01 | 8:00 | 1.1
GasSF | 1 |  | Gas Savings Factor | 3.5 |  |  |  |  | 8.225 | 3.525 | 9.3504 | 0 | 0 | 0 | 0 | 0 | 2.45 | 0.17 | #DIV/0! | #DIV/0! | [8 empty] | 9 | [12 empty] | 1976-01-01 | 9:00 | 1.1
Et, gas | 0% |  | Thermal Efficiency | 4 |  |  |  |  | 9.4 | 3.9579 | 10.3346 | 0 | 0 | 0 | 0 | 0 | 2.73 | 0.18 | #DIV/0! | #DIV/0! | [8 empty] | 10 | [12 empty] | 1976-01-01 | 10:00 | 1.1
Et, gas (with interactivity) | 0% |  | Thermal Efficiency | 4.5 |  |  |  |  | 10.575 | 4.4217 | 11.2697 | 0 | 0 | 0 | 0 | 0 | 3.1555 | 0.2113 | #DIV/0! | #DIV/0! | [8 empty] | 11 | [12 empty] | 1976-01-01 | 11:00 | 1.7
|  |  |  | 5 |  |  |  |  | 11.7501 | 4.8855 | 12.2047 | 0 | 0 | 0 | 0 | 0 | 3.34 | 0.22 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 12:00 | 2.2
Savings Without Interactivity |  | therms |  | 6 |  |  |  |  | 14.1619 | 5.875 | 14.0748 | 0 | 0 | 0 | 0 | 0 | 3.94 | 0.25 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 13:00 | 3.9
Savings With Interactivity |  | therms |  | 8 |  |  |  |  | 18.8619 | 7.854 | 17.5197 | 0 | 0 | 0 | 0 | 0 | 5.06 | 0.3 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 14:00 | 4.4
Incentive Rate | 0 |  |  | 10 |  |  |  |  | 23.5619 | 9.8329 | 21.2598 | 0 | 0 | 0 | 0 | 0 | 6.6873 | 0.36955 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 15:00 | 4.4
Total Incentive | #VALUE! |  |  | Return Piping Survey |  |  |  |  | Estimated Linear Equivalent Length (in) |  |  | Total Length (in) | [29 empty] | 1976-01-01 | 16:00 | 3.3
|  |  |  | Diameter | Linear (ft) | 90° Elbows | 45° Elbows | Tees | 90° Elbows | 45° Elbows | Tees | 90° Elbows | 45° Elbows | Tees | Sum | ft | UA/L Baseline | UA/L ee | Savings | [22 empty] | 1976-01-01 | 17:00 | 1.7
Inputs |  |  |  | 0.5 |  |  |  |  | 2.35 | 0.98948 | 2.4606 | 0 | 0 | 0 | 0 | 0 | 0.69074 | 0.077322 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 18:00 | 1.1
Outputs |  |  |  | 0.75 |  |  |  |  | 2.35 | 1.175 | 2.8543 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0.08 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 19:00 | 1.1
|  |  |  | 1 |  |  |  |  | 2.35 | 1.3605 | 3.7402 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0.09 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 20:00 | 1.1
|  |  |  | 1.25 |  |  |  |  | 2.9684 | 1.5461 | 4.7244 | 0 | 0 | 0 | 0 | 0 | 1.09 | 0.1 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 21:00 | 0.6
Boiler Input | 0 | MBH |  | 1.5 |  |  |  |  | 3.525 | 1.7934 | 5.6102 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0.11 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 22:00 | 0
Heating Usage from Utility | #DIV/0! | therms |  | 2 |  |  |  |  | 4.7 | 2.1645 | 6.3976 | 0 | 0 | 0 | 0 | 0 | 1.51 | 0.12 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 23:00 | -0.6
Calculated Full Load Hours | #DIV/0! | EFLH |  | 2.5 |  |  |  |  | 5.875 | 2.7211 | 7.4803 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0.14 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-01 | 24:00 | -1.1
|  |  |  | 3 |  |  |  |  | 7.05 | 3.154 | 8.4646 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0.16 | #DIV/0! | #DIV/0! | [21 empty] | 1976-01-02 | 1:00 | -2.8
[35 empty] | Pipe Diameters | Total Length | [5 empty] | 1976-01-02 | 2:00 | -3.3
Nighttime Outdoor Cutoff | 40 | F | [8 empty] | Measurements estimated from: | [23 empty] | 0.5 | 0 | [5 empty] | 1976-01-02 | 3:00 | -3.9
Daytime Cutoff | 55 | F | [8 empty] | https://www.redearthsteels.com/asme-b16-9-90-degree-long-radius-elbow.html | [23 empty] | 0.75 | 0 | [5 empty] | 1976-01-02 | 4:00 | -4.4
Heating Season Start Date | 2021-10-15 | [9 empty] | https://www.asme.org/codes-standards/find-codes-standards/b16-9-factory-made-wrought-buttwelding-fittings | [23 empty] | 1 | 0 | [5 empty] | 1976-01-02 | 5:00 | -5
Heating Season End Date | 2021-04-15 | [33 empty] | 1.25 | 0 | [5 empty] | 1976-01-02 | 6:00 | -5.6
Heating Hours | 2937 | hrs | Aproximation based on hours below 45 °F | [31 empty] | 1.5 | 0 | [5 empty] | 1976-01-02 | 7:00 | -5.6
[35 empty] | 2 | 0 | [5 empty] | 1976-01-02 | 8:00 | -5.6
[7 empty] | 0.5" | 1" | 1.5" | 2" | [24 empty] | 2.5 | 0 | [5 empty] | 1976-01-02 | 9:00 | -5.6
[5 empty] | diameter | UA/L Baseline | UA/L ee | UA/L ee | UA/L ee | UA/L ee | [24 empty] | 3 | 0 | [5 empty] | 1976-01-02 | 10:00 | -4.4
[5 empty] | 0.5 | 0.69074 | 0.13 | 0.09 | 0.08 | 0.077322 | [24 empty] | 3.5 | 0 | [5 empty] | 1976-01-02 | 11:00 | -2.8
[5 empty] | 0.75 | 0.72 | 0.14 | 0.11 | 0.09 | 0.08 | [24 empty] | 4 | 0 | [5 empty] | 1976-01-02 | 12:00 | -2.2
[5 empty] | 1 | 0.88 | 0.17 | 0.12 | 0.1 | 0.09 | [24 empty] | 5 | 0 | [5 empty] | 1976-01-02 | 13:00 | -1.7
[5 empty] | 1.25 | 1.09 | 0.2 | 0.14 | 0.11 | 0.1 | [24 empty] | 6 | 0 | [5 empty] | 1976-01-02 | 14:00 | -1.1
[5 empty] | 1.5 | 1.23 | 0.22 | 0.15 | 0.12 | 0.11 | [24 empty] | 8 | 0 | [5 empty] | 1976-01-02 | 15:00 | -0.6
[5 empty] | 2 | 1.51 | 0.26 | 0.18 | 0.14 | 0.12 | [24 empty] | 9 | 0 | [5 empty] | 1976-01-02 | 16:00 | -0.6
[5 empty] | 2.5 | 1.8 | 0.3 | 0.2 | 0.16 | 0.14 | [11 empty] | 90 Degree Elbows |  |  |  | 45 Degree Elbows | [8 empty] | 10 | 0 | [5 empty] | 1976-01-02 | 17:00 | -1.1
|  |  |  | 4.5 and 10 interpolated using GROWTH formula | 3 | 2.16 | 0.35 | 0.24 | 0.18 | 0.16 | [10 empty] | Diameter | Radius | Arclength (mm) | Arclength (in) | Dimension B | Radius | Arclength (mm) | Arclength (in) | [6 empty] | 12 | 0 | [5 empty] | 1976-01-02 | 18:00 | -1.1
[5 empty] | 3.5 | 2.45 | 0.4 | 0.26 | 0.2 | 0.17 | [10 empty] | 0.5 | 38 | 59.6903 | 2.35 | 16 | 32 | 50.2655 | 0.98948 | [6 empty] | 14 | 0 | [5 empty] | 1976-01-02 | 19:00 | -0.6
[5 empty] | 4 | 2.73 | 0.44 | 0.29 | 0.22 | 0.18 | [10 empty] | 0.75 | 38 | 59.6903 | 2.35 | 19 | 38 | 59.6903 | 1.175 | [6 empty] | 16 | 0 | [5 empty] | 1976-01-02 | 20:00 | -0.6
[5 empty] | 4.5 | 3.1555 | 0.49362 | 0.3222 | 0.24807 | 0.2113 | [10 empty] | 1 | 38 | 59.6903 | 2.35 | 22 | 44 | 69.115 | 1.3605 | [13 empty] | 1976-01-02 | 21:00 | -0.6
[5 empty] | 5 | 3.34 | 0.52 | 0.34 | 0.26 | 0.22 | [10 empty] | 1.25 | 48 | 75.3982 | 2.9684 | 25 | 50 | 78.5398 | 1.5461 | [13 empty] | 1976-01-02 | 22:00 | 0
[5 empty] | 6 | 3.94 | 0.61 | 0.39 | 0.3 | 0.25 | [10 empty] | 1.5 | 57 | 89.5354 | 3.525 | 29 | 58 | 91.1062 | 1.7934 | [13 empty] | 1976-01-02 | 23:00 | 0
[5 empty] | 8 | 5.06 | 0.77 | 0.49 | 0.37 | 0.3 | [10 empty] | 2 | 76 | 119.3805 | 4.7 | 35 | 70 | 109.9557 | 2.1645 | [13 empty] | 1976-01-02 | 24:00 | 0
[5 empty] | 10 | 6.6873 | 1.0024 | 0.62587 | 0.46897 | 0.36955 | [10 empty] | 2.5 | 95 | 149.2257 | 5.875 | 44 | 88 | 138.2301 | 2.7211 | [13 empty] | 1976-01-03 | 1:00 | 0
[21 empty] | 3 | 114 | 179.0708 | 7.05 | 51 | 102 | 160.2212 | 3.154 | [13 empty] | 1976-01-03 | 2:00 | 1.7
[21 empty] | 3.25 | 123.5 | 193.9933 | 7.6375 | 54 | 108 | 169.646 | 3.3395 | [13 empty] | 1976-01-03 | 3:00 | 1.7
[21 empty] | 3.5 | 133 | 208.9159 | 8.225 | 57 | 114 | 179.0708 | 3.525 | [13 empty] | 1976-01-03 | 4:00 | 1.7
[21 empty] | 4 | 152 | 238.761 | 9.4 | 64 | 128 | 201.0619 | 3.9579 | [13 empty] | 1976-01-03 | 5:00 | 2.2
[21 empty] | 4.5 | 171 | 268.6062 | 10.575 | 71.5 | 143 | 224.6239 | 4.4217 | [13 empty] | 1976-01-03 | 6:00 | 2.2
[21 empty] | 5 | 190 | 298.4513 | 11.7501 | 79 | 158 | 248.1858 | 4.8855 | [13 empty] | 1976-01-03 | 7:00 | 2.8
[21 empty] | 6 | 229 | 359.7124 | 14.1619 | 95 | 190 | 298.4513 | 5.875 | [13 empty] | 1976-01-03 | 8:00 | 4.4
[21 empty] | 8 | 305 | 479.0929 | 18.8619 | 127 | 254 | 398.9823 | 7.854 | [13 empty] | 1976-01-03 | 9:00 | 4.4
[21 empty] | 10 | 381 | 598.4734 | 23.5619 | 159 | 318 | 499.5132 | 9.8329 | [13 empty] | 1976-01-03 | 10:00 | 5
[42 empty] | 1976-01-03 | 11:00 | 5.6
[42 empty] | 1976-01-03 | 12:00 | 5.6
[42 empty] | 1976-01-03 | 13:00 | 5
[42 empty] | 1976-01-03 | 14:00 | 5
[42 empty] | 1976-01-03 | 15:00 | 5
[42 empty] | 1976-01-03 | 16:00 | 4.4
[42 empty] | 1976-01-03 | 17:00 | 4.4
[42 empty] | 1976-01-03 | 18:00 | 4.4
[42 empty] | 1976-01-03 | 19:00 | 4.4
[42 empty] | 1976-01-03 | 20:00 | 3.9
[42 empty] | 1976-01-03 | 21:00 | 3.9
[42 empty] | 1976-01-03 | 22:00 | 3.3
[42 empty] | 1976-01-03 | 23:00 | 3.3
[42 empty] | 1976-01-03 | 24:00 | 3.3
[42 empty] | 1976-01-04 | 1:00 | 2.8
[42 empty] | 1976-01-04 | 2:00 | 2.2
[11 empty] | https://hardhatengineer.com/pipe-tee-dimensions-reducing-equal/ | [30 empty] | 1976-01-04 | 3:00 | 1.7
[42 empty] | 1976-01-04 | 4:00 | 1.1
[42 empty] | 1976-01-04 | 5:00 | 0
[42 empty] | 1976-01-04 | 6:00 | -0.6
[42 empty] | 1976-01-04 | 7:00 | -0.6
[42 empty] | 1976-01-04 | 8:00 | -1.7
[42 empty] | 1976-01-04 | 9:00 | -1.7
[22 empty] | Diameter | C (mm) | M (mm) | Total Length (mm) | Total Length (in) | [15 empty] | 1976-01-04 | 10:00 | -1.7
[22 empty] | 0.5 | 25 | 25 | 62.5 | 2.4606 | [15 empty] | 1976-01-04 | 11:00 | -2.2
[22 empty] | 0.75 | 29 | 29 | 72.5 | 2.8543 | [15 empty] | 1976-01-04 | 12:00 | -1.7
[22 empty] | 1 | 38 | 38 | 95 | 3.7402 | [15 empty] | 1976-01-04 | 13:00 | -1.1
[22 empty] | 1.25 | 48 | 48 | 120 | 4.7244 | [15 empty] | 1976-01-04 | 14:00 | -0.6
[22 empty] | 1.5 | 57 | 57 | 142.5 | 5.6102 | [15 empty] | 1976-01-04 | 15:00 | -0.6
[22 empty] | 2 | 65 | 65 | 162.5 | 6.3976 | [15 empty] | 1976-01-04 | 16:00 | -0.6
[22 empty] | 2.5 | 76 | 76 | 190 | 7.4803 | [15 empty] | 1976-01-04 | 17:00 | -0.6
[22 empty] | 3 | 86 | 86 | 215 | 8.4646 | [15 empty] | 1976-01-04 | 18:00 | -1.1
[22 empty] | 3.25 | 90.5 | 90.5 | 226.25 | 8.9075 | [15 empty] | 1976-01-04 | 19:00 | -1.1
[22 empty] | 3.5 | 95 | 95 | 237.5 | 9.3504 | [15 empty] | 1976-01-04 | 20:00 | -1.7
[22 empty] | 4 | 105 | 105 | 262.5 | 10.3346 | [15 empty] | 1976-01-04 | 21:00 | -2.2
[22 empty] | 4.5 | 114.5 | 114.5 | 286.25 | 11.2697 | [15 empty] | 1976-01-04 | 22:00 | -2.8
[22 empty] | 5 | 124 | 124 | 310 | 12.2047 | [15 empty] | 1976-01-04 | 23:00 | -3.3
[22 empty] | 6 | 143 | 143 | 357.5 | 14.0748 | [15 empty] | 1976-01-04 | 24:00 | -3.3
[22 empty] | 8 | 178 | 178 | 445 | 17.5197 | [15 empty] | 1976-01-05 | 1:00 | -3.9
[22 empty] | 10 | 216 | 216 | 540 | 21.2598 | [15 empty] | 1976-01-05 | 2:00 | -3.9
[42 empty] | 1976-01-05 | 3:00 | -4.4
[42 empty] | 1976-01-05 | 4:00 | -4.4
[42 empty] | 1976-01-05 | 5:00 | -5
[42 empty] | 1976-01-05 | 6:00 | -5.6
[42 empty] | 1976-01-05 | 7:00 | -5.6
[42 empty] | 1976-01-05 | 8:00 | -5.6
[42 empty] | 1976-01-05 | 9:00 | -5.6
[42 empty] | 1976-01-05 | 10:00 | -5.6
[42 empty] | 1976-01-05 | 11:00 | -5.6
[42 empty] | 1976-01-05 | 12:00 | -5
[42 empty] | 1976-01-05 | 13:00 | -4.4
[42 empty] | 1976-01-05 | 14:00 | -3.9
[42 empty] | 1976-01-05 | 15:00 | -3.9
[42 empty] | 1976-01-05 | 16:00 | -3.3
[42 empty] | 1976-01-05 | 17:00 | -3.3
[42 empty] | 1976-01-05 | 18:00 | -4.4
[42 empty] | 1976-01-05 | 19:00 | -4.4
[42 empty] | 1976-01-05 | 20:00 | -4.4
[42 empty] | 1976-01-05 | 21:00 | -5
[42 empty] | 1976-01-05 | 22:00 | -5.6
[42 empty] | 1976-01-05 | 23:00 | -5.6
[42 empty] | 1976-01-05 | 24:00 | -6.1
[42 empty] | 1976-01-06 | 1:00 | -6.7
Bin Temperature (Range is +/- 2.5 °F) | Enthalpy (BTU/lbda) | Daytime Hours | [39 empty] | 1976-01-06 | 2:00 | -6.7
107.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 3:00 | -7.2
102.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 4:00 | -6.7
97.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 5:00 | -6.7
92.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 6:00 | -6.7
87.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 7:00 | -6.7
82.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 8:00 | -6.1
77.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 9:00 | -5
72.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 10:00 | -3.9
67.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 11:00 | -2.8
62.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 12:00 | -2.2
57.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 13:00 | -1.7
52.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 14:00 | -1.1
47.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 15:00 | -0.6
42.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 16:00 | -1.1
37.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 17:00 | -0.6
32.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 18:00 | -1.1
27.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 19:00 | -1.1
22.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 20:00 | -1.1
17.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 21:00 | -1.1
12.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 22:00 | -1.7
7.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 23:00 | -1.7
2.5 | 0 | #VALUE! | [39 empty] | 1976-01-06 | 24:00 | -1.7
-2.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 1:00 | -1.7
-7.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 2:00 | -1.1
|  | #VALUE! | [39 empty] | 1976-01-07 | 3:00 | -1.7
[42 empty] | 1976-01-07 | 4:00 | -1.7
Bin Temperature (Range is +/- 2.5 °F) | Enthalpy (BTU/lbda) | Hours | [39 empty] | 1976-01-07 | 5:00 | -1.7
107.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 6:00 | -1.7
102.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 7:00 | -1.1
97.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 8:00 | -0.6
92.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 9:00 | 0.6
87.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 10:00 | 2.2
82.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 11:00 | 2.8
77.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 12:00 | 2.8
72.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 13:00 | 2.8
67.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 14:00 | 2.8
62.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 15:00 | 2.8
57.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 16:00 | 1.7
52.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 17:00 | 1.7
47.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 18:00 | 1.7
42.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 19:00 | 1.7
37.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 20:00 | 1.7
32.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 21:00 | 1.7
27.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 22:00 | 2.2
22.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 23:00 | 2.2
17.5 | 0 | #VALUE! | [39 empty] | 1976-01-07 | 24:00 | 2.2
12.5 | 0 | #VALUE! | [39 empty] | 1976-01-08 | 1:00 | 2.8
7.5 | 0 | #VALUE! | [39 empty] | 1976-01-08 | 2:00 | 2.2
2.5 | 0 | #VALUE! | [39 empty] | 1976-01-08 | 3:00 | 2.2
-2.5 | 0 | #VALUE! | [39 empty] | 1976-01-08 | 4:00 | 2.2
-7.5 | 0 | #VALUE! | [39 empty] | 1976-01-08 | 5:00 | 2.2
|  | #VALUE! | [39 empty] | 1976-01-08 | 6:00 | 2.2
[42 empty] | 1976-01-08 | 7:00 | 2.2
[42 empty] | 1976-01-08 | 8:00 | 2.2
[42 empty] | 1976-01-08 | 9:00 | 2.2
[42 empty] | 1976-01-08 | 10:00 | 2.2
[42 empty] | 1976-01-08 | 11:00 | 1.1
[42 empty] | 1976-01-08 | 12:00 | 0
[42 empty] | 1976-01-08 | 13:00 | -0.6
[42 empty] | 1976-01-08 | 14:00 | -1.1
[42 empty] | 1976-01-08 | 15:00 | -1.1
[42 empty] | 1976-01-08 | 16:00 | -1.7
[42 empty] | 1976-01-08 | 17:00 | -2.2
[42 empty] | 1976-01-08 | 18:00 | -3.3
[42 empty] | 1976-01-08 | 19:00 | -3.9
[42 empty] | 1976-01-08 | 20:00 | -5
[42 empty] | 1976-01-08 | 21:00 | -6.7
[42 empty] | 1976-01-08 | 22:00 | -7.8
[42 empty] | 1976-01-08 | 23:00 | -7.8
[42 empty] | 1976-01-08 | 24:00 | -8.3
[42 empty] | 1976-01-09 | 1:00 | -8.3
[42 empty] | 1976-01-09 | 2:00 | -8.9
[42 empty] | 1976-01-09 | 3:00 | -8.9
[42 empty] | 1976-01-09 | 4:00 | -8.9
[42 empty] | 1976-01-09 | 5:00 | -8.3
[42 empty] | 1976-01-09 | 6:00 | -8.3
[42 empty] | 1976-01-09 | 7:00 | -8.9
[42 empty] | 1976-01-09 | 8:00 | -8.9
[42 empty] | 1976-01-09 | 9:00 | -8.3
[42 empty] | 1976-01-09 | 10:00 | -7.8
[42 empty] | 1976-01-09 | 11:00 | -7.2
[42 empty] | 1976-01-09 | 12:00 | -6.1
[42 empty] | 1976-01-09 | 13:00 | -5.6
[42 empty] | 1976-01-09 | 14:00 | -5.6
[42 empty] | 1976-01-09 | 15:00 | -5.6
[42 empty] | 1976-01-09 | 16:00 | -5.6
[42 empty] | 1976-01-09 | 17:00 | -5.6
[42 empty] | 1976-01-09 | 18:00 | -6.1
[42 empty] | 1976-01-09 | 19:00 | -6.7
[42 empty] | 1976-01-09 | 20:00 | -7.2
[42 empty] | 1976-01-09 | 21:00 | -7.8
[42 empty] | 1976-01-09 | 22:00 | -7.8
[42 empty] | 1976-01-09 | 23:00 | -8.3
[42 empty] | 1976-01-09 | 24:00 | -8.3
[42 empty] | 1976-01-10 | 1:00 | -8.9
[42 empty] | 1976-01-10 | 2:00 | -8.9
[42 empty] | 1976-01-10 | 3:00 | -8.9
[42 empty] | 1976-01-10 | 4:00 | -8.9
[42 empty] | 1976-01-10 | 5:00 | -8.9
[42 empty] | 1976-01-10 | 6:00 | -8.9
[42 empty] | 1976-01-10 | 7:00 | -8.9
[42 empty] | 1976-01-10 | 8:00 | -8.9
[42 empty] | 1976-01-10 | 9:00 | -8.3
[42 empty] | 1976-01-10 | 10:00 | -7.8
[42 empty] | 1976-01-10 | 11:00 | -6.7
[42 empty] | 1976-01-10 | 12:00 | -5.6
[42 empty] | 1976-01-10 | 13:00 | -4.4
[42 empty] | 1976-01-10 | 14:00 | -4.4
[42 empty] | 1976-01-10 | 15:00 | -3.9
[42 empty] | 1976-01-10 | 16:00 | -3.9
[42 empty] | 1976-01-10 | 17:00 | -3.9
[42 empty] | 1976-01-10 | 18:00 | -3.9
[42 empty] | 1976-01-10 | 19:00 | -3.9
[42 empty] | 1976-01-10 | 20:00 | -4.4
[42 empty] | 1976-01-10 | 21:00 | -4.4
[42 empty] | 1976-01-10 | 22:00 | -4.4
[42 empty] | 1976-01-10 | 23:00 | -4.4
[42 empty] | 1976-01-10 | 24:00 | -4.4
[42 empty] | 1976-01-11 | 1:00 | -5
[42 empty] | 1976-01-11 | 2:00 | -5
[42 empty] | 1976-01-11 | 3:00 | -5
[42 empty] | 1976-01-11 | 4:00 | -5
[42 empty] | 1976-01-11 | 5:00 | -4.4
[42 empty] | 1976-01-11 | 6:00 | -4.4
[42 empty] | 1976-01-11 | 7:00 | -5
[42 empty] | 1976-01-11 | 8:00 | -5
[42 empty] | 1976-01-11 | 9:00 | -5
[42 empty] | 1976-01-11 | 10:00 | -3.9
[42 empty] | 1976-01-11 | 11:00 | -3.9
[42 empty] | 1976-01-11 | 12:00 | -3.3
[42 empty] | 1976-01-11 | 13:00 | -2.8
[42 empty] | 1976-01-11 | 14:00 | -1.7
[42 empty] | 1976-01-11 | 15:00 | 0
[42 empty] | 1976-01-11 | 16:00 | 0
[42 empty] | 1976-01-11 | 17:00 | 1.1
[42 empty] | 1976-01-11 | 18:00 | 1.7
[42 empty] | 1976-01-11 | 19:00 | 2.2
[42 empty] | 1976-01-11 | 20:00 | 1.1
[42 empty] | 1976-01-11 | 21:00 | 1.1
[42 empty] | 1976-01-11 | 22:00 | -0.6
[42 empty] | 1976-01-11 | 23:00 | -1.1
[42 empty] | 1976-01-11 | 24:00 | -2.2
[42 empty] | 1976-01-12 | 1:00 | -2.8
[42 empty] | 1976-01-12 | 2:00 | -3.3
[42 empty] | 1976-01-12 | 3:00 | -3.3
[42 empty] | 1976-01-12 | 4:00 | -3.3
[42 empty] | 1976-01-12 | 5:00 | -3.3
[42 empty] | 1976-01-12 | 6:00 | -3.3
[42 empty] | 1976-01-12 | 7:00 | -3.3
[42 empty] | 1976-01-12 | 8:00 | -2.8
[42 empty] | 1976-01-12 | 9:00 | -1.7
[42 empty] | 1976-01-12 | 10:00 | 0
[42 empty] | 1976-01-12 | 11:00 | 0.6
[42 empty] | 1976-01-12 | 12:00 | 1.1
[42 empty] | 1976-01-12 | 13:00 | 1.7
[42 empty] | 1976-01-12 | 14:00 | 2.2
[42 empty] | 1976-01-12 | 15:00 | 1.7
[42 empty] | 1976-01-12 | 16:00 | 1.7
[42 empty] | 1976-01-12 | 17:00 | 1.1
[42 empty] | 1976-01-12 | 18:00 | 0
[42 empty] | 1976-01-12 | 19:00 | -0.6
[42 empty] | 1976-01-12 | 20:00 | -1.1
[42 empty] | 1976-01-12 | 21:00 | -1.7
[42 empty] | 1976-01-12 | 22:00 | -1.7
[42 empty] | 1976-01-12 | 23:00 | -2.2
[42 empty] | 1976-01-12 | 24:00 | -2.8
[42 empty] | 1976-01-13 | 1:00 | -2.8
[42 empty] | 1976-01-13 | 2:00 | -3.3
[42 empty] | 1976-01-13 | 3:00 | -3.3
[42 empty] | 1976-01-13 | 4:00 | -3.3
[42 empty] | 1976-01-13 | 5:00 | -3.9
[42 empty] | 1976-01-13 | 6:00 | -3.9
[42 empty] | 1976-01-13 | 7:00 | -3.9
[42 empty] | 1976-01-13 | 8:00 | -3.3
[42 empty] | 1976-01-13 | 9:00 | -2.8
[42 empty] | 1976-01-13 | 10:00 | -1.7
[42 empty] | 1976-01-13 | 11:00 | -0.6
[42 empty] | 1976-01-13 | 12:00 | 3.3
[42 empty] | 1976-01-13 | 13:00 | 4.4
[42 empty] | 1976-01-13 | 14:00 | 5
[42 empty] | 1976-01-13 | 15:00 | 5.6
[42 empty] | 1976-01-13 | 16:00 | 6.1
[42 empty] | 1976-01-13 | 17:00 | 6.1
[42 empty] | 1976-01-13 | 18:00 | 6.1
[42 empty] | 1976-01-13 | 19:00 | 6.7
[42 empty] | 1976-01-13 | 20:00 | 7.2
[42 empty] | 1976-01-13 | 21:00 | 7.8
[42 empty] | 1976-01-13 | 22:00 | 7.8
[42 empty] | 1976-01-13 | 23:00 | 8.9
[42 empty] | 1976-01-13 | 24:00 | 8.9
[42 empty] | 1976-01-14 | 1:00 | 10.6
[42 empty] | 1976-01-14 | 2:00 | 10.6
[42 empty] | 1976-01-14 | 3:00 | 11.7
[42 empty] | 1976-01-14 | 4:00 | 12.2
[42 empty] | 1976-01-14 | 5:00 | 8.9
[42 empty] | 1976-01-14 | 6:00 | 7.2
[42 empty] | 1976-01-14 | 7:00 | 6.7
[42 empty] | 1976-01-14 | 8:00 | 6.1
[42 empty] | 1976-01-14 | 9:00 | 6.1
[42 empty] | 1976-01-14 | 10:00 | 6.1
[42 empty] | 1976-01-14 | 11:00 | 6.1
[42 empty] | 1976-01-14 | 12:00 | 5.6
[42 empty] | 1976-01-14 | 13:00 | 5.6
[42 empty] | 1976-01-14 | 14:00 | 6.1
[42 empty] | 1976-01-14 | 15:00 | 6.1
[42 empty] | 1976-01-14 | 16:00 | 5.6
[42 empty] | 1976-01-14 | 17:00 | 4.4
[42 empty] | 1976-01-14 | 18:00 | 3.9
[42 empty] | 1976-01-14 | 19:00 | 3.3
[42 empty] | 1976-01-14 | 20:00 | 2.8
[42 empty] | 1976-01-14 | 21:00 | 2.2
[42 empty] | 1976-01-14 | 22:00 | 1.7
[42 empty] | 1976-01-14 | 23:00 | 1.1
[42 empty] | 1976-01-14 | 24:00 | 0.6
[42 empty] | 1976-01-15 | 1:00 | 0
[42 empty] | 1976-01-15 | 2:00 | -0.6
[42 empty] | 1976-01-15 | 3:00 | -0.6
[42 empty] | 1976-01-15 | 4:00 | -0.6
[42 empty] | 1976-01-15 | 5:00 | -0.6
[42 empty] | 1976-01-15 | 6:00 | -0.6
[42 empty] | 1976-01-15 | 7:00 | -0.6
[42 empty] | 1976-01-15 | 8:00 | -0.6
[42 empty] | 1976-01-15 | 9:00 | -0.6
[42 empty] | 1976-01-15 | 10:00 | -1.7
[42 empty] | 1976-01-15 | 11:00 | -1.7
[42 empty] | 1976-01-15 | 12:00 | -1.1
[42 empty] | 1976-01-15 | 13:00 | -0.6
[42 empty] | 1976-01-15 | 14:00 | -0.6
[42 empty] | 1976-01-15 | 15:00 | 0
[42 empty] | 1976-01-15 | 16:00 | 0
[42 empty] | 1976-01-15 | 17:00 | -0.6
[42 empty] | 1976-01-15 | 18:00 | -1.1
[42 empty] | 1976-01-15 | 19:00 | -1.7
[42 empty] | 1976-01-15 | 20:00 | -2.2
[42 empty] | 1976-01-15 | 21:00 | -2.8
[42 empty] | 1976-01-15 | 22:00 | -3.3
[42 empty] | 1976-01-15 | 23:00 | -2.8
[42 empty] | 1976-01-15 | 24:00 | -2.8
[42 empty] | 1976-01-16 | 1:00 | -2.8
[42 empty] | 1976-01-16 | 2:00 | -2.8
[42 empty] | 1976-01-16 | 3:00 | -2.8
[42 empty] | 1976-01-16 | 4:00 | -2.8
[42 empty] | 1976-01-16 | 5:00 | -2.8
[42 empty] | 1976-01-16 | 6:00 | -2.8
[42 empty] | 1976-01-16 | 7:00 | -2.2
[42 empty] | 1976-01-16 | 8:00 | -0.6
[42 empty] | 1976-01-16 | 9:00 | 0.6
[42 empty] | 1976-01-16 | 10:00 | 5.6
[42 empty] | 1976-01-16 | 11:00 | 6.7
[42 empty] | 1976-01-16 | 12:00 | 6.7
[42 empty] | 1976-01-16 | 13:00 | 7.2
[42 empty] | 1976-01-16 | 14:00 | 5
[42 empty] | 1976-01-16 | 15:00 | 4.4
[42 empty] | 1976-01-16 | 16:00 | 3.9
[42 empty] | 1976-01-16 | 17:00 | 3.9
[42 empty] | 1976-01-16 | 18:00 | 3.9
[42 empty] | 1976-01-16 | 19:00 | 3.9
[42 empty] | 1976-01-16 | 20:00 | 3.3
[42 empty] | 1976-01-16 | 21:00 | 3.3
[42 empty] | 1976-01-16 | 22:00 | 3.3
[42 empty] | 1976-01-16 | 23:00 | 3.3
[42 empty] | 1976-01-16 | 24:00 | 2.8
[42 empty] | 1976-01-17 | 1:00 | 2.8
[42 empty] | 1976-01-17 | 2:00 | 2.8
[42 empty] | 1976-01-17 | 3:00 | 1.7
[42 empty] | 1976-01-17 | 4:00 | 0.6
[42 empty] | 1976-01-17 | 5:00 | -0.6
[42 empty] | 1976-01-17 | 6:00 | -1.7
[42 empty] | 1976-01-17 | 7:00 | -2.8
[42 empty] | 1976-01-17 | 8:00 | -3.9
[42 empty] | 1976-01-17 | 9:00 | -4.4
[42 empty] | 1976-01-17 | 10:00 | -5
[42 empty] | 1976-01-17 | 11:00 | -3.9
[42 empty] | 1976-01-17 | 12:00 | -3.3
[42 empty] | 1976-01-17 | 13:00 | -3.3
[42 empty] | 1976-01-17 | 14:00 | -3.3
[42 empty] | 1976-01-17 | 15:00 | -3.9
[42 empty] | 1976-01-17 | 16:00 | -4.4
[42 empty] | 1976-01-17 | 17:00 | -5
[42 empty] | 1976-01-17 | 18:00 | -5.6
[42 empty] | 1976-01-17 | 19:00 | -6.1
[42 empty] | 1976-01-17 | 20:00 | -6.7
[42 empty] | 1976-01-17 | 21:00 | -7.2
[42 empty] | 1976-01-17 | 22:00 | -8.3
[42 empty] | 1976-01-17 | 23:00 | -8.9
[42 empty] | 1976-01-17 | 24:00 | -9.4
[42 empty] | 1976-01-18 | 1:00 | -10
[42 empty] | 1976-01-18 | 2:00 | -11.1
[42 empty] | 1976-01-18 | 3:00 | -11.1
[42 empty] | 1976-01-18 | 4:00 | -11.7
[42 empty] | 1976-01-18 | 5:00 | -12.2
[42 empty] | 1976-01-18 | 6:00 | -12.8
[42 empty] | 1976-01-18 | 7:00 | -13.3
[42 empty] | 1976-01-18 | 8:00 | -13.9
[42 empty] | 1976-01-18 | 9:00 | -13.3
[42 empty] | 1976-01-18 | 10:00 | -12.8
[42 empty] | 1976-01-18 | 11:00 | -11.7
[42 empty] | 1976-01-18 | 12:00 | -10
[42 empty] | 1976-01-18 | 13:00 | -8.9
[42 empty] | 1976-01-18 | 14:00 | -7.8
[42 empty] | 1976-01-18 | 15:00 | -8.3
[42 empty] | 1976-01-18 | 16:00 | -7.8
[42 empty] | 1976-01-18 | 17:00 | -8.3
[42 empty] | 1976-01-18 | 18:00 | -8.9
[42 empty] | 1976-01-18 | 19:00 | -8.9
[42 empty] | 1976-01-18 | 20:00 | -9.4
[42 empty] | 1976-01-18 | 21:00 | -10
[42 empty] | 1976-01-18 | 22:00 | -10.6
[42 empty] | 1976-01-18 | 23:00 | -11.1
[42 empty] | 1976-01-18 | 24:00 | -11.7
[42 empty] | 1976-01-19 | 1:00 | -11.7
[42 empty] | 1976-01-19 | 2:00 | -12.2
[42 empty] | 1976-01-19 | 3:00 | -12.2
[42 empty] | 1976-01-19 | 4:00 | -12.8
[42 empty] | 1976-01-19 | 5:00 | -13.3
[42 empty] | 1976-01-19 | 6:00 | -13.3
[42 empty] | 1976-01-19 | 7:00 | -13.3
[42 empty] | 1976-01-19 | 8:00 | -13.3
[42 empty] | 1976-01-19 | 9:00 | -12.2
[42 empty] | 1976-01-19 | 10:00 | -10.6
[42 empty] | 1976-01-19 | 11:00 | -8.3
[42 empty] | 1976-01-19 | 12:00 | -7.2
[42 empty] | 1976-01-19 | 13:00 | -6.1
[42 empty] | 1976-01-19 | 14:00 | -4.4
[42 empty] | 1976-01-19 | 15:00 | -3.9
[42 empty] | 1976-01-19 | 16:00 | -3.3
[42 empty] | 1976-01-19 | 17:00 | -3.3
[42 empty] | 1976-01-19 | 18:00 | -3.9
[42 empty] | 1976-01-19 | 19:00 | -3.9
[42 empty] | 1976-01-19 | 20:00 | -4.4
[42 empty] | 1976-01-19 | 21:00 | -4.4
[42 empty] | 1976-01-19 | 22:00 | -4.4
[42 empty] | 1976-01-19 | 23:00 | -4.4
[42 empty] | 1976-01-19 | 24:00 | -4.4
[42 empty] | 1976-01-20 | 1:00 | -4.4
[42 empty] | 1976-01-20 | 2:00 | -4.4
[42 empty] | 1976-01-20 | 3:00 | -4.4
[42 empty] | 1976-01-20 | 4:00 | -3.9
[42 empty] | 1976-01-20 | 5:00 | -3.3
[42 empty] | 1976-01-20 | 6:00 | -3.3
[42 empty] | 1976-01-20 | 7:00 | -2.8
[42 empty] | 1976-01-20 | 8:00 | -2.2
[42 empty] | 1976-01-20 | 9:00 | -1.7
[42 empty] | 1976-01-20 | 10:00 | -1.1
[42 empty] | 1976-01-20 | 11:00 | -2.2
[42 empty] | 1976-01-20 | 12:00 | -1.7
[42 empty] | 1976-01-20 | 13:00 | -1.7
[42 empty] | 1976-01-20 | 14:00 | -2.2
[42 empty] | 1976-01-20 | 15:00 | -1.7
[42 empty] | 1976-01-20 | 16:00 | -1.7
[42 empty] | 1976-01-20 | 17:00 | -1.1
[42 empty] | 1976-01-20 | 18:00 | -1.7
[42 empty] | 1976-01-20 | 19:00 | -2.2
[42 empty] | 1976-01-20 | 20:00 | -2.2
[42 empty] | 1976-01-20 | 21:00 | -2.2
[42 empty] | 1976-01-20 | 22:00 | -2.2
[42 empty] | 1976-01-20 | 23:00 | -2.8
[42 empty] | 1976-01-20 | 24:00 | -2.8
[42 empty] | 1976-01-21 | 1:00 | -2.8
[42 empty] | 1976-01-21 | 2:00 | -2.8
[42 empty] | 1976-01-21 | 3:00 | -3.9
[42 empty] | 1976-01-21 | 4:00 | -3.3
[42 empty] | 1976-01-21 | 5:00 | -3.3
[42 empty] | 1976-01-21 | 6:00 | -2.8
[42 empty] | 1976-01-21 | 7:00 | -1.7
[42 empty] | 1976-01-21 | 8:00 | -1.7
[42 empty] | 1976-01-21 | 9:00 | -1.7
[42 empty] | 1976-01-21 | 10:00 | -0.6
[42 empty] | 1976-01-21 | 11:00 | 0.6
[42 empty] | 1976-01-21 | 12:00 | 1.1
[42 empty] | 1976-01-21 | 13:00 | 1.1
[42 empty] | 1976-01-21 | 14:00 | 1.1
[42 empty] | 1976-01-21 | 15:00 | 0.6
[42 empty] | 1976-01-21 | 16:00 | 0.6
[42 empty] | 1976-01-21 | 17:00 | 0.6
[42 empty] | 1976-01-21 | 18:00 | 0.6
[42 empty] | 1976-01-21 | 19:00 | 0.6
[42 empty] | 1976-01-21 | 20:00 | 0.6
[42 empty] | 1976-01-21 | 21:00 | 0
[42 empty] | 1976-01-21 | 22:00 | 0
[42 empty] | 1976-01-21 | 23:00 | -0.6
[42 empty] | 1976-01-21 | 24:00 | -0.6
[42 empty] | 1976-01-22 | 1:00 | -1.7
[42 empty] | 1976-01-22 | 2:00 | -2.2
[42 empty] | 1976-01-22 | 3:00 | -2.2
[42 empty] | 1976-01-22 | 4:00 | -2.8
[42 empty] | 1976-01-22 | 5:00 | -2.8
[42 empty] | 1976-01-22 | 6:00 | -3.3
[42 empty] | 1976-01-22 | 7:00 | -3.3
[42 empty] | 1976-01-22 | 8:00 | -3.9
[42 empty] | 1976-01-22 | 9:00 | -4.4
[42 empty] | 1976-01-22 | 10:00 | -4.4
[42 empty] | 1976-01-22 | 11:00 | -4.4
[42 empty] | 1976-01-22 | 12:00 | -5
[42 empty] | 1976-01-22 | 13:00 | -6.1
[42 empty] | 1976-01-22 | 14:00 | -5.6
[42 empty] | 1976-01-22 | 15:00 | -5.6
[42 empty] | 1976-01-22 | 16:00 | -6.1
[42 empty] | 1976-01-22 | 17:00 | -6.7
[42 empty] | 1976-01-22 | 18:00 | -7.8
[42 empty] | 1976-01-22 | 19:00 | -9.4
[42 empty] | 1976-01-22 | 20:00 | -10.6
[42 empty] | 1976-01-22 | 21:00 | -11.1
[42 empty] | 1976-01-22 | 22:00 | -12.2
[42 empty] | 1976-01-22 | 23:00 | -12.8
[42 empty] | 1976-01-22 | 24:00 | -13.3
[42 empty] | 1976-01-23 | 1:00 | -13.9
[42 empty] | 1976-01-23 | 2:00 | -14.4
[42 empty] | 1976-01-23 | 3:00 | -14.4
[42 empty] | 1976-01-23 | 4:00 | -15
[42 empty] | 1976-01-23 | 5:00 | -15
[42 empty] | 1976-01-23 | 6:00 | -15.6
[42 empty] | 1976-01-23 | 7:00 | -15.6
[42 empty] | 1976-01-23 | 8:00 | -15.6
[42 empty] | 1976-01-23 | 9:00 | -15.6
[42 empty] | 1976-01-23 | 10:00 | -15.6
[42 empty] | 1976-01-23 | 11:00 | -14.4
[42 empty] | 1976-01-23 | 12:00 | -13.3
[42 empty] | 1976-01-23 | 13:00 | -12.8
[42 empty] | 1976-01-23 | 14:00 | -12.2
[42 empty] | 1976-01-23 | 15:00 | -11.7
[42 empty] | 1976-01-23 | 16:00 | -11.1
[42 empty] | 1976-01-23 | 17:00 | -10.6
[42 empty] | 1976-01-23 | 18:00 | -10.6
[42 empty] | 1976-01-23 | 19:00 | -10.6
[42 empty] | 1976-01-23 | 20:00 | -10
[42 empty] | 1976-01-23 | 21:00 | -10
[42 empty] | 1976-01-23 | 22:00 | -9.4
[42 empty] | 1976-01-23 | 23:00 | -9.4
[42 empty] | 1976-01-23 | 24:00 | -9.4
[42 empty] | 1976-01-24 | 1:00 | -9.4
[42 empty] | 1976-01-24 | 2:00 | -8.9
[42 empty] | 1976-01-24 | 3:00 | -8.9
[42 empty] | 1976-01-24 | 4:00 | -9.4
[42 empty] | 1976-01-24 | 5:00 | -9.4
[42 empty] | 1976-01-24 | 6:00 | -9.4
[42 empty] | 1976-01-24 | 7:00 | -8.9
[42 empty] | 1976-01-24 | 8:00 | -8.9
[42 empty] | 1976-01-24 | 9:00 | -8.3
[42 empty] | 1976-01-24 | 10:00 | -7.8
[42 empty] | 1976-01-24 | 11:00 | -7.2
[42 empty] | 1976-01-24 | 12:00 | -7.2
[42 empty] | 1976-01-24 | 13:00 | -6.7
[42 empty] | 1976-01-24 | 14:00 | -6.7
[42 empty] | 1976-01-24 | 15:00 | -5
[42 empty] | 1976-01-24 | 16:00 | -5
[42 empty] | 1976-01-24 | 17:00 | -5
[42 empty] | 1976-01-24 | 18:00 | -5
[42 empty] | 1976-01-24 | 19:00 | -5
[42 empty] | 1976-01-24 | 20:00 | -5
[42 empty] | 1976-01-24 | 21:00 | -5
[42 empty] | 1976-01-24 | 22:00 | -5
[42 empty] | 1976-01-24 | 23:00 | -5
[42 empty] | 1976-01-24 | 24:00 | -5.6
[42 empty] | 1976-01-25 | 1:00 | -5
[42 empty] | 1976-01-25 | 2:00 | -5
[42 empty] | 1976-01-25 | 3:00 | -5
[42 empty] | 1976-01-25 | 4:00 | -5.6
[42 empty] | 1976-01-25 | 5:00 | -5
[42 empty] | 1976-01-25 | 6:00 | -5
[42 empty] | 1976-01-25 | 7:00 | -5.6
[42 empty] | 1976-01-25 | 8:00 | -5.6
[42 empty] | 1976-01-25 | 9:00 | -5.6
[42 empty] | 1976-01-25 | 10:00 | -5
[42 empty] | 1976-01-25 | 11:00 | -3.9
[42 empty] | 1976-01-25 | 12:00 | -2.2
[42 empty] | 1976-01-25 | 13:00 | -0.6
[42 empty] | 1976-01-25 | 14:00 | -0.6
[42 empty] | 1976-01-25 | 15:00 | -1.1
[42 empty] | 1976-01-25 | 16:00 | -1.1
[42 empty] | 1976-01-25 | 17:00 | -1.1
[42 empty] | 1976-01-25 | 18:00 | -1.1
[42 empty] | 1976-01-25 | 19:00 | -0.6
[42 empty] | 1976-01-25 | 20:00 | -0.6
[42 empty] | 1976-01-25 | 21:00 | 0
[42 empty] | 1976-01-25 | 22:00 | 0
[42 empty] | 1976-01-25 | 23:00 | 0
[42 empty] | 1976-01-25 | 24:00 | 0.6
[42 empty] | 1976-01-26 | 1:00 | 0.6
[42 empty] | 1976-01-26 | 2:00 | 0
[42 empty] | 1976-01-26 | 3:00 | 0.6
[42 empty] | 1976-01-26 | 4:00 | 0.6
[42 empty] | 1976-01-26 | 5:00 | 0.6
[42 empty] | 1976-01-26 | 6:00 | 0.6
[42 empty] | 1976-01-26 | 7:00 | 0.6
[42 empty] | 1976-01-26 | 8:00 | 1.1
[42 empty] | 1976-01-26 | 9:00 | 1.7
[42 empty] | 1976-01-26 | 10:00 | 1.7
[42 empty] | 1976-01-26 | 11:00 | 2.2
[42 empty] | 1976-01-26 | 12:00 | 3.9
[42 empty] | 1976-01-26 | 13:00 | 10
[42 empty] | 1976-01-26 | 14:00 | 11.1
[42 empty] | 1976-01-26 | 15:00 | 11.7
[42 empty] | 1976-01-26 | 16:00 | 11.1
[42 empty] | 1976-01-26 | 17:00 | 11.1
[42 empty] | 1976-01-26 | 18:00 | 10
[42 empty] | 1976-01-26 | 19:00 | 10
[42 empty] | 1976-01-26 | 20:00 | 10
[42 empty] | 1976-01-26 | 21:00 | 10
[42 empty] | 1976-01-26 | 22:00 | 10
[42 empty] | 1976-01-26 | 23:00 | 11.1
[42 empty] | 1976-01-26 | 24:00 | 10.6
[42 empty] | 1976-01-27 | 1:00 | 10.6
[42 empty] | 1976-01-27 | 2:00 | 10.6
[42 empty] | 1976-01-27 | 3:00 | 10
[42 empty] | 1976-01-27 | 4:00 | 9.4
[42 empty] | 1976-01-27 | 5:00 | 10.6
[42 empty] | 1976-01-27 | 6:00 | 10.6
[42 empty] | 1976-01-27 | 7:00 | 10
[42 empty] | 1976-01-27 | 8:00 | 9.4
[42 empty] | 1976-01-27 | 9:00 | 10.6
[42 empty] | 1976-01-27 | 10:00 | 10.6
[42 empty] | 1976-01-27 | 11:00 | 10.6
[42 empty] | 1976-01-27 | 12:00 | 10.6
[42 empty] | 1976-01-27 | 13:00 | 10.6
[42 empty] | 1976-01-27 | 14:00 | 10.6
[42 empty] | 1976-01-27 | 15:00 | 6.7
[42 empty] | 1976-01-27 | 16:00 | 6.1
[42 empty] | 1976-01-27 | 17:00 | 6.1
[42 empty] | 1976-01-27 | 18:00 | 5.6
[42 empty] | 1976-01-27 | 19:00 | 5
[42 empty] | 1976-01-27 | 20:00 | 4.4
[42 empty] | 1976-01-27 | 21:00 | 3.9
[42 empty] | 1976-01-27 | 22:00 | 3.9
[42 empty] | 1976-01-27 | 23:00 | 3.9
[42 empty] | 1976-01-27 | 24:00 | 3.9
[42 empty] | 1976-01-28 | 1:00 | 3.3
[42 empty] | 1976-01-28 | 2:00 | 3.3
[42 empty] | 1976-01-28 | 3:00 | 2.8
[42 empty] | 1976-01-28 | 4:00 | 2.8
[42 empty] | 1976-01-28 | 5:00 | 2.8
[42 empty] | 1976-01-28 | 6:00 | 2.8
[42 empty] | 1976-01-28 | 7:00 | 2.2
[42 empty] | 1976-01-28 | 8:00 | 1.7
[42 empty] | 1976-01-28 | 9:00 | 1.7
[42 empty] | 1976-01-28 | 10:00 | 1.7
[42 empty] | 1976-01-28 | 11:00 | 1.7
[42 empty] | 1976-01-28 | 12:00 | 2.2
[42 empty] | 1976-01-28 | 13:00 | 2.2
[42 empty] | 1976-01-28 | 14:00 | 1.7
[42 empty] | 1976-01-28 | 15:00 | 1.1
[42 empty] | 1976-01-28 | 16:00 | 1.1
[42 empty] | 1976-01-28 | 17:00 | 0.6
[42 empty] | 1976-01-28 | 18:00 | 0.6
[42 empty] | 1976-01-28 | 19:00 | 0
[42 empty] | 1976-01-28 | 20:00 | -0.6
[42 empty] | 1976-01-28 | 21:00 | -0.6
[42 empty] | 1976-01-28 | 22:00 | -0.6
[42 empty] | 1976-01-28 | 23:00 | -0.6
[42 empty] | 1976-01-28 | 24:00 | -0.6
[42 empty] | 1976-01-29 | 1:00 | -0.6
[42 empty] | 1976-01-29 | 2:00 | -0.6
[42 empty] | 1976-01-29 | 3:00 | -0.6
[42 empty] | 1976-01-29 | 4:00 | -0.6
[42 empty] | 1976-01-29 | 5:00 | -0.6
[42 empty] | 1976-01-29 | 6:00 | 0
[42 empty] | 1976-01-29 | 7:00 | 0.6
[42 empty] | 1976-01-29 | 8:00 | 1.1
[42 empty] | 1976-01-29 | 9:00 | 1.7
[42 empty] | 1976-01-29 | 10:00 | 2.2
[42 empty] | 1976-01-29 | 11:00 | 3.3
[42 empty] | 1976-01-29 | 12:00 | 4.4
[42 empty] | 1976-01-29 | 13:00 | 4.4
[42 empty] | 1976-01-29 | 14:00 | 5.6
[42 empty] | 1976-01-29 | 15:00 | 5.6
[42 empty] | 1976-01-29 | 16:00 | 6.1
[42 empty] | 1976-01-29 | 17:00 | 6.1
[42 empty] | 1976-01-29 | 18:00 | 5.6
[42 empty] | 1976-01-29 | 19:00 | 5.6
[42 empty] | 1976-01-29 | 20:00 | 5
[42 empty] | 1976-01-29 | 21:00 | 5
[42 empty] | 1976-01-29 | 22:00 | 4.4
[42 empty] | 1976-01-29 | 23:00 | 2.8
[42 empty] | 1976-01-29 | 24:00 | 2.2
[42 empty] | 1976-01-30 | 1:00 | 1.7
[42 empty] | 1976-01-30 | 2:00 | 0
[42 empty] | 1976-01-30 | 3:00 | -0.6
[42 empty] | 1976-01-30 | 4:00 | -1.1
[42 empty] | 1976-01-30 | 5:00 | -1.1
[42 empty] | 1976-01-30 | 6:00 | -1.7
[42 empty] | 1976-01-30 | 7:00 | -1.7
[42 empty] | 1976-01-30 | 8:00 | -2.2
[42 empty] | 1976-01-30 | 9:00 | -2.2
[42 empty] | 1976-01-30 | 10:00 | -1.7
[42 empty] | 1976-01-30 | 11:00 | -1.7
[42 empty] | 1976-01-30 | 12:00 | -1.1
[42 empty] | 1976-01-30 | 13:00 | -1.1
[42 empty] | 1976-01-30 | 14:00 | -0.6
[42 empty] | 1976-01-30 | 15:00 | -0.6
[42 empty] | 1976-01-30 | 16:00 | -0.6
[42 empty] | 1976-01-30 | 17:00 | -0.6
[42 empty] | 1976-01-30 | 18:00 | -0.6
[42 empty] | 1976-01-30 | 19:00 | -0.6
[42 empty] | 1976-01-30 | 20:00 | -0.6
[42 empty] | 1976-01-30 | 21:00 | -1.1
[42 empty] | 1976-01-30 | 22:00 | -1.7
[42 empty] | 1976-01-30 | 23:00 | -1.7
[42 empty] | 1976-01-30 | 24:00 | -2.2
[42 empty] | 1976-01-31 | 1:00 | -2.2
[42 empty] | 1976-01-31 | 2:00 | -2.8
[42 empty] | 1976-01-31 | 3:00 | -3.3
[42 empty] | 1976-01-31 | 4:00 | -3.9
[42 empty] | 1976-01-31 | 5:00 | -3.9
[42 empty] | 1976-01-31 | 6:00 | -4.4
[42 empty] | 1976-01-31 | 7:00 | -5
[42 empty] | 1976-01-31 | 8:00 | -5
[42 empty] | 1976-01-31 | 9:00 | -4.4
[42 empty] | 1976-01-31 | 10:00 | -3.9
[42 empty] | 1976-01-31 | 11:00 | -2.8
[42 empty] | 1976-01-31 | 12:00 | -2.8
[42 empty] | 1976-01-31 | 13:00 | -2.2
[42 empty] | 1976-01-31 | 14:00 | -1.1
[42 empty] | 1976-01-31 | 15:00 | -0.6
[42 empty] | 1976-01-31 | 16:00 | -0.6
[42 empty] | 1976-01-31 | 17:00 | 0
[42 empty] | 1976-01-31 | 18:00 | 0
[42 empty] | 1976-01-31 | 19:00 | 0
[42 empty] | 1976-01-31 | 20:00 | 0.6
[42 empty] | 1976-01-31 | 21:00 | 1.1
[42 empty] | 1976-01-31 | 22:00 | 2.5
[42 empty] | 1976-01-31 | 23:00 | 3.8
[42 empty] | 1976-01-31 | 24:00 | 5.2
[42 empty] | 1988-02-01 | 1:00 | 6.5
[42 empty] | 1988-02-01 | 2:00 | 7.9
[42 empty] | 1988-02-01 | 3:00 | 9.2
[42 empty] | 1988-02-01 | 4:00 | 10.6
[42 empty] | 1988-02-01 | 5:00 | 10.6
[42 empty] | 1988-02-01 | 6:00 | 11.7
[42 empty] | 1988-02-01 | 7:00 | 11.7
[42 empty] | 1988-02-01 | 8:00 | 11.7
[42 empty] | 1988-02-01 | 9:00 | 12.8
[42 empty] | 1988-02-01 | 10:00 | 12.2
[42 empty] | 1988-02-01 | 11:00 | 13.3
[42 empty] | 1988-02-01 | 12:00 | 13.9
[42 empty] | 1988-02-01 | 13:00 | 15
[42 empty] | 1988-02-01 | 14:00 | 15.6
[42 empty] | 1988-02-01 | 15:00 | 16.1
[42 empty] | 1988-02-01 | 16:00 | 15
[42 empty] | 1988-02-01 | 17:00 | 13.3
[42 empty] | 1988-02-01 | 18:00 | 11.7
[42 empty] | 1988-02-01 | 19:00 | 11.1
[42 empty] | 1988-02-01 | 20:00 | 10
[42 empty] | 1988-02-01 | 21:00 | 9.4
[42 empty] | 1988-02-01 | 22:00 | 10
[42 empty] | 1988-02-01 | 23:00 | 10
[42 empty] | 1988-02-01 | 24:00 | 10.6
[42 empty] | 1988-02-02 | 1:00 | 10
[42 empty] | 1988-02-02 | 2:00 | 9.4
[42 empty] | 1988-02-02 | 3:00 | 9.4
[42 empty] | 1988-02-02 | 4:00 | 10
[42 empty] | 1988-02-02 | 5:00 | 13.9
[42 empty] | 1988-02-02 | 6:00 | 14.4
[42 empty] | 1988-02-02 | 7:00 | 14.4
[42 empty] | 1988-02-02 | 8:00 | 14.4
[42 empty] | 1988-02-02 | 9:00 | 14.4
[42 empty] | 1988-02-02 | 10:00 | 14.4
[42 empty] | 1988-02-02 | 11:00 | 13.9
[42 empty] | 1988-02-02 | 12:00 | 15
[42 empty] | 1988-02-02 | 13:00 | 14.4
[42 empty] | 1988-02-02 | 14:00 | 14.4
[42 empty] | 1988-02-02 | 15:00 | 11.1
[42 empty] | 1988-02-02 | 16:00 | 7.8
[42 empty] | 1988-02-02 | 17:00 | 6.1
[42 empty] | 1988-02-02 | 18:00 | 5
[42 empty] | 1988-02-02 | 19:00 | 4.4
[42 empty] | 1988-02-02 | 20:00 | 3.9
[42 empty] | 1988-02-02 | 21:00 | 3.9
[42 empty] | 1988-02-02 | 22:00 | 2.8
[42 empty] | 1988-02-02 | 23:00 | 2.2
[42 empty] | 1988-02-02 | 24:00 | 2.2
[42 empty] | 1988-02-03 | 1:00 | 1.7
[42 empty] | 1988-02-03 | 2:00 | 1.1
[42 empty] | 1988-02-03 | 3:00 | 0.6
[42 empty] | 1988-02-03 | 4:00 | 0
[42 empty] | 1988-02-03 | 5:00 | -0.6
[42 empty] | 1988-02-03 | 6:00 | -1.1
[42 empty] | 1988-02-03 | 7:00 | -1.7
[42 empty] | 1988-02-03 | 8:00 | -1.7
[42 empty] | 1988-02-03 | 9:00 | -1.7
[42 empty] | 1988-02-03 | 10:00 | 0
[42 empty] | 1988-02-03 | 11:00 | 0.6
[42 empty] | 1988-02-03 | 12:00 | 1.1
[42 empty] | 1988-02-03 | 13:00 | 1.1
[42 empty] | 1988-02-03 | 14:00 | 1.1
[42 empty] | 1988-02-03 | 15:00 | 1.1
[42 empty] | 1988-02-03 | 16:00 | 0
[42 empty] | 1988-02-03 | 17:00 | 0
[42 empty] | 1988-02-03 | 18:00 | 0
[42 empty] | 1988-02-03 | 19:00 | 1.1
[42 empty] | 1988-02-03 | 20:00 | 1.1
[42 empty] | 1988-02-03 | 21:00 | 1.1
[42 empty] | 1988-02-03 | 22:00 | 0.6
[42 empty] | 1988-02-03 | 23:00 | 0.6
[42 empty] | 1988-02-03 | 24:00 | 1.1
[42 empty] | 1988-02-04 | 1:00 | 1.1
[42 empty] | 1988-02-04 | 2:00 | 1.7
[42 empty] | 1988-02-04 | 3:00 | 1.7
[42 empty] | 1988-02-04 | 4:00 | 2.2
[42 empty] | 1988-02-04 | 5:00 | 2.8
[42 empty] | 1988-02-04 | 6:00 | 2.8
[42 empty] | 1988-02-04 | 7:00 | 1.7
[42 empty] | 1988-02-04 | 8:00 | 1.7
[42 empty] | 1988-02-04 | 9:00 | 1.7
[42 empty] | 1988-02-04 | 10:00 | 1.7
[42 empty] | 1988-02-04 | 11:00 | 2.2
[42 empty] | 1988-02-04 | 12:00 | 1.7
[42 empty] | 1988-02-04 | 13:00 | 2.2
[42 empty] | 1988-02-04 | 14:00 | 2.2
[42 empty] | 1988-02-04 | 15:00 | 2.2
[42 empty] | 1988-02-04 | 16:00 | 2.8
[42 empty] | 1988-02-04 | 17:00 | 2.8
[42 empty] | 1988-02-04 | 18:00 | 2.2
[42 empty] | 1988-02-04 | 19:00 | 0.6
[42 empty] | 1988-02-04 | 20:00 | -1.7
[42 empty] | 1988-02-04 | 21:00 | -2.2
[42 empty] | 1988-02-04 | 22:00 | -3.3
[42 empty] | 1988-02-04 | 23:00 | -4.4
[42 empty] | 1988-02-04 | 24:00 | -5
[42 empty] | 1988-02-05 | 1:00 | -5
[42 empty] | 1988-02-05 | 2:00 | -5.6
[42 empty] | 1988-02-05 | 3:00 | -5.6
[42 empty] | 1988-02-05 | 4:00 | -6.1
[42 empty] | 1988-02-05 | 5:00 | -6.1
[42 empty] | 1988-02-05 | 6:00 | -6.7
[42 empty] | 1988-02-05 | 7:00 | -6.7
[42 empty] | 1988-02-05 | 8:00 | -6.7
[42 empty] | 1988-02-05 | 9:00 | -5.6
[42 empty] | 1988-02-05 | 10:00 | -5
[42 empty] | 1988-02-05 | 11:00 | -4.4
[42 empty] | 1988-02-05 | 12:00 | -3.3
[42 empty] | 1988-02-05 | 13:00 | -2.8
[42 empty] | 1988-02-05 | 14:00 | -1.7
[42 empty] | 1988-02-05 | 15:00 | -2.2
[42 empty] | 1988-02-05 | 16:00 | -2.2
[42 empty] | 1988-02-05 | 17:00 | -2.2
[42 empty] | 1988-02-05 | 18:00 | -2.8
[42 empty] | 1988-02-05 | 19:00 | -2.8
[42 empty] | 1988-02-05 | 20:00 | -3.3
[42 empty] | 1988-02-05 | 21:00 | -3.3
[42 empty] | 1988-02-05 | 22:00 | -3.9
[42 empty] | 1988-02-05 | 23:00 | -4.4
[42 empty] | 1988-02-05 | 24:00 | -5
[42 empty] | 1988-02-06 | 1:00 | -5.6
[42 empty] | 1988-02-06 | 2:00 | -6.7
[42 empty] | 1988-02-06 | 3:00 | -7.2
[42 empty] | 1988-02-06 | 4:00 | -7.8
[42 empty] | 1988-02-06 | 5:00 | -7.8
[42 empty] | 1988-02-06 | 6:00 | -8.3
[42 empty] | 1988-02-06 | 7:00 | -8.9
[42 empty] | 1988-02-06 | 8:00 | -9.4
[42 empty] | 1988-02-06 | 9:00 | -8.9
[42 empty] | 1988-02-06 | 10:00 | -8.3
[42 empty] | 1988-02-06 | 11:00 | -7.2
[42 empty] | 1988-02-06 | 12:00 | -6.7
[42 empty] | 1988-02-06 | 13:00 | -6.1
[42 empty] | 1988-02-06 | 14:00 | -5.6
[42 empty] | 1988-02-06 | 15:00 | -5.6
[42 empty] | 1988-02-06 | 16:00 | -5
[42 empty] | 1988-02-06 | 17:00 | -6.1
[42 empty] | 1988-02-06 | 18:00 | -6.7
[42 empty] | 1988-02-06 | 19:00 | -6.7
[42 empty] | 1988-02-06 | 20:00 | -7.2
[42 empty] | 1988-02-06 | 21:00 | -7.2
[42 empty] | 1988-02-06 | 22:00 | -7.8
[42 empty] | 1988-02-06 | 23:00 | -8.3
[42 empty] | 1988-02-06 | 24:00 | -9.4
[42 empty] | 1988-02-07 | 1:00 | -9.4
[42 empty] | 1988-02-07 | 2:00 | -10.6
[42 empty] | 1988-02-07 | 3:00 | -10.6
[42 empty] | 1988-02-07 | 4:00 | -11.1
[42 empty] | 1988-02-07 | 5:00 | -11.1
[42 empty] | 1988-02-07 | 6:00 | -11.7
[42 empty] | 1988-02-07 | 7:00 | -11.7
[42 empty] | 1988-02-07 | 8:00 | -11.1
[42 empty] | 1988-02-07 | 9:00 | -10.6
[42 empty] | 1988-02-07 | 10:00 | -9.4
[42 empty] | 1988-02-07 | 11:00 | -7.8
[42 empty] | 1988-02-07 | 12:00 | -6.7
[42 empty] | 1988-02-07 | 13:00 | -6.1
[42 empty] | 1988-02-07 | 14:00 | -4.4
[42 empty] | 1988-02-07 | 15:00 | -4.4
[42 empty] | 1988-02-07 | 16:00 | -4.4
[42 empty] | 1988-02-07 | 17:00 | -3.9
[42 empty] | 1988-02-07 | 18:00 | -4.4
[42 empty] | 1988-02-07 | 19:00 | -3.9
[42 empty] | 1988-02-07 | 20:00 | -3.9
[42 empty] | 1988-02-07 | 21:00 | -4.4
[42 empty] | 1988-02-07 | 22:00 | -4.4
[42 empty] | 1988-02-07 | 23:00 | -3.9
[42 empty] | 1988-02-07 | 24:00 | -3.9
[42 empty] | 1988-02-08 | 1:00 | -3.3
[42 empty] | 1988-02-08 | 2:00 | -3.3
[42 empty] | 1988-02-08 | 3:00 | -3.3
[42 empty] | 1988-02-08 | 4:00 | -3.3
[42 empty] | 1988-02-08 | 5:00 | -2.8
[42 empty] | 1988-02-08 | 6:00 | -2.8
[42 empty] | 1988-02-08 | 7:00 | -2.8
[42 empty] | 1988-02-08 | 8:00 | -2.2
[42 empty] | 1988-02-08 | 9:00 | -0.6
[42 empty] | 1988-02-08 | 10:00 | 0.6
[42 empty] | 1988-02-08 | 11:00 | 1.1
[42 empty] | 1988-02-08 | 12:00 | 2.2
[42 empty] | 1988-02-08 | 13:00 | 2.8
[42 empty] | 1988-02-08 | 14:00 | 2.8
[42 empty] | 1988-02-08 | 15:00 | 2.8
[42 empty] | 1988-02-08 | 16:00 | 1.7
[42 empty] | 1988-02-08 | 17:00 | 1.1
[42 empty] | 1988-02-08 | 18:00 | 0.6
[42 empty] | 1988-02-08 | 19:00 | 0
[42 empty] | 1988-02-08 | 20:00 | -0.6
[42 empty] | 1988-02-08 | 21:00 | -0.6
[42 empty] | 1988-02-08 | 22:00 | -1.1
[42 empty] | 1988-02-08 | 23:00 | -1.7
[42 empty] | 1988-02-08 | 24:00 | -1.7
[42 empty] | 1988-02-09 | 1:00 | -1.7
[42 empty] | 1988-02-09 | 2:00 | -2.2
[42 empty] | 1988-02-09 | 3:00 | -3.3
[42 empty] | 1988-02-09 | 4:00 | -3.9
[42 empty] | 1988-02-09 | 5:00 | -3.9
[42 empty] | 1988-02-09 | 6:00 | -4.4
[42 empty] | 1988-02-09 | 7:00 | -4.4
[42 empty] | 1988-02-09 | 8:00 | -3.9
[42 empty] | 1988-02-09 | 9:00 | -2.2
[42 empty] | 1988-02-09 | 10:00 | -1.1
[42 empty] | 1988-02-09 | 11:00 | 0
[42 empty] | 1988-02-09 | 12:00 | 1.7
[42 empty] | 1988-02-09 | 13:00 | 2.8
[42 empty] | 1988-02-09 | 14:00 | 2.8
[42 empty] | 1988-02-09 | 15:00 | 2.8
[42 empty] | 1988-02-09 | 16:00 | 2.8
[42 empty] | 1988-02-09 | 17:00 | 2.8
[42 empty] | 1988-02-09 | 18:00 | 2.2
[42 empty] | 1988-02-09 | 19:00 | 2.2
[42 empty] | 1988-02-09 | 20:00 | 2.2
[42 empty] | 1988-02-09 | 21:00 | 2.2
[42 empty] | 1988-02-09 | 22:00 | 2.2
[42 empty] | 1988-02-09 | 23:00 | 1.7
[42 empty] | 1988-02-09 | 24:00 | 1.7
[42 empty] | 1988-02-10 | 1:00 | 1.7
[42 empty] | 1988-02-10 | 2:00 | 1.7
[42 empty] | 1988-02-10 | 3:00 | 2.2
[42 empty] | 1988-02-10 | 4:00 | 1.7
[42 empty] | 1988-02-10 | 5:00 | 1.1
[42 empty] | 1988-02-10 | 6:00 | 1.1
[42 empty] | 1988-02-10 | 7:00 | 1.1
[42 empty] | 1988-02-10 | 8:00 | 2.2
[42 empty] | 1988-02-10 | 9:00 | 2.8
[42 empty] | 1988-02-10 | 10:00 | 2.8
[42 empty] | 1988-02-10 | 11:00 | 3.9
[42 empty] | 1988-02-10 | 12:00 | 3.9
[42 empty] | 1988-02-10 | 13:00 | 4.4
[42 empty] | 1988-02-10 | 14:00 | 4.4
[42 empty] | 1988-02-10 | 15:00 | 4.4
[42 empty] | 1988-02-10 | 16:00 | 3.9
[42 empty] | 1988-02-10 | 17:00 | 2.8
[42 empty] | 1988-02-10 | 18:00 | 1.7
[42 empty] | 1988-02-10 | 19:00 | 1.7
[42 empty] | 1988-02-10 | 20:00 | 1.1
[42 empty] | 1988-02-10 | 21:00 | 1.1
[42 empty] | 1988-02-10 | 22:00 | 0.6
[42 empty] | 1988-02-10 | 23:00 | 0
[42 empty] | 1988-02-10 | 24:00 | -0.6
[42 empty] | 1988-02-11 | 1:00 | -1.7
[42 empty] | 1988-02-11 | 2:00 | -2.2
[42 empty] | 1988-02-11 | 3:00 | -2.8
[42 empty] | 1988-02-11 | 4:00 | -2.8
[42 empty] | 1988-02-11 | 5:00 | -2.8
[42 empty] | 1988-02-11 | 6:00 | -3.3
[42 empty] | 1988-02-11 | 7:00 | -3.3
[42 empty] | 1988-02-11 | 8:00 | -2.8
[42 empty] | 1988-02-11 | 9:00 | -1.7
[42 empty] | 1988-02-11 | 10:00 | 0
[42 empty] | 1988-02-11 | 11:00 | 0.6
[42 empty] | 1988-02-11 | 12:00 | 1.7
[42 empty] | 1988-02-11 | 13:00 | 1.1
[42 empty] | 1988-02-11 | 14:00 | 0.6
[42 empty] | 1988-02-11 | 15:00 | 1.7
[42 empty] | 1988-02-11 | 16:00 | 2.8
[42 empty] | 1988-02-11 | 17:00 | 1.7
[42 empty] | 1988-02-11 | 18:00 | 1.7
[42 empty] | 1988-02-11 | 19:00 | 1.7
[42 empty] | 1988-02-11 | 20:00 | 1.7
[42 empty] | 1988-02-11 | 21:00 | 2.8
[42 empty] | 1988-02-11 | 22:00 | 2.8
[42 empty] | 1988-02-11 | 23:00 | 2.2
[42 empty] | 1988-02-11 | 24:00 | 1.7
[42 empty] | 1988-02-12 | 1:00 | 1.1
[42 empty] | 1988-02-12 | 2:00 | 0.6
[42 empty] | 1988-02-12 | 3:00 | 0.6
[42 empty] | 1988-02-12 | 4:00 | 0.6
[42 empty] | 1988-02-12 | 5:00 | 1.1
[42 empty] | 1988-02-12 | 6:00 | 1.1
[42 empty] | 1988-02-12 | 7:00 | 1.7
[42 empty] | 1988-02-12 | 8:00 | 1.7
[42 empty] | 1988-02-12 | 9:00 | 1.7
[42 empty] | 1988-02-12 | 10:00 | 1.7
[42 empty] | 1988-02-12 | 11:00 | 2.2
[42 empty] | 1988-02-12 | 12:00 | 2.8
[42 empty] | 1988-02-12 | 13:00 | 2.8
[42 empty] | 1988-02-12 | 14:00 | 2.8
[42 empty] | 1988-02-12 | 15:00 | 3.9
[42 empty] | 1988-02-12 | 16:00 | 3.3
[42 empty] | 1988-02-12 | 17:00 | 2.8
[42 empty] | 1988-02-12 | 18:00 | 2.8
[42 empty] | 1988-02-12 | 19:00 | 2.2
[42 empty] | 1988-02-12 | 20:00 | 2.2
[42 empty] | 1988-02-12 | 21:00 | 2.2
[42 empty] | 1988-02-12 | 22:00 | 1.7
[42 empty] | 1988-02-12 | 23:00 | -0.6
[42 empty] | 1988-02-12 | 24:00 | -1.1
[42 empty] | 1988-02-13 | 1:00 | -1.7
[42 empty] | 1988-02-13 | 2:00 | -3.9
[42 empty] | 1988-02-13 | 3:00 | -3.9
[42 empty] | 1988-02-13 | 4:00 | -5
[42 empty] | 1988-02-13 | 5:00 | -5.6
[42 empty] | 1988-02-13 | 6:00 | -6.1
[42 empty] | 1988-02-13 | 7:00 | -6.1
[42 empty] | 1988-02-13 | 8:00 | -6.7
[42 empty] | 1988-02-13 | 9:00 | -5.6
[42 empty] | 1988-02-13 | 10:00 | -5
[42 empty] | 1988-02-13 | 11:00 | -4.4
[42 empty] | 1988-02-13 | 12:00 | -3.9
[42 empty] | 1988-02-13 | 13:00 | -3.9
[42 empty] | 1988-02-13 | 14:00 | -3.9
[42 empty] | 1988-02-13 | 15:00 | -3.3
[42 empty] | 1988-02-13 | 16:00 | -3.3
[42 empty] | 1988-02-13 | 17:00 | -2.8
[42 empty] | 1988-02-13 | 18:00 | -3.3
[42 empty] | 1988-02-13 | 19:00 | -3.3
[42 empty] | 1988-02-13 | 20:00 | -3.3
[42 empty] | 1988-02-13 | 21:00 | -3.9
[42 empty] | 1988-02-13 | 22:00 | -3.9
[42 empty] | 1988-02-13 | 23:00 | -3.9
[42 empty] | 1988-02-13 | 24:00 | -3.9
[42 empty] | 1988-02-14 | 1:00 | -3.9
[42 empty] | 1988-02-14 | 2:00 | -3.9
[42 empty] | 1988-02-14 | 3:00 | -3.9
[42 empty] | 1988-02-14 | 4:00 | -3.3
[42 empty] | 1988-02-14 | 5:00 | -3.3
[42 empty] | 1988-02-14 | 6:00 | -3.3
[42 empty] | 1988-02-14 | 7:00 | -3.3
[42 empty] | 1988-02-14 | 8:00 | -2.8
[42 empty] | 1988-02-14 | 9:00 | -2.2
[42 empty] | 1988-02-14 | 10:00 | -1.1
[42 empty] | 1988-02-14 | 11:00 | -0.6
[42 empty] | 1988-02-14 | 12:00 | 0
[42 empty] | 1988-02-14 | 13:00 | 1.1
[42 empty] | 1988-02-14 | 14:00 | 2.2
[42 empty] | 1988-02-14 | 15:00 | 2.2
[42 empty] | 1988-02-14 | 16:00 | 2.8
[42 empty] | 1988-02-14 | 17:00 | 1.7
[42 empty] | 1988-02-14 | 18:00 | 0.6
[42 empty] | 1988-02-14 | 19:00 | 0
[42 empty] | 1988-02-14 | 20:00 | 0
[42 empty] | 1988-02-14 | 21:00 | -0.6
[42 empty] | 1988-02-14 | 22:00 | 0
[42 empty] | 1988-02-14 | 23:00 | -0.6
[42 empty] | 1988-02-14 | 24:00 | -0.6
[42 empty] | 1988-02-15 | 1:00 | 0
[42 empty] | 1988-02-15 | 2:00 | 0
[42 empty] | 1988-02-15 | 3:00 | 0.6
[42 empty] | 1988-02-15 | 4:00 | 1.1
[42 empty] | 1988-02-15 | 5:00 | 0.6
[42 empty] | 1988-02-15 | 6:00 | 0.6
[42 empty] | 1988-02-15 | 7:00 | 1.1
[42 empty] | 1988-02-15 | 8:00 | 2.8
[42 empty] | 1988-02-15 | 9:00 | 5
[42 empty] | 1988-02-15 | 10:00 | 6.7
[42 empty] | 1988-02-15 | 11:00 | 7.8
[42 empty] | 1988-02-15 | 12:00 | 8.9
[42 empty] | 1988-02-15 | 13:00 | 8.9
[42 empty] | 1988-02-15 | 14:00 | 10
[42 empty] | 1988-02-15 | 15:00 | 9.4
[42 empty] | 1988-02-15 | 16:00 | 9.4
[42 empty] | 1988-02-15 | 17:00 | 9.4
[42 empty] | 1988-02-15 | 18:00 | 8.3
[42 empty] | 1988-02-15 | 19:00 | 8.3
[42 empty] | 1988-02-15 | 20:00 | 8.3
[42 empty] | 1988-02-15 | 21:00 | 8.3
[42 empty] | 1988-02-15 | 22:00 | 8.3
[42 empty] | 1988-02-15 | 23:00 | 7.2
[42 empty] | 1988-02-15 | 24:00 | 6.7
[42 empty] | 1988-02-16 | 1:00 | 6.7
[42 empty] | 1988-02-16 | 2:00 | 6.1
[42 empty] | 1988-02-16 | 3:00 | 5.6
[42 empty] | 1988-02-16 | 4:00 | 5
[42 empty] | 1988-02-16 | 5:00 | 5.6
[42 empty] | 1988-02-16 | 6:00 | 6.1
[42 empty] | 1988-02-16 | 7:00 | 5.6
[42 empty] | 1988-02-16 | 8:00 | 4.4
[42 empty] | 1988-02-16 | 9:00 | 3.9
[42 empty] | 1988-02-16 | 10:00 | 3.9
[42 empty] | 1988-02-16 | 11:00 | 5
[42 empty] | 1988-02-16 | 12:00 | 5.6
[42 empty] | 1988-02-16 | 13:00 | 6.1
[42 empty] | 1988-02-16 | 14:00 | 5
[42 empty] | 1988-02-16 | 15:00 | 4.4
[42 empty] | 1988-02-16 | 16:00 | 4.4
[42 empty] | 1988-02-16 | 17:00 | 3.3
[42 empty] | 1988-02-16 | 18:00 | 2.2
[42 empty] | 1988-02-16 | 19:00 | 1.7
[42 empty] | 1988-02-16 | 20:00 | 1.1
[42 empty] | 1988-02-16 | 21:00 | 1.1
[42 empty] | 1988-02-16 | 22:00 | 0.6
[42 empty] | 1988-02-16 | 23:00 | 0.6
[42 empty] | 1988-02-16 | 24:00 | 0
[42 empty] | 1988-02-17 | 1:00 | 0
[42 empty] | 1988-02-17 | 2:00 | 0
[42 empty] | 1988-02-17 | 3:00 | 0
[42 empty] | 1988-02-17 | 4:00 | 0
[42 empty] | 1988-02-17 | 5:00 | -0.6
[42 empty] | 1988-02-17 | 6:00 | -0.6
[42 empty] | 1988-02-17 | 7:00 | -0.6
[42 empty] | 1988-02-17 | 8:00 | 1.7
[42 empty] | 1988-02-17 | 9:00 | 3.3
[42 empty] | 1988-02-17 | 10:00 | 4.4
[42 empty] | 1988-02-17 | 11:00 | 5
[42 empty] | 1988-02-17 | 12:00 | 6.7
[42 empty] | 1988-02-17 | 13:00 | 7.8
[42 empty] | 1988-02-17 | 14:00 | 8.9
[42 empty] | 1988-02-17 | 15:00 | 8.9
[42 empty] | 1988-02-17 | 16:00 | 9.4
[42 empty] | 1988-02-17 | 17:00 | 6.7
[42 empty] | 1988-02-17 | 18:00 | 5.6
[42 empty] | 1988-02-17 | 19:00 | 5
[42 empty] | 1988-02-17 | 20:00 | 5.6
[42 empty] | 1988-02-17 | 21:00 | 5
[42 empty] | 1988-02-17 | 22:00 | 5
[42 empty] | 1988-02-17 | 23:00 | 5
[42 empty] | 1988-02-17 | 24:00 | 3.9
[42 empty] | 1988-02-18 | 1:00 | 4.4
[42 empty] | 1988-02-18 | 2:00 | 3.9
[42 empty] | 1988-02-18 | 3:00 | 3.9
[42 empty] | 1988-02-18 | 4:00 | 2.8
[42 empty] | 1988-02-18 | 5:00 | 3.9
[42 empty] | 1988-02-18 | 6:00 | 3.9
[42 empty] | 1988-02-18 | 7:00 | 4.4
[42 empty] | 1988-02-18 | 8:00 | 5
[42 empty] | 1988-02-18 | 9:00 | 5.6
[42 empty] | 1988-02-18 | 10:00 | 6.1
[42 empty] | 1988-02-18 | 11:00 | 7.2
[42 empty] | 1988-02-18 | 12:00 | 8.3
[42 empty] | 1988-02-18 | 13:00 | 8.9
[42 empty] | 1988-02-18 | 14:00 | 9.4
[42 empty] | 1988-02-18 | 15:00 | 9.4
[42 empty] | 1988-02-18 | 16:00 | 8.9
[42 empty] | 1988-02-18 | 17:00 | 8.9
[42 empty] | 1988-02-18 | 18:00 | 7.2
[42 empty] | 1988-02-18 | 19:00 | 6.7
[42 empty] | 1988-02-18 | 20:00 | 5.6
[42 empty] | 1988-02-18 | 21:00 | 5
[42 empty] | 1988-02-18 | 22:00 | 4.4
[42 empty] | 1988-02-18 | 23:00 | 3.9
[42 empty] | 1988-02-18 | 24:00 | 1.7
[42 empty] | 1988-02-19 | 1:00 | 1.1
[42 empty] | 1988-02-19 | 2:00 | 0.6
[42 empty] | 1988-02-19 | 3:00 | 0
[42 empty] | 1988-02-19 | 4:00 | 0
[42 empty] | 1988-02-19 | 5:00 | 0
[42 empty] | 1988-02-19 | 6:00 | 0
[42 empty] | 1988-02-19 | 7:00 | 0
[42 empty] | 1988-02-19 | 8:00 | 0.6
[42 empty] | 1988-02-19 | 9:00 | 1.7
[42 empty] | 1988-02-19 | 10:00 | 1.7
[42 empty] | 1988-02-19 | 11:00 | 2.8
[42 empty] | 1988-02-19 | 12:00 | 2.8
[42 empty] | 1988-02-19 | 13:00 | 3.3
[42 empty] | 1988-02-19 | 14:00 | 3.9
[42 empty] | 1988-02-19 | 15:00 | 6.7
[42 empty] | 1988-02-19 | 16:00 | 6.1
[42 empty] | 1988-02-19 | 17:00 | 5
[42 empty] | 1988-02-19 | 18:00 | 5
[42 empty] | 1988-02-19 | 19:00 | 5
[42 empty] | 1988-02-19 | 20:00 | 5.6
[42 empty] | 1988-02-19 | 21:00 | 5.6
[42 empty] | 1988-02-19 | 22:00 | 5
[42 empty] | 1988-02-19 | 23:00 | 6.1
[42 empty] | 1988-02-19 | 24:00 | 6.7
[42 empty] | 1988-02-20 | 1:00 | 8.9
[42 empty] | 1988-02-20 | 2:00 | 8.9
[42 empty] | 1988-02-20 | 3:00 | 8.3
[42 empty] | 1988-02-20 | 4:00 | 8.9
[42 empty] | 1988-02-20 | 5:00 | 8.3
[42 empty] | 1988-02-20 | 6:00 | 7.8
[42 empty] | 1988-02-20 | 7:00 | 7.8
[42 empty] | 1988-02-20 | 8:00 | 7.2
[42 empty] | 1988-02-20 | 9:00 | 7.2
[42 empty] | 1988-02-20 | 10:00 | 7.8
[42 empty] | 1988-02-20 | 11:00 | 8.9
[42 empty] | 1988-02-20 | 12:00 | 9.4
[42 empty] | 1988-02-20 | 13:00 | 9.4
[42 empty] | 1988-02-20 | 14:00 | 9.4
[42 empty] | 1988-02-20 | 15:00 | 9.4
[42 empty] | 1988-02-20 | 16:00 | 9.4
[42 empty] | 1988-02-20 | 17:00 | 9.4
[42 empty] | 1988-02-20 | 18:00 | 8.9
[42 empty] | 1988-02-20 | 19:00 | 8.3
[42 empty] | 1988-02-20 | 20:00 | 8.3
[42 empty] | 1988-02-20 | 21:00 | 8.3
[42 empty] | 1988-02-20 | 22:00 | 8.3
[42 empty] | 1988-02-20 | 23:00 | 7.8
[42 empty] | 1988-02-20 | 24:00 | 6.7
[42 empty] | 1988-02-21 | 1:00 | 5.6
[42 empty] | 1988-02-21 | 2:00 | 5.6
[42 empty] | 1988-02-21 | 3:00 | 5
[42 empty] | 1988-02-21 | 4:00 | 3.9
[42 empty] | 1988-02-21 | 5:00 | 2.2
[42 empty] | 1988-02-21 | 6:00 | 1.7
[42 empty] | 1988-02-21 | 7:00 | 0
[42 empty] | 1988-02-21 | 8:00 | -1.1
[42 empty] | 1988-02-21 | 9:00 | -0.6
[42 empty] | 1988-02-21 | 10:00 | -1.1
[42 empty] | 1988-02-21 | 11:00 | -2.2
[42 empty] | 1988-02-21 | 12:00 | -3.3
[42 empty] | 1988-02-21 | 13:00 | -3.3
[42 empty] | 1988-02-21 | 14:00 | -2.8
[42 empty] | 1988-02-21 | 15:00 | -2.2
[42 empty] | 1988-02-21 | 16:00 | -2.8
[42 empty] | 1988-02-21 | 17:00 | -3.3
[42 empty] | 1988-02-21 | 18:00 | -3.3
[42 empty] | 1988-02-21 | 19:00 | -3.9
[42 empty] | 1988-02-21 | 20:00 | -4.4
[42 empty] | 1988-02-21 | 21:00 | -4.4
[42 empty] | 1988-02-21 | 22:00 | -5
[42 empty] | 1988-02-21 | 23:00 | -5
[42 empty] | 1988-02-21 | 24:00 | -4.4
[42 empty] | 1988-02-22 | 1:00 | -5
[42 empty] | 1988-02-22 | 2:00 | -5
[42 empty] | 1988-02-22 | 3:00 | -5
[42 empty] | 1988-02-22 | 4:00 | -5
[42 empty] | 1988-02-22 | 5:00 | -4.4
[42 empty] | 1988-02-22 | 6:00 | -4.4
[42 empty] | 1988-02-22 | 7:00 | -3.9
[42 empty] | 1988-02-22 | 8:00 | -3.3
[42 empty] | 1988-02-22 | 9:00 | -1.7
[42 empty] | 1988-02-22 | 10:00 | 0.6
[42 empty] | 1988-02-22 | 11:00 | 2.2
[42 empty] | 1988-02-22 | 12:00 | 3.9
[42 empty] | 1988-02-22 | 13:00 | 5
[42 empty] | 1988-02-22 | 14:00 | 6.7
[42 empty] | 1988-02-22 | 15:00 | 7.2
[42 empty] | 1988-02-22 | 16:00 | 6.1
[42 empty] | 1988-02-22 | 17:00 | 5.6
[42 empty] | 1988-02-22 | 18:00 | 5
[42 empty] | 1988-02-22 | 19:00 | 5
[42 empty] | 1988-02-22 | 20:00 | 4.4
[42 empty] | 1988-02-22 | 21:00 | 5
[42 empty] | 1988-02-22 | 22:00 | 5.6
[42 empty] | 1988-02-22 | 23:00 | 5
[42 empty] | 1988-02-22 | 24:00 | 5
[42 empty] | 1988-02-23 | 1:00 | 5
[42 empty] | 1988-02-23 | 2:00 | 6.1
[42 empty] | 1988-02-23 | 3:00 | 6.7
[42 empty] | 1988-02-23 | 4:00 | 6.7
[42 empty] | 1988-02-23 | 5:00 | 6.7
[42 empty] | 1988-02-23 | 6:00 | 6.1
[42 empty] | 1988-02-23 | 7:00 | 7.2
[42 empty] | 1988-02-23 | 8:00 | 8.9
[42 empty] | 1988-02-23 | 9:00 | 10
[42 empty] | 1988-02-23 | 10:00 | 11.7
[42 empty] | 1988-02-23 | 11:00 | 13.3
[42 empty] | 1988-02-23 | 12:00 | 14.4
[42 empty] | 1988-02-23 | 13:00 | 15.6
[42 empty] | 1988-02-23 | 14:00 | 16.1
[42 empty] | 1988-02-23 | 15:00 | 11.7
[42 empty] | 1988-02-23 | 16:00 | 8.9
[42 empty] | 1988-02-23 | 17:00 | 7.2
[42 empty] | 1988-02-23 | 18:00 | 6.7
[42 empty] | 1988-02-23 | 19:00 | 6.1
[42 empty] | 1988-02-23 | 20:00 | 6.1
[42 empty] | 1988-02-23 | 21:00 | 5.6
[42 empty] | 1988-02-23 | 22:00 | 5.6
[42 empty] | 1988-02-23 | 23:00 | 5.6
[42 empty] | 1988-02-23 | 24:00 | 5.6
[42 empty] | 1988-02-24 | 1:00 | 5
[42 empty] | 1988-02-24 | 2:00 | 5
[42 empty] | 1988-02-24 | 3:00 | 5
[42 empty] | 1988-02-24 | 4:00 | 4.4
[42 empty] | 1988-02-24 | 5:00 | 3.9
[42 empty] | 1988-02-24 | 6:00 | 1.7
[42 empty] | 1988-02-24 | 7:00 | 1.1
[42 empty] | 1988-02-24 | 8:00 | 1.1
[42 empty] | 1988-02-24 | 9:00 | 2.2
[42 empty] | 1988-02-24 | 10:00 | 2.2
[42 empty] | 1988-02-24 | 11:00 | 2.8
[42 empty] | 1988-02-24 | 12:00 | 3.9
[42 empty] | 1988-02-24 | 13:00 | 3.3
[42 empty] | 1988-02-24 | 14:00 | 2.8
[42 empty] | 1988-02-24 | 15:00 | 3.3
[42 empty] | 1988-02-24 | 16:00 | 2.8
[42 empty] | 1988-02-24 | 17:00 | 2.2
[42 empty] | 1988-02-24 | 18:00 | 1.7
[42 empty] | 1988-02-24 | 19:00 | 1.1
[42 empty] | 1988-02-24 | 20:00 | 0.6
[42 empty] | 1988-02-24 | 21:00 | 0.6
[42 empty] | 1988-02-24 | 22:00 | 0
[42 empty] | 1988-02-24 | 23:00 | 0
[42 empty] | 1988-02-24 | 24:00 | 0
[42 empty] | 1988-02-25 | 1:00 | 0
[42 empty] | 1988-02-25 | 2:00 | 0
[42 empty] | 1988-02-25 | 3:00 | -0.6
[42 empty] | 1988-02-25 | 4:00 | -1.1
[42 empty] | 1988-02-25 | 5:00 | -1.7
[42 empty] | 1988-02-25 | 6:00 | -2.2
[42 empty] | 1988-02-25 | 7:00 | -2.2
[42 empty] | 1988-02-25 | 8:00 | -1.7
[42 empty] | 1988-02-25 | 9:00 | -1.1
[42 empty] | 1988-02-25 | 10:00 | 0.6
[42 empty] | 1988-02-25 | 11:00 | 0.6
[42 empty] | 1988-02-25 | 12:00 | 0.6
[42 empty] | 1988-02-25 | 13:00 | 1.1
[42 empty] | 1988-02-25 | 14:00 | 1.7
[42 empty] | 1988-02-25 | 15:00 | 2.2
[42 empty] | 1988-02-25 | 16:00 | 0.6
[42 empty] | 1988-02-25 | 17:00 | 0.6
[42 empty] | 1988-02-25 | 18:00 | -0.6
[42 empty] | 1988-02-25 | 19:00 | -0.6
[42 empty] | 1988-02-25 | 20:00 | -0.6
[42 empty] | 1988-02-25 | 21:00 | -1.1
[42 empty] | 1988-02-25 | 22:00 | -1.7
[42 empty] | 1988-02-25 | 23:00 | -2.2
[42 empty] | 1988-02-25 | 24:00 | -2.2
[42 empty] | 1988-02-26 | 1:00 | -2.8
[42 empty] | 1988-02-26 | 2:00 | -3.3
[42 empty] | 1988-02-26 | 3:00 | -3.3
[42 empty] | 1988-02-26 | 4:00 | -3.9
[42 empty] | 1988-02-26 | 5:00 | -3.9
[42 empty] | 1988-02-26 | 6:00 | -4.4
[42 empty] | 1988-02-26 | 7:00 | -4.4
[42 empty] | 1988-02-26 | 8:00 | -3.9
[42 empty] | 1988-02-26 | 9:00 | -3.3
[42 empty] | 1988-02-26 | 10:00 | -2.2
[42 empty] | 1988-02-26 | 11:00 | -0.6
[42 empty] | 1988-02-26 | 12:00 | 0.6
[42 empty] | 1988-02-26 | 13:00 | 0
[42 empty] | 1988-02-26 | 14:00 | 1.1
[42 empty] | 1988-02-26 | 15:00 | 1.7
[42 empty] | 1988-02-26 | 16:00 | 1.7
[42 empty] | 1988-02-26 | 17:00 | 1.1
[42 empty] | 1988-02-26 | 18:00 | 0.6
[42 empty] | 1988-02-26 | 19:00 | 0
[42 empty] | 1988-02-26 | 20:00 | 0
[42 empty] | 1988-02-26 | 21:00 | 0
[42 empty] | 1988-02-26 | 22:00 | 0
[42 empty] | 1988-02-26 | 23:00 | 0
[42 empty] | 1988-02-26 | 24:00 | 0
[42 empty] | 1988-02-27 | 1:00 | -0.6
[42 empty] | 1988-02-27 | 2:00 | -0.6
[42 empty] | 1988-02-27 | 3:00 | -0.6
[42 empty] | 1988-02-27 | 4:00 | -0.6
[42 empty] | 1988-02-27 | 5:00 | -0.6
[42 empty] | 1988-02-27 | 6:00 | -0.6
[42 empty] | 1988-02-27 | 7:00 | -0.6
[42 empty] | 1988-02-27 | 8:00 | 0
[42 empty] | 1988-02-27 | 9:00 | 1.1
[42 empty] | 1988-02-27 | 10:00 | 1.7
[42 empty] | 1988-02-27 | 11:00 | 1.7
[42 empty] | 1988-02-27 | 12:00 | 0.6
[42 empty] | 1988-02-27 | 13:00 | 0.6
[42 empty] | 1988-02-27 | 14:00 | 0.6
[42 empty] | 1988-02-27 | 15:00 | 0.6
[42 empty] | 1988-02-27 | 16:00 | 0.6
[42 empty] | 1988-02-27 | 17:00 | 0.6
[42 empty] | 1988-02-27 | 18:00 | 0.6
[42 empty] | 1988-02-27 | 19:00 | 0
[42 empty] | 1988-02-27 | 20:00 | -0.6
[42 empty] | 1988-02-27 | 21:00 | -0.6
[42 empty] | 1988-02-27 | 22:00 | -0.6
[42 empty] | 1988-02-27 | 23:00 | -0.6
[42 empty] | 1988-02-27 | 24:00 | -0.6
[42 empty] | 1988-02-28 | 1:00 | -0.6
[42 empty] | 1988-02-28 | 2:00 | -1.1
[42 empty] | 1988-02-28 | 3:00 | -1.7
[42 empty] | 1988-02-28 | 4:00 | -1.7
[42 empty] | 1988-02-28 | 5:00 | -2.2
[42 empty] | 1988-02-28 | 6:00 | -2.2
[42 empty] | 1988-02-28 | 7:00 | -2.2
[42 empty] | 1988-02-28 | 8:00 | -1.7
[42 empty] | 1988-02-28 | 9:00 | -0.6
[42 empty] | 1988-02-28 | 10:00 | 1.1
[42 empty] | 1988-02-28 | 11:00 | 1.1
[42 empty] | 1988-02-28 | 12:00 | 1.7
[42 empty] | 1988-02-28 | 13:00 | 2.8
[42 empty] | 1988-02-28 | 14:00 | 3.3
[42 empty] | 1988-02-28 | 15:00 | 3.3
[42 empty] | 1988-02-28 | 16:00 | 4.4
[42 empty] | 1988-02-28 | 17:00 | 3.9
[42 empty] | 1988-02-28 | 18:00 | 2.2
[42 empty] | 1988-02-28 | 19:00 | 2.2
[42 empty] | 1988-02-28 | 20:00 | 1.7
[42 empty] | 1988-02-28 | 21:00 | 2.2
[42 empty] | 1988-02-28 | 22:00 | 1.4
[42 empty] | 1988-02-28 | 23:00 | 0.6
[42 empty] | 1988-02-28 | 24:00 | -0.1
[42 empty] | 1990-03-01 | 1:00 | -0.8
[42 empty] | 1990-03-01 | 2:00 | -1.6
[42 empty] | 1990-03-01 | 3:00 | -2.4
[42 empty] | 1990-03-01 | 4:00 | -3.3
[42 empty] | 1990-03-01 | 5:00 | -3.3
[42 empty] | 1990-03-01 | 6:00 | -3.9
[42 empty] | 1990-03-01 | 7:00 | -3.9
[42 empty] | 1990-03-01 | 8:00 | -3.9
[42 empty] | 1990-03-01 | 9:00 | -2.8
[42 empty] | 1990-03-01 | 10:00 | -1.7
[42 empty] | 1990-03-01 | 11:00 | 0
[42 empty] | 1990-03-01 | 12:00 | 1.1
[42 empty] | 1990-03-01 | 13:00 | 2.2
[42 empty] | 1990-03-01 | 14:00 | 3.3
[42 empty] | 1990-03-01 | 15:00 | 4.4
[42 empty] | 1990-03-01 | 16:00 | 4.4
[42 empty] | 1990-03-01 | 17:00 | 4.4
[42 empty] | 1990-03-01 | 18:00 | 4.4
[42 empty] | 1990-03-01 | 19:00 | 3.9
[42 empty] | 1990-03-01 | 20:00 | 3.9
[42 empty] | 1990-03-01 | 21:00 | 3.3
[42 empty] | 1990-03-01 | 22:00 | 2.8
[42 empty] | 1990-03-01 | 23:00 | 2.2
[42 empty] | 1990-03-01 | 24:00 | 1.7
[42 empty] | 1990-03-02 | 1:00 | 1.7
[42 empty] | 1990-03-02 | 2:00 | 1.1
[42 empty] | 1990-03-02 | 3:00 | 1.1
[42 empty] | 1990-03-02 | 4:00 | 1.1
[42 empty] | 1990-03-02 | 5:00 | 0.6
[42 empty] | 1990-03-02 | 6:00 | 0.6
[42 empty] | 1990-03-02 | 7:00 | 1.1
[42 empty] | 1990-03-02 | 8:00 | 1.7
[42 empty] | 1990-03-02 | 9:00 | 2.8
[42 empty] | 1990-03-02 | 10:00 | 5
[42 empty] | 1990-03-02 | 11:00 | 6.7
[42 empty] | 1990-03-02 | 12:00 | 9.4
[42 empty] | 1990-03-02 | 13:00 | 10
[42 empty] | 1990-03-02 | 14:00 | 10
[42 empty] | 1990-03-02 | 15:00 | 9.4
[42 empty] | 1990-03-02 | 16:00 | 10
[42 empty] | 1990-03-02 | 17:00 | 9.4
[42 empty] | 1990-03-02 | 18:00 | 8.9
[42 empty] | 1990-03-02 | 19:00 | 8.9
[42 empty] | 1990-03-02 | 20:00 | 8.9
[42 empty] | 1990-03-02 | 21:00 | 8.3
[42 empty] | 1990-03-02 | 22:00 | 7.8
[42 empty] | 1990-03-02 | 23:00 | 7.8
[42 empty] | 1990-03-02 | 24:00 | 7.2
[42 empty] | 1990-03-03 | 1:00 | 7.2
[42 empty] | 1990-03-03 | 2:00 | 6.7
[42 empty] | 1990-03-03 | 3:00 | 6.1
[42 empty] | 1990-03-03 | 4:00 | 6.7
[42 empty] | 1990-03-03 | 5:00 | 6.1
[42 empty] | 1990-03-03 | 6:00 | 5.6
[42 empty] | 1990-03-03 | 7:00 | 5
[42 empty] | 1990-03-03 | 8:00 | 6.1
[42 empty] | 1990-03-03 | 9:00 | 6.1
[42 empty] | 1990-03-03 | 10:00 | 6.7
[42 empty] | 1990-03-03 | 11:00 | 6.7
[42 empty] | 1990-03-03 | 12:00 | 7.8
[42 empty] | 1990-03-03 | 13:00 | 8.9
[42 empty] | 1990-03-03 | 14:00 | 9.4
[42 empty] | 1990-03-03 | 15:00 | 9.4
[42 empty] | 1990-03-03 | 16:00 | 9.4
[42 empty] | 1990-03-03 | 17:00 | 9.4
[42 empty] | 1990-03-03 | 18:00 | 8.3
[42 empty] | 1990-03-03 | 19:00 | 8.3
[42 empty] | 1990-03-03 | 20:00 | 7.8
[42 empty] | 1990-03-03 | 21:00 | 6.7
[42 empty] | 1990-03-03 | 22:00 | 5.6
[42 empty] | 1990-03-03 | 23:00 | 4.4
[42 empty] | 1990-03-03 | 24:00 | 4.4
[42 empty] | 1990-03-04 | 1:00 | 3.3
[42 empty] | 1990-03-04 | 2:00 | 1.1
[42 empty] | 1990-03-04 | 3:00 | 0
[42 empty] | 1990-03-04 | 4:00 | -1.7
[42 empty] | 1990-03-04 | 5:00 | -3.3
[42 empty] | 1990-03-04 | 6:00 | -3.9
[42 empty] | 1990-03-04 | 7:00 | -3.9
[42 empty] | 1990-03-04 | 8:00 | -4.4
[42 empty] | 1990-03-04 | 9:00 | -3.9
[42 empty] | 1990-03-04 | 10:00 | -3.9
[42 empty] | 1990-03-04 | 11:00 | -2.8
[42 empty] | 1990-03-04 | 12:00 | -2.2
[42 empty] | 1990-03-04 | 13:00 | -1.1
[42 empty] | 1990-03-04 | 14:00 | 0
[42 empty] | 1990-03-04 | 15:00 | 1.1
[42 empty] | 1990-03-04 | 16:00 | 1.1
[42 empty] | 1990-03-04 | 17:00 | 1.1
[42 empty] | 1990-03-04 | 18:00 | 0.6
[42 empty] | 1990-03-04 | 19:00 | 0
[42 empty] | 1990-03-04 | 20:00 | -0.6
[42 empty] | 1990-03-04 | 21:00 | -1.1
[42 empty] | 1990-03-04 | 22:00 | -1.7
[42 empty] | 1990-03-04 | 23:00 | -1.7
[42 empty] | 1990-03-04 | 24:00 | -1.7
[42 empty] | 1990-03-05 | 1:00 | -1.7
[42 empty] | 1990-03-05 | 2:00 | -2.8
[42 empty] | 1990-03-05 | 3:00 | -3.3
[42 empty] | 1990-03-05 | 4:00 | -3.9
[42 empty] | 1990-03-05 | 5:00 | -3.9
[42 empty] | 1990-03-05 | 6:00 | -3.3
[42 empty] | 1990-03-05 | 7:00 | -3.3
[42 empty] | 1990-03-05 | 8:00 | -2.8
[42 empty] | 1990-03-05 | 9:00 | -2.8
[42 empty] | 1990-03-05 | 10:00 | -2.2
[42 empty] | 1990-03-05 | 11:00 | -1.7
[42 empty] | 1990-03-05 | 12:00 | 0
[42 empty] | 1990-03-05 | 13:00 | 0.6
[42 empty] | 1990-03-05 | 14:00 | 1.7
[42 empty] | 1990-03-05 | 15:00 | 1.7
[42 empty] | 1990-03-05 | 16:00 | 1.1
[42 empty] | 1990-03-05 | 17:00 | 1.1
[42 empty] | 1990-03-05 | 18:00 | 1.1
[42 empty] | 1990-03-05 | 19:00 | 1.1
[42 empty] | 1990-03-05 | 20:00 | 1.7
[42 empty] | 1990-03-05 | 21:00 | 1.1
[42 empty] | 1990-03-05 | 22:00 | 0.6
[42 empty] | 1990-03-05 | 23:00 | 0.6
[42 empty] | 1990-03-05 | 24:00 | 0.6
[42 empty] | 1990-03-06 | 1:00 | 0
[42 empty] | 1990-03-06 | 2:00 | 0
[42 empty] | 1990-03-06 | 3:00 | 0
[42 empty] | 1990-03-06 | 4:00 | 0
[42 empty] | 1990-03-06 | 5:00 | 0
[42 empty] | 1990-03-06 | 6:00 | 0
[42 empty] | 1990-03-06 | 7:00 | 0
[42 empty] | 1990-03-06 | 8:00 | 0
[42 empty] | 1990-03-06 | 9:00 | -0.6
[42 empty] | 1990-03-06 | 10:00 | -0.6
[42 empty] | 1990-03-06 | 11:00 | -1.1
[42 empty] | 1990-03-06 | 12:00 | -2.2
[42 empty] | 1990-03-06 | 13:00 | -2.8
[42 empty] | 1990-03-06 | 14:00 | -2.8
[42 empty] | 1990-03-06 | 15:00 | -2.2
[42 empty] | 1990-03-06 | 16:00 | -1.7
[42 empty] | 1990-03-06 | 17:00 | -1.1
[42 empty] | 1990-03-06 | 18:00 | -1.7
[42 empty] | 1990-03-06 | 19:00 | -2.2
[42 empty] | 1990-03-06 | 20:00 | -2.2
[42 empty] | 1990-03-06 | 21:00 | -2.8
[42 empty] | 1990-03-06 | 22:00 | -3.3
[42 empty] | 1990-03-06 | 23:00 | -3.9
[42 empty] | 1990-03-06 | 24:00 | -5
[42 empty] | 1990-03-07 | 1:00 | -6.7
[42 empty] | 1990-03-07 | 2:00 | -7.8
[42 empty] | 1990-03-07 | 3:00 | -8.3
[42 empty] | 1990-03-07 | 4:00 | -9.4
[42 empty] | 1990-03-07 | 5:00 | -10
[42 empty] | 1990-03-07 | 6:00 | -10
[42 empty] | 1990-03-07 | 7:00 | -10
[42 empty] | 1990-03-07 | 8:00 | -8.9
[42 empty] | 1990-03-07 | 9:00 | -7.2
[42 empty] | 1990-03-07 | 10:00 | -5.6
[42 empty] | 1990-03-07 | 11:00 | -5
[42 empty] | 1990-03-07 | 12:00 | -3.9
[42 empty] | 1990-03-07 | 13:00 | -2.8
[42 empty] | 1990-03-07 | 14:00 | -1.7
[42 empty] | 1990-03-07 | 15:00 | -1.1
[42 empty] | 1990-03-07 | 16:00 | 0
[42 empty] | 1990-03-07 | 17:00 | 0
[42 empty] | 1990-03-07 | 18:00 | 0
[42 empty] | 1990-03-07 | 19:00 | 0
[42 empty] | 1990-03-07 | 20:00 | -0.6
[42 empty] | 1990-03-07 | 21:00 | -0.6
[42 empty] | 1990-03-07 | 22:00 | -1.1
[42 empty] | 1990-03-07 | 23:00 | -1.7
[42 empty] | 1990-03-07 | 24:00 | -1.7
[42 empty] | 1990-03-08 | 1:00 | -2.2
[42 empty] | 1990-03-08 | 2:00 | -2.2
[42 empty] | 1990-03-08 | 3:00 | -2.2
[42 empty] | 1990-03-08 | 4:00 | -2.8
[42 empty] | 1990-03-08 | 5:00 | -3.3
[42 empty] | 1990-03-08 | 6:00 | -3.3
[42 empty] | 1990-03-08 | 7:00 | -3.3
[42 empty] | 1990-03-08 | 8:00 | -2.2
[42 empty] | 1990-03-08 | 9:00 | -1.1
[42 empty] | 1990-03-08 | 10:00 | 0
[42 empty] | 1990-03-08 | 11:00 | 0.6
[42 empty] | 1990-03-08 | 12:00 | 2.8
[42 empty] | 1990-03-08 | 13:00 | 3.3
[42 empty] | 1990-03-08 | 14:00 | 4.4
[42 empty] | 1990-03-08 | 15:00 | 6.1
[42 empty] | 1990-03-08 | 16:00 | 6.7
[42 empty] | 1990-03-08 | 17:00 | 4.4
[42 empty] | 1990-03-08 | 18:00 | 3.3
[42 empty] | 1990-03-08 | 19:00 | 2.2
[42 empty] | 1990-03-08 | 20:00 | 3.3
[42 empty] | 1990-03-08 | 21:00 | 3.3
[42 empty] | 1990-03-08 | 22:00 | 2.2
[42 empty] | 1990-03-08 | 23:00 | 2.2
[42 empty] | 1990-03-08 | 24:00 | 2.2
[42 empty] | 1990-03-09 | 1:00 | 2.2
[42 empty] | 1990-03-09 | 2:00 | 2.8
[42 empty] | 1990-03-09 | 3:00 | 2.2
[42 empty] | 1990-03-09 | 4:00 | 1.7
[42 empty] | 1990-03-09 | 5:00 | 1.7
[42 empty] | 1990-03-09 | 6:00 | 1.1
[42 empty] | 1990-03-09 | 7:00 | 1.7
[42 empty] | 1990-03-09 | 8:00 | 3.3
[42 empty] | 1990-03-09 | 9:00 | 6.1
[42 empty] | 1990-03-09 | 10:00 | 6.7
[42 empty] | 1990-03-09 | 11:00 | 7.2
[42 empty] | 1990-03-09 | 12:00 | 8.3
[42 empty] | 1990-03-09 | 13:00 | 7.8
[42 empty] | 1990-03-09 | 14:00 | 8.3
[42 empty] | 1990-03-09 | 15:00 | 8.3
[42 empty] | 1990-03-09 | 16:00 | 7.8
[42 empty] | 1990-03-09 | 17:00 | 7.8
[42 empty] | 1990-03-09 | 18:00 | 6.7
[42 empty] | 1990-03-09 | 19:00 | 6.7
[42 empty] | 1990-03-09 | 20:00 | 7.2
[42 empty] | 1990-03-09 | 21:00 | 7.8
[42 empty] | 1990-03-09 | 22:00 | 7.2
[42 empty] | 1990-03-09 | 23:00 | 6.7
[42 empty] | 1990-03-09 | 24:00 | 6.1
[42 empty] | 1990-03-10 | 1:00 | 5
[42 empty] | 1990-03-10 | 2:00 | 4.4
[42 empty] | 1990-03-10 | 3:00 | 4.4
[42 empty] | 1990-03-10 | 4:00 | 3.9
[42 empty] | 1990-03-10 | 5:00 | 3.9
[42 empty] | 1990-03-10 | 6:00 | 3.9
[42 empty] | 1990-03-10 | 7:00 | 3.9
[42 empty] | 1990-03-10 | 8:00 | 3.9
[42 empty] | 1990-03-10 | 9:00 | 4.4
[42 empty] | 1990-03-10 | 10:00 | 4.4
[42 empty] | 1990-03-10 | 11:00 | 4.4
[42 empty] | 1990-03-10 | 12:00 | 6.1
[42 empty] | 1990-03-10 | 13:00 | 8.3
[42 empty] | 1990-03-10 | 14:00 | 11.1
[42 empty] | 1990-03-10 | 15:00 | 11.1
[42 empty] | 1990-03-10 | 16:00 | 10
[42 empty] | 1990-03-10 | 17:00 | 9.4
[42 empty] | 1990-03-10 | 18:00 | 7.2
[42 empty] | 1990-03-10 | 19:00 | 6.7
[42 empty] | 1990-03-10 | 20:00 | 7.2
[42 empty] | 1990-03-10 | 21:00 | 7.2
[42 empty] | 1990-03-10 | 22:00 | 7.8
[42 empty] | 1990-03-10 | 23:00 | 7.8
[42 empty] | 1990-03-10 | 24:00 | 8.3
[42 empty] | 1990-03-11 | 1:00 | 7.8
[42 empty] | 1990-03-11 | 2:00 | 7.8
[42 empty] | 1990-03-11 | 3:00 | 8.3
[42 empty] | 1990-03-11 | 4:00 | 8.3
[42 empty] | 1990-03-11 | 5:00 | 8.3
[42 empty] | 1990-03-11 | 6:00 | 8.3
[42 empty] | 1990-03-11 | 7:00 | 8.3
[42 empty] | 1990-03-11 | 8:00 | 8.3
[42 empty] | 1990-03-11 | 9:00 | 9.4
[42 empty] | 1990-03-11 | 10:00 | 9.4
[42 empty] | 1990-03-11 | 11:00 | 10.6
[42 empty] | 1990-03-11 | 12:00 | 12.2
[42 empty] | 1990-03-11 | 13:00 | 15
[42 empty] | 1990-03-11 | 14:00 | 16.7
[42 empty] | 1990-03-11 | 15:00 | 17.2
[42 empty] | 1990-03-11 | 16:00 | 17.8
[42 empty] | 1990-03-11 | 17:00 | 18.9
[42 empty] | 1990-03-11 | 18:00 | 16.1
[42 empty] | 1990-03-11 | 19:00 | 14.4
[42 empty] | 1990-03-11 | 20:00 | 15.6
[42 empty] | 1990-03-11 | 21:00 | 13.9
[42 empty] | 1990-03-11 | 22:00 | 13.3
[42 empty] | 1990-03-11 | 23:00 | 12.2
[42 empty] | 1990-03-11 | 24:00 | 9.4
[42 empty] | 1990-03-12 | 1:00 | 8.9
[42 empty] | 1990-03-12 | 2:00 | 9.4
[42 empty] | 1990-03-12 | 3:00 | 9.4
[42 empty] | 1990-03-12 | 4:00 | 9.4
[42 empty] | 1990-03-12 | 5:00 | 8.9
[42 empty] | 1990-03-12 | 6:00 | 7.8
[42 empty] | 1990-03-12 | 7:00 | 7.2
[42 empty] | 1990-03-12 | 8:00 | 8.3
[42 empty] | 1990-03-12 | 9:00 | 8.3
[42 empty] | 1990-03-12 | 10:00 | 7.2
[42 empty] | 1990-03-12 | 11:00 | 7.2
[42 empty] | 1990-03-12 | 12:00 | 7.2
[42 empty] | 1990-03-12 | 13:00 | 7.2
[42 empty] | 1990-03-12 | 14:00 | 6.7
[42 empty] | 1990-03-12 | 15:00 | 6.7
[42 empty] | 1990-03-12 | 16:00 | 8.3
[42 empty] | 1990-03-12 | 17:00 | 7.8
[42 empty] | 1990-03-12 | 18:00 | 7.2
[42 empty] | 1990-03-12 | 19:00 | 6.1
[42 empty] | 1990-03-12 | 20:00 | 5.6
[42 empty] | 1990-03-12 | 21:00 | 5.6
[42 empty] | 1990-03-12 | 22:00 | 5.6
[42 empty] | 1990-03-12 | 23:00 | 5.6
[42 empty] | 1990-03-12 | 24:00 | 5.6
[42 empty] | 1990-03-13 | 1:00 | 5
[42 empty] | 1990-03-13 | 2:00 | 4.4
[42 empty] | 1990-03-13 | 3:00 | 4.4
[42 empty] | 1990-03-13 | 4:00 | 4.4
[42 empty] | 1990-03-13 | 5:00 | 4.4
[42 empty] | 1990-03-13 | 6:00 | 5
[42 empty] | 1990-03-13 | 7:00 | 5.6
[42 empty] | 1990-03-13 | 8:00 | 10.6
[42 empty] | 1990-03-13 | 9:00 | 13.9
[42 empty] | 1990-03-13 | 10:00 | 19.4
[42 empty] | 1990-03-13 | 11:00 | 23.9
[42 empty] | 1990-03-13 | 12:00 | 25
[42 empty] | 1990-03-13 | 13:00 | 26.1
[42 empty] | 1990-03-13 | 14:00 | 26.1
[42 empty] | 1990-03-13 | 15:00 | 25
[42 empty] | 1990-03-13 | 16:00 | 27.8
[42 empty] | 1990-03-13 | 17:00 | 27.2
[42 empty] | 1990-03-13 | 18:00 | 23.3
[42 empty] | 1990-03-13 | 19:00 | 22.8
[42 empty] | 1990-03-13 | 20:00 | 21.1
[42 empty] | 1990-03-13 | 21:00 | 19.4
[42 empty] | 1990-03-13 | 22:00 | 20
[42 empty] | 1990-03-13 | 23:00 | 17.8
[42 empty] | 1990-03-13 | 24:00 | 13.9
[42 empty] | 1990-03-14 | 1:00 | 13.9
[42 empty] | 1990-03-14 | 2:00 | 13.9
[42 empty] | 1990-03-14 | 3:00 | 12.8
[42 empty] | 1990-03-14 | 4:00 | 10
[42 empty] | 1990-03-14 | 5:00 | 6.7
[42 empty] | 1990-03-14 | 6:00 | 6.7
[42 empty] | 1990-03-14 | 7:00 | 6.1
[42 empty] | 1990-03-14 | 8:00 | 7.2
[42 empty] | 1990-03-14 | 9:00 | 8.3
[42 empty] | 1990-03-14 | 10:00 | 9.4
[42 empty] | 1990-03-14 | 11:00 | 10
[42 empty] | 1990-03-14 | 12:00 | 10
[42 empty] | 1990-03-14 | 13:00 | 8.3
[42 empty] | 1990-03-14 | 14:00 | 9.4
[42 empty] | 1990-03-14 | 15:00 | 8.3
[42 empty] | 1990-03-14 | 16:00 | 8.3
[42 empty] | 1990-03-14 | 17:00 | 7.2
[42 empty] | 1990-03-14 | 18:00 | 7.2
[42 empty] | 1990-03-14 | 19:00 | 6.7
[42 empty] | 1990-03-14 | 20:00 | 6.1
[42 empty] | 1990-03-14 | 21:00 | 5.6
[42 empty] | 1990-03-14 | 22:00 | 5.6
[42 empty] | 1990-03-14 | 23:00 | 5
[42 empty] | 1990-03-14 | 24:00 | 5
[42 empty] | 1990-03-15 | 1:00 | 4.4
[42 empty] | 1990-03-15 | 2:00 | 5
[42 empty] | 1990-03-15 | 3:00 | 4.4
[42 empty] | 1990-03-15 | 4:00 | 5
[42 empty] | 1990-03-15 | 5:00 | 5
[42 empty] | 1990-03-15 | 6:00 | 5
[42 empty] | 1990-03-15 | 7:00 | 5.6
[42 empty] | 1990-03-15 | 8:00 | 6.7
[42 empty] | 1990-03-15 | 9:00 | 9.4
[42 empty] | 1990-03-15 | 10:00 | 11.7
[42 empty] | 1990-03-15 | 11:00 | 15
[42 empty] | 1990-03-15 | 12:00 | 18.9
[42 empty] | 1990-03-15 | 13:00 | 20.6
[42 empty] | 1990-03-15 | 14:00 | 22.8
[42 empty] | 1990-03-15 | 15:00 | 22.2
[42 empty] | 1990-03-15 | 16:00 | 20
[42 empty] | 1990-03-15 | 17:00 | 18.3
[42 empty] | 1990-03-15 | 18:00 | 17.8
[42 empty] | 1990-03-15 | 19:00 | 16.7
[42 empty] | 1990-03-15 | 20:00 | 16.7
[42 empty] | 1990-03-15 | 21:00 | 16.7
[42 empty] | 1990-03-15 | 22:00 | 18.9
[42 empty] | 1990-03-15 | 23:00 | 17.2
[42 empty] | 1990-03-15 | 24:00 | 16.1
[42 empty] | 1990-03-16 | 1:00 | 14.4
[42 empty] | 1990-03-16 | 2:00 | 13.3
[42 empty] | 1990-03-16 | 3:00 | 12.8
[42 empty] | 1990-03-16 | 4:00 | 11.7
[42 empty] | 1990-03-16 | 5:00 | 12.2
[42 empty] | 1990-03-16 | 6:00 | 12.8
[42 empty] | 1990-03-16 | 7:00 | 12.8
[42 empty] | 1990-03-16 | 8:00 | 14.4
[42 empty] | 1990-03-16 | 9:00 | 17.8
[42 empty] | 1990-03-16 | 10:00 | 20
[42 empty] | 1990-03-16 | 11:00 | 22.2
[42 empty] | 1990-03-16 | 12:00 | 23.3
[42 empty] | 1990-03-16 | 13:00 | 22.8
[42 empty] | 1990-03-16 | 14:00 | 23.9
[42 empty] | 1990-03-16 | 15:00 | 24.4
[42 empty] | 1990-03-16 | 16:00 | 24.4
[42 empty] | 1990-03-16 | 17:00 | 21.1
[42 empty] | 1990-03-16 | 18:00 | 20
[42 empty] | 1990-03-16 | 19:00 | 18.3
[42 empty] | 1990-03-16 | 20:00 | 18.3
[42 empty] | 1990-03-16 | 21:00 | 16.7
[42 empty] | 1990-03-16 | 22:00 | 16.1
[42 empty] | 1990-03-16 | 23:00 | 16.7
[42 empty] | 1990-03-16 | 24:00 | 15.6
[42 empty] | 1990-03-17 | 1:00 | 15
[42 empty] | 1990-03-17 | 2:00 | 14.4
[42 empty] | 1990-03-17 | 3:00 | 13.9
[42 empty] | 1990-03-17 | 4:00 | 13.3
[42 empty] | 1990-03-17 | 5:00 | 12.8
[42 empty] | 1990-03-17 | 6:00 | 12.8
[42 empty] | 1990-03-17 | 7:00 | 13.3
[42 empty] | 1990-03-17 | 8:00 | 13.3
[42 empty] | 1990-03-17 | 9:00 | 15.6
[42 empty] | 1990-03-17 | 10:00 | 16.1
[42 empty] | 1990-03-17 | 11:00 | 18.3
[42 empty] | 1990-03-17 | 12:00 | 18.9
[42 empty] | 1990-03-17 | 13:00 | 19.4
[42 empty] | 1990-03-17 | 14:00 | 18.9
[42 empty] | 1990-03-17 | 15:00 | 17.8
[42 empty] | 1990-03-17 | 16:00 | 16.7
[42 empty] | 1990-03-17 | 17:00 | 15.6
[42 empty] | 1990-03-17 | 18:00 | 15
[42 empty] | 1990-03-17 | 19:00 | 15
[42 empty] | 1990-03-17 | 20:00 | 17.2
[42 empty] | 1990-03-17 | 21:00 | 16.7
[42 empty] | 1990-03-17 | 22:00 | 14.4
[42 empty] | 1990-03-17 | 23:00 | 12.8
[42 empty] | 1990-03-17 | 24:00 | 12.2
[42 empty] | 1990-03-18 | 1:00 | 11.7
[42 empty] | 1990-03-18 | 2:00 | 11.7
[42 empty] | 1990-03-18 | 3:00 | 11.1
[42 empty] | 1990-03-18 | 4:00 | 11.1
[42 empty] | 1990-03-18 | 5:00 | 9.4
[42 empty] | 1990-03-18 | 6:00 | 8.9
[42 empty] | 1990-03-18 | 7:00 | 9.4
[42 empty] | 1990-03-18 | 8:00 | 9.4
[42 empty] | 1990-03-18 | 9:00 | 9.4
[42 empty] | 1990-03-18 | 10:00 | 10.6
[42 empty] | 1990-03-18 | 11:00 | 11.7
[42 empty] | 1990-03-18 | 12:00 | 12.2
[42 empty] | 1990-03-18 | 13:00 | 12.8
[42 empty] | 1990-03-18 | 14:00 | 13.9
[42 empty] | 1990-03-18 | 15:00 | 14.4
[42 empty] | 1990-03-18 | 16:00 | 14.4
[42 empty] | 1990-03-18 | 17:00 | 13.9
[42 empty] | 1990-03-18 | 18:00 | 13.3
[42 empty] | 1990-03-18 | 19:00 | 12.2
[42 empty] | 1990-03-18 | 20:00 | 11.1
[42 empty] | 1990-03-18 | 21:00 | 10
[42 empty] | 1990-03-18 | 22:00 | 10
[42 empty] | 1990-03-18 | 23:00 | 9.4
[42 empty] | 1990-03-18 | 24:00 | 8.9
[42 empty] | 1990-03-19 | 1:00 | 8.3
[42 empty] | 1990-03-19 | 2:00 | 8.3
[42 empty] | 1990-03-19 | 3:00 | 7.2
[42 empty] | 1990-03-19 | 4:00 | 6.7
[42 empty] | 1990-03-19 | 5:00 | 6.7
[42 empty] | 1990-03-19 | 6:00 | 7.2
[42 empty] | 1990-03-19 | 7:00 | 7.2
[42 empty] | 1990-03-19 | 8:00 | 8.3
[42 empty] | 1990-03-19 | 9:00 | 10
[42 empty] | 1990-03-19 | 10:00 | 11.7
[42 empty] | 1990-03-19 | 11:00 | 11.7
[42 empty] | 1990-03-19 | 12:00 | 11.7
[42 empty] | 1990-03-19 | 13:00 | 11.7
[42 empty] | 1990-03-19 | 14:00 | 12.2
[42 empty] | 1990-03-19 | 15:00 | 11.1
[42 empty] | 1990-03-19 | 16:00 | 10.6
[42 empty] | 1990-03-19 | 17:00 | 10.6
[42 empty] | 1990-03-19 | 18:00 | 10.6
[42 empty] | 1990-03-19 | 19:00 | 10.6
[42 empty] | 1990-03-19 | 20:00 | 11.1
[42 empty] | 1990-03-19 | 21:00 | 7.8
[42 empty] | 1990-03-19 | 22:00 | 7.2
[42 empty] | 1990-03-19 | 23:00 | 6.7
[42 empty] | 1990-03-19 | 24:00 | 6.7
[42 empty] | 1990-03-20 | 1:00 | 6.7
[42 empty] | 1990-03-20 | 2:00 | 7.2
[42 empty] | 1990-03-20 | 3:00 | 8.3
[42 empty] | 1990-03-20 | 4:00 | 7.2
[42 empty] | 1990-03-20 | 5:00 | 7.2
[42 empty] | 1990-03-20 | 6:00 | 8.3
[42 empty] | 1990-03-20 | 7:00 | 8.9
[42 empty] | 1990-03-20 | 8:00 | 8.9
[42 empty] | 1990-03-20 | 9:00 | 9.4
[42 empty] | 1990-03-20 | 10:00 | 8.9
[42 empty] | 1990-03-20 | 11:00 | 8.9
[42 empty] | 1990-03-20 | 12:00 | 8.3
[42 empty] | 1990-03-20 | 13:00 | 8.3
[42 empty] | 1990-03-20 | 14:00 | 6.1
[42 empty] | 1990-03-20 | 15:00 | 6.1
[42 empty] | 1990-03-20 | 16:00 | 6.1
[42 empty] | 1990-03-20 | 17:00 | 5
[42 empty] | 1990-03-20 | 18:00 | 5.6
[42 empty] | 1990-03-20 | 19:00 | 5
[42 empty] | 1990-03-20 | 20:00 | 4.4
[42 empty] | 1990-03-20 | 21:00 | 4.4
[42 empty] | 1990-03-20 | 22:00 | 4.4
[42 empty] | 1990-03-20 | 23:00 | 4.4
[42 empty] | 1990-03-20 | 24:00 | 4.4
[42 empty] | 1990-03-21 | 1:00 | 4.4
[42 empty] | 1990-03-21 | 2:00 | 3.3
[42 empty] | 1990-03-21 | 3:00 | 4.4
[42 empty] | 1990-03-21 | 4:00 | 4.4
[42 empty] | 1990-03-21 | 5:00 | 5
[42 empty] | 1990-03-21 | 6:00 | 4.4
[42 empty] | 1990-03-21 | 7:00 | 4.4
[42 empty] | 1990-03-21 | 8:00 | 4.4
[42 empty] | 1990-03-21 | 9:00 | 5.6
[42 empty] | 1990-03-21 | 10:00 | 6.1
[42 empty] | 1990-03-21 | 11:00 | 7.2
[42 empty] | 1990-03-21 | 12:00 | 8.3
[42 empty] | 1990-03-21 | 13:00 | 8.9
[42 empty] | 1990-03-21 | 14:00 | 10
[42 empty] | 1990-03-21 | 15:00 | 10.6
[42 empty] | 1990-03-21 | 16:00 | 10.6
[42 empty] | 1990-03-21 | 17:00 | 10.6
[42 empty] | 1990-03-21 | 18:00 | 10.6
[42 empty] | 1990-03-21 | 19:00 | 10
[42 empty] | 1990-03-21 | 20:00 | 8.9
[42 empty] | 1990-03-21 | 21:00 | 8.9
[42 empty] | 1990-03-21 | 22:00 | 7.8
[42 empty] | 1990-03-21 | 23:00 | 7.8
[42 empty] | 1990-03-21 | 24:00 | 7.2
[42 empty] | 1990-03-22 | 1:00 | 6.7
[42 empty] | 1990-03-22 | 2:00 | 7.8
[42 empty] | 1990-03-22 | 3:00 | 6.1
[42 empty] | 1990-03-22 | 4:00 | 5
[42 empty] | 1990-03-22 | 5:00 | 4.4
[42 empty] | 1990-03-22 | 6:00 | 6.1
[42 empty] | 1990-03-22 | 7:00 | 7.2
[42 empty] | 1990-03-22 | 8:00 | 8.3
[42 empty] | 1990-03-22 | 9:00 | 11.1
[42 empty] | 1990-03-22 | 10:00 | 11.1
[42 empty] | 1990-03-22 | 11:00 | 12.2
[42 empty] | 1990-03-22 | 12:00 | 12.2
[42 empty] | 1990-03-22 | 13:00 | 12.8
[42 empty] | 1990-03-22 | 14:00 | 12.8
[42 empty] | 1990-03-22 | 15:00 | 13.3
[42 empty] | 1990-03-22 | 16:00 | 12.2
[42 empty] | 1990-03-22 | 17:00 | 11.1
[42 empty] | 1990-03-22 | 18:00 | 10.6
[42 empty] | 1990-03-22 | 19:00 | 10
[42 empty] | 1990-03-22 | 20:00 | 9.4
[42 empty] | 1990-03-22 | 21:00 | 9.4
[42 empty] | 1990-03-22 | 22:00 | 9.4
[42 empty] | 1990-03-22 | 23:00 | 8.9
[42 empty] | 1990-03-22 | 24:00 | 8.9
[42 empty] | 1990-03-23 | 1:00 | 8.9
[42 empty] | 1990-03-23 | 2:00 | 9.4
[42 empty] | 1990-03-23 | 3:00 | 8.9
[42 empty] | 1990-03-23 | 4:00 | 8.9
[42 empty] | 1990-03-23 | 5:00 | 8.9
[42 empty] | 1990-03-23 | 6:00 | 10
[42 empty] | 1990-03-23 | 7:00 | 12.2
[42 empty] | 1990-03-23 | 8:00 | 13.3
[42 empty] | 1990-03-23 | 9:00 | 15
[42 empty] | 1990-03-23 | 10:00 | 16.7
[42 empty] | 1990-03-23 | 11:00 | 17.8
[42 empty] | 1990-03-23 | 12:00 | 18.3
[42 empty] | 1990-03-23 | 13:00 | 18.9
[42 empty] | 1990-03-23 | 14:00 | 17.8
[42 empty] | 1990-03-23 | 15:00 | 16.1
[42 empty] | 1990-03-23 | 16:00 | 11.1
[42 empty] | 1990-03-23 | 17:00 | 9.4
[42 empty] | 1990-03-23 | 18:00 | 7.8
[42 empty] | 1990-03-23 | 19:00 | 6.7
[42 empty] | 1990-03-23 | 20:00 | 6.1
[42 empty] | 1990-03-23 | 21:00 | 5.6
[42 empty] | 1990-03-23 | 22:00 | 3.9
[42 empty] | 1990-03-23 | 23:00 | 3.3
[42 empty] | 1990-03-23 | 24:00 | 2.8
[42 empty] | 1990-03-24 | 1:00 | 2.2
[42 empty] | 1990-03-24 | 2:00 | 2.2
[42 empty] | 1990-03-24 | 3:00 | 1.7
[42 empty] | 1990-03-24 | 4:00 | 1.7
[42 empty] | 1990-03-24 | 5:00 | 1.1
[42 empty] | 1990-03-24 | 6:00 | 1.1
[42 empty] | 1990-03-24 | 7:00 | 1.1
[42 empty] | 1990-03-24 | 8:00 | 1.1
[42 empty] | 1990-03-24 | 9:00 | 1.7
[42 empty] | 1990-03-24 | 10:00 | 2.2
[42 empty] | 1990-03-24 | 11:00 | 2.8
[42 empty] | 1990-03-24 | 12:00 | 2.8
[42 empty] | 1990-03-24 | 13:00 | 2.2
[42 empty] | 1990-03-24 | 14:00 | 2.8
[42 empty] | 1990-03-24 | 15:00 | 2.8
[42 empty] | 1990-03-24 | 16:00 | 2.8
[42 empty] | 1990-03-24 | 17:00 | 2.8
[42 empty] | 1990-03-24 | 18:00 | 2.8
[42 empty] | 1990-03-24 | 19:00 | 2.8
[42 empty] | 1990-03-24 | 20:00 | 2.8
[42 empty] | 1990-03-24 | 21:00 | 2.8
[42 empty] | 1990-03-24 | 22:00 | 2.8
[42 empty] | 1990-03-24 | 23:00 | 2.8
[42 empty] | 1990-03-24 | 24:00 | 2.8
[42 empty] | 1990-03-25 | 1:00 | 2.8
[42 empty] | 1990-03-25 | 2:00 | 2.8
[42 empty] | 1990-03-25 | 3:00 | 2.2
[42 empty] | 1990-03-25 | 4:00 | 2.8
[42 empty] | 1990-03-25 | 5:00 | 2.8
[42 empty] | 1990-03-25 | 6:00 | 2.8
[42 empty] | 1990-03-25 | 7:00 | 2.8
[42 empty] | 1990-03-25 | 8:00 | 3.3
[42 empty] | 1990-03-25 | 9:00 | 4.4
[42 empty] | 1990-03-25 | 10:00 | 6.1
[42 empty] | 1990-03-25 | 11:00 | 6.1
[42 empty] | 1990-03-25 | 12:00 | 7.8
[42 empty] | 1990-03-25 | 13:00 | 7.8
[42 empty] | 1990-03-25 | 14:00 | 7.8
[42 empty] | 1990-03-25 | 15:00 | 7.8
[42 empty] | 1990-03-25 | 16:00 | 8.3
[42 empty] | 1990-03-25 | 17:00 | 7.8
[42 empty] | 1990-03-25 | 18:00 | 7.8
[42 empty] | 1990-03-25 | 19:00 | 7.2
[42 empty] | 1990-03-25 | 20:00 | 7.2
[42 empty] | 1990-03-25 | 21:00 | 7.2
[42 empty] | 1990-03-25 | 22:00 | 6.1
[42 empty] | 1990-03-25 | 23:00 | 6.1
[42 empty] | 1990-03-25 | 24:00 | 6.1
[42 empty] | 1990-03-26 | 1:00 | 5
[42 empty] | 1990-03-26 | 2:00 | 5.6
[42 empty] | 1990-03-26 | 3:00 | 5
[42 empty] | 1990-03-26 | 4:00 | 5
[42 empty] | 1990-03-26 | 5:00 | 4.4
[42 empty] | 1990-03-26 | 6:00 | 5
[42 empty] | 1990-03-26 | 7:00 | 5.6
[42 empty] | 1990-03-26 | 8:00 | 6.1
[42 empty] | 1990-03-26 | 9:00 | 6.7
[42 empty] | 1990-03-26 | 10:00 | 7.8
[42 empty] | 1990-03-26 | 11:00 | 8.9
[42 empty] | 1990-03-26 | 12:00 | 10
[42 empty] | 1990-03-26 | 13:00 | 10.6
[42 empty] | 1990-03-26 | 14:00 | 11.7
[42 empty] | 1990-03-26 | 15:00 | 11.1
[42 empty] | 1990-03-26 | 16:00 | 10.6
[42 empty] | 1990-03-26 | 17:00 | 8.3
[42 empty] | 1990-03-26 | 18:00 | 7.2
[42 empty] | 1990-03-26 | 19:00 | 6.1
[42 empty] | 1990-03-26 | 20:00 | 4.4
[42 empty] | 1990-03-26 | 21:00 | 3.3
[42 empty] | 1990-03-26 | 22:00 | 2.8
[42 empty] | 1990-03-26 | 23:00 | 1.7
[42 empty] | 1990-03-26 | 24:00 | 1.1
[42 empty] | 1990-03-27 | 1:00 | 0.6
[42 empty] | 1990-03-27 | 2:00 | -0.6
[42 empty] | 1990-03-27 | 3:00 | -1.1
[42 empty] | 1990-03-27 | 4:00 | -1.7
[42 empty] | 1990-03-27 | 5:00 | -1.7
[42 empty] | 1990-03-27 | 6:00 | -2.2
[42 empty] | 1990-03-27 | 7:00 | -2.2
[42 empty] | 1990-03-27 | 8:00 | -2.2
[42 empty] | 1990-03-27 | 9:00 | -0.6
[42 empty] | 1990-03-27 | 10:00 | 0
[42 empty] | 1990-03-27 | 11:00 | 1.1
[42 empty] | 1990-03-27 | 12:00 | 2.8
[42 empty] | 1990-03-27 | 13:00 | 2.8
[42 empty] | 1990-03-27 | 14:00 | 3.3
[42 empty] | 1990-03-27 | 15:00 | 4.4
[42 empty] | 1990-03-27 | 16:00 | 5
[42 empty] | 1990-03-27 | 17:00 | 4.4
[42 empty] | 1990-03-27 | 18:00 | 3.9
[42 empty] | 1990-03-27 | 19:00 | 3.3
[42 empty] | 1990-03-27 | 20:00 | 2.8
[42 empty] | 1990-03-27 | 21:00 | 2.2
[42 empty] | 1990-03-27 | 22:00 | 2.2
[42 empty] | 1990-03-27 | 23:00 | 1.7
[42 empty] | 1990-03-27 | 24:00 | 1.1
[42 empty] | 1990-03-28 | 1:00 | 1.1
[42 empty] | 1990-03-28 | 2:00 | 0.6
[42 empty] | 1990-03-28 | 3:00 | 0.6
[42 empty] | 1990-03-28 | 4:00 | 0.6
[42 empty] | 1990-03-28 | 5:00 | 0.6
[42 empty] | 1990-03-28 | 6:00 | 0.6
[42 empty] | 1990-03-28 | 7:00 | 1.7
[42 empty] | 1990-03-28 | 8:00 | 2.8
[42 empty] | 1990-03-28 | 9:00 | 4.4
[42 empty] | 1990-03-28 | 10:00 | 5.6
[42 empty] | 1990-03-28 | 11:00 | 6.7
[42 empty] | 1990-03-28 | 12:00 | 7.2
[42 empty] | 1990-03-28 | 13:00 | 8.9
[42 empty] | 1990-03-28 | 14:00 | 9.4
[42 empty] | 1990-03-28 | 15:00 | 10
[42 empty] | 1990-03-28 | 16:00 | 10.6
[42 empty] | 1990-03-28 | 17:00 | 11.1
[42 empty] | 1990-03-28 | 18:00 | 10.6
[42 empty] | 1990-03-28 | 19:00 | 10.6
[42 empty] | 1990-03-28 | 20:00 | 10
[42 empty] | 1990-03-28 | 21:00 | 10
[42 empty] | 1990-03-28 | 22:00 | 10
[42 empty] | 1990-03-28 | 23:00 | 8.9
[42 empty] | 1990-03-28 | 24:00 | 7.2
[42 empty] | 1990-03-29 | 1:00 | 6.7
[42 empty] | 1990-03-29 | 2:00 | 5
[42 empty] | 1990-03-29 | 3:00 | 4.4
[42 empty] | 1990-03-29 | 4:00 | 3.9
[42 empty] | 1990-03-29 | 5:00 | 3.3
[42 empty] | 1990-03-29 | 6:00 | 2.8
[42 empty] | 1990-03-29 | 7:00 | 3.3
[42 empty] | 1990-03-29 | 8:00 | 4.4
[42 empty] | 1990-03-29 | 9:00 | 6.1
[42 empty] | 1990-03-29 | 10:00 | 6.7
[42 empty] | 1990-03-29 | 11:00 | 6.1
[42 empty] | 1990-03-29 | 12:00 | 7.2
[42 empty] | 1990-03-29 | 13:00 | 7.2
[42 empty] | 1990-03-29 | 14:00 | 8.9
[42 empty] | 1990-03-29 | 15:00 | 7.8
[42 empty] | 1990-03-29 | 16:00 | 7.8
[42 empty] | 1990-03-29 | 17:00 | 7.2
[42 empty] | 1990-03-29 | 18:00 | 6.7
[42 empty] | 1990-03-29 | 19:00 | 6.7
[42 empty] | 1990-03-29 | 20:00 | 6.1
[42 empty] | 1990-03-29 | 21:00 | 6.1
[42 empty] | 1990-03-29 | 22:00 | 6.1
[42 empty] | 1990-03-29 | 23:00 | 5
[42 empty] | 1990-03-29 | 24:00 | 4.4
[42 empty] | 1990-03-30 | 1:00 | 4.4
[42 empty] | 1990-03-30 | 2:00 | 3.9
[42 empty] | 1990-03-30 | 3:00 | 3.9
[42 empty] | 1990-03-30 | 4:00 | 3.3
[42 empty] | 1990-03-30 | 5:00 | 2.8
[42 empty] | 1990-03-30 | 6:00 | 2.2
[42 empty] | 1990-03-30 | 7:00 | 2.2
[42 empty] | 1990-03-30 | 8:00 | 2.8
[42 empty] | 1990-03-30 | 9:00 | 2.8
[42 empty] | 1990-03-30 | 10:00 | 3.3
[42 empty] | 1990-03-30 | 11:00 | 3.3
[42 empty] | 1990-03-30 | 12:00 | 3.3
[42 empty] | 1990-03-30 | 13:00 | 3.3
[42 empty] | 1990-03-30 | 14:00 | 3.9
[42 empty] | 1990-03-30 | 15:00 | 3.9
[42 empty] | 1990-03-30 | 16:00 | 3.9
[42 empty] | 1990-03-30 | 17:00 | 4.4
[42 empty] | 1990-03-30 | 18:00 | 4.4
[42 empty] | 1990-03-30 | 19:00 | 4.4
[42 empty] | 1990-03-30 | 20:00 | 3.9
[42 empty] | 1990-03-30 | 21:00 | 3.3
[42 empty] | 1990-03-30 | 22:00 | 3.9
[42 empty] | 1990-03-30 | 23:00 | 3.9
[42 empty] | 1990-03-30 | 24:00 | 3.9
[42 empty] | 1990-03-31 | 1:00 | 3.9
[42 empty] | 1990-03-31 | 2:00 | 3.9
[42 empty] | 1990-03-31 | 3:00 | 3.9
[42 empty] | 1990-03-31 | 4:00 | 3.9
[42 empty] | 1990-03-31 | 5:00 | 3.9
[42 empty] | 1990-03-31 | 6:00 | 3.9
[42 empty] | 1990-03-31 | 7:00 | 3.9
[42 empty] | 1990-03-31 | 8:00 | 4.4
[42 empty] | 1990-03-31 | 9:00 | 4.4
[42 empty] | 1990-03-31 | 10:00 | 5.6
[42 empty] | 1990-03-31 | 11:00 | 5.6
[42 empty] | 1990-03-31 | 12:00 | 6.7
[42 empty] | 1990-03-31 | 13:00 | 6.7
[42 empty] | 1990-03-31 | 14:00 | 7.2
[42 empty] | 1990-03-31 | 15:00 | 7.8
[42 empty] | 1990-03-31 | 16:00 | 8.9
[42 empty] | 1990-03-31 | 17:00 | 8.3
[42 empty] | 1990-03-31 | 18:00 | 8.3
[42 empty] | 1990-03-31 | 19:00 | 7.2
[42 empty] | 1990-03-31 | 20:00 | 6.7
[42 empty] | 1990-03-31 | 21:00 | 7.2
[42 empty] | 1990-03-31 | 22:00 | 7
[42 empty] | 1990-03-31 | 23:00 | 6.7
[42 empty] | 1990-03-31 | 24:00 | 6.5
[42 empty] | 1990-04-01 | 1:00 | 6.3
[42 empty] | 1990-04-01 | 2:00 | 6.1
[42 empty] | 1990-04-01 | 3:00 | 5.8
[42 empty] | 1990-04-01 | 4:00 | 5.6
[42 empty] | 1990-04-01 | 5:00 | 5.6
[42 empty] | 1990-04-01 | 6:00 | 5.6
[42 empty] | 1990-04-01 | 7:00 | 5.6
[42 empty] | 1990-04-01 | 8:00 | 5.6
[42 empty] | 1990-04-01 | 9:00 | 6.1
[42 empty] | 1990-04-01 | 10:00 | 6.7
[42 empty] | 1990-04-01 | 11:00 | 6.7
[42 empty] | 1990-04-01 | 12:00 | 7.2
[42 empty] | 1990-04-01 | 13:00 | 7.2
[42 empty] | 1990-04-01 | 14:00 | 7.2
[42 empty] | 1990-04-01 | 15:00 | 7.2
[42 empty] | 1990-04-01 | 16:00 | 7.2
[42 empty] | 1990-04-01 | 17:00 | 7.2
[42 empty] | 1990-04-01 | 18:00 | 6.7
[42 empty] | 1990-04-01 | 19:00 | 6.7
[42 empty] | 1990-04-01 | 20:00 | 6.7
[42 empty] | 1990-04-01 | 21:00 | 6.7
[42 empty] | 1990-04-01 | 22:00 | 6.7
[42 empty] | 1990-04-01 | 23:00 | 6.7
[42 empty] | 1990-04-01 | 24:00 | 6.7
[42 empty] | 1990-04-02 | 1:00 | 6.7
[42 empty] | 1990-04-02 | 2:00 | 6.7
[42 empty] | 1990-04-02 | 3:00 | 6.7
[42 empty] | 1990-04-02 | 4:00 | 6.7
[42 empty] | 1990-04-02 | 5:00 | 6.7
[42 empty] | 1990-04-02 | 6:00 | 6.7
[42 empty] | 1990-04-02 | 7:00 | 7.2
[42 empty] | 1990-04-02 | 8:00 | 7.2
[42 empty] | 1990-04-02 | 9:00 | 8.3
[42 empty] | 1990-04-02 | 10:00 | 8.3
[42 empty] | 1990-04-02 | 11:00 | 8.9
[42 empty] | 1990-04-02 | 12:00 | 8.9
[42 empty] | 1990-04-02 | 13:00 | 8.9
[42 empty] | 1990-04-02 | 14:00 | 8.9
[42 empty] | 1990-04-02 | 15:00 | 8.9
[42 empty] | 1990-04-02 | 16:00 | 9.4
[42 empty] | 1990-04-02 | 17:00 | 9.4
[42 empty] | 1990-04-02 | 18:00 | 8.9
[42 empty] | 1990-04-02 | 19:00 | 9.4
[42 empty] | 1990-04-02 | 20:00 | 8.3
[42 empty] | 1990-04-02 | 21:00 | 8.3
[42 empty] | 1990-04-02 | 22:00 | 7.8
[42 empty] | 1990-04-02 | 23:00 | 7.8
[42 empty] | 1990-04-02 | 24:00 | 7.8
[42 empty] | 1990-04-03 | 1:00 | 7.8
[42 empty] | 1990-04-03 | 2:00 | 6.1
[42 empty] | 1990-04-03 | 3:00 | 5.6
[42 empty] | 1990-04-03 | 4:00 | 5.6
[42 empty] | 1990-04-03 | 5:00 | 5.6
[42 empty] | 1990-04-03 | 6:00 | 5.6
[42 empty] | 1990-04-03 | 7:00 | 5.6
[42 empty] | 1990-04-03 | 8:00 | 5.6
[42 empty] | 1990-04-03 | 9:00 | 6.1
[42 empty] | 1990-04-03 | 10:00 | 6.1
[42 empty] | 1990-04-03 | 11:00 | 6.7
[42 empty] | 1990-04-03 | 12:00 | 6.7
[42 empty] | 1990-04-03 | 13:00 | 6.7
[42 empty] | 1990-04-03 | 14:00 | 6.7
[42 empty] | 1990-04-03 | 15:00 | 7.2
[42 empty] | 1990-04-03 | 16:00 | 7.2
[42 empty] | 1990-04-03 | 17:00 | 6.7
[42 empty] | 1990-04-03 | 18:00 | 6.7
[42 empty] | 1990-04-03 | 19:00 | 6.7
[42 empty] | 1990-04-03 | 20:00 | 6.7
[42 empty] | 1990-04-03 | 21:00 | 6.7
[42 empty] | 1990-04-03 | 22:00 | 6.7
[42 empty] | 1990-04-03 | 23:00 | 6.7
[42 empty] | 1990-04-03 | 24:00 | 6.7
[42 empty] | 1990-04-04 | 1:00 | 6.1
[42 empty] | 1990-04-04 | 2:00 | 6.1
[42 empty] | 1990-04-04 | 3:00 | 6.1
[42 empty] | 1990-04-04 | 4:00 | 6.1
[42 empty] | 1990-04-04 | 5:00 | 6.1
[42 empty] | 1990-04-04 | 6:00 | 6.1
[42 empty] | 1990-04-04 | 7:00 | 6.1
[42 empty] | 1990-04-04 | 8:00 | 6.1
[42 empty] | 1990-04-04 | 9:00 | 6.7
[42 empty] | 1990-04-04 | 10:00 | 7.2
[42 empty] | 1990-04-04 | 11:00 | 7.8
[42 empty] | 1990-04-04 | 12:00 | 8.3
[42 empty] | 1990-04-04 | 13:00 | 8.3
[42 empty] | 1990-04-04 | 14:00 | 7.8
[42 empty] | 1990-04-04 | 15:00 | 8.3
[42 empty] | 1990-04-04 | 16:00 | 7.2
[42 empty] | 1990-04-04 | 17:00 | 6.7
[42 empty] | 1990-04-04 | 18:00 | 6.1
[42 empty] | 1990-04-04 | 19:00 | 5.6
[42 empty] | 1990-04-04 | 20:00 | 5.6
[42 empty] | 1990-04-04 | 21:00 | 5.6
[42 empty] | 1990-04-04 | 22:00 | 5.6
[42 empty] | 1990-04-04 | 23:00 | 6.1
[42 empty] | 1990-04-04 | 24:00 | 7.2
[42 empty] | 1990-04-05 | 1:00 | 7.2
[42 empty] | 1990-04-05 | 2:00 | 7.8
[42 empty] | 1990-04-05 | 3:00 | 7.2
[42 empty] | 1990-04-05 | 4:00 | 7.2
[42 empty] | 1990-04-05 | 5:00 | 6.7
[42 empty] | 1990-04-05 | 6:00 | 7.2
[42 empty] | 1990-04-05 | 7:00 | 7.8
[42 empty] | 1990-04-05 | 8:00 | 7.8
[42 empty] | 1990-04-05 | 9:00 | 8.3
[42 empty] | 1990-04-05 | 10:00 | 9.4
[42 empty] | 1990-04-05 | 11:00 | 9.4
[42 empty] | 1990-04-05 | 12:00 | 10.6
[42 empty] | 1990-04-05 | 13:00 | 11.1
[42 empty] | 1990-04-05 | 14:00 | 12.2
[42 empty] | 1990-04-05 | 15:00 | 12.8
[42 empty] | 1990-04-05 | 16:00 | 13.3
[42 empty] | 1990-04-05 | 17:00 | 13.9
[42 empty] | 1990-04-05 | 18:00 | 13.3
[42 empty] | 1990-04-05 | 19:00 | 12.8
[42 empty] | 1990-04-05 | 20:00 | 12.2
[42 empty] | 1990-04-05 | 21:00 | 12.2
[42 empty] | 1990-04-05 | 22:00 | 10
[42 empty] | 1990-04-05 | 23:00 | 10
[42 empty] | 1990-04-05 | 24:00 | 11.1
[42 empty] | 1990-04-06 | 1:00 | 11.7
[42 empty] | 1990-04-06 | 2:00 | 10
[42 empty] | 1990-04-06 | 3:00 | 9.4
[42 empty] | 1990-04-06 | 4:00 | 9.4
[42 empty] | 1990-04-06 | 5:00 | 9.4
[42 empty] | 1990-04-06 | 6:00 | 9.4
[42 empty] | 1990-04-06 | 7:00 | 8.3
[42 empty] | 1990-04-06 | 8:00 | 8.9
[42 empty] | 1990-04-06 | 9:00 | 8.9
[42 empty] | 1990-04-06 | 10:00 | 9.4
[42 empty] | 1990-04-06 | 11:00 | 9.4
[42 empty] | 1990-04-06 | 12:00 | 10
[42 empty] | 1990-04-06 | 13:00 | 10.6
[42 empty] | 1990-04-06 | 14:00 | 10.6
[42 empty] | 1990-04-06 | 15:00 | 10.6
[42 empty] | 1990-04-06 | 16:00 | 10
[42 empty] | 1990-04-06 | 17:00 | 10
[42 empty] | 1990-04-06 | 18:00 | 10
[42 empty] | 1990-04-06 | 19:00 | 9.4
[42 empty] | 1990-04-06 | 20:00 | 7.8
[42 empty] | 1990-04-06 | 21:00 | 6.7
[42 empty] | 1990-04-06 | 22:00 | 6.1
[42 empty] | 1990-04-06 | 23:00 | 5.6
[42 empty] | 1990-04-06 | 24:00 | 5.6
[42 empty] | 1990-04-07 | 1:00 | 5
[42 empty] | 1990-04-07 | 2:00 | 3.9
[42 empty] | 1990-04-07 | 3:00 | 1.7
[42 empty] | 1990-04-07 | 4:00 | 1.1
[42 empty] | 1990-04-07 | 5:00 | 1.1
[42 empty] | 1990-04-07 | 6:00 | 0.6
[42 empty] | 1990-04-07 | 7:00 | 1.1
[42 empty] | 1990-04-07 | 8:00 | 0.6
[42 empty] | 1990-04-07 | 9:00 | 1.7
[42 empty] | 1990-04-07 | 10:00 | 2.8
[42 empty] | 1990-04-07 | 11:00 | 3.9
[42 empty] | 1990-04-07 | 12:00 | 5
[42 empty] | 1990-04-07 | 13:00 | 6.1
[42 empty] | 1990-04-07 | 14:00 | 8.3
[42 empty] | 1990-04-07 | 15:00 | 8.3
[42 empty] | 1990-04-07 | 16:00 | 9.4
[42 empty] | 1990-04-07 | 17:00 | 8.3
[42 empty] | 1990-04-07 | 18:00 | 8.9
[42 empty] | 1990-04-07 | 19:00 | 8.3
[42 empty] | 1990-04-07 | 20:00 | 7.8
[42 empty] | 1990-04-07 | 21:00 | 7.2
[42 empty] | 1990-04-07 | 22:00 | 6.7
[42 empty] | 1990-04-07 | 23:00 | 5.6
[42 empty] | 1990-04-07 | 24:00 | 4.4
[42 empty] | 1990-04-08 | 1:00 | 3.9
[42 empty] | 1990-04-08 | 2:00 | 3.3
[42 empty] | 1990-04-08 | 3:00 | 3.3
[42 empty] | 1990-04-08 | 4:00 | 2.8
[42 empty] | 1990-04-08 | 5:00 | 2.8
[42 empty] | 1990-04-08 | 6:00 | 2.8
[42 empty] | 1990-04-08 | 7:00 | 3.3
[42 empty] | 1990-04-08 | 8:00 | 3.9
[42 empty] | 1990-04-08 | 9:00 | 5
[42 empty] | 1990-04-08 | 10:00 | 5
[42 empty] | 1990-04-08 | 11:00 | 5.6
[42 empty] | 1990-04-08 | 12:00 | 5.6
[42 empty] | 1990-04-08 | 13:00 | 6.1
[42 empty] | 1990-04-08 | 14:00 | 7.2
[42 empty] | 1990-04-08 | 15:00 | 8.3
[42 empty] | 1990-04-08 | 16:00 | 8.9
[42 empty] | 1990-04-08 | 17:00 | 8.9
[42 empty] | 1990-04-08 | 18:00 | 8.3
[42 empty] | 1990-04-08 | 19:00 | 8.3
[42 empty] | 1990-04-08 | 20:00 | 7.8
[42 empty] | 1990-04-08 | 21:00 | 7.8
[42 empty] | 1990-04-08 | 22:00 | 7.8
[42 empty] | 1990-04-08 | 23:00 | 7.2
[42 empty] | 1990-04-08 | 24:00 | 6.7
[42 empty] | 1990-04-09 | 1:00 | 6.1
[42 empty] | 1990-04-09 | 2:00 | 5
[42 empty] | 1990-04-09 | 3:00 | 5.6
[42 empty] | 1990-04-09 | 4:00 | 5
[42 empty] | 1990-04-09 | 5:00 | 5
[42 empty] | 1990-04-09 | 6:00 | 5
[42 empty] | 1990-04-09 | 7:00 | 7.8
[42 empty] | 1990-04-09 | 8:00 | 9.4
[42 empty] | 1990-04-09 | 9:00 | 10.6
[42 empty] | 1990-04-09 | 10:00 | 12.2
[42 empty] | 1990-04-09 | 11:00 | 12.2
[42 empty] | 1990-04-09 | 12:00 | 13.3
[42 empty] | 1990-04-09 | 13:00 | 15
[42 empty] | 1990-04-09 | 14:00 | 13.9
[42 empty] | 1990-04-09 | 15:00 | 13.9
[42 empty] | 1990-04-09 | 16:00 | 13.3
[42 empty] | 1990-04-09 | 17:00 | 13.3
[42 empty] | 1990-04-09 | 18:00 | 13.3
[42 empty] | 1990-04-09 | 19:00 | 12.8
[42 empty] | 1990-04-09 | 20:00 | 11.1
[42 empty] | 1990-04-09 | 21:00 | 10.6
[42 empty] | 1990-04-09 | 22:00 | 10
[42 empty] | 1990-04-09 | 23:00 | 10.6
[42 empty] | 1990-04-09 | 24:00 | 10
[42 empty] | 1990-04-10 | 1:00 | 10
[42 empty] | 1990-04-10 | 2:00 | 10
[42 empty] | 1990-04-10 | 3:00 | 10
[42 empty] | 1990-04-10 | 4:00 | 10
[42 empty] | 1990-04-10 | 5:00 | 10
[42 empty] | 1990-04-10 | 6:00 | 10
[42 empty] | 1990-04-10 | 7:00 | 10.6
[42 empty] | 1990-04-10 | 8:00 | 12.2
[42 empty] | 1990-04-10 | 9:00 | 13.9
[42 empty] | 1990-04-10 | 10:00 | 15
[42 empty] | 1990-04-10 | 11:00 | 17.2
[42 empty] | 1990-04-10 | 12:00 | 18.3
[42 empty] | 1990-04-10 | 13:00 | 19.4
[42 empty] | 1990-04-10 | 14:00 | 19.4
[42 empty] | 1990-04-10 | 15:00 | 17.2
[42 empty] | 1990-04-10 | 16:00 | 17.2
[42 empty] | 1990-04-10 | 17:00 | 16.7
[42 empty] | 1990-04-10 | 18:00 | 14.4
[42 empty] | 1990-04-10 | 19:00 | 14.4
[42 empty] | 1990-04-10 | 20:00 | 13.9
[42 empty] | 1990-04-10 | 21:00 | 12.2
[42 empty] | 1990-04-10 | 22:00 | 14.4
[42 empty] | 1990-04-10 | 23:00 | 14.4
[42 empty] | 1990-04-10 | 24:00 | 15.6
[42 empty] | 1990-04-11 | 1:00 | 17.2
[42 empty] | 1990-04-11 | 2:00 | 16.7
[42 empty] | 1990-04-11 | 3:00 | 16.1
[42 empty] | 1990-04-11 | 4:00 | 15
[42 empty] | 1990-04-11 | 5:00 | 15
[42 empty] | 1990-04-11 | 6:00 | 15
[42 empty] | 1990-04-11 | 7:00 | 13.9
[42 empty] | 1990-04-11 | 8:00 | 11.7
[42 empty] | 1990-04-11 | 9:00 | 12.2
[42 empty] | 1990-04-11 | 10:00 | 12.2
[42 empty] | 1990-04-11 | 11:00 | 12.2
[42 empty] | 1990-04-11 | 12:00 | 11.7
[42 empty] | 1990-04-11 | 13:00 | 12.2
[42 empty] | 1990-04-11 | 14:00 | 12.8
[42 empty] | 1990-04-11 | 15:00 | 11.7
[42 empty] | 1990-04-11 | 16:00 | 10.6
[42 empty] | 1990-04-11 | 17:00 | 9.4
[42 empty] | 1990-04-11 | 18:00 | 8.9
[42 empty] | 1990-04-11 | 19:00 | 7.8
[42 empty] | 1990-04-11 | 20:00 | 7.2
[42 empty] | 1990-04-11 | 21:00 | 6.7
[42 empty] | 1990-04-11 | 22:00 | 6.1
[42 empty] | 1990-04-11 | 23:00 | 5.6
[42 empty] | 1990-04-11 | 24:00 | 5.6
[42 empty] | 1990-04-12 | 1:00 | 5.6
[42 empty] | 1990-04-12 | 2:00 | 5.6
[42 empty] | 1990-04-12 | 3:00 | 5.6
[42 empty] | 1990-04-12 | 4:00 | 5
[42 empty] | 1990-04-12 | 5:00 | 5
[42 empty] | 1990-04-12 | 6:00 | 4.4
[42 empty] | 1990-04-12 | 7:00 | 4.4
[42 empty] | 1990-04-12 | 8:00 | 4.4
[42 empty] | 1990-04-12 | 9:00 | 5
[42 empty] | 1990-04-12 | 10:00 | 5
[42 empty] | 1990-04-12 | 11:00 | 6.7
[42 empty] | 1990-04-12 | 12:00 | 7.8
[42 empty] | 1990-04-12 | 13:00 | 8.9
[42 empty] | 1990-04-12 | 14:00 | 8.9
[42 empty] | 1990-04-12 | 15:00 | 9.4
[42 empty] | 1990-04-12 | 16:00 | 8.3
[42 empty] | 1990-04-12 | 17:00 | 7.8
[42 empty] | 1990-04-12 | 18:00 | 7.8
[42 empty] | 1990-04-12 | 19:00 | 7.2
[42 empty] | 1990-04-12 | 20:00 | 6.7
[42 empty] | 1990-04-12 | 21:00 | 6.1
[42 empty] | 1990-04-12 | 22:00 | 5.6
[42 empty] | 1990-04-12 | 23:00 | 5
[42 empty] | 1990-04-12 | 24:00 | 3.9
[42 empty] | 1990-04-13 | 1:00 | 3.3
[42 empty] | 1990-04-13 | 2:00 | 2.8
[42 empty] | 1990-04-13 | 3:00 | 2.2
[42 empty] | 1990-04-13 | 4:00 | 2.2
[42 empty] | 1990-04-13 | 5:00 | 2.2
[42 empty] | 1990-04-13 | 6:00 | 2.2
[42 empty] | 1990-04-13 | 7:00 | 3.3
[42 empty] | 1990-04-13 | 8:00 | 3.9
[42 empty] | 1990-04-13 | 9:00 | 5
[42 empty] | 1990-04-13 | 10:00 | 5.6
[42 empty] | 1990-04-13 | 11:00 | 6.7
[42 empty] | 1990-04-13 | 12:00 | 7.8
[42 empty] | 1990-04-13 | 13:00 | 8.9
[42 empty] | 1990-04-13 | 14:00 | 10
[42 empty] | 1990-04-13 | 15:00 | 10.6
[42 empty] | 1990-04-13 | 16:00 | 10.6
[42 empty] | 1990-04-13 | 17:00 | 8.9
[42 empty] | 1990-04-13 | 18:00 | 7.2
[42 empty] | 1990-04-13 | 19:00 | 6.1
[42 empty] | 1990-04-13 | 20:00 | 6.1
[42 empty] | 1990-04-13 | 21:00 | 6.1
[42 empty] | 1990-04-13 | 22:00 | 6.1
[42 empty] | 1990-04-13 | 23:00 | 6.1
[42 empty] | 1990-04-13 | 24:00 | 6.1
[42 empty] | 1990-04-14 | 1:00 | 5.6
[42 empty] | 1990-04-14 | 2:00 | 5
[42 empty] | 1990-04-14 | 3:00 | 5
[42 empty] | 1990-04-14 | 4:00 | 5
[42 empty] | 1990-04-14 | 5:00 | 4.4
[42 empty] | 1990-04-14 | 6:00 | 5
[42 empty] | 1990-04-14 | 7:00 | 6.7
[42 empty] | 1990-04-14 | 8:00 | 8.3
[42 empty] | 1990-04-14 | 9:00 | 10
[42 empty] | 1990-04-14 | 10:00 | 10.6
[42 empty] | 1990-04-14 | 11:00 | 10
[42 empty] | 1990-04-14 | 12:00 | 11.1
[42 empty] | 1990-04-14 | 13:00 | 11.1
[42 empty] | 1990-04-14 | 14:00 | 11.1
[42 empty] | 1990-04-14 | 15:00 | 11.1
[42 empty] | 1990-04-14 | 16:00 | 10.6
[42 empty] | 1990-04-14 | 17:00 | 10
[42 empty] | 1990-04-14 | 18:00 | 9.4
[42 empty] | 1990-04-14 | 19:00 | 8.9
[42 empty] | 1990-04-14 | 20:00 | 9.4
[42 empty] | 1990-04-14 | 21:00 | 9.4
[42 empty] | 1990-04-14 | 22:00 | 9.4
[42 empty] | 1990-04-14 | 23:00 | 8.9
[42 empty] | 1990-04-14 | 24:00 | 8.9
[42 empty] | 1990-04-15 | 1:00 | 8.9
[42 empty] | 1990-04-15 | 2:00 | 8.9
[42 empty] | 1990-04-15 | 3:00 | 8.9
[42 empty] | 1990-04-15 | 4:00 | 9.4
[42 empty] | 1990-04-15 | 5:00 | 10
[42 empty] | 1990-04-15 | 6:00 | 11.1
[42 empty] | 1990-04-15 | 7:00 | 11.7
[42 empty] | 1990-04-15 | 8:00 | 12.2
[42 empty] | 1990-04-15 | 9:00 | 11.7
[42 empty] | 1990-04-15 | 10:00 | 12.8
[42 empty] | 1990-04-15 | 11:00 | 14.4
[42 empty] | 1990-04-15 | 12:00 | 14.4
[42 empty] | 1990-04-15 | 13:00 | 15
[42 empty] | 1990-04-15 | 14:00 | 16.1
[42 empty] | 1990-04-15 | 15:00 | 15.6
[42 empty] | 1990-04-15 | 16:00 | 16.7
[42 empty] | 1990-04-15 | 17:00 | 15.6
[42 empty] | 1990-04-15 | 18:00 | 13.9
[42 empty] | 1990-04-15 | 19:00 | 11.7
[42 empty] | 1990-04-15 | 20:00 | 11.7
[42 empty] | 1990-04-15 | 21:00 | 11.7
[42 empty] | 1990-04-15 | 22:00 | 11.7
[42 empty] | 1990-04-15 | 23:00 | 11.7
[42 empty] | 1990-04-15 | 24:00 | 13.3
[42 empty] | 1990-04-16 | 1:00 | 12.2
[42 empty] | 1990-04-16 | 2:00 | 12.8
[42 empty] | 1990-04-16 | 3:00 | 12.2
[42 empty] | 1990-04-16 | 4:00 | 11.1
[42 empty] | 1990-04-16 | 5:00 | 10.6
[42 empty] | 1990-04-16 | 6:00 | 10.6
[42 empty] | 1990-04-16 | 7:00 | 11.1
[42 empty] | 1990-04-16 | 8:00 | 11.7
[42 empty] | 1990-04-16 | 9:00 | 12.2
[42 empty] | 1990-04-16 | 10:00 | 13.3
[42 empty] | 1990-04-16 | 11:00 | 15
[42 empty] | 1990-04-16 | 12:00 | 16.1
[42 empty] | 1990-04-16 | 13:00 | 16.7
[42 empty] | 1990-04-16 | 14:00 | 18.3
[42 empty] | 1990-04-16 | 15:00 | 18.9
[42 empty] | 1990-04-16 | 16:00 | 18.9
[42 empty] | 1990-04-16 | 17:00 | 19.4
[42 empty] | 1990-04-16 | 18:00 | 16.1
[42 empty] | 1990-04-16 | 19:00 | 14.4
[42 empty] | 1990-04-16 | 20:00 | 13.3
[42 empty] | 1990-04-16 | 21:00 | 12.8
[42 empty] | 1990-04-16 | 22:00 | 12.8
[42 empty] | 1990-04-16 | 23:00 | 12.2
[42 empty] | 1990-04-16 | 24:00 | 11.7
[42 empty] | 1990-04-17 | 1:00 | 11.1
[42 empty] | 1990-04-17 | 2:00 | 10.6
[42 empty] | 1990-04-17 | 3:00 | 10
[42 empty] | 1990-04-17 | 4:00 | 9.4
[42 empty] | 1990-04-17 | 5:00 | 10
[42 empty] | 1990-04-17 | 6:00 | 10.6
[42 empty] | 1990-04-17 | 7:00 | 11.1
[42 empty] | 1990-04-17 | 8:00 | 12.8
[42 empty] | 1990-04-17 | 9:00 | 16.1
[42 empty] | 1990-04-17 | 10:00 | 16.7
[42 empty] | 1990-04-17 | 11:00 | 18.9
[42 empty] | 1990-04-17 | 12:00 | 18.9
[42 empty] | 1990-04-17 | 13:00 | 18.3
[42 empty] | 1990-04-17 | 14:00 | 15.6
[42 empty] | 1990-04-17 | 15:00 | 10
[42 empty] | 1990-04-17 | 16:00 | 9.4
[42 empty] | 1990-04-17 | 17:00 | 7.8
[42 empty] | 1990-04-17 | 18:00 | 7.8
[42 empty] | 1990-04-17 | 19:00 | 8.3
[42 empty] | 1990-04-17 | 20:00 | 8.3
[42 empty] | 1990-04-17 | 21:00 | 8.3
[42 empty] | 1990-04-17 | 22:00 | 7.2
[42 empty] | 1990-04-17 | 23:00 | 6.1
[42 empty] | 1990-04-17 | 24:00 | 5.6
[42 empty] | 1990-04-18 | 1:00 | 5
[42 empty] | 1990-04-18 | 2:00 | 4.4
[42 empty] | 1990-04-18 | 3:00 | 3.9
[42 empty] | 1990-04-18 | 4:00 | 3.9
[42 empty] | 1990-04-18 | 5:00 | 3.3
[42 empty] | 1990-04-18 | 6:00 | 3.3
[42 empty] | 1990-04-18 | 7:00 | 3.9
[42 empty] | 1990-04-18 | 8:00 | 4.4
[42 empty] | 1990-04-18 | 9:00 | 5.6
[42 empty] | 1990-04-18 | 10:00 | 7.2
[42 empty] | 1990-04-18 | 11:00 | 8.3
[42 empty] | 1990-04-18 | 12:00 | 8.9
[42 empty] | 1990-04-18 | 13:00 | 10
[42 empty] | 1990-04-18 | 14:00 | 10
[42 empty] | 1990-04-18 | 15:00 | 10
[42 empty] | 1990-04-18 | 16:00 | 10.6
[42 empty] | 1990-04-18 | 17:00 | 10.6
[42 empty] | 1990-04-18 | 18:00 | 10
[42 empty] | 1990-04-18 | 19:00 | 9.4
[42 empty] | 1990-04-18 | 20:00 | 8.9
[42 empty] | 1990-04-18 | 21:00 | 8.3
[42 empty] | 1990-04-18 | 22:00 | 7.8
[42 empty] | 1990-04-18 | 23:00 | 7.2
[42 empty] | 1990-04-18 | 24:00 | 7.2
[42 empty] | 1990-04-19 | 1:00 | 6.7
[42 empty] | 1990-04-19 | 2:00 | 6.7
[42 empty] | 1990-04-19 | 3:00 | 6.1
[42 empty] | 1990-04-19 | 4:00 | 6.1
[42 empty] | 1990-04-19 | 5:00 | 5.6
[42 empty] | 1990-04-19 | 6:00 | 6.7
[42 empty] | 1990-04-19 | 7:00 | 8.9
[42 empty] | 1990-04-19 | 8:00 | 10
[42 empty] | 1990-04-19 | 9:00 | 10.6
[42 empty] | 1990-04-19 | 10:00 | 11.7
[42 empty] | 1990-04-19 | 11:00 | 12.8
[42 empty] | 1990-04-19 | 12:00 | 13.9
[42 empty] | 1990-04-19 | 13:00 | 13.9
[42 empty] | 1990-04-19 | 14:00 | 13.9
[42 empty] | 1990-04-19 | 15:00 | 12.8
[42 empty] | 1990-04-19 | 16:00 | 12.8
[42 empty] | 1990-04-19 | 17:00 | 12.8
[42 empty] | 1990-04-19 | 18:00 | 11.7
[42 empty] | 1990-04-19 | 19:00 | 10
[42 empty] | 1990-04-19 | 20:00 | 10
[42 empty] | 1990-04-19 | 21:00 | 10
[42 empty] | 1990-04-19 | 22:00 | 10
[42 empty] | 1990-04-19 | 23:00 | 9.4
[42 empty] | 1990-04-19 | 24:00 | 8.9
[42 empty] | 1990-04-20 | 1:00 | 8.9
[42 empty] | 1990-04-20 | 2:00 | 8.3
[42 empty] | 1990-04-20 | 3:00 | 8.3
[42 empty] | 1990-04-20 | 4:00 | 8.3
[42 empty] | 1990-04-20 | 5:00 | 8.3
[42 empty] | 1990-04-20 | 6:00 | 8.3
[42 empty] | 1990-04-20 | 7:00 | 9.4
[42 empty] | 1990-04-20 | 8:00 | 10.6
[42 empty] | 1990-04-20 | 9:00 | 11.1
[42 empty] | 1990-04-20 | 10:00 | 12.2
[42 empty] | 1990-04-20 | 11:00 | 14.4
[42 empty] | 1990-04-20 | 12:00 | 16.7
[42 empty] | 1990-04-20 | 13:00 | 16.7
[42 empty] | 1990-04-20 | 14:00 | 15.6
[42 empty] | 1990-04-20 | 15:00 | 16.1
[42 empty] | 1990-04-20 | 16:00 | 16.1
[42 empty] | 1990-04-20 | 17:00 | 16.7
[42 empty] | 1990-04-20 | 18:00 | 16.1
[42 empty] | 1990-04-20 | 19:00 | 15.6
[42 empty] | 1990-04-20 | 20:00 | 15.6
[42 empty] | 1990-04-20 | 21:00 | 15.6
[42 empty] | 1990-04-20 | 22:00 | 16.7
[42 empty] | 1990-04-20 | 23:00 | 15
[42 empty] | 1990-04-20 | 24:00 | 13.9
[42 empty] | 1990-04-21 | 1:00 | 13.3
[42 empty] | 1990-04-21 | 2:00 | 12.8
[42 empty] | 1990-04-21 | 3:00 | 12.2
[42 empty] | 1990-04-21 | 4:00 | 11.7
[42 empty] | 1990-04-21 | 5:00 | 11.7
[42 empty] | 1990-04-21 | 6:00 | 11.7
[42 empty] | 1990-04-21 | 7:00 | 12.2
[42 empty] | 1990-04-21 | 8:00 | 12.2
[42 empty] | 1990-04-21 | 9:00 | 13.9
[42 empty] | 1990-04-21 | 10:00 | 13.3
[42 empty] | 1990-04-21 | 11:00 | 13.9
[42 empty] | 1990-04-21 | 12:00 | 14.4
[42 empty] | 1990-04-21 | 13:00 | 15
[42 empty] | 1990-04-21 | 14:00 | 15.6
[42 empty] | 1990-04-21 | 15:00 | 16.1
[42 empty] | 1990-04-21 | 16:00 | 14.4
[42 empty] | 1990-04-21 | 17:00 | 14.4
[42 empty] | 1990-04-21 | 18:00 | 14.4
[42 empty] | 1990-04-21 | 19:00 | 14.4
[42 empty] | 1990-04-21 | 20:00 | 13.9
[42 empty] | 1990-04-21 | 21:00 | 12.2
[42 empty] | 1990-04-21 | 22:00 | 11.7
[42 empty] | 1990-04-21 | 23:00 | 12.8
[42 empty] | 1990-04-21 | 24:00 | 12.2
[42 empty] | 1990-04-22 | 1:00 | 11.7
[42 empty] | 1990-04-22 | 2:00 | 11.1
[42 empty] | 1990-04-22 | 3:00 | 10.6
[42 empty] | 1990-04-22 | 4:00 | 10.6
[42 empty] | 1990-04-22 | 5:00 | 10.6
[42 empty] | 1990-04-22 | 6:00 | 10.6
[42 empty] | 1990-04-22 | 7:00 | 11.1
[42 empty] | 1990-04-22 | 8:00 | 12.8
[42 empty] | 1990-04-22 | 9:00 | 14.4
[42 empty] | 1990-04-22 | 10:00 | 15.6
[42 empty] | 1990-04-22 | 11:00 | 15.6
[42 empty] | 1990-04-22 | 12:00 | 16.7
[42 empty] | 1990-04-22 | 13:00 | 17.8
[42 empty] | 1990-04-22 | 14:00 | 18.9
[42 empty] | 1990-04-22 | 15:00 | 20
[42 empty] | 1990-04-22 | 16:00 | 20.6
[42 empty] | 1990-04-22 | 17:00 | 22.2
[42 empty] | 1990-04-22 | 18:00 | 16.1
[42 empty] | 1990-04-22 | 19:00 | 14.4
[42 empty] | 1990-04-22 | 20:00 | 13.9
[42 empty] | 1990-04-22 | 21:00 | 13.9
[42 empty] | 1990-04-22 | 22:00 | 13.9
[42 empty] | 1990-04-22 | 23:00 | 14.4
[42 empty] | 1990-04-22 | 24:00 | 14.4
[42 empty] | 1990-04-23 | 1:00 | 15.6
[42 empty] | 1990-04-23 | 2:00 | 16.1
[42 empty] | 1990-04-23 | 3:00 | 15.6
[42 empty] | 1990-04-23 | 4:00 | 15.6
[42 empty] | 1990-04-23 | 5:00 | 15.6
[42 empty] | 1990-04-23 | 6:00 | 15
[42 empty] | 1990-04-23 | 7:00 | 16.1
[42 empty] | 1990-04-23 | 8:00 | 17.2
[42 empty] | 1990-04-23 | 9:00 | 18.3
[42 empty] | 1990-04-23 | 10:00 | 20
[42 empty] | 1990-04-23 | 11:00 | 20.6
[42 empty] | 1990-04-23 | 12:00 | 21.7
[42 empty] | 1990-04-23 | 13:00 | 22.8
[42 empty] | 1990-04-23 | 14:00 | 23.9
[42 empty] | 1990-04-23 | 15:00 | 25
[42 empty] | 1990-04-23 | 16:00 | 25.6
[42 empty] | 1990-04-23 | 17:00 | 25.6
[42 empty] | 1990-04-23 | 18:00 | 24.4
[42 empty] | 1990-04-23 | 19:00 | 23.9
[42 empty] | 1990-04-23 | 20:00 | 22.2
[42 empty] | 1990-04-23 | 21:00 | 21.1
[42 empty] | 1990-04-23 | 22:00 | 12.2
[42 empty] | 1990-04-23 | 23:00 | 14.4
[42 empty] | 1990-04-23 | 24:00 | 12.8
[42 empty] | 1990-04-24 | 1:00 | 11.1
[42 empty] | 1990-04-24 | 2:00 | 10
[42 empty] | 1990-04-24 | 3:00 | 10
[42 empty] | 1990-04-24 | 4:00 | 9.4
[42 empty] | 1990-04-24 | 5:00 | 9.4
[42 empty] | 1990-04-24 | 6:00 | 9.4
[42 empty] | 1990-04-24 | 7:00 | 10
[42 empty] | 1990-04-24 | 8:00 | 11.1
[42 empty] | 1990-04-24 | 9:00 | 12.2
[42 empty] | 1990-04-24 | 10:00 | 12.8
[42 empty] | 1990-04-24 | 11:00 | 15
[42 empty] | 1990-04-24 | 12:00 | 16.7
[42 empty] | 1990-04-24 | 13:00 | 16.7
[42 empty] | 1990-04-24 | 14:00 | 16.7
[42 empty] | 1990-04-24 | 15:00 | 15
[42 empty] | 1990-04-24 | 16:00 | 14.4
[42 empty] | 1990-04-24 | 17:00 | 13.9
[42 empty] | 1990-04-24 | 18:00 | 12.8
[42 empty] | 1990-04-24 | 19:00 | 11.7
[42 empty] | 1990-04-24 | 20:00 | 11.7
[42 empty] | 1990-04-24 | 21:00 | 11.1
[42 empty] | 1990-04-24 | 22:00 | 11.1
[42 empty] | 1990-04-24 | 23:00 | 10.6
[42 empty] | 1990-04-24 | 24:00 | 10.6
[42 empty] | 1990-04-25 | 1:00 | 10
[42 empty] | 1990-04-25 | 2:00 | 10
[42 empty] | 1990-04-25 | 3:00 | 10
[42 empty] | 1990-04-25 | 4:00 | 10
[42 empty] | 1990-04-25 | 5:00 | 10
[42 empty] | 1990-04-25 | 6:00 | 10.6
[42 empty] | 1990-04-25 | 7:00 | 11.1
[42 empty] | 1990-04-25 | 8:00 | 11.7
[42 empty] | 1990-04-25 | 9:00 | 11.1
[42 empty] | 1990-04-25 | 10:00 | 10.6
[42 empty] | 1990-04-25 | 11:00 | 10.6
[42 empty] | 1990-04-25 | 12:00 | 11.1
[42 empty] | 1990-04-25 | 13:00 | 12.2
[42 empty] | 1990-04-25 | 14:00 | 15
[42 empty] | 1990-04-25 | 15:00 | 15.6
[42 empty] | 1990-04-25 | 16:00 | 16.7
[42 empty] | 1990-04-25 | 17:00 | 16.7
[42 empty] | 1990-04-25 | 18:00 | 16.1
[42 empty] | 1990-04-25 | 19:00 | 15
[42 empty] | 1990-04-25 | 20:00 | 12.8
[42 empty] | 1990-04-25 | 21:00 | 12.8
[42 empty] | 1990-04-25 | 22:00 | 12.2
[42 empty] | 1990-04-25 | 23:00 | 11.7
[42 empty] | 1990-04-25 | 24:00 | 11.1
[42 empty] | 1990-04-26 | 1:00 | 10.6
[42 empty] | 1990-04-26 | 2:00 | 10
[42 empty] | 1990-04-26 | 3:00 | 9.4
[42 empty] | 1990-04-26 | 4:00 | 10
[42 empty] | 1990-04-26 | 5:00 | 10
[42 empty] | 1990-04-26 | 6:00 | 10
[42 empty] | 1990-04-26 | 7:00 | 10.6
[42 empty] | 1990-04-26 | 8:00 | 12.8
[42 empty] | 1990-04-26 | 9:00 | 15.6
[42 empty] | 1990-04-26 | 10:00 | 18.3
[42 empty] | 1990-04-26 | 11:00 | 20.6
[42 empty] | 1990-04-26 | 12:00 | 22.2
[42 empty] | 1990-04-26 | 13:00 | 22.2
[42 empty] | 1990-04-26 | 14:00 | 21.7
[42 empty] | 1990-04-26 | 15:00 | 20.6
[42 empty] | 1990-04-26 | 16:00 | 20.6
[42 empty] | 1990-04-26 | 17:00 | 18.9
[42 empty] | 1990-04-26 | 18:00 | 17.8
[42 empty] | 1990-04-26 | 19:00 | 15.6
[42 empty] | 1990-04-26 | 20:00 | 15.6
[42 empty] | 1990-04-26 | 21:00 | 14.4
[42 empty] | 1990-04-26 | 22:00 | 13.9
[42 empty] | 1990-04-26 | 23:00 | 13.3
[42 empty] | 1990-04-26 | 24:00 | 12.8
[42 empty] | 1990-04-27 | 1:00 | 12.2
[42 empty] | 1990-04-27 | 2:00 | 11.7
[42 empty] | 1990-04-27 | 3:00 | 11.1
[42 empty] | 1990-04-27 | 4:00 | 11.1
[42 empty] | 1990-04-27 | 5:00 | 11.1
[42 empty] | 1990-04-27 | 6:00 | 10
[42 empty] | 1990-04-27 | 7:00 | 11.7
[42 empty] | 1990-04-27 | 8:00 | 15
[42 empty] | 1990-04-27 | 9:00 | 18.3
[42 empty] | 1990-04-27 | 10:00 | 23.3
[42 empty] | 1990-04-27 | 11:00 | 26.1
[42 empty] | 1990-04-27 | 12:00 | 30
[42 empty] | 1990-04-27 | 13:00 | 31.1
[42 empty] | 1990-04-27 | 14:00 | 30.6
[42 empty] | 1990-04-27 | 15:00 | 31.1
[42 empty] | 1990-04-27 | 16:00 | 28.9
[42 empty] | 1990-04-27 | 17:00 | 26.7
[42 empty] | 1990-04-27 | 18:00 | 26.7
[42 empty] | 1990-04-27 | 19:00 | 27.2
[42 empty] | 1990-04-27 | 20:00 | 27.2
[42 empty] | 1990-04-27 | 21:00 | 26.7
[42 empty] | 1990-04-27 | 22:00 | 26.1
[42 empty] | 1990-04-27 | 23:00 | 25
[42 empty] | 1990-04-27 | 24:00 | 25
[42 empty] | 1990-04-28 | 1:00 | 24.4
[42 empty] | 1990-04-28 | 2:00 | 23.3
[42 empty] | 1990-04-28 | 3:00 | 20.6
[42 empty] | 1990-04-28 | 4:00 | 21.1
[42 empty] | 1990-04-28 | 5:00 | 18.9
[42 empty] | 1990-04-28 | 6:00 | 21.1
[42 empty] | 1990-04-28 | 7:00 | 20
[42 empty] | 1990-04-28 | 8:00 | 22.8
[42 empty] | 1990-04-28 | 9:00 | 25
[42 empty] | 1990-04-28 | 10:00 | 30.6
[42 empty] | 1990-04-28 | 11:00 | 30
[42 empty] | 1990-04-28 | 12:00 | 30.6
[42 empty] | 1990-04-28 | 13:00 | 30.6
[42 empty] | 1990-04-28 | 14:00 | 29.4
[42 empty] | 1990-04-28 | 15:00 | 28.3
[42 empty] | 1990-04-28 | 16:00 | 27.8
[42 empty] | 1990-04-28 | 17:00 | 26.7
[42 empty] | 1990-04-28 | 18:00 | 24.4
[42 empty] | 1990-04-28 | 19:00 | 23.3
[42 empty] | 1990-04-28 | 20:00 | 22.2
[42 empty] | 1990-04-28 | 21:00 | 21.1
[42 empty] | 1990-04-28 | 22:00 | 21.1
[42 empty] | 1990-04-28 | 23:00 | 21.1
[42 empty] | 1990-04-28 | 24:00 | 20.6
[42 empty] | 1990-04-29 | 1:00 | 17.8
[42 empty] | 1990-04-29 | 2:00 | 14.4
[42 empty] | 1990-04-29 | 3:00 | 13.3
[42 empty] | 1990-04-29 | 4:00 | 12.2
[42 empty] | 1990-04-29 | 5:00 | 11.1
[42 empty] | 1990-04-29 | 6:00 | 11.1
[42 empty] | 1990-04-29 | 7:00 | 11.1
[42 empty] | 1990-04-29 | 8:00 | 11.1
[42 empty] | 1990-04-29 | 9:00 | 10.6
[42 empty] | 1990-04-29 | 10:00 | 11.1
[42 empty] | 1990-04-29 | 11:00 | 11.7
[42 empty] | 1990-04-29 | 12:00 | 11.7
[42 empty] | 1990-04-29 | 13:00 | 12.2
[42 empty] | 1990-04-29 | 14:00 | 12.2
[42 empty] | 1990-04-29 | 15:00 | 12.2
[42 empty] | 1990-04-29 | 16:00 | 12.2
[42 empty] | 1990-04-29 | 17:00 | 12.2
[42 empty] | 1990-04-29 | 18:00 | 11.1
[42 empty] | 1990-04-29 | 19:00 | 10.6
[42 empty] | 1990-04-29 | 20:00 | 11.1
[42 empty] | 1990-04-29 | 21:00 | 10
[42 empty] | 1990-04-29 | 22:00 | 10.6
[42 empty] | 1990-04-29 | 23:00 | 10
[42 empty] | 1990-04-29 | 24:00 | 10
[42 empty] | 1990-04-30 | 1:00 | 10.6
[42 empty] | 1990-04-30 | 2:00 | 10
[42 empty] | 1990-04-30 | 3:00 | 10
[42 empty] | 1990-04-30 | 4:00 | 10
[42 empty] | 1990-04-30 | 5:00 | 10
[42 empty] | 1990-04-30 | 6:00 | 10.6
[42 empty] | 1990-04-30 | 7:00 | 10.6
[42 empty] | 1990-04-30 | 8:00 | 11.1
[42 empty] | 1990-04-30 | 9:00 | 11.7
[42 empty] | 1990-04-30 | 10:00 | 11.7
[42 empty] | 1990-04-30 | 11:00 | 11.7
[42 empty] | 1990-04-30 | 12:00 | 11.7
[42 empty] | 1990-04-30 | 13:00 | 11.7
[42 empty] | 1990-04-30 | 14:00 | 11.7
[42 empty] | 1990-04-30 | 15:00 | 11.7
[42 empty] | 1990-04-30 | 16:00 | 11.7
[42 empty] | 1990-04-30 | 17:00 | 11.1
[42 empty] | 1990-04-30 | 18:00 | 11.7
[42 empty] | 1990-04-30 | 19:00 | 11.7
[42 empty] | 1990-04-30 | 20:00 | 12.2
[42 empty] | 1990-04-30 | 21:00 | 12.8
[42 empty] | 1990-04-30 | 22:00 | 12
[42 empty] | 1990-04-30 | 23:00 | 11.2
[42 empty] | 1990-04-30 | 24:00 | 10.4
[42 empty] | 1987-05-01 | 1:00 | 9.6
[42 empty] | 1987-05-01 | 2:00 | 8.8
[42 empty] | 1987-05-01 | 3:00 | 8
[42 empty] | 1987-05-01 | 4:00 | 7.2
[42 empty] | 1987-05-01 | 5:00 | 7.8
[42 empty] | 1987-05-01 | 6:00 | 8.9
[42 empty] | 1987-05-01 | 7:00 | 8.9
[42 empty] | 1987-05-01 | 8:00 | 10
[42 empty] | 1987-05-01 | 9:00 | 11.1
[42 empty] | 1987-05-01 | 10:00 | 12.8
[42 empty] | 1987-05-01 | 11:00 | 13.9
[42 empty] | 1987-05-01 | 12:00 | 15.6
[42 empty] | 1987-05-01 | 13:00 | 16.1
[42 empty] | 1987-05-01 | 14:00 | 16.7
[42 empty] | 1987-05-01 | 15:00 | 17.2
[42 empty] | 1987-05-01 | 16:00 | 17.8
[42 empty] | 1987-05-01 | 17:00 | 18.3
[42 empty] | 1987-05-01 | 18:00 | 17.8
[42 empty] | 1987-05-01 | 19:00 | 17.2
[42 empty] | 1987-05-01 | 20:00 | 16.7
[42 empty] | 1987-05-01 | 21:00 | 16.1
[42 empty] | 1987-05-01 | 22:00 | 15.6
[42 empty] | 1987-05-01 | 23:00 | 15
[42 empty] | 1987-05-01 | 24:00 | 14.4
[42 empty] | 1987-05-02 | 1:00 | 13.3
[42 empty] | 1987-05-02 | 2:00 | 12.8
[42 empty] | 1987-05-02 | 3:00 | 12.2
[42 empty] | 1987-05-02 | 4:00 | 12.2
[42 empty] | 1987-05-02 | 5:00 | 12.2
[42 empty] | 1987-05-02 | 6:00 | 12.2
[42 empty] | 1987-05-02 | 7:00 | 12.8
[42 empty] | 1987-05-02 | 8:00 | 13.9
[42 empty] | 1987-05-02 | 9:00 | 15.6
[42 empty] | 1987-05-02 | 10:00 | 16.1
[42 empty] | 1987-05-02 | 11:00 | 16.7
[42 empty] | 1987-05-02 | 12:00 | 15.6
[42 empty] | 1987-05-02 | 13:00 | 16.1
[42 empty] | 1987-05-02 | 14:00 | 15.6
[42 empty] | 1987-05-02 | 15:00 | 15
[42 empty] | 1987-05-02 | 16:00 | 15
[42 empty] | 1987-05-02 | 17:00 | 16.1
[42 empty] | 1987-05-02 | 18:00 | 16.1
[42 empty] | 1987-05-02 | 19:00 | 16.1
[42 empty] | 1987-05-02 | 20:00 | 13.3
[42 empty] | 1987-05-02 | 21:00 | 12.8
[42 empty] | 1987-05-02 | 22:00 | 12.2
[42 empty] | 1987-05-02 | 23:00 | 11.7
[42 empty] | 1987-05-02 | 24:00 | 10.6
[42 empty] | 1987-05-03 | 1:00 | 11.1
[42 empty] | 1987-05-03 | 2:00 | 10.6
[42 empty] | 1987-05-03 | 3:00 | 10.6
[42 empty] | 1987-05-03 | 4:00 | 10.6
[42 empty] | 1987-05-03 | 5:00 | 10.6
[42 empty] | 1987-05-03 | 6:00 | 10.6
[42 empty] | 1987-05-03 | 7:00 | 11.1
[42 empty] | 1987-05-03 | 8:00 | 11.1
[42 empty] | 1987-05-03 | 9:00 | 11.7
[42 empty] | 1987-05-03 | 10:00 | 11.1
[42 empty] | 1987-05-03 | 11:00 | 12.2
[42 empty] | 1987-05-03 | 12:00 | 12.2
[42 empty] | 1987-05-03 | 13:00 | 12.8
[42 empty] | 1987-05-03 | 14:00 | 13.9
[42 empty] | 1987-05-03 | 15:00 | 12.8
[42 empty] | 1987-05-03 | 16:00 | 12.8
[42 empty] | 1987-05-03 | 17:00 | 10.6
[42 empty] | 1987-05-03 | 18:00 | 10
[42 empty] | 1987-05-03 | 19:00 | 10
[42 empty] | 1987-05-03 | 20:00 | 10
[42 empty] | 1987-05-03 | 21:00 | 10
[42 empty] | 1987-05-03 | 22:00 | 10
[42 empty] | 1987-05-03 | 23:00 | 9.4
[42 empty] | 1987-05-03 | 24:00 | 9.4
[42 empty] | 1987-05-04 | 1:00 | 9.4
[42 empty] | 1987-05-04 | 2:00 | 8.9
[42 empty] | 1987-05-04 | 3:00 | 8.9
[42 empty] | 1987-05-04 | 4:00 | 8.3
[42 empty] | 1987-05-04 | 5:00 | 8.3
[42 empty] | 1987-05-04 | 6:00 | 8.3
[42 empty] | 1987-05-04 | 7:00 | 8.3
[42 empty] | 1987-05-04 | 8:00 | 8.9
[42 empty] | 1987-05-04 | 9:00 | 9.4
[42 empty] | 1987-05-04 | 10:00 | 8.9
[42 empty] | 1987-05-04 | 11:00 | 8.9
[42 empty] | 1987-05-04 | 12:00 | 8.9
[42 empty] | 1987-05-04 | 13:00 | 8.9
[42 empty] | 1987-05-04 | 14:00 | 9.4
[42 empty] | 1987-05-04 | 15:00 | 9.4
[42 empty] | 1987-05-04 | 16:00 | 8.9
[42 empty] | 1987-05-04 | 17:00 | 8.9
[42 empty] | 1987-05-04 | 18:00 | 8.3
[42 empty] | 1987-05-04 | 19:00 | 7.8
[42 empty] | 1987-05-04 | 20:00 | 7.8
[42 empty] | 1987-05-04 | 21:00 | 7.2
[42 empty] | 1987-05-04 | 22:00 | 7.2
[42 empty] | 1987-05-04 | 23:00 | 7.2
[42 empty] | 1987-05-04 | 24:00 | 6.7
[42 empty] | 1987-05-05 | 1:00 | 7.2
[42 empty] | 1987-05-05 | 2:00 | 6.7
[42 empty] | 1987-05-05 | 3:00 | 7.2
[42 empty] | 1987-05-05 | 4:00 | 6.7
[42 empty] | 1987-05-05 | 5:00 | 7.2
[42 empty] | 1987-05-05 | 6:00 | 7.2
[42 empty] | 1987-05-05 | 7:00 | 7.2
[42 empty] | 1987-05-05 | 8:00 | 8.3
[42 empty] | 1987-05-05 | 9:00 | 8.9
[42 empty] | 1987-05-05 | 10:00 | 8.9
[42 empty] | 1987-05-05 | 11:00 | 9.4
[42 empty] | 1987-05-05 | 12:00 | 9.4
[42 empty] | 1987-05-05 | 13:00 | 10
[42 empty] | 1987-05-05 | 14:00 | 9.4
[42 empty] | 1987-05-05 | 15:00 | 8.9
[42 empty] | 1987-05-05 | 16:00 | 9.4
[42 empty] | 1987-05-05 | 17:00 | 9.4
[42 empty] | 1987-05-05 | 18:00 | 9.4
[42 empty] | 1987-05-05 | 19:00 | 8.9
[42 empty] | 1987-05-05 | 20:00 | 8.9
[42 empty] | 1987-05-05 | 21:00 | 8.9
[42 empty] | 1987-05-05 | 22:00 | 8.3
[42 empty] | 1987-05-05 | 23:00 | 8.9
[42 empty] | 1987-05-05 | 24:00 | 8.9
[42 empty] | 1987-05-06 | 1:00 | 8.9
[42 empty] | 1987-05-06 | 2:00 | 8.9
[42 empty] | 1987-05-06 | 3:00 | 8.9
[42 empty] | 1987-05-06 | 4:00 | 9.4
[42 empty] | 1987-05-06 | 5:00 | 8.9
[42 empty] | 1987-05-06 | 6:00 | 8.9
[42 empty] | 1987-05-06 | 7:00 | 9.4
[42 empty] | 1987-05-06 | 8:00 | 11.1
[42 empty] | 1987-05-06 | 9:00 | 11.7
[42 empty] | 1987-05-06 | 10:00 | 13.3
[42 empty] | 1987-05-06 | 11:00 | 12.8
[42 empty] | 1987-05-06 | 12:00 | 13.9
[42 empty] | 1987-05-06 | 13:00 | 13.9
[42 empty] | 1987-05-06 | 14:00 | 14.4
[42 empty] | 1987-05-06 | 15:00 | 15
[42 empty] | 1987-05-06 | 16:00 | 16.1
[42 empty] | 1987-05-06 | 17:00 | 15.6
[42 empty] | 1987-05-06 | 18:00 | 16.1
[42 empty] | 1987-05-06 | 19:00 | 13.9
[42 empty] | 1987-05-06 | 20:00 | 13.3
[42 empty] | 1987-05-06 | 21:00 | 12.8
[42 empty] | 1987-05-06 | 22:00 | 12.2
[42 empty] | 1987-05-06 | 23:00 | 10.6
[42 empty] | 1987-05-06 | 24:00 | 10
[42 empty] | 1987-05-07 | 1:00 | 9.4
[42 empty] | 1987-05-07 | 2:00 | 9.4
[42 empty] | 1987-05-07 | 3:00 | 9.4
[42 empty] | 1987-05-07 | 4:00 | 9.4
[42 empty] | 1987-05-07 | 5:00 | 9.4
[42 empty] | 1987-05-07 | 6:00 | 11.7
[42 empty] | 1987-05-07 | 7:00 | 14.4
[42 empty] | 1987-05-07 | 8:00 | 17.8
[42 empty] | 1987-05-07 | 9:00 | 20
[42 empty] | 1987-05-07 | 10:00 | 21.7
[42 empty] | 1987-05-07 | 11:00 | 22.8
[42 empty] | 1987-05-07 | 12:00 | 24.4
[42 empty] | 1987-05-07 | 13:00 | 25
[42 empty] | 1987-05-07 | 14:00 | 25
[42 empty] | 1987-05-07 | 15:00 | 25.6
[42 empty] | 1987-05-07 | 16:00 | 23.3
[42 empty] | 1987-05-07 | 17:00 | 22.2
[42 empty] | 1987-05-07 | 18:00 | 20.6
[42 empty] | 1987-05-07 | 19:00 | 20
[42 empty] | 1987-05-07 | 20:00 | 19.4
[42 empty] | 1987-05-07 | 21:00 | 18.9
[42 empty] | 1987-05-07 | 22:00 | 17.2
[42 empty] | 1987-05-07 | 23:00 | 14.4
[42 empty] | 1987-05-07 | 24:00 | 14.4
[42 empty] | 1987-05-08 | 1:00 | 15
[42 empty] | 1987-05-08 | 2:00 | 13.9
[42 empty] | 1987-05-08 | 3:00 | 13.3
[42 empty] | 1987-05-08 | 4:00 | 12.8
[42 empty] | 1987-05-08 | 5:00 | 12.8
[42 empty] | 1987-05-08 | 6:00 | 12.2
[42 empty] | 1987-05-08 | 7:00 | 12.8
[42 empty] | 1987-05-08 | 8:00 | 12.2
[42 empty] | 1987-05-08 | 9:00 | 13.3
[42 empty] | 1987-05-08 | 10:00 | 14.4
[42 empty] | 1987-05-08 | 11:00 | 15.6
[42 empty] | 1987-05-08 | 12:00 | 17.8
[42 empty] | 1987-05-08 | 13:00 | 17.8
[42 empty] | 1987-05-08 | 14:00 | 17.8
[42 empty] | 1987-05-08 | 15:00 | 18.9
[42 empty] | 1987-05-08 | 16:00 | 18.9
[42 empty] | 1987-05-08 | 17:00 | 16.1
[42 empty] | 1987-05-08 | 18:00 | 14.4
[42 empty] | 1987-05-08 | 19:00 | 12.8
[42 empty] | 1987-05-08 | 20:00 | 11.7
[42 empty] | 1987-05-08 | 21:00 | 11.1
[42 empty] | 1987-05-08 | 22:00 | 11.1
[42 empty] | 1987-05-08 | 23:00 | 11.1
[42 empty] | 1987-05-08 | 24:00 | 10.6
[42 empty] | 1987-05-09 | 1:00 | 10.6
[42 empty] | 1987-05-09 | 2:00 | 10.6
[42 empty] | 1987-05-09 | 3:00 | 10
[42 empty] | 1987-05-09 | 4:00 | 10
[42 empty] | 1987-05-09 | 5:00 | 10
[42 empty] | 1987-05-09 | 6:00 | 10.6
[42 empty] | 1987-05-09 | 7:00 | 12.8
[42 empty] | 1987-05-09 | 8:00 | 16.1
[42 empty] | 1987-05-09 | 9:00 | 18.3
[42 empty] | 1987-05-09 | 10:00 | 20
[42 empty] | 1987-05-09 | 11:00 | 20.6
[42 empty] | 1987-05-09 | 12:00 | 22.2
[42 empty] | 1987-05-09 | 13:00 | 23.3
[42 empty] | 1987-05-09 | 14:00 | 23.3
[42 empty] | 1987-05-09 | 15:00 | 23.9
[42 empty] | 1987-05-09 | 16:00 | 25
[42 empty] | 1987-05-09 | 17:00 | 24.4
[42 empty] | 1987-05-09 | 18:00 | 24.4
[42 empty] | 1987-05-09 | 19:00 | 22.8
[42 empty] | 1987-05-09 | 20:00 | 22.2
[42 empty] | 1987-05-09 | 21:00 | 21.7
[42 empty] | 1987-05-09 | 22:00 | 20.6
[42 empty] | 1987-05-09 | 23:00 | 19.4
[42 empty] | 1987-05-09 | 24:00 | 19.4
[42 empty] | 1987-05-10 | 1:00 | 18.9
[42 empty] | 1987-05-10 | 2:00 | 18.9
[42 empty] | 1987-05-10 | 3:00 | 17.8
[42 empty] | 1987-05-10 | 4:00 | 17.2
[42 empty] | 1987-05-10 | 5:00 | 16.7
[42 empty] | 1987-05-10 | 6:00 | 16.7
[42 empty] | 1987-05-10 | 7:00 | 18.9
[42 empty] | 1987-05-10 | 8:00 | 22.2
[42 empty] | 1987-05-10 | 9:00 | 23.3
[42 empty] | 1987-05-10 | 10:00 | 25.6
[42 empty] | 1987-05-10 | 11:00 | 27.8
[42 empty] | 1987-05-10 | 12:00 | 28.3
[42 empty] | 1987-05-10 | 13:00 | 30
[42 empty] | 1987-05-10 | 14:00 | 30.6
[42 empty] | 1987-05-10 | 15:00 | 30
[42 empty] | 1987-05-10 | 16:00 | 28.9
[42 empty] | 1987-05-10 | 17:00 | 27.2
[42 empty] | 1987-05-10 | 18:00 | 27.2
[42 empty] | 1987-05-10 | 19:00 | 26.1
[42 empty] | 1987-05-10 | 20:00 | 23.9
[42 empty] | 1987-05-10 | 21:00 | 23.9
[42 empty] | 1987-05-10 | 22:00 | 21.7
[42 empty] | 1987-05-10 | 23:00 | 20
[42 empty] | 1987-05-10 | 24:00 | 20
[42 empty] | 1987-05-11 | 1:00 | 19.4
[42 empty] | 1987-05-11 | 2:00 | 18.3
[42 empty] | 1987-05-11 | 3:00 | 17.2
[42 empty] | 1987-05-11 | 4:00 | 17.2
[42 empty] | 1987-05-11 | 5:00 | 15.6
[42 empty] | 1987-05-11 | 6:00 | 16.1
[42 empty] | 1987-05-11 | 7:00 | 18.9
[42 empty] | 1987-05-11 | 8:00 | 21.7
[42 empty] | 1987-05-11 | 9:00 | 22.2
[42 empty] | 1987-05-11 | 10:00 | 21.7
[42 empty] | 1987-05-11 | 11:00 | 22.2
[42 empty] | 1987-05-11 | 12:00 | 22.8
[42 empty] | 1987-05-11 | 13:00 | 23.3
[42 empty] | 1987-05-11 | 14:00 | 23.9
[42 empty] | 1987-05-11 | 15:00 | 23.9
[42 empty] | 1987-05-11 | 16:00 | 23.3
[42 empty] | 1987-05-11 | 17:00 | 22.2
[42 empty] | 1987-05-11 | 18:00 | 21.1
[42 empty] | 1987-05-11 | 19:00 | 20
[42 empty] | 1987-05-11 | 20:00 | 18.3
[42 empty] | 1987-05-11 | 21:00 | 17.2
[42 empty] | 1987-05-11 | 22:00 | 16.7
[42 empty] | 1987-05-11 | 23:00 | 16.1
[42 empty] | 1987-05-11 | 24:00 | 16.1
[42 empty] | 1987-05-12 | 1:00 | 13.9
[42 empty] | 1987-05-12 | 2:00 | 13.9
[42 empty] | 1987-05-12 | 3:00 | 14.4
[42 empty] | 1987-05-12 | 4:00 | 17.8
[42 empty] | 1987-05-12 | 5:00 | 18.3
[42 empty] | 1987-05-12 | 6:00 | 20
[42 empty] | 1987-05-12 | 7:00 | 21.1
[42 empty] | 1987-05-12 | 8:00 | 22.8
[42 empty] | 1987-05-12 | 9:00 | 25
[42 empty] | 1987-05-12 | 10:00 | 26.7
[42 empty] | 1987-05-12 | 11:00 | 27.8
[42 empty] | 1987-05-12 | 12:00 | 27.8
[42 empty] | 1987-05-12 | 13:00 | 28.9
[42 empty] | 1987-05-12 | 14:00 | 26.7
[42 empty] | 1987-05-12 | 15:00 | 24.4
[42 empty] | 1987-05-12 | 16:00 | 21.7
[42 empty] | 1987-05-12 | 17:00 | 19.4
[42 empty] | 1987-05-12 | 18:00 | 18.9
[42 empty] | 1987-05-12 | 19:00 | 18.9
[42 empty] | 1987-05-12 | 20:00 | 18.3
[42 empty] | 1987-05-12 | 21:00 | 17.8
[42 empty] | 1987-05-12 | 22:00 | 17.8
[42 empty] | 1987-05-12 | 23:00 | 17.2
[42 empty] | 1987-05-12 | 24:00 | 16.1
[42 empty] | 1987-05-13 | 1:00 | 16.1
[42 empty] | 1987-05-13 | 2:00 | 14.4
[42 empty] | 1987-05-13 | 3:00 | 13.3
[42 empty] | 1987-05-13 | 4:00 | 12.2
[42 empty] | 1987-05-13 | 5:00 | 11.1
[42 empty] | 1987-05-13 | 6:00 | 11.7
[42 empty] | 1987-05-13 | 7:00 | 12.8
[42 empty] | 1987-05-13 | 8:00 | 13.9
[42 empty] | 1987-05-13 | 9:00 | 15
[42 empty] | 1987-05-13 | 10:00 | 15
[42 empty] | 1987-05-13 | 11:00 | 15.6
[42 empty] | 1987-05-13 | 12:00 | 16.7
[42 empty] | 1987-05-13 | 13:00 | 17.2
[42 empty] | 1987-05-13 | 14:00 | 17.8
[42 empty] | 1987-05-13 | 15:00 | 17.8
[42 empty] | 1987-05-13 | 16:00 | 17.2
[42 empty] | 1987-05-13 | 17:00 | 16.1
[42 empty] | 1987-05-13 | 18:00 | 14.4
[42 empty] | 1987-05-13 | 19:00 | 13.3
[42 empty] | 1987-05-13 | 20:00 | 12.2
[42 empty] | 1987-05-13 | 21:00 | 10.6
[42 empty] | 1987-05-13 | 22:00 | 10
[42 empty] | 1987-05-13 | 23:00 | 9.4
[42 empty] | 1987-05-13 | 24:00 | 9.4
[42 empty] | 1987-05-14 | 1:00 | 8.3
[42 empty] | 1987-05-14 | 2:00 | 8.3
[42 empty] | 1987-05-14 | 3:00 | 7.8
[42 empty] | 1987-05-14 | 4:00 | 7.2
[42 empty] | 1987-05-14 | 5:00 | 7.2
[42 empty] | 1987-05-14 | 6:00 | 8.3
[42 empty] | 1987-05-14 | 7:00 | 10
[42 empty] | 1987-05-14 | 8:00 | 11.7
[42 empty] | 1987-05-14 | 9:00 | 13.9
[42 empty] | 1987-05-14 | 10:00 | 15
[42 empty] | 1987-05-14 | 11:00 | 17.8
[42 empty] | 1987-05-14 | 12:00 | 18.9
[42 empty] | 1987-05-14 | 13:00 | 18.9
[42 empty] | 1987-05-14 | 14:00 | 19.4
[42 empty] | 1987-05-14 | 15:00 | 20
[42 empty] | 1987-05-14 | 16:00 | 18.3
[42 empty] | 1987-05-14 | 17:00 | 17.2
[42 empty] | 1987-05-14 | 18:00 | 16.1
[42 empty] | 1987-05-14 | 19:00 | 14.4
[42 empty] | 1987-05-14 | 20:00 | 13.3
[42 empty] | 1987-05-14 | 21:00 | 13.3
[42 empty] | 1987-05-14 | 22:00 | 13.3
[42 empty] | 1987-05-14 | 23:00 | 12.8
[42 empty] | 1987-05-14 | 24:00 | 13.3
[42 empty] | 1987-05-15 | 1:00 | 14.4
[42 empty] | 1987-05-15 | 2:00 | 16.7
[42 empty] | 1987-05-15 | 3:00 | 16.7
[42 empty] | 1987-05-15 | 4:00 | 16.1
[42 empty] | 1987-05-15 | 5:00 | 16.1
[42 empty] | 1987-05-15 | 6:00 | 15.6
[42 empty] | 1987-05-15 | 7:00 | 16.1
[42 empty] | 1987-05-15 | 8:00 | 16.7
[42 empty] | 1987-05-15 | 9:00 | 16.7
[42 empty] | 1987-05-15 | 10:00 | 17.2
[42 empty] | 1987-05-15 | 11:00 | 17.8
[42 empty] | 1987-05-15 | 12:00 | 20
[42 empty] | 1987-05-15 | 13:00 | 20
[42 empty] | 1987-05-15 | 14:00 | 22.2
[42 empty] | 1987-05-15 | 15:00 | 22.8
[42 empty] | 1987-05-15 | 16:00 | 22.8
[42 empty] | 1987-05-15 | 17:00 | 21.7
[42 empty] | 1987-05-15 | 18:00 | 20.6
[42 empty] | 1987-05-15 | 19:00 | 19.4
[42 empty] | 1987-05-15 | 20:00 | 18.3
[42 empty] | 1987-05-15 | 21:00 | 17.2
[42 empty] | 1987-05-15 | 22:00 | 15.6
[42 empty] | 1987-05-15 | 23:00 | 14.4
[42 empty] | 1987-05-15 | 24:00 | 13.3
[42 empty] | 1987-05-16 | 1:00 | 12.2
[42 empty] | 1987-05-16 | 2:00 | 11.1
[42 empty] | 1987-05-16 | 3:00 | 10.6
[42 empty] | 1987-05-16 | 4:00 | 9.4
[42 empty] | 1987-05-16 | 5:00 | 8.9
[42 empty] | 1987-05-16 | 6:00 | 9.4
[42 empty] | 1987-05-16 | 7:00 | 10.6
[42 empty] | 1987-05-16 | 8:00 | 11.7
[42 empty] | 1987-05-16 | 9:00 | 12.8
[42 empty] | 1987-05-16 | 10:00 | 13.9
[42 empty] | 1987-05-16 | 11:00 | 16.1
[42 empty] | 1987-05-16 | 12:00 | 17.2
[42 empty] | 1987-05-16 | 13:00 | 18.3
[42 empty] | 1987-05-16 | 14:00 | 19.4
[42 empty] | 1987-05-16 | 15:00 | 20.6
[42 empty] | 1987-05-16 | 16:00 | 21.1
[42 empty] | 1987-05-16 | 17:00 | 20
[42 empty] | 1987-05-16 | 18:00 | 17.2
[42 empty] | 1987-05-16 | 19:00 | 15.6
[42 empty] | 1987-05-16 | 20:00 | 15.6
[42 empty] | 1987-05-16 | 21:00 | 16.7
[42 empty] | 1987-05-16 | 22:00 | 16.1
[42 empty] | 1987-05-16 | 23:00 | 16.7
[42 empty] | 1987-05-16 | 24:00 | 16.7
[42 empty] | 1987-05-17 | 1:00 | 16.7
[42 empty] | 1987-05-17 | 2:00 | 15.6
[42 empty] | 1987-05-17 | 3:00 | 15.6
[42 empty] | 1987-05-17 | 4:00 | 15
[42 empty] | 1987-05-17 | 5:00 | 15.6
[42 empty] | 1987-05-17 | 6:00 | 16.1
[42 empty] | 1987-05-17 | 7:00 | 17.2
[42 empty] | 1987-05-17 | 8:00 | 18.9
[42 empty] | 1987-05-17 | 9:00 | 20.6
[42 empty] | 1987-05-17 | 10:00 | 21.7
[42 empty] | 1987-05-17 | 11:00 | 26.1
[42 empty] | 1987-05-17 | 12:00 | 26.7
[42 empty] | 1987-05-17 | 13:00 | 28.3
[42 empty] | 1987-05-17 | 14:00 | 29.4
[42 empty] | 1987-05-17 | 15:00 | 30
[42 empty] | 1987-05-17 | 16:00 | 30
[42 empty] | 1987-05-17 | 17:00 | 29.4
[42 empty] | 1987-05-17 | 18:00 | 29.4
[42 empty] | 1987-05-17 | 19:00 | 27.8
[42 empty] | 1987-05-17 | 20:00 | 26.7
[42 empty] | 1987-05-17 | 21:00 | 25.6
[42 empty] | 1987-05-17 | 22:00 | 25
[42 empty] | 1987-05-17 | 23:00 | 24.4
[42 empty] | 1987-05-17 | 24:00 | 23.3
[42 empty] | 1987-05-18 | 1:00 | 23.3
[42 empty] | 1987-05-18 | 2:00 | 22.2
[42 empty] | 1987-05-18 | 3:00 | 18.9
[42 empty] | 1987-05-18 | 4:00 | 18.3
[42 empty] | 1987-05-18 | 5:00 | 16.7
[42 empty] | 1987-05-18 | 6:00 | 19.4
[42 empty] | 1987-05-18 | 7:00 | 19.4
[42 empty] | 1987-05-18 | 8:00 | 21.1
[42 empty] | 1987-05-18 | 9:00 | 22.2
[42 empty] | 1987-05-18 | 10:00 | 21.1
[42 empty] | 1987-05-18 | 11:00 | 22.2
[42 empty] | 1987-05-18 | 12:00 | 21.7
[42 empty] | 1987-05-18 | 13:00 | 22.8
[42 empty] | 1987-05-18 | 14:00 | 23.3
[42 empty] | 1987-05-18 | 15:00 | 25.6
[42 empty] | 1987-05-18 | 16:00 | 22.8
[42 empty] | 1987-05-18 | 17:00 | 20
[42 empty] | 1987-05-18 | 18:00 | 16.7
[42 empty] | 1987-05-18 | 19:00 | 16.7
[42 empty] | 1987-05-18 | 20:00 | 15.6
[42 empty] | 1987-05-18 | 21:00 | 14.4
[42 empty] | 1987-05-18 | 22:00 | 13.9
[42 empty] | 1987-05-18 | 23:00 | 12.8
[42 empty] | 1987-05-18 | 24:00 | 12.8
[42 empty] | 1987-05-19 | 1:00 | 11.7
[42 empty] | 1987-05-19 | 2:00 | 11.7
[42 empty] | 1987-05-19 | 3:00 | 11.1
[42 empty] | 1987-05-19 | 4:00 | 11.7
[42 empty] | 1987-05-19 | 5:00 | 11.1
[42 empty] | 1987-05-19 | 6:00 | 11.1
[42 empty] | 1987-05-19 | 7:00 | 11.1
[42 empty] | 1987-05-19 | 8:00 | 12.2
[42 empty] | 1987-05-19 | 9:00 | 12.2
[42 empty] | 1987-05-19 | 10:00 | 12.8
[42 empty] | 1987-05-19 | 11:00 | 12.8
[42 empty] | 1987-05-19 | 12:00 | 13.3
[42 empty] | 1987-05-19 | 13:00 | 13.3
[42 empty] | 1987-05-19 | 14:00 | 13.3
[42 empty] | 1987-05-19 | 15:00 | 13.3
[42 empty] | 1987-05-19 | 16:00 | 13.3
[42 empty] | 1987-05-19 | 17:00 | 13.3
[42 empty] | 1987-05-19 | 18:00 | 13.3
[42 empty] | 1987-05-19 | 19:00 | 13.3
[42 empty] | 1987-05-19 | 20:00 | 13.3
[42 empty] | 1987-05-19 | 21:00 | 13.3
[42 empty] | 1987-05-19 | 22:00 | 13.3
[42 empty] | 1987-05-19 | 23:00 | 12.8
[42 empty] | 1987-05-19 | 24:00 | 12.8
[42 empty] | 1987-05-20 | 1:00 | 12.8
[42 empty] | 1987-05-20 | 2:00 | 12.2
[42 empty] | 1987-05-20 | 3:00 | 12.2
[42 empty] | 1987-05-20 | 4:00 | 11.7
[42 empty] | 1987-05-20 | 5:00 | 11.7
[42 empty] | 1987-05-20 | 6:00 | 11.1
[42 empty] | 1987-05-20 | 7:00 | 12.2
[42 empty] | 1987-05-20 | 8:00 | 11.7
[42 empty] | 1987-05-20 | 9:00 | 11.7
[42 empty] | 1987-05-20 | 10:00 | 11.7
[42 empty] | 1987-05-20 | 11:00 | 11.7
[42 empty] | 1987-05-20 | 12:00 | 11.1
[42 empty] | 1987-05-20 | 13:00 | 11.1
[42 empty] | 1987-05-20 | 14:00 | 11.1
[42 empty] | 1987-05-20 | 15:00 | 11.1
[42 empty] | 1987-05-20 | 16:00 | 11.7
[42 empty] | 1987-05-20 | 17:00 | 11.7
[42 empty] | 1987-05-20 | 18:00 | 12.2
[42 empty] | 1987-05-20 | 19:00 | 11.7
[42 empty] | 1987-05-20 | 20:00 | 11.7
[42 empty] | 1987-05-20 | 21:00 | 11.7
[42 empty] | 1987-05-20 | 22:00 | 11.7
[42 empty] | 1987-05-20 | 23:00 | 11.7
[42 empty] | 1987-05-20 | 24:00 | 11.1
[42 empty] | 1987-05-21 | 1:00 | 11.7
[42 empty] | 1987-05-21 | 2:00 | 11.7
[42 empty] | 1987-05-21 | 3:00 | 11.7
[42 empty] | 1987-05-21 | 4:00 | 11.7
[42 empty] | 1987-05-21 | 5:00 | 11.7
[42 empty] | 1987-05-21 | 6:00 | 12.2
[42 empty] | 1987-05-21 | 7:00 | 12.8
[42 empty] | 1987-05-21 | 8:00 | 13.9
[42 empty] | 1987-05-21 | 9:00 | 15
[42 empty] | 1987-05-21 | 10:00 | 15
[42 empty] | 1987-05-21 | 11:00 | 16.7
[42 empty] | 1987-05-21 | 12:00 | 16.1
[42 empty] | 1987-05-21 | 13:00 | 17.8
[42 empty] | 1987-05-21 | 14:00 | 19.4
[42 empty] | 1987-05-21 | 15:00 | 22.2
[42 empty] | 1987-05-21 | 16:00 | 21.7
[42 empty] | 1987-05-21 | 17:00 | 21.1
[42 empty] | 1987-05-21 | 18:00 | 19.4
[42 empty] | 1987-05-21 | 19:00 | 18.3
[42 empty] | 1987-05-21 | 20:00 | 16.7
[42 empty] | 1987-05-21 | 21:00 | 16.7
[42 empty] | 1987-05-21 | 22:00 | 16.1
[42 empty] | 1987-05-21 | 23:00 | 15.6
[42 empty] | 1987-05-21 | 24:00 | 15.6
[42 empty] | 1987-05-22 | 1:00 | 15
[42 empty] | 1987-05-22 | 2:00 | 14.4
[42 empty] | 1987-05-22 | 3:00 | 14.4
[42 empty] | 1987-05-22 | 4:00 | 14.4
[42 empty] | 1987-05-22 | 5:00 | 14.4
[42 empty] | 1987-05-22 | 6:00 | 15.6
[42 empty] | 1987-05-22 | 7:00 | 15.6
[42 empty] | 1987-05-22 | 8:00 | 18.9
[42 empty] | 1987-05-22 | 9:00 | 19.4
[42 empty] | 1987-05-22 | 10:00 | 20.6
[42 empty] | 1987-05-22 | 11:00 | 22.2
[42 empty] | 1987-05-22 | 12:00 | 23.3
[42 empty] | 1987-05-22 | 13:00 | 24.4
[42 empty] | 1987-05-22 | 14:00 | 23.9
[42 empty] | 1987-05-22 | 15:00 | 24.4
[42 empty] | 1987-05-22 | 16:00 | 25
[42 empty] | 1987-05-22 | 17:00 | 23.3
[42 empty] | 1987-05-22 | 18:00 | 23.3
[42 empty] | 1987-05-22 | 19:00 | 22.8
[42 empty] | 1987-05-22 | 20:00 | 21.7
[42 empty] | 1987-05-22 | 21:00 | 21.7
[42 empty] | 1987-05-22 | 22:00 | 21.7
[42 empty] | 1987-05-22 | 23:00 | 21.7
[42 empty] | 1987-05-22 | 24:00 | 21.1
[42 empty] | 1987-05-23 | 1:00 | 21.1
[42 empty] | 1987-05-23 | 2:00 | 20.6
[42 empty] | 1987-05-23 | 3:00 | 20.6
[42 empty] | 1987-05-23 | 4:00 | 20.6
[42 empty] | 1987-05-23 | 5:00 | 20.6
[42 empty] | 1987-05-23 | 6:00 | 21.1
[42 empty] | 1987-05-23 | 7:00 | 21.7
[42 empty] | 1987-05-23 | 8:00 | 22.8
[42 empty] | 1987-05-23 | 9:00 | 22.2
[42 empty] | 1987-05-23 | 10:00 | 21.7
[42 empty] | 1987-05-23 | 11:00 | 22.8
[42 empty] | 1987-05-23 | 12:00 | 22.8
[42 empty] | 1987-05-23 | 13:00 | 23.9
[42 empty] | 1987-05-23 | 14:00 | 25
[42 empty] | 1987-05-23 | 15:00 | 25.6
[42 empty] | 1987-05-23 | 16:00 | 26.1
[42 empty] | 1987-05-23 | 17:00 | 24.4
[42 empty] | 1987-05-23 | 18:00 | 23.3
[42 empty] | 1987-05-23 | 19:00 | 19.4
[42 empty] | 1987-05-23 | 20:00 | 16.1
[42 empty] | 1987-05-23 | 21:00 | 15.6
[42 empty] | 1987-05-23 | 22:00 | 14.4
[42 empty] | 1987-05-23 | 23:00 | 13.9
[42 empty] | 1987-05-23 | 24:00 | 13.3
[42 empty] | 1987-05-24 | 1:00 | 12.8
[42 empty] | 1987-05-24 | 2:00 | 12.8
[42 empty] | 1987-05-24 | 3:00 | 12.8
[42 empty] | 1987-05-24 | 4:00 | 12.2
[42 empty] | 1987-05-24 | 5:00 | 12.2
[42 empty] | 1987-05-24 | 6:00 | 12.2
[42 empty] | 1987-05-24 | 7:00 | 13.3
[42 empty] | 1987-05-24 | 8:00 | 14.4
[42 empty] | 1987-05-24 | 9:00 | 15
[42 empty] | 1987-05-24 | 10:00 | 17.8
[42 empty] | 1987-05-24 | 11:00 | 21.1
[42 empty] | 1987-05-24 | 12:00 | 22.2
[42 empty] | 1987-05-24 | 13:00 | 21.7
[42 empty] | 1987-05-24 | 14:00 | 23.9
[42 empty] | 1987-05-24 | 15:00 | 22.2
[42 empty] | 1987-05-24 | 16:00 | 21.7
[42 empty] | 1987-05-24 | 17:00 | 19.4
[42 empty] | 1987-05-24 | 18:00 | 17.8
[42 empty] | 1987-05-24 | 19:00 | 16.7
[42 empty] | 1987-05-24 | 20:00 | 16.1
[42 empty] | 1987-05-24 | 21:00 | 15
[42 empty] | 1987-05-24 | 22:00 | 14.4
[42 empty] | 1987-05-24 | 23:00 | 13.9
[42 empty] | 1987-05-24 | 24:00 | 12.8
[42 empty] | 1987-05-25 | 1:00 | 12.8
[42 empty] | 1987-05-25 | 2:00 | 12.2
[42 empty] | 1987-05-25 | 3:00 | 12.2
[42 empty] | 1987-05-25 | 4:00 | 12.2
[42 empty] | 1987-05-25 | 5:00 | 12.2
[42 empty] | 1987-05-25 | 6:00 | 12.2
[42 empty] | 1987-05-25 | 7:00 | 12.8
[42 empty] | 1987-05-25 | 8:00 | 13.9
[42 empty] | 1987-05-25 | 9:00 | 15
[42 empty] | 1987-05-25 | 10:00 | 17.2
[42 empty] | 1987-05-25 | 11:00 | 17.8
[42 empty] | 1987-05-25 | 12:00 | 16.7
[42 empty] | 1987-05-25 | 13:00 | 16.7
[42 empty] | 1987-05-25 | 14:00 | 15.6
[42 empty] | 1987-05-25 | 15:00 | 15.6
[42 empty] | 1987-05-25 | 16:00 | 16.1
[42 empty] | 1987-05-25 | 17:00 | 15
[42 empty] | 1987-05-25 | 18:00 | 14.4
[42 empty] | 1987-05-25 | 19:00 | 13.9
[42 empty] | 1987-05-25 | 20:00 | 13.3
[42 empty] | 1987-05-25 | 21:00 | 12.8
[42 empty] | 1987-05-25 | 22:00 | 13.3
[42 empty] | 1987-05-25 | 23:00 | 12.8
[42 empty] | 1987-05-25 | 24:00 | 12.8
[42 empty] | 1987-05-26 | 1:00 | 12.2
[42 empty] | 1987-05-26 | 2:00 | 12.8
[42 empty] | 1987-05-26 | 3:00 | 12.8
[42 empty] | 1987-05-26 | 4:00 | 12.8
[42 empty] | 1987-05-26 | 5:00 | 13.3
[42 empty] | 1987-05-26 | 6:00 | 13.9
[42 empty] | 1987-05-26 | 7:00 | 13.9
[42 empty] | 1987-05-26 | 8:00 | 15
[42 empty] | 1987-05-26 | 9:00 | 16.1
[42 empty] | 1987-05-26 | 10:00 | 16.7
[42 empty] | 1987-05-26 | 11:00 | 16.7
[42 empty] | 1987-05-26 | 12:00 | 16.7
[42 empty] | 1987-05-26 | 13:00 | 16.7
[42 empty] | 1987-05-26 | 14:00 | 16.7
[42 empty] | 1987-05-26 | 15:00 | 16.7
[42 empty] | 1987-05-26 | 16:00 | 17.2
[42 empty] | 1987-05-26 | 17:00 | 16.7
[42 empty] | 1987-05-26 | 18:00 | 15.6
[42 empty] | 1987-05-26 | 19:00 | 15
[42 empty] | 1987-05-26 | 20:00 | 14.4
[42 empty] | 1987-05-26 | 21:00 | 14.4
[42 empty] | 1987-05-26 | 22:00 | 14.4
[42 empty] | 1987-05-26 | 23:00 | 14.4
[42 empty] | 1987-05-26 | 24:00 | 14.4
[42 empty] | 1987-05-27 | 1:00 | 13.9
[42 empty] | 1987-05-27 | 2:00 | 13.9
[42 empty] | 1987-05-27 | 3:00 | 13.9
[42 empty] | 1987-05-27 | 4:00 | 13.3
[42 empty] | 1987-05-27 | 5:00 | 13.3
[42 empty] | 1987-05-27 | 6:00 | 13.3
[42 empty] | 1987-05-27 | 7:00 | 13.9
[42 empty] | 1987-05-27 | 8:00 | 12.8
[42 empty] | 1987-05-27 | 9:00 | 12.8
[42 empty] | 1987-05-27 | 10:00 | 11.7
[42 empty] | 1987-05-27 | 11:00 | 11.7
[42 empty] | 1987-05-27 | 12:00 | 12.8
[42 empty] | 1987-05-27 | 13:00 | 13.9
[42 empty] | 1987-05-27 | 14:00 | 13.3
[42 empty] | 1987-05-27 | 15:00 | 14.4
[42 empty] | 1987-05-27 | 16:00 | 15
[42 empty] | 1987-05-27 | 17:00 | 16.1
[42 empty] | 1987-05-27 | 18:00 | 15
[42 empty] | 1987-05-27 | 19:00 | 15
[42 empty] | 1987-05-27 | 20:00 | 14.4
[42 empty] | 1987-05-27 | 21:00 | 13.9
[42 empty] | 1987-05-27 | 22:00 | 13.9
[42 empty] | 1987-05-27 | 23:00 | 13.9
[42 empty] | 1987-05-27 | 24:00 | 14.4
[42 empty] | 1987-05-28 | 1:00 | 14.4
[42 empty] | 1987-05-28 | 2:00 | 15
[42 empty] | 1987-05-28 | 3:00 | 15
[42 empty] | 1987-05-28 | 4:00 | 15.6
[42 empty] | 1987-05-28 | 5:00 | 16.1
[42 empty] | 1987-05-28 | 6:00 | 16.7
[42 empty] | 1987-05-28 | 7:00 | 17.8
[42 empty] | 1987-05-28 | 8:00 | 18.9
[42 empty] | 1987-05-28 | 9:00 | 20.6
[42 empty] | 1987-05-28 | 10:00 | 22.2
[42 empty] | 1987-05-28 | 11:00 | 25.6
[42 empty] | 1987-05-28 | 12:00 | 26.1
[42 empty] | 1987-05-28 | 13:00 | 28.3
[42 empty] | 1987-05-28 | 14:00 | 28.9
[42 empty] | 1987-05-28 | 15:00 | 30
[42 empty] | 1987-05-28 | 16:00 | 30
[42 empty] | 1987-05-28 | 17:00 | 29.4
[42 empty] | 1987-05-28 | 18:00 | 28.9
[42 empty] | 1987-05-28 | 19:00 | 27.8
[42 empty] | 1987-05-28 | 20:00 | 26.7
[42 empty] | 1987-05-28 | 21:00 | 26.1
[42 empty] | 1987-05-28 | 22:00 | 26.1
[42 empty] | 1987-05-28 | 23:00 | 25.6
[42 empty] | 1987-05-28 | 24:00 | 25
[42 empty] | 1987-05-29 | 1:00 | 21.7
[42 empty] | 1987-05-29 | 2:00 | 24.4
[42 empty] | 1987-05-29 | 3:00 | 23.3
[42 empty] | 1987-05-29 | 4:00 | 22.2
[42 empty] | 1987-05-29 | 5:00 | 22.2
[42 empty] | 1987-05-29 | 6:00 | 23.3
[42 empty] | 1987-05-29 | 7:00 | 24.4
[42 empty] | 1987-05-29 | 8:00 | 27.2
[42 empty] | 1987-05-29 | 9:00 | 28.3
[42 empty] | 1987-05-29 | 10:00 | 31.1
[42 empty] | 1987-05-29 | 11:00 | 32.2
[42 empty] | 1987-05-29 | 12:00 | 32.8
[42 empty] | 1987-05-29 | 13:00 | 33.9
[42 empty] | 1987-05-29 | 14:00 | 34.4
[42 empty] | 1987-05-29 | 15:00 | 33.9
[42 empty] | 1987-05-29 | 16:00 | 32.2
[42 empty] | 1987-05-29 | 17:00 | 31.7
[42 empty] | 1987-05-29 | 18:00 | 29.4
[42 empty] | 1987-05-29 | 19:00 | 26.7
[42 empty] | 1987-05-29 | 20:00 | 27.2
[42 empty] | 1987-05-29 | 21:00 | 24.4
[42 empty] | 1987-05-29 | 22:00 | 26.1
[42 empty] | 1987-05-29 | 23:00 | 26.7
[42 empty] | 1987-05-29 | 24:00 | 22.8
[42 empty] | 1987-05-30 | 1:00 | 22.8
[42 empty] | 1987-05-30 | 2:00 | 23.3
[42 empty] | 1987-05-30 | 3:00 | 22.8
[42 empty] | 1987-05-30 | 4:00 | 22.2
[42 empty] | 1987-05-30 | 5:00 | 22.8
[42 empty] | 1987-05-30 | 6:00 | 23.3
[42 empty] | 1987-05-30 | 7:00 | 25.6
[42 empty] | 1987-05-30 | 8:00 | 27.8
[42 empty] | 1987-05-30 | 9:00 | 30
[42 empty] | 1987-05-30 | 10:00 | 32.2
[42 empty] | 1987-05-30 | 11:00 | 33.3
[42 empty] | 1987-05-30 | 12:00 | 34.4
[42 empty] | 1987-05-30 | 13:00 | 35
[42 empty] | 1987-05-30 | 14:00 | 33.9
[42 empty] | 1987-05-30 | 15:00 | 33.9
[42 empty] | 1987-05-30 | 16:00 | 35
[42 empty] | 1987-05-30 | 17:00 | 33.9
[42 empty] | 1987-05-30 | 18:00 | 33.3
[42 empty] | 1987-05-30 | 19:00 | 29.4
[42 empty] | 1987-05-30 | 20:00 | 30.6
[42 empty] | 1987-05-30 | 21:00 | 27.8
[42 empty] | 1987-05-30 | 22:00 | 30.6
[42 empty] | 1987-05-30 | 23:00 | 30.6
[42 empty] | 1987-05-30 | 24:00 | 29.4
[42 empty] | 1987-05-31 | 1:00 | 27.8
[42 empty] | 1987-05-31 | 2:00 | 27.8
[42 empty] | 1987-05-31 | 3:00 | 27.2
[42 empty] | 1987-05-31 | 4:00 | 26.1
[42 empty] | 1987-05-31 | 5:00 | 26.1
[42 empty] | 1987-05-31 | 6:00 | 26.1
[42 empty] | 1987-05-31 | 7:00 | 25.6
[42 empty] | 1987-05-31 | 8:00 | 28.3
[42 empty] | 1987-05-31 | 9:00 | 30
[42 empty] | 1987-05-31 | 10:00 | 32.2
[42 empty] | 1987-05-31 | 11:00 | 33.3
[42 empty] | 1987-05-31 | 12:00 | 34.4
[42 empty] | 1987-05-31 | 13:00 | 35
[42 empty] | 1987-05-31 | 14:00 | 32.8
[42 empty] | 1987-05-31 | 15:00 | 31.7
[42 empty] | 1987-05-31 | 16:00 | 31.7
[42 empty] | 1987-05-31 | 17:00 | 31.7
[42 empty] | 1987-05-31 | 18:00 | 30.6
[42 empty] | 1987-05-31 | 19:00 | 29.4
[42 empty] | 1987-05-31 | 20:00 | 28.9
[42 empty] | 1987-05-31 | 21:00 | 27.8
[42 empty] | 1987-05-31 | 22:00 | 26.2
[42 empty] | 1987-05-31 | 23:00 | 24.6
[42 empty] | 1987-05-31 | 24:00 | 23
[42 empty] | 1990-06-01 | 1:00 | 21.5
[42 empty] | 1990-06-01 | 2:00 | 19.9
[42 empty] | 1990-06-01 | 3:00 | 18.3
[42 empty] | 1990-06-01 | 4:00 | 16.7
[42 empty] | 1990-06-01 | 5:00 | 16.1
[42 empty] | 1990-06-01 | 6:00 | 17.8
[42 empty] | 1990-06-01 | 7:00 | 18.9
[42 empty] | 1990-06-01 | 8:00 | 20.6
[42 empty] | 1990-06-01 | 9:00 | 21.7
[42 empty] | 1990-06-01 | 10:00 | 23.3
[42 empty] | 1990-06-01 | 11:00 | 25
[42 empty] | 1990-06-01 | 12:00 | 25.6
[42 empty] | 1990-06-01 | 13:00 | 26.7
[42 empty] | 1990-06-01 | 14:00 | 27.2
[42 empty] | 1990-06-01 | 15:00 | 27.8
[42 empty] | 1990-06-01 | 16:00 | 25.6
[42 empty] | 1990-06-01 | 17:00 | 24.4
[42 empty] | 1990-06-01 | 18:00 | 24.4
[42 empty] | 1990-06-01 | 19:00 | 22.8
[42 empty] | 1990-06-01 | 20:00 | 22.8
[42 empty] | 1990-06-01 | 21:00 | 22.8
[42 empty] | 1990-06-01 | 22:00 | 22.2
[42 empty] | 1990-06-01 | 23:00 | 21.1
[42 empty] | 1990-06-01 | 24:00 | 20.6
[42 empty] | 1990-06-02 | 1:00 | 20
[42 empty] | 1990-06-02 | 2:00 | 19.4
[42 empty] | 1990-06-02 | 3:00 | 19.4
[42 empty] | 1990-06-02 | 4:00 | 18.9
[42 empty] | 1990-06-02 | 5:00 | 18.9
[42 empty] | 1990-06-02 | 6:00 | 19.4
[42 empty] | 1990-06-02 | 7:00 | 20.6
[42 empty] | 1990-06-02 | 8:00 | 21.7
[42 empty] | 1990-06-02 | 9:00 | 23.3
[42 empty] | 1990-06-02 | 10:00 | 25
[42 empty] | 1990-06-02 | 11:00 | 27.2
[42 empty] | 1990-06-02 | 12:00 | 28.9
[42 empty] | 1990-06-02 | 13:00 | 29.4
[42 empty] | 1990-06-02 | 14:00 | 29.4
[42 empty] | 1990-06-02 | 15:00 | 30
[42 empty] | 1990-06-02 | 16:00 | 29.4
[42 empty] | 1990-06-02 | 17:00 | 27.8
[42 empty] | 1990-06-02 | 18:00 | 27.2
[42 empty] | 1990-06-02 | 19:00 | 25.6
[42 empty] | 1990-06-02 | 20:00 | 23.3
[42 empty] | 1990-06-02 | 21:00 | 23.3
[42 empty] | 1990-06-02 | 22:00 | 23.3
[42 empty] | 1990-06-02 | 23:00 | 21.7
[42 empty] | 1990-06-02 | 24:00 | 22.2
[42 empty] | 1990-06-03 | 1:00 | 22.2
[42 empty] | 1990-06-03 | 2:00 | 21.7
[42 empty] | 1990-06-03 | 3:00 | 20
[42 empty] | 1990-06-03 | 4:00 | 20
[42 empty] | 1990-06-03 | 5:00 | 20
[42 empty] | 1990-06-03 | 6:00 | 20
[42 empty] | 1990-06-03 | 7:00 | 20
[42 empty] | 1990-06-03 | 8:00 | 20.6
[42 empty] | 1990-06-03 | 9:00 | 22.2
[42 empty] | 1990-06-03 | 10:00 | 20.6
[42 empty] | 1990-06-03 | 11:00 | 21.7
[42 empty] | 1990-06-03 | 12:00 | 22.2
[42 empty] | 1990-06-03 | 13:00 | 22.2
[42 empty] | 1990-06-03 | 14:00 | 23.3
[42 empty] | 1990-06-03 | 15:00 | 23.9
[42 empty] | 1990-06-03 | 16:00 | 26.7
[42 empty] | 1990-06-03 | 17:00 | 23.9
[42 empty] | 1990-06-03 | 18:00 | 23.3
[42 empty] | 1990-06-03 | 19:00 | 22.8
[42 empty] | 1990-06-03 | 20:00 | 21.1
[42 empty] | 1990-06-03 | 21:00 | 20
[42 empty] | 1990-06-03 | 22:00 | 21.7
[42 empty] | 1990-06-03 | 23:00 | 21.1
[42 empty] | 1990-06-03 | 24:00 | 21.1
[42 empty] | 1990-06-04 | 1:00 | 20.6
[42 empty] | 1990-06-04 | 2:00 | 20.6
[42 empty] | 1990-06-04 | 3:00 | 20.6
[42 empty] | 1990-06-04 | 4:00 | 20
[42 empty] | 1990-06-04 | 5:00 | 20
[42 empty] | 1990-06-04 | 6:00 | 21.1
[42 empty] | 1990-06-04 | 7:00 | 22.2
[42 empty] | 1990-06-04 | 8:00 | 22.8
[42 empty] | 1990-06-04 | 9:00 | 22.8
[42 empty] | 1990-06-04 | 10:00 | 23.9
[42 empty] | 1990-06-04 | 11:00 | 23.9
[42 empty] | 1990-06-04 | 12:00 | 20.6
[42 empty] | 1990-06-04 | 13:00 | 20.6
[42 empty] | 1990-06-04 | 14:00 | 18.3
[42 empty] | 1990-06-04 | 15:00 | 18.9
[42 empty] | 1990-06-04 | 16:00 | 20.6
[42 empty] | 1990-06-04 | 17:00 | 20
[42 empty] | 1990-06-04 | 18:00 | 18.3
[42 empty] | 1990-06-04 | 19:00 | 17.8
[42 empty] | 1990-06-04 | 20:00 | 16.7
[42 empty] | 1990-06-04 | 21:00 | 16.7
[42 empty] | 1990-06-04 | 22:00 | 15.6
[42 empty] | 1990-06-04 | 23:00 | 13.3
[42 empty] | 1990-06-04 | 24:00 | 12.8
[42 empty] | 1990-06-05 | 1:00 | 12.8
[42 empty] | 1990-06-05 | 2:00 | 12.8
[42 empty] | 1990-06-05 | 3:00 | 12.2
[42 empty] | 1990-06-05 | 4:00 | 11.7
[42 empty] | 1990-06-05 | 5:00 | 11.7
[42 empty] | 1990-06-05 | 6:00 | 11.7
[42 empty] | 1990-06-05 | 7:00 | 12.8
[42 empty] | 1990-06-05 | 8:00 | 14.4
[42 empty] | 1990-06-05 | 9:00 | 15.6
[42 empty] | 1990-06-05 | 10:00 | 16.7
[42 empty] | 1990-06-05 | 11:00 | 17.8
[42 empty] | 1990-06-05 | 12:00 | 18.3
[42 empty] | 1990-06-05 | 13:00 | 19.4
[42 empty] | 1990-06-05 | 14:00 | 20.6
[42 empty] | 1990-06-05 | 15:00 | 21.7
[42 empty] | 1990-06-05 | 16:00 | 22.2
[42 empty] | 1990-06-05 | 17:00 | 22.2
[42 empty] | 1990-06-05 | 18:00 | 21.7
[42 empty] | 1990-06-05 | 19:00 | 21.1
[42 empty] | 1990-06-05 | 20:00 | 20
[42 empty] | 1990-06-05 | 21:00 | 20
[42 empty] | 1990-06-05 | 22:00 | 19.4
[42 empty] | 1990-06-05 | 23:00 | 18.3
[42 empty] | 1990-06-05 | 24:00 | 17.8
[42 empty] | 1990-06-06 | 1:00 | 17.2
[42 empty] | 1990-06-06 | 2:00 | 16.7
[42 empty] | 1990-06-06 | 3:00 | 16.7
[42 empty] | 1990-06-06 | 4:00 | 15.6
[42 empty] | 1990-06-06 | 5:00 | 15.6
[42 empty] | 1990-06-06 | 6:00 | 16.7
[42 empty] | 1990-06-06 | 7:00 | 17.2
[42 empty] | 1990-06-06 | 8:00 | 19.4
[42 empty] | 1990-06-06 | 9:00 | 20.6
[42 empty] | 1990-06-06 | 10:00 | 21.1
[42 empty] | 1990-06-06 | 11:00 | 22.8
[42 empty] | 1990-06-06 | 12:00 | 21.7
[42 empty] | 1990-06-06 | 13:00 | 22.2
[42 empty] | 1990-06-06 | 14:00 | 22.2
[42 empty] | 1990-06-06 | 15:00 | 22.8
[42 empty] | 1990-06-06 | 16:00 | 21.1
[42 empty] | 1990-06-06 | 17:00 | 22.2
[42 empty] | 1990-06-06 | 18:00 | 21.1
[42 empty] | 1990-06-06 | 19:00 | 20.6
[42 empty] | 1990-06-06 | 20:00 | 19.4
[42 empty] | 1990-06-06 | 21:00 | 19.4
[42 empty] | 1990-06-06 | 22:00 | 19.4
[42 empty] | 1990-06-06 | 23:00 | 18.9
[42 empty] | 1990-06-06 | 24:00 | 18.3
[42 empty] | 1990-06-07 | 1:00 | 18.9
[42 empty] | 1990-06-07 | 2:00 | 18.3
[42 empty] | 1990-06-07 | 3:00 | 18.3
[42 empty] | 1990-06-07 | 4:00 | 18.3
[42 empty] | 1990-06-07 | 5:00 | 17.8
[42 empty] | 1990-06-07 | 6:00 | 18.3
[42 empty] | 1990-06-07 | 7:00 | 19.4
[42 empty] | 1990-06-07 | 8:00 | 20.6
[42 empty] | 1990-06-07 | 9:00 | 23.3
[42 empty] | 1990-06-07 | 10:00 | 23.3
[42 empty] | 1990-06-07 | 11:00 | 25
[42 empty] | 1990-06-07 | 12:00 | 25.6
[42 empty] | 1990-06-07 | 13:00 | 26.1
[42 empty] | 1990-06-07 | 14:00 | 27.2
[42 empty] | 1990-06-07 | 15:00 | 27.2
[42 empty] | 1990-06-07 | 16:00 | 27.2
[42 empty] | 1990-06-07 | 17:00 | 27.2
[42 empty] | 1990-06-07 | 18:00 | 25.6
[42 empty] | 1990-06-07 | 19:00 | 25
[42 empty] | 1990-06-07 | 20:00 | 24.4
[42 empty] | 1990-06-07 | 21:00 | 23.9
[42 empty] | 1990-06-07 | 22:00 | 23.3
[42 empty] | 1990-06-07 | 23:00 | 22.2
[42 empty] | 1990-06-07 | 24:00 | 21.1
[42 empty] | 1990-06-08 | 1:00 | 20.6
[42 empty] | 1990-06-08 | 2:00 | 18.9
[42 empty] | 1990-06-08 | 3:00 | 18.3
[42 empty] | 1990-06-08 | 4:00 | 18.3
[42 empty] | 1990-06-08 | 5:00 | 17.8
[42 empty] | 1990-06-08 | 6:00 | 17.8
[42 empty] | 1990-06-08 | 7:00 | 19.4
[42 empty] | 1990-06-08 | 8:00 | 21.1
[42 empty] | 1990-06-08 | 9:00 | 22.2
[42 empty] | 1990-06-08 | 10:00 | 23.3
[42 empty] | 1990-06-08 | 11:00 | 25.6
[42 empty] | 1990-06-08 | 12:00 | 24.4
[42 empty] | 1990-06-08 | 13:00 | 23.3
[42 empty] | 1990-06-08 | 14:00 | 22.8
[42 empty] | 1990-06-08 | 15:00 | 20.6
[42 empty] | 1990-06-08 | 16:00 | 20.6
[42 empty] | 1990-06-08 | 17:00 | 20
[42 empty] | 1990-06-08 | 18:00 | 20
[42 empty] | 1990-06-08 | 19:00 | 18.3
[42 empty] | 1990-06-08 | 20:00 | 17.8
[42 empty] | 1990-06-08 | 21:00 | 17.8
[42 empty] | 1990-06-08 | 22:00 | 17.8
[42 empty] | 1990-06-08 | 23:00 | 16.7
[42 empty] | 1990-06-08 | 24:00 | 16.7
[42 empty] | 1990-06-09 | 1:00 | 16.7
[42 empty] | 1990-06-09 | 2:00 | 16.7
[42 empty] | 1990-06-09 | 3:00 | 17.8
[42 empty] | 1990-06-09 | 4:00 | 18.3
[42 empty] | 1990-06-09 | 5:00 | 17.8
[42 empty] | 1990-06-09 | 6:00 | 17.8
[42 empty] | 1990-06-09 | 7:00 | 17.8
[42 empty] | 1990-06-09 | 8:00 | 21.1
[42 empty] | 1990-06-09 | 9:00 | 22.8
[42 empty] | 1990-06-09 | 10:00 | 22.2
[42 empty] | 1990-06-09 | 11:00 | 25.6
[42 empty] | 1990-06-09 | 12:00 | 27.8
[42 empty] | 1990-06-09 | 13:00 | 27.2
[42 empty] | 1990-06-09 | 14:00 | 26.1
[42 empty] | 1990-06-09 | 15:00 | 26.7
[42 empty] | 1990-06-09 | 16:00 | 26.7
[42 empty] | 1990-06-09 | 17:00 | 27.2
[42 empty] | 1990-06-09 | 18:00 | 27.2
[42 empty] | 1990-06-09 | 19:00 | 26.1
[42 empty] | 1990-06-09 | 20:00 | 26.1
[42 empty] | 1990-06-09 | 21:00 | 25.6
[42 empty] | 1990-06-09 | 22:00 | 25.6
[42 empty] | 1990-06-09 | 23:00 | 25.6
[42 empty] | 1990-06-09 | 24:00 | 25
[42 empty] | 1990-06-10 | 1:00 | 24.4
[42 empty] | 1990-06-10 | 2:00 | 23.9
[42 empty] | 1990-06-10 | 3:00 | 23.3
[42 empty] | 1990-06-10 | 4:00 | 22.8
[42 empty] | 1990-06-10 | 5:00 | 21.7
[42 empty] | 1990-06-10 | 6:00 | 22.2
[42 empty] | 1990-06-10 | 7:00 | 22.2
[42 empty] | 1990-06-10 | 8:00 | 22.2
[42 empty] | 1990-06-10 | 9:00 | 23.9
[42 empty] | 1990-06-10 | 10:00 | 25
[42 empty] | 1990-06-10 | 11:00 | 25
[42 empty] | 1990-06-10 | 12:00 | 26.1
[42 empty] | 1990-06-10 | 13:00 | 25
[42 empty] | 1990-06-10 | 14:00 | 26.1
[42 empty] | 1990-06-10 | 15:00 | 25.6
[42 empty] | 1990-06-10 | 16:00 | 25
[42 empty] | 1990-06-10 | 17:00 | 25.6
[42 empty] | 1990-06-10 | 18:00 | 22.8
[42 empty] | 1990-06-10 | 19:00 | 22.2
[42 empty] | 1990-06-10 | 20:00 | 22.2
[42 empty] | 1990-06-10 | 21:00 | 21.7
[42 empty] | 1990-06-10 | 22:00 | 20.6
[42 empty] | 1990-06-10 | 23:00 | 19.4
[42 empty] | 1990-06-10 | 24:00 | 18.9
[42 empty] | 1990-06-11 | 1:00 | 18.9
[42 empty] | 1990-06-11 | 2:00 | 18.9
[42 empty] | 1990-06-11 | 3:00 | 18.3
[42 empty] | 1990-06-11 | 4:00 | 18.3
[42 empty] | 1990-06-11 | 5:00 | 17.8
[42 empty] | 1990-06-11 | 6:00 | 19.4
[42 empty] | 1990-06-11 | 7:00 | 19.4
[42 empty] | 1990-06-11 | 8:00 | 19.4
[42 empty] | 1990-06-11 | 9:00 | 18.9
[42 empty] | 1990-06-11 | 10:00 | 19.4
[42 empty] | 1990-06-11 | 11:00 | 19.4
[42 empty] | 1990-06-11 | 12:00 | 19.4
[42 empty] | 1990-06-11 | 13:00 | 19.4
[42 empty] | 1990-06-11 | 14:00 | 18.3
[42 empty] | 1990-06-11 | 15:00 | 17.8
[42 empty] | 1990-06-11 | 16:00 | 16.1
[42 empty] | 1990-06-11 | 17:00 | 16.1
[42 empty] | 1990-06-11 | 18:00 | 16.1
[42 empty] | 1990-06-11 | 19:00 | 16.1
[42 empty] | 1990-06-11 | 20:00 | 15.6
[42 empty] | 1990-06-11 | 21:00 | 15.6
[42 empty] | 1990-06-11 | 22:00 | 15.6
[42 empty] | 1990-06-11 | 23:00 | 15.6
[42 empty] | 1990-06-11 | 24:00 | 15.6
[42 empty] | 1990-06-12 | 1:00 | 15.6
[42 empty] | 1990-06-12 | 2:00 | 15
[42 empty] | 1990-06-12 | 3:00 | 15.6
[42 empty] | 1990-06-12 | 4:00 | 15
[42 empty] | 1990-06-12 | 5:00 | 15.6
[42 empty] | 1990-06-12 | 6:00 | 16.1
[42 empty] | 1990-06-12 | 7:00 | 17.2
[42 empty] | 1990-06-12 | 8:00 | 18.9
[42 empty] | 1990-06-12 | 9:00 | 20
[42 empty] | 1990-06-12 | 10:00 | 21.1
[42 empty] | 1990-06-12 | 11:00 | 21.7
[42 empty] | 1990-06-12 | 12:00 | 22.2
[42 empty] | 1990-06-12 | 13:00 | 23.3
[42 empty] | 1990-06-12 | 14:00 | 23.9
[42 empty] | 1990-06-12 | 15:00 | 24.4
[42 empty] | 1990-06-12 | 16:00 | 25
[42 empty] | 1990-06-12 | 17:00 | 25.6
[42 empty] | 1990-06-12 | 18:00 | 25.6
[42 empty] | 1990-06-12 | 19:00 | 20.6
[42 empty] | 1990-06-12 | 20:00 | 18.3
[42 empty] | 1990-06-12 | 21:00 | 17.8
[42 empty] | 1990-06-12 | 22:00 | 17.2
[42 empty] | 1990-06-12 | 23:00 | 16.7
[42 empty] | 1990-06-12 | 24:00 | 16.1
[42 empty] | 1990-06-13 | 1:00 | 16.1
[42 empty] | 1990-06-13 | 2:00 | 16.1
[42 empty] | 1990-06-13 | 3:00 | 15.6
[42 empty] | 1990-06-13 | 4:00 | 15.6
[42 empty] | 1990-06-13 | 5:00 | 16.1
[42 empty] | 1990-06-13 | 6:00 | 16.1
[42 empty] | 1990-06-13 | 7:00 | 17.2
[42 empty] | 1990-06-13 | 8:00 | 18.9
[42 empty] | 1990-06-13 | 9:00 | 20
[42 empty] | 1990-06-13 | 10:00 | 22.2
[42 empty] | 1990-06-13 | 11:00 | 23.9
[42 empty] | 1990-06-13 | 12:00 | 25
[42 empty] | 1990-06-13 | 13:00 | 26.7
[42 empty] | 1990-06-13 | 14:00 | 26.1
[42 empty] | 1990-06-13 | 15:00 | 26.7
[42 empty] | 1990-06-13 | 16:00 | 23.3
[42 empty] | 1990-06-13 | 17:00 | 22.2
[42 empty] | 1990-06-13 | 18:00 | 21.1
[42 empty] | 1990-06-13 | 19:00 | 20
[42 empty] | 1990-06-13 | 20:00 | 21.1
[42 empty] | 1990-06-13 | 21:00 | 21.7
[42 empty] | 1990-06-13 | 22:00 | 21.1
[42 empty] | 1990-06-13 | 23:00 | 21.7
[42 empty] | 1990-06-13 | 24:00 | 21.1
[42 empty] | 1990-06-14 | 1:00 | 19.4
[42 empty] | 1990-06-14 | 2:00 | 18.9
[42 empty] | 1990-06-14 | 3:00 | 18.3
[42 empty] | 1990-06-14 | 4:00 | 17.8
[42 empty] | 1990-06-14 | 5:00 | 18.3
[42 empty] | 1990-06-14 | 6:00 | 18.9
[42 empty] | 1990-06-14 | 7:00 | 18.9
[42 empty] | 1990-06-14 | 8:00 | 18.9
[42 empty] | 1990-06-14 | 9:00 | 19.4
[42 empty] | 1990-06-14 | 10:00 | 19.4
[42 empty] | 1990-06-14 | 11:00 | 18.9
[42 empty] | 1990-06-14 | 12:00 | 18.9
[42 empty] | 1990-06-14 | 13:00 | 18.9
[42 empty] | 1990-06-14 | 14:00 | 20
[42 empty] | 1990-06-14 | 15:00 | 18.9
[42 empty] | 1990-06-14 | 16:00 | 18.3
[42 empty] | 1990-06-14 | 17:00 | 17.2
[42 empty] | 1990-06-14 | 18:00 | 17.8
[42 empty] | 1990-06-14 | 19:00 | 17.8
[42 empty] | 1990-06-14 | 20:00 | 17.2
[42 empty] | 1990-06-14 | 21:00 | 17.2
[42 empty] | 1990-06-14 | 22:00 | 17.2
[42 empty] | 1990-06-14 | 23:00 | 17.2
[42 empty] | 1990-06-14 | 24:00 | 17.2
[42 empty] | 1990-06-15 | 1:00 | 16.7
[42 empty] | 1990-06-15 | 2:00 | 16.7
[42 empty] | 1990-06-15 | 3:00 | 16.7
[42 empty] | 1990-06-15 | 4:00 | 16.1
[42 empty] | 1990-06-15 | 5:00 | 16.1
[42 empty] | 1990-06-15 | 6:00 | 17.2
[42 empty] | 1990-06-15 | 7:00 | 17.8
[42 empty] | 1990-06-15 | 8:00 | 18.3
[42 empty] | 1990-06-15 | 9:00 | 20
[42 empty] | 1990-06-15 | 10:00 | 21.1
[42 empty] | 1990-06-15 | 11:00 | 21.7
[42 empty] | 1990-06-15 | 12:00 | 22.2
[42 empty] | 1990-06-15 | 13:00 | 23.3
[42 empty] | 1990-06-15 | 14:00 | 25
[42 empty] | 1990-06-15 | 15:00 | 24.4
[42 empty] | 1990-06-15 | 16:00 | 23.9
[42 empty] | 1990-06-15 | 17:00 | 23.3
[42 empty] | 1990-06-15 | 18:00 | 21.7
[42 empty] | 1990-06-15 | 19:00 | 21.1
[42 empty] | 1990-06-15 | 20:00 | 20.6
[42 empty] | 1990-06-15 | 21:00 | 19.4
[42 empty] | 1990-06-15 | 22:00 | 18.3
[42 empty] | 1990-06-15 | 23:00 | 18.3
[42 empty] | 1990-06-15 | 24:00 | 17.2
[42 empty] | 1990-06-16 | 1:00 | 16.7
[42 empty] | 1990-06-16 | 2:00 | 17.2
[42 empty] | 1990-06-16 | 3:00 | 16.7
[42 empty] | 1990-06-16 | 4:00 | 16.1
[42 empty] | 1990-06-16 | 5:00 | 15.6
[42 empty] | 1990-06-16 | 6:00 | 15.6
[42 empty] | 1990-06-16 | 7:00 | 16.1
[42 empty] | 1990-06-16 | 8:00 | 16.7
[42 empty] | 1990-06-16 | 9:00 | 17.8
[42 empty] | 1990-06-16 | 10:00 | 18.9
[42 empty] | 1990-06-16 | 11:00 | 20
[42 empty] | 1990-06-16 | 12:00 | 22.2
[42 empty] | 1990-06-16 | 13:00 | 23.9
[42 empty] | 1990-06-16 | 14:00 | 25
[42 empty] | 1990-06-16 | 15:00 | 25
[42 empty] | 1990-06-16 | 16:00 | 26.1
[42 empty] | 1990-06-16 | 17:00 | 25.6
[42 empty] | 1990-06-16 | 18:00 | 23.9
[42 empty] | 1990-06-16 | 19:00 | 22.8
[42 empty] | 1990-06-16 | 20:00 | 21.7
[42 empty] | 1990-06-16 | 21:00 | 21.1
[42 empty] | 1990-06-16 | 22:00 | 20.6
[42 empty] | 1990-06-16 | 23:00 | 20.6
[42 empty] | 1990-06-16 | 24:00 | 20
[42 empty] | 1990-06-17 | 1:00 | 19.4
[42 empty] | 1990-06-17 | 2:00 | 19.4
[42 empty] | 1990-06-17 | 3:00 | 18.9
[42 empty] | 1990-06-17 | 4:00 | 18.3
[42 empty] | 1990-06-17 | 5:00 | 17.8
[42 empty] | 1990-06-17 | 6:00 | 18.3
[42 empty] | 1990-06-17 | 7:00 | 18.9
[42 empty] | 1990-06-17 | 8:00 | 21.1
[42 empty] | 1990-06-17 | 9:00 | 21.7
[42 empty] | 1990-06-17 | 10:00 | 24.4
[42 empty] | 1990-06-17 | 11:00 | 26.7
[42 empty] | 1990-06-17 | 12:00 | 27.2
[42 empty] | 1990-06-17 | 13:00 | 27.8
[42 empty] | 1990-06-17 | 14:00 | 27.2
[42 empty] | 1990-06-17 | 15:00 | 26.7
[42 empty] | 1990-06-17 | 16:00 | 26.7
[42 empty] | 1990-06-17 | 17:00 | 26.1
[42 empty] | 1990-06-17 | 18:00 | 23.9
[42 empty] | 1990-06-17 | 19:00 | 22.8
[42 empty] | 1990-06-17 | 20:00 | 20.6
[42 empty] | 1990-06-17 | 21:00 | 20
[42 empty] | 1990-06-17 | 22:00 | 19.4
[42 empty] | 1990-06-17 | 23:00 | 18.9
[42 empty] | 1990-06-17 | 24:00 | 18.9
[42 empty] | 1990-06-18 | 1:00 | 18.9
[42 empty] | 1990-06-18 | 2:00 | 18.9
[42 empty] | 1990-06-18 | 3:00 | 18.3
[42 empty] | 1990-06-18 | 4:00 | 18.3
[42 empty] | 1990-06-18 | 5:00 | 18.3
[42 empty] | 1990-06-18 | 6:00 | 19.4
[42 empty] | 1990-06-18 | 7:00 | 20
[42 empty] | 1990-06-18 | 8:00 | 22.8
[42 empty] | 1990-06-18 | 9:00 | 25.6
[42 empty] | 1990-06-18 | 10:00 | 25.6
[42 empty] | 1990-06-18 | 11:00 | 26.1
[42 empty] | 1990-06-18 | 12:00 | 25
[42 empty] | 1990-06-18 | 13:00 | 25.6
[42 empty] | 1990-06-18 | 14:00 | 26.7
[42 empty] | 1990-06-18 | 15:00 | 25
[42 empty] | 1990-06-18 | 16:00 | 24.4
[42 empty] | 1990-06-18 | 17:00 | 22.8
[42 empty] | 1990-06-18 | 18:00 | 21.1
[42 empty] | 1990-06-18 | 19:00 | 21.7
[42 empty] | 1990-06-18 | 20:00 | 21.7
[42 empty] | 1990-06-18 | 21:00 | 21.1
[42 empty] | 1990-06-18 | 22:00 | 21.1
[42 empty] | 1990-06-18 | 23:00 | 21.1
[42 empty] | 1990-06-18 | 24:00 | 21.1
[42 empty] | 1990-06-19 | 1:00 | 21.1
[42 empty] | 1990-06-19 | 2:00 | 20.6
[42 empty] | 1990-06-19 | 3:00 | 20.6
[42 empty] | 1990-06-19 | 4:00 | 21.1
[42 empty] | 1990-06-19 | 5:00 | 20.6
[42 empty] | 1990-06-19 | 6:00 | 21.1
[42 empty] | 1990-06-19 | 7:00 | 22.2
[42 empty] | 1990-06-19 | 8:00 | 22.8
[42 empty] | 1990-06-19 | 9:00 | 22.8
[42 empty] | 1990-06-19 | 10:00 | 23.3
[42 empty] | 1990-06-19 | 11:00 | 25
[42 empty] | 1990-06-19 | 12:00 | 26.1
[42 empty] | 1990-06-19 | 13:00 | 27.8
[42 empty] | 1990-06-19 | 14:00 | 26.7
[42 empty] | 1990-06-19 | 15:00 | 26.1
[42 empty] | 1990-06-19 | 16:00 | 24.4
[42 empty] | 1990-06-19 | 17:00 | 20
[42 empty] | 1990-06-19 | 18:00 | 20.6
[42 empty] | 1990-06-19 | 19:00 | 20
[42 empty] | 1990-06-19 | 20:00 | 20.6
[42 empty] | 1990-06-19 | 21:00 | 20.6
[42 empty] | 1990-06-19 | 22:00 | 20.6
[42 empty] | 1990-06-19 | 23:00 | 19.4
[42 empty] | 1990-06-19 | 24:00 | 19.4
[42 empty] | 1990-06-20 | 1:00 | 19.4
[42 empty] | 1990-06-20 | 2:00 | 20
[42 empty] | 1990-06-20 | 3:00 | 18.9
[42 empty] | 1990-06-20 | 4:00 | 18.9
[42 empty] | 1990-06-20 | 5:00 | 18.3
[42 empty] | 1990-06-20 | 6:00 | 18.9
[42 empty] | 1990-06-20 | 7:00 | 19.4
[42 empty] | 1990-06-20 | 8:00 | 21.1
[42 empty] | 1990-06-20 | 9:00 | 22.2
[42 empty] | 1990-06-20 | 10:00 | 23.3
[42 empty] | 1990-06-20 | 11:00 | 23.9
[42 empty] | 1990-06-20 | 12:00 | 24.4
[42 empty] | 1990-06-20 | 13:00 | 24.4
[42 empty] | 1990-06-20 | 14:00 | 24.4
[42 empty] | 1990-06-20 | 15:00 | 25
[42 empty] | 1990-06-20 | 16:00 | 25.6
[42 empty] | 1990-06-20 | 17:00 | 25.6
[42 empty] | 1990-06-20 | 18:00 | 25
[42 empty] | 1990-06-20 | 19:00 | 24.4
[42 empty] | 1990-06-20 | 20:00 | 23.9
[42 empty] | 1990-06-20 | 21:00 | 23.9
[42 empty] | 1990-06-20 | 22:00 | 23.3
[42 empty] | 1990-06-20 | 23:00 | 23.9
[42 empty] | 1990-06-20 | 24:00 | 23.3
[42 empty] | 1990-06-21 | 1:00 | 23.3
[42 empty] | 1990-06-21 | 2:00 | 23.3
[42 empty] | 1990-06-21 | 3:00 | 22.8
[42 empty] | 1990-06-21 | 4:00 | 22.8
[42 empty] | 1990-06-21 | 5:00 | 22.2
[42 empty] | 1990-06-21 | 6:00 | 21.7
[42 empty] | 1990-06-21 | 7:00 | 20.6
[42 empty] | 1990-06-21 | 8:00 | 21.1
[42 empty] | 1990-06-21 | 9:00 | 20.6
[42 empty] | 1990-06-21 | 10:00 | 21.7
[42 empty] | 1990-06-21 | 11:00 | 21.7
[42 empty] | 1990-06-21 | 12:00 | 22.8
[42 empty] | 1990-06-21 | 13:00 | 22.8
[42 empty] | 1990-06-21 | 14:00 | 23.9
[42 empty] | 1990-06-21 | 15:00 | 24.4
[42 empty] | 1990-06-21 | 16:00 | 24.4
[42 empty] | 1990-06-21 | 17:00 | 25.6
[42 empty] | 1990-06-21 | 18:00 | 24.4
[42 empty] | 1990-06-21 | 19:00 | 23.3
[42 empty] | 1990-06-21 | 20:00 | 22.8
[42 empty] | 1990-06-21 | 21:00 | 21.7
[42 empty] | 1990-06-21 | 22:00 | 22.8
[42 empty] | 1990-06-21 | 23:00 | 22.2
[42 empty] | 1990-06-21 | 24:00 | 21.7
[42 empty] | 1990-06-22 | 1:00 | 21.7
[42 empty] | 1990-06-22 | 2:00 | 21.1
[42 empty] | 1990-06-22 | 3:00 | 20.6
[42 empty] | 1990-06-22 | 4:00 | 20
[42 empty] | 1990-06-22 | 5:00 | 20
[42 empty] | 1990-06-22 | 6:00 | 20.6
[42 empty] | 1990-06-22 | 7:00 | 25
[42 empty] | 1990-06-22 | 8:00 | 26.1
[42 empty] | 1990-06-22 | 9:00 | 28.9
[42 empty] | 1990-06-22 | 10:00 | 29.4
[42 empty] | 1990-06-22 | 11:00 | 30.6
[42 empty] | 1990-06-22 | 12:00 | 31.1
[42 empty] | 1990-06-22 | 13:00 | 31.7
[42 empty] | 1990-06-22 | 14:00 | 31.1
[42 empty] | 1990-06-22 | 15:00 | 31.1
[42 empty] | 1990-06-22 | 16:00 | 29.4
[42 empty] | 1990-06-22 | 17:00 | 28.9
[42 empty] | 1990-06-22 | 18:00 | 27.8
[42 empty] | 1990-06-22 | 19:00 | 28.3
[42 empty] | 1990-06-22 | 20:00 | 25
[42 empty] | 1990-06-22 | 21:00 | 25
[42 empty] | 1990-06-22 | 22:00 | 24.4
[42 empty] | 1990-06-22 | 23:00 | 23.9
[42 empty] | 1990-06-22 | 24:00 | 23.3
[42 empty] | 1990-06-23 | 1:00 | 22.8
[42 empty] | 1990-06-23 | 2:00 | 22.2
[42 empty] | 1990-06-23 | 3:00 | 21.7
[42 empty] | 1990-06-23 | 4:00 | 22.2
[42 empty] | 1990-06-23 | 5:00 | 21.7
[42 empty] | 1990-06-23 | 6:00 | 21.7
[42 empty] | 1990-06-23 | 7:00 | 22.8
[42 empty] | 1990-06-23 | 8:00 | 23.3
[42 empty] | 1990-06-23 | 9:00 | 25
[42 empty] | 1990-06-23 | 10:00 | 25
[42 empty] | 1990-06-23 | 11:00 | 25
[42 empty] | 1990-06-23 | 12:00 | 25.6
[42 empty] | 1990-06-23 | 13:00 | 26.1
[42 empty] | 1990-06-23 | 14:00 | 28.9
[42 empty] | 1990-06-23 | 15:00 | 28.9
[42 empty] | 1990-06-23 | 16:00 | 27.8
[42 empty] | 1990-06-23 | 17:00 | 27.8
[42 empty] | 1990-06-23 | 18:00 | 28.9
[42 empty] | 1990-06-23 | 19:00 | 27.8
[42 empty] | 1990-06-23 | 20:00 | 27.2
[42 empty] | 1990-06-23 | 21:00 | 26.7
[42 empty] | 1990-06-23 | 22:00 | 25
[42 empty] | 1990-06-23 | 23:00 | 25
[42 empty] | 1990-06-23 | 24:00 | 24.4
[42 empty] | 1990-06-24 | 1:00 | 23.9
[42 empty] | 1990-06-24 | 2:00 | 23.3
[42 empty] | 1990-06-24 | 3:00 | 22.8
[42 empty] | 1990-06-24 | 4:00 | 22.8
[42 empty] | 1990-06-24 | 5:00 | 22.8
[42 empty] | 1990-06-24 | 6:00 | 22.8
[42 empty] | 1990-06-24 | 7:00 | 22.8
[42 empty] | 1990-06-24 | 8:00 | 23.3
[42 empty] | 1990-06-24 | 9:00 | 24.4
[42 empty] | 1990-06-24 | 10:00 | 25
[42 empty] | 1990-06-24 | 11:00 | 26.1
[42 empty] | 1990-06-24 | 12:00 | 25.6
[42 empty] | 1990-06-24 | 13:00 | 25
[42 empty] | 1990-06-24 | 14:00 | 25.6
[42 empty] | 1990-06-24 | 15:00 | 26.7
[42 empty] | 1990-06-24 | 16:00 | 26.1
[42 empty] | 1990-06-24 | 17:00 | 25.6
[42 empty] | 1990-06-24 | 18:00 | 25.6
[42 empty] | 1990-06-24 | 19:00 | 25
[42 empty] | 1990-06-24 | 20:00 | 24.4
[42 empty] | 1990-06-24 | 21:00 | 23.9
[42 empty] | 1990-06-24 | 22:00 | 23.3
[42 empty] | 1990-06-24 | 23:00 | 22.8
[42 empty] | 1990-06-24 | 24:00 | 22.2
[42 empty] | 1990-06-25 | 1:00 | 21.1
[42 empty] | 1990-06-25 | 2:00 | 20.6
[42 empty] | 1990-06-25 | 3:00 | 20
[42 empty] | 1990-06-25 | 4:00 | 19.4
[42 empty] | 1990-06-25 | 5:00 | 19.4
[42 empty] | 1990-06-25 | 6:00 | 20.6
[42 empty] | 1990-06-25 | 7:00 | 20.6
[42 empty] | 1990-06-25 | 8:00 | 21.7
[42 empty] | 1990-06-25 | 9:00 | 21.7
[42 empty] | 1990-06-25 | 10:00 | 22.8
[42 empty] | 1990-06-25 | 11:00 | 22.8
[42 empty] | 1990-06-25 | 12:00 | 24.4
[42 empty] | 1990-06-25 | 13:00 | 25
[42 empty] | 1990-06-25 | 14:00 | 25
[42 empty] | 1990-06-25 | 15:00 | 26.1
[42 empty] | 1990-06-25 | 16:00 | 25.6
[42 empty] | 1990-06-25 | 17:00 | 25
[42 empty] | 1990-06-25 | 18:00 | 24.4
[42 empty] | 1990-06-25 | 19:00 | 23.9
[42 empty] | 1990-06-25 | 20:00 | 22.8
[42 empty] | 1990-06-25 | 21:00 | 22.8
[42 empty] | 1990-06-25 | 22:00 | 22.2
[42 empty] | 1990-06-25 | 23:00 | 21.7
[42 empty] | 1990-06-25 | 24:00 | 21.7
[42 empty] | 1990-06-26 | 1:00 | 20.6
[42 empty] | 1990-06-26 | 2:00 | 20.6
[42 empty] | 1990-06-26 | 3:00 | 20
[42 empty] | 1990-06-26 | 4:00 | 19.4
[42 empty] | 1990-06-26 | 5:00 | 19.4
[42 empty] | 1990-06-26 | 6:00 | 19.4
[42 empty] | 1990-06-26 | 7:00 | 21.1
[42 empty] | 1990-06-26 | 8:00 | 22.8
[42 empty] | 1990-06-26 | 9:00 | 23.9
[42 empty] | 1990-06-26 | 10:00 | 25
[42 empty] | 1990-06-26 | 11:00 | 26.7
[42 empty] | 1990-06-26 | 12:00 | 27.2
[42 empty] | 1990-06-26 | 13:00 | 28.3
[42 empty] | 1990-06-26 | 14:00 | 28.9
[42 empty] | 1990-06-26 | 15:00 | 27.8
[42 empty] | 1990-06-26 | 16:00 | 27.8
[42 empty] | 1990-06-26 | 17:00 | 26.7
[42 empty] | 1990-06-26 | 18:00 | 25.6
[42 empty] | 1990-06-26 | 19:00 | 26.1
[42 empty] | 1990-06-26 | 20:00 | 25.6
[42 empty] | 1990-06-26 | 21:00 | 25
[42 empty] | 1990-06-26 | 22:00 | 24.4
[42 empty] | 1990-06-26 | 23:00 | 23.9
[42 empty] | 1990-06-26 | 24:00 | 23.3
[42 empty] | 1990-06-27 | 1:00 | 23.3
[42 empty] | 1990-06-27 | 2:00 | 22.8
[42 empty] | 1990-06-27 | 3:00 | 22.8
[42 empty] | 1990-06-27 | 4:00 | 22.8
[42 empty] | 1990-06-27 | 5:00 | 22.8
[42 empty] | 1990-06-27 | 6:00 | 22.8
[42 empty] | 1990-06-27 | 7:00 | 23.3
[42 empty] | 1990-06-27 | 8:00 | 25
[42 empty] | 1990-06-27 | 9:00 | 26.1
[42 empty] | 1990-06-27 | 10:00 | 26.1
[42 empty] | 1990-06-27 | 11:00 | 28.3
[42 empty] | 1990-06-27 | 12:00 | 30
[42 empty] | 1990-06-27 | 13:00 | 30
[42 empty] | 1990-06-27 | 14:00 | 28.9
[42 empty] | 1990-06-27 | 15:00 | 28.3
[42 empty] | 1990-06-27 | 16:00 | 27.2
[42 empty] | 1990-06-27 | 17:00 | 26.1
[42 empty] | 1990-06-27 | 18:00 | 26.1
[42 empty] | 1990-06-27 | 19:00 | 25
[42 empty] | 1990-06-27 | 20:00 | 26.1
[42 empty] | 1990-06-27 | 21:00 | 26.1
[42 empty] | 1990-06-27 | 22:00 | 25
[42 empty] | 1990-06-27 | 23:00 | 25
[42 empty] | 1990-06-27 | 24:00 | 25
[42 empty] | 1990-06-28 | 1:00 | 24.4
[42 empty] | 1990-06-28 | 2:00 | 25
[42 empty] | 1990-06-28 | 3:00 | 23.3
[42 empty] | 1990-06-28 | 4:00 | 22.2
[42 empty] | 1990-06-28 | 5:00 | 22.2
[42 empty] | 1990-06-28 | 6:00 | 22.8
[42 empty] | 1990-06-28 | 7:00 | 23.9
[42 empty] | 1990-06-28 | 8:00 | 25.6
[42 empty] | 1990-06-28 | 9:00 | 26.7
[42 empty] | 1990-06-28 | 10:00 | 27.2
[42 empty] | 1990-06-28 | 11:00 | 28.9
[42 empty] | 1990-06-28 | 12:00 | 30
[42 empty] | 1990-06-28 | 13:00 | 30.6
[42 empty] | 1990-06-28 | 14:00 | 30
[42 empty] | 1990-06-28 | 15:00 | 30.6
[42 empty] | 1990-06-28 | 16:00 | 30.6
[42 empty] | 1990-06-28 | 17:00 | 28.9
[42 empty] | 1990-06-28 | 18:00 | 30
[42 empty] | 1990-06-28 | 19:00 | 28.3
[42 empty] | 1990-06-28 | 20:00 | 27.2
[42 empty] | 1990-06-28 | 21:00 | 26.7
[42 empty] | 1990-06-28 | 22:00 | 25.6
[42 empty] | 1990-06-28 | 23:00 | 26.1
[42 empty] | 1990-06-28 | 24:00 | 23.9
[42 empty] | 1990-06-29 | 1:00 | 22.8
[42 empty] | 1990-06-29 | 2:00 | 22.8
[42 empty] | 1990-06-29 | 3:00 | 22.2
[42 empty] | 1990-06-29 | 4:00 | 21.7
[42 empty] | 1990-06-29 | 5:00 | 21.1
[42 empty] | 1990-06-29 | 6:00 | 21.1
[42 empty] | 1990-06-29 | 7:00 | 21.7
[42 empty] | 1990-06-29 | 8:00 | 21.7
[42 empty] | 1990-06-29 | 9:00 | 21.1
[42 empty] | 1990-06-29 | 10:00 | 22.8
[42 empty] | 1990-06-29 | 11:00 | 23.3
[42 empty] | 1990-06-29 | 12:00 | 23.3
[42 empty] | 1990-06-29 | 13:00 | 23.3
[42 empty] | 1990-06-29 | 14:00 | 26.7
[42 empty] | 1990-06-29 | 15:00 | 30
[42 empty] | 1990-06-29 | 16:00 | 30.6
[42 empty] | 1990-06-29 | 17:00 | 28.3
[42 empty] | 1990-06-29 | 18:00 | 27.8
[42 empty] | 1990-06-29 | 19:00 | 28.3
[42 empty] | 1990-06-29 | 20:00 | 28.3
[42 empty] | 1990-06-29 | 21:00 | 27.2
[42 empty] | 1990-06-29 | 22:00 | 22.2
[42 empty] | 1990-06-29 | 23:00 | 23.3
[42 empty] | 1990-06-29 | 24:00 | 21.7
[42 empty] | 1990-06-30 | 1:00 | 22.8
[42 empty] | 1990-06-30 | 2:00 | 22.2
[42 empty] | 1990-06-30 | 3:00 | 22.8
[42 empty] | 1990-06-30 | 4:00 | 23.3
[42 empty] | 1990-06-30 | 5:00 | 23.3
[42 empty] | 1990-06-30 | 6:00 | 23.9
[42 empty] | 1990-06-30 | 7:00 | 24.4
[42 empty] | 1990-06-30 | 8:00 | 25
[42 empty] | 1990-06-30 | 9:00 | 25
[42 empty] | 1990-06-30 | 10:00 | 25.6
[42 empty] | 1990-06-30 | 11:00 | 26.7
[42 empty] | 1990-06-30 | 12:00 | 26.7
[42 empty] | 1990-06-30 | 13:00 | 27.8
[42 empty] | 1990-06-30 | 14:00 | 29.4
[42 empty] | 1990-06-30 | 15:00 | 28.3
[42 empty] | 1990-06-30 | 16:00 | 29.4
[42 empty] | 1990-06-30 | 17:00 | 29.4
[42 empty] | 1990-06-30 | 18:00 | 30
[42 empty] | 1990-06-30 | 19:00 | 27.2
[42 empty] | 1990-06-30 | 20:00 | 26.1
[42 empty] | 1990-06-30 | 21:00 | 23.3
[42 empty] | 1990-06-30 | 22:00 | 23.3
[42 empty] | 1990-06-30 | 23:00 | 23.3
[42 empty] | 1990-06-30 | 24:00 | 23.3
[42 empty] | 1987-07-01 | 1:00 | 23.3
[42 empty] | 1987-07-01 | 2:00 | 23.3
[42 empty] | 1987-07-01 | 3:00 | 23.3
[42 empty] | 1987-07-01 | 4:00 | 23.3
[42 empty] | 1987-07-01 | 5:00 | 22.8
[42 empty] | 1987-07-01 | 6:00 | 22.8
[42 empty] | 1987-07-01 | 7:00 | 23.3
[42 empty] | 1987-07-01 | 8:00 | 24.4
[42 empty] | 1987-07-01 | 9:00 | 25
[42 empty] | 1987-07-01 | 10:00 | 26.1
[42 empty] | 1987-07-01 | 11:00 | 25
[42 empty] | 1987-07-01 | 12:00 | 26.7
[42 empty] | 1987-07-01 | 13:00 | 26.7
[42 empty] | 1987-07-01 | 14:00 | 27.2
[42 empty] | 1987-07-01 | 15:00 | 26.7
[42 empty] | 1987-07-01 | 16:00 | 26.7
[42 empty] | 1987-07-01 | 17:00 | 26.7
[42 empty] | 1987-07-01 | 18:00 | 24.4
[42 empty] | 1987-07-01 | 19:00 | 20.6
[42 empty] | 1987-07-01 | 20:00 | 21.1
[42 empty] | 1987-07-01 | 21:00 | 21.1
[42 empty] | 1987-07-01 | 22:00 | 21.1
[42 empty] | 1987-07-01 | 23:00 | 21.1
[42 empty] | 1987-07-01 | 24:00 | 20.6
[42 empty] | 1987-07-02 | 1:00 | 20.6
[42 empty] | 1987-07-02 | 2:00 | 20
[42 empty] | 1987-07-02 | 3:00 | 20
[42 empty] | 1987-07-02 | 4:00 | 19.4
[42 empty] | 1987-07-02 | 5:00 | 20
[42 empty] | 1987-07-02 | 6:00 | 19.4
[42 empty] | 1987-07-02 | 7:00 | 18.9
[42 empty] | 1987-07-02 | 8:00 | 18.9
[42 empty] | 1987-07-02 | 9:00 | 18.9
[42 empty] | 1987-07-02 | 10:00 | 19.4
[42 empty] | 1987-07-02 | 11:00 | 19.4
[42 empty] | 1987-07-02 | 12:00 | 19.4
[42 empty] | 1987-07-02 | 13:00 | 20
[42 empty] | 1987-07-02 | 14:00 | 20
[42 empty] | 1987-07-02 | 15:00 | 20.6
[42 empty] | 1987-07-02 | 16:00 | 20.6
[42 empty] | 1987-07-02 | 17:00 | 20.6
[42 empty] | 1987-07-02 | 18:00 | 20
[42 empty] | 1987-07-02 | 19:00 | 19.4
[42 empty] | 1987-07-02 | 20:00 | 18.9
[42 empty] | 1987-07-02 | 21:00 | 18.9
[42 empty] | 1987-07-02 | 22:00 | 18.9
[42 empty] | 1987-07-02 | 23:00 | 18.9
[42 empty] | 1987-07-02 | 24:00 | 18.3
[42 empty] | 1987-07-03 | 1:00 | 18.3
[42 empty] | 1987-07-03 | 2:00 | 17.8
[42 empty] | 1987-07-03 | 3:00 | 18.3
[42 empty] | 1987-07-03 | 4:00 | 18.9
[42 empty] | 1987-07-03 | 5:00 | 18.3
[42 empty] | 1987-07-03 | 6:00 | 18.3
[42 empty] | 1987-07-03 | 7:00 | 18.3
[42 empty] | 1987-07-03 | 8:00 | 18.9
[42 empty] | 1987-07-03 | 9:00 | 19.4
[42 empty] | 1987-07-03 | 10:00 | 21.1
[42 empty] | 1987-07-03 | 11:00 | 21.7
[42 empty] | 1987-07-03 | 12:00 | 24.4
[42 empty] | 1987-07-03 | 13:00 | 25.6
[42 empty] | 1987-07-03 | 14:00 | 26.1
[42 empty] | 1987-07-03 | 15:00 | 29.4
[42 empty] | 1987-07-03 | 16:00 | 29.4
[42 empty] | 1987-07-03 | 17:00 | 29.4
[42 empty] | 1987-07-03 | 18:00 | 28.9
[42 empty] | 1987-07-03 | 19:00 | 28.3
[42 empty] | 1987-07-03 | 20:00 | 26.7
[42 empty] | 1987-07-03 | 21:00 | 26.7
[42 empty] | 1987-07-03 | 22:00 | 26.1
[42 empty] | 1987-07-03 | 23:00 | 26.1
[42 empty] | 1987-07-03 | 24:00 | 24.4
[42 empty] | 1987-07-04 | 1:00 | 25
[42 empty] | 1987-07-04 | 2:00 | 23.9
[42 empty] | 1987-07-04 | 3:00 | 24.4
[42 empty] | 1987-07-04 | 4:00 | 23.9
[42 empty] | 1987-07-04 | 5:00 | 23.9
[42 empty] | 1987-07-04 | 6:00 | 23.9
[42 empty] | 1987-07-04 | 7:00 | 24.4
[42 empty] | 1987-07-04 | 8:00 | 25
[42 empty] | 1987-07-04 | 9:00 | 26.7
[42 empty] | 1987-07-04 | 10:00 | 28.3
[42 empty] | 1987-07-04 | 11:00 | 29.4
[42 empty] | 1987-07-04 | 12:00 | 30
[42 empty] | 1987-07-04 | 13:00 | 30
[42 empty] | 1987-07-04 | 14:00 | 30.6
[42 empty] | 1987-07-04 | 15:00 | 30.6
[42 empty] | 1987-07-04 | 16:00 | 30
[42 empty] | 1987-07-04 | 17:00 | 30
[42 empty] | 1987-07-04 | 18:00 | 28.9
[42 empty] | 1987-07-04 | 19:00 | 28.9
[42 empty] | 1987-07-04 | 20:00 | 27.8
[42 empty] | 1987-07-04 | 21:00 | 28.3
[42 empty] | 1987-07-04 | 22:00 | 25
[42 empty] | 1987-07-04 | 23:00 | 25.6
[42 empty] | 1987-07-04 | 24:00 | 23.9
[42 empty] | 1987-07-05 | 1:00 | 22.8
[42 empty] | 1987-07-05 | 2:00 | 21.7
[42 empty] | 1987-07-05 | 3:00 | 21.1
[42 empty] | 1987-07-05 | 4:00 | 20.6
[42 empty] | 1987-07-05 | 5:00 | 20.6
[42 empty] | 1987-07-05 | 6:00 | 21.1
[42 empty] | 1987-07-05 | 7:00 | 22.2
[42 empty] | 1987-07-05 | 8:00 | 23.9
[42 empty] | 1987-07-05 | 9:00 | 23.9
[42 empty] | 1987-07-05 | 10:00 | 25
[42 empty] | 1987-07-05 | 11:00 | 26.7
[42 empty] | 1987-07-05 | 12:00 | 27.8
[42 empty] | 1987-07-05 | 13:00 | 28.3
[42 empty] | 1987-07-05 | 14:00 | 28.3
[42 empty] | 1987-07-05 | 15:00 | 28.9
[42 empty] | 1987-07-05 | 16:00 | 28.3
[42 empty] | 1987-07-05 | 17:00 | 26.7
[42 empty] | 1987-07-05 | 18:00 | 25.6
[42 empty] | 1987-07-05 | 19:00 | 24.4
[42 empty] | 1987-07-05 | 20:00 | 23.3
[42 empty] | 1987-07-05 | 21:00 | 22.8
[42 empty] | 1987-07-05 | 22:00 | 22.2
[42 empty] | 1987-07-05 | 23:00 | 22.2
[42 empty] | 1987-07-05 | 24:00 | 21.1
[42 empty] | 1987-07-06 | 1:00 | 20.6
[42 empty] | 1987-07-06 | 2:00 | 20
[42 empty] | 1987-07-06 | 3:00 | 19.4
[42 empty] | 1987-07-06 | 4:00 | 19.4
[42 empty] | 1987-07-06 | 5:00 | 18.9
[42 empty] | 1987-07-06 | 6:00 | 19.4
[42 empty] | 1987-07-06 | 7:00 | 20
[42 empty] | 1987-07-06 | 8:00 | 21.1
[42 empty] | 1987-07-06 | 9:00 | 21.7
[42 empty] | 1987-07-06 | 10:00 | 22.8
[42 empty] | 1987-07-06 | 11:00 | 23.3
[42 empty] | 1987-07-06 | 12:00 | 26.1
[42 empty] | 1987-07-06 | 13:00 | 25
[42 empty] | 1987-07-06 | 14:00 | 25
[42 empty] | 1987-07-06 | 15:00 | 25
[42 empty] | 1987-07-06 | 16:00 | 25.6
[42 empty] | 1987-07-06 | 17:00 | 23.9
[42 empty] | 1987-07-06 | 18:00 | 23.3
[42 empty] | 1987-07-06 | 19:00 | 21.7
[42 empty] | 1987-07-06 | 20:00 | 20
[42 empty] | 1987-07-06 | 21:00 | 19.4
[42 empty] | 1987-07-06 | 22:00 | 18.9
[42 empty] | 1987-07-06 | 23:00 | 18.3
[42 empty] | 1987-07-06 | 24:00 | 18.3
[42 empty] | 1987-07-07 | 1:00 | 18.9
[42 empty] | 1987-07-07 | 2:00 | 18.9
[42 empty] | 1987-07-07 | 3:00 | 19.4
[42 empty] | 1987-07-07 | 4:00 | 18.9
[42 empty] | 1987-07-07 | 5:00 | 18.9
[42 empty] | 1987-07-07 | 6:00 | 19.4
[42 empty] | 1987-07-07 | 7:00 | 20.6
[42 empty] | 1987-07-07 | 8:00 | 20.6
[42 empty] | 1987-07-07 | 9:00 | 21.7
[42 empty] | 1987-07-07 | 10:00 | 21.7
[42 empty] | 1987-07-07 | 11:00 | 21.1
[42 empty] | 1987-07-07 | 12:00 | 21.1
[42 empty] | 1987-07-07 | 13:00 | 21.7
[42 empty] | 1987-07-07 | 14:00 | 22.2
[42 empty] | 1987-07-07 | 15:00 | 21.7
[42 empty] | 1987-07-07 | 16:00 | 21.7
[42 empty] | 1987-07-07 | 17:00 | 21.7
[42 empty] | 1987-07-07 | 18:00 | 22.2
[42 empty] | 1987-07-07 | 19:00 | 21.7
[42 empty] | 1987-07-07 | 20:00 | 21.1
[42 empty] | 1987-07-07 | 21:00 | 21.1
[42 empty] | 1987-07-07 | 22:00 | 21.1
[42 empty] | 1987-07-07 | 23:00 | 21.1
[42 empty] | 1987-07-07 | 24:00 | 21.7
[42 empty] | 1987-07-08 | 1:00 | 21.1
[42 empty] | 1987-07-08 | 2:00 | 21.7
[42 empty] | 1987-07-08 | 3:00 | 21.7
[42 empty] | 1987-07-08 | 4:00 | 20.6
[42 empty] | 1987-07-08 | 5:00 | 21.1
[42 empty] | 1987-07-08 | 6:00 | 21.1
[42 empty] | 1987-07-08 | 7:00 | 21.1
[42 empty] | 1987-07-08 | 8:00 | 21.7
[42 empty] | 1987-07-08 | 9:00 | 22.2
[42 empty] | 1987-07-08 | 10:00 | 22.8
[42 empty] | 1987-07-08 | 11:00 | 23.9
[42 empty] | 1987-07-08 | 12:00 | 24.4
[42 empty] | 1987-07-08 | 13:00 | 25.6
[42 empty] | 1987-07-08 | 14:00 | 26.7
[42 empty] | 1987-07-08 | 15:00 | 27.8
[42 empty] | 1987-07-08 | 16:00 | 27.8
[42 empty] | 1987-07-08 | 17:00 | 27.8
[42 empty] | 1987-07-08 | 18:00 | 26.7
[42 empty] | 1987-07-08 | 19:00 | 26.7
[42 empty] | 1987-07-08 | 20:00 | 25
[42 empty] | 1987-07-08 | 21:00 | 23.9
[42 empty] | 1987-07-08 | 22:00 | 23.9
[42 empty] | 1987-07-08 | 23:00 | 23.9
[42 empty] | 1987-07-08 | 24:00 | 22.8
[42 empty] | 1987-07-09 | 1:00 | 22.8
[42 empty] | 1987-07-09 | 2:00 | 22.8
[42 empty] | 1987-07-09 | 3:00 | 23.3
[42 empty] | 1987-07-09 | 4:00 | 22.8
[42 empty] | 1987-07-09 | 5:00 | 22.8
[42 empty] | 1987-07-09 | 6:00 | 23.3
[42 empty] | 1987-07-09 | 7:00 | 25.6
[42 empty] | 1987-07-09 | 8:00 | 27.2
[42 empty] | 1987-07-09 | 9:00 | 28.3
[42 empty] | 1987-07-09 | 10:00 | 30
[42 empty] | 1987-07-09 | 11:00 | 31.7
[42 empty] | 1987-07-09 | 12:00 | 32.2
[42 empty] | 1987-07-09 | 13:00 | 33.3
[42 empty] | 1987-07-09 | 14:00 | 31.7
[42 empty] | 1987-07-09 | 15:00 | 23.9
[42 empty] | 1987-07-09 | 16:00 | 26.7
[42 empty] | 1987-07-09 | 17:00 | 28.3
[42 empty] | 1987-07-09 | 18:00 | 28.9
[42 empty] | 1987-07-09 | 19:00 | 29.4
[42 empty] | 1987-07-09 | 20:00 | 28.3
[42 empty] | 1987-07-09 | 21:00 | 27.2
[42 empty] | 1987-07-09 | 22:00 | 27.2
[42 empty] | 1987-07-09 | 23:00 | 26.7
[42 empty] | 1987-07-09 | 24:00 | 25
[42 empty] | 1987-07-10 | 1:00 | 25
[42 empty] | 1987-07-10 | 2:00 | 23.9
[42 empty] | 1987-07-10 | 3:00 | 23.9
[42 empty] | 1987-07-10 | 4:00 | 23.3
[42 empty] | 1987-07-10 | 5:00 | 22.8
[42 empty] | 1987-07-10 | 6:00 | 23.9
[42 empty] | 1987-07-10 | 7:00 | 26.1
[42 empty] | 1987-07-10 | 8:00 | 27.8
[42 empty] | 1987-07-10 | 9:00 | 28.3
[42 empty] | 1987-07-10 | 10:00 | 28.3
[42 empty] | 1987-07-10 | 11:00 | 29.4
[42 empty] | 1987-07-10 | 12:00 | 31.1
[42 empty] | 1987-07-10 | 13:00 | 31.7
[42 empty] | 1987-07-10 | 14:00 | 31.7
[42 empty] | 1987-07-10 | 15:00 | 32.8
[42 empty] | 1987-07-10 | 16:00 | 32.8
[42 empty] | 1987-07-10 | 17:00 | 32.8
[42 empty] | 1987-07-10 | 18:00 | 30
[42 empty] | 1987-07-10 | 19:00 | 28.3
[42 empty] | 1987-07-10 | 20:00 | 26.7
[42 empty] | 1987-07-10 | 21:00 | 26.7
[42 empty] | 1987-07-10 | 22:00 | 27.2
[42 empty] | 1987-07-10 | 23:00 | 25.6
[42 empty] | 1987-07-10 | 24:00 | 26.1
[42 empty] | 1987-07-11 | 1:00 | 26.1
[42 empty] | 1987-07-11 | 2:00 | 24.4
[42 empty] | 1987-07-11 | 3:00 | 24.4
[42 empty] | 1987-07-11 | 4:00 | 23.9
[42 empty] | 1987-07-11 | 5:00 | 23.9
[42 empty] | 1987-07-11 | 6:00 | 25
[42 empty] | 1987-07-11 | 7:00 | 25.6
[42 empty] | 1987-07-11 | 8:00 | 26.7
[42 empty] | 1987-07-11 | 9:00 | 27.8
[42 empty] | 1987-07-11 | 10:00 | 29.4
[42 empty] | 1987-07-11 | 11:00 | 30.6
[42 empty] | 1987-07-11 | 12:00 | 31.7
[42 empty] | 1987-07-11 | 13:00 | 32.8
[42 empty] | 1987-07-11 | 14:00 | 31.7
[42 empty] | 1987-07-11 | 15:00 | 31.7
[42 empty] | 1987-07-11 | 16:00 | 32.2
[42 empty] | 1987-07-11 | 17:00 | 31.7
[42 empty] | 1987-07-11 | 18:00 | 30.6
[42 empty] | 1987-07-11 | 19:00 | 27.2
[42 empty] | 1987-07-11 | 20:00 | 26.1
[42 empty] | 1987-07-11 | 21:00 | 26.1
[42 empty] | 1987-07-11 | 22:00 | 25.6
[42 empty] | 1987-07-11 | 23:00 | 25
[42 empty] | 1987-07-11 | 24:00 | 25
[42 empty] | 1987-07-12 | 1:00 | 25
[42 empty] | 1987-07-12 | 2:00 | 25.6
[42 empty] | 1987-07-12 | 3:00 | 25
[42 empty] | 1987-07-12 | 4:00 | 25
[42 empty] | 1987-07-12 | 5:00 | 24.4
[42 empty] | 1987-07-12 | 6:00 | 24.4
[42 empty] | 1987-07-12 | 7:00 | 25
[42 empty] | 1987-07-12 | 8:00 | 26.1
[42 empty] | 1987-07-12 | 9:00 | 27.8
[42 empty] | 1987-07-12 | 10:00 | 28.9
[42 empty] | 1987-07-12 | 11:00 | 30
[42 empty] | 1987-07-12 | 12:00 | 30.6
[42 empty] | 1987-07-12 | 13:00 | 31.1
[42 empty] | 1987-07-12 | 14:00 | 30
[42 empty] | 1987-07-12 | 15:00 | 30
[42 empty] | 1987-07-12 | 16:00 | 28.9
[42 empty] | 1987-07-12 | 17:00 | 27.2
[42 empty] | 1987-07-12 | 18:00 | 26.7
[42 empty] | 1987-07-12 | 19:00 | 25.6
[42 empty] | 1987-07-12 | 20:00 | 25
[42 empty] | 1987-07-12 | 21:00 | 24.4
[42 empty] | 1987-07-12 | 22:00 | 25
[42 empty] | 1987-07-12 | 23:00 | 24.4
[42 empty] | 1987-07-12 | 24:00 | 23.9
[42 empty] | 1987-07-13 | 1:00 | 23.9
[42 empty] | 1987-07-13 | 2:00 | 23.9
[42 empty] | 1987-07-13 | 3:00 | 22.8
[42 empty] | 1987-07-13 | 4:00 | 22.8
[42 empty] | 1987-07-13 | 5:00 | 22.2
[42 empty] | 1987-07-13 | 6:00 | 24.4
[42 empty] | 1987-07-13 | 7:00 | 25.6
[42 empty] | 1987-07-13 | 8:00 | 27.2
[42 empty] | 1987-07-13 | 9:00 | 28.3
[42 empty] | 1987-07-13 | 10:00 | 28.9
[42 empty] | 1987-07-13 | 11:00 | 30.6
[42 empty] | 1987-07-13 | 12:00 | 30.6
[42 empty] | 1987-07-13 | 13:00 | 31.1
[42 empty] | 1987-07-13 | 14:00 | 30.6
[42 empty] | 1987-07-13 | 15:00 | 30.6
[42 empty] | 1987-07-13 | 16:00 | 29.4
[42 empty] | 1987-07-13 | 17:00 | 28.9
[42 empty] | 1987-07-13 | 18:00 | 27.8
[42 empty] | 1987-07-13 | 19:00 | 26.7
[42 empty] | 1987-07-13 | 20:00 | 26.1
[42 empty] | 1987-07-13 | 21:00 | 25.6
[42 empty] | 1987-07-13 | 22:00 | 25
[42 empty] | 1987-07-13 | 23:00 | 25.6
[42 empty] | 1987-07-13 | 24:00 | 25
[42 empty] | 1987-07-14 | 1:00 | 25
[42 empty] | 1987-07-14 | 2:00 | 25
[42 empty] | 1987-07-14 | 3:00 | 24.4
[42 empty] | 1987-07-14 | 4:00 | 24.4
[42 empty] | 1987-07-14 | 5:00 | 24.4
[42 empty] | 1987-07-14 | 6:00 | 25
[42 empty] | 1987-07-14 | 7:00 | 25.6
[42 empty] | 1987-07-14 | 8:00 | 26.1
[42 empty] | 1987-07-14 | 9:00 | 26.1
[42 empty] | 1987-07-14 | 10:00 | 26.1
[42 empty] | 1987-07-14 | 11:00 | 27.2
[42 empty] | 1987-07-14 | 12:00 | 28.9
[42 empty] | 1987-07-14 | 13:00 | 28.9
[42 empty] | 1987-07-14 | 14:00 | 28.9
[42 empty] | 1987-07-14 | 15:00 | 26.1
[42 empty] | 1987-07-14 | 16:00 | 22.8
[42 empty] | 1987-07-14 | 17:00 | 22.2
[42 empty] | 1987-07-14 | 18:00 | 22.2
[42 empty] | 1987-07-14 | 19:00 | 22.8
[42 empty] | 1987-07-14 | 20:00 | 22.8
[42 empty] | 1987-07-14 | 21:00 | 20
[42 empty] | 1987-07-14 | 22:00 | 20
[42 empty] | 1987-07-14 | 23:00 | 19.4
[42 empty] | 1987-07-14 | 24:00 | 20
[42 empty] | 1987-07-15 | 1:00 | 20
[42 empty] | 1987-07-15 | 2:00 | 20
[42 empty] | 1987-07-15 | 3:00 | 19.4
[42 empty] | 1987-07-15 | 4:00 | 18.9
[42 empty] | 1987-07-15 | 5:00 | 18.3
[42 empty] | 1987-07-15 | 6:00 | 18.3
[42 empty] | 1987-07-15 | 7:00 | 18.9
[42 empty] | 1987-07-15 | 8:00 | 19.4
[42 empty] | 1987-07-15 | 9:00 | 20.6
[42 empty] | 1987-07-15 | 10:00 | 22.2
[42 empty] | 1987-07-15 | 11:00 | 23.3
[42 empty] | 1987-07-15 | 12:00 | 23.3
[42 empty] | 1987-07-15 | 13:00 | 24.4
[42 empty] | 1987-07-15 | 14:00 | 25
[42 empty] | 1987-07-15 | 15:00 | 25
[42 empty] | 1987-07-15 | 16:00 | 25
[42 empty] | 1987-07-15 | 17:00 | 24.4
[42 empty] | 1987-07-15 | 18:00 | 24.4
[42 empty] | 1987-07-15 | 19:00 | 23.3
[42 empty] | 1987-07-15 | 20:00 | 22.2
[42 empty] | 1987-07-15 | 21:00 | 21.7
[42 empty] | 1987-07-15 | 22:00 | 21.1
[42 empty] | 1987-07-15 | 23:00 | 20
[42 empty] | 1987-07-15 | 24:00 | 19.4
[42 empty] | 1987-07-16 | 1:00 | 19.4
[42 empty] | 1987-07-16 | 2:00 | 18.9
[42 empty] | 1987-07-16 | 3:00 | 18.3
[42 empty] | 1987-07-16 | 4:00 | 17.8
[42 empty] | 1987-07-16 | 5:00 | 18.3
[42 empty] | 1987-07-16 | 6:00 | 18.3
[42 empty] | 1987-07-16 | 7:00 | 18.9
[42 empty] | 1987-07-16 | 8:00 | 20
[42 empty] | 1987-07-16 | 9:00 | 21.1
[42 empty] | 1987-07-16 | 10:00 | 22.2
[42 empty] | 1987-07-16 | 11:00 | 22.8
[42 empty] | 1987-07-16 | 12:00 | 23.3
[42 empty] | 1987-07-16 | 13:00 | 22.8
[42 empty] | 1987-07-16 | 14:00 | 22.8
[42 empty] | 1987-07-16 | 15:00 | 22.8
[42 empty] | 1987-07-16 | 16:00 | 22.8
[42 empty] | 1987-07-16 | 17:00 | 23.3
[42 empty] | 1987-07-16 | 18:00 | 23.3
[42 empty] | 1987-07-16 | 19:00 | 23.3
[42 empty] | 1987-07-16 | 20:00 | 21.7
[42 empty] | 1987-07-16 | 21:00 | 21.1
[42 empty] | 1987-07-16 | 22:00 | 20.6
[42 empty] | 1987-07-16 | 23:00 | 20
[42 empty] | 1987-07-16 | 24:00 | 20
[42 empty] | 1987-07-17 | 1:00 | 18.9
[42 empty] | 1987-07-17 | 2:00 | 17.8
[42 empty] | 1987-07-17 | 3:00 | 17.8
[42 empty] | 1987-07-17 | 4:00 | 17.8
[42 empty] | 1987-07-17 | 5:00 | 17.8
[42 empty] | 1987-07-17 | 6:00 | 19.4
[42 empty] | 1987-07-17 | 7:00 | 21.1
[42 empty] | 1987-07-17 | 8:00 | 22.8
[42 empty] | 1987-07-17 | 9:00 | 23.9
[42 empty] | 1987-07-17 | 10:00 | 24.4
[42 empty] | 1987-07-17 | 11:00 | 25.6
[42 empty] | 1987-07-17 | 12:00 | 25.6
[42 empty] | 1987-07-17 | 13:00 | 26.7
[42 empty] | 1987-07-17 | 14:00 | 27.2
[42 empty] | 1987-07-17 | 15:00 | 27.2
[42 empty] | 1987-07-17 | 16:00 | 27.2
[42 empty] | 1987-07-17 | 17:00 | 27.2
[42 empty] | 1987-07-17 | 18:00 | 25.6
[42 empty] | 1987-07-17 | 19:00 | 25
[42 empty] | 1987-07-17 | 20:00 | 23.9
[42 empty] | 1987-07-17 | 21:00 | 23.3
[42 empty] | 1987-07-17 | 22:00 | 23.3
[42 empty] | 1987-07-17 | 23:00 | 23.3
[42 empty] | 1987-07-17 | 24:00 | 22.2
[42 empty] | 1987-07-18 | 1:00 | 21.7
[42 empty] | 1987-07-18 | 2:00 | 21.1
[42 empty] | 1987-07-18 | 3:00 | 20.6
[42 empty] | 1987-07-18 | 4:00 | 21.1
[42 empty] | 1987-07-18 | 5:00 | 21.7
[42 empty] | 1987-07-18 | 6:00 | 21.7
[42 empty] | 1987-07-18 | 7:00 | 22.2
[42 empty] | 1987-07-18 | 8:00 | 24.4
[42 empty] | 1987-07-18 | 9:00 | 26.1
[42 empty] | 1987-07-18 | 10:00 | 27.8
[42 empty] | 1987-07-18 | 11:00 | 28.9
[42 empty] | 1987-07-18 | 12:00 | 29.4
[42 empty] | 1987-07-18 | 13:00 | 30.6
[42 empty] | 1987-07-18 | 14:00 | 31.1
[42 empty] | 1987-07-18 | 15:00 | 31.7
[42 empty] | 1987-07-18 | 16:00 | 31.7
[42 empty] | 1987-07-18 | 17:00 | 31.1
[42 empty] | 1987-07-18 | 18:00 | 30
[42 empty] | 1987-07-18 | 19:00 | 30
[42 empty] | 1987-07-18 | 20:00 | 29.4
[42 empty] | 1987-07-18 | 21:00 | 28.9
[42 empty] | 1987-07-18 | 22:00 | 27.8
[42 empty] | 1987-07-18 | 23:00 | 27.2
[42 empty] | 1987-07-18 | 24:00 | 26.7
[42 empty] | 1987-07-19 | 1:00 | 26.1
[42 empty] | 1987-07-19 | 2:00 | 25
[42 empty] | 1987-07-19 | 3:00 | 25
[42 empty] | 1987-07-19 | 4:00 | 24.4
[42 empty] | 1987-07-19 | 5:00 | 24.4
[42 empty] | 1987-07-19 | 6:00 | 25
[42 empty] | 1987-07-19 | 7:00 | 25.6
[42 empty] | 1987-07-19 | 8:00 | 26.7
[42 empty] | 1987-07-19 | 9:00 | 28.3
[42 empty] | 1987-07-19 | 10:00 | 30
[42 empty] | 1987-07-19 | 11:00 | 30
[42 empty] | 1987-07-19 | 12:00 | 30.6
[42 empty] | 1987-07-19 | 13:00 | 31.7
[42 empty] | 1987-07-19 | 14:00 | 31.1
[42 empty] | 1987-07-19 | 15:00 | 30
[42 empty] | 1987-07-19 | 16:00 | 29.4
[42 empty] | 1987-07-19 | 17:00 | 26.1
[42 empty] | 1987-07-19 | 18:00 | 26.1
[42 empty] | 1987-07-19 | 19:00 | 25.6
[42 empty] | 1987-07-19 | 20:00 | 24.4
[42 empty] | 1987-07-19 | 21:00 | 23.9
[42 empty] | 1987-07-19 | 22:00 | 23.3
[42 empty] | 1987-07-19 | 23:00 | 22.8
[42 empty] | 1987-07-19 | 24:00 | 22.8
[42 empty] | 1987-07-20 | 1:00 | 22.8
[42 empty] | 1987-07-20 | 2:00 | 22.2
[42 empty] | 1987-07-20 | 3:00 | 22.8
[42 empty] | 1987-07-20 | 4:00 | 22.8
[42 empty] | 1987-07-20 | 5:00 | 22.8
[42 empty] | 1987-07-20 | 6:00 | 22.8
[42 empty] | 1987-07-20 | 7:00 | 23.3
[42 empty] | 1987-07-20 | 8:00 | 23.9
[42 empty] | 1987-07-20 | 9:00 | 24.4
[42 empty] | 1987-07-20 | 10:00 | 26.1
[42 empty] | 1987-07-20 | 11:00 | 26.1
[42 empty] | 1987-07-20 | 12:00 | 23.9
[42 empty] | 1987-07-20 | 13:00 | 25.6
[42 empty] | 1987-07-20 | 14:00 | 27.8
[42 empty] | 1987-07-20 | 15:00 | 28.9
[42 empty] | 1987-07-20 | 16:00 | 28.3
[42 empty] | 1987-07-20 | 17:00 | 28.9
[42 empty] | 1987-07-20 | 18:00 | 29.4
[42 empty] | 1987-07-20 | 19:00 | 29.4
[42 empty] | 1987-07-20 | 20:00 | 28.3
[42 empty] | 1987-07-20 | 21:00 | 27.8
[42 empty] | 1987-07-20 | 22:00 | 25.6
[42 empty] | 1987-07-20 | 23:00 | 25.6
[42 empty] | 1987-07-20 | 24:00 | 26.1
[42 empty] | 1987-07-21 | 1:00 | 25.6
[42 empty] | 1987-07-21 | 2:00 | 26.1
[42 empty] | 1987-07-21 | 3:00 | 24.4
[42 empty] | 1987-07-21 | 4:00 | 23.9
[42 empty] | 1987-07-21 | 5:00 | 23.9
[42 empty] | 1987-07-21 | 6:00 | 23.9
[42 empty] | 1987-07-21 | 7:00 | 25
[42 empty] | 1987-07-21 | 8:00 | 26.1
[42 empty] | 1987-07-21 | 9:00 | 28.3
[42 empty] | 1987-07-21 | 10:00 | 28.9
[42 empty] | 1987-07-21 | 11:00 | 29.4
[42 empty] | 1987-07-21 | 12:00 | 31.1
[42 empty] | 1987-07-21 | 13:00 | 31.1
[42 empty] | 1987-07-21 | 14:00 | 32.2
[42 empty] | 1987-07-21 | 15:00 | 32.2
[42 empty] | 1987-07-21 | 16:00 | 32.8
[42 empty] | 1987-07-21 | 17:00 | 32.2
[42 empty] | 1987-07-21 | 18:00 | 31.7
[42 empty] | 1987-07-21 | 19:00 | 31.1
[42 empty] | 1987-07-21 | 20:00 | 29.4
[42 empty] | 1987-07-21 | 21:00 | 29.4
[42 empty] | 1987-07-21 | 22:00 | 28.3
[42 empty] | 1987-07-21 | 23:00 | 26.7
[42 empty] | 1987-07-21 | 24:00 | 25
[42 empty] | 1987-07-22 | 1:00 | 25.6
[42 empty] | 1987-07-22 | 2:00 | 24.4
[42 empty] | 1987-07-22 | 3:00 | 23.3
[42 empty] | 1987-07-22 | 4:00 | 22.8
[42 empty] | 1987-07-22 | 5:00 | 22.2
[42 empty] | 1987-07-22 | 6:00 | 22.8
[42 empty] | 1987-07-22 | 7:00 | 23.3
[42 empty] | 1987-07-22 | 8:00 | 24.4
[42 empty] | 1987-07-22 | 9:00 | 26.1
[42 empty] | 1987-07-22 | 10:00 | 27.8
[42 empty] | 1987-07-22 | 11:00 | 28.9
[42 empty] | 1987-07-22 | 12:00 | 30
[42 empty] | 1987-07-22 | 13:00 | 30.6
[42 empty] | 1987-07-22 | 14:00 | 31.1
[42 empty] | 1987-07-22 | 15:00 | 31.1
[42 empty] | 1987-07-22 | 16:00 | 30.6
[42 empty] | 1987-07-22 | 17:00 | 30
[42 empty] | 1987-07-22 | 18:00 | 29.4
[42 empty] | 1987-07-22 | 19:00 | 28.3
[42 empty] | 1987-07-22 | 20:00 | 27.2
[42 empty] | 1987-07-22 | 21:00 | 26.7
[42 empty] | 1987-07-22 | 22:00 | 27.2
[42 empty] | 1987-07-22 | 23:00 | 26.7
[42 empty] | 1987-07-22 | 24:00 | 25
[42 empty] | 1987-07-23 | 1:00 | 23.3
[42 empty] | 1987-07-23 | 2:00 | 22.8
[42 empty] | 1987-07-23 | 3:00 | 23.3
[42 empty] | 1987-07-23 | 4:00 | 22.8
[42 empty] | 1987-07-23 | 5:00 | 22.8
[42 empty] | 1987-07-23 | 6:00 | 22.8
[42 empty] | 1987-07-23 | 7:00 | 23.3
[42 empty] | 1987-07-23 | 8:00 | 23.9
[42 empty] | 1987-07-23 | 9:00 | 25
[42 empty] | 1987-07-23 | 10:00 | 27.8
[42 empty] | 1987-07-23 | 11:00 | 28.3
[42 empty] | 1987-07-23 | 12:00 | 28.9
[42 empty] | 1987-07-23 | 13:00 | 30
[42 empty] | 1987-07-23 | 14:00 | 29.4
[42 empty] | 1987-07-23 | 15:00 | 29.4
[42 empty] | 1987-07-23 | 16:00 | 29.4
[42 empty] | 1987-07-23 | 17:00 | 28.3
[42 empty] | 1987-07-23 | 18:00 | 27.2
[42 empty] | 1987-07-23 | 19:00 | 26.1
[42 empty] | 1987-07-23 | 20:00 | 25
[42 empty] | 1987-07-23 | 21:00 | 25
[42 empty] | 1987-07-23 | 22:00 | 25
[42 empty] | 1987-07-23 | 23:00 | 25
[42 empty] | 1987-07-23 | 24:00 | 25
[42 empty] | 1987-07-24 | 1:00 | 25
[42 empty] | 1987-07-24 | 2:00 | 25
[42 empty] | 1987-07-24 | 3:00 | 25
[42 empty] | 1987-07-24 | 4:00 | 24.4
[42 empty] | 1987-07-24 | 5:00 | 24.4
[42 empty] | 1987-07-24 | 6:00 | 25
[42 empty] | 1987-07-24 | 7:00 | 25.6
[42 empty] | 1987-07-24 | 8:00 | 27.2
[42 empty] | 1987-07-24 | 9:00 | 28.9
[42 empty] | 1987-07-24 | 10:00 | 30.6
[42 empty] | 1987-07-24 | 11:00 | 32.2
[42 empty] | 1987-07-24 | 12:00 | 33.3
[42 empty] | 1987-07-24 | 13:00 | 33.3
[42 empty] | 1987-07-24 | 14:00 | 33.9
[42 empty] | 1987-07-24 | 15:00 | 32.8
[42 empty] | 1987-07-24 | 16:00 | 33.3
[42 empty] | 1987-07-24 | 17:00 | 32.2
[42 empty] | 1987-07-24 | 18:00 | 31.1
[42 empty] | 1987-07-24 | 19:00 | 31.1
[42 empty] | 1987-07-24 | 20:00 | 31.1
[42 empty] | 1987-07-24 | 21:00 | 30
[42 empty] | 1987-07-24 | 22:00 | 27.8
[42 empty] | 1987-07-24 | 23:00 | 27.8
[42 empty] | 1987-07-24 | 24:00 | 27.2
[42 empty] | 1987-07-25 | 1:00 | 27.2
[42 empty] | 1987-07-25 | 2:00 | 26.7
[42 empty] | 1987-07-25 | 3:00 | 26.7
[42 empty] | 1987-07-25 | 4:00 | 26.1
[42 empty] | 1987-07-25 | 5:00 | 26.1
[42 empty] | 1987-07-25 | 6:00 | 26.7
[42 empty] | 1987-07-25 | 7:00 | 27.2
[42 empty] | 1987-07-25 | 8:00 | 28.3
[42 empty] | 1987-07-25 | 9:00 | 30
[42 empty] | 1987-07-25 | 10:00 | 31.7
[42 empty] | 1987-07-25 | 11:00 | 32.8
[42 empty] | 1987-07-25 | 12:00 | 32.8
[42 empty] | 1987-07-25 | 13:00 | 32.2
[42 empty] | 1987-07-25 | 14:00 | 33.3
[42 empty] | 1987-07-25 | 15:00 | 33.9
[42 empty] | 1987-07-25 | 16:00 | 33.3
[42 empty] | 1987-07-25 | 17:00 | 31.7
[42 empty] | 1987-07-25 | 18:00 | 31.7
[42 empty] | 1987-07-25 | 19:00 | 28.9
[42 empty] | 1987-07-25 | 20:00 | 29.4
[42 empty] | 1987-07-25 | 21:00 | 30.6
[42 empty] | 1987-07-25 | 22:00 | 30
[42 empty] | 1987-07-25 | 23:00 | 29.4
[42 empty] | 1987-07-25 | 24:00 | 29.4
[42 empty] | 1987-07-26 | 1:00 | 28.3
[42 empty] | 1987-07-26 | 2:00 | 24.4
[42 empty] | 1987-07-26 | 3:00 | 24.4
[42 empty] | 1987-07-26 | 4:00 | 23.9
[42 empty] | 1987-07-26 | 5:00 | 23.9
[42 empty] | 1987-07-26 | 6:00 | 24.4
[42 empty] | 1987-07-26 | 7:00 | 25.6
[42 empty] | 1987-07-26 | 8:00 | 27.2
[42 empty] | 1987-07-26 | 9:00 | 28.3
[42 empty] | 1987-07-26 | 10:00 | 27.8
[42 empty] | 1987-07-26 | 11:00 | 26.1
[42 empty] | 1987-07-26 | 12:00 | 21.7
[42 empty] | 1987-07-26 | 13:00 | 22.8
[42 empty] | 1987-07-26 | 14:00 | 26.1
[42 empty] | 1987-07-26 | 15:00 | 25.6
[42 empty] | 1987-07-26 | 16:00 | 25.6
[42 empty] | 1987-07-26 | 17:00 | 26.7
[42 empty] | 1987-07-26 | 18:00 | 27.2
[42 empty] | 1987-07-26 | 19:00 | 26.1
[42 empty] | 1987-07-26 | 20:00 | 25.6
[42 empty] | 1987-07-26 | 21:00 | 25
[42 empty] | 1987-07-26 | 22:00 | 25
[42 empty] | 1987-07-26 | 23:00 | 24.4
[42 empty] | 1987-07-26 | 24:00 | 24.4
[42 empty] | 1987-07-27 | 1:00 | 23.9
[42 empty] | 1987-07-27 | 2:00 | 23.3
[42 empty] | 1987-07-27 | 3:00 | 23.3
[42 empty] | 1987-07-27 | 4:00 | 21.7
[42 empty] | 1987-07-27 | 5:00 | 21.1
[42 empty] | 1987-07-27 | 6:00 | 21.7
[42 empty] | 1987-07-27 | 7:00 | 22.8
[42 empty] | 1987-07-27 | 8:00 | 23.9
[42 empty] | 1987-07-27 | 9:00 | 25
[42 empty] | 1987-07-27 | 10:00 | 26.1
[42 empty] | 1987-07-27 | 11:00 | 27.2
[42 empty] | 1987-07-27 | 12:00 | 26.7
[42 empty] | 1987-07-27 | 13:00 | 27.2
[42 empty] | 1987-07-27 | 14:00 | 27.8
[42 empty] | 1987-07-27 | 15:00 | 28.3
[42 empty] | 1987-07-27 | 16:00 | 28.3
[42 empty] | 1987-07-27 | 17:00 | 28.3
[42 empty] | 1987-07-27 | 18:00 | 27.2
[42 empty] | 1987-07-27 | 19:00 | 25.6
[42 empty] | 1987-07-27 | 20:00 | 23.9
[42 empty] | 1987-07-27 | 21:00 | 23.9
[42 empty] | 1987-07-27 | 22:00 | 23.3
[42 empty] | 1987-07-27 | 23:00 | 23.3
[42 empty] | 1987-07-27 | 24:00 | 22.8
[42 empty] | 1987-07-28 | 1:00 | 22.8
[42 empty] | 1987-07-28 | 2:00 | 22.2
[42 empty] | 1987-07-28 | 3:00 | 21.7
[42 empty] | 1987-07-28 | 4:00 | 21.7
[42 empty] | 1987-07-28 | 5:00 | 21.1
[42 empty] | 1987-07-28 | 6:00 | 22.2
[42 empty] | 1987-07-28 | 7:00 | 23.3
[42 empty] | 1987-07-28 | 8:00 | 25
[42 empty] | 1987-07-28 | 9:00 | 25.6
[42 empty] | 1987-07-28 | 10:00 | 26.7
[42 empty] | 1987-07-28 | 11:00 | 28.3
[42 empty] | 1987-07-28 | 12:00 | 29.4
[42 empty] | 1987-07-28 | 13:00 | 30
[42 empty] | 1987-07-28 | 14:00 | 30
[42 empty] | 1987-07-28 | 15:00 | 27.8
[42 empty] | 1987-07-28 | 16:00 | 27.8
[42 empty] | 1987-07-28 | 17:00 | 27.2
[42 empty] | 1987-07-28 | 18:00 | 27.2
[42 empty] | 1987-07-28 | 19:00 | 26.7
[42 empty] | 1987-07-28 | 20:00 | 25
[42 empty] | 1987-07-28 | 21:00 | 25
[42 empty] | 1987-07-28 | 22:00 | 23.9
[42 empty] | 1987-07-28 | 23:00 | 23.3
[42 empty] | 1987-07-28 | 24:00 | 22.2
[42 empty] | 1987-07-29 | 1:00 | 21.1
[42 empty] | 1987-07-29 | 2:00 | 20
[42 empty] | 1987-07-29 | 3:00 | 18.9
[42 empty] | 1987-07-29 | 4:00 | 18.3
[42 empty] | 1987-07-29 | 5:00 | 17.2
[42 empty] | 1987-07-29 | 6:00 | 18.3
[42 empty] | 1987-07-29 | 7:00 | 19.4
[42 empty] | 1987-07-29 | 8:00 | 20.6
[42 empty] | 1987-07-29 | 9:00 | 21.1
[42 empty] | 1987-07-29 | 10:00 | 22.2
[42 empty] | 1987-07-29 | 11:00 | 23.9
[42 empty] | 1987-07-29 | 12:00 | 24.4
[42 empty] | 1987-07-29 | 13:00 | 25.6
[42 empty] | 1987-07-29 | 14:00 | 26.1
[42 empty] | 1987-07-29 | 15:00 | 26.7
[42 empty] | 1987-07-29 | 16:00 | 26.7
[42 empty] | 1987-07-29 | 17:00 | 24.4
[42 empty] | 1987-07-29 | 18:00 | 25.6
[42 empty] | 1987-07-29 | 19:00 | 23.3
[42 empty] | 1987-07-29 | 20:00 | 22.8
[42 empty] | 1987-07-29 | 21:00 | 21.7
[42 empty] | 1987-07-29 | 22:00 | 21.7
[42 empty] | 1987-07-29 | 23:00 | 21.1
[42 empty] | 1987-07-29 | 24:00 | 21.1
[42 empty] | 1987-07-30 | 1:00 | 20.6
[42 empty] | 1987-07-30 | 2:00 | 20.6
[42 empty] | 1987-07-30 | 3:00 | 20.6
[42 empty] | 1987-07-30 | 4:00 | 20.6
[42 empty] | 1987-07-30 | 5:00 | 20.6
[42 empty] | 1987-07-30 | 6:00 | 20.6
[42 empty] | 1987-07-30 | 7:00 | 21.7
[42 empty] | 1987-07-30 | 8:00 | 23.9
[42 empty] | 1987-07-30 | 9:00 | 25
[42 empty] | 1987-07-30 | 10:00 | 25.6
[42 empty] | 1987-07-30 | 11:00 | 27.2
[42 empty] | 1987-07-30 | 12:00 | 28.3
[42 empty] | 1987-07-30 | 13:00 | 27.8
[42 empty] | 1987-07-30 | 14:00 | 27.2
[42 empty] | 1987-07-30 | 15:00 | 27.8
[42 empty] | 1987-07-30 | 16:00 | 24.4
[42 empty] | 1987-07-30 | 17:00 | 25.6
[42 empty] | 1987-07-30 | 18:00 | 26.1
[42 empty] | 1987-07-30 | 19:00 | 25
[42 empty] | 1987-07-30 | 20:00 | 25
[42 empty] | 1987-07-30 | 21:00 | 24.4
[42 empty] | 1987-07-30 | 22:00 | 24.4
[42 empty] | 1987-07-30 | 23:00 | 24.4
[42 empty] | 1987-07-30 | 24:00 | 23.9
[42 empty] | 1987-07-31 | 1:00 | 22.8
[42 empty] | 1987-07-31 | 2:00 | 23.3
[42 empty] | 1987-07-31 | 3:00 | 22.2
[42 empty] | 1987-07-31 | 4:00 | 22.2
[42 empty] | 1987-07-31 | 5:00 | 22.8
[42 empty] | 1987-07-31 | 6:00 | 22.2
[42 empty] | 1987-07-31 | 7:00 | 22.2
[42 empty] | 1987-07-31 | 8:00 | 23.9
[42 empty] | 1987-07-31 | 9:00 | 23.9
[42 empty] | 1987-07-31 | 10:00 | 24.4
[42 empty] | 1987-07-31 | 11:00 | 25
[42 empty] | 1987-07-31 | 12:00 | 26.7
[42 empty] | 1987-07-31 | 13:00 | 27.2
[42 empty] | 1987-07-31 | 14:00 | 28.3
[42 empty] | 1987-07-31 | 15:00 | 28.9
[42 empty] | 1987-07-31 | 16:00 | 26.7
[42 empty] | 1987-07-31 | 17:00 | 26.1
[42 empty] | 1987-07-31 | 18:00 | 25.6
[42 empty] | 1987-07-31 | 19:00 | 24.4
[42 empty] | 1987-07-31 | 20:00 | 23.9
[42 empty] | 1987-07-31 | 21:00 | 22.8
[42 empty] | 1987-07-31 | 22:00 | 22.5
[42 empty] | 1987-07-31 | 23:00 | 22.2
[42 empty] | 1987-07-31 | 24:00 | 21.9
[42 empty] | 1987-08-01 | 1:00 | 21.5
[42 empty] | 1987-08-01 | 2:00 | 21.2
[42 empty] | 1987-08-01 | 3:00 | 20.9
[42 empty] | 1987-08-01 | 4:00 | 20.6
[42 empty] | 1987-08-01 | 5:00 | 18.9
[42 empty] | 1987-08-01 | 6:00 | 18.9
[42 empty] | 1987-08-01 | 7:00 | 20.6
[42 empty] | 1987-08-01 | 8:00 | 21.1
[42 empty] | 1987-08-01 | 9:00 | 22.8
[42 empty] | 1987-08-01 | 10:00 | 25
[42 empty] | 1987-08-01 | 11:00 | 25.6
[42 empty] | 1987-08-01 | 12:00 | 26.7
[42 empty] | 1987-08-01 | 13:00 | 25.6
[42 empty] | 1987-08-01 | 14:00 | 25.6
[42 empty] | 1987-08-01 | 15:00 | 27.2
[42 empty] | 1987-08-01 | 16:00 | 26.7
[42 empty] | 1987-08-01 | 17:00 | 26.1
[42 empty] | 1987-08-01 | 18:00 | 25
[42 empty] | 1987-08-01 | 19:00 | 24.4
[42 empty] | 1987-08-01 | 20:00 | 23.3
[42 empty] | 1987-08-01 | 21:00 | 23.3
[42 empty] | 1987-08-01 | 22:00 | 23.3
[42 empty] | 1987-08-01 | 23:00 | 22.8
[42 empty] | 1987-08-01 | 24:00 | 22.8
[42 empty] | 1987-08-02 | 1:00 | 22.8
[42 empty] | 1987-08-02 | 2:00 | 22.8
[42 empty] | 1987-08-02 | 3:00 | 22.2
[42 empty] | 1987-08-02 | 4:00 | 22.2
[42 empty] | 1987-08-02 | 5:00 | 22.2
[42 empty] | 1987-08-02 | 6:00 | 22.2
[42 empty] | 1987-08-02 | 7:00 | 22.8
[42 empty] | 1987-08-02 | 8:00 | 24.4
[42 empty] | 1987-08-02 | 9:00 | 25
[42 empty] | 1987-08-02 | 10:00 | 25
[42 empty] | 1987-08-02 | 11:00 | 24.4
[42 empty] | 1987-08-02 | 12:00 | 25
[42 empty] | 1987-08-02 | 13:00 | 25.6
[42 empty] | 1987-08-02 | 14:00 | 25
[42 empty] | 1987-08-02 | 15:00 | 25
[42 empty] | 1987-08-02 | 16:00 | 24.4
[42 empty] | 1987-08-02 | 17:00 | 25
[42 empty] | 1987-08-02 | 18:00 | 23.9
[42 empty] | 1987-08-02 | 19:00 | 24.4
[42 empty] | 1987-08-02 | 20:00 | 24.4
[42 empty] | 1987-08-02 | 21:00 | 23.9
[42 empty] | 1987-08-02 | 22:00 | 23.9
[42 empty] | 1987-08-02 | 23:00 | 23.9
[42 empty] | 1987-08-02 | 24:00 | 23.9
[42 empty] | 1987-08-03 | 1:00 | 23.9
[42 empty] | 1987-08-03 | 2:00 | 23.9
[42 empty] | 1987-08-03 | 3:00 | 23.9
[42 empty] | 1987-08-03 | 4:00 | 24.4
[42 empty] | 1987-08-03 | 5:00 | 23.3
[42 empty] | 1987-08-03 | 6:00 | 23.9
[42 empty] | 1987-08-03 | 7:00 | 23.9
[42 empty] | 1987-08-03 | 8:00 | 23.9
[42 empty] | 1987-08-03 | 9:00 | 24.4
[42 empty] | 1987-08-03 | 10:00 | 25.6
[42 empty] | 1987-08-03 | 11:00 | 27.8
[42 empty] | 1987-08-03 | 12:00 | 28.3
[42 empty] | 1987-08-03 | 13:00 | 30
[42 empty] | 1987-08-03 | 14:00 | 31.7
[42 empty] | 1987-08-03 | 15:00 | 31.1
[42 empty] | 1987-08-03 | 16:00 | 31.7
[42 empty] | 1987-08-03 | 17:00 | 31.1
[42 empty] | 1987-08-03 | 18:00 | 30.6
[42 empty] | 1987-08-03 | 19:00 | 29.4
[42 empty] | 1987-08-03 | 20:00 | 27.8
[42 empty] | 1987-08-03 | 21:00 | 27.2
[42 empty] | 1987-08-03 | 22:00 | 26.1
[42 empty] | 1987-08-03 | 23:00 | 26.1
[42 empty] | 1987-08-03 | 24:00 | 25
[42 empty] | 1987-08-04 | 1:00 | 25
[42 empty] | 1987-08-04 | 2:00 | 24.4
[42 empty] | 1987-08-04 | 3:00 | 24.4
[42 empty] | 1987-08-04 | 4:00 | 23.3
[42 empty] | 1987-08-04 | 5:00 | 23.3
[42 empty] | 1987-08-04 | 6:00 | 24.4
[42 empty] | 1987-08-04 | 7:00 | 25.6
[42 empty] | 1987-08-04 | 8:00 | 27.8
[42 empty] | 1987-08-04 | 9:00 | 28.3
[42 empty] | 1987-08-04 | 10:00 | 28.9
[42 empty] | 1987-08-04 | 11:00 | 29.4
[42 empty] | 1987-08-04 | 12:00 | 30.6
[42 empty] | 1987-08-04 | 13:00 | 31.7
[42 empty] | 1987-08-04 | 14:00 | 32.2
[42 empty] | 1987-08-04 | 15:00 | 31.7
[42 empty] | 1987-08-04 | 16:00 | 32.8
[42 empty] | 1987-08-04 | 17:00 | 32.8
[42 empty] | 1987-08-04 | 18:00 | 30.6
[42 empty] | 1987-08-04 | 19:00 | 29.4
[42 empty] | 1987-08-04 | 20:00 | 27.8
[42 empty] | 1987-08-04 | 21:00 | 27.8
[42 empty] | 1987-08-04 | 22:00 | 27.2
[42 empty] | 1987-08-04 | 23:00 | 26.7
[42 empty] | 1987-08-04 | 24:00 | 26.1
[42 empty] | 1987-08-05 | 1:00 | 26.1
[42 empty] | 1987-08-05 | 2:00 | 25
[42 empty] | 1987-08-05 | 3:00 | 25
[42 empty] | 1987-08-05 | 4:00 | 24.4
[42 empty] | 1987-08-05 | 5:00 | 23.9
[42 empty] | 1987-08-05 | 6:00 | 25
[42 empty] | 1987-08-05 | 7:00 | 26.1
[42 empty] | 1987-08-05 | 8:00 | 26.7
[42 empty] | 1987-08-05 | 9:00 | 26.7
[42 empty] | 1987-08-05 | 10:00 | 26.7
[42 empty] | 1987-08-05 | 11:00 | 28.3
[42 empty] | 1987-08-05 | 12:00 | 28.3
[42 empty] | 1987-08-05 | 13:00 | 27.8
[42 empty] | 1987-08-05 | 14:00 | 26.7
[42 empty] | 1987-08-05 | 15:00 | 23.9
[42 empty] | 1987-08-05 | 16:00 | 23.3
[42 empty] | 1987-08-05 | 17:00 | 22.8
[42 empty] | 1987-08-05 | 18:00 | 21.7
[42 empty] | 1987-08-05 | 19:00 | 21.7
[42 empty] | 1987-08-05 | 20:00 | 21.7
[42 empty] | 1987-08-05 | 21:00 | 22.2
[42 empty] | 1987-08-05 | 22:00 | 22.2
[42 empty] | 1987-08-05 | 23:00 | 21.7
[42 empty] | 1987-08-05 | 24:00 | 20.6
[42 empty] | 1987-08-06 | 1:00 | 20
[42 empty] | 1987-08-06 | 2:00 | 20
[42 empty] | 1987-08-06 | 3:00 | 19.4
[42 empty] | 1987-08-06 | 4:00 | 18.9
[42 empty] | 1987-08-06 | 5:00 | 18.9
[42 empty] | 1987-08-06 | 6:00 | 18.9
[42 empty] | 1987-08-06 | 7:00 | 19.4
[42 empty] | 1987-08-06 | 8:00 | 20
[42 empty] | 1987-08-06 | 9:00 | 20
[42 empty] | 1987-08-06 | 10:00 | 20
[42 empty] | 1987-08-06 | 11:00 | 22.2
[42 empty] | 1987-08-06 | 12:00 | 23.3
[42 empty] | 1987-08-06 | 13:00 | 25
[42 empty] | 1987-08-06 | 14:00 | 25.6
[42 empty] | 1987-08-06 | 15:00 | 25.6
[42 empty] | 1987-08-06 | 16:00 | 25.6
[42 empty] | 1987-08-06 | 17:00 | 24.4
[42 empty] | 1987-08-06 | 18:00 | 23.9
[42 empty] | 1987-08-06 | 19:00 | 23.9
[42 empty] | 1987-08-06 | 20:00 | 23.3
[42 empty] | 1987-08-06 | 21:00 | 22.2
[42 empty] | 1987-08-06 | 22:00 | 21.7
[42 empty] | 1987-08-06 | 23:00 | 21.1
[42 empty] | 1987-08-06 | 24:00 | 21.1
[42 empty] | 1987-08-07 | 1:00 | 21.1
[42 empty] | 1987-08-07 | 2:00 | 20.6
[42 empty] | 1987-08-07 | 3:00 | 21.1
[42 empty] | 1987-08-07 | 4:00 | 21.1
[42 empty] | 1987-08-07 | 5:00 | 20.6
[42 empty] | 1987-08-07 | 6:00 | 20.6
[42 empty] | 1987-08-07 | 7:00 | 21.1
[42 empty] | 1987-08-07 | 8:00 | 22.2
[42 empty] | 1987-08-07 | 9:00 | 23.9
[42 empty] | 1987-08-07 | 10:00 | 25
[42 empty] | 1987-08-07 | 11:00 | 25.6
[42 empty] | 1987-08-07 | 12:00 | 25.6
[42 empty] | 1987-08-07 | 13:00 | 26.1
[42 empty] | 1987-08-07 | 14:00 | 25.6
[42 empty] | 1987-08-07 | 15:00 | 25.6
[42 empty] | 1987-08-07 | 16:00 | 25.6
[42 empty] | 1987-08-07 | 17:00 | 25
[42 empty] | 1987-08-07 | 18:00 | 23.9
[42 empty] | 1987-08-07 | 19:00 | 22.8
[42 empty] | 1987-08-07 | 20:00 | 22.2
[42 empty] | 1987-08-07 | 21:00 | 22.2
[42 empty] | 1987-08-07 | 22:00 | 22.2
[42 empty] | 1987-08-07 | 23:00 | 22.2
[42 empty] | 1987-08-07 | 24:00 | 22.2
[42 empty] | 1987-08-08 | 1:00 | 21.7
[42 empty] | 1987-08-08 | 2:00 | 21.7
[42 empty] | 1987-08-08 | 3:00 | 21.7
[42 empty] | 1987-08-08 | 4:00 | 21.7
[42 empty] | 1987-08-08 | 5:00 | 21.7
[42 empty] | 1987-08-08 | 6:00 | 21.7
[42 empty] | 1987-08-08 | 7:00 | 23.3
[42 empty] | 1987-08-08 | 8:00 | 23.9
[42 empty] | 1987-08-08 | 9:00 | 25.6
[42 empty] | 1987-08-08 | 10:00 | 26.7
[42 empty] | 1987-08-08 | 11:00 | 27.8
[42 empty] | 1987-08-08 | 12:00 | 28.3
[42 empty] | 1987-08-08 | 13:00 | 29.4
[42 empty] | 1987-08-08 | 14:00 | 30.6
[42 empty] | 1987-08-08 | 15:00 | 31.1
[42 empty] | 1987-08-08 | 16:00 | 30.6
[42 empty] | 1987-08-08 | 17:00 | 30
[42 empty] | 1987-08-08 | 18:00 | 27.8
[42 empty] | 1987-08-08 | 19:00 | 28.3
[42 empty] | 1987-08-08 | 20:00 | 26.7
[42 empty] | 1987-08-08 | 21:00 | 27.2
[42 empty] | 1987-08-08 | 22:00 | 26.1
[42 empty] | 1987-08-08 | 23:00 | 26.7
[42 empty] | 1987-08-08 | 24:00 | 25.6
[42 empty] | 1987-08-09 | 1:00 | 25
[42 empty] | 1987-08-09 | 2:00 | 24.4
[42 empty] | 1987-08-09 | 3:00 | 23.9
[42 empty] | 1987-08-09 | 4:00 | 22.8
[42 empty] | 1987-08-09 | 5:00 | 22.8
[42 empty] | 1987-08-09 | 6:00 | 22.2
[42 empty] | 1987-08-09 | 7:00 | 22.2
[42 empty] | 1987-08-09 | 8:00 | 23.3
[42 empty] | 1987-08-09 | 9:00 | 23.3
[42 empty] | 1987-08-09 | 10:00 | 23.9
[42 empty] | 1987-08-09 | 11:00 | 24.4
[42 empty] | 1987-08-09 | 12:00 | 25.6
[42 empty] | 1987-08-09 | 13:00 | 26.1
[42 empty] | 1987-08-09 | 14:00 | 24.4
[42 empty] | 1987-08-09 | 15:00 | 24.4
[42 empty] | 1987-08-09 | 16:00 | 25.6
[42 empty] | 1987-08-09 | 17:00 | 25.6
[42 empty] | 1987-08-09 | 18:00 | 25
[42 empty] | 1987-08-09 | 19:00 | 23.9
[42 empty] | 1987-08-09 | 20:00 | 22.2
[42 empty] | 1987-08-09 | 21:00 | 21.7
[42 empty] | 1987-08-09 | 22:00 | 20.6
[42 empty] | 1987-08-09 | 23:00 | 20
[42 empty] | 1987-08-09 | 24:00 | 20.6
[42 empty] | 1987-08-10 | 1:00 | 20
[42 empty] | 1987-08-10 | 2:00 | 20
[42 empty] | 1987-08-10 | 3:00 | 20
[42 empty] | 1987-08-10 | 4:00 | 20.6
[42 empty] | 1987-08-10 | 5:00 | 20.6
[42 empty] | 1987-08-10 | 6:00 | 20.6
[42 empty] | 1987-08-10 | 7:00 | 20.6
[42 empty] | 1987-08-10 | 8:00 | 21.1
[42 empty] | 1987-08-10 | 9:00 | 21.7
[42 empty] | 1987-08-10 | 10:00 | 22.2
[42 empty] | 1987-08-10 | 11:00 | 22.2
[42 empty] | 1987-08-10 | 12:00 | 23.3
[42 empty] | 1987-08-10 | 13:00 | 23.9
[42 empty] | 1987-08-10 | 14:00 | 25.6
[42 empty] | 1987-08-10 | 15:00 | 25.6
[42 empty] | 1987-08-10 | 16:00 | 23.9
[42 empty] | 1987-08-10 | 17:00 | 23.9
[42 empty] | 1987-08-10 | 18:00 | 23.3
[42 empty] | 1987-08-10 | 19:00 | 22.2
[42 empty] | 1987-08-10 | 20:00 | 21.1
[42 empty] | 1987-08-10 | 21:00 | 21.1
[42 empty] | 1987-08-10 | 22:00 | 20
[42 empty] | 1987-08-10 | 23:00 | 19.4
[42 empty] | 1987-08-10 | 24:00 | 18.9
[42 empty] | 1987-08-11 | 1:00 | 18.9
[42 empty] | 1987-08-11 | 2:00 | 18.3
[42 empty] | 1987-08-11 | 3:00 | 18.3
[42 empty] | 1987-08-11 | 4:00 | 17.8
[42 empty] | 1987-08-11 | 5:00 | 17.2
[42 empty] | 1987-08-11 | 6:00 | 18.3
[42 empty] | 1987-08-11 | 7:00 | 18.9
[42 empty] | 1987-08-11 | 8:00 | 21.1
[42 empty] | 1987-08-11 | 9:00 | 23.9
[42 empty] | 1987-08-11 | 10:00 | 26.1
[42 empty] | 1987-08-11 | 11:00 | 26.7
[42 empty] | 1987-08-11 | 12:00 | 27.2
[42 empty] | 1987-08-11 | 13:00 | 27.8
[42 empty] | 1987-08-11 | 14:00 | 27.2
[42 empty] | 1987-08-11 | 15:00 | 27.8
[42 empty] | 1987-08-11 | 16:00 | 27.8
[42 empty] | 1987-08-11 | 17:00 | 27.8
[42 empty] | 1987-08-11 | 18:00 | 26.7
[42 empty] | 1987-08-11 | 19:00 | 25.6
[42 empty] | 1987-08-11 | 20:00 | 25
[42 empty] | 1987-08-11 | 21:00 | 23.9
[42 empty] | 1987-08-11 | 22:00 | 22.8
[42 empty] | 1987-08-11 | 23:00 | 22.2
[42 empty] | 1987-08-11 | 24:00 | 20.6
[42 empty] | 1987-08-12 | 1:00 | 21.1
[42 empty] | 1987-08-12 | 2:00 | 20
[42 empty] | 1987-08-12 | 3:00 | 18.3
[42 empty] | 1987-08-12 | 4:00 | 17.8
[42 empty] | 1987-08-12 | 5:00 | 17.2
[42 empty] | 1987-08-12 | 6:00 | 17.8
[42 empty] | 1987-08-12 | 7:00 | 18.3
[42 empty] | 1987-08-12 | 8:00 | 20
[42 empty] | 1987-08-12 | 9:00 | 21.1
[42 empty] | 1987-08-12 | 10:00 | 21.7
[42 empty] | 1987-08-12 | 11:00 | 22.8
[42 empty] | 1987-08-12 | 12:00 | 23.9
[42 empty] | 1987-08-12 | 13:00 | 24.4
[42 empty] | 1987-08-12 | 14:00 | 25
[42 empty] | 1987-08-12 | 15:00 | 25.6
[42 empty] | 1987-08-12 | 16:00 | 25.6
[42 empty] | 1987-08-12 | 17:00 | 25
[42 empty] | 1987-08-12 | 18:00 | 23.3
[42 empty] | 1987-08-12 | 19:00 | 22.2
[42 empty] | 1987-08-12 | 20:00 | 21.7
[42 empty] | 1987-08-12 | 21:00 | 21.7
[42 empty] | 1987-08-12 | 22:00 | 21.1
[42 empty] | 1987-08-12 | 23:00 | 20.6
[42 empty] | 1987-08-12 | 24:00 | 20
[42 empty] | 1987-08-13 | 1:00 | 20
[42 empty] | 1987-08-13 | 2:00 | 19.4
[42 empty] | 1987-08-13 | 3:00 | 18.9
[42 empty] | 1987-08-13 | 4:00 | 18.3
[42 empty] | 1987-08-13 | 5:00 | 18.3
[42 empty] | 1987-08-13 | 6:00 | 18.9
[42 empty] | 1987-08-13 | 7:00 | 20.6
[42 empty] | 1987-08-13 | 8:00 | 21.7
[42 empty] | 1987-08-13 | 9:00 | 22.8
[42 empty] | 1987-08-13 | 10:00 | 23.3
[42 empty] | 1987-08-13 | 11:00 | 24.4
[42 empty] | 1987-08-13 | 12:00 | 24.4
[42 empty] | 1987-08-13 | 13:00 | 25
[42 empty] | 1987-08-13 | 14:00 | 23.9
[42 empty] | 1987-08-13 | 15:00 | 23.9
[42 empty] | 1987-08-13 | 16:00 | 24.4
[42 empty] | 1987-08-13 | 17:00 | 23.3
[42 empty] | 1987-08-13 | 18:00 | 22.8
[42 empty] | 1987-08-13 | 19:00 | 22.8
[42 empty] | 1987-08-13 | 20:00 | 20.6
[42 empty] | 1987-08-13 | 21:00 | 20
[42 empty] | 1987-08-13 | 22:00 | 20
[42 empty] | 1987-08-13 | 23:00 | 19.4
[42 empty] | 1987-08-13 | 24:00 | 19.4
[42 empty] | 1987-08-14 | 1:00 | 18.9
[42 empty] | 1987-08-14 | 2:00 | 18.3
[42 empty] | 1987-08-14 | 3:00 | 18.3
[42 empty] | 1987-08-14 | 4:00 | 17.8
[42 empty] | 1987-08-14 | 5:00 | 17.8
[42 empty] | 1987-08-14 | 6:00 | 18.3
[42 empty] | 1987-08-14 | 7:00 | 20
[42 empty] | 1987-08-14 | 8:00 | 21.1
[42 empty] | 1987-08-14 | 9:00 | 21.7
[42 empty] | 1987-08-14 | 10:00 | 22.8
[42 empty] | 1987-08-14 | 11:00 | 23.9
[42 empty] | 1987-08-14 | 12:00 | 24.4
[42 empty] | 1987-08-14 | 13:00 | 25.6
[42 empty] | 1987-08-14 | 14:00 | 26.1
[42 empty] | 1987-08-14 | 15:00 | 26.1
[42 empty] | 1987-08-14 | 16:00 | 26.1
[42 empty] | 1987-08-14 | 17:00 | 25
[42 empty] | 1987-08-14 | 18:00 | 24.4
[42 empty] | 1987-08-14 | 19:00 | 23.3
[42 empty] | 1987-08-14 | 20:00 | 22.2
[42 empty] | 1987-08-14 | 21:00 | 22.2
[42 empty] | 1987-08-14 | 22:00 | 22.2
[42 empty] | 1987-08-14 | 23:00 | 22.2
[42 empty] | 1987-08-14 | 24:00 | 22.8
[42 empty] | 1987-08-15 | 1:00 | 22.8
[42 empty] | 1987-08-15 | 2:00 | 22.2
[42 empty] | 1987-08-15 | 3:00 | 22.8
[42 empty] | 1987-08-15 | 4:00 | 22.8
[42 empty] | 1987-08-15 | 5:00 | 22.2
[42 empty] | 1987-08-15 | 6:00 | 22.8
[42 empty] | 1987-08-15 | 7:00 | 23.3
[42 empty] | 1987-08-15 | 8:00 | 24.4
[42 empty] | 1987-08-15 | 9:00 | 25.6
[42 empty] | 1987-08-15 | 10:00 | 26.7
[42 empty] | 1987-08-15 | 11:00 | 27.8
[42 empty] | 1987-08-15 | 12:00 | 28.3
[42 empty] | 1987-08-15 | 13:00 | 30
[42 empty] | 1987-08-15 | 14:00 | 30
[42 empty] | 1987-08-15 | 15:00 | 28.9
[42 empty] | 1987-08-15 | 16:00 | 28.3
[42 empty] | 1987-08-15 | 17:00 | 27.8
[42 empty] | 1987-08-15 | 18:00 | 26.7
[42 empty] | 1987-08-15 | 19:00 | 25.6
[42 empty] | 1987-08-15 | 20:00 | 25
[42 empty] | 1987-08-15 | 21:00 | 25
[42 empty] | 1987-08-15 | 22:00 | 25
[42 empty] | 1987-08-15 | 23:00 | 25
[42 empty] | 1987-08-15 | 24:00 | 24.4
[42 empty] | 1987-08-16 | 1:00 | 23.9
[42 empty] | 1987-08-16 | 2:00 | 22.8
[42 empty] | 1987-08-16 | 3:00 | 22.8
[42 empty] | 1987-08-16 | 4:00 | 22.2
[42 empty] | 1987-08-16 | 5:00 | 22.2
[42 empty] | 1987-08-16 | 6:00 | 22.8
[42 empty] | 1987-08-16 | 7:00 | 23.9
[42 empty] | 1987-08-16 | 8:00 | 25.6
[42 empty] | 1987-08-16 | 9:00 | 26.1
[42 empty] | 1987-08-16 | 10:00 | 28.3
[42 empty] | 1987-08-16 | 11:00 | 29.4
[42 empty] | 1987-08-16 | 12:00 | 29.4
[42 empty] | 1987-08-16 | 13:00 | 30.6
[42 empty] | 1987-08-16 | 14:00 | 30
[42 empty] | 1987-08-16 | 15:00 | 29.4
[42 empty] | 1987-08-16 | 16:00 | 28.9
[42 empty] | 1987-08-16 | 17:00 | 28.3
[42 empty] | 1987-08-16 | 18:00 | 27.8
[42 empty] | 1987-08-16 | 19:00 | 27.2
[42 empty] | 1987-08-16 | 20:00 | 26.7
[42 empty] | 1987-08-16 | 21:00 | 27.2
[42 empty] | 1987-08-16 | 22:00 | 27.2
[42 empty] | 1987-08-16 | 23:00 | 26.7
[42 empty] | 1987-08-16 | 24:00 | 26.1
[42 empty] | 1987-08-17 | 1:00 | 25.6
[42 empty] | 1987-08-17 | 2:00 | 25.6
[42 empty] | 1987-08-17 | 3:00 | 25
[42 empty] | 1987-08-17 | 4:00 | 25
[42 empty] | 1987-08-17 | 5:00 | 24.4
[42 empty] | 1987-08-17 | 6:00 | 25.6
[42 empty] | 1987-08-17 | 7:00 | 26.7
[42 empty] | 1987-08-17 | 8:00 | 27.8
[42 empty] | 1987-08-17 | 9:00 | 29.4
[42 empty] | 1987-08-17 | 10:00 | 30.6
[42 empty] | 1987-08-17 | 11:00 | 32.2
[42 empty] | 1987-08-17 | 12:00 | 33.3
[42 empty] | 1987-08-17 | 13:00 | 32.2
[42 empty] | 1987-08-17 | 14:00 | 32.2
[42 empty] | 1987-08-17 | 15:00 | 31.7
[42 empty] | 1987-08-17 | 16:00 | 31.1
[42 empty] | 1987-08-17 | 17:00 | 31.1
[42 empty] | 1987-08-17 | 18:00 | 30
[42 empty] | 1987-08-17 | 19:00 | 29.4
[42 empty] | 1987-08-17 | 20:00 | 28.9
[42 empty] | 1987-08-17 | 21:00 | 29.4
[42 empty] | 1987-08-17 | 22:00 | 29.4
[42 empty] | 1987-08-17 | 23:00 | 28.9
[42 empty] | 1987-08-17 | 24:00 | 28.3
[42 empty] | 1987-08-18 | 1:00 | 28.3
[42 empty] | 1987-08-18 | 2:00 | 28.9
[42 empty] | 1987-08-18 | 3:00 | 27.8
[42 empty] | 1987-08-18 | 4:00 | 27.8
[42 empty] | 1987-08-18 | 5:00 | 26.7
[42 empty] | 1987-08-18 | 6:00 | 26.7
[42 empty] | 1987-08-18 | 7:00 | 26.7
[42 empty] | 1987-08-18 | 8:00 | 27.2
[42 empty] | 1987-08-18 | 9:00 | 28.3
[42 empty] | 1987-08-18 | 10:00 | 29.4
[42 empty] | 1987-08-18 | 11:00 | 30
[42 empty] | 1987-08-18 | 12:00 | 31.1
[42 empty] | 1987-08-18 | 13:00 | 31.7
[42 empty] | 1987-08-18 | 14:00 | 32.2
[42 empty] | 1987-08-18 | 15:00 | 32.2
[42 empty] | 1987-08-18 | 16:00 | 32.2
[42 empty] | 1987-08-18 | 17:00 | 31.1
[42 empty] | 1987-08-18 | 18:00 | 30
[42 empty] | 1987-08-18 | 19:00 | 29.4
[42 empty] | 1987-08-18 | 20:00 | 28.3
[42 empty] | 1987-08-18 | 21:00 | 27.2
[42 empty] | 1987-08-18 | 22:00 | 26.7
[42 empty] | 1987-08-18 | 23:00 | 25.6
[42 empty] | 1987-08-18 | 24:00 | 24.4
[42 empty] | 1987-08-19 | 1:00 | 23.9
[42 empty] | 1987-08-19 | 2:00 | 23.3
[42 empty] | 1987-08-19 | 3:00 | 22.8
[42 empty] | 1987-08-19 | 4:00 | 22.2
[42 empty] | 1987-08-19 | 5:00 | 21.1
[42 empty] | 1987-08-19 | 6:00 | 22.2
[42 empty] | 1987-08-19 | 7:00 | 23.3
[42 empty] | 1987-08-19 | 8:00 | 23.9
[42 empty] | 1987-08-19 | 9:00 | 25.6
[42 empty] | 1987-08-19 | 10:00 | 27.2
[42 empty] | 1987-08-19 | 11:00 | 28.3
[42 empty] | 1987-08-19 | 12:00 | 29.4
[42 empty] | 1987-08-19 | 13:00 | 30
[42 empty] | 1987-08-19 | 14:00 | 30.6
[42 empty] | 1987-08-19 | 15:00 | 31.1
[42 empty] | 1987-08-19 | 16:00 | 30.6
[42 empty] | 1987-08-19 | 17:00 | 30
[42 empty] | 1987-08-19 | 18:00 | 28.3
[42 empty] | 1987-08-19 | 19:00 | 27.2
[42 empty] | 1987-08-19 | 20:00 | 26.1
[42 empty] | 1987-08-19 | 21:00 | 26.1
[42 empty] | 1987-08-19 | 22:00 | 26.1
[42 empty] | 1987-08-19 | 23:00 | 25.6
[42 empty] | 1987-08-19 | 24:00 | 22.8
[42 empty] | 1987-08-20 | 1:00 | 22.2
[42 empty] | 1987-08-20 | 2:00 | 21.7
[42 empty] | 1987-08-20 | 3:00 | 21.7
[42 empty] | 1987-08-20 | 4:00 | 21.7
[42 empty] | 1987-08-20 | 5:00 | 21.7
[42 empty] | 1987-08-20 | 6:00 | 21.7
[42 empty] | 1987-08-20 | 7:00 | 22.8
[42 empty] | 1987-08-20 | 8:00 | 24.4
[42 empty] | 1987-08-20 | 9:00 | 25.6
[42 empty] | 1987-08-20 | 10:00 | 26.1
[42 empty] | 1987-08-20 | 11:00 | 26.7
[42 empty] | 1987-08-20 | 12:00 | 27.8
[42 empty] | 1987-08-20 | 13:00 | 28.9
[42 empty] | 1987-08-20 | 14:00 | 28.3
[42 empty] | 1987-08-20 | 15:00 | 28.9
[42 empty] | 1987-08-20 | 16:00 | 27.8
[42 empty] | 1987-08-20 | 17:00 | 27.2
[42 empty] | 1987-08-20 | 18:00 | 26.7
[42 empty] | 1987-08-20 | 19:00 | 26.1
[42 empty] | 1987-08-20 | 20:00 | 25
[42 empty] | 1987-08-20 | 21:00 | 23.9
[42 empty] | 1987-08-20 | 22:00 | 22.8
[42 empty] | 1987-08-20 | 23:00 | 22.8
[42 empty] | 1987-08-20 | 24:00 | 22.2
[42 empty] | 1987-08-21 | 1:00 | 21.7
[42 empty] | 1987-08-21 | 2:00 | 20.6
[42 empty] | 1987-08-21 | 3:00 | 20.6
[42 empty] | 1987-08-21 | 4:00 | 20
[42 empty] | 1987-08-21 | 5:00 | 19.4
[42 empty] | 1987-08-21 | 6:00 | 19.4
[42 empty] | 1987-08-21 | 7:00 | 20
[42 empty] | 1987-08-21 | 8:00 | 23.3
[42 empty] | 1987-08-21 | 9:00 | 25
[42 empty] | 1987-08-21 | 10:00 | 25
[42 empty] | 1987-08-21 | 11:00 | 26.1
[42 empty] | 1987-08-21 | 12:00 | 26.7
[42 empty] | 1987-08-21 | 13:00 | 27.2
[42 empty] | 1987-08-21 | 14:00 | 28.3
[42 empty] | 1987-08-21 | 15:00 | 28.3
[42 empty] | 1987-08-21 | 16:00 | 28.3
[42 empty] | 1987-08-21 | 17:00 | 27.8
[42 empty] | 1987-08-21 | 18:00 | 27.2
[42 empty] | 1987-08-21 | 19:00 | 26.1
[42 empty] | 1987-08-21 | 20:00 | 26.1
[42 empty] | 1987-08-21 | 21:00 | 25.6
[42 empty] | 1987-08-21 | 22:00 | 25
[42 empty] | 1987-08-21 | 23:00 | 23.9
[42 empty] | 1987-08-21 | 24:00 | 23.3
[42 empty] | 1987-08-22 | 1:00 | 22.8
[42 empty] | 1987-08-22 | 2:00 | 22.2
[42 empty] | 1987-08-22 | 3:00 | 22.2
[42 empty] | 1987-08-22 | 4:00 | 22.2
[42 empty] | 1987-08-22 | 5:00 | 22.8
[42 empty] | 1987-08-22 | 6:00 | 22.8
[42 empty] | 1987-08-22 | 7:00 | 23.3
[42 empty] | 1987-08-22 | 8:00 | 24.4
[42 empty] | 1987-08-22 | 9:00 | 24.4
[42 empty] | 1987-08-22 | 10:00 | 23.3
[42 empty] | 1987-08-22 | 11:00 | 23.9
[42 empty] | 1987-08-22 | 12:00 | 24.4
[42 empty] | 1987-08-22 | 13:00 | 26.1
[42 empty] | 1987-08-22 | 14:00 | 27.8
[42 empty] | 1987-08-22 | 15:00 | 27.2
[42 empty] | 1987-08-22 | 16:00 | 27.8
[42 empty] | 1987-08-22 | 17:00 | 27.2
[42 empty] | 1987-08-22 | 18:00 | 27.2
[42 empty] | 1987-08-22 | 19:00 | 27.2
[42 empty] | 1987-08-22 | 20:00 | 26.7
[42 empty] | 1987-08-22 | 21:00 | 26.1
[42 empty] | 1987-08-22 | 22:00 | 26.1
[42 empty] | 1987-08-22 | 23:00 | 25.6
[42 empty] | 1987-08-22 | 24:00 | 25.6
[42 empty] | 1987-08-23 | 1:00 | 24.4
[42 empty] | 1987-08-23 | 2:00 | 22.8
[42 empty] | 1987-08-23 | 3:00 | 21.7
[42 empty] | 1987-08-23 | 4:00 | 20.6
[42 empty] | 1987-08-23 | 5:00 | 20
[42 empty] | 1987-08-23 | 6:00 | 18.9
[42 empty] | 1987-08-23 | 7:00 | 19.4
[42 empty] | 1987-08-23 | 8:00 | 20
[42 empty] | 1987-08-23 | 9:00 | 21.1
[42 empty] | 1987-08-23 | 10:00 | 21.1
[42 empty] | 1987-08-23 | 11:00 | 22.2
[42 empty] | 1987-08-23 | 12:00 | 23.3
[42 empty] | 1987-08-23 | 13:00 | 23.3
[42 empty] | 1987-08-23 | 14:00 | 22.8
[42 empty] | 1987-08-23 | 15:00 | 23.3
[42 empty] | 1987-08-23 | 16:00 | 23.3
[42 empty] | 1987-08-23 | 17:00 | 23.3
[42 empty] | 1987-08-23 | 18:00 | 22.2
[42 empty] | 1987-08-23 | 19:00 | 21.7
[42 empty] | 1987-08-23 | 20:00 | 20.6
[42 empty] | 1987-08-23 | 21:00 | 20
[42 empty] | 1987-08-23 | 22:00 | 18.9
[42 empty] | 1987-08-23 | 23:00 | 18.9
[42 empty] | 1987-08-23 | 24:00 | 17.8
[42 empty] | 1987-08-24 | 1:00 | 17.8
[42 empty] | 1987-08-24 | 2:00 | 16.7
[42 empty] | 1987-08-24 | 3:00 | 16.1
[42 empty] | 1987-08-24 | 4:00 | 15.6
[42 empty] | 1987-08-24 | 5:00 | 15.6
[42 empty] | 1987-08-24 | 6:00 | 15
[42 empty] | 1987-08-24 | 7:00 | 16.1
[42 empty] | 1987-08-24 | 8:00 | 17.8
[42 empty] | 1987-08-24 | 9:00 | 18.3
[42 empty] | 1987-08-24 | 10:00 | 20
[42 empty] | 1987-08-24 | 11:00 | 19.4
[42 empty] | 1987-08-24 | 12:00 | 20.6
[42 empty] | 1987-08-24 | 13:00 | 21.7
[42 empty] | 1987-08-24 | 14:00 | 22.8
[42 empty] | 1987-08-24 | 15:00 | 21.7
[42 empty] | 1987-08-24 | 16:00 | 22.8
[42 empty] | 1987-08-24 | 17:00 | 22.8
[42 empty] | 1987-08-24 | 18:00 | 22.2
[42 empty] | 1987-08-24 | 19:00 | 21.1
[42 empty] | 1987-08-24 | 20:00 | 20.6
[42 empty] | 1987-08-24 | 21:00 | 20
[42 empty] | 1987-08-24 | 22:00 | 20
[42 empty] | 1987-08-24 | 23:00 | 18.3
[42 empty] | 1987-08-24 | 24:00 | 18.3
[42 empty] | 1987-08-25 | 1:00 | 17.2
[42 empty] | 1987-08-25 | 2:00 | 17.2
[42 empty] | 1987-08-25 | 3:00 | 16.7
[42 empty] | 1987-08-25 | 4:00 | 16.1
[42 empty] | 1987-08-25 | 5:00 | 16.1
[42 empty] | 1987-08-25 | 6:00 | 16.1
[42 empty] | 1987-08-25 | 7:00 | 17.8
[42 empty] | 1987-08-25 | 8:00 | 18.9
[42 empty] | 1987-08-25 | 9:00 | 20
[42 empty] | 1987-08-25 | 10:00 | 20
[42 empty] | 1987-08-25 | 11:00 | 20
[42 empty] | 1987-08-25 | 12:00 | 20.6
[42 empty] | 1987-08-25 | 13:00 | 21.7
[42 empty] | 1987-08-25 | 14:00 | 22.2
[42 empty] | 1987-08-25 | 15:00 | 23.3
[42 empty] | 1987-08-25 | 16:00 | 23.9
[42 empty] | 1987-08-25 | 17:00 | 23.3
[42 empty] | 1987-08-25 | 18:00 | 22.2
[42 empty] | 1987-08-25 | 19:00 | 21.1
[42 empty] | 1987-08-25 | 20:00 | 21.1
[42 empty] | 1987-08-25 | 21:00 | 20.6
[42 empty] | 1987-08-25 | 22:00 | 20.6
[42 empty] | 1987-08-25 | 23:00 | 19.4
[42 empty] | 1987-08-25 | 24:00 | 18.9
[42 empty] | 1987-08-26 | 1:00 | 18.3
[42 empty] | 1987-08-26 | 2:00 | 17.8
[42 empty] | 1987-08-26 | 3:00 | 17.8
[42 empty] | 1987-08-26 | 4:00 | 17.8
[42 empty] | 1987-08-26 | 5:00 | 16.7
[42 empty] | 1987-08-26 | 6:00 | 16.7
[42 empty] | 1987-08-26 | 7:00 | 17.2
[42 empty] | 1987-08-26 | 8:00 | 19.4
[42 empty] | 1987-08-26 | 9:00 | 22.8
[42 empty] | 1987-08-26 | 10:00 | 24.4
[42 empty] | 1987-08-26 | 11:00 | 24.4
[42 empty] | 1987-08-26 | 12:00 | 26.1
[42 empty] | 1987-08-26 | 13:00 | 26.1
[42 empty] | 1987-08-26 | 14:00 | 25.6
[42 empty] | 1987-08-26 | 15:00 | 25.6
[42 empty] | 1987-08-26 | 16:00 | 25
[42 empty] | 1987-08-26 | 17:00 | 23.9
[42 empty] | 1987-08-26 | 18:00 | 23.3
[42 empty] | 1987-08-26 | 19:00 | 22.8
[42 empty] | 1987-08-26 | 20:00 | 22.8
[42 empty] | 1987-08-26 | 21:00 | 23.3
[42 empty] | 1987-08-26 | 22:00 | 22.2
[42 empty] | 1987-08-26 | 23:00 | 21.7
[42 empty] | 1987-08-26 | 24:00 | 21.7
[42 empty] | 1987-08-27 | 1:00 | 21.7
[42 empty] | 1987-08-27 | 2:00 | 21.7
[42 empty] | 1987-08-27 | 3:00 | 20.6
[42 empty] | 1987-08-27 | 4:00 | 20
[42 empty] | 1987-08-27 | 5:00 | 18.3
[42 empty] | 1987-08-27 | 6:00 | 16.7
[42 empty] | 1987-08-27 | 7:00 | 16.1
[42 empty] | 1987-08-27 | 8:00 | 16.7
[42 empty] | 1987-08-27 | 9:00 | 17.8
[42 empty] | 1987-08-27 | 10:00 | 17.2
[42 empty] | 1987-08-27 | 11:00 | 17.2
[42 empty] | 1987-08-27 | 12:00 | 16.7
[42 empty] | 1987-08-27 | 13:00 | 17.2
[42 empty] | 1987-08-27 | 14:00 | 17.2
[42 empty] | 1987-08-27 | 15:00 | 17.2
[42 empty] | 1987-08-27 | 16:00 | 16.7
[42 empty] | 1987-08-27 | 17:00 | 16.7
[42 empty] | 1987-08-27 | 18:00 | 17.2
[42 empty] | 1987-08-27 | 19:00 | 17.2
[42 empty] | 1987-08-27 | 20:00 | 17.8
[42 empty] | 1987-08-27 | 21:00 | 17.2
[42 empty] | 1987-08-27 | 22:00 | 16.7
[42 empty] | 1987-08-27 | 23:00 | 16.7
[42 empty] | 1987-08-27 | 24:00 | 16.7
[42 empty] | 1987-08-28 | 1:00 | 17.2
[42 empty] | 1987-08-28 | 2:00 | 17.2
[42 empty] | 1987-08-28 | 3:00 | 17.2
[42 empty] | 1987-08-28 | 4:00 | 17.2
[42 empty] | 1987-08-28 | 5:00 | 16.7
[42 empty] | 1987-08-28 | 6:00 | 16.7
[42 empty] | 1987-08-28 | 7:00 | 16.7
[42 empty] | 1987-08-28 | 8:00 | 16.7
[42 empty] | 1987-08-28 | 9:00 | 17.2
[42 empty] | 1987-08-28 | 10:00 | 17.2
[42 empty] | 1987-08-28 | 11:00 | 17.2
[42 empty] | 1987-08-28 | 12:00 | 17.8
[42 empty] | 1987-08-28 | 13:00 | 17.8
[42 empty] | 1987-08-28 | 14:00 | 17.2
[42 empty] | 1987-08-28 | 15:00 | 17.2
[42 empty] | 1987-08-28 | 16:00 | 17.8
[42 empty] | 1987-08-28 | 17:00 | 17.8
[42 empty] | 1987-08-28 | 18:00 | 17.2
[42 empty] | 1987-08-28 | 19:00 | 16.7
[42 empty] | 1987-08-28 | 20:00 | 16.1
[42 empty] | 1987-08-28 | 21:00 | 16.1
[42 empty] | 1987-08-28 | 22:00 | 16.1
[42 empty] | 1987-08-28 | 23:00 | 16.7
[42 empty] | 1987-08-28 | 24:00 | 16.7
[42 empty] | 1987-08-29 | 1:00 | 16.7
[42 empty] | 1987-08-29 | 2:00 | 16.7
[42 empty] | 1987-08-29 | 3:00 | 17.2
[42 empty] | 1987-08-29 | 4:00 | 17.2
[42 empty] | 1987-08-29 | 5:00 | 17.2
[42 empty] | 1987-08-29 | 6:00 | 16.1
[42 empty] | 1987-08-29 | 7:00 | 16.1
[42 empty] | 1987-08-29 | 8:00 | 16.7
[42 empty] | 1987-08-29 | 9:00 | 18.3
[42 empty] | 1987-08-29 | 10:00 | 20
[42 empty] | 1987-08-29 | 11:00 | 21.1
[42 empty] | 1987-08-29 | 12:00 | 22.8
[42 empty] | 1987-08-29 | 13:00 | 23.3
[42 empty] | 1987-08-29 | 14:00 | 23.3
[42 empty] | 1987-08-29 | 15:00 | 24.4
[42 empty] | 1987-08-29 | 16:00 | 23.9
[42 empty] | 1987-08-29 | 17:00 | 22.8
[42 empty] | 1987-08-29 | 18:00 | 21.7
[42 empty] | 1987-08-29 | 19:00 | 21.1
[42 empty] | 1987-08-29 | 20:00 | 20.6
[42 empty] | 1987-08-29 | 21:00 | 20
[42 empty] | 1987-08-29 | 22:00 | 18.9
[42 empty] | 1987-08-29 | 23:00 | 18.3
[42 empty] | 1987-08-29 | 24:00 | 17.8
[42 empty] | 1987-08-30 | 1:00 | 17.2
[42 empty] | 1987-08-30 | 2:00 | 16.7
[42 empty] | 1987-08-30 | 3:00 | 16.1
[42 empty] | 1987-08-30 | 4:00 | 16.1
[42 empty] | 1987-08-30 | 5:00 | 15.6
[42 empty] | 1987-08-30 | 6:00 | 15.6
[42 empty] | 1987-08-30 | 7:00 | 16.7
[42 empty] | 1987-08-30 | 8:00 | 18.3
[42 empty] | 1987-08-30 | 9:00 | 18.9
[42 empty] | 1987-08-30 | 10:00 | 21.7
[42 empty] | 1987-08-30 | 11:00 | 23.9
[42 empty] | 1987-08-30 | 12:00 | 24.4
[42 empty] | 1987-08-30 | 13:00 | 24.4
[42 empty] | 1987-08-30 | 14:00 | 25
[42 empty] | 1987-08-30 | 15:00 | 25
[42 empty] | 1987-08-30 | 16:00 | 24.4
[42 empty] | 1987-08-30 | 17:00 | 23.3
[42 empty] | 1987-08-30 | 18:00 | 22.2
[42 empty] | 1987-08-30 | 19:00 | 20.6
[42 empty] | 1987-08-30 | 20:00 | 20
[42 empty] | 1987-08-30 | 21:00 | 19.4
[42 empty] | 1987-08-30 | 22:00 | 19.4
[42 empty] | 1987-08-30 | 23:00 | 18.9
[42 empty] | 1987-08-30 | 24:00 | 18.3
[42 empty] | 1987-08-31 | 1:00 | 17.8
[42 empty] | 1987-08-31 | 2:00 | 17.2
[42 empty] | 1987-08-31 | 3:00 | 17.2
[42 empty] | 1987-08-31 | 4:00 | 16.7
[42 empty] | 1987-08-31 | 5:00 | 16.7
[42 empty] | 1987-08-31 | 6:00 | 16.7
[42 empty] | 1987-08-31 | 7:00 | 17.8
[42 empty] | 1987-08-31 | 8:00 | 20
[42 empty] | 1987-08-31 | 9:00 | 21.7
[42 empty] | 1987-08-31 | 10:00 | 22.8
[42 empty] | 1987-08-31 | 11:00 | 22.8
[42 empty] | 1987-08-31 | 12:00 | 22.8
[42 empty] | 1987-08-31 | 13:00 | 23.3
[42 empty] | 1987-08-31 | 14:00 | 23.9
[42 empty] | 1987-08-31 | 15:00 | 23.3
[42 empty] | 1987-08-31 | 16:00 | 22.8
[42 empty] | 1987-08-31 | 17:00 | 22.2
[42 empty] | 1987-08-31 | 18:00 | 21.1
[42 empty] | 1987-08-31 | 19:00 | 20.6
[42 empty] | 1987-08-31 | 20:00 | 21.1
[42 empty] | 1987-08-31 | 21:00 | 21.1
[42 empty] | 1987-08-31 | 22:00 | 21
[42 empty] | 1987-08-31 | 23:00 | 21
[42 empty] | 1987-08-31 | 24:00 | 20.9
[42 empty] | 1979-09-01 | 1:00 | 20.8
[42 empty] | 1979-09-01 | 2:00 | 20.7
[42 empty] | 1979-09-01 | 3:00 | 20.7
[42 empty] | 1979-09-01 | 4:00 | 20.6
[42 empty] | 1979-09-01 | 5:00 | 21
[42 empty] | 1979-09-01 | 6:00 | 21.3
[42 empty] | 1979-09-01 | 7:00 | 21.7
[42 empty] | 1979-09-01 | 8:00 | 22.8
[42 empty] | 1979-09-01 | 9:00 | 23.9
[42 empty] | 1979-09-01 | 10:00 | 25
[42 empty] | 1979-09-01 | 11:00 | 25.6
[42 empty] | 1979-09-01 | 12:00 | 26.1
[42 empty] | 1979-09-01 | 13:00 | 26.7
[42 empty] | 1979-09-01 | 14:00 | 26.5
[42 empty] | 1979-09-01 | 15:00 | 26.3
[42 empty] | 1979-09-01 | 16:00 | 26.1
[42 empty] | 1979-09-01 | 17:00 | 25.2
[42 empty] | 1979-09-01 | 18:00 | 24.2
[42 empty] | 1979-09-01 | 19:00 | 23.3
[42 empty] | 1979-09-01 | 20:00 | 22.9
[42 empty] | 1979-09-01 | 21:00 | 22.6
[42 empty] | 1979-09-01 | 22:00 | 22.2
[42 empty] | 1979-09-01 | 23:00 | 22
[42 empty] | 1979-09-01 | 24:00 | 21.9
[42 empty] | 1979-09-02 | 1:00 | 21.7
[42 empty] | 1979-09-02 | 2:00 | 21.3
[42 empty] | 1979-09-02 | 3:00 | 21
[42 empty] | 1979-09-02 | 4:00 | 20.6
[42 empty] | 1979-09-02 | 5:00 | 20.8
[42 empty] | 1979-09-02 | 6:00 | 20.9
[42 empty] | 1979-09-02 | 7:00 | 21.1
[42 empty] | 1979-09-02 | 8:00 | 21.8
[42 empty] | 1979-09-02 | 9:00 | 22.6
[42 empty] | 1979-09-02 | 10:00 | 23.3
[42 empty] | 1979-09-02 | 11:00 | 23.7
[42 empty] | 1979-09-02 | 12:00 | 24
[42 empty] | 1979-09-02 | 13:00 | 24.4
[42 empty] | 1979-09-02 | 14:00 | 24.4
[42 empty] | 1979-09-02 | 15:00 | 24.4
[42 empty] | 1979-09-02 | 16:00 | 24.4
[42 empty] | 1979-09-02 | 17:00 | 24.6
[42 empty] | 1979-09-02 | 18:00 | 24.8
[42 empty] | 1979-09-02 | 19:00 | 25
[42 empty] | 1979-09-02 | 20:00 | 25
[42 empty] | 1979-09-02 | 21:00 | 25
[42 empty] | 1979-09-02 | 22:00 | 25
[42 empty] | 1979-09-02 | 23:00 | 24.8
[42 empty] | 1979-09-02 | 24:00 | 24.6
[42 empty] | 1979-09-03 | 1:00 | 24.4
[42 empty] | 1979-09-03 | 2:00 | 24.4
[42 empty] | 1979-09-03 | 3:00 | 24.4
[42 empty] | 1979-09-03 | 4:00 | 24.4
[42 empty] | 1979-09-03 | 5:00 | 24.2
[42 empty] | 1979-09-03 | 6:00 | 24.1
[42 empty] | 1979-09-03 | 7:00 | 23.9
[42 empty] | 1979-09-03 | 8:00 | 24.5
[42 empty] | 1979-09-03 | 9:00 | 25
[42 empty] | 1979-09-03 | 10:00 | 25.6
[42 empty] | 1979-09-03 | 11:00 | 26.5
[42 empty] | 1979-09-03 | 12:00 | 27.4
[42 empty] | 1979-09-03 | 13:00 | 28.3
[42 empty] | 1979-09-03 | 14:00 | 28.3
[42 empty] | 1979-09-03 | 15:00 | 28.3
[42 empty] | 1979-09-03 | 16:00 | 28.3
[42 empty] | 1979-09-03 | 17:00 | 27.9
[42 empty] | 1979-09-03 | 18:00 | 27.6
[42 empty] | 1979-09-03 | 19:00 | 27.2
[42 empty] | 1979-09-03 | 20:00 | 26.8
[42 empty] | 1979-09-03 | 21:00 | 26.5
[42 empty] | 1979-09-03 | 22:00 | 26.1
[42 empty] | 1979-09-03 | 23:00 | 25.7
[42 empty] | 1979-09-03 | 24:00 | 25.4
[42 empty] | 1979-09-04 | 1:00 | 25
[42 empty] | 1979-09-04 | 2:00 | 24.3
[42 empty] | 1979-09-04 | 3:00 | 23.5
[42 empty] | 1979-09-04 | 4:00 | 22.8
[42 empty] | 1979-09-04 | 5:00 | 23.2
[42 empty] | 1979-09-04 | 6:00 | 23.5
[42 empty] | 1979-09-04 | 7:00 | 23.9
[42 empty] | 1979-09-04 | 8:00 | 24.8
[42 empty] | 1979-09-04 | 9:00 | 25.8
[42 empty] | 1979-09-04 | 10:00 | 26.7
[42 empty] | 1979-09-04 | 11:00 | 27.4
[42 empty] | 1979-09-04 | 12:00 | 28.2
[42 empty] | 1979-09-04 | 13:00 | 28.9
[42 empty] | 1979-09-04 | 14:00 | 28.7
[42 empty] | 1979-09-04 | 15:00 | 28.5
[42 empty] | 1979-09-04 | 16:00 | 28.3
[42 empty] | 1979-09-04 | 17:00 | 27.4
[42 empty] | 1979-09-04 | 18:00 | 26.5
[42 empty] | 1979-09-04 | 19:00 | 25.6
[42 empty] | 1979-09-04 | 20:00 | 25.2
[42 empty] | 1979-09-04 | 21:00 | 24.8
[42 empty] | 1979-09-04 | 22:00 | 24.4
[42 empty] | 1979-09-04 | 23:00 | 24.2
[42 empty] | 1979-09-04 | 24:00 | 24.1
[42 empty] | 1979-09-05 | 1:00 | 23.9
[42 empty] | 1979-09-05 | 2:00 | 23.9
[42 empty] | 1979-09-05 | 3:00 | 23.9
[42 empty] | 1979-09-05 | 4:00 | 23.9
[42 empty] | 1979-09-05 | 5:00 | 24.1
[42 empty] | 1979-09-05 | 6:00 | 24.2
[42 empty] | 1979-09-05 | 7:00 | 24.4
[42 empty] | 1979-09-05 | 8:00 | 25.3
[42 empty] | 1979-09-05 | 9:00 | 26.3
[42 empty] | 1979-09-05 | 10:00 | 27.2
[42 empty] | 1979-09-05 | 11:00 | 27.6
[42 empty] | 1979-09-05 | 12:00 | 27.9
[42 empty] | 1979-09-05 | 13:00 | 28.3
[42 empty] | 1979-09-05 | 14:00 | 27.9
[42 empty] | 1979-09-05 | 15:00 | 27.6
[42 empty] | 1979-09-05 | 16:00 | 27.2
[42 empty] | 1979-09-05 | 17:00 | 26.8
[42 empty] | 1979-09-05 | 18:00 | 26.5
[42 empty] | 1979-09-05 | 19:00 | 26.1
[42 empty] | 1979-09-05 | 20:00 | 25.9
[42 empty] | 1979-09-05 | 21:00 | 25.8
[42 empty] | 1979-09-05 | 22:00 | 25.6
[42 empty] | 1979-09-05 | 23:00 | 25.6
[42 empty] | 1979-09-05 | 24:00 | 25.6
[42 empty] | 1979-09-06 | 1:00 | 25.6
[42 empty] | 1979-09-06 | 2:00 | 25.4
[42 empty] | 1979-09-06 | 3:00 | 25.2
[42 empty] | 1979-09-06 | 4:00 | 25
[42 empty] | 1979-09-06 | 5:00 | 24.8
[42 empty] | 1979-09-06 | 6:00 | 24.6
[42 empty] | 1979-09-06 | 7:00 | 24.4
[42 empty] | 1979-09-06 | 8:00 | 24.2
[42 empty] | 1979-09-06 | 9:00 | 24.1
[42 empty] | 1979-09-06 | 10:00 | 23.9
[42 empty] | 1979-09-06 | 11:00 | 23.9
[42 empty] | 1979-09-06 | 12:00 | 23.9
[42 empty] | 1979-09-06 | 13:00 | 23.9
[42 empty] | 1979-09-06 | 14:00 | 25.4
[42 empty] | 1979-09-06 | 15:00 | 26.8
[42 empty] | 1979-09-06 | 16:00 | 28.3
[42 empty] | 1979-09-06 | 17:00 | 27.8
[42 empty] | 1979-09-06 | 18:00 | 27.2
[42 empty] | 1979-09-06 | 19:00 | 26.7
[42 empty] | 1979-09-06 | 20:00 | 26.5
[42 empty] | 1979-09-06 | 21:00 | 26.3
[42 empty] | 1979-09-06 | 22:00 | 26.1
[42 empty] | 1979-09-06 | 23:00 | 25.5
[42 empty] | 1979-09-06 | 24:00 | 25
[42 empty] | 1979-09-07 | 1:00 | 24.4
[42 empty] | 1979-09-07 | 2:00 | 23.7
[42 empty] | 1979-09-07 | 3:00 | 22.9
[42 empty] | 1979-09-07 | 4:00 | 22.2
[42 empty] | 1979-09-07 | 5:00 | 22.4
[42 empty] | 1979-09-07 | 6:00 | 22.6
[42 empty] | 1979-09-07 | 7:00 | 22.8
[42 empty] | 1979-09-07 | 8:00 | 23.3
[42 empty] | 1979-09-07 | 9:00 | 23.9
[42 empty] | 1979-09-07 | 10:00 | 24.4
[42 empty] | 1979-09-07 | 11:00 | 25.2
[42 empty] | 1979-09-07 | 12:00 | 25.9
[42 empty] | 1979-09-07 | 13:00 | 26.7
[42 empty] | 1979-09-07 | 14:00 | 26.7
[42 empty] | 1979-09-07 | 15:00 | 26.7
[42 empty] | 1979-09-07 | 16:00 | 26.7
[42 empty] | 1979-09-07 | 17:00 | 26.1
[42 empty] | 1979-09-07 | 18:00 | 25.6
[42 empty] | 1979-09-07 | 19:00 | 25
[42 empty] | 1979-09-07 | 20:00 | 24.1
[42 empty] | 1979-09-07 | 21:00 | 23.1
[42 empty] | 1979-09-07 | 22:00 | 22.2
[42 empty] | 1979-09-07 | 23:00 | 21.8
[42 empty] | 1979-09-07 | 24:00 | 21.5
[42 empty] | 1979-09-08 | 1:00 | 21.1
[42 empty] | 1979-09-08 | 2:00 | 20.5
[42 empty] | 1979-09-08 | 3:00 | 20
[42 empty] | 1979-09-08 | 4:00 | 19.4
[42 empty] | 1979-09-08 | 5:00 | 19.2
[42 empty] | 1979-09-08 | 6:00 | 19.1
[42 empty] | 1979-09-08 | 7:00 | 18.9
[42 empty] | 1979-09-08 | 8:00 | 19.1
[42 empty] | 1979-09-08 | 9:00 | 19.2
[42 empty] | 1979-09-08 | 10:00 | 19.4
[42 empty] | 1979-09-08 | 11:00 | 20
[42 empty] | 1979-09-08 | 12:00 | 20.5
[42 empty] | 1979-09-08 | 13:00 | 21.1
[42 empty] | 1979-09-08 | 14:00 | 21.3
[42 empty] | 1979-09-08 | 15:00 | 21.5
[42 empty] | 1979-09-08 | 16:00 | 21.7
[42 empty] | 1979-09-08 | 17:00 | 21.1
[42 empty] | 1979-09-08 | 18:00 | 20.6
[42 empty] | 1979-09-08 | 19:00 | 20
[42 empty] | 1979-09-08 | 20:00 | 19.4
[42 empty] | 1979-09-08 | 21:00 | 18.9
[42 empty] | 1979-09-08 | 22:00 | 18.3
[42 empty] | 1979-09-08 | 23:00 | 17.4
[42 empty] | 1979-09-08 | 24:00 | 16.5
[42 empty] | 1979-09-09 | 1:00 | 15.6
[42 empty] | 1979-09-09 | 2:00 | 14.8
[42 empty] | 1979-09-09 | 3:00 | 14.1
[42 empty] | 1979-09-09 | 4:00 | 13.3
[42 empty] | 1979-09-09 | 5:00 | 13.1
[42 empty] | 1979-09-09 | 6:00 | 13
[42 empty] | 1979-09-09 | 7:00 | 12.8
[42 empty] | 1979-09-09 | 8:00 | 14.5
[42 empty] | 1979-09-09 | 9:00 | 16.1
[42 empty] | 1979-09-09 | 10:00 | 17.8
[42 empty] | 1979-09-09 | 11:00 | 18.7
[42 empty] | 1979-09-09 | 12:00 | 19.7
[42 empty] | 1979-09-09 | 13:00 | 20.6
[42 empty] | 1979-09-09 | 14:00 | 21
[42 empty] | 1979-09-09 | 15:00 | 21.3
[42 empty] | 1979-09-09 | 16:00 | 21.7
[42 empty] | 1979-09-09 | 17:00 | 20.9
[42 empty] | 1979-09-09 | 18:00 | 20.2
[42 empty] | 1979-09-09 | 19:00 | 19.4
[42 empty] | 1979-09-09 | 20:00 | 19
[42 empty] | 1979-09-09 | 21:00 | 18.7
[42 empty] | 1979-09-09 | 22:00 | 18.3
[42 empty] | 1979-09-09 | 23:00 | 17.8
[42 empty] | 1979-09-09 | 24:00 | 17.2
[42 empty] | 1979-09-10 | 1:00 | 16.7
[42 empty] | 1979-09-10 | 2:00 | 16.1
[42 empty] | 1979-09-10 | 3:00 | 15.6
[42 empty] | 1979-09-10 | 4:00 | 15
[42 empty] | 1979-09-10 | 5:00 | 15.7
[42 empty] | 1979-09-10 | 6:00 | 16.5
[42 empty] | 1979-09-10 | 7:00 | 17.2
[42 empty] | 1979-09-10 | 8:00 | 18.5
[42 empty] | 1979-09-10 | 9:00 | 19.8
[42 empty] | 1979-09-10 | 10:00 | 21.1
[42 empty] | 1979-09-10 | 11:00 | 22
[42 empty] | 1979-09-10 | 12:00 | 23
[42 empty] | 1979-09-10 | 13:00 | 23.9
[42 empty] | 1979-09-10 | 14:00 | 23.2
[42 empty] | 1979-09-10 | 15:00 | 22.4
[42 empty] | 1979-09-10 | 16:00 | 21.7
[42 empty] | 1979-09-10 | 17:00 | 21.1
[42 empty] | 1979-09-10 | 18:00 | 20.6
[42 empty] | 1979-09-10 | 19:00 | 20
[42 empty] | 1979-09-10 | 20:00 | 20
[42 empty] | 1979-09-10 | 21:00 | 20
[42 empty] | 1979-09-10 | 22:00 | 20
[42 empty] | 1979-09-10 | 23:00 | 19.6
[42 empty] | 1979-09-10 | 24:00 | 19.3
[42 empty] | 1979-09-11 | 1:00 | 18.9
[42 empty] | 1979-09-11 | 2:00 | 19.1
[42 empty] | 1979-09-11 | 3:00 | 19.2
[42 empty] | 1979-09-11 | 4:00 | 19.4
[42 empty] | 1979-09-11 | 5:00 | 19.4
[42 empty] | 1979-09-11 | 6:00 | 19.4
[42 empty] | 1979-09-11 | 7:00 | 19.4
[42 empty] | 1979-09-11 | 8:00 | 20.3
[42 empty] | 1979-09-11 | 9:00 | 21.3
[42 empty] | 1979-09-11 | 10:00 | 22.2
[42 empty] | 1979-09-11 | 11:00 | 22.8
[42 empty] | 1979-09-11 | 12:00 | 23.3
[42 empty] | 1979-09-11 | 13:00 | 23.9
[42 empty] | 1979-09-11 | 14:00 | 24.1
[42 empty] | 1979-09-11 | 15:00 | 24.2
[42 empty] | 1979-09-11 | 16:00 | 24.4
[42 empty] | 1979-09-11 | 17:00 | 23.3
[42 empty] | 1979-09-11 | 18:00 | 22.2
[42 empty] | 1979-09-11 | 19:00 | 21.1
[42 empty] | 1979-09-11 | 20:00 | 20.2
[42 empty] | 1979-09-11 | 21:00 | 19.2
[42 empty] | 1979-09-11 | 22:00 | 18.3
[42 empty] | 1979-09-11 | 23:00 | 17.6
[42 empty] | 1979-09-11 | 24:00 | 16.8
[42 empty] | 1979-09-12 | 1:00 | 16.1
[42 empty] | 1979-09-12 | 2:00 | 15.4
[42 empty] | 1979-09-12 | 3:00 | 14.6
[42 empty] | 1979-09-12 | 4:00 | 13.9
[42 empty] | 1979-09-12 | 5:00 | 14.3
[42 empty] | 1979-09-12 | 6:00 | 14.6
[42 empty] | 1979-09-12 | 7:00 | 15
[42 empty] | 1979-09-12 | 8:00 | 16.3
[42 empty] | 1979-09-12 | 9:00 | 17.6
[42 empty] | 1979-09-12 | 10:00 | 18.9
[42 empty] | 1979-09-12 | 11:00 | 19.8
[42 empty] | 1979-09-12 | 12:00 | 20.8
[42 empty] | 1979-09-12 | 13:00 | 21.7
[42 empty] | 1979-09-12 | 14:00 | 21.9
[42 empty] | 1979-09-12 | 15:00 | 22
[42 empty] | 1979-09-12 | 16:00 | 22.2
[42 empty] | 1979-09-12 | 17:00 | 21.5
[42 empty] | 1979-09-12 | 18:00 | 20.7
[42 empty] | 1979-09-12 | 19:00 | 20
[42 empty] | 1979-09-12 | 20:00 | 19.6
[42 empty] | 1979-09-12 | 21:00 | 19.3
[42 empty] | 1979-09-12 | 22:00 | 18.9
[42 empty] | 1979-09-12 | 23:00 | 18.5
[42 empty] | 1979-09-12 | 24:00 | 18.2
[42 empty] | 1979-09-13 | 1:00 | 17.8
[42 empty] | 1979-09-13 | 2:00 | 17.6
[42 empty] | 1979-09-13 | 3:00 | 17.4
[42 empty] | 1979-09-13 | 4:00 | 17.2
[42 empty] | 1979-09-13 | 5:00 | 17.6
[42 empty] | 1979-09-13 | 6:00 | 17.9
[42 empty] | 1979-09-13 | 7:00 | 18.3
[42 empty] | 1979-09-13 | 8:00 | 19.8
[42 empty] | 1979-09-13 | 9:00 | 21.3
[42 empty] | 1979-09-13 | 10:00 | 22.8
[42 empty] | 1979-09-13 | 11:00 | 23
[42 empty] | 1979-09-13 | 12:00 | 23.1
[42 empty] | 1979-09-13 | 13:00 | 23.3
[42 empty] | 1979-09-13 | 14:00 | 23.1
[42 empty] | 1979-09-13 | 15:00 | 23
[42 empty] | 1979-09-13 | 16:00 | 22.8
[42 empty] | 1979-09-13 | 17:00 | 22.2
[42 empty] | 1979-09-13 | 18:00 | 21.7
[42 empty] | 1979-09-13 | 19:00 | 21.1
[42 empty] | 1979-09-13 | 20:00 | 20.9
[42 empty] | 1979-09-13 | 21:00 | 20.8
[42 empty] | 1979-09-13 | 22:00 | 20.6
[42 empty] | 1979-09-13 | 23:00 | 21.3
[42 empty] | 1979-09-13 | 24:00 | 22.1
[42 empty] | 1979-09-14 | 1:00 | 22.8
[42 empty] | 1979-09-14 | 2:00 | 22.8
[42 empty] | 1979-09-14 | 3:00 | 22.8
[42 empty] | 1979-09-14 | 4:00 | 22.8
[42 empty] | 1979-09-14 | 5:00 | 23
[42 empty] | 1979-09-14 | 6:00 | 23.1
[42 empty] | 1979-09-14 | 7:00 | 23.3
[42 empty] | 1979-09-14 | 8:00 | 23.7
[42 empty] | 1979-09-14 | 9:00 | 24
[42 empty] | 1979-09-14 | 10:00 | 24.4
[42 empty] | 1979-09-14 | 11:00 | 24.4
[42 empty] | 1979-09-14 | 12:00 | 24.4
[42 empty] | 1979-09-14 | 13:00 | 24.4
[42 empty] | 1979-09-14 | 14:00 | 24.4
[42 empty] | 1979-09-14 | 15:00 | 24.4
[42 empty] | 1979-09-14 | 16:00 | 24.4
[42 empty] | 1979-09-14 | 17:00 | 24.2
[42 empty] | 1979-09-14 | 18:00 | 24.1
[42 empty] | 1979-09-14 | 19:00 | 23.9
[42 empty] | 1979-09-14 | 20:00 | 23
[42 empty] | 1979-09-14 | 21:00 | 22
[42 empty] | 1979-09-14 | 22:00 | 21.1
[42 empty] | 1979-09-14 | 23:00 | 20.9
[42 empty] | 1979-09-14 | 24:00 | 20.8
[42 empty] | 1979-09-15 | 1:00 | 20.6
[42 empty] | 1979-09-15 | 2:00 | 19.5
[42 empty] | 1979-09-15 | 3:00 | 18.3
[42 empty] | 1979-09-15 | 4:00 | 17.2
[42 empty] | 1979-09-15 | 5:00 | 17.2
[42 empty] | 1979-09-15 | 6:00 | 17.2
[42 empty] | 1979-09-15 | 7:00 | 17.2
[42 empty] | 1979-09-15 | 8:00 | 18.3
[42 empty] | 1979-09-15 | 9:00 | 19.5
[42 empty] | 1979-09-15 | 10:00 | 20.6
[42 empty] | 1979-09-15 | 11:00 | 20.8
[42 empty] | 1979-09-15 | 12:00 | 20.9
[42 empty] | 1979-09-15 | 13:00 | 21.1
[42 empty] | 1979-09-15 | 14:00 | 21.3
[42 empty] | 1979-09-15 | 15:00 | 21.5
[42 empty] | 1979-09-15 | 16:00 | 21.7
[42 empty] | 1979-09-15 | 17:00 | 20.9
[42 empty] | 1979-09-15 | 18:00 | 20.2
[42 empty] | 1979-09-15 | 19:00 | 19.4
[42 empty] | 1979-09-15 | 20:00 | 18.9
[42 empty] | 1979-09-15 | 21:00 | 18.3
[42 empty] | 1979-09-15 | 22:00 | 17.8
[42 empty] | 1979-09-15 | 23:00 | 17.2
[42 empty] | 1979-09-15 | 24:00 | 16.7
[42 empty] | 1979-09-16 | 1:00 | 16.1
[42 empty] | 1979-09-16 | 2:00 | 15.4
[42 empty] | 1979-09-16 | 3:00 | 14.6
[42 empty] | 1979-09-16 | 4:00 | 13.9
[42 empty] | 1979-09-16 | 5:00 | 14.5
[42 empty] | 1979-09-16 | 6:00 | 15
[42 empty] | 1979-09-16 | 7:00 | 15.6
[42 empty] | 1979-09-16 | 8:00 | 16.9
[42 empty] | 1979-09-16 | 9:00 | 18.1
[42 empty] | 1979-09-16 | 10:00 | 19.4
[42 empty] | 1979-09-16 | 11:00 | 20.2
[42 empty] | 1979-09-16 | 12:00 | 20.9
[42 empty] | 1979-09-16 | 13:00 | 21.7
[42 empty] | 1979-09-16 | 14:00 | 22.1
[42 empty] | 1979-09-16 | 15:00 | 22.4
[42 empty] | 1979-09-16 | 16:00 | 22.8
[42 empty] | 1979-09-16 | 17:00 | 22.1
[42 empty] | 1979-09-16 | 18:00 | 21.3
[42 empty] | 1979-09-16 | 19:00 | 20.6
[42 empty] | 1979-09-16 | 20:00 | 20
[42 empty] | 1979-09-16 | 21:00 | 19.5
[42 empty] | 1979-09-16 | 22:00 | 18.9
[42 empty] | 1979-09-16 | 23:00 | 18.5
[42 empty] | 1979-09-16 | 24:00 | 18.2
[42 empty] | 1979-09-17 | 1:00 | 17.8
[42 empty] | 1979-09-17 | 2:00 | 17.6
[42 empty] | 1979-09-17 | 3:00 | 17.4
[42 empty] | 1979-09-17 | 4:00 | 17.2
[42 empty] | 1979-09-17 | 5:00 | 17.4
[42 empty] | 1979-09-17 | 6:00 | 17.6
[42 empty] | 1979-09-17 | 7:00 | 17.8
[42 empty] | 1979-09-17 | 8:00 | 19.5
[42 empty] | 1979-09-17 | 9:00 | 21.1
[42 empty] | 1979-09-17 | 10:00 | 22.8
[42 empty] | 1979-09-17 | 11:00 | 23.2
[42 empty] | 1979-09-17 | 12:00 | 23.5
[42 empty] | 1979-09-17 | 13:00 | 23.9
[42 empty] | 1979-09-17 | 14:00 | 23.9
[42 empty] | 1979-09-17 | 15:00 | 23.9
[42 empty] | 1979-09-17 | 16:00 | 23.9
[42 empty] | 1979-09-17 | 17:00 | 23.2
[42 empty] | 1979-09-17 | 18:00 | 22.4
[42 empty] | 1979-09-17 | 19:00 | 21.7
[42 empty] | 1979-09-17 | 20:00 | 20.9
[42 empty] | 1979-09-17 | 21:00 | 20.2
[42 empty] | 1979-09-17 | 22:00 | 19.4
[42 empty] | 1979-09-17 | 23:00 | 19
[42 empty] | 1979-09-17 | 24:00 | 18.7
[42 empty] | 1979-09-18 | 1:00 | 18.3
[42 empty] | 1979-09-18 | 2:00 | 17.9
[42 empty] | 1979-09-18 | 3:00 | 17.6
[42 empty] | 1979-09-18 | 4:00 | 17.2
[42 empty] | 1979-09-18 | 5:00 | 17.6
[42 empty] | 1979-09-18 | 6:00 | 17.9
[42 empty] | 1979-09-18 | 7:00 | 18.3
[42 empty] | 1979-09-18 | 8:00 | 19.8
[42 empty] | 1979-09-18 | 9:00 | 21.3
[42 empty] | 1979-09-18 | 10:00 | 22.8
[42 empty] | 1979-09-18 | 11:00 | 23.5
[42 empty] | 1979-09-18 | 12:00 | 24.3
[42 empty] | 1979-09-18 | 13:00 | 25
[42 empty] | 1979-09-18 | 14:00 | 24.6
[42 empty] | 1979-09-18 | 15:00 | 24.3
[42 empty] | 1979-09-18 | 16:00 | 23.9
[42 empty] | 1979-09-18 | 17:00 | 23.2
[42 empty] | 1979-09-18 | 18:00 | 22.4
[42 empty] | 1979-09-18 | 19:00 | 21.7
[42 empty] | 1979-09-18 | 20:00 | 21.3
[42 empty] | 1979-09-18 | 21:00 | 21
[42 empty] | 1979-09-18 | 22:00 | 20.6
[42 empty] | 1979-09-18 | 23:00 | 20.2
[42 empty] | 1979-09-18 | 24:00 | 19.8
[42 empty] | 1979-09-19 | 1:00 | 19.4
[42 empty] | 1979-09-19 | 2:00 | 19.4
[42 empty] | 1979-09-19 | 3:00 | 19.4
[42 empty] | 1979-09-19 | 4:00 | 19.4
[42 empty] | 1979-09-19 | 5:00 | 19
[42 empty] | 1979-09-19 | 6:00 | 18.7
[42 empty] | 1979-09-19 | 7:00 | 18.3
[42 empty] | 1979-09-19 | 8:00 | 19.2
[42 empty] | 1979-09-19 | 9:00 | 20.2
[42 empty] | 1979-09-19 | 10:00 | 21.1
[42 empty] | 1979-09-19 | 11:00 | 20.7
[42 empty] | 1979-09-19 | 12:00 | 20.4
[42 empty] | 1979-09-19 | 13:00 | 20
[42 empty] | 1979-09-19 | 14:00 | 19.4
[42 empty] | 1979-09-19 | 15:00 | 18.9
[42 empty] | 1979-09-19 | 16:00 | 18.3
[42 empty] | 1979-09-19 | 17:00 | 17.4
[42 empty] | 1979-09-19 | 18:00 | 16.5
[42 empty] | 1979-09-19 | 19:00 | 15.6
[42 empty] | 1979-09-19 | 20:00 | 14.5
[42 empty] | 1979-09-19 | 21:00 | 13.3
[42 empty] | 1979-09-19 | 22:00 | 12.2
[42 empty] | 1979-09-19 | 23:00 | 11.3
[42 empty] | 1979-09-19 | 24:00 | 10.3
[42 empty] | 1979-09-20 | 1:00 | 9.4
[42 empty] | 1979-09-20 | 2:00 | 8.9
[42 empty] | 1979-09-20 | 3:00 | 8.3
[42 empty] | 1979-09-20 | 4:00 | 7.8
[42 empty] | 1979-09-20 | 5:00 | 8.5
[42 empty] | 1979-09-20 | 6:00 | 9.3
[42 empty] | 1979-09-20 | 7:00 | 10
[42 empty] | 1979-09-20 | 8:00 | 11.3
[42 empty] | 1979-09-20 | 9:00 | 12.6
[42 empty] | 1979-09-20 | 10:00 | 13.9
[42 empty] | 1979-09-20 | 11:00 | 14.5
[42 empty] | 1979-09-20 | 12:00 | 15
[42 empty] | 1979-09-20 | 13:00 | 15.6
[42 empty] | 1979-09-20 | 14:00 | 15.8
[42 empty] | 1979-09-20 | 15:00 | 15.9
[42 empty] | 1979-09-20 | 16:00 | 16.1
[42 empty] | 1979-09-20 | 17:00 | 15.9
[42 empty] | 1979-09-20 | 18:00 | 15.8
[42 empty] | 1979-09-20 | 19:00 | 15.6
[42 empty] | 1979-09-20 | 20:00 | 15.6
[42 empty] | 1979-09-20 | 21:00 | 15.6
[42 empty] | 1979-09-20 | 22:00 | 15.6
[42 empty] | 1979-09-20 | 23:00 | 16
[42 empty] | 1979-09-20 | 24:00 | 16.3
[42 empty] | 1979-09-21 | 1:00 | 16.7
[42 empty] | 1979-09-21 | 2:00 | 16.5
[42 empty] | 1979-09-21 | 3:00 | 16.3
[42 empty] | 1979-09-21 | 4:00 | 16.1
[42 empty] | 1979-09-21 | 5:00 | 16.5
[42 empty] | 1979-09-21 | 6:00 | 16.8
[42 empty] | 1979-09-21 | 7:00 | 17.2
[42 empty] | 1979-09-21 | 8:00 | 17.9
[42 empty] | 1979-09-21 | 9:00 | 18.7
[42 empty] | 1979-09-21 | 10:00 | 19.4
[42 empty] | 1979-09-21 | 11:00 | 19.8
[42 empty] | 1979-09-21 | 12:00 | 20.2
[42 empty] | 1979-09-21 | 13:00 | 20.6
[42 empty] | 1979-09-21 | 14:00 | 20.6
[42 empty] | 1979-09-21 | 15:00 | 20.6
[42 empty] | 1979-09-21 | 16:00 | 20.6
[42 empty] | 1979-09-21 | 17:00 | 20.4
[42 empty] | 1979-09-21 | 18:00 | 20.2
[42 empty] | 1979-09-21 | 19:00 | 20
[42 empty] | 1979-09-21 | 20:00 | 20.2
[42 empty] | 1979-09-21 | 21:00 | 20.4
[42 empty] | 1979-09-21 | 22:00 | 20.6
[42 empty] | 1979-09-21 | 23:00 | 20.4
[42 empty] | 1979-09-21 | 24:00 | 20.2
[42 empty] | 1979-09-22 | 1:00 | 20
[42 empty] | 1979-09-22 | 2:00 | 20
[42 empty] | 1979-09-22 | 3:00 | 20
[42 empty] | 1979-09-22 | 4:00 | 20
[42 empty] | 1979-09-22 | 5:00 | 20
[42 empty] | 1979-09-22 | 6:00 | 20
[42 empty] | 1979-09-22 | 7:00 | 20
[42 empty] | 1979-09-22 | 8:00 | 19.4
[42 empty] | 1979-09-22 | 9:00 | 18.9
[42 empty] | 1979-09-22 | 10:00 | 18.3
[42 empty] | 1979-09-22 | 11:00 | 18.5
[42 empty] | 1979-09-22 | 12:00 | 18.7
[42 empty] | 1979-09-22 | 13:00 | 18.9
[42 empty] | 1979-09-22 | 14:00 | 18.9
[42 empty] | 1979-09-22 | 15:00 | 18.9
[42 empty] | 1979-09-22 | 16:00 | 18.9
[42 empty] | 1979-09-22 | 17:00 | 18.2
[42 empty] | 1979-09-22 | 18:00 | 17.4
[42 empty] | 1979-09-22 | 19:00 | 16.7
[42 empty] | 1979-09-22 | 20:00 | 16.7
[42 empty] | 1979-09-22 | 21:00 | 16.7
[42 empty] | 1979-09-22 | 22:00 | 16.7
[42 empty] | 1979-09-22 | 23:00 | 16.3
[42 empty] | 1979-09-22 | 24:00 | 16
[42 empty] | 1979-09-23 | 1:00 | 15.6
[42 empty] | 1979-09-23 | 2:00 | 15
[42 empty] | 1979-09-23 | 3:00 | 14.5
[42 empty] | 1979-09-23 | 4:00 | 13.9
[42 empty] | 1979-09-23 | 5:00 | 13.5
[42 empty] | 1979-09-23 | 6:00 | 13.2
[42 empty] | 1979-09-23 | 7:00 | 12.8
[42 empty] | 1979-09-23 | 8:00 | 14.1
[42 empty] | 1979-09-23 | 9:00 | 15.4
[42 empty] | 1979-09-23 | 10:00 | 16.7
[42 empty] | 1979-09-23 | 11:00 | 17.4
[42 empty] | 1979-09-23 | 12:00 | 18.2
[42 empty] | 1979-09-23 | 13:00 | 18.9
[42 empty] | 1979-09-23 | 14:00 | 18.9
[42 empty] | 1979-09-23 | 15:00 | 18.9
[42 empty] | 1979-09-23 | 16:00 | 18.9
[42 empty] | 1979-09-23 | 17:00 | 18
[42 empty] | 1979-09-23 | 18:00 | 17
[42 empty] | 1979-09-23 | 19:00 | 16.1
[42 empty] | 1979-09-23 | 20:00 | 15.4
[42 empty] | 1979-09-23 | 21:00 | 14.6
[42 empty] | 1979-09-23 | 22:00 | 13.9
[42 empty] | 1979-09-23 | 23:00 | 13.5
[42 empty] | 1979-09-23 | 24:00 | 13.2
[42 empty] | 1979-09-24 | 1:00 | 12.8
[42 empty] | 1979-09-24 | 2:00 | 12.2
[42 empty] | 1979-09-24 | 3:00 | 11.7
[42 empty] | 1979-09-24 | 4:00 | 11.1
[42 empty] | 1979-09-24 | 5:00 | 11.3
[42 empty] | 1979-09-24 | 6:00 | 11.5
[42 empty] | 1979-09-24 | 7:00 | 11.7
[42 empty] | 1979-09-24 | 8:00 | 13.4
[42 empty] | 1979-09-24 | 9:00 | 15
[42 empty] | 1979-09-24 | 10:00 | 16.7
[42 empty] | 1979-09-24 | 11:00 | 17.2
[42 empty] | 1979-09-24 | 12:00 | 17.8
[42 empty] | 1979-09-24 | 13:00 | 18.3
[42 empty] | 1979-09-24 | 14:00 | 18.3
[42 empty] | 1979-09-24 | 15:00 | 18.3
[42 empty] | 1979-09-24 | 16:00 | 18.3
[42 empty] | 1979-09-24 | 17:00 | 17.6
[42 empty] | 1979-09-24 | 18:00 | 16.8
[42 empty] | 1979-09-24 | 19:00 | 16.1
[42 empty] | 1979-09-24 | 20:00 | 15.5
[42 empty] | 1979-09-24 | 21:00 | 15
[42 empty] | 1979-09-24 | 22:00 | 14.4
[42 empty] | 1979-09-24 | 23:00 | 14.4
[42 empty] | 1979-09-24 | 24:00 | 14.4
[42 empty] | 1979-09-25 | 1:00 | 14.4
[42 empty] | 1979-09-25 | 2:00 | 14
[42 empty] | 1979-09-25 | 3:00 | 13.7
[42 empty] | 1979-09-25 | 4:00 | 13.3
[42 empty] | 1979-09-25 | 5:00 | 13.1
[42 empty] | 1979-09-25 | 6:00 | 13
[42 empty] | 1979-09-25 | 7:00 | 12.8
[42 empty] | 1979-09-25 | 8:00 | 13.7
[42 empty] | 1979-09-25 | 9:00 | 14.7
[42 empty] | 1979-09-25 | 10:00 | 15.6
[42 empty] | 1979-09-25 | 11:00 | 16.1
[42 empty] | 1979-09-25 | 12:00 | 16.7
[42 empty] | 1979-09-25 | 13:00 | 17.2
[42 empty] | 1979-09-25 | 14:00 | 17.8
[42 empty] | 1979-09-25 | 15:00 | 18.3
[42 empty] | 1979-09-25 | 16:00 | 18.9
[42 empty] | 1979-09-25 | 17:00 | 18.3
[42 empty] | 1979-09-25 | 18:00 | 17.8
[42 empty] | 1979-09-25 | 19:00 | 17.2
[42 empty] | 1979-09-25 | 20:00 | 17
[42 empty] | 1979-09-25 | 21:00 | 16.9
[42 empty] | 1979-09-25 | 22:00 | 16.7
[42 empty] | 1979-09-25 | 23:00 | 16.1
[42 empty] | 1979-09-25 | 24:00 | 15.6
[42 empty] | 1979-09-26 | 1:00 | 15
[42 empty] | 1979-09-26 | 2:00 | 15.2
[42 empty] | 1979-09-26 | 3:00 | 15.4
[42 empty] | 1979-09-26 | 4:00 | 15.6
[42 empty] | 1979-09-26 | 5:00 | 15.6
[42 empty] | 1979-09-26 | 6:00 | 15.6
[42 empty] | 1979-09-26 | 7:00 | 15.6
[42 empty] | 1979-09-26 | 8:00 | 17.3
[42 empty] | 1979-09-26 | 9:00 | 18.9
[42 empty] | 1979-09-26 | 10:00 | 20.6
[42 empty] | 1979-09-26 | 11:00 | 21.9
[42 empty] | 1979-09-26 | 12:00 | 23.1
[42 empty] | 1979-09-26 | 13:00 | 24.4
[42 empty] | 1979-09-26 | 14:00 | 24.2
[42 empty] | 1979-09-26 | 15:00 | 24.1
[42 empty] | 1979-09-26 | 16:00 | 23.9
[42 empty] | 1979-09-26 | 17:00 | 23.3
[42 empty] | 1979-09-26 | 18:00 | 22.8
[42 empty] | 1979-09-26 | 19:00 | 22.2
[42 empty] | 1979-09-26 | 20:00 | 21.5
[42 empty] | 1979-09-26 | 21:00 | 20.7
[42 empty] | 1979-09-26 | 22:00 | 20
[42 empty] | 1979-09-26 | 23:00 | 18.9
[42 empty] | 1979-09-26 | 24:00 | 17.8
[42 empty] | 1979-09-27 | 1:00 | 16.7
[42 empty] | 1979-09-27 | 2:00 | 16.5
[42 empty] | 1979-09-27 | 3:00 | 16.3
[42 empty] | 1979-09-27 | 4:00 | 16.1
[42 empty] | 1979-09-27 | 5:00 | 15.9
[42 empty] | 1979-09-27 | 6:00 | 15.8
[42 empty] | 1979-09-27 | 7:00 | 15.6
[42 empty] | 1979-09-27 | 8:00 | 16.5
[42 empty] | 1979-09-27 | 9:00 | 17.4
[42 empty] | 1979-09-27 | 10:00 | 18.3
[42 empty] | 1979-09-27 | 11:00 | 19.2
[42 empty] | 1979-09-27 | 12:00 | 20.2
[42 empty] | 1979-09-27 | 13:00 | 21.1
[42 empty] | 1979-09-27 | 14:00 | 21.3
[42 empty] | 1979-09-27 | 15:00 | 21.5
[42 empty] | 1979-09-27 | 16:00 | 21.7
[42 empty] | 1979-09-27 | 17:00 | 20.6
[42 empty] | 1979-09-27 | 18:00 | 19.4
[42 empty] | 1979-09-27 | 19:00 | 18.3
[42 empty] | 1979-09-27 | 20:00 | 17.9
[42 empty] | 1979-09-27 | 21:00 | 17.6
[42 empty] | 1979-09-27 | 22:00 | 17.2
[42 empty] | 1979-09-27 | 23:00 | 17
[42 empty] | 1979-09-27 | 24:00 | 16.9
[42 empty] | 1979-09-28 | 1:00 | 16.7
[42 empty] | 1979-09-28 | 2:00 | 16.5
[42 empty] | 1979-09-28 | 3:00 | 16.3
[42 empty] | 1979-09-28 | 4:00 | 16.1
[42 empty] | 1979-09-28 | 5:00 | 16.1
[42 empty] | 1979-09-28 | 6:00 | 16.1
[42 empty] | 1979-09-28 | 7:00 | 16.1
[42 empty] | 1979-09-28 | 8:00 | 17.8
[42 empty] | 1979-09-28 | 9:00 | 19.4
[42 empty] | 1979-09-28 | 10:00 | 21.1
[42 empty] | 1979-09-28 | 11:00 | 21.7
[42 empty] | 1979-09-28 | 12:00 | 22.2
[42 empty] | 1979-09-28 | 13:00 | 22.8
[42 empty] | 1979-09-28 | 14:00 | 22.8
[42 empty] | 1979-09-28 | 15:00 | 22.8
[42 empty] | 1979-09-28 | 16:00 | 22.8
[42 empty] | 1979-09-28 | 17:00 | 22.4
[42 empty] | 1979-09-28 | 18:00 | 22.1
[42 empty] | 1979-09-28 | 19:00 | 21.7
[42 empty] | 1979-09-28 | 20:00 | 21.7
[42 empty] | 1979-09-28 | 21:00 | 21.7
[42 empty] | 1979-09-28 | 22:00 | 21.7
[42 empty] | 1979-09-28 | 23:00 | 21.7
[42 empty] | 1979-09-28 | 24:00 | 21.7
[42 empty] | 1979-09-29 | 1:00 | 21.7
[42 empty] | 1979-09-29 | 2:00 | 21.9
[42 empty] | 1979-09-29 | 3:00 | 22
[42 empty] | 1979-09-29 | 4:00 | 22.2
[42 empty] | 1979-09-29 | 5:00 | 22
[42 empty] | 1979-09-29 | 6:00 | 21.9
[42 empty] | 1979-09-29 | 7:00 | 21.7
[42 empty] | 1979-09-29 | 8:00 | 22.1
[42 empty] | 1979-09-29 | 9:00 | 22.4
[42 empty] | 1979-09-29 | 10:00 | 22.8
[42 empty] | 1979-09-29 | 11:00 | 23.3
[42 empty] | 1979-09-29 | 12:00 | 23.9
[42 empty] | 1979-09-29 | 13:00 | 24.4
[42 empty] | 1979-09-29 | 14:00 | 24
[42 empty] | 1979-09-29 | 15:00 | 23.7
[42 empty] | 1979-09-29 | 16:00 | 23.3
[42 empty] | 1979-09-29 | 17:00 | 22.8
[42 empty] | 1979-09-29 | 18:00 | 22.2
[42 empty] | 1979-09-29 | 19:00 | 21.7
[42 empty] | 1979-09-29 | 20:00 | 21.5
[42 empty] | 1979-09-29 | 21:00 | 21.3
[42 empty] | 1979-09-29 | 22:00 | 21.1
[42 empty] | 1979-09-29 | 23:00 | 20.7
[42 empty] | 1979-09-29 | 24:00 | 20.4
[42 empty] | 1979-09-30 | 1:00 | 20
[42 empty] | 1979-09-30 | 2:00 | 19.8
[42 empty] | 1979-09-30 | 3:00 | 19.6
[42 empty] | 1979-09-30 | 4:00 | 19.4
[42 empty] | 1979-09-30 | 5:00 | 18.9
[42 empty] | 1979-09-30 | 6:00 | 18.3
[42 empty] | 1979-09-30 | 7:00 | 17.8
[42 empty] | 1979-09-30 | 8:00 | 18
[42 empty] | 1979-09-30 | 9:00 | 18.1
[42 empty] | 1979-09-30 | 10:00 | 18.3
[42 empty] | 1979-09-30 | 11:00 | 18.1
[42 empty] | 1979-09-30 | 12:00 | 18
[42 empty] | 1979-09-30 | 13:00 | 17.8
[42 empty] | 1979-09-30 | 14:00 | 17.8
[42 empty] | 1979-09-30 | 15:00 | 17.8
[42 empty] | 1979-09-30 | 16:00 | 17.8
[42 empty] | 1979-09-30 | 17:00 | 17.6
[42 empty] | 1979-09-30 | 18:00 | 17.4
[42 empty] | 1979-09-30 | 19:00 | 17.2
[42 empty] | 1979-09-30 | 20:00 | 17.2
[42 empty] | 1979-09-30 | 21:00 | 17.2
[42 empty] | 1979-09-30 | 22:00 | 17.2
[42 empty] | 1979-09-30 | 23:00 | 17.2
[42 empty] | 1979-09-30 | 24:00 | 17.2
[42 empty] | 1980-10-01 | 1:00 | 17.2
[42 empty] | 1980-10-01 | 2:00 | 17.2
[42 empty] | 1980-10-01 | 3:00 | 17.2
[42 empty] | 1980-10-01 | 4:00 | 17.2
[42 empty] | 1980-10-01 | 5:00 | 17
[42 empty] | 1980-10-01 | 6:00 | 16.9
[42 empty] | 1980-10-01 | 7:00 | 16.7
[42 empty] | 1980-10-01 | 8:00 | 18
[42 empty] | 1980-10-01 | 9:00 | 19.3
[42 empty] | 1980-10-01 | 10:00 | 20.6
[42 empty] | 1980-10-01 | 11:00 | 21.5
[42 empty] | 1980-10-01 | 12:00 | 22.4
[42 empty] | 1980-10-01 | 13:00 | 23.3
[42 empty] | 1980-10-01 | 14:00 | 23.1
[42 empty] | 1980-10-01 | 15:00 | 23
[42 empty] | 1980-10-01 | 16:00 | 22.8
[42 empty] | 1980-10-01 | 17:00 | 21.9
[42 empty] | 1980-10-01 | 18:00 | 20.9
[42 empty] | 1980-10-01 | 19:00 | 20
[42 empty] | 1980-10-01 | 20:00 | 19.8
[42 empty] | 1980-10-01 | 21:00 | 19.6
[42 empty] | 1980-10-01 | 22:00 | 19.4
[42 empty] | 1980-10-01 | 23:00 | 18.7
[42 empty] | 1980-10-01 | 24:00 | 17.9
[42 empty] | 1980-10-02 | 1:00 | 17.2
[42 empty] | 1980-10-02 | 2:00 | 17.2
[42 empty] | 1980-10-02 | 3:00 | 17.2
[42 empty] | 1980-10-02 | 4:00 | 17.2
[42 empty] | 1980-10-02 | 5:00 | 17.2
[42 empty] | 1980-10-02 | 6:00 | 17.2
[42 empty] | 1980-10-02 | 7:00 | 17.2
[42 empty] | 1980-10-02 | 8:00 | 17.6
[42 empty] | 1980-10-02 | 9:00 | 17.9
[42 empty] | 1980-10-02 | 10:00 | 18.3
[42 empty] | 1980-10-02 | 11:00 | 18.7
[42 empty] | 1980-10-02 | 12:00 | 19
[42 empty] | 1980-10-02 | 13:00 | 19.4
[42 empty] | 1980-10-02 | 14:00 | 20
[42 empty] | 1980-10-02 | 15:00 | 20.5
[42 empty] | 1980-10-02 | 16:00 | 21.1
[42 empty] | 1980-10-02 | 17:00 | 20.5
[42 empty] | 1980-10-02 | 18:00 | 20
[42 empty] | 1980-10-02 | 19:00 | 19.4
[42 empty] | 1980-10-02 | 20:00 | 18.1
[42 empty] | 1980-10-02 | 21:00 | 16.9
[42 empty] | 1980-10-02 | 22:00 | 15.6
[42 empty] | 1980-10-02 | 23:00 | 15.2
[42 empty] | 1980-10-02 | 24:00 | 14.8
[42 empty] | 1980-10-03 | 1:00 | 14.4
[42 empty] | 1980-10-03 | 2:00 | 14.2
[42 empty] | 1980-10-03 | 3:00 | 14.1
[42 empty] | 1980-10-03 | 4:00 | 13.9
[42 empty] | 1980-10-03 | 5:00 | 13.9
[42 empty] | 1980-10-03 | 6:00 | 13.9
[42 empty] | 1980-10-03 | 7:00 | 13.9
[42 empty] | 1980-10-03 | 8:00 | 14.6
[42 empty] | 1980-10-03 | 9:00 | 15.4
[42 empty] | 1980-10-03 | 10:00 | 16.1
[42 empty] | 1980-10-03 | 11:00 | 16.8
[42 empty] | 1980-10-03 | 12:00 | 17.6
[42 empty] | 1980-10-03 | 13:00 | 18.3
[42 empty] | 1980-10-03 | 14:00 | 17.9
[42 empty] | 1980-10-03 | 15:00 | 17.6
[42 empty] | 1980-10-03 | 16:00 | 17.2
[42 empty] | 1980-10-03 | 17:00 | 16.7
[42 empty] | 1980-10-03 | 18:00 | 16.1
[42 empty] | 1980-10-03 | 19:00 | 15.6
[42 empty] | 1980-10-03 | 20:00 | 15
[42 empty] | 1980-10-03 | 21:00 | 14.5
[42 empty] | 1980-10-03 | 22:00 | 13.9
[42 empty] | 1980-10-03 | 23:00 | 13.9
[42 empty] | 1980-10-03 | 24:00 | 13.9
[42 empty] | 1980-10-04 | 1:00 | 13.9
[42 empty] | 1980-10-04 | 2:00 | 13.7
[42 empty] | 1980-10-04 | 3:00 | 13.5
[42 empty] | 1980-10-04 | 4:00 | 13.3
[42 empty] | 1980-10-04 | 5:00 | 13.1
[42 empty] | 1980-10-04 | 6:00 | 13
[42 empty] | 1980-10-04 | 7:00 | 12.8
[42 empty] | 1980-10-04 | 8:00 | 13.5
[42 empty] | 1980-10-04 | 9:00 | 14.3
[42 empty] | 1980-10-04 | 10:00 | 15
[42 empty] | 1980-10-04 | 11:00 | 15.7
[42 empty] | 1980-10-04 | 12:00 | 16.5
[42 empty] | 1980-10-04 | 13:00 | 17.2
[42 empty] | 1980-10-04 | 14:00 | 17.4
[42 empty] | 1980-10-04 | 15:00 | 17.6
[42 empty] | 1980-10-04 | 16:00 | 17.8
[42 empty] | 1980-10-04 | 17:00 | 17.1
[42 empty] | 1980-10-04 | 18:00 | 16.3
[42 empty] | 1980-10-04 | 19:00 | 15.6
[42 empty] | 1980-10-04 | 20:00 | 14.8
[42 empty] | 1980-10-04 | 21:00 | 14.1
[42 empty] | 1980-10-04 | 22:00 | 13.3
[42 empty] | 1980-10-04 | 23:00 | 13.1
[42 empty] | 1980-10-04 | 24:00 | 13
[42 empty] | 1980-10-05 | 1:00 | 12.8
[42 empty] | 1980-10-05 | 2:00 | 12.6
[42 empty] | 1980-10-05 | 3:00 | 12.4
[42 empty] | 1980-10-05 | 4:00 | 12.2
[42 empty] | 1980-10-05 | 5:00 | 12.2
[42 empty] | 1980-10-05 | 6:00 | 12.2
[42 empty] | 1980-10-05 | 7:00 | 12.2
[42 empty] | 1980-10-05 | 8:00 | 13.3
[42 empty] | 1980-10-05 | 9:00 | 14.5
[42 empty] | 1980-10-05 | 10:00 | 15.6
[42 empty] | 1980-10-05 | 11:00 | 16
[42 empty] | 1980-10-05 | 12:00 | 16.3
[42 empty] | 1980-10-05 | 13:00 | 16.7
[42 empty] | 1980-10-05 | 14:00 | 16.9
[42 empty] | 1980-10-05 | 15:00 | 17
[42 empty] | 1980-10-05 | 16:00 | 17.2
[42 empty] | 1980-10-05 | 17:00 | 16.7
[42 empty] | 1980-10-05 | 18:00 | 16.1
[42 empty] | 1980-10-05 | 19:00 | 15.6
[42 empty] | 1980-10-05 | 20:00 | 15
[42 empty] | 1980-10-05 | 21:00 | 14.5
[42 empty] | 1980-10-05 | 22:00 | 13.9
[42 empty] | 1980-10-05 | 23:00 | 13.5
[42 empty] | 1980-10-05 | 24:00 | 13.2
[42 empty] | 1980-10-06 | 1:00 | 12.8
[42 empty] | 1980-10-06 | 2:00 | 12.6
[42 empty] | 1980-10-06 | 3:00 | 12.4
[42 empty] | 1980-10-06 | 4:00 | 12.2
[42 empty] | 1980-10-06 | 5:00 | 12
[42 empty] | 1980-10-06 | 6:00 | 11.9
[42 empty] | 1980-10-06 | 7:00 | 11.7
[42 empty] | 1980-10-06 | 8:00 | 12.4
[42 empty] | 1980-10-06 | 9:00 | 13.2
[42 empty] | 1980-10-06 | 10:00 | 13.9
[42 empty] | 1980-10-06 | 11:00 | 14.8
[42 empty] | 1980-10-06 | 12:00 | 15.8
[42 empty] | 1980-10-06 | 13:00 | 16.7
[42 empty] | 1980-10-06 | 14:00 | 16.7
[42 empty] | 1980-10-06 | 15:00 | 16.7
[42 empty] | 1980-10-06 | 16:00 | 16.7
[42 empty] | 1980-10-06 | 17:00 | 16.1
[42 empty] | 1980-10-06 | 18:00 | 15.6
[42 empty] | 1980-10-06 | 19:00 | 15
[42 empty] | 1980-10-06 | 20:00 | 14.6
[42 empty] | 1980-10-06 | 21:00 | 14.3
[42 empty] | 1980-10-06 | 22:00 | 13.9
[42 empty] | 1980-10-06 | 23:00 | 13.3
[42 empty] | 1980-10-06 | 24:00 | 12.8
[42 empty] | 1980-10-07 | 1:00 | 12.2
[42 empty] | 1980-10-07 | 2:00 | 12
[42 empty] | 1980-10-07 | 3:00 | 11.9
[42 empty] | 1980-10-07 | 4:00 | 11.7
[42 empty] | 1980-10-07 | 5:00 | 11.7
[42 empty] | 1980-10-07 | 6:00 | 11.7
[42 empty] | 1980-10-07 | 7:00 | 11.7
[42 empty] | 1980-10-07 | 8:00 | 12.1
[42 empty] | 1980-10-07 | 9:00 | 12.4
[42 empty] | 1980-10-07 | 10:00 | 12.8
[42 empty] | 1980-10-07 | 11:00 | 13.7
[42 empty] | 1980-10-07 | 12:00 | 14.7
[42 empty] | 1980-10-07 | 13:00 | 15.6
[42 empty] | 1980-10-07 | 14:00 | 16
[42 empty] | 1980-10-07 | 15:00 | 16.3
[42 empty] | 1980-10-07 | 16:00 | 16.7
[42 empty] | 1980-10-07 | 17:00 | 16.1
[42 empty] | 1980-10-07 | 18:00 | 15.6
[42 empty] | 1980-10-07 | 19:00 | 15
[42 empty] | 1980-10-07 | 20:00 | 14.8
[42 empty] | 1980-10-07 | 21:00 | 14.6
[42 empty] | 1980-10-07 | 22:00 | 14.4
[42 empty] | 1980-10-07 | 23:00 | 14
[42 empty] | 1980-10-07 | 24:00 | 13.7
[42 empty] | 1980-10-08 | 1:00 | 13.3
[42 empty] | 1980-10-08 | 2:00 | 12.8
[42 empty] | 1980-10-08 | 3:00 | 12.2
[42 empty] | 1980-10-08 | 4:00 | 11.7
[42 empty] | 1980-10-08 | 5:00 | 11.7
[42 empty] | 1980-10-08 | 6:00 | 11.7
[42 empty] | 1980-10-08 | 7:00 | 11.7
[42 empty] | 1980-10-08 | 8:00 | 13.4
[42 empty] | 1980-10-08 | 9:00 | 15
[42 empty] | 1980-10-08 | 10:00 | 16.7
[42 empty] | 1980-10-08 | 11:00 | 17.6
[42 empty] | 1980-10-08 | 12:00 | 18.5
[42 empty] | 1980-10-08 | 13:00 | 19.4
[42 empty] | 1980-10-08 | 14:00 | 19.8
[42 empty] | 1980-10-08 | 15:00 | 20.2
[42 empty] | 1980-10-08 | 16:00 | 20.6
[42 empty] | 1980-10-08 | 17:00 | 20.2
[42 empty] | 1980-10-08 | 18:00 | 19.8
[42 empty] | 1980-10-08 | 19:00 | 19.4
[42 empty] | 1980-10-08 | 20:00 | 18.9
[42 empty] | 1980-10-08 | 21:00 | 18.3
[42 empty] | 1980-10-08 | 22:00 | 17.8
[42 empty] | 1980-10-08 | 23:00 | 17.4
[42 empty] | 1980-10-08 | 24:00 | 17.1
[42 empty] | 1980-10-09 | 1:00 | 16.7
[42 empty] | 1980-10-09 | 2:00 | 16.1
[42 empty] | 1980-10-09 | 3:00 | 15.6
[42 empty] | 1980-10-09 | 4:00 | 15
[42 empty] | 1980-10-09 | 5:00 | 15.2
[42 empty] | 1980-10-09 | 6:00 | 15.4
[42 empty] | 1980-10-09 | 7:00 | 15.6
[42 empty] | 1980-10-09 | 8:00 | 16.3
[42 empty] | 1980-10-09 | 9:00 | 17.1
[42 empty] | 1980-10-09 | 10:00 | 17.8
[42 empty] | 1980-10-09 | 11:00 | 18.5
[42 empty] | 1980-10-09 | 12:00 | 19.3
[42 empty] | 1980-10-09 | 13:00 | 20
[42 empty] | 1980-10-09 | 14:00 | 20
[42 empty] | 1980-10-09 | 15:00 | 20
[42 empty] | 1980-10-09 | 16:00 | 20
[42 empty] | 1980-10-09 | 17:00 | 18.9
[42 empty] | 1980-10-09 | 18:00 | 17.8
[42 empty] | 1980-10-09 | 19:00 | 16.7
[42 empty] | 1980-10-09 | 20:00 | 15.2
[42 empty] | 1980-10-09 | 21:00 | 13.7
[42 empty] | 1980-10-09 | 22:00 | 12.2
[42 empty] | 1980-10-09 | 23:00 | 11.5
[42 empty] | 1980-10-09 | 24:00 | 10.7
[42 empty] | 1980-10-10 | 1:00 | 10
[42 empty] | 1980-10-10 | 2:00 | 9.6
[42 empty] | 1980-10-10 | 3:00 | 9.3
[42 empty] | 1980-10-10 | 4:00 | 8.9
[42 empty] | 1980-10-10 | 5:00 | 8.7
[42 empty] | 1980-10-10 | 6:00 | 8.5
[42 empty] | 1980-10-10 | 7:00 | 8.3
[42 empty] | 1980-10-10 | 8:00 | 9.2
[42 empty] | 1980-10-10 | 9:00 | 10.2
[42 empty] | 1980-10-10 | 10:00 | 11.1
[42 empty] | 1980-10-10 | 11:00 | 12
[42 empty] | 1980-10-10 | 12:00 | 13
[42 empty] | 1980-10-10 | 13:00 | 13.9
[42 empty] | 1980-10-10 | 14:00 | 13.9
[42 empty] | 1980-10-10 | 15:00 | 13.9
[42 empty] | 1980-10-10 | 16:00 | 13.9
[42 empty] | 1980-10-10 | 17:00 | 13.5
[42 empty] | 1980-10-10 | 18:00 | 13.2
[42 empty] | 1980-10-10 | 19:00 | 12.8
[42 empty] | 1980-10-10 | 20:00 | 12.8
[42 empty] | 1980-10-10 | 21:00 | 12.8
[42 empty] | 1980-10-10 | 22:00 | 12.8
[42 empty] | 1980-10-10 | 23:00 | 13
[42 empty] | 1980-10-10 | 24:00 | 13.1
[42 empty] | 1980-10-11 | 1:00 | 13.3
[42 empty] | 1980-10-11 | 2:00 | 14.4
[42 empty] | 1980-10-11 | 3:00 | 15.6
[42 empty] | 1980-10-11 | 4:00 | 16.7
[42 empty] | 1980-10-11 | 5:00 | 17.1
[42 empty] | 1980-10-11 | 6:00 | 17.4
[42 empty] | 1980-10-11 | 7:00 | 17.8
[42 empty] | 1980-10-11 | 8:00 | 17.8
[42 empty] | 1980-10-11 | 9:00 | 17.8
[42 empty] | 1980-10-11 | 10:00 | 17.8
[42 empty] | 1980-10-11 | 11:00 | 17.8
[42 empty] | 1980-10-11 | 12:00 | 17.8
[42 empty] | 1980-10-11 | 13:00 | 17.8
[42 empty] | 1980-10-11 | 14:00 | 18
[42 empty] | 1980-10-11 | 15:00 | 18.1
[42 empty] | 1980-10-11 | 16:00 | 18.3
[42 empty] | 1980-10-11 | 17:00 | 17.4
[42 empty] | 1980-10-11 | 18:00 | 16.5
[42 empty] | 1980-10-11 | 19:00 | 15.6
[42 empty] | 1980-10-11 | 20:00 | 15
[42 empty] | 1980-10-11 | 21:00 | 14.5
[42 empty] | 1980-10-11 | 22:00 | 13.9
[42 empty] | 1980-10-11 | 23:00 | 14.1
[42 empty] | 1980-10-11 | 24:00 | 14.2
[42 empty] | 1980-10-12 | 1:00 | 14.4
[42 empty] | 1980-10-12 | 2:00 | 13.7
[42 empty] | 1980-10-12 | 3:00 | 12.9
[42 empty] | 1980-10-12 | 4:00 | 12.2
[42 empty] | 1980-10-12 | 5:00 | 11.7
[42 empty] | 1980-10-12 | 6:00 | 11.1
[42 empty] | 1980-10-12 | 7:00 | 10.6
[42 empty] | 1980-10-12 | 8:00 | 11.5
[42 empty] | 1980-10-12 | 9:00 | 12.4
[42 empty] | 1980-10-12 | 10:00 | 13.3
[42 empty] | 1980-10-12 | 11:00 | 13.9
[42 empty] | 1980-10-12 | 12:00 | 14.4
[42 empty] | 1980-10-12 | 13:00 | 15
[42 empty] | 1980-10-12 | 14:00 | 15.2
[42 empty] | 1980-10-12 | 15:00 | 15.4
[42 empty] | 1980-10-12 | 16:00 | 15.6
[42 empty] | 1980-10-12 | 17:00 | 14.7
[42 empty] | 1980-10-12 | 18:00 | 13.7
[42 empty] | 1980-10-12 | 19:00 | 12.8
[42 empty] | 1980-10-12 | 20:00 | 12.4
[42 empty] | 1980-10-12 | 21:00 | 12.1
[42 empty] | 1980-10-12 | 22:00 | 11.7
[42 empty] | 1980-10-12 | 23:00 | 11.3
[42 empty] | 1980-10-12 | 24:00 | 11
[42 empty] | 1980-10-13 | 1:00 | 10.6
[42 empty] | 1980-10-13 | 2:00 | 10.2
[42 empty] | 1980-10-13 | 3:00 | 9.8
[42 empty] | 1980-10-13 | 4:00 | 9.4
[42 empty] | 1980-10-13 | 5:00 | 8.9
[42 empty] | 1980-10-13 | 6:00 | 8.3
[42 empty] | 1980-10-13 | 7:00 | 7.8
[42 empty] | 1980-10-13 | 8:00 | 8.5
[42 empty] | 1980-10-13 | 9:00 | 9.3
[42 empty] | 1980-10-13 | 10:00 | 10
[42 empty] | 1980-10-13 | 11:00 | 10.7
[42 empty] | 1980-10-13 | 12:00 | 11.5
[42 empty] | 1980-10-13 | 13:00 | 12.2
[42 empty] | 1980-10-13 | 14:00 | 11.8
[42 empty] | 1980-10-13 | 15:00 | 11.5
[42 empty] | 1980-10-13 | 16:00 | 11.1
[42 empty] | 1980-10-13 | 17:00 | 10.2
[42 empty] | 1980-10-13 | 18:00 | 9.2
[42 empty] | 1980-10-13 | 19:00 | 8.3
[42 empty] | 1980-10-13 | 20:00 | 8.1
[42 empty] | 1980-10-13 | 21:00 | 8
[42 empty] | 1980-10-13 | 22:00 | 7.8
[42 empty] | 1980-10-13 | 23:00 | 7.6
[42 empty] | 1980-10-13 | 24:00 | 7.4
[42 empty] | 1980-10-14 | 1:00 | 7.2
[42 empty] | 1980-10-14 | 2:00 | 7.2
[42 empty] | 1980-10-14 | 3:00 | 7.2
[42 empty] | 1980-10-14 | 4:00 | 7.2
[42 empty] | 1980-10-14 | 5:00 | 7.2
[42 empty] | 1980-10-14 | 6:00 | 7.2
[42 empty] | 1980-10-14 | 7:00 | 7.2
[42 empty] | 1980-10-14 | 8:00 | 7.8
[42 empty] | 1980-10-14 | 9:00 | 8.3
[42 empty] | 1980-10-14 | 10:00 | 8.9
[42 empty] | 1980-10-14 | 11:00 | 10
[42 empty] | 1980-10-14 | 12:00 | 11.1
[42 empty] | 1980-10-14 | 13:00 | 12.2
[42 empty] | 1980-10-14 | 14:00 | 12.8
[42 empty] | 1980-10-14 | 15:00 | 13.3
[42 empty] | 1980-10-14 | 16:00 | 13.9
[42 empty] | 1980-10-14 | 17:00 | 13.2
[42 empty] | 1980-10-14 | 18:00 | 12.4
[42 empty] | 1980-10-14 | 19:00 | 11.7
[42 empty] | 1980-10-14 | 20:00 | 11.5
[42 empty] | 1980-10-14 | 21:00 | 11.3
[42 empty] | 1980-10-14 | 22:00 | 11.1
[42 empty] | 1980-10-14 | 23:00 | 11.1
[42 empty] | 1980-10-14 | 24:00 | 11.1
[42 empty] | 1980-10-15 | 1:00 | 11.1
[42 empty] | 1980-10-15 | 2:00 | 10.9
[42 empty] | 1980-10-15 | 3:00 | 10.8
[42 empty] | 1980-10-15 | 4:00 | 10.6
[42 empty] | 1980-10-15 | 5:00 | 10.4
[42 empty] | 1980-10-15 | 6:00 | 10.2
[42 empty] | 1980-10-15 | 7:00 | 10
[42 empty] | 1980-10-15 | 8:00 | 10.6
[42 empty] | 1980-10-15 | 9:00 | 11.1
[42 empty] | 1980-10-15 | 10:00 | 11.7
[42 empty] | 1980-10-15 | 11:00 | 12.1
[42 empty] | 1980-10-15 | 12:00 | 12.4
[42 empty] | 1980-10-15 | 13:00 | 12.8
[42 empty] | 1980-10-15 | 14:00 | 13.2
[42 empty] | 1980-10-15 | 15:00 | 13.5
[42 empty] | 1980-10-15 | 16:00 | 13.9
[42 empty] | 1980-10-15 | 17:00 | 13.3
[42 empty] | 1980-10-15 | 18:00 | 12.8
[42 empty] | 1980-10-15 | 19:00 | 12.2
[42 empty] | 1980-10-15 | 20:00 | 12
[42 empty] | 1980-10-15 | 21:00 | 11.9
[42 empty] | 1980-10-15 | 22:00 | 11.7
[42 empty] | 1980-10-15 | 23:00 | 12.1
[42 empty] | 1980-10-15 | 24:00 | 12.4
[42 empty] | 1980-10-16 | 1:00 | 12.8
[42 empty] | 1980-10-16 | 2:00 | 12.6
[42 empty] | 1980-10-16 | 3:00 | 12.4
[42 empty] | 1980-10-16 | 4:00 | 12.2
[42 empty] | 1980-10-16 | 5:00 | 11.8
[42 empty] | 1980-10-16 | 6:00 | 11.5
[42 empty] | 1980-10-16 | 7:00 | 11.1
[42 empty] | 1980-10-16 | 8:00 | 12.2
[42 empty] | 1980-10-16 | 9:00 | 13.3
[42 empty] | 1980-10-16 | 10:00 | 14.4
[42 empty] | 1980-10-16 | 11:00 | 16.6
[42 empty] | 1980-10-16 | 12:00 | 18.9
[42 empty] | 1980-10-16 | 13:00 | 21.1
[42 empty] | 1980-10-16 | 14:00 | 20.7
[42 empty] | 1980-10-16 | 15:00 | 20.4
[42 empty] | 1980-10-16 | 16:00 | 20
[42 empty] | 1980-10-16 | 17:00 | 19.6
[42 empty] | 1980-10-16 | 18:00 | 19.3
[42 empty] | 1980-10-16 | 19:00 | 18.9
[42 empty] | 1980-10-16 | 20:00 | 18.9
[42 empty] | 1980-10-16 | 21:00 | 18.9
[42 empty] | 1980-10-16 | 22:00 | 18.9
[42 empty] | 1980-10-16 | 23:00 | 18.7
[42 empty] | 1980-10-16 | 24:00 | 18.5
[42 empty] | 1980-10-17 | 1:00 | 18.3
[42 empty] | 1980-10-17 | 2:00 | 18.1
[42 empty] | 1980-10-17 | 3:00 | 18
[42 empty] | 1980-10-17 | 4:00 | 17.8
[42 empty] | 1980-10-17 | 5:00 | 17.1
[42 empty] | 1980-10-17 | 6:00 | 16.3
[42 empty] | 1980-10-17 | 7:00 | 15.6
[42 empty] | 1980-10-17 | 8:00 | 17.4
[42 empty] | 1980-10-17 | 9:00 | 19.3
[42 empty] | 1980-10-17 | 10:00 | 21.1
[42 empty] | 1980-10-17 | 11:00 | 22.2
[42 empty] | 1980-10-17 | 12:00 | 23.3
[42 empty] | 1980-10-17 | 13:00 | 24.4
[42 empty] | 1980-10-17 | 14:00 | 23.3
[42 empty] | 1980-10-17 | 15:00 | 22.2
[42 empty] | 1980-10-17 | 16:00 | 21.1
[42 empty] | 1980-10-17 | 17:00 | 20.5
[42 empty] | 1980-10-17 | 18:00 | 20
[42 empty] | 1980-10-17 | 19:00 | 19.4
[42 empty] | 1980-10-17 | 20:00 | 19
[42 empty] | 1980-10-17 | 21:00 | 18.7
[42 empty] | 1980-10-17 | 22:00 | 18.3
[42 empty] | 1980-10-17 | 23:00 | 18.3
[42 empty] | 1980-10-17 | 24:00 | 18.3
[42 empty] | 1980-10-18 | 1:00 | 18.3
[42 empty] | 1980-10-18 | 2:00 | 18.5
[42 empty] | 1980-10-18 | 3:00 | 18.7
[42 empty] | 1980-10-18 | 4:00 | 18.9
[42 empty] | 1980-10-18 | 5:00 | 19.1
[42 empty] | 1980-10-18 | 6:00 | 19.2
[42 empty] | 1980-10-18 | 7:00 | 19.4
[42 empty] | 1980-10-18 | 8:00 | 20
[42 empty] | 1980-10-18 | 9:00 | 20.5
[42 empty] | 1980-10-18 | 10:00 | 21.1
[42 empty] | 1980-10-18 | 11:00 | 21.7
[42 empty] | 1980-10-18 | 12:00 | 22.2
[42 empty] | 1980-10-18 | 13:00 | 22.8
[42 empty] | 1980-10-18 | 14:00 | 22.1
[42 empty] | 1980-10-18 | 15:00 | 21.3
[42 empty] | 1980-10-18 | 16:00 | 20.6
[42 empty] | 1980-10-18 | 17:00 | 19.5
[42 empty] | 1980-10-18 | 18:00 | 18.3
[42 empty] | 1980-10-18 | 19:00 | 17.2
[42 empty] | 1980-10-18 | 20:00 | 17
[42 empty] | 1980-10-18 | 21:00 | 16.9
[42 empty] | 1980-10-18 | 22:00 | 16.7
[42 empty] | 1980-10-18 | 23:00 | 16.7
[42 empty] | 1980-10-18 | 24:00 | 16.7
[42 empty] | 1980-10-19 | 1:00 | 16.7
[42 empty] | 1980-10-19 | 2:00 | 16.5
[42 empty] | 1980-10-19 | 3:00 | 16.3
[42 empty] | 1980-10-19 | 4:00 | 16.1
[42 empty] | 1980-10-19 | 5:00 | 15.9
[42 empty] | 1980-10-19 | 6:00 | 15.8
[42 empty] | 1980-10-19 | 7:00 | 15.6
[42 empty] | 1980-10-19 | 8:00 | 15.6
[42 empty] | 1980-10-19 | 9:00 | 15.6
[42 empty] | 1980-10-19 | 10:00 | 15.6
[42 empty] | 1980-10-19 | 11:00 | 16.7
[42 empty] | 1980-10-19 | 12:00 | 17.8
[42 empty] | 1980-10-19 | 13:00 | 18.9
[42 empty] | 1980-10-19 | 14:00 | 18.9
[42 empty] | 1980-10-19 | 15:00 | 18.9
[42 empty] | 1980-10-19 | 16:00 | 18.9
[42 empty] | 1980-10-19 | 17:00 | 18.2
[42 empty] | 1980-10-19 | 18:00 | 17.4
[42 empty] | 1980-10-19 | 19:00 | 16.7
[42 empty] | 1980-10-19 | 20:00 | 16.7
[42 empty] | 1980-10-19 | 21:00 | 16.7
[42 empty] | 1980-10-19 | 22:00 | 16.7
[42 empty] | 1980-10-19 | 23:00 | 16.1
[42 empty] | 1980-10-19 | 24:00 | 15.6
[42 empty] | 1980-10-20 | 1:00 | 15
[42 empty] | 1980-10-20 | 2:00 | 13.7
[42 empty] | 1980-10-20 | 3:00 | 12.4
[42 empty] | 1980-10-20 | 4:00 | 11.1
[42 empty] | 1980-10-20 | 5:00 | 10.7
[42 empty] | 1980-10-20 | 6:00 | 10.4
[42 empty] | 1980-10-20 | 7:00 | 10
[42 empty] | 1980-10-20 | 8:00 | 10.7
[42 empty] | 1980-10-20 | 9:00 | 11.5
[42 empty] | 1980-10-20 | 10:00 | 12.2
[42 empty] | 1980-10-20 | 11:00 | 12.9
[42 empty] | 1980-10-20 | 12:00 | 13.7
[42 empty] | 1980-10-20 | 13:00 | 14.4
[42 empty] | 1980-10-20 | 14:00 | 14.4
[42 empty] | 1980-10-20 | 15:00 | 14.4
[42 empty] | 1980-10-20 | 16:00 | 14.4
[42 empty] | 1980-10-20 | 17:00 | 13.9
[42 empty] | 1980-10-20 | 18:00 | 13.3
[42 empty] | 1980-10-20 | 19:00 | 12.8
[42 empty] | 1980-10-20 | 20:00 | 11.9
[42 empty] | 1980-10-20 | 21:00 | 10.9
[42 empty] | 1980-10-20 | 22:00 | 10
[42 empty] | 1980-10-20 | 23:00 | 9.8
[42 empty] | 1980-10-20 | 24:00 | 9.6
[42 empty] | 1980-10-21 | 1:00 | 9.4
[42 empty] | 1980-10-21 | 2:00 | 9.6
[42 empty] | 1980-10-21 | 3:00 | 9.8
[42 empty] | 1980-10-21 | 4:00 | 10
[42 empty] | 1980-10-21 | 5:00 | 10
[42 empty] | 1980-10-21 | 6:00 | 10
[42 empty] | 1980-10-21 | 7:00 | 10
[42 empty] | 1980-10-21 | 8:00 | 10.6
[42 empty] | 1980-10-21 | 9:00 | 11.1
[42 empty] | 1980-10-21 | 10:00 | 11.7
[42 empty] | 1980-10-21 | 11:00 | 13.2
[42 empty] | 1980-10-21 | 12:00 | 14.6
[42 empty] | 1980-10-21 | 13:00 | 16.1
[42 empty] | 1980-10-21 | 14:00 | 16.3
[42 empty] | 1980-10-21 | 15:00 | 16.5
[42 empty] | 1980-10-21 | 16:00 | 16.7
[42 empty] | 1980-10-21 | 17:00 | 15.9
[42 empty] | 1980-10-21 | 18:00 | 15.2
[42 empty] | 1980-10-21 | 19:00 | 14.4
[42 empty] | 1980-10-21 | 20:00 | 14
[42 empty] | 1980-10-21 | 21:00 | 13.7
[42 empty] | 1980-10-21 | 22:00 | 13.3
[42 empty] | 1980-10-21 | 23:00 | 12.9
[42 empty] | 1980-10-21 | 24:00 | 12.6
[42 empty] | 1980-10-22 | 1:00 | 12.2
[42 empty] | 1980-10-22 | 2:00 | 11.5
[42 empty] | 1980-10-22 | 3:00 | 10.7
[42 empty] | 1980-10-22 | 4:00 | 10
[42 empty] | 1980-10-22 | 5:00 | 9.6
[42 empty] | 1980-10-22 | 6:00 | 9.3
[42 empty] | 1980-10-22 | 7:00 | 8.9
[42 empty] | 1980-10-22 | 8:00 | 9.6
[42 empty] | 1980-10-22 | 9:00 | 10.4
[42 empty] | 1980-10-22 | 10:00 | 11.1
[42 empty] | 1980-10-22 | 11:00 | 11.7
[42 empty] | 1980-10-22 | 12:00 | 12.2
[42 empty] | 1980-10-22 | 13:00 | 12.8
[42 empty] | 1980-10-22 | 14:00 | 12.8
[42 empty] | 1980-10-22 | 15:00 | 12.8
[42 empty] | 1980-10-22 | 16:00 | 12.8
[42 empty] | 1980-10-22 | 17:00 | 12.1
[42 empty] | 1980-10-22 | 18:00 | 11.3
[42 empty] | 1980-10-22 | 19:00 | 10.6
[42 empty] | 1980-10-22 | 20:00 | 10.2
[42 empty] | 1980-10-22 | 21:00 | 9.8
[42 empty] | 1980-10-22 | 22:00 | 9.4
[42 empty] | 1980-10-22 | 23:00 | 8.9
[42 empty] | 1980-10-22 | 24:00 | 8.3
[42 empty] | 1980-10-23 | 1:00 | 7.8
[42 empty] | 1980-10-23 | 2:00 | 7.4
[42 empty] | 1980-10-23 | 3:00 | 7.1
[42 empty] | 1980-10-23 | 4:00 | 6.7
[42 empty] | 1980-10-23 | 5:00 | 6.5
[42 empty] | 1980-10-23 | 6:00 | 6.3
[42 empty] | 1980-10-23 | 7:00 | 6.1
[42 empty] | 1980-10-23 | 8:00 | 6.5
[42 empty] | 1980-10-23 | 9:00 | 6.8
[42 empty] | 1980-10-23 | 10:00 | 7.2
[42 empty] | 1980-10-23 | 11:00 | 8.1
[42 empty] | 1980-10-23 | 12:00 | 9.1
[42 empty] | 1980-10-23 | 13:00 | 10
[42 empty] | 1980-10-23 | 14:00 | 10.2
[42 empty] | 1980-10-23 | 15:00 | 10.4
[42 empty] | 1980-10-23 | 16:00 | 10.6
[42 empty] | 1980-10-23 | 17:00 | 10.2
[42 empty] | 1980-10-23 | 18:00 | 9.8
[42 empty] | 1980-10-23 | 19:00 | 9.4
[42 empty] | 1980-10-23 | 20:00 | 8.7
[42 empty] | 1980-10-23 | 21:00 | 7.9
[42 empty] | 1980-10-23 | 22:00 | 7.2
[42 empty] | 1980-10-23 | 23:00 | 7
[42 empty] | 1980-10-23 | 24:00 | 6.9
[42 empty] | 1980-10-24 | 1:00 | 6.7
[42 empty] | 1980-10-24 | 2:00 | 6.1
[42 empty] | 1980-10-24 | 3:00 | 5.6
[42 empty] | 1980-10-24 | 4:00 | 5
[42 empty] | 1980-10-24 | 5:00 | 4.8
[42 empty] | 1980-10-24 | 6:00 | 4.6
[42 empty] | 1980-10-24 | 7:00 | 4.4
[42 empty] | 1980-10-24 | 8:00 | 5.3
[42 empty] | 1980-10-24 | 9:00 | 6.3
[42 empty] | 1980-10-24 | 10:00 | 7.2
[42 empty] | 1980-10-24 | 11:00 | 8.1
[42 empty] | 1980-10-24 | 12:00 | 9.1
[42 empty] | 1980-10-24 | 13:00 | 10
[42 empty] | 1980-10-24 | 14:00 | 10.6
[42 empty] | 1980-10-24 | 15:00 | 11.1
[42 empty] | 1980-10-24 | 16:00 | 11.7
[42 empty] | 1980-10-24 | 17:00 | 11.3
[42 empty] | 1980-10-24 | 18:00 | 11
[42 empty] | 1980-10-24 | 19:00 | 10.6
[42 empty] | 1980-10-24 | 20:00 | 10.4
[42 empty] | 1980-10-24 | 21:00 | 10.2
[42 empty] | 1980-10-24 | 22:00 | 10
[42 empty] | 1980-10-24 | 23:00 | 10
[42 empty] | 1980-10-24 | 24:00 | 10
[42 empty] | 1980-10-25 | 1:00 | 10
[42 empty] | 1980-10-25 | 2:00 | 10
[42 empty] | 1980-10-25 | 3:00 | 10
[42 empty] | 1980-10-25 | 4:00 | 10
[42 empty] | 1980-10-25 | 5:00 | 10.2
[42 empty] | 1980-10-25 | 6:00 | 10.4
[42 empty] | 1980-10-25 | 7:00 | 10.6
[42 empty] | 1980-10-25 | 8:00 | 11.1
[42 empty] | 1980-10-25 | 9:00 | 11.7
[42 empty] | 1980-10-25 | 10:00 | 12.2
[42 empty] | 1980-10-25 | 11:00 | 13.7
[42 empty] | 1980-10-25 | 12:00 | 15.2
[42 empty] | 1980-10-25 | 13:00 | 16.7
[42 empty] | 1980-10-25 | 14:00 | 16.7
[42 empty] | 1980-10-25 | 15:00 | 16.7
[42 empty] | 1980-10-25 | 16:00 | 16.7
[42 empty] | 1980-10-25 | 17:00 | 16.1
[42 empty] | 1980-10-25 | 18:00 | 15.6
[42 empty] | 1980-10-25 | 19:00 | 15
[42 empty] | 1980-10-25 | 20:00 | 13
[42 empty] | 1980-10-25 | 21:00 | 10.9
[42 empty] | 1980-10-25 | 22:00 | 8.9
[42 empty] | 1980-10-25 | 23:00 | 8.7
[42 empty] | 1980-10-25 | 24:00 | 8.5
[42 empty] | 1980-10-26 | 1:00 | 8.3
[42 empty] | 1980-10-26 | 2:00 | 7.8
[42 empty] | 1980-10-26 | 3:00 | 7.2
[42 empty] | 1980-10-26 | 4:00 | 6.7
[42 empty] | 1980-10-26 | 5:00 | 6.7
[42 empty] | 1980-10-26 | 6:00 | 6.7
[42 empty] | 1980-10-26 | 7:00 | 6.7
[42 empty] | 1980-10-26 | 8:00 | 6.9
[42 empty] | 1980-10-26 | 9:00 | 7
[42 empty] | 1980-10-26 | 10:00 | 7.2
[42 empty] | 1980-10-26 | 11:00 | 7.8
[42 empty] | 1980-10-26 | 12:00 | 8.3
[42 empty] | 1980-10-26 | 13:00 | 8.9
[42 empty] | 1980-10-26 | 14:00 | 8.9
[42 empty] | 1980-10-26 | 15:00 | 8.9
[42 empty] | 1980-10-26 | 16:00 | 8.9
[42 empty] | 1980-10-26 | 17:00 | 8.7
[42 empty] | 1980-10-26 | 18:00 | 8.5
[42 empty] | 1980-10-26 | 19:00 | 8.3
[42 empty] | 1980-10-26 | 20:00 | 7.9
[42 empty] | 1980-10-26 | 21:00 | 7.6
[42 empty] | 1980-10-26 | 22:00 | 7.2
[42 empty] | 1980-10-26 | 23:00 | 7
[42 empty] | 1980-10-26 | 24:00 | 6.9
[42 empty] | 1980-10-27 | 1:00 | 6.7
[42 empty] | 1980-10-27 | 2:00 | 6.9
[42 empty] | 1980-10-27 | 3:00 | 7
[42 empty] | 1980-10-27 | 4:00 | 7.2
[42 empty] | 1980-10-27 | 5:00 | 6.8
[42 empty] | 1980-10-27 | 6:00 | 6.5
[42 empty] | 1980-10-27 | 7:00 | 6.1
[42 empty] | 1980-10-27 | 8:00 | 6.7
[42 empty] | 1980-10-27 | 9:00 | 7.2
[42 empty] | 1980-10-27 | 10:00 | 7.8
[42 empty] | 1980-10-27 | 11:00 | 8.7
[42 empty] | 1980-10-27 | 12:00 | 9.7
[42 empty] | 1980-10-27 | 13:00 | 10.6
[42 empty] | 1980-10-27 | 14:00 | 10.8
[42 empty] | 1980-10-27 | 15:00 | 10.9
[42 empty] | 1980-10-27 | 16:00 | 11.1
[42 empty] | 1980-10-27 | 17:00 | 10.5
[42 empty] | 1980-10-27 | 18:00 | 10
[42 empty] | 1980-10-27 | 19:00 | 9.4
[42 empty] | 1980-10-27 | 20:00 | 9.2
[42 empty] | 1980-10-27 | 21:00 | 9.1
[42 empty] | 1980-10-27 | 22:00 | 8.9
[42 empty] | 1980-10-27 | 23:00 | 8.9
[42 empty] | 1980-10-27 | 24:00 | 8.9
[42 empty] | 1980-10-28 | 1:00 | 8.9
[42 empty] | 1980-10-28 | 2:00 | 8.7
[42 empty] | 1980-10-28 | 3:00 | 8.5
[42 empty] | 1980-10-28 | 4:00 | 8.3
[42 empty] | 1980-10-28 | 5:00 | 8.3
[42 empty] | 1980-10-28 | 6:00 | 8.3
[42 empty] | 1980-10-28 | 7:00 | 8.3
[42 empty] | 1980-10-28 | 8:00 | 9.1
[42 empty] | 1980-10-28 | 9:00 | 9.8
[42 empty] | 1980-10-28 | 10:00 | 10.6
[42 empty] | 1980-10-28 | 11:00 | 11
[42 empty] | 1980-10-28 | 12:00 | 11.3
[42 empty] | 1980-10-28 | 13:00 | 11.7
[42 empty] | 1980-10-28 | 14:00 | 11.9
[42 empty] | 1980-10-28 | 15:00 | 12
[42 empty] | 1980-10-28 | 16:00 | 12.2
[42 empty] | 1980-10-28 | 17:00 | 11.8
[42 empty] | 1980-10-28 | 18:00 | 11.5
[42 empty] | 1980-10-28 | 19:00 | 11.1
[42 empty] | 1980-10-28 | 20:00 | 10.4
[42 empty] | 1980-10-28 | 21:00 | 9.6
[42 empty] | 1980-10-28 | 22:00 | 8.9
[42 empty] | 1980-10-28 | 23:00 | 8.2
[42 empty] | 1980-10-28 | 24:00 | 7.4
[42 empty] | 1980-10-29 | 1:00 | 6.7
[42 empty] | 1980-10-29 | 2:00 | 6.1
[42 empty] | 1980-10-29 | 3:00 | 5.6
[42 empty] | 1980-10-29 | 4:00 | 5
[42 empty] | 1980-10-29 | 5:00 | 4.8
[42 empty] | 1980-10-29 | 6:00 | 4.6
[42 empty] | 1980-10-29 | 7:00 | 4.4
[42 empty] | 1980-10-29 | 8:00 | 5.3
[42 empty] | 1980-10-29 | 9:00 | 6.3
[42 empty] | 1980-10-29 | 10:00 | 7.2
[42 empty] | 1980-10-29 | 11:00 | 7.9
[42 empty] | 1980-10-29 | 12:00 | 8.7
[42 empty] | 1980-10-29 | 13:00 | 9.4
[42 empty] | 1980-10-29 | 14:00 | 9.6
[42 empty] | 1980-10-29 | 15:00 | 9.8
[42 empty] | 1980-10-29 | 16:00 | 10
[42 empty] | 1980-10-29 | 17:00 | 9.3
[42 empty] | 1980-10-29 | 18:00 | 8.5
[42 empty] | 1980-10-29 | 19:00 | 7.8
[42 empty] | 1980-10-29 | 20:00 | 7.6
[42 empty] | 1980-10-29 | 21:00 | 7.4
[42 empty] | 1980-10-29 | 22:00 | 7.2
[42 empty] | 1980-10-29 | 23:00 | 6.8
[42 empty] | 1980-10-29 | 24:00 | 6.5
[42 empty] | 1980-10-30 | 1:00 | 6.1
[42 empty] | 1980-10-30 | 2:00 | 5.9
[42 empty] | 1980-10-30 | 3:00 | 5.8
[42 empty] | 1980-10-30 | 4:00 | 5.6
[42 empty] | 1980-10-30 | 5:00 | 5.6
[42 empty] | 1980-10-30 | 6:00 | 5.6
[42 empty] | 1980-10-30 | 7:00 | 5.6
[42 empty] | 1980-10-30 | 8:00 | 6.1
[42 empty] | 1980-10-30 | 9:00 | 6.7
[42 empty] | 1980-10-30 | 10:00 | 7.2
[42 empty] | 1980-10-30 | 11:00 | 7.8
[42 empty] | 1980-10-30 | 12:00 | 8.3
[42 empty] | 1980-10-30 | 13:00 | 8.9
[42 empty] | 1980-10-30 | 14:00 | 9.1
[42 empty] | 1980-10-30 | 15:00 | 9.2
[42 empty] | 1980-10-30 | 16:00 | 9.4
[42 empty] | 1980-10-30 | 17:00 | 8.9
[42 empty] | 1980-10-30 | 18:00 | 8.3
[42 empty] | 1980-10-30 | 19:00 | 7.8
[42 empty] | 1980-10-30 | 20:00 | 7.4
[42 empty] | 1980-10-30 | 21:00 | 7.1
[42 empty] | 1980-10-30 | 22:00 | 6.7
[42 empty] | 1980-10-30 | 23:00 | 6.3
[42 empty] | 1980-10-30 | 24:00 | 6
[42 empty] | 1980-10-31 | 1:00 | 5.6
[42 empty] | 1980-10-31 | 2:00 | 5.4
[42 empty] | 1980-10-31 | 3:00 | 5.2
[42 empty] | 1980-10-31 | 4:00 | 5
[42 empty] | 1980-10-31 | 5:00 | 5.2
[42 empty] | 1980-10-31 | 6:00 | 5.4
[42 empty] | 1980-10-31 | 7:00 | 5.6
[42 empty] | 1980-10-31 | 8:00 | 6.7
[42 empty] | 1980-10-31 | 9:00 | 7.8
[42 empty] | 1980-10-31 | 10:00 | 8.9
[42 empty] | 1980-10-31 | 11:00 | 10
[42 empty] | 1980-10-31 | 12:00 | 11.1
[42 empty] | 1980-10-31 | 13:00 | 12.2
[42 empty] | 1980-10-31 | 14:00 | 12.8
[42 empty] | 1980-10-31 | 15:00 | 13.3
[42 empty] | 1980-10-31 | 16:00 | 13.9
[42 empty] | 1980-10-31 | 17:00 | 13.5
[42 empty] | 1980-10-31 | 18:00 | 13.2
[42 empty] | 1980-10-31 | 19:00 | 12.8
[42 empty] | 1980-10-31 | 20:00 | 12.4
[42 empty] | 1980-10-31 | 21:00 | 12.1
[42 empty] | 1980-10-31 | 22:00 | 12
[42 empty] | 1980-10-31 | 23:00 | 12
[42 empty] | 1980-10-31 | 24:00 | 11.9
[42 empty] | 1978-11-01 | 1:00 | 11.9
[42 empty] | 1978-11-01 | 2:00 | 11.8
[42 empty] | 1978-11-01 | 3:00 | 11.8
[42 empty] | 1978-11-01 | 4:00 | 11.7
[42 empty] | 1978-11-01 | 5:00 | 11.1
[42 empty] | 1978-11-01 | 6:00 | 11.1
[42 empty] | 1978-11-01 | 7:00 | 10.6
[42 empty] | 1978-11-01 | 8:00 | 11.1
[42 empty] | 1978-11-01 | 9:00 | 12.2
[42 empty] | 1978-11-01 | 10:00 | 13.3
[42 empty] | 1978-11-01 | 11:00 | 14.4
[42 empty] | 1978-11-01 | 12:00 | 15.6
[42 empty] | 1978-11-01 | 13:00 | 16.7
[42 empty] | 1978-11-01 | 14:00 | 15.6
[42 empty] | 1978-11-01 | 15:00 | 16.1
[42 empty] | 1978-11-01 | 16:00 | 15
[42 empty] | 1978-11-01 | 17:00 | 12.8
[42 empty] | 1978-11-01 | 18:00 | 12.2
[42 empty] | 1978-11-01 | 19:00 | 12.2
[42 empty] | 1978-11-01 | 20:00 | 11.7
[42 empty] | 1978-11-01 | 21:00 | 11.1
[42 empty] | 1978-11-01 | 22:00 | 10
[42 empty] | 1978-11-01 | 23:00 | 10.6
[42 empty] | 1978-11-01 | 24:00 | 10
[42 empty] | 1978-11-02 | 1:00 | 10
[42 empty] | 1978-11-02 | 2:00 | 8.3
[42 empty] | 1978-11-02 | 3:00 | 7.8
[42 empty] | 1978-11-02 | 4:00 | 7.8
[42 empty] | 1978-11-02 | 5:00 | 7.2
[42 empty] | 1978-11-02 | 6:00 | 7.8
[42 empty] | 1978-11-02 | 7:00 | 7.2
[42 empty] | 1978-11-02 | 8:00 | 9.4
[42 empty] | 1978-11-02 | 9:00 | 12.2
[42 empty] | 1978-11-02 | 10:00 | 13.9
[42 empty] | 1978-11-02 | 11:00 | 15.6
[42 empty] | 1978-11-02 | 12:00 | 16.1
[42 empty] | 1978-11-02 | 13:00 | 17.2
[42 empty] | 1978-11-02 | 14:00 | 17.8
[42 empty] | 1978-11-02 | 15:00 | 17.8
[42 empty] | 1978-11-02 | 16:00 | 17.2
[42 empty] | 1978-11-02 | 17:00 | 16.1
[42 empty] | 1978-11-02 | 18:00 | 15.6
[42 empty] | 1978-11-02 | 19:00 | 15
[42 empty] | 1978-11-02 | 20:00 | 14.4
[42 empty] | 1978-11-02 | 21:00 | 13.9
[42 empty] | 1978-11-02 | 22:00 | 12.8
[42 empty] | 1978-11-02 | 23:00 | 13.3
[42 empty] | 1978-11-02 | 24:00 | 12.8
[42 empty] | 1978-11-03 | 1:00 | 11.7
[42 empty] | 1978-11-03 | 2:00 | 11.1
[42 empty] | 1978-11-03 | 3:00 | 10.6
[42 empty] | 1978-11-03 | 4:00 | 10.6
[42 empty] | 1978-11-03 | 5:00 | 10.6
[42 empty] | 1978-11-03 | 6:00 | 10
[42 empty] | 1978-11-03 | 7:00 | 9.4
[42 empty] | 1978-11-03 | 8:00 | 11.1
[42 empty] | 1978-11-03 | 9:00 | 13.3
[42 empty] | 1978-11-03 | 10:00 | 15
[42 empty] | 1978-11-03 | 11:00 | 16.1
[42 empty] | 1978-11-03 | 12:00 | 16.7
[42 empty] | 1978-11-03 | 13:00 | 16.7
[42 empty] | 1978-11-03 | 14:00 | 17.8
[42 empty] | 1978-11-03 | 15:00 | 17.2
[42 empty] | 1978-11-03 | 16:00 | 16.1
[42 empty] | 1978-11-03 | 17:00 | 13.9
[42 empty] | 1978-11-03 | 18:00 | 12.8
[42 empty] | 1978-11-03 | 19:00 | 13.3
[42 empty] | 1978-11-03 | 20:00 | 12.8
[42 empty] | 1978-11-03 | 21:00 | 11.7
[42 empty] | 1978-11-03 | 22:00 | 11.7
[42 empty] | 1978-11-03 | 23:00 | 10.6
[42 empty] | 1978-11-03 | 24:00 | 10.6
[42 empty] | 1978-11-04 | 1:00 | 10
[42 empty] | 1978-11-04 | 2:00 | 10
[42 empty] | 1978-11-04 | 3:00 | 10
[42 empty] | 1978-11-04 | 4:00 | 10
[42 empty] | 1978-11-04 | 5:00 | 10
[42 empty] | 1978-11-04 | 6:00 | 10
[42 empty] | 1978-11-04 | 7:00 | 10
[42 empty] | 1978-11-04 | 8:00 | 10.6
[42 empty] | 1978-11-04 | 9:00 | 10.6
[42 empty] | 1978-11-04 | 10:00 | 11.1
[42 empty] | 1978-11-04 | 11:00 | 11.1
[42 empty] | 1978-11-04 | 12:00 | 11.7
[42 empty] | 1978-11-04 | 13:00 | 11.7
[42 empty] | 1978-11-04 | 14:00 | 11.7
[42 empty] | 1978-11-04 | 15:00 | 11.7
[42 empty] | 1978-11-04 | 16:00 | 12.2
[42 empty] | 1978-11-04 | 17:00 | 11.7
[42 empty] | 1978-11-04 | 18:00 | 11.1
[42 empty] | 1978-11-04 | 19:00 | 11.7
[42 empty] | 1978-11-04 | 20:00 | 11.1
[42 empty] | 1978-11-04 | 21:00 | 11.1
[42 empty] | 1978-11-04 | 22:00 | 11.7
[42 empty] | 1978-11-04 | 23:00 | 11.7
[42 empty] | 1978-11-04 | 24:00 | 11.7
[42 empty] | 1978-11-05 | 1:00 | 11.7
[42 empty] | 1978-11-05 | 2:00 | 11.7
[42 empty] | 1978-11-05 | 3:00 | 12.2
[42 empty] | 1978-11-05 | 4:00 | 12.2
[42 empty] | 1978-11-05 | 5:00 | 12.2
[42 empty] | 1978-11-05 | 6:00 | 11.1
[42 empty] | 1978-11-05 | 7:00 | 10.6
[42 empty] | 1978-11-05 | 8:00 | 11.1
[42 empty] | 1978-11-05 | 9:00 | 12.2
[42 empty] | 1978-11-05 | 10:00 | 14.4
[42 empty] | 1978-11-05 | 11:00 | 15.6
[42 empty] | 1978-11-05 | 12:00 | 15.6
[42 empty] | 1978-11-05 | 13:00 | 16.1
[42 empty] | 1978-11-05 | 14:00 | 16.1
[42 empty] | 1978-11-05 | 15:00 | 16.7
[42 empty] | 1978-11-05 | 16:00 | 15.6
[42 empty] | 1978-11-05 | 17:00 | 13.9
[42 empty] | 1978-11-05 | 18:00 | 13.3
[42 empty] | 1978-11-05 | 19:00 | 13.3
[42 empty] | 1978-11-05 | 20:00 | 13.3
[42 empty] | 1978-11-05 | 21:00 | 12.8
[42 empty] | 1978-11-05 | 22:00 | 12.8
[42 empty] | 1978-11-05 | 23:00 | 12.2
[42 empty] | 1978-11-05 | 24:00 | 11.7
[42 empty] | 1978-11-06 | 1:00 | 10.6
[42 empty] | 1978-11-06 | 2:00 | 10.6
[42 empty] | 1978-11-06 | 3:00 | 10.6
[42 empty] | 1978-11-06 | 4:00 | 10
[42 empty] | 1978-11-06 | 5:00 | 10.6
[42 empty] | 1978-11-06 | 6:00 | 10
[42 empty] | 1978-11-06 | 7:00 | 9.4
[42 empty] | 1978-11-06 | 8:00 | 11.7
[42 empty] | 1978-11-06 | 9:00 | 13.3
[42 empty] | 1978-11-06 | 10:00 | 15.6
[42 empty] | 1978-11-06 | 11:00 | 17.2
[42 empty] | 1978-11-06 | 12:00 | 18.3
[42 empty] | 1978-11-06 | 13:00 | 18.9
[42 empty] | 1978-11-06 | 14:00 | 19.4
[42 empty] | 1978-11-06 | 15:00 | 17.8
[42 empty] | 1978-11-06 | 16:00 | 16.7
[42 empty] | 1978-11-06 | 17:00 | 15
[42 empty] | 1978-11-06 | 18:00 | 14.4
[42 empty] | 1978-11-06 | 19:00 | 14.4
[42 empty] | 1978-11-06 | 20:00 | 14.4
[42 empty] | 1978-11-06 | 21:00 | 14.4
[42 empty] | 1978-11-06 | 22:00 | 14.4
[42 empty] | 1978-11-06 | 23:00 | 13.9
[42 empty] | 1978-11-06 | 24:00 | 13.3
[42 empty] | 1978-11-07 | 1:00 | 12.8
[42 empty] | 1978-11-07 | 2:00 | 11.7
[42 empty] | 1978-11-07 | 3:00 | 10.6
[42 empty] | 1978-11-07 | 4:00 | 10.6
[42 empty] | 1978-11-07 | 5:00 | 11.1
[42 empty] | 1978-11-07 | 6:00 | 10.6
[42 empty] | 1978-11-07 | 7:00 | 10
[42 empty] | 1978-11-07 | 8:00 | 11.7
[42 empty] | 1978-11-07 | 9:00 | 12.8
[42 empty] | 1978-11-07 | 10:00 | 13.9
[42 empty] | 1978-11-07 | 11:00 | 15
[42 empty] | 1978-11-07 | 12:00 | 16.1
[42 empty] | 1978-11-07 | 13:00 | 15.6
[42 empty] | 1978-11-07 | 14:00 | 15.6
[42 empty] | 1978-11-07 | 15:00 | 15.6
[42 empty] | 1978-11-07 | 16:00 | 15
[42 empty] | 1978-11-07 | 17:00 | 14.4
[42 empty] | 1978-11-07 | 18:00 | 13.3
[42 empty] | 1978-11-07 | 19:00 | 12.8
[42 empty] | 1978-11-07 | 20:00 | 12.8
[42 empty] | 1978-11-07 | 21:00 | 11.7
[42 empty] | 1978-11-07 | 22:00 | 11.1
[42 empty] | 1978-11-07 | 23:00 | 10.6
[42 empty] | 1978-11-07 | 24:00 | 10.6
[42 empty] | 1978-11-08 | 1:00 | 10
[42 empty] | 1978-11-08 | 2:00 | 10
[42 empty] | 1978-11-08 | 3:00 | 9.4
[42 empty] | 1978-11-08 | 4:00 | 9.4
[42 empty] | 1978-11-08 | 5:00 | 8.9
[42 empty] | 1978-11-08 | 6:00 | 8.9
[42 empty] | 1978-11-08 | 7:00 | 8.9
[42 empty] | 1978-11-08 | 8:00 | 8.9
[42 empty] | 1978-11-08 | 9:00 | 8.9
[42 empty] | 1978-11-08 | 10:00 | 8.3
[42 empty] | 1978-11-08 | 11:00 | 8.9
[42 empty] | 1978-11-08 | 12:00 | 8.9
[42 empty] | 1978-11-08 | 13:00 | 9.4
[42 empty] | 1978-11-08 | 14:00 | 9.4
[42 empty] | 1978-11-08 | 15:00 | 9.4
[42 empty] | 1978-11-08 | 16:00 | 9.4
[42 empty] | 1978-11-08 | 17:00 | 9.4
[42 empty] | 1978-11-08 | 18:00 | 9.4
[42 empty] | 1978-11-08 | 19:00 | 8.9
[42 empty] | 1978-11-08 | 20:00 | 8.9
[42 empty] | 1978-11-08 | 21:00 | 8.9
[42 empty] | 1978-11-08 | 22:00 | 8.9
[42 empty] | 1978-11-08 | 23:00 | 8.9
[42 empty] | 1978-11-08 | 24:00 | 8.3
[42 empty] | 1978-11-09 | 1:00 | 8.3
[42 empty] | 1978-11-09 | 2:00 | 6.7
[42 empty] | 1978-11-09 | 3:00 | 7.2
[42 empty] | 1978-11-09 | 4:00 | 6.7
[42 empty] | 1978-11-09 | 5:00 | 6.1
[42 empty] | 1978-11-09 | 6:00 | 6.1
[42 empty] | 1978-11-09 | 7:00 | 7.2
[42 empty] | 1978-11-09 | 8:00 | 7.8
[42 empty] | 1978-11-09 | 9:00 | 10
[42 empty] | 1978-11-09 | 10:00 | 10.6
[42 empty] | 1978-11-09 | 11:00 | 12.2
[42 empty] | 1978-11-09 | 12:00 | 13.3
[42 empty] | 1978-11-09 | 13:00 | 14.4
[42 empty] | 1978-11-09 | 14:00 | 15.6
[42 empty] | 1978-11-09 | 15:00 | 15.6
[42 empty] | 1978-11-09 | 16:00 | 15
[42 empty] | 1978-11-09 | 17:00 | 14.4
[42 empty] | 1978-11-09 | 18:00 | 14.4
[42 empty] | 1978-11-09 | 19:00 | 13.9
[42 empty] | 1978-11-09 | 20:00 | 12.8
[42 empty] | 1978-11-09 | 21:00 | 12.8
[42 empty] | 1978-11-09 | 22:00 | 12.2
[42 empty] | 1978-11-09 | 23:00 | 11.7
[42 empty] | 1978-11-09 | 24:00 | 10.6
[42 empty] | 1978-11-10 | 1:00 | 10
[42 empty] | 1978-11-10 | 2:00 | 8.9
[42 empty] | 1978-11-10 | 3:00 | 8.3
[42 empty] | 1978-11-10 | 4:00 | 8.3
[42 empty] | 1978-11-10 | 5:00 | 7.8
[42 empty] | 1978-11-10 | 6:00 | 8.3
[42 empty] | 1978-11-10 | 7:00 | 8.3
[42 empty] | 1978-11-10 | 8:00 | 10
[42 empty] | 1978-11-10 | 9:00 | 12.8
[42 empty] | 1978-11-10 | 10:00 | 13.9
[42 empty] | 1978-11-10 | 11:00 | 15
[42 empty] | 1978-11-10 | 12:00 | 16.1
[42 empty] | 1978-11-10 | 13:00 | 16.1
[42 empty] | 1978-11-10 | 14:00 | 15.6
[42 empty] | 1978-11-10 | 15:00 | 15.6
[42 empty] | 1978-11-10 | 16:00 | 15
[42 empty] | 1978-11-10 | 17:00 | 13.9
[42 empty] | 1978-11-10 | 18:00 | 14.4
[42 empty] | 1978-11-10 | 19:00 | 13.3
[42 empty] | 1978-11-10 | 20:00 | 12.2
[42 empty] | 1978-11-10 | 21:00 | 11.7
[42 empty] | 1978-11-10 | 22:00 | 11.1
[42 empty] | 1978-11-10 | 23:00 | 11.1
[42 empty] | 1978-11-10 | 24:00 | 11.7
[42 empty] | 1978-11-11 | 1:00 | 11.1
[42 empty] | 1978-11-11 | 2:00 | 11.1
[42 empty] | 1978-11-11 | 3:00 | 11.1
[42 empty] | 1978-11-11 | 4:00 | 11.7
[42 empty] | 1978-11-11 | 5:00 | 11.7
[42 empty] | 1978-11-11 | 6:00 | 11.7
[42 empty] | 1978-11-11 | 7:00 | 12.2
[42 empty] | 1978-11-11 | 8:00 | 12.2
[42 empty] | 1978-11-11 | 9:00 | 12.2
[42 empty] | 1978-11-11 | 10:00 | 12.2
[42 empty] | 1978-11-11 | 11:00 | 12.2
[42 empty] | 1978-11-11 | 12:00 | 12.8
[42 empty] | 1978-11-11 | 13:00 | 13.3
[42 empty] | 1978-11-11 | 14:00 | 13.9
[42 empty] | 1978-11-11 | 15:00 | 15
[42 empty] | 1978-11-11 | 16:00 | 15
[42 empty] | 1978-11-11 | 17:00 | 13.9
[42 empty] | 1978-11-11 | 18:00 | 13.3
[42 empty] | 1978-11-11 | 19:00 | 11.7
[42 empty] | 1978-11-11 | 20:00 | 11.7
[42 empty] | 1978-11-11 | 21:00 | 12.2
[42 empty] | 1978-11-11 | 22:00 | 12.2
[42 empty] | 1978-11-11 | 23:00 | 11.7
[42 empty] | 1978-11-11 | 24:00 | 11.7
[42 empty] | 1978-11-12 | 1:00 | 10.6
[42 empty] | 1978-11-12 | 2:00 | 11.7
[42 empty] | 1978-11-12 | 3:00 | 11.1
[42 empty] | 1978-11-12 | 4:00 | 11.1
[42 empty] | 1978-11-12 | 5:00 | 11.1
[42 empty] | 1978-11-12 | 6:00 | 10.6
[42 empty] | 1978-11-12 | 7:00 | 10
[42 empty] | 1978-11-12 | 8:00 | 10.6
[42 empty] | 1978-11-12 | 9:00 | 10.6
[42 empty] | 1978-11-12 | 10:00 | 11.1
[42 empty] | 1978-11-12 | 11:00 | 10
[42 empty] | 1978-11-12 | 12:00 | 10
[42 empty] | 1978-11-12 | 13:00 | 8.9
[42 empty] | 1978-11-12 | 14:00 | 8.9
[42 empty] | 1978-11-12 | 15:00 | 9.4
[42 empty] | 1978-11-12 | 16:00 | 8.9
[42 empty] | 1978-11-12 | 17:00 | 8.9
[42 empty] | 1978-11-12 | 18:00 | 8.9
[42 empty] | 1978-11-12 | 19:00 | 8.9
[42 empty] | 1978-11-12 | 20:00 | 8.9
[42 empty] | 1978-11-12 | 21:00 | 8.3
[42 empty] | 1978-11-12 | 22:00 | 8.3
[42 empty] | 1978-11-12 | 23:00 | 7.2
[42 empty] | 1978-11-12 | 24:00 | 7.2
[42 empty] | 1978-11-13 | 1:00 | 7.2
[42 empty] | 1978-11-13 | 2:00 | 7.2
[42 empty] | 1978-11-13 | 3:00 | 7.2
[42 empty] | 1978-11-13 | 4:00 | 6.7
[42 empty] | 1978-11-13 | 5:00 | 6.7
[42 empty] | 1978-11-13 | 6:00 | 6.7
[42 empty] | 1978-11-13 | 7:00 | 6.1
[42 empty] | 1978-11-13 | 8:00 | 6.7
[42 empty] | 1978-11-13 | 9:00 | 6.7
[42 empty] | 1978-11-13 | 10:00 | 7.2
[42 empty] | 1978-11-13 | 11:00 | 7.2
[42 empty] | 1978-11-13 | 12:00 | 8.3
[42 empty] | 1978-11-13 | 13:00 | 8.9
[42 empty] | 1978-11-13 | 14:00 | 9.4
[42 empty] | 1978-11-13 | 15:00 | 9.4
[42 empty] | 1978-11-13 | 16:00 | 9.4
[42 empty] | 1978-11-13 | 17:00 | 9.4
[42 empty] | 1978-11-13 | 18:00 | 9.4
[42 empty] | 1978-11-13 | 19:00 | 10
[42 empty] | 1978-11-13 | 20:00 | 10.6
[42 empty] | 1978-11-13 | 21:00 | 10.6
[42 empty] | 1978-11-13 | 22:00 | 11.1
[42 empty] | 1978-11-13 | 23:00 | 11.1
[42 empty] | 1978-11-13 | 24:00 | 11.7
[42 empty] | 1978-11-14 | 1:00 | 11.7
[42 empty] | 1978-11-14 | 2:00 | 11.7
[42 empty] | 1978-11-14 | 3:00 | 12.2
[42 empty] | 1978-11-14 | 4:00 | 12.8
[42 empty] | 1978-11-14 | 5:00 | 12.8
[42 empty] | 1978-11-14 | 6:00 | 12.8
[42 empty] | 1978-11-14 | 7:00 | 13.3
[42 empty] | 1978-11-14 | 8:00 | 13.3
[42 empty] | 1978-11-14 | 9:00 | 13.3
[42 empty] | 1978-11-14 | 10:00 | 15
[42 empty] | 1978-11-14 | 11:00 | 16.1
[42 empty] | 1978-11-14 | 12:00 | 17.2
[42 empty] | 1978-11-14 | 13:00 | 17.8
[42 empty] | 1978-11-14 | 14:00 | 18.3
[42 empty] | 1978-11-14 | 15:00 | 18.9
[42 empty] | 1978-11-14 | 16:00 | 18.3
[42 empty] | 1978-11-14 | 17:00 | 17.8
[42 empty] | 1978-11-14 | 18:00 | 17.8
[42 empty] | 1978-11-14 | 19:00 | 17.8
[42 empty] | 1978-11-14 | 20:00 | 17.8
[42 empty] | 1978-11-14 | 21:00 | 17.2
[42 empty] | 1978-11-14 | 22:00 | 17.2
[42 empty] | 1978-11-14 | 23:00 | 16.7
[42 empty] | 1978-11-14 | 24:00 | 16.7
[42 empty] | 1978-11-15 | 1:00 | 16.7
[42 empty] | 1978-11-15 | 2:00 | 16.1
[42 empty] | 1978-11-15 | 3:00 | 15.6
[42 empty] | 1978-11-15 | 4:00 | 15.6
[42 empty] | 1978-11-15 | 5:00 | 13.3
[42 empty] | 1978-11-15 | 6:00 | 12.8
[42 empty] | 1978-11-15 | 7:00 | 11.7
[42 empty] | 1978-11-15 | 8:00 | 11.1
[42 empty] | 1978-11-15 | 9:00 | 10.6
[42 empty] | 1978-11-15 | 10:00 | 10.6
[42 empty] | 1978-11-15 | 11:00 | 11.7
[42 empty] | 1978-11-15 | 12:00 | 11.7
[42 empty] | 1978-11-15 | 13:00 | 12.2
[42 empty] | 1978-11-15 | 14:00 | 12.2
[42 empty] | 1978-11-15 | 15:00 | 12.2
[42 empty] | 1978-11-15 | 16:00 | 11.7
[42 empty] | 1978-11-15 | 17:00 | 11.1
[42 empty] | 1978-11-15 | 18:00 | 11.1
[42 empty] | 1978-11-15 | 19:00 | 11.1
[42 empty] | 1978-11-15 | 20:00 | 11.1
[42 empty] | 1978-11-15 | 21:00 | 9.4
[42 empty] | 1978-11-15 | 22:00 | 8.3
[42 empty] | 1978-11-15 | 23:00 | 8.3
[42 empty] | 1978-11-15 | 24:00 | 7.8
[42 empty] | 1978-11-16 | 1:00 | 6.7
[42 empty] | 1978-11-16 | 2:00 | 5.6
[42 empty] | 1978-11-16 | 3:00 | 5.6
[42 empty] | 1978-11-16 | 4:00 | 5
[42 empty] | 1978-11-16 | 5:00 | 5
[42 empty] | 1978-11-16 | 6:00 | 5
[42 empty] | 1978-11-16 | 7:00 | 5.6
[42 empty] | 1978-11-16 | 8:00 | 6.1
[42 empty] | 1978-11-16 | 9:00 | 6.7
[42 empty] | 1978-11-16 | 10:00 | 7.2
[42 empty] | 1978-11-16 | 11:00 | 8.3
[42 empty] | 1978-11-16 | 12:00 | 9.4
[42 empty] | 1978-11-16 | 13:00 | 10.6
[42 empty] | 1978-11-16 | 14:00 | 10
[42 empty] | 1978-11-16 | 15:00 | 10.6
[42 empty] | 1978-11-16 | 16:00 | 8.9
[42 empty] | 1978-11-16 | 17:00 | 8.3
[42 empty] | 1978-11-16 | 18:00 | 8.3
[42 empty] | 1978-11-16 | 19:00 | 7.8
[42 empty] | 1978-11-16 | 20:00 | 7.2
[42 empty] | 1978-11-16 | 21:00 | 7.2
[42 empty] | 1978-11-16 | 22:00 | 7.2
[42 empty] | 1978-11-16 | 23:00 | 7.2
[42 empty] | 1978-11-16 | 24:00 | 7.2
[42 empty] | 1978-11-17 | 1:00 | 7.8
[42 empty] | 1978-11-17 | 2:00 | 8.3
[42 empty] | 1978-11-17 | 3:00 | 8.3
[42 empty] | 1978-11-17 | 4:00 | 8.3
[42 empty] | 1978-11-17 | 5:00 | 7.8
[42 empty] | 1978-11-17 | 6:00 | 8.3
[42 empty] | 1978-11-17 | 7:00 | 8.3
[42 empty] | 1978-11-17 | 8:00 | 8.9
[42 empty] | 1978-11-17 | 9:00 | 9.4
[42 empty] | 1978-11-17 | 10:00 | 10.6
[42 empty] | 1978-11-17 | 11:00 | 11.1
[42 empty] | 1978-11-17 | 12:00 | 10
[42 empty] | 1978-11-17 | 13:00 | 10.6
[42 empty] | 1978-11-17 | 14:00 | 10
[42 empty] | 1978-11-17 | 15:00 | 10.6
[42 empty] | 1978-11-17 | 16:00 | 11.1
[42 empty] | 1978-11-17 | 17:00 | 12.2
[42 empty] | 1978-11-17 | 18:00 | 13.9
[42 empty] | 1978-11-17 | 19:00 | 15
[42 empty] | 1978-11-17 | 20:00 | 16.1
[42 empty] | 1978-11-17 | 21:00 | 16.7
[42 empty] | 1978-11-17 | 22:00 | 16.1
[42 empty] | 1978-11-17 | 23:00 | 15.6
[42 empty] | 1978-11-17 | 24:00 | 16.1
[42 empty] | 1978-11-18 | 1:00 | 16.1
[42 empty] | 1978-11-18 | 2:00 | 15.6
[42 empty] | 1978-11-18 | 3:00 | 15.6
[42 empty] | 1978-11-18 | 4:00 | 16.7
[42 empty] | 1978-11-18 | 5:00 | 16.7
[42 empty] | 1978-11-18 | 6:00 | 17.2
[42 empty] | 1978-11-18 | 7:00 | 17.8
[42 empty] | 1978-11-18 | 8:00 | 17.2
[42 empty] | 1978-11-18 | 9:00 | 17.2
[42 empty] | 1978-11-18 | 10:00 | 17.8
[42 empty] | 1978-11-18 | 11:00 | 18.3
[42 empty] | 1978-11-18 | 12:00 | 17.8
[42 empty] | 1978-11-18 | 13:00 | 17.8
[42 empty] | 1978-11-18 | 14:00 | 17.2
[42 empty] | 1978-11-18 | 15:00 | 16.1
[42 empty] | 1978-11-18 | 16:00 | 14.4
[42 empty] | 1978-11-18 | 17:00 | 12.8
[42 empty] | 1978-11-18 | 18:00 | 11.1
[42 empty] | 1978-11-18 | 19:00 | 10.6
[42 empty] | 1978-11-18 | 20:00 | 10
[42 empty] | 1978-11-18 | 21:00 | 9.4
[42 empty] | 1978-11-18 | 22:00 | 8.9
[42 empty] | 1978-11-18 | 23:00 | 8.9
[42 empty] | 1978-11-18 | 24:00 | 8.9
[42 empty] | 1978-11-19 | 1:00 | 8.3
[42 empty] | 1978-11-19 | 2:00 | 7.8
[42 empty] | 1978-11-19 | 3:00 | 7.8
[42 empty] | 1978-11-19 | 4:00 | 7.2
[42 empty] | 1978-11-19 | 5:00 | 7.8
[42 empty] | 1978-11-19 | 6:00 | 7.2
[42 empty] | 1978-11-19 | 7:00 | 7.8
[42 empty] | 1978-11-19 | 8:00 | 8.3
[42 empty] | 1978-11-19 | 9:00 | 9.4
[42 empty] | 1978-11-19 | 10:00 | 9.4
[42 empty] | 1978-11-19 | 11:00 | 9.4
[42 empty] | 1978-11-19 | 12:00 | 11.1
[42 empty] | 1978-11-19 | 13:00 | 11.1
[42 empty] | 1978-11-19 | 14:00 | 11.7
[42 empty] | 1978-11-19 | 15:00 | 11.7
[42 empty] | 1978-11-19 | 16:00 | 11.7
[42 empty] | 1978-11-19 | 17:00 | 10.6
[42 empty] | 1978-11-19 | 18:00 | 10.6
[42 empty] | 1978-11-19 | 19:00 | 10.6
[42 empty] | 1978-11-19 | 20:00 | 10.6
[42 empty] | 1978-11-19 | 21:00 | 10
[42 empty] | 1978-11-19 | 22:00 | 9.4
[42 empty] | 1978-11-19 | 23:00 | 8.3
[42 empty] | 1978-11-19 | 24:00 | 7.8
[42 empty] | 1978-11-20 | 1:00 | 7.2
[42 empty] | 1978-11-20 | 2:00 | 6.7
[42 empty] | 1978-11-20 | 3:00 | 5.6
[42 empty] | 1978-11-20 | 4:00 | 5.6
[42 empty] | 1978-11-20 | 5:00 | 5
[42 empty] | 1978-11-20 | 6:00 | 5
[42 empty] | 1978-11-20 | 7:00 | 3.9
[42 empty] | 1978-11-20 | 8:00 | 5
[42 empty] | 1978-11-20 | 9:00 | 6.1
[42 empty] | 1978-11-20 | 10:00 | 7.2
[42 empty] | 1978-11-20 | 11:00 | 7.8
[42 empty] | 1978-11-20 | 12:00 | 7.8
[42 empty] | 1978-11-20 | 13:00 | 8.9
[42 empty] | 1978-11-20 | 14:00 | 8.9
[42 empty] | 1978-11-20 | 15:00 | 8.9
[42 empty] | 1978-11-20 | 16:00 | 8.3
[42 empty] | 1978-11-20 | 17:00 | 8.3
[42 empty] | 1978-11-20 | 18:00 | 7.2
[42 empty] | 1978-11-20 | 19:00 | 6.7
[42 empty] | 1978-11-20 | 20:00 | 7.2
[42 empty] | 1978-11-20 | 21:00 | 5
[42 empty] | 1978-11-20 | 22:00 | 4.4
[42 empty] | 1978-11-20 | 23:00 | 3.9
[42 empty] | 1978-11-20 | 24:00 | 3.9
[42 empty] | 1978-11-21 | 1:00 | 3.3
[42 empty] | 1978-11-21 | 2:00 | 2.8
[42 empty] | 1978-11-21 | 3:00 | 2.8
[42 empty] | 1978-11-21 | 4:00 | 3.3
[42 empty] | 1978-11-21 | 5:00 | 3.3
[42 empty] | 1978-11-21 | 6:00 | 3.3
[42 empty] | 1978-11-21 | 7:00 | 3.3
[42 empty] | 1978-11-21 | 8:00 | 3.3
[42 empty] | 1978-11-21 | 9:00 | 3.3
[42 empty] | 1978-11-21 | 10:00 | 4.4
[42 empty] | 1978-11-21 | 11:00 | 5
[42 empty] | 1978-11-21 | 12:00 | 4.4
[42 empty] | 1978-11-21 | 13:00 | 3.9
[42 empty] | 1978-11-21 | 14:00 | 3.3
[42 empty] | 1978-11-21 | 15:00 | 3.9
[42 empty] | 1978-11-21 | 16:00 | 3.3
[42 empty] | 1978-11-21 | 17:00 | 2.8
[42 empty] | 1978-11-21 | 18:00 | 2.8
[42 empty] | 1978-11-21 | 19:00 | 2.8
[42 empty] | 1978-11-21 | 20:00 | 2.2
[42 empty] | 1978-11-21 | 21:00 | 1.7
[42 empty] | 1978-11-21 | 22:00 | 1.7
[42 empty] | 1978-11-21 | 23:00 | 1.7
[42 empty] | 1978-11-21 | 24:00 | 1.1
[42 empty] | 1978-11-22 | 1:00 | 1.7
[42 empty] | 1978-11-22 | 2:00 | 1.7
[42 empty] | 1978-11-22 | 3:00 | 1.7
[42 empty] | 1978-11-22 | 4:00 | 1.7
[42 empty] | 1978-11-22 | 5:00 | 1.1
[42 empty] | 1978-11-22 | 6:00 | 1.1
[42 empty] | 1978-11-22 | 7:00 | 1.1
[42 empty] | 1978-11-22 | 8:00 | 1.1
[42 empty] | 1978-11-22 | 9:00 | 1.7
[42 empty] | 1978-11-22 | 10:00 | 2.2
[42 empty] | 1978-11-22 | 11:00 | 2.8
[42 empty] | 1978-11-22 | 12:00 | 3.3
[42 empty] | 1978-11-22 | 13:00 | 3.3
[42 empty] | 1978-11-22 | 14:00 | 3.3
[42 empty] | 1978-11-22 | 15:00 | 3.3
[42 empty] | 1978-11-22 | 16:00 | 3.3
[42 empty] | 1978-11-22 | 17:00 | 2.8
[42 empty] | 1978-11-22 | 18:00 | 2.8
[42 empty] | 1978-11-22 | 19:00 | 2.8
[42 empty] | 1978-11-22 | 20:00 | 2.8
[42 empty] | 1978-11-22 | 21:00 | 2.8
[42 empty] | 1978-11-22 | 22:00 | 2.2
[42 empty] | 1978-11-22 | 23:00 | 1.1
[42 empty] | 1978-11-22 | 24:00 | 1.1
[42 empty] | 1978-11-23 | 1:00 | 1.1
[42 empty] | 1978-11-23 | 2:00 | 1.1
[42 empty] | 1978-11-23 | 3:00 | 1.1
[42 empty] | 1978-11-23 | 4:00 | 1.7
[42 empty] | 1978-11-23 | 5:00 | 2.2
[42 empty] | 1978-11-23 | 6:00 | 2.8
[42 empty] | 1978-11-23 | 7:00 | 2.8
[42 empty] | 1978-11-23 | 8:00 | 3.3
[42 empty] | 1978-11-23 | 9:00 | 3.9
[42 empty] | 1978-11-23 | 10:00 | 4.4
[42 empty] | 1978-11-23 | 11:00 | 4.4
[42 empty] | 1978-11-23 | 12:00 | 4.4
[42 empty] | 1978-11-23 | 13:00 | 5.6
[42 empty] | 1978-11-23 | 14:00 | 6.1
[42 empty] | 1978-11-23 | 15:00 | 6.7
[42 empty] | 1978-11-23 | 16:00 | 7.8
[42 empty] | 1978-11-23 | 17:00 | 7.8
[42 empty] | 1978-11-23 | 18:00 | 8.3
[42 empty] | 1978-11-23 | 19:00 | 7.8
[42 empty] | 1978-11-23 | 20:00 | 8.9
[42 empty] | 1978-11-23 | 21:00 | 8.9
[42 empty] | 1978-11-23 | 22:00 | 8.9
[42 empty] | 1978-11-23 | 23:00 | 10
[42 empty] | 1978-11-23 | 24:00 | 10.6
[42 empty] | 1978-11-24 | 1:00 | 11.1
[42 empty] | 1978-11-24 | 2:00 | 10
[42 empty] | 1978-11-24 | 3:00 | 10
[42 empty] | 1978-11-24 | 4:00 | 10
[42 empty] | 1978-11-24 | 5:00 | 9.4
[42 empty] | 1978-11-24 | 6:00 | 8.9
[42 empty] | 1978-11-24 | 7:00 | 8.9
[42 empty] | 1978-11-24 | 8:00 | 9.4
[42 empty] | 1978-11-24 | 9:00 | 9.4
[42 empty] | 1978-11-24 | 10:00 | 10
[42 empty] | 1978-11-24 | 11:00 | 10
[42 empty] | 1978-11-24 | 12:00 | 10
[42 empty] | 1978-11-24 | 13:00 | 10.6
[42 empty] | 1978-11-24 | 14:00 | 10.6
[42 empty] | 1978-11-24 | 15:00 | 10
[42 empty] | 1978-11-24 | 16:00 | 9.4
[42 empty] | 1978-11-24 | 17:00 | 8.9
[42 empty] | 1978-11-24 | 18:00 | 8.9
[42 empty] | 1978-11-24 | 19:00 | 8.3
[42 empty] | 1978-11-24 | 20:00 | 8.3
[42 empty] | 1978-11-24 | 21:00 | 7.8
[42 empty] | 1978-11-24 | 22:00 | 7.8
[42 empty] | 1978-11-24 | 23:00 | 7.8
[42 empty] | 1978-11-24 | 24:00 | 7.2
[42 empty] | 1978-11-25 | 1:00 | 7.2
[42 empty] | 1978-11-25 | 2:00 | 7.2
[42 empty] | 1978-11-25 | 3:00 | 6.7
[42 empty] | 1978-11-25 | 4:00 | 6.7
[42 empty] | 1978-11-25 | 5:00 | 6.1
[42 empty] | 1978-11-25 | 6:00 | 6.1
[42 empty] | 1978-11-25 | 7:00 | 5.6
[42 empty] | 1978-11-25 | 8:00 | 5
[42 empty] | 1978-11-25 | 9:00 | 5.6
[42 empty] | 1978-11-25 | 10:00 | 6.7
[42 empty] | 1978-11-25 | 11:00 | 6.1
[42 empty] | 1978-11-25 | 12:00 | 6.1
[42 empty] | 1978-11-25 | 13:00 | 5.6
[42 empty] | 1978-11-25 | 14:00 | 5.6
[42 empty] | 1978-11-25 | 15:00 | 4.4
[42 empty] | 1978-11-25 | 16:00 | 4.4
[42 empty] | 1978-11-25 | 17:00 | 3.9
[42 empty] | 1978-11-25 | 18:00 | 2.8
[42 empty] | 1978-11-25 | 19:00 | 2.2
[42 empty] | 1978-11-25 | 20:00 | 2.2
[42 empty] | 1978-11-25 | 21:00 | 1.7
[42 empty] | 1978-11-25 | 22:00 | 1.1
[42 empty] | 1978-11-25 | 23:00 | 0.6
[42 empty] | 1978-11-25 | 24:00 | 0
[42 empty] | 1978-11-26 | 1:00 | 0
[42 empty] | 1978-11-26 | 2:00 | -0.6
[42 empty] | 1978-11-26 | 3:00 | -0.6
[42 empty] | 1978-11-26 | 4:00 | -1.1
[42 empty] | 1978-11-26 | 5:00 | -1.7
[42 empty] | 1978-11-26 | 6:00 | -2.2
[42 empty] | 1978-11-26 | 7:00 | -2.8
[42 empty] | 1978-11-26 | 8:00 | -2.8
[42 empty] | 1978-11-26 | 9:00 | -2.2
[42 empty] | 1978-11-26 | 10:00 | -1.7
[42 empty] | 1978-11-26 | 11:00 | -0.6
[42 empty] | 1978-11-26 | 12:00 | 0.6
[42 empty] | 1978-11-26 | 13:00 | 0.6
[42 empty] | 1978-11-26 | 14:00 | 1.7
[42 empty] | 1978-11-26 | 15:00 | 1.1
[42 empty] | 1978-11-26 | 16:00 | 0.6
[42 empty] | 1978-11-26 | 17:00 | -0.6
[42 empty] | 1978-11-26 | 18:00 | -0.6
[42 empty] | 1978-11-26 | 19:00 | -1.1
[42 empty] | 1978-11-26 | 20:00 | -1.1
[42 empty] | 1978-11-26 | 21:00 | -1.7
[42 empty] | 1978-11-26 | 22:00 | -2.2
[42 empty] | 1978-11-26 | 23:00 | -2.2
[42 empty] | 1978-11-26 | 24:00 | -2.8
[42 empty] | 1978-11-27 | 1:00 | -2.8
[42 empty] | 1978-11-27 | 2:00 | -2.8
[42 empty] | 1978-11-27 | 3:00 | -3.3
[42 empty] | 1978-11-27 | 4:00 | -3.3
[42 empty] | 1978-11-27 | 5:00 | -3.3
[42 empty] | 1978-11-27 | 6:00 | -2.8
[42 empty] | 1978-11-27 | 7:00 | -3.3
[42 empty] | 1978-11-27 | 8:00 | -3.3
[42 empty] | 1978-11-27 | 9:00 | -2.8
[42 empty] | 1978-11-27 | 10:00 | -2.2
[42 empty] | 1978-11-27 | 11:00 | -1.7
[42 empty] | 1978-11-27 | 12:00 | -1.1
[42 empty] | 1978-11-27 | 13:00 | -0.6
[42 empty] | 1978-11-27 | 14:00 | -0.6
[42 empty] | 1978-11-27 | 15:00 | 0.6
[42 empty] | 1978-11-27 | 16:00 | 1.1
[42 empty] | 1978-11-27 | 17:00 | 1.7
[42 empty] | 1978-11-27 | 18:00 | 2.8
[42 empty] | 1978-11-27 | 19:00 | 3.3
[42 empty] | 1978-11-27 | 20:00 | 2.2
[42 empty] | 1978-11-27 | 21:00 | 2.8
[42 empty] | 1978-11-27 | 22:00 | 2.8
[42 empty] | 1978-11-27 | 23:00 | 2.2
[42 empty] | 1978-11-27 | 24:00 | 1.7
[42 empty] | 1978-11-28 | 1:00 | 1.7
[42 empty] | 1978-11-28 | 2:00 | 1.1
[42 empty] | 1978-11-28 | 3:00 | 1.7
[42 empty] | 1978-11-28 | 4:00 | 1.7
[42 empty] | 1978-11-28 | 5:00 | 1.7
[42 empty] | 1978-11-28 | 6:00 | 2.2
[42 empty] | 1978-11-28 | 7:00 | 2.8
[42 empty] | 1978-11-28 | 8:00 | 2.8
[42 empty] | 1978-11-28 | 9:00 | 2.8
[42 empty] | 1978-11-28 | 10:00 | 3.3
[42 empty] | 1978-11-28 | 11:00 | 3.3
[42 empty] | 1978-11-28 | 12:00 | 3.9
[42 empty] | 1978-11-28 | 13:00 | 3.9
[42 empty] | 1978-11-28 | 14:00 | 4.4
[42 empty] | 1978-11-28 | 15:00 | 5
[42 empty] | 1978-11-28 | 16:00 | 5.6
[42 empty] | 1978-11-28 | 17:00 | 5.6
[42 empty] | 1978-11-28 | 18:00 | 5
[42 empty] | 1978-11-28 | 19:00 | 5
[42 empty] | 1978-11-28 | 20:00 | 4.4
[42 empty] | 1978-11-28 | 21:00 | 4.4
[42 empty] | 1978-11-28 | 22:00 | 3.9
[42 empty] | 1978-11-28 | 23:00 | 3.9
[42 empty] | 1978-11-28 | 24:00 | 3.3
[42 empty] | 1978-11-29 | 1:00 | 2.8
[42 empty] | 1978-11-29 | 2:00 | 2.8
[42 empty] | 1978-11-29 | 3:00 | 2.2
[42 empty] | 1978-11-29 | 4:00 | 2.2
[42 empty] | 1978-11-29 | 5:00 | 1.7
[42 empty] | 1978-11-29 | 6:00 | 1.1
[42 empty] | 1978-11-29 | 7:00 | 1.1
[42 empty] | 1978-11-29 | 8:00 | 2.2
[42 empty] | 1978-11-29 | 9:00 | 2.8
[42 empty] | 1978-11-29 | 10:00 | 3.9
[42 empty] | 1978-11-29 | 11:00 | 5.6
[42 empty] | 1978-11-29 | 12:00 | 6.1
[42 empty] | 1978-11-29 | 13:00 | 6.7
[42 empty] | 1978-11-29 | 14:00 | 6.7
[42 empty] | 1978-11-29 | 15:00 | 6.7
[42 empty] | 1978-11-29 | 16:00 | 6.1
[42 empty] | 1978-11-29 | 17:00 | 5.6
[42 empty] | 1978-11-29 | 18:00 | 6.1
[42 empty] | 1978-11-29 | 19:00 | 6.7
[42 empty] | 1978-11-29 | 20:00 | 6.1
[42 empty] | 1978-11-29 | 21:00 | 5.6
[42 empty] | 1978-11-29 | 22:00 | 5.6
[42 empty] | 1978-11-29 | 23:00 | 4.4
[42 empty] | 1978-11-29 | 24:00 | 4.4
[42 empty] | 1978-11-30 | 1:00 | 4.4
[42 empty] | 1978-11-30 | 2:00 | 4.4
[42 empty] | 1978-11-30 | 3:00 | 4.4
[42 empty] | 1978-11-30 | 4:00 | 3.9
[42 empty] | 1978-11-30 | 5:00 | 3.9
[42 empty] | 1978-11-30 | 6:00 | 3.9
[42 empty] | 1978-11-30 | 7:00 | 4.4
[42 empty] | 1978-11-30 | 8:00 | 4.4
[42 empty] | 1978-11-30 | 9:00 | 5
[42 empty] | 1978-11-30 | 10:00 | 6.1
[42 empty] | 1978-11-30 | 11:00 | 6.7
[42 empty] | 1978-11-30 | 12:00 | 7.2
[42 empty] | 1978-11-30 | 13:00 | 7.8
[42 empty] | 1978-11-30 | 14:00 | 8.3
[42 empty] | 1978-11-30 | 15:00 | 8.3
[42 empty] | 1978-11-30 | 16:00 | 7.8
[42 empty] | 1978-11-30 | 17:00 | 7.2
[42 empty] | 1978-11-30 | 18:00 | 7.2
[42 empty] | 1978-11-30 | 19:00 | 7.8
[42 empty] | 1978-11-30 | 20:00 | 7.8
[42 empty] | 1978-11-30 | 21:00 | 7.8
[42 empty] | 1978-11-30 | 22:00 | 7.6
[42 empty] | 1978-11-30 | 23:00 | 7.5
[42 empty] | 1978-11-30 | 24:00 | 7.3
[42 empty] | 1977-12-01 | 1:00 | 7.2
[42 empty] | 1977-12-01 | 2:00 | 7
[42 empty] | 1977-12-01 | 3:00 | 6.9
[42 empty] | 1977-12-01 | 4:00 | 6.7
[42 empty] | 1977-12-01 | 5:00 | 6.7
[42 empty] | 1977-12-01 | 6:00 | 7.2
[42 empty] | 1977-12-01 | 7:00 | 7.2
[42 empty] | 1977-12-01 | 8:00 | 7.2
[42 empty] | 1977-12-01 | 9:00 | 7.2
[42 empty] | 1977-12-01 | 10:00 | 7.2
[42 empty] | 1977-12-01 | 11:00 | 7.2
[42 empty] | 1977-12-01 | 12:00 | 7.2
[42 empty] | 1977-12-01 | 13:00 | 7.2
[42 empty] | 1977-12-01 | 14:00 | 7.8
[42 empty] | 1977-12-01 | 15:00 | 7.8
[42 empty] | 1977-12-01 | 16:00 | 7.8
[42 empty] | 1977-12-01 | 17:00 | 7.8
[42 empty] | 1977-12-01 | 18:00 | 7.8
[42 empty] | 1977-12-01 | 19:00 | 8.3
[42 empty] | 1977-12-01 | 20:00 | 8.3
[42 empty] | 1977-12-01 | 21:00 | 8.3
[42 empty] | 1977-12-01 | 22:00 | 8.3
[42 empty] | 1977-12-01 | 23:00 | 8.3
[42 empty] | 1977-12-01 | 24:00 | 8.3
[42 empty] | 1977-12-02 | 1:00 | 7.8
[42 empty] | 1977-12-02 | 2:00 | 7.2
[42 empty] | 1977-12-02 | 3:00 | 7.2
[42 empty] | 1977-12-02 | 4:00 | 7.2
[42 empty] | 1977-12-02 | 5:00 | 6.7
[42 empty] | 1977-12-02 | 6:00 | 6.7
[42 empty] | 1977-12-02 | 7:00 | 6.7
[42 empty] | 1977-12-02 | 8:00 | 6.7
[42 empty] | 1977-12-02 | 9:00 | 7.2
[42 empty] | 1977-12-02 | 10:00 | 7.2
[42 empty] | 1977-12-02 | 11:00 | 7.8
[42 empty] | 1977-12-02 | 12:00 | 8.3
[42 empty] | 1977-12-02 | 13:00 | 8.3
[42 empty] | 1977-12-02 | 14:00 | 8.3
[42 empty] | 1977-12-02 | 15:00 | 8.3
[42 empty] | 1977-12-02 | 16:00 | 8.3
[42 empty] | 1977-12-02 | 17:00 | 8.3
[42 empty] | 1977-12-02 | 18:00 | 8.3
[42 empty] | 1977-12-02 | 19:00 | 8.3
[42 empty] | 1977-12-02 | 20:00 | 8.3
[42 empty] | 1977-12-02 | 21:00 | 8.3
[42 empty] | 1977-12-02 | 22:00 | 8.3
[42 empty] | 1977-12-02 | 23:00 | 7.2
[42 empty] | 1977-12-02 | 24:00 | 7.2
[42 empty] | 1977-12-03 | 1:00 | 7.2
[42 empty] | 1977-12-03 | 2:00 | 6.1
[42 empty] | 1977-12-03 | 3:00 | 5
[42 empty] | 1977-12-03 | 4:00 | 5.6
[42 empty] | 1977-12-03 | 5:00 | 5
[42 empty] | 1977-12-03 | 6:00 | 5
[42 empty] | 1977-12-03 | 7:00 | 5
[42 empty] | 1977-12-03 | 8:00 | 5
[42 empty] | 1977-12-03 | 9:00 | 5
[42 empty] | 1977-12-03 | 10:00 | 5.6
[42 empty] | 1977-12-03 | 11:00 | 6.7
[42 empty] | 1977-12-03 | 12:00 | 7.2
[42 empty] | 1977-12-03 | 13:00 | 7.8
[42 empty] | 1977-12-03 | 14:00 | 7.8
[42 empty] | 1977-12-03 | 15:00 | 8.3
[42 empty] | 1977-12-03 | 16:00 | 7.8
[42 empty] | 1977-12-03 | 17:00 | 7.2
[42 empty] | 1977-12-03 | 18:00 | 7.8
[42 empty] | 1977-12-03 | 19:00 | 7.8
[42 empty] | 1977-12-03 | 20:00 | 7.8
[42 empty] | 1977-12-03 | 21:00 | 7.2
[42 empty] | 1977-12-03 | 22:00 | 6.7
[42 empty] | 1977-12-03 | 23:00 | 6.1
[42 empty] | 1977-12-03 | 24:00 | 5
[42 empty] | 1977-12-04 | 1:00 | 5.6
[42 empty] | 1977-12-04 | 2:00 | 4.4
[42 empty] | 1977-12-04 | 3:00 | 3.9
[42 empty] | 1977-12-04 | 4:00 | 2.8
[42 empty] | 1977-12-04 | 5:00 | 2.8
[42 empty] | 1977-12-04 | 6:00 | 2.8
[42 empty] | 1977-12-04 | 7:00 | 1.7
[42 empty] | 1977-12-04 | 8:00 | 1.7
[42 empty] | 1977-12-04 | 9:00 | 1.7
[42 empty] | 1977-12-04 | 10:00 | 2.2
[42 empty] | 1977-12-04 | 11:00 | 2.8
[42 empty] | 1977-12-04 | 12:00 | 3.3
[42 empty] | 1977-12-04 | 13:00 | 3.9
[42 empty] | 1977-12-04 | 14:00 | 4.4
[42 empty] | 1977-12-04 | 15:00 | 4.4
[42 empty] | 1977-12-04 | 16:00 | 4.4
[42 empty] | 1977-12-04 | 17:00 | 4.4
[42 empty] | 1977-12-04 | 18:00 | 3.9
[42 empty] | 1977-12-04 | 19:00 | 3.3
[42 empty] | 1977-12-04 | 20:00 | 3.3
[42 empty] | 1977-12-04 | 21:00 | 3.3
[42 empty] | 1977-12-04 | 22:00 | 2.8
[42 empty] | 1977-12-04 | 23:00 | 2.8
[42 empty] | 1977-12-04 | 24:00 | 2.8
[42 empty] | 1977-12-05 | 1:00 | 2.8
[42 empty] | 1977-12-05 | 2:00 | 2.2
[42 empty] | 1977-12-05 | 3:00 | 2.2
[42 empty] | 1977-12-05 | 4:00 | 1.7
[42 empty] | 1977-12-05 | 5:00 | 1.7
[42 empty] | 1977-12-05 | 6:00 | 1.7
[42 empty] | 1977-12-05 | 7:00 | 1.7
[42 empty] | 1977-12-05 | 8:00 | 1.7
[42 empty] | 1977-12-05 | 9:00 | 1.7
[42 empty] | 1977-12-05 | 10:00 | 1.7
[42 empty] | 1977-12-05 | 11:00 | 1.1
[42 empty] | 1977-12-05 | 12:00 | 1.1
[42 empty] | 1977-12-05 | 13:00 | 1.7
[42 empty] | 1977-12-05 | 14:00 | 2.8
[42 empty] | 1977-12-05 | 15:00 | 2.8
[42 empty] | 1977-12-05 | 16:00 | 3.3
[42 empty] | 1977-12-05 | 17:00 | 3.9
[42 empty] | 1977-12-05 | 18:00 | 3.9
[42 empty] | 1977-12-05 | 19:00 | 3.9
[42 empty] | 1977-12-05 | 20:00 | 3.9
[42 empty] | 1977-12-05 | 21:00 | 3.9
[42 empty] | 1977-12-05 | 22:00 | 4.4
[42 empty] | 1977-12-05 | 23:00 | 4.4
[42 empty] | 1977-12-05 | 24:00 | 4.4
[42 empty] | 1977-12-06 | 1:00 | 4.4
[42 empty] | 1977-12-06 | 2:00 | 3.9
[42 empty] | 1977-12-06 | 3:00 | 2.8
[42 empty] | 1977-12-06 | 4:00 | 2.8
[42 empty] | 1977-12-06 | 5:00 | 2.8
[42 empty] | 1977-12-06 | 6:00 | 2.8
[42 empty] | 1977-12-06 | 7:00 | 2.8
[42 empty] | 1977-12-06 | 8:00 | 3.3
[42 empty] | 1977-12-06 | 9:00 | 2.8
[42 empty] | 1977-12-06 | 10:00 | 2.8
[42 empty] | 1977-12-06 | 11:00 | 2.8
[42 empty] | 1977-12-06 | 12:00 | 2.8
[42 empty] | 1977-12-06 | 13:00 | 2.2
[42 empty] | 1977-12-06 | 14:00 | 2.8
[42 empty] | 1977-12-06 | 15:00 | 1.7
[42 empty] | 1977-12-06 | 16:00 | 1.1
[42 empty] | 1977-12-06 | 17:00 | 0.6
[42 empty] | 1977-12-06 | 18:00 | 0.6
[42 empty] | 1977-12-06 | 19:00 | 0.6
[42 empty] | 1977-12-06 | 20:00 | 0
[42 empty] | 1977-12-06 | 21:00 | -0.6
[42 empty] | 1977-12-06 | 22:00 | -1.1
[42 empty] | 1977-12-06 | 23:00 | -1.1
[42 empty] | 1977-12-06 | 24:00 | -1.1
[42 empty] | 1977-12-07 | 1:00 | -2.2
[42 empty] | 1977-12-07 | 2:00 | -2.8
[42 empty] | 1977-12-07 | 3:00 | -2.8
[42 empty] | 1977-12-07 | 4:00 | -2.8
[42 empty] | 1977-12-07 | 5:00 | -3.3
[42 empty] | 1977-12-07 | 6:00 | -3.3
[42 empty] | 1977-12-07 | 7:00 | -2.8
[42 empty] | 1977-12-07 | 8:00 | -2.8
[42 empty] | 1977-12-07 | 9:00 | -2.8
[42 empty] | 1977-12-07 | 10:00 | -2.8
[42 empty] | 1977-12-07 | 11:00 | -2.2
[42 empty] | 1977-12-07 | 12:00 | -2.2
[42 empty] | 1977-12-07 | 13:00 | -2.8
[42 empty] | 1977-12-07 | 14:00 | -2.8
[42 empty] | 1977-12-07 | 15:00 | -2.2
[42 empty] | 1977-12-07 | 16:00 | -2.2
[42 empty] | 1977-12-07 | 17:00 | -2.2
[42 empty] | 1977-12-07 | 18:00 | -2.2
[42 empty] | 1977-12-07 | 19:00 | -2.2
[42 empty] | 1977-12-07 | 20:00 | -2.2
[42 empty] | 1977-12-07 | 21:00 | -2.8
[42 empty] | 1977-12-07 | 22:00 | -2.8
[42 empty] | 1977-12-07 | 23:00 | -2.8
[42 empty] | 1977-12-07 | 24:00 | -2.8
[42 empty] | 1977-12-08 | 1:00 | -3.3
[42 empty] | 1977-12-08 | 2:00 | -3.3
[42 empty] | 1977-12-08 | 3:00 | -3.3
[42 empty] | 1977-12-08 | 4:00 | -3.9
[42 empty] | 1977-12-08 | 5:00 | -3.9
[42 empty] | 1977-12-08 | 6:00 | -3.9
[42 empty] | 1977-12-08 | 7:00 | -3.9
[42 empty] | 1977-12-08 | 8:00 | -3.9
[42 empty] | 1977-12-08 | 9:00 | -3.9
[42 empty] | 1977-12-08 | 10:00 | -3.9
[42 empty] | 1977-12-08 | 11:00 | -1.7
[42 empty] | 1977-12-08 | 12:00 | -1.1
[42 empty] | 1977-12-08 | 13:00 | -0.6
[42 empty] | 1977-12-08 | 14:00 | 0
[42 empty] | 1977-12-08 | 15:00 | 1.1
[42 empty] | 1977-12-08 | 16:00 | 0
[42 empty] | 1977-12-08 | 17:00 | 0
[42 empty] | 1977-12-08 | 18:00 | 0
[42 empty] | 1977-12-08 | 19:00 | 0
[42 empty] | 1977-12-08 | 20:00 | -0.6
[42 empty] | 1977-12-08 | 21:00 | -0.6
[42 empty] | 1977-12-08 | 22:00 | -0.6
[42 empty] | 1977-12-08 | 23:00 | 0
[42 empty] | 1977-12-08 | 24:00 | 0
[42 empty] | 1977-12-09 | 1:00 | 1.1
[42 empty] | 1977-12-09 | 2:00 | 2.2
[42 empty] | 1977-12-09 | 3:00 | 3.9
[42 empty] | 1977-12-09 | 4:00 | 3.9
[42 empty] | 1977-12-09 | 5:00 | 5.6
[42 empty] | 1977-12-09 | 6:00 | 4.4
[42 empty] | 1977-12-09 | 7:00 | 3.3
[42 empty] | 1977-12-09 | 8:00 | 3.3
[42 empty] | 1977-12-09 | 9:00 | 3.9
[42 empty] | 1977-12-09 | 10:00 | 4.4
[42 empty] | 1977-12-09 | 11:00 | 5
[42 empty] | 1977-12-09 | 12:00 | 5
[42 empty] | 1977-12-09 | 13:00 | 5
[42 empty] | 1977-12-09 | 14:00 | 4.4
[42 empty] | 1977-12-09 | 15:00 | 4.4
[42 empty] | 1977-12-09 | 16:00 | 4.4
[42 empty] | 1977-12-09 | 17:00 | 4.4
[42 empty] | 1977-12-09 | 18:00 | 3.3
[42 empty] | 1977-12-09 | 19:00 | 2.2
[42 empty] | 1977-12-09 | 20:00 | -1.1
[42 empty] | 1977-12-09 | 21:00 | -2.2
[42 empty] | 1977-12-09 | 22:00 | -3.9
[42 empty] | 1977-12-09 | 23:00 | -5
[42 empty] | 1977-12-09 | 24:00 | -5
[42 empty] | 1977-12-10 | 1:00 | -6.1
[42 empty] | 1977-12-10 | 2:00 | -6.1
[42 empty] | 1977-12-10 | 3:00 | -6.7
[42 empty] | 1977-12-10 | 4:00 | -6.7
[42 empty] | 1977-12-10 | 5:00 | -6.7
[42 empty] | 1977-12-10 | 6:00 | -6.7
[42 empty] | 1977-12-10 | 7:00 | -6.1
[42 empty] | 1977-12-10 | 8:00 | -6.7
[42 empty] | 1977-12-10 | 9:00 | -6.1
[42 empty] | 1977-12-10 | 10:00 | -5
[42 empty] | 1977-12-10 | 11:00 | -4.4
[42 empty] | 1977-12-10 | 12:00 | -3.3
[42 empty] | 1977-12-10 | 13:00 | -3.3
[42 empty] | 1977-12-10 | 14:00 | -2.8
[42 empty] | 1977-12-10 | 15:00 | -2.8
[42 empty] | 1977-12-10 | 16:00 | -2.2
[42 empty] | 1977-12-10 | 17:00 | -3.3
[42 empty] | 1977-12-10 | 18:00 | -4.4
[42 empty] | 1977-12-10 | 19:00 | -5
[42 empty] | 1977-12-10 | 20:00 | -6.1
[42 empty] | 1977-12-10 | 21:00 | -6.1
[42 empty] | 1977-12-10 | 22:00 | -6.7
[42 empty] | 1977-12-10 | 23:00 | -6.7
[42 empty] | 1977-12-10 | 24:00 | -6.7
[42 empty] | 1977-12-11 | 1:00 | -7.2
[42 empty] | 1977-12-11 | 2:00 | -7.2
[42 empty] | 1977-12-11 | 3:00 | -8.3
[42 empty] | 1977-12-11 | 4:00 | -8.3
[42 empty] | 1977-12-11 | 5:00 | -8.3
[42 empty] | 1977-12-11 | 6:00 | -8.3
[42 empty] | 1977-12-11 | 7:00 | -9.4
[42 empty] | 1977-12-11 | 8:00 | -9.4
[42 empty] | 1977-12-11 | 9:00 | -9.4
[42 empty] | 1977-12-11 | 10:00 | -7.2
[42 empty] | 1977-12-11 | 11:00 | -6.1
[42 empty] | 1977-12-11 | 12:00 | -5.6
[42 empty] | 1977-12-11 | 13:00 | -4.4
[42 empty] | 1977-12-11 | 14:00 | -4.4
[42 empty] | 1977-12-11 | 15:00 | -4.4
[42 empty] | 1977-12-11 | 16:00 | -5.6
[42 empty] | 1977-12-11 | 17:00 | -5.6
[42 empty] | 1977-12-11 | 18:00 | -6.1
[42 empty] | 1977-12-11 | 19:00 | -6.7
[42 empty] | 1977-12-11 | 20:00 | -6.7
[42 empty] | 1977-12-11 | 21:00 | -7.2
[42 empty] | 1977-12-11 | 22:00 | -7.2
[42 empty] | 1977-12-11 | 23:00 | -7.2
[42 empty] | 1977-12-11 | 24:00 | -7.2
[42 empty] | 1977-12-12 | 1:00 | -7.8
[42 empty] | 1977-12-12 | 2:00 | -7.8
[42 empty] | 1977-12-12 | 3:00 | -7.8
[42 empty] | 1977-12-12 | 4:00 | -8.3
[42 empty] | 1977-12-12 | 5:00 | -8.3
[42 empty] | 1977-12-12 | 6:00 | -7.8
[42 empty] | 1977-12-12 | 7:00 | -8.3
[42 empty] | 1977-12-12 | 8:00 | -8.3
[42 empty] | 1977-12-12 | 9:00 | -7.8
[42 empty] | 1977-12-12 | 10:00 | -5.6
[42 empty] | 1977-12-12 | 11:00 | -5
[42 empty] | 1977-12-12 | 12:00 | -5
[42 empty] | 1977-12-12 | 13:00 | -5
[42 empty] | 1977-12-12 | 14:00 | -5
[42 empty] | 1977-12-12 | 15:00 | -5
[42 empty] | 1977-12-12 | 16:00 | -2.8
[42 empty] | 1977-12-12 | 17:00 | -2.2
[42 empty] | 1977-12-12 | 18:00 | -2.8
[42 empty] | 1977-12-12 | 19:00 | -2.8
[42 empty] | 1977-12-12 | 20:00 | -2.2
[42 empty] | 1977-12-12 | 21:00 | -0.6
[42 empty] | 1977-12-12 | 22:00 | 0
[42 empty] | 1977-12-12 | 23:00 | 0
[42 empty] | 1977-12-12 | 24:00 | 0
[42 empty] | 1977-12-13 | 1:00 | 1.1
[42 empty] | 1977-12-13 | 2:00 | 1.1
[42 empty] | 1977-12-13 | 3:00 | 1.1
[42 empty] | 1977-12-13 | 4:00 | 1.1
[42 empty] | 1977-12-13 | 5:00 | 0.6
[42 empty] | 1977-12-13 | 6:00 | 1.7
[42 empty] | 1977-12-13 | 7:00 | 2.2
[42 empty] | 1977-12-13 | 8:00 | 2.2
[42 empty] | 1977-12-13 | 9:00 | 2.2
[42 empty] | 1977-12-13 | 10:00 | 1.7
[42 empty] | 1977-12-13 | 11:00 | 2.2
[42 empty] | 1977-12-13 | 12:00 | 3.3
[42 empty] | 1977-12-13 | 13:00 | 3.3
[42 empty] | 1977-12-13 | 14:00 | 2.2
[42 empty] | 1977-12-13 | 15:00 | 1.7
[42 empty] | 1977-12-13 | 16:00 | 1.7
[42 empty] | 1977-12-13 | 17:00 | 1.7
[42 empty] | 1977-12-13 | 18:00 | 1.7
[42 empty] | 1977-12-13 | 19:00 | 1.7
[42 empty] | 1977-12-13 | 20:00 | 1.7
[42 empty] | 1977-12-13 | 21:00 | 1.7
[42 empty] | 1977-12-13 | 22:00 | 1.7
[42 empty] | 1977-12-13 | 23:00 | 3.3
[42 empty] | 1977-12-13 | 24:00 | 2.2
[42 empty] | 1977-12-14 | 1:00 | 1.7
[42 empty] | 1977-12-14 | 2:00 | 1.7
[42 empty] | 1977-12-14 | 3:00 | 1.7
[42 empty] | 1977-12-14 | 4:00 | 1.7
[42 empty] | 1977-12-14 | 5:00 | 1.1
[42 empty] | 1977-12-14 | 6:00 | 1.7
[42 empty] | 1977-12-14 | 7:00 | 4.4
[42 empty] | 1977-12-14 | 8:00 | 2.2
[42 empty] | 1977-12-14 | 9:00 | 2.8
[42 empty] | 1977-12-14 | 10:00 | 2.8
[42 empty] | 1977-12-14 | 11:00 | 2.8
[42 empty] | 1977-12-14 | 12:00 | 2.8
[42 empty] | 1977-12-14 | 13:00 | 3.3
[42 empty] | 1977-12-14 | 14:00 | 3.9
[42 empty] | 1977-12-14 | 15:00 | 5
[42 empty] | 1977-12-14 | 16:00 | 10
[42 empty] | 1977-12-14 | 17:00 | 10
[42 empty] | 1977-12-14 | 18:00 | 10.6
[42 empty] | 1977-12-14 | 19:00 | 11.1
[42 empty] | 1977-12-14 | 20:00 | 11.1
[42 empty] | 1977-12-14 | 21:00 | 11.7
[42 empty] | 1977-12-14 | 22:00 | 13.3
[42 empty] | 1977-12-14 | 23:00 | 11.7
[42 empty] | 1977-12-14 | 24:00 | 11.7
[42 empty] | 1977-12-15 | 1:00 | 11.1
[42 empty] | 1977-12-15 | 2:00 | 12.8
[42 empty] | 1977-12-15 | 3:00 | 12.8
[42 empty] | 1977-12-15 | 4:00 | 11.1
[42 empty] | 1977-12-15 | 5:00 | 8.9
[42 empty] | 1977-12-15 | 6:00 | 8.9
[42 empty] | 1977-12-15 | 7:00 | 8.3
[42 empty] | 1977-12-15 | 8:00 | 7.8
[42 empty] | 1977-12-15 | 9:00 | 7.8
[42 empty] | 1977-12-15 | 10:00 | 7.8
[42 empty] | 1977-12-15 | 11:00 | 7.8
[42 empty] | 1977-12-15 | 12:00 | 7.8
[42 empty] | 1977-12-15 | 13:00 | 8.9
[42 empty] | 1977-12-15 | 14:00 | 7.8
[42 empty] | 1977-12-15 | 15:00 | 7.2
[42 empty] | 1977-12-15 | 16:00 | 6.7
[42 empty] | 1977-12-15 | 17:00 | 5.6
[42 empty] | 1977-12-15 | 18:00 | 6.7
[42 empty] | 1977-12-15 | 19:00 | 7.2
[42 empty] | 1977-12-15 | 20:00 | 6.1
[42 empty] | 1977-12-15 | 21:00 | 6.1
[42 empty] | 1977-12-15 | 22:00 | 5
[42 empty] | 1977-12-15 | 23:00 | 5
[42 empty] | 1977-12-15 | 24:00 | 5
[42 empty] | 1977-12-16 | 1:00 | 6.1
[42 empty] | 1977-12-16 | 2:00 | 5
[42 empty] | 1977-12-16 | 3:00 | 5.6
[42 empty] | 1977-12-16 | 4:00 | 4.4
[42 empty] | 1977-12-16 | 5:00 | 3.3
[42 empty] | 1977-12-16 | 6:00 | 3.9
[42 empty] | 1977-12-16 | 7:00 | 3.3
[42 empty] | 1977-12-16 | 8:00 | 2.8
[42 empty] | 1977-12-16 | 9:00 | 2.8
[42 empty] | 1977-12-16 | 10:00 | 3.9
[42 empty] | 1977-12-16 | 11:00 | 5
[42 empty] | 1977-12-16 | 12:00 | 5
[42 empty] | 1977-12-16 | 13:00 | 6.1
[42 empty] | 1977-12-16 | 14:00 | 6.1
[42 empty] | 1977-12-16 | 15:00 | 8.9
[42 empty] | 1977-12-16 | 16:00 | 8.9
[42 empty] | 1977-12-16 | 17:00 | 7.8
[42 empty] | 1977-12-16 | 18:00 | 7.2
[42 empty] | 1977-12-16 | 19:00 | 6.7
[42 empty] | 1977-12-16 | 20:00 | 6.1
[42 empty] | 1977-12-16 | 21:00 | 6.1
[42 empty] | 1977-12-16 | 22:00 | 5
[42 empty] | 1977-12-16 | 23:00 | 5
[42 empty] | 1977-12-16 | 24:00 | 4.4
[42 empty] | 1977-12-17 | 1:00 | 3.3
[42 empty] | 1977-12-17 | 2:00 | 2.8
[42 empty] | 1977-12-17 | 3:00 | 2.2
[42 empty] | 1977-12-17 | 4:00 | 2.2
[42 empty] | 1977-12-17 | 5:00 | 2.2
[42 empty] | 1977-12-17 | 6:00 | 2.2
[42 empty] | 1977-12-17 | 7:00 | 3.3
[42 empty] | 1977-12-17 | 8:00 | 2.8
[42 empty] | 1977-12-17 | 9:00 | 2.8
[42 empty] | 1977-12-17 | 10:00 | 3.9
[42 empty] | 1977-12-17 | 11:00 | 5.6
[42 empty] | 1977-12-17 | 12:00 | 6.1
[42 empty] | 1977-12-17 | 13:00 | 7.2
[42 empty] | 1977-12-17 | 14:00 | 6.7
[42 empty] | 1977-12-17 | 15:00 | 6.7
[42 empty] | 1977-12-17 | 16:00 | 6.7
[42 empty] | 1977-12-17 | 17:00 | 5.6
[42 empty] | 1977-12-17 | 18:00 | 5
[42 empty] | 1977-12-17 | 19:00 | 3.9
[42 empty] | 1977-12-17 | 20:00 | 3.3
[42 empty] | 1977-12-17 | 21:00 | 3.3
[42 empty] | 1977-12-17 | 22:00 | 3.9
[42 empty] | 1977-12-17 | 23:00 | 3.9
[42 empty] | 1977-12-17 | 24:00 | 3.9
[42 empty] | 1977-12-18 | 1:00 | 1.7
[42 empty] | 1977-12-18 | 2:00 | 1.7
[42 empty] | 1977-12-18 | 3:00 | 1.1
[42 empty] | 1977-12-18 | 4:00 | 1.1
[42 empty] | 1977-12-18 | 5:00 | 0.6
[42 empty] | 1977-12-18 | 6:00 | 1.1
[42 empty] | 1977-12-18 | 7:00 | 1.1
[42 empty] | 1977-12-18 | 8:00 | 2.2
[42 empty] | 1977-12-18 | 9:00 | 1.7
[42 empty] | 1977-12-18 | 10:00 | 1.7
[42 empty] | 1977-12-18 | 11:00 | 1.7
[42 empty] | 1977-12-18 | 12:00 | 1.7
[42 empty] | 1977-12-18 | 13:00 | 2.2
[42 empty] | 1977-12-18 | 14:00 | 2.2
[42 empty] | 1977-12-18 | 15:00 | 1.1
[42 empty] | 1977-12-18 | 16:00 | 0.6
[42 empty] | 1977-12-18 | 17:00 | 1.1
[42 empty] | 1977-12-18 | 18:00 | 1.1
[42 empty] | 1977-12-18 | 19:00 | 1.7
[42 empty] | 1977-12-18 | 20:00 | 2.2
[42 empty] | 1977-12-18 | 21:00 | 2.8
[42 empty] | 1977-12-18 | 22:00 | 2.2
[42 empty] | 1977-12-18 | 23:00 | 1.7
[42 empty] | 1977-12-18 | 24:00 | 2.2
[42 empty] | 1977-12-19 | 1:00 | 2.2
[42 empty] | 1977-12-19 | 2:00 | 2.8
[42 empty] | 1977-12-19 | 3:00 | 3.3
[42 empty] | 1977-12-19 | 4:00 | 3.3
[42 empty] | 1977-12-19 | 5:00 | 3.3
[42 empty] | 1977-12-19 | 6:00 | 3.3
[42 empty] | 1977-12-19 | 7:00 | 3.9
[42 empty] | 1977-12-19 | 8:00 | 3.9
[42 empty] | 1977-12-19 | 9:00 | 3.9
[42 empty] | 1977-12-19 | 10:00 | 4.4
[42 empty] | 1977-12-19 | 11:00 | 3.9
[42 empty] | 1977-12-19 | 12:00 | 4.4
[42 empty] | 1977-12-19 | 13:00 | 4.4
[42 empty] | 1977-12-19 | 14:00 | 4.4
[42 empty] | 1977-12-19 | 15:00 | 4.4
[42 empty] | 1977-12-19 | 16:00 | 3.9
[42 empty] | 1977-12-19 | 17:00 | 5
[42 empty] | 1977-12-19 | 18:00 | 5
[42 empty] | 1977-12-19 | 19:00 | 5.6
[42 empty] | 1977-12-19 | 20:00 | 4.4
[42 empty] | 1977-12-19 | 21:00 | 5
[42 empty] | 1977-12-19 | 22:00 | 5
[42 empty] | 1977-12-19 | 23:00 | 4.4
[42 empty] | 1977-12-19 | 24:00 | 5
[42 empty] | 1977-12-20 | 1:00 | 4.4
[42 empty] | 1977-12-20 | 2:00 | 3.9
[42 empty] | 1977-12-20 | 3:00 | 3.3
[42 empty] | 1977-12-20 | 4:00 | 3.3
[42 empty] | 1977-12-20 | 5:00 | 2.8
[42 empty] | 1977-12-20 | 6:00 | 2.2
[42 empty] | 1977-12-20 | 7:00 | 1.7
[42 empty] | 1977-12-20 | 8:00 | 1.7
[42 empty] | 1977-12-20 | 9:00 | 1.7
[42 empty] | 1977-12-20 | 10:00 | 1.7
[42 empty] | 1977-12-20 | 11:00 | 2.2
[42 empty] | 1977-12-20 | 12:00 | 2.2
[42 empty] | 1977-12-20 | 13:00 | 2.8
[42 empty] | 1977-12-20 | 14:00 | 3.9
[42 empty] | 1977-12-20 | 15:00 | 3.9
[42 empty] | 1977-12-20 | 16:00 | 3.9
[42 empty] | 1977-12-20 | 17:00 | 3.9
[42 empty] | 1977-12-20 | 18:00 | 5
[42 empty] | 1977-12-20 | 19:00 | 5
[42 empty] | 1977-12-20 | 20:00 | 4.4
[42 empty] | 1977-12-20 | 21:00 | 4.4
[42 empty] | 1977-12-20 | 22:00 | 4.4
[42 empty] | 1977-12-20 | 23:00 | 5
[42 empty] | 1977-12-20 | 24:00 | 5
[42 empty] | 1977-12-21 | 1:00 | 5
[42 empty] | 1977-12-21 | 2:00 | 5
[42 empty] | 1977-12-21 | 3:00 | 5.6
[42 empty] | 1977-12-21 | 4:00 | 5.6
[42 empty] | 1977-12-21 | 5:00 | 5.6
[42 empty] | 1977-12-21 | 6:00 | 5.6
[42 empty] | 1977-12-21 | 7:00 | 6.7
[42 empty] | 1977-12-21 | 8:00 | 8.9
[42 empty] | 1977-12-21 | 9:00 | 8.9
[42 empty] | 1977-12-21 | 10:00 | 9.4
[42 empty] | 1977-12-21 | 11:00 | 7.2
[42 empty] | 1977-12-21 | 12:00 | 7.8
[42 empty] | 1977-12-21 | 13:00 | 12.2
[42 empty] | 1977-12-21 | 14:00 | 12.2
[42 empty] | 1977-12-21 | 15:00 | 11.7
[42 empty] | 1977-12-21 | 16:00 | 11.1
[42 empty] | 1977-12-21 | 17:00 | 9.4
[42 empty] | 1977-12-21 | 18:00 | 7.8
[42 empty] | 1977-12-21 | 19:00 | 6.7
[42 empty] | 1977-12-21 | 20:00 | 6.1
[42 empty] | 1977-12-21 | 21:00 | 6.1
[42 empty] | 1977-12-21 | 22:00 | 4.4
[42 empty] | 1977-12-21 | 23:00 | 4.4
[42 empty] | 1977-12-21 | 24:00 | 4.4
[42 empty] | 1977-12-22 | 1:00 | 3.9
[42 empty] | 1977-12-22 | 2:00 | 3.3
[42 empty] | 1977-12-22 | 3:00 | 2.8
[42 empty] | 1977-12-22 | 4:00 | 2.2
[42 empty] | 1977-12-22 | 5:00 | 1.7
[42 empty] | 1977-12-22 | 6:00 | 1.1
[42 empty] | 1977-12-22 | 7:00 | 1.1
[42 empty] | 1977-12-22 | 8:00 | 0.6
[42 empty] | 1977-12-22 | 9:00 | 1.1
[42 empty] | 1977-12-22 | 10:00 | 1.7
[42 empty] | 1977-12-22 | 11:00 | 2.2
[42 empty] | 1977-12-22 | 12:00 | 2.8
[42 empty] | 1977-12-22 | 13:00 | 3.3
[42 empty] | 1977-12-22 | 14:00 | 3.3
[42 empty] | 1977-12-22 | 15:00 | 3.3
[42 empty] | 1977-12-22 | 16:00 | 2.8
[42 empty] | 1977-12-22 | 17:00 | 2.8
[42 empty] | 1977-12-22 | 18:00 | 1.7
[42 empty] | 1977-12-22 | 19:00 | 1.7
[42 empty] | 1977-12-22 | 20:00 | 1.1
[42 empty] | 1977-12-22 | 21:00 | 1.1
[42 empty] | 1977-12-22 | 22:00 | 1.1
[42 empty] | 1977-12-22 | 23:00 | 1.1
[42 empty] | 1977-12-22 | 24:00 | 1.1
[42 empty] | 1977-12-23 | 1:00 | 1.1
[42 empty] | 1977-12-23 | 2:00 | 0.6
[42 empty] | 1977-12-23 | 3:00 | 0.6
[42 empty] | 1977-12-23 | 4:00 | 0
[42 empty] | 1977-12-23 | 5:00 | 0
[42 empty] | 1977-12-23 | 6:00 | 0.6
[42 empty] | 1977-12-23 | 7:00 | 0.6
[42 empty] | 1977-12-23 | 8:00 | 1.1
[42 empty] | 1977-12-23 | 9:00 | 2.2
[42 empty] | 1977-12-23 | 10:00 | 3.3
[42 empty] | 1977-12-23 | 11:00 | 3.9
[42 empty] | 1977-12-23 | 12:00 | 5
[42 empty] | 1977-12-23 | 13:00 | 7.2
[42 empty] | 1977-12-23 | 14:00 | 7.8
[42 empty] | 1977-12-23 | 15:00 | 8.9
[42 empty] | 1977-12-23 | 16:00 | 8.9
[42 empty] | 1977-12-23 | 17:00 | 7.8
[42 empty] | 1977-12-23 | 18:00 | 6.7
[42 empty] | 1977-12-23 | 19:00 | 6.7
[42 empty] | 1977-12-23 | 20:00 | 6.1
[42 empty] | 1977-12-23 | 21:00 | 5.6
[42 empty] | 1977-12-23 | 22:00 | 5.6
[42 empty] | 1977-12-23 | 23:00 | 5
[42 empty] | 1977-12-23 | 24:00 | 5
[42 empty] | 1977-12-24 | 1:00 | 5
[42 empty] | 1977-12-24 | 2:00 | 5
[42 empty] | 1977-12-24 | 3:00 | 5
[42 empty] | 1977-12-24 | 4:00 | 5
[42 empty] | 1977-12-24 | 5:00 | 3.9
[42 empty] | 1977-12-24 | 6:00 | 3.9
[42 empty] | 1977-12-24 | 7:00 | 3.3
[42 empty] | 1977-12-24 | 8:00 | 2.2
[42 empty] | 1977-12-24 | 9:00 | 5
[42 empty] | 1977-12-24 | 10:00 | 7.2
[42 empty] | 1977-12-24 | 11:00 | 8.3
[42 empty] | 1977-12-24 | 12:00 | 10
[42 empty] | 1977-12-24 | 13:00 | 10
[42 empty] | 1977-12-24 | 14:00 | 11.1
[42 empty] | 1977-12-24 | 15:00 | 10.6
[42 empty] | 1977-12-24 | 16:00 | 9.4
[42 empty] | 1977-12-24 | 17:00 | 8.3
[42 empty] | 1977-12-24 | 18:00 | 6.7
[42 empty] | 1977-12-24 | 19:00 | 6.1
[42 empty] | 1977-12-24 | 20:00 | 6.1
[42 empty] | 1977-12-24 | 21:00 | 5
[42 empty] | 1977-12-24 | 22:00 | 5
[42 empty] | 1977-12-24 | 23:00 | 5.6
[42 empty] | 1977-12-24 | 24:00 | 6.1
[42 empty] | 1977-12-25 | 1:00 | 6.7
[42 empty] | 1977-12-25 | 2:00 | 6.7
[42 empty] | 1977-12-25 | 3:00 | 6.7
[42 empty] | 1977-12-25 | 4:00 | 6.7
[42 empty] | 1977-12-25 | 5:00 | 7.2
[42 empty] | 1977-12-25 | 6:00 | 7.2
[42 empty] | 1977-12-25 | 7:00 | 8.9
[42 empty] | 1977-12-25 | 8:00 | 10
[42 empty] | 1977-12-25 | 9:00 | 9.4
[42 empty] | 1977-12-25 | 10:00 | 8.3
[42 empty] | 1977-12-25 | 11:00 | 8.3
[42 empty] | 1977-12-25 | 12:00 | 9.4
[42 empty] | 1977-12-25 | 13:00 | 9.4
[42 empty] | 1977-12-25 | 14:00 | 8.9
[42 empty] | 1977-12-25 | 15:00 | 8.3
[42 empty] | 1977-12-25 | 16:00 | 7.2
[42 empty] | 1977-12-25 | 17:00 | 7.2
[42 empty] | 1977-12-25 | 18:00 | 6.1
[42 empty] | 1977-12-25 | 19:00 | 5.6
[42 empty] | 1977-12-25 | 20:00 | 3.9
[42 empty] | 1977-12-25 | 21:00 | 2.8
[42 empty] | 1977-12-25 | 22:00 | 2.8
[42 empty] | 1977-12-25 | 23:00 | 2.2
[42 empty] | 1977-12-25 | 24:00 | 1.7
[42 empty] | 1977-12-26 | 1:00 | 1.1
[42 empty] | 1977-12-26 | 2:00 | 0.6
[42 empty] | 1977-12-26 | 3:00 | -0.6
[42 empty] | 1977-12-26 | 4:00 | -2.2
[42 empty] | 1977-12-26 | 5:00 | -3.3
[42 empty] | 1977-12-26 | 6:00 | -4.4
[42 empty] | 1977-12-26 | 7:00 | -5
[42 empty] | 1977-12-26 | 8:00 | -5.6
[42 empty] | 1977-12-26 | 9:00 | -5
[42 empty] | 1977-12-26 | 10:00 | -4.4
[42 empty] | 1977-12-26 | 11:00 | -3.9
[42 empty] | 1977-12-26 | 12:00 | -3.9
[42 empty] | 1977-12-26 | 13:00 | -2.8
[42 empty] | 1977-12-26 | 14:00 | -2.8
[42 empty] | 1977-12-26 | 15:00 | -2.8
[42 empty] | 1977-12-26 | 16:00 | -2.8
[42 empty] | 1977-12-26 | 17:00 | -3.9
[42 empty] | 1977-12-26 | 18:00 | -4.4
[42 empty] | 1977-12-26 | 19:00 | -5
[42 empty] | 1977-12-26 | 20:00 | -5.6
[42 empty] | 1977-12-26 | 21:00 | -6.1
[42 empty] | 1977-12-26 | 22:00 | -6.7
[42 empty] | 1977-12-26 | 23:00 | -6.7
[42 empty] | 1977-12-26 | 24:00 | -7.2
[42 empty] | 1977-12-27 | 1:00 | -7.8
[42 empty] | 1977-12-27 | 2:00 | -8.3
[42 empty] | 1977-12-27 | 3:00 | -8.3
[42 empty] | 1977-12-27 | 4:00 | -8.3
[42 empty] | 1977-12-27 | 5:00 | -8.9
[42 empty] | 1977-12-27 | 6:00 | -9.4
[42 empty] | 1977-12-27 | 7:00 | -9.4
[42 empty] | 1977-12-27 | 8:00 | -9.4
[42 empty] | 1977-12-27 | 9:00 | -7.8
[42 empty] | 1977-12-27 | 10:00 | -6.7
[42 empty] | 1977-12-27 | 11:00 | -5
[42 empty] | 1977-12-27 | 12:00 | -4.4
[42 empty] | 1977-12-27 | 13:00 | -3.9
[42 empty] | 1977-12-27 | 14:00 | -3.9
[42 empty] | 1977-12-27 | 15:00 | -3.9
[42 empty] | 1977-12-27 | 16:00 | -3.9
[42 empty] | 1977-12-27 | 17:00 | -4.4
[42 empty] | 1977-12-27 | 18:00 | -4.4
[42 empty] | 1977-12-27 | 19:00 | -5
[42 empty] | 1977-12-27 | 20:00 | -5
[42 empty] | 1977-12-27 | 21:00 | -5
[42 empty] | 1977-12-27 | 22:00 | -5
[42 empty] | 1977-12-27 | 23:00 | -5
[42 empty] | 1977-12-27 | 24:00 | -5
[42 empty] | 1977-12-28 | 1:00 | -5
[42 empty] | 1977-12-28 | 2:00 | -5.6
[42 empty] | 1977-12-28 | 3:00 | -5.6
[42 empty] | 1977-12-28 | 4:00 | -6.1
[42 empty] | 1977-12-28 | 5:00 | -6.7
[42 empty] | 1977-12-28 | 6:00 | -7.2
[42 empty] | 1977-12-28 | 7:00 | -7.2
[42 empty] | 1977-12-28 | 8:00 | -7.2
[42 empty] | 1977-12-28 | 9:00 | -6.7
[42 empty] | 1977-12-28 | 10:00 | -5.6
[42 empty] | 1977-12-28 | 11:00 | -4.4
[42 empty] | 1977-12-28 | 12:00 | -3.9
[42 empty] | 1977-12-28 | 13:00 | -3.9
[42 empty] | 1977-12-28 | 14:00 | -2.2
[42 empty] | 1977-12-28 | 15:00 | -2.8
[42 empty] | 1977-12-28 | 16:00 | -3.3
[42 empty] | 1977-12-28 | 17:00 | -3.9
[42 empty] | 1977-12-28 | 18:00 | -3.9
[42 empty] | 1977-12-28 | 19:00 | -3.9
[42 empty] | 1977-12-28 | 20:00 | -3.9
[42 empty] | 1977-12-28 | 21:00 | -5
[42 empty] | 1977-12-28 | 22:00 | -5.6
[42 empty] | 1977-12-28 | 23:00 | -6.1
[42 empty] | 1977-12-28 | 24:00 | -7.2
[42 empty] | 1977-12-29 | 1:00 | -7.2
[42 empty] | 1977-12-29 | 2:00 | -7.2
[42 empty] | 1977-12-29 | 3:00 | -7.2
[42 empty] | 1977-12-29 | 4:00 | -7.2
[42 empty] | 1977-12-29 | 5:00 | -7.8
[42 empty] | 1977-12-29 | 6:00 | -7.8
[42 empty] | 1977-12-29 | 7:00 | -7.8
[42 empty] | 1977-12-29 | 8:00 | -7.8
[42 empty] | 1977-12-29 | 9:00 | -6.7
[42 empty] | 1977-12-29 | 10:00 | -5.6
[42 empty] | 1977-12-29 | 11:00 | -3.9
[42 empty] | 1977-12-29 | 12:00 | -3.3
[42 empty] | 1977-12-29 | 13:00 | -2.8
[42 empty] | 1977-12-29 | 14:00 | -1.7
[42 empty] | 1977-12-29 | 15:00 | -1.7
[42 empty] | 1977-12-29 | 16:00 | -1.7
[42 empty] | 1977-12-29 | 17:00 | -1.7
[42 empty] | 1977-12-29 | 18:00 | -1.7
[42 empty] | 1977-12-29 | 19:00 | -2.2
[42 empty] | 1977-12-29 | 20:00 | -2.2
[42 empty] | 1977-12-29 | 21:00 | -1.7
[42 empty] | 1977-12-29 | 22:00 | -0.6
[42 empty] | 1977-12-29 | 23:00 | 0
[42 empty] | 1977-12-29 | 24:00 | -1.1
[42 empty] | 1977-12-30 | 1:00 | -1.1
[42 empty] | 1977-12-30 | 2:00 | -1.1
[42 empty] | 1977-12-30 | 3:00 | -1.7
[42 empty] | 1977-12-30 | 4:00 | -1.1
[42 empty] | 1977-12-30 | 5:00 | -1.1
[42 empty] | 1977-12-30 | 6:00 | -1.7
[42 empty] | 1977-12-30 | 7:00 | -1.7
[42 empty] | 1977-12-30 | 8:00 | -1.1
[42 empty] | 1977-12-30 | 9:00 | 0
[42 empty] | 1977-12-30 | 10:00 | 1.1
[42 empty] | 1977-12-30 | 11:00 | 2.8
[42 empty] | 1977-12-30 | 12:00 | 3.3
[42 empty] | 1977-12-30 | 13:00 | 5.6
[42 empty] | 1977-12-30 | 14:00 | 6.1
[42 empty] | 1977-12-30 | 15:00 | 6.7
[42 empty] | 1977-12-30 | 16:00 | 8.3
[42 empty] | 1977-12-30 | 17:00 | 6.7
[42 empty] | 1977-12-30 | 18:00 | 6.1
[42 empty] | 1977-12-30 | 19:00 | 6.1
[42 empty] | 1977-12-30 | 20:00 | 6.1
[42 empty] | 1977-12-30 | 21:00 | 5
[42 empty] | 1977-12-30 | 22:00 | 5.6
[42 empty] | 1977-12-30 | 23:00 | 4.4
[42 empty] | 1977-12-30 | 24:00 | 3.3
[42 empty] | 1977-12-31 | 1:00 | 2.8
[42 empty] | 1977-12-31 | 2:00 | 2.8
[42 empty] | 1977-12-31 | 3:00 | 2.8
[42 empty] | 1977-12-31 | 4:00 | 2.8
[42 empty] | 1977-12-31 | 5:00 | 2.8
[42 empty] | 1977-12-31 | 6:00 | 2.8
[42 empty] | 1977-12-31 | 7:00 | 2.8
[42 empty] | 1977-12-31 | 8:00 | 3.9
[42 empty] | 1977-12-31 | 9:00 | 3.3
[42 empty] | 1977-12-31 | 10:00 | 3.9
[42 empty] | 1977-12-31 | 11:00 | 4.4
[42 empty] | 1977-12-31 | 12:00 | 5
[42 empty] | 1977-12-31 | 13:00 | 5.6
[42 empty] | 1977-12-31 | 14:00 | 6.1
[42 empty] | 1977-12-31 | 15:00 | 6.7
[42 empty] | 1977-12-31 | 16:00 | 5
[42 empty] | 1977-12-31 | 17:00 | 3.9
[42 empty] | 1977-12-31 | 18:00 | 2.8
[42 empty] | 1977-12-31 | 19:00 | 2.2
[42 empty] | 1977-12-31 | 20:00 | 1.7
[42 empty] | 1977-12-31 | 21:00 | 1.1
[42 empty] | 1977-12-31 | 22:00 | 1.1
[42 empty] | 1977-12-31 | 23:00 | 0
[42 empty] | 1977-12-31 | 24:00 | -0.6

## Storage Tank Water Heater
Storage Tank Water Heater |  |  |  |  | Click to go to Summary of Savings
Total # of Apartment Units Served | # of Units Installed | Existing Water Heater Fuel Type | Proposed Storage Tank Volume | Proposed Unit Input Capacity [BTU/hr] | Proposed Water Heater Standby Loss [BTU/hr/°F] | Proposed Water Heater Efficiency | Water Heater Setpoint Temperature [°F] | Tset | ΔTmain | ΔTamb | Existing Equipment Efficiency | Standby Loss baseline | UA baseline | UA ee | GPD | kWh Savings | kW Savings | Therm Savings
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[6 empty] | #DIV/0! |  |  |  |  | #DIV/0! |  |  |  |  | 0 | 0 | 0
[19 empty] | Tamb: | 70 | Water Heater Type
[19 empty] | TMain: | 60.7 | Gas
[19 empty] | Tdel: | 125 | Electric
[19 empty] | CF: | 0.8

## Boiler, Furnace, & Unit H
Boiler, Furnace, & Unit Heater Replacement | [5 empty] | Click to go to Summary of Savings
Gas Provider
Heating EFLH
Index | Qty | Floor # | Location | Existing Heating Equipment Size (MBH) | Replacement Heating Equipment Size (MBH) | Heating Equipment Type | Replacement Estimated Efficiency | Boiler Age | Custom Baseline Efficiency | Equipment Size Range | Baseline Efficiency | Therm Saving
0
1
2
3
4
0
[26 empty] | NYS TRM V10 | Commercial and Industrial Measures
[13 empty] | Garage | Boiler, Steam, Gas Fired, Natural Draft |  |  | Heating |  | ConEd
[13 empty] | Floor Range | Heating System Type |  |  | 0 | 4 | Equipment Type | Look up values | Size Range | Heating System Type and Size Range | NYCECC Min Efficiency | Factor | AMEEP Min Replacement Efficiency | pg 664 | BOILER, FURNACE AND UNIT HEATER
[13 empty] | Exterior | Boiler, Hot Water, Gas Fired | Lookup | Building age | Low-Rise | High-Rise | Warm Air Furnace, Gas Fired | 0 | < 225 kBTU/h | Warm Air Furnace, Gas Fired< 225 kBTU/h | 0.8 | Et | 0.8 |  | Issue Date – December 30, 2022
[13 empty] | Parking Lot | Boiler, Steam, Gas Fired, All Except Natural Draft | 0 | 1940 & Prior | 974 | 987 | Warm Air Furnace, Gas Fired | 225 | ≥ 225 kBTU/h | Warm Air Furnace, Gas Fired≥ 225 kBTU/h | 0.8 | Et | 0.8 |  | Effective Date – January 1, 2023
[13 empty] | Garage | Boiler, Steam, Gas Fired, Natural Draft | 1941 | 1941-1978 | 738 | 513 | Warm Air Furnace, Oil Fired |  | < 225 kBTU/h | Warm Air Furnace, Oil Fired< 225 kBTU/h | 0.83 | AFUE | 0.83
[13 empty] | Tunnel | Warm Air Furnace, Gas Fired | 1979 | 1979-2006 | 705 | 385 | Warm Air Furnace, Oil Fired |  | ≥ 225 kBTU/h | Warm Air Furnace, Oil Fired≥ 225 kBTU/h | 0.81 | Et | 0.81
[13 empty] | Roof | Warm Air Unit Heaters, Gas Fired | 2007 | 2007-Now | 491 | 214 | Warm Air Unit Heaters, Gas Fired | 0 | All Capacities | Warm Air Unit Heaters, Gas FiredAll Capacities | 0.8 | Ec | 0.8
[13 empty] | Basement | Warm Air Furnace, Oil Fired |  |  |  |  | Warm Air Unit Heaters, Oil Fired |  | All Capacities | Warm Air Unit Heaters, Oil FiredAll Capacities | 0.8 | Ec | 0.8
[13 empty] | Sub Basement | Warm Air Unit Heaters, Oil Fired |  |  |  |  | Boiler, Hot Water, Gas Fired | 0 | < 300 kBTU/h | Boiler, Hot Water, Gas Fired< 300 kBTU/h | 0.82 | AFUE | 0.85
[13 empty] | Penthouse | Boiler, Hot Water, Oil Fired | Utility |  |  |  | Boiler, Hot Water, Gas Fired | 300 | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Hot Water, Gas Fired≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.8 | Et | 0.85
[13 empty] | Mezzanine |  | ConEd |  |  |  | Boiler, Hot Water, Gas Fired | 2500.1 | > 2,500 kBTU/h | Boiler, Hot Water, Gas Fired> 2,500 kBTU/h | 0.82 | Et | 0.88
[13 empty] | Ground |  | National Grid |  |  |  | Boiler, Hot Water, Oil Fired |  | < 300 kBTU/h | Boiler, Hot Water, Oil Fired< 300 kBTU/h | 0.84 | AFUE | 0.84
[13 empty] | Stairs | [5 empty] | Boiler, Hot Water, Oil Fired |  | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Hot Water, Oil Fired≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.82 | Et | 0.82
[13 empty] | Hallway | [5 empty] | Boiler, Hot Water, Oil Fired |  | > 2,500 kBTU/h | Boiler, Hot Water, Oil Fired> 2,500 kBTU/h | 0.84 | Et | 0.84
[13 empty] | Other | [5 empty] | Boiler, Steam, Gas Fired, All Except Natural Draft |  | < 300 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft< 300 kBTU/h | 0.8 | AFUE | 0.82
[13 empty] | 1 | [5 empty] | Boiler, Steam, Gas Fired, All Except Natural Draft |  | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.79 | Et | 0.82
[13 empty] | 2 | [5 empty] | Boiler, Steam, Gas Fired, All Except Natural Draft |  | > 2,500 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft> 2,500 kBTU/h | 0.79 | Et | 0.82
[13 empty] | 3 | [5 empty] | Boiler, Steam, Gas Fired, Natural Draft |  | < 300 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft< 300 kBTU/h | 0.8 | AFUE | 0.82
[13 empty] | 4 | [5 empty] | Boiler, Steam, Gas Fired, Natural Draft |  | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.77 | Et | 0.82
[13 empty] | 5 | [5 empty] | Boiler, Steam, Gas Fired, Natural Draft |  | > 2,500 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft> 2,500 kBTU/h | 0.77 | Et | 0.82
6
[13 empty] | 7 | [5 empty] | National Grid
[13 empty] | 8 | [5 empty] | Equipment Type | Look up values | Size Range | Heating System Type and Size Range | NYCECC Min Efficiency | Factor | AMEEP Min Replacement Efficiency
[13 empty] | 9 | [5 empty] | Warm Air Furnace, Gas Fired | 0 | < 225 kBTU/h | Warm Air Furnace, Gas Fired< 225 kBTU/h | 0.8 | Et | 0.8
[13 empty] | 10 | [5 empty] | Warm Air Furnace, Gas Fired | 225 | ≥ 225 kBTU/h | Warm Air Furnace, Gas Fired≥ 225 kBTU/h | 0.8 | Et | 0.8
11
12
[13 empty] | 13 | [5 empty] | Warm Air Unit Heaters, Gas Fired | 0 | All Capacities | Warm Air Unit Heaters, Gas FiredAll Capacities | 0.8 | Ec | 0.8
14
[13 empty] | 15 | [5 empty] | Boiler, Hot Water, Gas Fired | 0 | < 300 kBTU/h | Boiler, Hot Water, Gas Fired< 300 kBTU/h | 0.84 |  | 0.85
[13 empty] | 16 | [5 empty] | Boiler, Hot Water, Gas Fired | 300 | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Hot Water, Gas Fired≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.84 |  | 0.85
[13 empty] | 17 | [5 empty] | Boiler, Hot Water, Gas Fired | 2500.1 | > 2,500 kBTU/h | Boiler, Hot Water, Gas Fired> 2,500 kBTU/h | 0.84 |  | 0.88
18
19
20
[13 empty] | 21 | [5 empty] | Boiler, Steam, Gas Fired, All Except Natural Draft |  | < 300 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft< 300 kBTU/h | 0.82 |  | 0.82
[13 empty] | 22 | [5 empty] | Boiler, Steam, Gas Fired, All Except Natural Draft |  | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.82 |  | 0.82
[13 empty] | 23 | [5 empty] | Boiler, Steam, Gas Fired, All Except Natural Draft |  | > 2,500 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft> 2,500 kBTU/h | 0.82 |  | 0.82
[13 empty] | 24 | [5 empty] | Boiler, Steam, Gas Fired, Natural Draft |  | < 300 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft< 300 kBTU/h | 0.82 |  | 0.82
[13 empty] | 25 | [5 empty] | Boiler, Steam, Gas Fired, Natural Draft |  | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.82 |  | 0.82
[13 empty] | 26 | [5 empty] | Boiler, Steam, Gas Fired, Natural Draft |  | > 2,500 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft> 2,500 kBTU/h | 0.82 |  | 0.82
27
28
[13 empty] | 29 | [5 empty] | Measure Category | System Type | EUL
[13 empty] | 30 | [5 empty] | Combi Boiler | Boiler and Furnace - Combination Boiler | 22
[13 empty] | 31 | [5 empty] | Combi Furnace | Boiler and Furnace - Combination Furnace | 20
[13 empty] | 32 | [5 empty] | Boiler and Furnace | Boiler, Hot water - Steel Water Tube | 24
[13 empty] | 33 | [5 empty] | Boiler and Furnace | Boiler, Hot water - Steel Fire Tube | 25
[13 empty] | 34 | [5 empty] | Boiler and Furnace | Boiler, Hot Water - Cast Iron | 35
[13 empty] | 35 | [5 empty] | Boiler and Furnace | Boiler, Steam - Steel Water Tube | 30
[13 empty] | 36 | [5 empty] | Boiler and Furnace | Boiler, Steam - Steel Fire Tube | 25
[13 empty] | 37 | [5 empty] | Boiler and Furnace | Boiler, Steam - Cast Iron | 30
[13 empty] | 38 | [5 empty] | Boiler and Furnace | Furnace, Gas Fired | 23
[13 empty] | 39 | [5 empty] | Boiler and Furnace | Unit Heater, Gas Fired | 13
[13 empty] | 40 | [5 empty] | Infrared Heater | Infrared Heater | 17
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150

## Induction Stovetop
Induction Stovetop |  |  |  |  | Click to go to Summary of Savings
Location | Quantity | What is the Existing Cooktop Technology? | Annual Energy Consumption by Proposed Induction Cooktop (kWh) | Annual Energy Consumption by Existing Electric Resistance Cooktop (kWh) | Annual Energy Consumption by Existing Fossil Fuel Cooktop (MMBtu) | FElec,baseline | FFuel,baseline | kWhee (kWh) | kWhbaseline (kWh) | MMBtubaseline (MMBtu) | kW Savings without Interactivity (kW) | kWh Savings without Interactivity (kWh) | Therms Savings without Interactivity (therms)
[8 empty] | 125 | 141.875 | 0.89565
[8 empty] | 125 | 141.875 | 0.89565
[8 empty] | 125 | 141.875 | 0.89565
[8 empty] | 125 | 141.875 | 0.89565
[8 empty] | 125 | 141.875 | 0.89565
[8 empty] | 625 | 709.375 | 4.4783 | 0 | 0 | 0
[14 empty] | Constants | Values
[14 empty] | Default hours (hrs) | 365
[14 empty] | Default kWhee (kWh) | 125
[14 empty] | Default kWhbaseline multiplier | 1.135
[14 empty] | Default MMBtubaseline multiplier (MMBtu/kWh) | 0.0071652
[14 empty] | CF | 0.8
[14 empty] | What is the existing Cooktop type? | FElec,baseline | FFuel,baseline
[14 empty] | Fossil Fuel Combustion | 0 | 1
[14 empty] | Electric Resistance | 1 | 0
[14 empty] | Electric Induction | Not Eligible | Not Eligible

## Wi-Fi Thermostats (hidden)
Wi-Fi Thermostats |  |  |  |  | Click to go to Summary of Savings
Building Floors
Year Built
Electric Heating
Fossil Fuel Heating
Units | Eff_FuelHeat | F_ElecHeat | F_FuelHeat | COP | (kWh/unit)_cooling | (MMBtu/unit) | CF | EFLH_cooling | kW Savings | kWh Savings | Therm Savings | MMBtu Savings
| 0.8 | 0 | 0 |  |  |  |  | 0
Inputs
[15 empty] | Low-Rise | High-Rise
[13 empty] | 0 | Prior to 1979 | 470 | 736 | Building Floors
[13 empty] | 1979 | From 1979 Through 2006 | 510 | 782 | Year Built
[13 empty] | 2007 | From 2007 Through the Present | 521 | 885
Electric Heating
Fossil Fuel Heating
[14 empty] | No Electric Heating | 0 | No
[14 empty] | Heat Pump | 2.4 | Yes
[14 empty] | Electric Resistance | 1 | Yes
[14 empty] | No Fossil Fuel Heating | 0 | No
[14 empty] | Fossil Fuel Heating | 1 | Yes

## Connected Thermostat
Connected Thermostat |  |  |  |  | Click to go to Summary of Savings
*This measure is not applicable to multifamily central heating systems with additional capacity for domestic hot water.
|  | Building Year | 0 |  | Building Vintage | 1940 & Prior
|  | # of floors | 0 |  | Building Rise | Low-Rise
|  | # of Apartments | 0 |  | EFLHCooling | 470 |  | EFLHCooling, Interactive | 470
[5 empty] | EFLHHeating | 974 |  | EFLHHeating, Interactive | 974
[18 empty] | Savings without Interactivity |  | Savings with Interactivity
Units | Cooling Type | Heating Type | Cooling Capacity (tons) | Effcooling (SEER) | Is the cooling equipment centralized? | Electric Heating Capacity (kBtu/h) | EffElec,Heating (HSPF) | Gas Heating Capacity (kBtu/h) | Is the heating equipment centralized? | FElecCool | FElecHeat | FFuelHeat | Cooling Capacity/unit (tons) | Electric Heating Capacity/unit (kBtu/h) | Gas Heating Capacity/unit (kBtu/h) | EFLHCooling | EFLHHeating | ΔkWh | Δtherms | ΔkWh | Δtherms
[18 empty] | 0 |  | 0
[18 empty] | 0 |  | 0
[18 empty] | 0 |  | 0
[18 empty] | 0 |  | 0
[18 empty] | 0 |  | 0
[18 empty] | 0 | 0 | 0 | 0
[24 empty] | Heating |  | Cooling
[22 empty] | Lookup | Building age | Low-Rise | High-Rise | Low-Rise | High-Rise
[22 empty] | 0 | 1940 & Prior | 974 | 987 | 470 | 736
[22 empty] | 1941 | 1941-1978 | 738 | 513 | 470 | 736
[22 empty] | 1979 | 1979-2006 | 705 | 385 | 510 | 782
[22 empty] | 2007 | 2007-Now | 491 | 214 | 521 | 885
[22 empty] | Lookup | Rise
[22 empty] | 0 | Low-Rise
[22 empty] | 4 | High-Rise
[22 empty] | ESF | Values
[22 empty] | ESFcooling | 0.1
[22 empty] | ESFheating | 0.08
[23 empty] | FElecCool | FElecHeat | FFuelHeat
[22 empty] | Electric | 1 | 1 | 0
[22 empty] | Gas | 0 | 0 | 1
[22 empty] | Unknown | 0.43 | 0.19 | 0.61
Note on A10: Maximum of 1 per apartment
Note on I10: Input Capacity

## Window Film
Window Film | [5 empty] | HVAC Type: |  |  |  | Click to go to Summary of Savings
# | Location | Window ID | Qty | Window Type | Width (ft) | Height (ft) | SHGCee | Window Area (ft2) | (ΔkWh/100 SF)m | (ΔkWh/100 SF)b | (ΔkW/100 SF)m | (ΔkW/100 SF)b | (Δtherms/100 SF)m | (Δtherms/100 SF)b | ΔkWh | ΔkW | Δtherms
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
[15 empty] | 0 | 0 | 0
Single-Pane
[18 empty] | Window Type | HVAC_Type | (ΔkWh/ 100 SF)m | (ΔkWh/ 100 SF)b | (ΔkW/ 100 SF)m | (ΔkW/ 100 SF)b | (Δtherms/ 100 SF)m | (Δtherms/ 100 SF)b
[18 empty] | Single-Pane | AC with Gas Heat | -548.72 | 356.72 | -0.73 | 0.47 | 11.35 | -7.14
[18 empty] | Double-Pane | Heat Pump | 283.86 | -167.99 | -0.73 | 0.47 | 0 | 0
[19 empty] | AC with Electric Heat | 1116.44 | -692.7 | -0.73 | 0.47 | 0 | 0
[19 empty] | Gas Heat Only | 0 | 0 | 0 | 0 | 11.35 | -7.14
[19 empty] | Electric Heat Only | 1204.6 | -756.79 | 0 | 0 | 0 | 0
Double-Pane
[19 empty] | HVAC_Type | (ΔkWh/ 100 SF)m | (ΔkWh/ 100 SF)b | (ΔkW/ 100 SF)m | (ΔkW/ 100 SF)b | (Δtherms/ 100 SF)m | (Δtherms/ 100 SF)b
[19 empty] | AC with Gas Heat | -559.35 | 323.17 | -0.75 | 0.42 | 11.28 | -6.29
[19 empty] | Heat Pump | 268.83 | -141.25 | -0.75 | 0.42 | 0 | 0
[19 empty] | AC with Electric Heat | 1097.02 | -605.67 | 0.75 | 0.77 | 0 | 0
[19 empty] | Gas Heat Only | 0 | 0 | 0 | 0 | 11.28 | -6.29
[19 empty] | Electric Heat Only | 1195.42 | -669.81 | 0 | 0 | 0 | 0

## Roof & Wall Insulation
Roof & Wall Insulation |  |  |  |  | Click to go to Summary of Savings
[6 empty] | Efficiency Without Interactivity |  |  |  | Efficiency With Interactivity | [11 empty] | Savings Without Interactivity | [6 empty] | Savings With Interactivity
Index | Floor # | Location | HVAC System Type | Gas Equipment Type | Gas Equipment Size Range | Gas Equipment Efficiency | Cooling Equipment EER | Cooling Equipment SEER | Electric Heating Equipment HSPF | Gas Equipment Efficiency_Interactive | Cooling Equipment EER_Interactive | Cooling Equipment SEER_Interactive | Electric Heating Equipment HSPF_Interactive | Envelope Type | Replacement Type | Existing Insulation Quality | Area (sft) | Existing R Value | R Value Added | RBaseline, 1 | RBaseline, 2 | Therm Saving | Heating kWh Saving | Cooling kWh Saving | kWh Saving | kW Saving | EUL | Net MMBTU | Therm Saving_Interactive | Heating kWh Saving_Interactive | Cooling kWh Saving_Interactive | kWh Saving_Interactive | kW Saving_Interactive | Net MMBTU_Interactive | LMMBTU | Total Price | Uncapped Incentive | Final Incentive | Packaged Measure Bonus Incentive | Co-Pay | Depth Category
1 | [35 empty] | 9999
2
3
4
5
6
7
8
9
10
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[47 empty] | NYS TRM v11, Appendix G |  |  |  |  | Default Baseline R-Values |  |  |  | Uninsulated R-Values | [13 empty] | floor_range
[42 empty] | NG Capping | TRM Definition | Building_Rise | Lookup_Building_Age | Building_Age | Low_Rise_Heating_EFLH | High_Rise_Heating_EFLH | Low_Rise_Cooling_EFLH | High_Rise_Cooling_EFLH | HDD | Wall | Roof | Rim Joists | Floors | Wall | Roof | Rim Joists | Floors | Existing R Value | Delta R Value | Equipment Type |  | Size Range | Concatenation | NYCECC Min Efficiency | Factor |  |  | Exterior | F_framing |  | Existing Insulation Quality | Derate Factor | Replacement Type | NYS TRM V11 | Single and Multi-Family Residential Measures
[42 empty] | 0 | 0 | Low Rise | 0 | 1940 & Prior | 974 | 987 | 338 | 338 | 4900 | 4 | 2 | 10 | 19 | 4 | 2 | 4 | 2 | 1 | 11 | Warm Air Furnace, Gas Fired |  | < 225 kBTU/h | Warm Air Furnace, Gas Fired - < 225 kBTU/h | 0.8 | AFUE |  |  | Parking Lot | Wall | 0.25 | Good | 0.82 | No Existing Insulation - Adding New Insulation | Issue Date – October 6, 2023 | INSULATION - OPAQUE SHELL
[42 empty] | 5 | 3 | High Rise | 1941 | 1941-1978 | 738 | 513 | 470 | 736 |  | 7 | 11 | 10 | 19 | 7 | 2 | 7 | 2 | 2 | 13 | Warm Air Furnace, Gas Fired |  | ≥ 225 kBTU/h | Warm Air Furnace, Gas Fired - ≥ 225 kBTU/h | 0.8 | Et |  |  | Garage | Roof | 0.07 | Fair | 0.6 | Existing Insulation - Adding Insulation Layer | Effective Date – January 1, 2024 | ROR # | 6-23-1 | Issue Date | 2023-07-14
[45 empty] | 1979 | 1979-2006 | 705 | 385 | 510 | 782 | CDD | 11 | 19 | 10 | 19 | 7 | 2 | 7 | 2 | 3 | 17 | Warm Air Unit Heaters, Gas Fired |  | < 225 kBTU/h | Warm Air Unit Heaters, Gas Fired - < 225 kBTU/h | 0.8 | AFUE |  |  | Tunnel | Rim Joists | 0.05 | Poor | 0.23 | Existing Insulation - Replacing Insulation
[29 empty] | With Interactivity | With Capping | Cap | [13 empty] | 2007 | 2007-Now | 491 | 214 | 521 | 885 | 1017 | 19 | 38 | 10 | 19 | 7 | 2 | 7 | 2 | 4 | 19 | Warm Air Unit Heaters, Gas Fired |  | ≥ 225 kBTU/h | Warm Air Unit Heaters, Gas Fired - ≥ 225 kBTU/h | 0.8 | Et |  |  | Roof | Floors | 0.12
[28 empty] | Wall Therms Savings | 0 | 0 | 0 | [28 empty] | 5 | 21 | Boiler, Hot Water, Gas Fired | Gas_A | < 300 kBTU/h | Boiler, Hot Water, Gas Fired - < 300 kBTU/h | 0.82 | AFUE |  |  | Basement
[28 empty] | Roof Therms Savings | 0 | 0 | 0 | [19 empty] | CF | [8 empty] | 6 | 25 | Boiler, Hot Water, Gas Fired | Gas_A | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Hot Water, Gas Fired - ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.8 | Et |  |  | Sub Basement
[29 empty] | 0 | 0 | [20 empty] | 0.822 | [8 empty] | 7 | 27 | Boiler, Hot Water, Gas Fired | Gas_A | > 2,500 kBTU/h | Boiler, Hot Water, Gas Fired - > 2,500 kBTU/h | 0.82 | Et |  |  | Penthouse
[60 empty] | 8 | 30 | Boiler, Steam, Gas Fired, All Except Natural Draft | Steam_A | < 300 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft - < 300 kBTU/h | 0.8 | AFUE |  |  | Mezzanine
[44 empty] | National Grid Gas Capping | [15 empty] | 9 | 38 | Boiler, Steam, Gas Fired, All Except Natural Draft | Steam_A | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft - ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.79 | Et |  |  | Ground
[45 empty] | Savings Cap (%) |  | Savings Cap (Therms) | [12 empty] | 10 | 49 | Boiler, Steam, Gas Fired, All Except Natural Draft | Steam_A | > 2,500 kBTU/h | Boiler, Steam, Gas Fired, All Except Natural Draft - > 2,500 kBTU/h | 0.79 | Et |  |  | Stairs
[45 empty] | Low Rise | High Rise | Low Rise | High Rise | [11 empty] | 11 | 60 | Boiler, Steam, Gas Fired, Natural Draft | Steam_B | < 300 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft - < 300 kBTU/h | 0.8 | AFUE |  |  | Hallway
[44 empty] | Wall | 3.5% | 5.5% | 0 | 0 | [11 empty] | 12 |  | Boiler, Steam, Gas Fired, Natural Draft | Steam_B | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft - ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 0.77 | Et |  |  | Other
[44 empty] | Roof | 5.5% | 3.5% | 0 | 0 | [11 empty] | 13 |  | Boiler, Steam, Gas Fired, Natural Draft | Steam_B | > 2,500 kBTU/h | Boiler, Steam, Gas Fired, Natural Draft - > 2,500 kBTU/h | 0.77 | Et |  |  | 1
[60 empty] | 14 | [9 empty] | 2
[44 empty] | ConEd Grid Gas Capping | [15 empty] | 15 | [9 empty] | 3
[45 empty] | Savings Cap % | Savings Cap (Therms) | [13 empty] | 16 | [9 empty] | 4
[44 empty] | Wall | 30% | 0 |  | Building Rise | Low Rise | [10 empty] | 17 | [9 empty] | 5
[44 empty] | Roof | 10% | 0 |  | Gas Utilty | 0 | [10 empty] | 18 |  | Equipment Type | Lookup_Equipment Type | [6 empty] | 6
[60 empty] | 19 |  | Warm Air Furnace, Gas Fired | RWI_Warm_Air_Furnace__Gas_Fired | [6 empty] | 7
[60 empty] | 20 |  | Warm Air Unit Heaters, Gas Fired | RWI_Warm_Air_Unit_Heaters__Gas_Fired | [6 empty] | 8
[60 empty] | 21 |  | Boiler, Hot Water, Gas Fired | RWI_Boiler__Hot_Water__Gas_Fired | [6 empty] | 9
[60 empty] | 22 |  | Boiler, Steam, Gas Fired, All Except Natural Draft | RWI_Boiler__Steam__Gas_Fired__All_Except_Natural_Draft | [6 empty] | 10
[60 empty] | 23 |  | Boiler, Steam, Gas Fired, Natural Draft | RWI_Boiler__Steam__Gas_Fired__Natural_Draft | [6 empty] | 11
[60 empty] | 24 | [9 empty] | 12
[43 empty] | Vlookup # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | [5 empty] | 25 |  | RWI_Warm_Air_Furnace__Gas_Fired | RWI_Warm_Air_Unit_Heaters__Gas_Fired | RWI_Boiler__Hot_Water__Gas_Fired | RWI_Boiler__Steam__Gas_Fired__All_Except_Natural_Draft | RWI_Boiler__Steam__Gas_Fired__Natural_Draft |  |  |  | 13
[44 empty] | 1: HVAC_System_Type Named range lookup; 3: Gas Equipment Type Dependant Dropdowns; 9: F_FuelHeat; 10: F_ElecCool; 11: F_ElecHeat | [5 empty] | 26 |  | < 225 kBTU/h | < 225 kBTU/h | < 300 kBTU/h | < 300 kBTU/h | < 300 kBTU/h | < 300 kBTU/h | < 300 kBTU/h | < 300 kBTU/h | 14
[44 empty] | Chiller and Boiler with FPFC | RWI_Chiller_and_Boiler_with_FPFC | Boiler, Hot Water, Gas Fired | Boiler, Steam, Gas Fired, All Except Natural Draft | Boiler, Steam, Gas Fired, Natural Draft |  |  |  | 1 | 1 | 0 | [5 empty] | 27 |  | ≥ 225 kBTU/h | ≥ 225 kBTU/h | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | ≥ 300 kBTU/h and ≤ 2,500 kBTU/h | 15
[44 empty] | Steam Boiler Only | RWI_Steam_Boiler_Only | Boiler, Steam, Gas Fired, All Except Natural Draft | Boiler, Steam, Gas Fired, Natural Draft |  |  |  |  | 1 | 0 | 0 | [5 empty] | 28 |  |  |  | > 2,500 kBTU/h | > 2,500 kBTU/h | > 2,500 kBTU/h | > 2,500 kBTU/h | > 2,500 kBTU/h | > 2,500 kBTU/h | 16
[44 empty] | AC with Gas Heat | RWI_AC_with_Gas_Heat | Warm Air Furnace, Gas Fired | Warm Air Unit Heaters, Gas Fired | Boiler, Hot Water, Gas Fired | Boiler, Steam, Gas Fired, All Except Natural Draft | Boiler, Steam, Gas Fired, Natural Draft |  | 1 | 1 | 0 | [5 empty] | 29 | [9 empty] | 17
[44 empty] | Gas Heat Only | RWI_Gas_Heat_Only | Warm Air Furnace, Gas Fired | Warm Air Unit Heaters, Gas Fired | Boiler, Hot Water, Gas Fired | Boiler, Steam, Gas Fired, All Except Natural Draft | Boiler, Steam, Gas Fired, Natural Draft |  | 1 | 0 | 0 | [5 empty] | 30 | [9 empty] | 18
[44 empty] | 1: Electric Heat Only; 2: RWI_Electric_Heat_Only; 9: 0; 10: 0; 11: 1 | [15 empty] | 19
[44 empty] | 1: AC with Electric Heat; 2: RWI_AC_with_Electric_Heat; 9: 0; 10: 1; 11: 1 | [15 empty] | 20
[44 empty] | 1: Heat Pump; 2: RWI_Heat_Pump; 9: 0; 10: 1; 11: 1 | [15 empty] | 21
[44 empty] | 1: AC with Oil Heat; 9: 0; 10: 1; 11: 0 | [15 empty] | 22
23
24
25
26
[44 empty] | 3: HVAC_System_Type | [15 empty] | 27
[44 empty] | 3: Chiller and Boiler with FPFC | [15 empty] | 28
[44 empty] | 3: Heat Pump | [15 empty] | 29
[44 empty] | 3: AC with Gas Heat | [15 empty] | 30
[44 empty] | 3: AC with Electric Heat | [15 empty] | 31
[44 empty] | 3: AC with Oil Heat | [15 empty] | 32
[44 empty] | 3: Steam Boiler Only | [15 empty] | 33
[44 empty] | 3: Gas Heat Only | [15 empty] | 34
[44 empty] | 3: Electric Heat Only | [15 empty] | 35
36
37 | bar: 3
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
Note on U3: Existing R ValueDerated
Note on V3: Only different from RBaseline, 1 when Replacement Type = "Existing Insulation - Replacing Insulation"
Note on BV18: NYS TRM V11 p.196

## Cool Roof (hidden)
Cool Roof |  |  |  | Click to go to Summary of Savings
| Input |  | Explanation
| Roof Area (SF) |  | Area of installed cool roof
| kSF | 0 | Thousand square feet of installed cool roof
| ∆KWh/1,000SF | 211 | Annual electric energy savings per thousand feet of cool roof
| ∆KW/1,000SF | 0.128 | Peak coincident demand electric savings per thousand feet of cool roof
| ∆MMBtu/1,000SF | -1.67 | Annual fossil fuel energy savings per thousand square feet of cool roof
| CF | 0.8 | Coincidence factor
| ∆KWh | 0 | Annual Electric Energy Savings
| ∆KW | 0 | Summer Peak Coincident Demand Savings
| ∆MMBtu | 0 | Annual Fossil Fuel Energy Savings
Note on D5: Default Formula: 'Building Info'!C12/'Building Info'!C10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Appendix I - Building Type: Other

## Window Replacement
Window Replacement |  |  |  | Click to go to Summary of Savings
PROJECT SITE AND ADDRESS
|  | Overview of the Building |  |  |  | INCENTIVE RATES
|  | Heating System |  |  |  | INCENTIVE RATES |  | 200
|  | Heating System Efficiency |  | With Interactivity → | 0%
|  | Cooling System |  |  |  | Heating type |  |  |  | 95%
|  | Cooling System COP |  | With Interactivity → | 0 | Cooling Type
|  | Existing Window Type |  | <<Input Information about Existing Window Type
|  | Number of Floors |  |  |  | PROJECT SUMMARY
|  | Number of Units |  |  |  |  | Savings without Interactivity |  |  | Savings with Interactivity
|  | LMI/Market Rate |  |  |  |  | kWh | Therms | Net MMBtu | kWh | Therms | Net MMBtu | Incentive ($)
|  | Number of Windows Being Replaced |  |  |  | Thermal Conduction Savings | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Surface Area per Window |  |  |  | Infiltration Savings | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | U-Factor of Existing Window (Btu/(h∙ft2∙°F)) |  |  |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
U-Factor of Proposed Window (Btu/(h∙ft2∙°F))
Infltration Rate of Existing Window (CFM/sq.ft)
Infltration Rate of Proposed Window (CFM/sq.ft)
|  | Inside Temperature- Cooling (F) | 72
|  | Inside Temperature- Heating (F) | 68
|  | Temperature at which Heating is turned on (F) | 55
|  | Temperature at which Cooling is turned on (F) | 78
ADD PROJECT NOTES (IF ANY) 1. 2. 3. 4. 5. 6.
[14 empty] | THERMAL CONDUCTION SAVINGS | [16 empty] | THERMAL CONDUCTION SAVINGS | [13 empty] | Infiltration Savings | [7 empty] | Infiltration Summary | [16 empty] | Perscriptive Incentive Rates | [8 empty] | Sample Size Guideline
[70 empty] | LMI Rates |  |  | Market Rates |  |  | Data
[14 empty] | Building description | [16 empty] | INFILTRATION SAVINGS SUMMARY | [14 empty] | EXISTING |  |  |  | PROPOSED |  |  | INFILTRATION SAVINGS SUMMARY | [8 empty] | Building Specification | [7 empty] | Gas (per therm) | 5 |  | Gas | 4 |  | LMI |  |  | WINDOW SAMPLE SIZE
[14 empty] | Number of Floors | 0 | [16 empty] | Btu/h | MMBtu | kWh | Therms | Total Incentive | [9 empty] | c | 0.24 | Specific Heat of Air |  | c | 0.24 | Specific Heat of Air |  | Btu/h | MMBtu | kWh | Therms | Electric Incentive | [11 empty] | Electric | 0.75 |  | Electric | 0.6 |  | Market Rate |  |  | Apartment Units | Building Size | Total no. of Windows that needs to be tested (whichever is greater)
[14 empty] | Number of Units | 0 | [15 empty] | Heating Season Savings | 0 | 0 | 0 | 0 | 0 | [9 empty] | ρ | 0.075 | Standard Density of Air |  | ρ | 0.075 | Standard Density of Air | Heating Season Savings | 0 | 0 | 0 | 0 | 0 |  |  | approximately 4 windows per unit | 1 to 20 | small | 0 to 80 | 4.8 | 6% or at least 3 windows whichever is greater | [14 empty] | Percentage of Windows (%) | No. of Windows
[14 empty] | Windows replaced | 0 | [15 empty] | Cooling Season Savings | 0 | 0 | 0 | 0 | 0 | [9 empty] | Window Infiltration | 0 | CFM/sq.ft |  | Window Infiltration | 0 | CFM/sq.ft | Cooling Season Savings | 0 | 0 | 0 | 0 | 0 |  |  |  | 20 to 100 units | medium | 80 to 400 | 8 | 2% or at least 5 windows whichever is greater |  |  |  | Heating Type | Gas Flag | Electric Flag | Cooling Type | Gas Flag | Electric Flag |  |  |  | 1 to 20 | Small | 6% | 3
[14 empty] | Av area/window (SF) | 0 | ft2 | [14 empty] | TOTAL | 0 | 0 | 0 | 0 | 0 | [9 empty] | QW | 0 | CFM for total sq. ft of window |  | QW | 0 | CFM for total sq. ft of window | TOTAL | 0 | 0 | 0 | 0 | 0 |  |  |  | 100 units or more | large | 400 and above | 10 | 1% or at least 8 windows whichever is greater |  |  |  | Oil Only | 0 | 0 | Electric | 0 | 1 |  |  |  | 21 to 100 | Medium | 2% | 5
[14 empty] | Existing Window U-Factor | 0 | Btu/(h∙ft2∙°F) | [29 empty] | Heating Equipment Efficiency | 0% | Efficiency |  | Heating Equipment Efficiency | 0% | Efficiency | [17 empty] | Firm Gas Only | 1 | 0 | Gas | 1 | 0 |  |  |  | 101 or more | Large | 1% | 8
[14 empty] | Proposed Window U-Factor | 0 | Btu/(h∙ft2∙°F) | [29 empty] | Cooling Equipment COP | 0 | COP |  | COP | 0 | COP | [17 empty] | Interruptible Gas | 0.95 | 0
[14 empty] | Inside Temperature- Cooling (F) | 72 | F | [53 empty] | Electric | 0 | 1
[14 empty] | Inside Temperature- Heating (F) | 68 | F | [14 empty] | Month | January | Unit |  |  | Month | February | Unit | Month | March | Unit | Month | April | Unit |  |  | No of Windows Being Replaced | 0 |  |  |  |  | Month | January | Unit |  |  | Month | February | Unit |  |  | Month | March | Unit |  | Month | April | Unit
[14 empty] | Temperature at which Heating is turned on (F) | 55 | F | [14 empty] | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  | No Of Windows | 0 |  | No Of Windows | 0 |  |  |  | Surface Area Per Window (sq. ft) | 0 |  |  |  |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  |  | No Of Windows | 0
[14 empty] | Temperature at which Cooling is turned on (F) | 78 | F | [14 empty] | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Total Window Sq. Ft | 0 |  |  |  |  | Total Area of Windows | 0 |  |  |  | Total Area of Windows | 0 |  |  |  | Total Area of Windows | 0 |  |  | Total Area of Windows | 0
[31 empty] | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Inside Temperature- Cooling (F) | 72 |  |  |  |  | Exsiting Infiltration | 0 | CFH |  |  | Exsiting Infiltration | 0 | CFH |  |  | Exsiting Infiltration | 0 | CFH |  | Exsiting Infiltration | 0 | CFH
[31 empty] | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h | Existing Consumption | 0 | Btu/h | Existing Consumption | 0 | Btu/h |  |  | Inside Temperature- Heating (F) | 68 |  |  |  |  | Proposed Infiltration | 0 | CFH |  |  | Proposed Infiltration | 0 | CFH |  |  | Proposed Infiltration | 0 | CFH |  | Proposed Infiltration | 0 | CFH
[31 empty] | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h | Proposed Consumption | 0 | Btu/h | Proposed Consumption | 0 | Btu/h |  |  | Temperature at which Heating is turned on (F) | 55 |  |  |  |  | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h |  | Existing Consumption | 0 | Btu/h
[31 empty] | Savings | 0 | Btu/h |  |  |  | 0 | Btu/h |  | 0 | Btu/h |  | 0 | Btu/h |  |  | Temperature at which Cooling is turned on (F) | 78 |  |  |  |  | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h |  | Proposed Consumption | 0 | Btu/h |  |  | kWh | MBH | kWh | MBH | per unit | per unit
[14 empty] | CALCULATIONS | [17 empty] | 0 | kWh |  |  |  | 0 | kWh |  | 0 | kWh |  | 0 | kWh | [8 empty] | Savings | 0 | Btu/h |  |  |  | 0 | Btu/h |  |  |  | 0 | Btu/h |  |  | 0 | Btu/h | Measure | Incentive Detail | Affordable Housing Incentive | Affordable Housing Incentive | Market Rate Incentive | Market Rate Incentive | Affordable Housing Incentive | Market Rate Incentive | EUL
[29 empty] | INCENTIVE |  |  | 0 | Therms |  |  |  | 0 | Therms |  | 0 | Therms |  | 0 | Therms | [9 empty] | 0 | kWh |  |  |  | 0 | kWh |  |  |  | 0 | kWh |  |  | 0 | kWh | Hot Water Boilers | Minimum Boiler Efficiency: Et or AFUE of 85% for boilers < 2,500 kBtu/h or 88% Ec for boilers > 2,500 kBtu/h |  |  |  |  | $8 per MBH | $5 per MBH
[29 empty] | 200 | $/MMBtu Savings' | [23 empty] | 0 | Therms |  |  |  | 0 | Therms |  |  |  | 0 | Therms |  |  | 0 | Therms | Condensing Boilers | Minimum Boiler Efficiency: Et or AFUE of 90% for boilers < 2,500 kBtu/h or 93% Ec for boilers > 2,500 kBtu/h |  |  |  |  | $16 per MBH | $9 per MBH
[15 empty] | Ucurrent (Btu/(h∙ft2∙°F) | Uproposed (Btu/(h∙ft2∙°F) | No of Windows Being Replaced | Window Area (sq.ft) | Heating Equipment Efficiency | Cooling Equipment Efficiency | Cooling Savings (Btuh) | Cooling Savings (MMBtu) | Cooling Savings (kWh) | Cooling Savings (Therms) | Heating Savings (Btuh) | Heating Savings (MMBtu) | Heating Savings (Therms) | Heating Savings (kWh) | Cooling Season Incentive per MMBtu ($) | Heating Season Incentive per MMBtu ($) | [39 empty] | Steam Boilers | Minimum Boiler Efficiency: Et or AFUE 82% |  |  |  |  | $8 per MBH | $5 per MBH
[14 empty] | Windows | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [39 empty] | Storage Tank Water Heaters | Storage tank volume > 70 gallons and Et>90% |  |  |  |  | $7,000 per tank | $4,000 per tank
[14 empty] | Total |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Month | May | Unit |  |  | Month | June | Unit | Month | July | Unit | Month | August | Unit | [25 empty] | Energy Management Systems | 10-19 Boiler control system with multiple temperature sensors for steam or water lines, flue gas, and indoor air, and remote system monitoring capability (250+ units may apply for the custom incentive rate) | 2021-10-19 |  |  |  | 3000 | 2000
[28 empty] | Total Incentive | 0 |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  | No Of Windows | 0 |  | No Of Windows | 0 | [9 empty] | Month | May | Unit |  |  | Month | June | Unit |  |  | Month | July | Unit |  | Month | August | Unit | Energy Management Systems | 20-40 Boiler control system with multiple temperature sensors for steam or water lines, flue gas, and indoor air, and remote system monitoring capability (250+ units may apply for the custom incentive rate) | 20-40 |  |  |  | 6000 | 4000
[31 empty] | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Day and Time | Temp Reading | Existing Sensible Load | Proposed Sensible Load | Sensible Load Savings (Btuh) |  |  |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  |  | No Of Windows | 0 |  | Energy Management Systems | 41-99 Boiler control system with multiple temperature sensors for steam or water lines, flue gas, and indoor air, and remote system monitoring capability (250+ units may apply for the custom incentive rate) | 41-99 |  |  |  | 12000 | 8000
[31 empty] | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | 01/01/2020 01:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Total Area of Windows | 0 |  |  |  | Total Area of Windows | 0 |  |  |  | Total Area of Windows | 0 |  |  | Total Area of Windows | 0 |  | Energy Management Systems | 100-249 Boiler control system with multiple temperature sensors for steam or water lines, flue gas, and indoor air, and remote system monitoring capability (250+ units may apply for the custom incentive rate) | 100-249 |  |  |  | 18000 | 12000
[31 empty] | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h | Existing Consumption | 0 | Btu/h | Existing Consumption | 0 | Btu/h | 01/01/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Exsiting Infiltration | 0 | CFH |  |  | Exsiting Infiltration | 0 | CFH |  |  | Exsiting Infiltration | 0 | CFH |  | Exsiting Infiltration | 0 | CFH | Linear Pipe Insulation | •Fiberglass insulation or rigid foam < 2” Pipe Diameter |  |  |  |  | •$10 per linear ft. | •$9 per linear ft.
[31 empty] | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h | Proposed Consumption | 0 | Btu/h | Proposed Consumption | 0 | Btu/h | 01/01/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Proposed Infiltration | 0 | CFH |  |  | Proposed Infiltration | 0 | CFH |  |  | Proposed Infiltration | 0 | CFH |  | Proposed Infiltration | 0 | CFH | Linear Pipe Insulation | •Fiberglass insulation or rigid foam > 2” Pipe Diameter |  |  |  |  | •$15 per linear ft. | •$14 per linear ft.
[32 empty] | 0 | Btu/h |  |  |  | 0 | Btu/h |  | 0 | Btu/h |  | 0 | Btu/h | 01/01/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h |  | Existing Consumption | 0 | Btu/h | Roof and Wall Insulation | •R-11 added |  |  |  |  | •$2.00 per sq ft. | •$1.00 per sq ft.
[32 empty] | 0 | kWh |  |  |  | 0 | kWh |  | 0 | kWh |  | 0 | kWh | 01/01/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h |  | Proposed Consumption | 0 | Btu/h | Roof and Wall Insulation | •R-19 added |  |  |  |  | •$4.00 per sq ft. | •$2.00 per sq ft.
[32 empty] | 0 | Therms |  |  |  | 0 | Therms |  | 0 | Therms |  | 0 | Therms | 01/01/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | Btu/h |  |  |  | 0 | Btu/h |  |  |  | 0 | Btu/h |  |  | 0 | Btu/h | Roof and Wall Insulation | •R-38 added |  |  |  |  | •$6.00 per sq ft. | •$3.00 per sq ft.
[45 empty] | 01/01/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | kWh |  |  |  | 0 | kWh |  |  |  | 0 | kWh |  |  | 0 | kWh | Steam Traps | Covers the repair or replacement of steam traps in low pressure heating systems (<15 psig). Incentive includes credit towards completing the program required survey |  |  |  |  | •Common areas - $500 per trap
[14 empty] | Day and Time | Temp Reading | Existing Energy Consumption | Proposed Energy Consumption | Savings | [26 empty] | 01/01/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | Therms |  |  |  | 0 | Therms |  |  |  | 0 | Therms |  |  | 0 | Therms | Steam Traps | Covers the repair or replacement of steam traps in low pressure heating systems (<15 psig). Incentive includes credit towards completing the program required survey |  |  |  |  | •All other radiators - $200 per trap
[14 empty] | 01/01/2020 01:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/01/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Steam Traps | Covers the repair or replacement of steam traps in low pressure heating systems (<15 psig). Incentive includes credit towards completing the program required survey |  |  |  |  | •$125 per trap
[14 empty] | 01/01/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [12 empty] | Month | September | Unit |  |  | Month | October | Unit | Month | November | Unit | Month | December | Unit | 01/01/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Steam Traps | Covers the repair or replacement of steam traps in low pressure heating systems (<15 psig). Incentive includes credit towards completing the program required survey |  |  |  |  | •$25 per trap
[14 empty] | 01/01/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [12 empty] | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  | No Of Windows | 0 |  | No Of Windows | 0 |  | 01/01/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Duct Seal |  | 50% of cost - up to $500 per unit |  |  |  | 50% of cost - up to $500 per unit | 50% of cost - up to $500 per unit
[14 empty] | 01/01/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [12 empty] | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | Exisiting U-Factor | 0 | Btu/(h∙ft2∙°F) | 01/01/2020 12:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Month | September | Unit |  |  | Month | October | Unit |  |  | Month | November | Unit |  | Month | December | Unit | Boiler Clean and Tune | This measure covers an advanced clean & tune procedure performed on a steam or hot water boiler (routine seasonal boiler tune-ups will not be incentivized) | •$1,500 per boiler |  |  |  | •$1,500 per boiler | •$1,500 per boiler
[14 empty] | 01/01/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [12 empty] | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) |  |  | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | Proposed U-Factor | 0 | Btu/(h∙ft2∙°F) | 01/01/2020 13:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  |  |  | No Of Windows | 0 |  |  | No Of Windows | 0 |  | Boiler Clean and Tune | This measure covers an advanced clean & tune procedure performed on a steam or hot water boiler (routine seasonal boiler tune-ups will not be incentivized) | •$2,100 for two-boiler plant |  |  |  | •$2,100 for two-boiler plant | •$2,100 for two-boiler plant
[14 empty] | 01/01/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [12 empty] | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h | Existing Consumption | 0 | Btu/h | Existing Consumption | 0 | Btu/h | 01/01/2020 14:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Total Area of Windows | 0 |  |  |  | Total Area of Windows | 0 |  |  |  | Total Area of Windows | 0 |  |  | Total Area of Windows | 0 |  | Boiler Clean and Tune | This measure covers an advanced clean & tune procedure performed on a steam or hot water boiler (routine seasonal boiler tune-ups will not be incentivized) | •$2,700 for three-boiler plant |  |  |  | •$2,700 for three-boiler plant | •$2,700 for three-boiler plant
[14 empty] | 01/01/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [12 empty] | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h | Proposed Consumption | 0 | Btu/h | Proposed Consumption | 0 | Btu/h | 01/01/2020 15:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Exsiting Infiltration | 0 | CFH |  |  | Exsiting Infiltration | 0 | CFH |  |  | Exsiting Infiltration | 0 | CFH |  | Exsiting Infiltration | 0 | CFH | Air Sealing | This package will include repair and weather sealing of louver vents, exterior doors, common area windows, and the general perimeter of the basement |  | Free |  | $3 per therm |  |  | 15
[14 empty] | 01/01/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [13 empty] | 0 | Btu/h |  |  |  | 0 | Btu/h |  | 0 | Btu/h |  | 0 | Btu/h | 01/01/2020 16:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Proposed Infiltration | 0 | CFH |  |  | Proposed Infiltration | 0 | CFH |  |  | Proposed Infiltration | 0 | CFH |  | Proposed Infiltration | 0 | CFH | 2-pipe Steam Retro-Commissioning | Treats heating imbalance issues by designing and installing: |  | $5 per Therm |  | $5 per Therm
[14 empty] | 01/01/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [13 empty] | 0 | kWh |  |  |  | 0 | kWh |  | 0 | kWh |  | 0 | kWh | 01/01/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h |  |  | Existing Consumption | 0 | Btu/h |  | Existing Consumption | 0 | Btu/h | 2-pipe Steam Retro-Commissioning | a)Air vents on all main pipes (atmospheric systems) |  | $5 per Therm |  | $5 per Therm
[14 empty] | 01/01/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [13 empty] | 0 | Therms |  |  |  | 0 | Therms |  | 0 | Therms |  | 0 | Therms | 01/01/2020 18:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h |  |  | Proposed Consumption | 0 | Btu/h |  | Proposed Consumption | 0 | Btu/h | 2-pipe Steam Retro-Commissioning | b)Thermostatic radiator valves and orifice plates on every radiator |  | $5 per Therm |  | $5 per Therm
[14 empty] | 01/01/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/01/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | Btu/h |  |  |  | 0 | Btu/h |  |  |  | 0 | Btu/h |  |  | 0 | Btu/h | 2-pipe Steam Retro-Commissioning | c)Clean and tune up of boiler and burner, including firing rate and draft adjustment, water cleaning, electronic pressure control, and combustion testing |  | $5 per Therm |  | $5 per Therm
[14 empty] | 01/01/2020 12:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/01/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | kWh |  |  |  | 0 | kWh |  |  |  | 0 | kWh |  |  | 0 | kWh | 2-pipe Steam Retro-Commissioning | d)Steam trap repair throughout common areas |  | $5 per Therm |  | $5 per Therm
[14 empty] | 01/01/2020 13:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/01/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | Therms |  |  |  | 0 | Therms |  |  |  | 0 | Therms |  |  | 0 | Therms | Unitary Controls | Any non-central building system control projects (e.g. Wi-Fi thermostats connected to an in-unit PTAC or PTHP) may be submitted as a custom project. Simple control equipment installations that do not allow for multiple data inputs (i.e. decision made on a single data point, is manually programmed/operated/or scheduled, or does not allow for real-time monitoring and control through a software package or building communications protocol). This includes: Wi-Fi thermostats, thermostatic radiator valves, building management systems, and ventilation controls | $0.16 per kWh | $1 per Therm | $0.16 per kWh | $1 per Therm |  |  | 10
[14 empty] | 01/01/2020 14:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/01/2020 22:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Custom | Other non-lighting efficiency upgrades not listed in this document may be eligible for performance-based custom incentive. Other energy efficiency upgrades not listed in this document may be eligible for custom incentives. Final custom measure eligibility, savings and incentives are determined at the sole discretion of Con Edison. Custom projects include but are not limited to: boiler economizers, linkageless burner controls, and heat pump boiler pre-heaters. | $0.75 per kWh | $5 per Therm | $0.60 per kWh | $4 per Therm |  |  | 10
[14 empty] | 01/01/2020 15:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/01/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Air Conditioner – Central Unit Replacement |  | $0.75 per kWh |  | $0.60 per kWh
[14 empty] | 01/01/2020 16:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 00:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Packaged Terminal Air Conditioner |  | $0.75 per kWh |  | $0.60 per kWh
[14 empty] | 01/01/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Elevator Modernization |  | $0.35 per kWh |  | $0.25 per kWh
[14 empty] | 01/01/2020 18:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 02:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Variable Frequency Drive |  | $0.29 per kWh |  | $0.19 per kWh
[14 empty] | 01/01/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 03:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Blower Fan – with Electronically Commutated Motor for Furnace Distribution |  | $0.75 per kWh |  | $0.60 per kWh
[14 empty] | 01/01/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Circulator Pump – with Electronically Commutated Motor for Hydronic Distribution |  | $0.75 per kWh |  | $0.60 per kWh
[14 empty] | 01/01/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [20 empty] | Air Conditioner and Heat Pump – Refrigerant Charge Correction |  | $0.75 per kWh |  | $0.60 per kWh
[14 empty] | 01/01/2020 22:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/01/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 07:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 00:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 02:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 03:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 14:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 07:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 17:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 18:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 14:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/02/2020 23:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 17:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 01:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 18:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 06:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/02/2020 23:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 08:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 01:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 06:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 08:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 17:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 18:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 20:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 22:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/03/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 17:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 01:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 18:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 02:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 20:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 22:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/03/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 01:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 02:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 13:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 13:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/04/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 02:00 | 40.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/04/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 02:00 | 40.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 12:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 17:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 12:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/05/2020 23:00 | 36.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 17:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 04:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/05/2020 23:00 | 36.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 09:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 10:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 04:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 13:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 09:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 10:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 13:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/06/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/06/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 19:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 22:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/07/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 19:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 22:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/07/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 10:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 11:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 14:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 10:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 11:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 21:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 14:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/08/2020 23:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 00:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 01:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 02:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 03:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 04:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 21:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 06:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/08/2020 23:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 07:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 00:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 08:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 01:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 09:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 02:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 10:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 03:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 11:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 04:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 12:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 13:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 06:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 14:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 07:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 08:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 09:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 10:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 18:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 11:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 19:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 12:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 13:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 14:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/09/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 18:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 19:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 03:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 05:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 06:00 | 36.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/09/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 08:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 10:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 03:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 05:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 06:00 | 36.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 08:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 17:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 10:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 19:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 20:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 22:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/10/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 00:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 17:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 01:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 02:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 19:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 03:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 20:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 04:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/10/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 05:00 | 56 | 0 | 0 | 0
[14 empty] | 01/10/2020 22:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 06:00 | 56 | 0 | 0 | 0
[14 empty] | 01/10/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 07:00 | 58 | 0 | 0 | 0
[14 empty] | 01/11/2020 00:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 08:00 | 59 | 0 | 0 | 0
[14 empty] | 01/11/2020 01:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 09:00 | 59 | 0 | 0 | 0
[14 empty] | 01/11/2020 02:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 10:00 | 59 | 0 | 0 | 0
[14 empty] | 01/11/2020 03:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 11:00 | 61 | 0 | 0 | 0
[14 empty] | 01/11/2020 04:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/11/2020 12:00 | 65 | 0 | 0 | 0
[14 empty] | 01/11/2020 05:00 | 56 | 0 | 0 | 0 | [26 empty] | 01/11/2020 13:00 | 65 | 0 | 0 | 0
[14 empty] | 01/11/2020 06:00 | 56 | 0 | 0 | 0 | [26 empty] | 01/11/2020 14:00 | 67 | 0 | 0 | 0
[14 empty] | 01/11/2020 07:00 | 58 | 0 | 0 | 0 | [26 empty] | 01/11/2020 15:00 | 68 | 0 | 0 | 0
[14 empty] | 01/11/2020 08:00 | 59 | 0 | 0 | 0 | [26 empty] | 01/11/2020 16:00 | 68 | 0 | 0 | 0
[14 empty] | 01/11/2020 09:00 | 59 | 0 | 0 | 0 | [26 empty] | 01/11/2020 17:00 | 64 | 0 | 0 | 0
[14 empty] | 01/11/2020 10:00 | 59 | 0 | 0 | 0 | [26 empty] | 01/11/2020 18:00 | 63 | 0 | 0 | 0
[14 empty] | 01/11/2020 11:00 | 61 | 0 | 0 | 0 | [26 empty] | 01/11/2020 19:00 | 62 | 0 | 0 | 0
[14 empty] | 01/11/2020 12:00 | 65 | 0 | 0 | 0 | [26 empty] | 01/11/2020 20:00 | 63 | 0 | 0 | 0
[14 empty] | 01/11/2020 13:00 | 65 | 0 | 0 | 0 | [26 empty] | 01/11/2020 21:00 | 64 | 0 | 0 | 0
[14 empty] | 01/11/2020 14:00 | 67 | 0 | 0 | 0 | [26 empty] | 01/11/2020 22:00 | 63 | 0 | 0 | 0
[14 empty] | 01/11/2020 15:00 | 68 | 0 | 0 | 0 | [26 empty] | 01/11/2020 23:00 | 62 | 0 | 0 | 0
[14 empty] | 01/11/2020 16:00 | 68 | 0 | 0 | 0 | [26 empty] | 01/12/2020 00:00 | 62 | 0 | 0 | 0
[14 empty] | 01/11/2020 17:00 | 64 | 0 | 0 | 0 | [26 empty] | 01/12/2020 01:00 | 63 | 0 | 0 | 0
[14 empty] | 01/11/2020 18:00 | 63 | 0 | 0 | 0 | [26 empty] | 01/12/2020 02:00 | 60 | 0 | 0 | 0
[14 empty] | 01/11/2020 19:00 | 62 | 0 | 0 | 0 | [26 empty] | 01/12/2020 03:00 | 60 | 0 | 0 | 0
[14 empty] | 01/11/2020 20:00 | 63 | 0 | 0 | 0 | [26 empty] | 01/12/2020 04:00 | 58 | 0 | 0 | 0
[14 empty] | 01/11/2020 21:00 | 64 | 0 | 0 | 0 | [26 empty] | 01/12/2020 05:00 | 62 | 0 | 0 | 0
[14 empty] | 01/11/2020 22:00 | 63 | 0 | 0 | 0 | [26 empty] | 01/12/2020 06:00 | 64 | 0 | 0 | 0
[14 empty] | 01/11/2020 23:00 | 62 | 0 | 0 | 0 | [26 empty] | 01/12/2020 07:00 | 64 | 0 | 0 | 0
[14 empty] | 01/12/2020 00:00 | 62 | 0 | 0 | 0 | [26 empty] | 01/12/2020 08:00 | 65 | 0 | 0 | 0
[14 empty] | 01/12/2020 01:00 | 63 | 0 | 0 | 0 | [26 empty] | 01/12/2020 09:00 | 66 | 0 | 0 | 0
[14 empty] | 01/12/2020 02:00 | 60 | 0 | 0 | 0 | [26 empty] | 01/12/2020 10:00 | 67 | 0 | 0 | 0
[14 empty] | 01/12/2020 03:00 | 60 | 0 | 0 | 0 | [26 empty] | 01/12/2020 11:00 | 66 | 0 | 0 | 0
[14 empty] | 01/12/2020 04:00 | 58 | 0 | 0 | 0 | [26 empty] | 01/12/2020 12:00 | 66 | 0 | 0 | 0
[14 empty] | 01/12/2020 05:00 | 62 | 0 | 0 | 0 | [26 empty] | 01/12/2020 13:00 | 66 | 0 | 0 | 0
[14 empty] | 01/12/2020 06:00 | 64 | 0 | 0 | 0 | [26 empty] | 01/12/2020 14:00 | 66 | 0 | 0 | 0
[14 empty] | 01/12/2020 07:00 | 64 | 0 | 0 | 0 | [26 empty] | 01/12/2020 15:00 | 67 | 0 | 0 | 0
[14 empty] | 01/12/2020 08:00 | 65 | 0 | 0 | 0 | [26 empty] | 01/12/2020 16:00 | 65 | 0 | 0 | 0
[14 empty] | 01/12/2020 09:00 | 66 | 0 | 0 | 0 | [26 empty] | 01/12/2020 17:00 | 63 | 0 | 0 | 0
[14 empty] | 01/12/2020 10:00 | 67 | 0 | 0 | 0 | [26 empty] | 01/12/2020 18:00 | 61 | 0 | 0 | 0
[14 empty] | 01/12/2020 11:00 | 66 | 0 | 0 | 0 | [26 empty] | 01/12/2020 19:00 | 58 | 0 | 0 | 0
[14 empty] | 01/12/2020 12:00 | 66 | 0 | 0 | 0 | [26 empty] | 01/12/2020 20:00 | 57 | 0 | 0 | 0
[14 empty] | 01/12/2020 13:00 | 66 | 0 | 0 | 0 | [26 empty] | 01/12/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 14:00 | 66 | 0 | 0 | 0 | [26 empty] | 01/12/2020 22:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 15:00 | 67 | 0 | 0 | 0 | [26 empty] | 01/12/2020 23:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 16:00 | 65 | 0 | 0 | 0 | [26 empty] | 01/13/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 17:00 | 63 | 0 | 0 | 0 | [26 empty] | 01/13/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 18:00 | 61 | 0 | 0 | 0 | [26 empty] | 01/13/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 19:00 | 58 | 0 | 0 | 0 | [26 empty] | 01/13/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 20:00 | 57 | 0 | 0 | 0 | [26 empty] | 01/13/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 22:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/12/2020 23:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/13/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 05:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/13/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 05:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 16:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/14/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 16:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/14/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 13:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 13:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/15/2020 23:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/15/2020 23:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 09:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 12:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 14:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 09:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 12:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 21:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 14:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 22:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/16/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 00:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 04:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 21:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 05:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 22:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/16/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 00:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 08:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 09:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 10:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 11:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 04:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 12:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 05:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 13:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 14:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 15:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 08:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 16:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 09:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 17:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 10:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 18:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 11:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 19:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 12:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 20:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 13:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 21:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 14:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 22:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 15:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/17/2020 23:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 16:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 00:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 17:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 01:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 18:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 02:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 19:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 03:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 20:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 04:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 21:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 05:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 22:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 06:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/17/2020 23:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 07:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 00:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 01:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 02:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 10:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 03:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 11:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 04:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 12:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 05:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 13:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 06:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 14:00 | 26.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 07:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 15:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 16:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 17:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 10:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 18:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 11:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 19:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 12:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 13:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 14:00 | 26.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 15:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/18/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 16:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 17:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 18:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 19:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 05:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/18/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 05:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 18:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 21:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/19/2020 23:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 01:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 18:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 02:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 03:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 04:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 21:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 05:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 06:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/19/2020 23:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 07:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 01:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 09:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 02:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 10:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 03:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 11:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 04:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 12:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 05:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 13:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 06:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 14:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 07:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 15:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 09:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 17:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 10:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 11:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 12:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 20:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 13:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 21:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 14:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 22:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 15:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/20/2020 23:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 00:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 17:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 01:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 02:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 03:00 | 19 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 20:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 04:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 21:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 05:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 22:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 06:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/20/2020 23:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 07:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 00:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 08:00 | 20.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 01:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 02:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 10:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 03:00 | 19 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 11:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 04:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 12:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 05:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 13:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 06:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 14:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 07:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 08:00 | 20.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 10:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 18:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 11:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 19:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 12:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 20:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 13:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 21:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 14:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 22:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/21/2020 23:00 | 28.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 00:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 01:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 18:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 02:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 19:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 03:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 20:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 04:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 21:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 05:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 22:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/21/2020 23:00 | 28.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 00:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 08:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 01:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 09:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 02:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 03:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 11:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 04:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 12:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 05:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 13:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 14:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 08:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 09:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 11:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 12:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 13:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 14:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/22/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 04:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 05:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/22/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 04:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 05:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 16:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 17:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 21:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/23/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 16:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 17:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 21:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/23/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/24/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/24/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 22:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/25/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 22:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/25/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 02:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 10:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 10:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/26/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/26/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/27/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/27/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 20:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/28/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 20:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 05:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 06:00 | 34.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/28/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 07:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 10:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 05:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 06:00 | 34.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 07:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 10:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/29/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 01:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 02:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 04:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 05:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 06:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/29/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 08:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 01:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 09:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 02:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 10:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 04:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 12:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 05:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 13:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 06:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 14:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 08:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 16:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 09:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 17:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 10:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 12:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 13:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 21:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 14:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/30/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 16:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 00:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 17:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 01:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 02:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 21:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 06:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/30/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 07:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 00:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 08:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 01:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 02:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 06:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 07:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 08:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 16:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 18:00 | 42.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 01/31/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 16:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 18:00 | 42.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 01/31/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/01/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 02:00 | 39.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/01/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 07:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 08:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 02:00 | 39.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 10:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 07:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 08:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 10:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 20:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 21:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 22:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/02/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 20:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 21:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 22:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/02/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 12:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 16:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 17:00 | 56 | 0 | 0 | 0
[14 empty] | 02/03/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 18:00 | 56 | 0 | 0 | 0
[14 empty] | 02/03/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 19:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 12:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 20:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 21:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 22:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/03/2020 23:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 16:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 00:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 17:00 | 56 | 0 | 0 | 0 | [26 empty] | 02/04/2020 01:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 18:00 | 56 | 0 | 0 | 0 | [26 empty] | 02/04/2020 02:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 19:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 20:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 21:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 22:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/03/2020 23:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 00:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 08:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 01:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 09:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 02:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 14:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 15:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 08:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 16:00 | 56 | 0 | 0 | 0
[14 empty] | 02/04/2020 09:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 17:00 | 58 | 0 | 0 | 0
[14 empty] | 02/04/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 18:00 | 58 | 0 | 0 | 0
[14 empty] | 02/04/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 19:00 | 59 | 0 | 0 | 0
[14 empty] | 02/04/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 20:00 | 60 | 0 | 0 | 0
[14 empty] | 02/04/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 21:00 | 60 | 0 | 0 | 0
[14 empty] | 02/04/2020 14:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 22:00 | 58 | 0 | 0 | 0
[14 empty] | 02/04/2020 15:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/04/2020 23:00 | 58 | 0 | 0 | 0
[14 empty] | 02/04/2020 16:00 | 56 | 0 | 0 | 0 | [26 empty] | 02/05/2020 00:00 | 57 | 0 | 0 | 0
[14 empty] | 02/04/2020 17:00 | 58 | 0 | 0 | 0 | [26 empty] | 02/05/2020 01:00 | 56 | 0 | 0 | 0
[14 empty] | 02/04/2020 18:00 | 58 | 0 | 0 | 0 | [26 empty] | 02/05/2020 02:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 19:00 | 59 | 0 | 0 | 0 | [26 empty] | 02/05/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 20:00 | 60 | 0 | 0 | 0 | [26 empty] | 02/05/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 21:00 | 60 | 0 | 0 | 0 | [26 empty] | 02/05/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 22:00 | 58 | 0 | 0 | 0 | [26 empty] | 02/05/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/04/2020 23:00 | 58 | 0 | 0 | 0 | [26 empty] | 02/05/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 00:00 | 57 | 0 | 0 | 0 | [26 empty] | 02/05/2020 08:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 01:00 | 56 | 0 | 0 | 0 | [26 empty] | 02/05/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 02:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 08:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 19:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/05/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 19:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/05/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 04:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 20:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/06/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 20:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/06/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 11:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 13:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 14:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 17:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 18:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 11:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 13:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 14:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 22:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/07/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 17:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 18:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 05:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 22:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/07/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 07:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 10:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 05:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 14:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 07:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 17:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 10:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 14:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/08/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 16:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 17:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 03:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 04:00 | 33.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 05:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/08/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 07:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 08:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 03:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 11:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 04:00 | 33.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 05:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 07:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 08:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 17:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 11:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 21:00 | 39.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/09/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 17:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 21:00 | 39.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/09/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 14:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 19:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 14:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/10/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 02:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 19:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 04:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 05:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/10/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 02:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 04:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 05:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 16:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/11/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 16:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 06:00 | 39.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/11/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 06:00 | 39.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/12/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/12/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 18:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/13/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 18:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/13/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 07:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 09:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 10:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 12:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 14:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 07:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 15:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 16:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 09:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 17:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 10:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 18:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 19:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 12:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 20:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 21:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 14:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 22:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 15:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/14/2020 23:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 16:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 00:00 | 19 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 17:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 01:00 | 18 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 18:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 02:00 | 17 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 19:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 03:00 | 16 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 20:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 04:00 | 16 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 21:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 05:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 22:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 06:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/14/2020 23:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 07:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 00:00 | 19 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 08:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 01:00 | 18 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 09:00 | 17 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 02:00 | 17 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 10:00 | 19 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 03:00 | 16 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 11:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 04:00 | 16 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 12:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 05:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 13:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 06:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 14:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 07:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 15:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 08:00 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 16:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 09:00 | 17 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 17:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 10:00 | 19 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 18:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 11:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 12:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 20:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 13:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 21:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 14:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 22:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 15:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/15/2020 23:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 16:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 00:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 17:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 01:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 18:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 02:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 20:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 21:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 05:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 22:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/15/2020 23:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 07:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 00:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 01:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 02:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 11:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 05:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 07:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 11:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/16/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/16/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 10:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 11:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 10:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 18:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 11:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 20:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 21:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 22:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/17/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 18:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 20:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 21:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 22:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 06:00 | 38.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/17/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 10:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 11:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 13:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 06:00 | 38.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 10:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 18:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 11:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 13:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/18/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 18:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 02:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 03:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/18/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 02:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 03:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 13:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 11:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 13:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/19/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 00:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 05:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 06:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/19/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 07:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 00:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 08:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 09:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 10:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 11:00 | 31.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 12:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 05:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 13:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 06:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 14:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 07:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 15:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 08:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 09:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 17:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 10:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 18:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 11:00 | 31.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 12:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 13:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 21:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 14:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 15:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/20/2020 23:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 00:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 17:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 18:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 02:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 03:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 04:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 21:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 05:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 06:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/20/2020 23:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 07:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 00:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 02:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 10:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 03:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 11:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 04:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 12:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 05:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 13:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 06:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 14:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 07:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 15:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 17:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 10:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 11:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 19:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 12:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 13:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 14:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 15:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/21/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 17:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 19:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 06:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/21/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 07:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 09:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 12:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 06:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 07:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 09:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 12:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/22/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 05:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/22/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 05:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 16:00 | 56 | 0 | 0 | 0
[14 empty] | 02/23/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 17:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 19:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 21:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 22:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/23/2020 23:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 16:00 | 56 | 0 | 0 | 0 | [26 empty] | 02/24/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 17:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 01:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 19:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 03:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 21:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 22:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 06:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/23/2020 23:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 07:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 01:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 03:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 12:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 13:00 | 58 | 0 | 0 | 0
[14 empty] | 02/24/2020 06:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 14:00 | 61 | 0 | 0 | 0
[14 empty] | 02/24/2020 07:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 15:00 | 61 | 0 | 0 | 0
[14 empty] | 02/24/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 16:00 | 59 | 0 | 0 | 0
[14 empty] | 02/24/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 17:00 | 56 | 0 | 0 | 0
[14 empty] | 02/24/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 12:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/24/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 13:00 | 58 | 0 | 0 | 0 | [26 empty] | 02/24/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 14:00 | 61 | 0 | 0 | 0 | [26 empty] | 02/24/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 15:00 | 61 | 0 | 0 | 0 | [26 empty] | 02/24/2020 23:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 16:00 | 59 | 0 | 0 | 0 | [26 empty] | 02/25/2020 00:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 17:00 | 56 | 0 | 0 | 0 | [26 empty] | 02/25/2020 01:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 02:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 03:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 04:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 05:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 06:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/24/2020 23:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 00:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 01:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 09:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 02:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 10:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 03:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 04:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 12:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 05:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 06:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 09:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 17:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 10:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 12:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 20:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/25/2020 23:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 17:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 02:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 20:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/25/2020 23:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 02:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 10:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 10:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 19:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 20:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/26/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 19:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 20:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/26/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/27/2020 23:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 01:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 02:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 05:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 06:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/27/2020 23:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 07:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 08:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 01:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 02:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 10:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 05:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 06:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 07:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 08:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 17:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 10:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 20:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/28/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 17:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 19:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 20:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 04:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 05:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 06:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/28/2020 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 07:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 08:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 01:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 09:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 10:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 03:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 11:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 04:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 12:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 05:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 13:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 06:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 14:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 07:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 15:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 08:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 09:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 17:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 10:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 18:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 11:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 12:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 20:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 13:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 21:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 14:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 22:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 15:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 02/29/2020 23:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 00:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 17:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 18:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 02:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 03:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 20:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 04:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 21:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 22:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 02/29/2020 23:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 00:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 08:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 09:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 02:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 10:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 03:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 11:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 04:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 08:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 09:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 10:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 11:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 15:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/01/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/01/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 11:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 14:00 | 56 | 0 | 0 | 0
[14 empty] | 03/02/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 15:00 | 57 | 0 | 0 | 0
[14 empty] | 03/02/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 16:00 | 57 | 0 | 0 | 0
[14 empty] | 03/02/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 17:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 11:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 19:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 20:00 | 56 | 0 | 0 | 0
[14 empty] | 03/02/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/02/2020 21:00 | 56 | 0 | 0 | 0
[14 empty] | 03/02/2020 14:00 | 56 | 0 | 0 | 0 | [26 empty] | 03/02/2020 22:00 | 56 | 0 | 0 | 0
[14 empty] | 03/02/2020 15:00 | 57 | 0 | 0 | 0 | [26 empty] | 03/02/2020 23:00 | 57 | 0 | 0 | 0
[14 empty] | 03/02/2020 16:00 | 57 | 0 | 0 | 0 | [26 empty] | 03/03/2020 00:00 | 57 | 0 | 0 | 0
[14 empty] | 03/02/2020 17:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 01:00 | 56 | 0 | 0 | 0
[14 empty] | 03/02/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 02:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 19:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 03:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 20:00 | 56 | 0 | 0 | 0 | [26 empty] | 03/03/2020 04:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 21:00 | 56 | 0 | 0 | 0 | [26 empty] | 03/03/2020 05:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 22:00 | 56 | 0 | 0 | 0 | [26 empty] | 03/03/2020 06:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/02/2020 23:00 | 57 | 0 | 0 | 0 | [26 empty] | 03/03/2020 07:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 00:00 | 57 | 0 | 0 | 0 | [26 empty] | 03/03/2020 08:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 01:00 | 56 | 0 | 0 | 0 | [26 empty] | 03/03/2020 09:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 02:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 10:00 | 56 | 0 | 0 | 0
[14 empty] | 03/03/2020 03:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 11:00 | 59 | 0 | 0 | 0
[14 empty] | 03/03/2020 04:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 12:00 | 58 | 0 | 0 | 0
[14 empty] | 03/03/2020 05:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 13:00 | 57 | 0 | 0 | 0
[14 empty] | 03/03/2020 06:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 14:00 | 58 | 0 | 0 | 0
[14 empty] | 03/03/2020 07:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 15:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 08:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 16:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 09:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 10:00 | 56 | 0 | 0 | 0 | [26 empty] | 03/03/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 11:00 | 59 | 0 | 0 | 0 | [26 empty] | 03/03/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 12:00 | 58 | 0 | 0 | 0 | [26 empty] | 03/03/2020 20:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 13:00 | 57 | 0 | 0 | 0 | [26 empty] | 03/03/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 14:00 | 58 | 0 | 0 | 0 | [26 empty] | 03/03/2020 22:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 15:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/03/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 16:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 00:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 01:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 03:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 20:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 22:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/03/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 00:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 01:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 03:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 16:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 17:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 18:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 19:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 20:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 22:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/04/2020 23:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 16:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 17:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 18:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 19:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 20:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 22:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/04/2020 23:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 11:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 13:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 16:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 09:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 11:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 13:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/05/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 16:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/05/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 10:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 07:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 10:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 15:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/06/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 16:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 01:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 06:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/06/2020 23:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 07:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 08:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 01:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 06:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 07:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 08:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 19:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 15:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/07/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 03:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 19:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 04:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 06:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 07:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/07/2020 23:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 08:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 09:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 10:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 03:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 11:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 04:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 06:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 07:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 08:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 16:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/08/2020 09:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 17:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 03/08/2020 10:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 18:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/08/2020 11:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 03/08/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 20:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/08/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/08/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/08/2020 23:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 16:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/09/2020 00:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 17:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 03/09/2020 01:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 18:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/09/2020 02:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 03/09/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 20:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/09/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/09/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/08/2020 23:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/09/2020 00:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/09/2020 01:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/09/2020 02:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 10:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/09/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/09/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/09/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 13:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 03/09/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 03/09/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 03/09/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 16:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 03/09/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 17:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 03/09/2020 10:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 03/09/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 19:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 03/09/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/09/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 03/09/2020 13:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 03/09/2020 21:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 03/09/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 03/09/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/09/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 03/09/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/09/2020 16:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 03/10/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 03/09/2020 17:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 03/10/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 03/09/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 03/10/2020 02:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 03/09/2020 19:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 03/10/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/09/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 03/10/2020 04:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 03/09/2020 21:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 03/10/2020 05:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 03/09/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/10/2020 06:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/09/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/10/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 03/10/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 03/10/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 02:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 03/10/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/10/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/10/2020 04:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 03/10/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/10/2020 05:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 03/10/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 03/10/2020 06:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/10/2020 14:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/10/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/10/2020 15:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/10/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/10/2020 16:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/10/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/10/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/10/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/10/2020 18:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/10/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/10/2020 19:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/10/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/10/2020 20:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/10/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 03/10/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/10/2020 14:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/10/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/10/2020 15:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/10/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 03/10/2020 16:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/11/2020 00:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 03/10/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/11/2020 01:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/10/2020 18:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/11/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/10/2020 19:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/11/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 20:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/11/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/11/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/11/2020 06:00 EDT | 47.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/10/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 03/11/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 00:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 03/11/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 01:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/11/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/11/2020 10:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 13:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 06:00 EDT | 47.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 14:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 15:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 10:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 13:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 14:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 15:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/11/2020 23:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 01:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/11/2020 23:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 07:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 08:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 01:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 09:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 13:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 14:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 07:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 15:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 08:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 09:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 13:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 14:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 22:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 15:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/12/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 00:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 01:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 22:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 06:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/12/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 00:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 01:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 11:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 13:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 03/13/2020 06:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 14:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 03/13/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 03/13/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 03/13/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 03/13/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 03/13/2020 11:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 19:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 03/13/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/13/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/13/2020 13:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 03/13/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 03/13/2020 14:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 03/13/2020 22:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 03/13/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 03/13/2020 23:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/13/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 03/14/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/13/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 03/14/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 03/14/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 19:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 03/14/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/14/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 03/14/2020 05:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 22:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 03/14/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/13/2020 23:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/14/2020 07:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/14/2020 08:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 10:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 05:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 13:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 14:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 07:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 08:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 16:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 10:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 13:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 21:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 14:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 22:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/14/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 16:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 04:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 21:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 22:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/14/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 08:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 04:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 08:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 18:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 19:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/15/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 01:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 18:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 19:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 03:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 04:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 05:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 06:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/15/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 07:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 08:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 01:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 09:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 10:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 03:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 11:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 04:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 12:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 05:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 13:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 06:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 14:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 07:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 15:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 08:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 09:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 17:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 10:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 18:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 11:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 19:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 12:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 20:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 13:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 21:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 14:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 22:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 15:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/16/2020 23:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 00:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 17:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 18:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 19:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 20:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 21:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 22:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/16/2020 23:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 07:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 00:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 07:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 17:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 18:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/17/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 17:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 18:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/17/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 10:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 11:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 10:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 11:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/18/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 00:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/18/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 07:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 00:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 07:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 15:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 22:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 15:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/19/2020 23:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 22:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/19/2020 23:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 09:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 11:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 14:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/20/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 15:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 03/20/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 16:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 03/20/2020 09:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 17:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 03/20/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 03/20/2020 11:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 03/20/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 20:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 03/20/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/20/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 03/20/2020 14:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/20/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 03/20/2020 15:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 03/20/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 03/20/2020 16:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 03/21/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 03/20/2020 17:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 03/21/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 03/20/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 03/21/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 03/20/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 03/21/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/20/2020 20:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 03/21/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 03/21/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 03/21/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/20/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 03/21/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 03/21/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 03/21/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 03/21/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/21/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 12:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 14:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 19:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 12:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 14:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/21/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 01:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 02:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 19:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 03:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 04:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 06:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/21/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 07:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 08:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 01:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 09:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 02:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 10:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 03:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 11:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 04:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 12:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 13:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 06:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 14:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 07:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 15:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 08:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 16:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 09:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 10:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 18:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 11:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 19:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 12:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 20:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 13:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 21:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 14:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 22:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 15:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/22/2020 23:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 16:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 00:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 01:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 18:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 19:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 03:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 20:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 04:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 21:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 05:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 22:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 06:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/22/2020 23:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 07:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 00:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 08:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 01:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 09:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 10:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 03:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 11:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 04:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 12:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 05:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 13:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 06:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 14:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 07:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 15:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 08:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 16:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 09:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 17:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 10:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 18:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 11:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 19:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 12:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 20:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 13:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 21:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 14:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 22:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 15:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/23/2020 23:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 16:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 00:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 17:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 01:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 18:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 19:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 03:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 20:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 04:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 21:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 22:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 06:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/23/2020 23:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 07:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 00:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 08:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 01:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 09:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 10:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 03:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 04:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 06:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 07:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 08:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 09:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 10:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 21:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 22:00 EDT | 48.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/24/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 21:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 22:00 EDT | 48.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 06:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/24/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 07:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 13:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 06:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 14:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 07:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 15:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 16:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 17:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 19:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 20:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 13:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 21:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 14:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 15:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/25/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 16:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 00:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 17:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 19:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 03:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 20:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 04:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 21:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 05:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 06:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/25/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 00:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 09:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 03:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 04:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 05:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 06:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 14:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 15:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 16:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 03/26/2020 09:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 17:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 03/26/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 03/26/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 14:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 15:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/26/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 16:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 03/27/2020 00:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 17:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 03/27/2020 01:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 03/27/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/26/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 00:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 01:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/27/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 12:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 03/27/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 03/27/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 14:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/27/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 03/27/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 03/27/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 03/27/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/27/2020 18:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 03/27/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/27/2020 19:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 03/27/2020 12:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 03/27/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 03/27/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 03/27/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 03/27/2020 14:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/27/2020 22:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 03/27/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 03/27/2020 23:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 03/27/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 03/28/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 03/27/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 03/28/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 18:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 03/28/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 19:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 03/28/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 03/28/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 03/28/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 22:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 03/28/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/27/2020 23:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 03/28/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 03/28/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 12:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 19:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 12:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 22:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/28/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 02:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 19:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 22:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/28/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 07:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 09:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 02:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 11:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 13:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 14:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 07:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 15:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 09:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 11:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 19:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 13:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 14:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 15:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/29/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 19:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 05:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/29/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 05:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 19:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/30/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 01:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 19:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/30/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 07:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 01:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 12:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 13:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 14:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 07:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 16:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 17:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 19:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 12:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 20:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 13:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 21:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 14:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 03/31/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 16:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 17:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 01:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 19:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 20:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 21:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 03/31/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 07:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 01:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 09:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 14:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 07:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 09:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 14:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 22:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/01/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 22:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/01/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 09:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 12:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 15:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 09:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 17:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/02/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 18:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/02/2020 11:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 19:00 EDT | 55.5 | 0 | 0 | 0
[14 empty] | 04/02/2020 12:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 20:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 22:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 15:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/02/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 17:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/03/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 18:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/03/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 19:00 EDT | 55.5 | 0 | 0 | 0 | [26 empty] | 04/03/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 20:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 22:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/02/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 09:00 EDT | 46.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 09:00 EDT | 46.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 17:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 19:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 20:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/03/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 17:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 01:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 19:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 20:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/03/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 01:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 09:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 14:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 15:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/04/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 16:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/04/2020 09:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 17:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/04/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/04/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 19:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/04/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 20:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 14:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/04/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 15:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/04/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 16:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/05/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 17:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/05/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/05/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 19:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/05/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 20:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 05:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/04/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 09:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 05:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/05/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 14:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/05/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/05/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/05/2020 09:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/05/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 18:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/05/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 19:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/05/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/05/2020 20:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/05/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/05/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 14:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/05/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/05/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/06/2020 00:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/06/2020 01:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 18:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/06/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 19:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/06/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 20:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/06/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/05/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 00:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 01:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 09:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 10:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 12:00 EDT | 56.5 | 0 | 0 | 0
[14 empty] | 04/06/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 13:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/06/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 14:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/06/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/06/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 16:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/06/2020 09:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 17:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/06/2020 10:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 18:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 04/06/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/06/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/06/2020 12:00 EDT | 56.5 | 0 | 0 | 0 | [26 empty] | 04/06/2020 20:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/06/2020 13:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/06/2020 21:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/06/2020 14:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/06/2020 22:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/06/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/06/2020 23:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/06/2020 16:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/07/2020 00:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/06/2020 17:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/07/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/06/2020 18:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 04/07/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/06/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/07/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 20:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/07/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 21:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/07/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 22:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/07/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/06/2020 23:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/07/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 00:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/07/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/07/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/07/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/07/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/07/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 13:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/07/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 14:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/07/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 04/07/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 16:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/07/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 17:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/07/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/07/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/07/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/07/2020 19:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/07/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/07/2020 20:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/07/2020 13:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/07/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 14:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/07/2020 22:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/07/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 04/07/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/07/2020 16:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/08/2020 00:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/07/2020 17:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/08/2020 01:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/07/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/08/2020 02:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/07/2020 19:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/08/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/07/2020 20:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/08/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 22:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/08/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/07/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/08/2020 07:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/08/2020 00:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/08/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 01:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/08/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 02:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/08/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/08/2020 11:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 13:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/08/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 14:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/08/2020 07:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/08/2020 15:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/08/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 16:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/08/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 17:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/08/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/08/2020 11:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 19:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/08/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/08/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/08/2020 13:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/08/2020 21:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/08/2020 14:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/08/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 15:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/08/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 16:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/09/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 17:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/09/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/09/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 19:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/09/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/09/2020 04:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 21:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/09/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/08/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 08:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 10:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 04:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 12:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 14:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/09/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 15:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/09/2020 08:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 10:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 12:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/09/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 14:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/09/2020 22:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 15:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/09/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 02:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 05:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 22:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 06:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/09/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 07:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 08:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 09:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 02:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 05:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 13:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 06:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 14:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 07:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 08:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 09:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 17:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 10:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 19:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 13:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 14:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 22:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/10/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 17:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 02:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 19:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 22:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/10/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 09:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 02:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 08:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 16:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 09:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 13:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/11/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 16:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 00:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 18:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 03:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 05:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/11/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 07:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/12/2020 00:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/12/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/12/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/12/2020 03:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/12/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/12/2020 05:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 13:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/12/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 14:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/12/2020 07:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 15:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/12/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 16:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/12/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 17:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/12/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 18:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/12/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/12/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/12/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/12/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/12/2020 13:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/12/2020 21:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/12/2020 14:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/12/2020 22:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/12/2020 15:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/12/2020 23:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/12/2020 16:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 00:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/12/2020 17:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/13/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/12/2020 18:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/13/2020 02:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/12/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/13/2020 03:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/12/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/13/2020 04:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/12/2020 21:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/12/2020 22:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/13/2020 06:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/12/2020 23:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/13/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 00:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/13/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 02:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 03:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/13/2020 04:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 12:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/13/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/13/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/13/2020 06:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/13/2020 14:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/13/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/13/2020 15:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/13/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/13/2020 16:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/13/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/13/2020 17:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/13/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/13/2020 18:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/13/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/13/2020 12:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 20:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 04/13/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/13/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/13/2020 14:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/13/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/13/2020 15:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/13/2020 23:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 04/13/2020 16:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/14/2020 00:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/13/2020 17:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/14/2020 01:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/13/2020 18:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/14/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/13/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/14/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 20:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 04/14/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/14/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/14/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/13/2020 23:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 04/14/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 00:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/14/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 01:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/14/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/14/2020 10:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 14:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 15:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/14/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 16:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/14/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 17:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/14/2020 10:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/14/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 19:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/14/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 20:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 14:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/14/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 15:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/14/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 16:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/15/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 17:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/15/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/15/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 19:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/15/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 20:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/14/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 13:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 09:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 10:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 13:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 22:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/15/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 02:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 22:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/15/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 07:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 02:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 04:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 12:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 14:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 07:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 17:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 18:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 19:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 12:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 20:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 14:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 22:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/16/2020 23:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 00:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 17:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 01:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 18:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 02:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 19:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 03:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 20:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 04:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 05:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 22:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 06:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/16/2020 23:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 07:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 00:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 08:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 01:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 09:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 02:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 10:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 03:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 04:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 05:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 06:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 07:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 08:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 09:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 10:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 11:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 19:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 12:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 15:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/17/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 00:00 EDT | 43.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 02:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 19:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 03:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/17/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 00:00 EDT | 43.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 08:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 09:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 02:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 03:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 12:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 13:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 14:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 15:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 08:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 09:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 19:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 12:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 20:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 13:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 21:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 14:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 15:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/18/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 19:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 20:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 21:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/18/2020 23:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 07:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 13:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/19/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 14:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/19/2020 07:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 15:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/19/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 16:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/19/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 17:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/19/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/19/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 19:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/19/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/19/2020 20:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/19/2020 13:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/19/2020 21:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/19/2020 14:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/19/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/19/2020 15:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/19/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/19/2020 16:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/20/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/19/2020 17:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/20/2020 01:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/19/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/20/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/19/2020 19:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/20/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 20:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/20/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 21:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/20/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/20/2020 06:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/19/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/20/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/20/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 01:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/20/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/20/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 12:00 EDT | 49.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 13:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 06:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 17:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/20/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 12:00 EDT | 49.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 13:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/20/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 17:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/21/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 03:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/20/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 03:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/21/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/21/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/21/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 15:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/21/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 16:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/21/2020 19:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/21/2020 20:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/21/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/21/2020 22:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 15:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/21/2020 23:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 16:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 00:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 01:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 02:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 19:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 03:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 20:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 04:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 05:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 22:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 06:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/21/2020 23:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 07:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 00:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 08:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 01:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 09:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 02:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 10:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 03:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 11:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 04:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 05:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 13:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 06:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 14:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 07:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 15:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 08:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 09:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 17:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 10:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 11:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 13:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 14:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 15:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/22/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 17:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 20:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 21:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/22/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 07:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 04:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 13:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 06:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 07:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 15:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 11:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 19:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 12:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 20:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 13:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 15:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/23/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 19:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 20:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/23/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 08:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 01:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 09:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 03:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 11:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 04:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 06:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 08:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 16:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 09:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 17:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 11:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 12:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 20:00 EDT | 48.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/24/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 16:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 17:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 20:00 EDT | 48.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 21:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 22:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/24/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 07:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 09:00 EDT | 47.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 03:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 12:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/25/2020 05:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/25/2020 06:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 14:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/25/2020 07:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 15:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/25/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 16:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/25/2020 09:00 EDT | 47.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 17:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 04/25/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 04/25/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/25/2020 19:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/25/2020 12:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/25/2020 20:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/25/2020 21:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 14:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/25/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 15:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/25/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 16:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/26/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 17:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 04/26/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 04/26/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 19:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/26/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 20:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 04:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 21:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/25/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 04:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 05:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 14:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 17:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 19:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 20:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 13:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 21:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 14:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 22:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 15:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/26/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 17:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 01:00 EDT | 42.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 18:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 19:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 20:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 04:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 21:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 22:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 06:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/26/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 08:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 01:00 EDT | 42.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 02:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 04:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 13:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 06:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 15:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 08:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 10:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 11:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 12:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 20:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 13:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 21:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 14:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 15:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/27/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 16:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 01:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 02:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 20:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 21:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/27/2020 23:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 00:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 01:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 02:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 04:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 05:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 13:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/28/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 14:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/28/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 04/28/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 04/28/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/28/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 18:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 04/28/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 04/28/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/28/2020 20:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/28/2020 13:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/28/2020 21:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/28/2020 14:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/28/2020 22:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 04/28/2020 23:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 04/29/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/29/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 18:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 04/29/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 04/29/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 20:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 04/29/2020 04:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 21:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/29/2020 05:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 22:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/28/2020 23:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 09:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 04:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 05:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 06:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 14:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 15:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/29/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 16:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/29/2020 09:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 10:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 14:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/29/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 15:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 04/29/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 16:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/30/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 17:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 01:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 18:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 19:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/29/2020 23:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 00:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 01:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 11:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 12:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/30/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 04/30/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 14:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/30/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 15:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/30/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 16:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/30/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 17:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/30/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 18:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 04/30/2020 11:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 04/30/2020 19:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/30/2020 12:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/30/2020 20:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/30/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 04/30/2020 21:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 04/30/2020 14:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 04/30/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 04/30/2020 15:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 04/30/2020 23:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 04/30/2020 16:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/01/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 17:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/01/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 18:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/01/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 19:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/01/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 20:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/01/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 21:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/01/2020 05:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/01/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 04/30/2020 23:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/01/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 08:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 12:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/01/2020 05:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 13:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/01/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 14:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/01/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 15:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/01/2020 08:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/01/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 17:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/01/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 18:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/01/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/01/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/01/2020 12:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/01/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/01/2020 13:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/01/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/01/2020 14:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/01/2020 22:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/01/2020 15:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/01/2020 23:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/01/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/02/2020 00:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/01/2020 17:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/02/2020 01:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/01/2020 18:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/02/2020 02:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/01/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/02/2020 03:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/01/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/02/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/02/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 22:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/02/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/01/2020 23:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/02/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/02/2020 00:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/02/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/02/2020 01:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/02/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/02/2020 02:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/02/2020 10:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/02/2020 03:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/02/2020 11:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/02/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/02/2020 12:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/02/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/02/2020 13:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/02/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/02/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/02/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/02/2020 15:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/02/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/02/2020 16:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/02/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/02/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 05/02/2020 10:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/02/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 05/02/2020 11:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/02/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/02/2020 12:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/02/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/02/2020 13:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/02/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/02/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/02/2020 22:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/02/2020 15:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/02/2020 23:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/02/2020 16:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/03/2020 00:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/02/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 05/03/2020 01:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/02/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 05/03/2020 02:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/02/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/03/2020 03:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/02/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/03/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/02/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/03/2020 05:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/02/2020 22:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/03/2020 06:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/02/2020 23:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/03/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/03/2020 00:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/03/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/03/2020 01:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/03/2020 09:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/03/2020 02:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/03/2020 10:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/03/2020 03:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/03/2020 11:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/03/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/03/2020 12:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/03/2020 05:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/03/2020 13:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/03/2020 06:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/03/2020 14:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/03/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/03/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/03/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/03/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/03/2020 09:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/03/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/03/2020 10:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/03/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/03/2020 11:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/03/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/03/2020 12:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/03/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 05/03/2020 13:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/03/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/03/2020 14:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/03/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/03/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/03/2020 23:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/03/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/04/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/03/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/04/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/03/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/04/2020 02:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/03/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/04/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/03/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 05/04/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/03/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/04/2020 05:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/03/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/04/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/03/2020 23:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/04/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/04/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/04/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/04/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/04/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/04/2020 02:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/04/2020 10:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/04/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/04/2020 11:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/04/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/04/2020 12:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/04/2020 05:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/04/2020 13:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/04/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/04/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/04/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/04/2020 15:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/04/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/04/2020 16:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/04/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/04/2020 17:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/04/2020 10:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/04/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/04/2020 11:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/04/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/04/2020 12:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/04/2020 20:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/04/2020 13:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/04/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/04/2020 22:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 15:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/04/2020 23:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 16:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/05/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 17:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/05/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/05/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/05/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 20:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/05/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 22:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/04/2020 23:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 10:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 12:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 13:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/05/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 14:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/05/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 15:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/05/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 16:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/05/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 17:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/05/2020 10:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 18:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/05/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/05/2020 12:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/05/2020 20:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/05/2020 13:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/05/2020 21:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/05/2020 14:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/05/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/05/2020 15:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/05/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/05/2020 16:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/06/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/05/2020 17:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/06/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 18:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/06/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/06/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 20:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/06/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 21:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/06/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/06/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/05/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/06/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/06/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 09:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 07:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 15:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 08:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 09:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 19:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 20:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 15:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/06/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 00:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 17:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 18:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 19:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 20:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 21:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 22:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/06/2020 23:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 00:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 01:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 12:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/07/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/07/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 14:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/07/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/07/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 16:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/07/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/07/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 18:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/07/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/07/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/07/2020 12:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/07/2020 20:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/07/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/07/2020 21:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/07/2020 14:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/07/2020 22:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/07/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/07/2020 23:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/07/2020 16:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/08/2020 00:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/07/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/08/2020 01:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/07/2020 18:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/08/2020 02:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/07/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/08/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 20:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/08/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 21:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/08/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 22:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/08/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/07/2020 23:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/08/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 00:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/08/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 01:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/08/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 02:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/08/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 15:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 08:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 17:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 18:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 19:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 14:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 15:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/08/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 17:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 18:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 19:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 03:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 20:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 04:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 06:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/08/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 07:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 00:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 08:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 09:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 10:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 03:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 11:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 04:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 12:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 05:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 13:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 06:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 14:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 07:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 15:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 08:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 09:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 17:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 10:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 11:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 19:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 12:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 20:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 13:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 21:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 14:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 22:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 15:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/09/2020 23:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 16:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 00:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 17:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 18:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 19:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 20:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 04:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 21:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 22:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 06:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/09/2020 23:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 00:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 08:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 01:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 02:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 03:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 04:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 05:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/10/2020 06:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 14:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/10/2020 07:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 15:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/10/2020 08:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 16:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/10/2020 09:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 17:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/10/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/10/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/10/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/10/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/10/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/10/2020 21:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/10/2020 14:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/10/2020 22:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/10/2020 15:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/10/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/10/2020 16:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/11/2020 00:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/10/2020 17:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/11/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/11/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/11/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/11/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 21:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/11/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 22:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/11/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/10/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/11/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 00:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/11/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/11/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 14:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/11/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 15:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/11/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 16:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/11/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/11/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 19:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/11/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/11/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 14:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/11/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 15:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/11/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 16:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/12/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 17:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 01:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/12/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 19:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 04:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 06:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/11/2020 23:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 01:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 09:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 02:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 10:00 EDT | 47.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 03:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 04:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 12:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 13:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 06:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 14:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/12/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 15:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/12/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 16:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/12/2020 09:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 17:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/12/2020 10:00 EDT | 47.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/12/2020 11:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/12/2020 12:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 20:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/12/2020 13:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/12/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 14:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/12/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 15:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/12/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 16:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/13/2020 00:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 17:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/13/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/13/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/13/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 20:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/13/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/12/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 07:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 00:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 05:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/13/2020 06:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 14:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/13/2020 07:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 15:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/13/2020 08:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 16:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/13/2020 09:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 17:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/13/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/13/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/13/2020 12:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/13/2020 20:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/13/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/13/2020 21:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/13/2020 14:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/13/2020 22:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/13/2020 15:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/13/2020 23:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 16:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/14/2020 00:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 17:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/14/2020 01:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/14/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/14/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 20:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/14/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 21:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/14/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 22:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/14/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/13/2020 23:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/14/2020 00:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 08:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/14/2020 01:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/14/2020 02:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 10:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/14/2020 03:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 11:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/14/2020 04:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 12:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/14/2020 05:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 14:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/14/2020 07:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 15:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/14/2020 08:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/14/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/14/2020 17:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/14/2020 10:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/14/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 11:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/14/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 12:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/14/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/14/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/14/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 14:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/14/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 15:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/14/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/15/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/14/2020 17:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/15/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/14/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/14/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 03:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/15/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/14/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 05:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/14/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/14/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/15/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/15/2020 08:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/15/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/15/2020 09:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/15/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/15/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/15/2020 03:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/15/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/15/2020 12:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/15/2020 05:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/15/2020 13:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/15/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/15/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/15/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 08:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/15/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 09:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/15/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/15/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/15/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 12:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/15/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 13:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/15/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/15/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/15/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/15/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/15/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 01:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/15/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/15/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/15/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/15/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/15/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 06:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/15/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/16/2020 07:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/16/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/16/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/16/2020 01:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/16/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/16/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/16/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/16/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/16/2020 11:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/16/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/16/2020 12:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/16/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/16/2020 13:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/16/2020 06:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/16/2020 14:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/16/2020 07:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/16/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/16/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/16/2020 16:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/16/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/16/2020 17:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/16/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/16/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/16/2020 11:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/16/2020 19:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/16/2020 12:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/16/2020 20:00 EDT | 72.5 | 0 | 0 | 0
[14 empty] | 05/16/2020 13:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/16/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/16/2020 14:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/16/2020 22:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/16/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/16/2020 23:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/16/2020 16:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/17/2020 00:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/16/2020 17:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/17/2020 01:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/16/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/17/2020 02:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/16/2020 19:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/17/2020 03:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/16/2020 20:00 EDT | 72.5 | 0 | 0 | 0 | [26 empty] | 05/17/2020 04:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/16/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/17/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/16/2020 22:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/17/2020 06:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/16/2020 23:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/17/2020 07:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/17/2020 00:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/17/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/17/2020 01:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/17/2020 09:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/17/2020 02:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/17/2020 10:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/17/2020 03:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/17/2020 11:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/17/2020 04:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/17/2020 12:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/17/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/17/2020 13:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/17/2020 06:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/17/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/17/2020 07:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/17/2020 15:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/17/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/17/2020 16:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/17/2020 09:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/17/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/17/2020 10:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/17/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/17/2020 11:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/17/2020 19:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/17/2020 12:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/17/2020 20:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/17/2020 13:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/17/2020 21:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/17/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/17/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/17/2020 15:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/17/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/17/2020 16:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/18/2020 00:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/17/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/18/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/17/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/18/2020 02:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/17/2020 19:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/18/2020 03:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/17/2020 20:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/18/2020 04:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/17/2020 21:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/18/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/17/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/18/2020 06:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/17/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/18/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/18/2020 00:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/18/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/18/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/18/2020 09:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/18/2020 02:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/18/2020 10:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/18/2020 03:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/18/2020 11:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/18/2020 04:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/18/2020 12:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/18/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/18/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/18/2020 06:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/18/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/18/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/18/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/18/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/18/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/18/2020 09:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/18/2020 17:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/18/2020 10:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/18/2020 18:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/18/2020 11:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/18/2020 19:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/18/2020 12:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/18/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/18/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/18/2020 21:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/18/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/18/2020 22:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/18/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/18/2020 23:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/18/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/19/2020 00:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/18/2020 17:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/19/2020 01:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/18/2020 18:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/19/2020 02:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/18/2020 19:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/19/2020 03:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/18/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/19/2020 04:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/18/2020 21:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/19/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/18/2020 22:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/19/2020 06:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/18/2020 23:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/19/2020 07:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/19/2020 00:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/19/2020 08:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/19/2020 01:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/19/2020 09:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/19/2020 02:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/19/2020 10:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/19/2020 03:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/19/2020 11:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/19/2020 04:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/19/2020 12:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/19/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/19/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/19/2020 06:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/19/2020 14:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/19/2020 07:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/19/2020 15:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/19/2020 08:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/19/2020 16:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/19/2020 09:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/19/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/19/2020 10:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/19/2020 18:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/19/2020 11:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/19/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/19/2020 12:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/19/2020 20:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/19/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/19/2020 21:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/19/2020 14:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/19/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/19/2020 15:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/19/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/19/2020 16:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/20/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/20/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 18:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/20/2020 02:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/20/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 20:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/20/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 21:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/20/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/20/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/19/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/20/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 02:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/20/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 12:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/20/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 13:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/20/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 14:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/20/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 15:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/20/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/20/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/20/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/20/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/20/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/20/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/20/2020 12:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/20/2020 20:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/20/2020 13:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/20/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/20/2020 14:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/20/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 15:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/20/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/21/2020 00:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/21/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/21/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/21/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 20:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/21/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/21/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 06:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/20/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 00:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 02:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/21/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 12:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/21/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/21/2020 06:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/21/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/21/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 16:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/21/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 17:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/21/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/21/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/21/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/21/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/21/2020 12:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/21/2020 20:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/21/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/21/2020 21:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/21/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/21/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/21/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/21/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/21/2020 16:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/22/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/21/2020 17:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/22/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/22/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/22/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 20:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/22/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 21:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/22/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/22/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/21/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/22/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/22/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/22/2020 08:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/22/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 09:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/22/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/22/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/22/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/22/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 13:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/22/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 14:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/22/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/22/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/22/2020 08:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/22/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/22/2020 09:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/22/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 05/22/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/22/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/22/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/22/2020 19:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/22/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/22/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/22/2020 13:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/22/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/22/2020 14:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/22/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/22/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/22/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/22/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/23/2020 00:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/22/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 05/23/2020 01:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/22/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/23/2020 02:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/22/2020 19:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/23/2020 03:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/22/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/23/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/22/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/23/2020 05:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/22/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/23/2020 06:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/22/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/23/2020 07:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/23/2020 00:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/23/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/23/2020 01:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 09:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/23/2020 02:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 10:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/23/2020 03:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 11:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/23/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 12:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/23/2020 05:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/23/2020 06:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 14:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/23/2020 07:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 15:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/23/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 16:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/23/2020 09:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/23/2020 10:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/23/2020 11:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/23/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/23/2020 12:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/23/2020 20:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/23/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 21:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/23/2020 14:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/23/2020 22:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/23/2020 15:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/23/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/23/2020 16:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/24/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/23/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/24/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/23/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/24/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/23/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/24/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/23/2020 20:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/24/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/23/2020 21:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/24/2020 05:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/23/2020 22:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/24/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/23/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/24/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/24/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/24/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/24/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/24/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/24/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/24/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/24/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/24/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 12:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/24/2020 05:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/24/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 14:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/24/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 15:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/24/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 16:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/24/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/24/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/24/2020 18:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/24/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/24/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/24/2020 12:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/24/2020 20:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/24/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/24/2020 21:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/24/2020 14:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/24/2020 22:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/24/2020 15:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/24/2020 23:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/24/2020 16:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/25/2020 00:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/24/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/25/2020 01:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/24/2020 18:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/25/2020 02:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/24/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/25/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/24/2020 20:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/25/2020 04:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/24/2020 21:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/25/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/24/2020 22:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/25/2020 06:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/24/2020 23:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/25/2020 07:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/25/2020 00:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/25/2020 08:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/25/2020 01:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/25/2020 09:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/25/2020 02:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/25/2020 10:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/25/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/25/2020 11:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/25/2020 04:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/25/2020 12:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/25/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/25/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/25/2020 06:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/25/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/25/2020 07:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/25/2020 15:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/25/2020 08:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/25/2020 16:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/25/2020 09:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/25/2020 17:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/25/2020 10:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/25/2020 18:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/25/2020 11:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/25/2020 19:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/25/2020 12:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/25/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/25/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/25/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/25/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/25/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/25/2020 15:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/25/2020 23:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/25/2020 16:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/26/2020 00:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/25/2020 17:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/26/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/25/2020 18:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/26/2020 02:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/25/2020 19:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/26/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/25/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/26/2020 04:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/25/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/26/2020 05:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/25/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/26/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/25/2020 23:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/26/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/26/2020 00:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/26/2020 08:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/26/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/26/2020 09:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/26/2020 02:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/26/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/26/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/26/2020 11:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/26/2020 04:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/26/2020 12:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/26/2020 05:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 05/26/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/26/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/26/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/26/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/26/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/26/2020 08:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/26/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/26/2020 09:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/26/2020 17:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/26/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/26/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 05/26/2020 11:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/26/2020 19:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/26/2020 12:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/26/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/26/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/26/2020 21:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/26/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/26/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/26/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/26/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/26/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/27/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/26/2020 17:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/27/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/26/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 05/27/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/26/2020 19:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/27/2020 03:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/26/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/27/2020 04:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/26/2020 21:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/27/2020 05:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/26/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/27/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/26/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/27/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/27/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/27/2020 08:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/27/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/27/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/27/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/27/2020 10:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/27/2020 03:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/27/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/27/2020 04:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/27/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/27/2020 05:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/27/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/27/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/27/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/27/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/27/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/27/2020 08:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/27/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/27/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/27/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/27/2020 10:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/27/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/27/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/27/2020 19:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/27/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/27/2020 20:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/27/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/27/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/27/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/27/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/27/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/27/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/27/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/28/2020 00:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/27/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/28/2020 01:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/27/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/28/2020 02:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/27/2020 19:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/28/2020 03:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/27/2020 20:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/28/2020 04:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/27/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/28/2020 05:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/27/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/28/2020 06:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/27/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/28/2020 07:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/28/2020 00:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/28/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/28/2020 01:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/28/2020 09:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/28/2020 02:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/28/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/28/2020 03:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 05/28/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/28/2020 04:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/28/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/28/2020 05:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/28/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/28/2020 06:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/28/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/28/2020 07:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/28/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/28/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/28/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/28/2020 09:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/28/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 05/28/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/28/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/28/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/28/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/28/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/28/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/28/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/28/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/28/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/28/2020 22:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/28/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/28/2020 23:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/28/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/29/2020 00:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/28/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 05/29/2020 01:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 05/28/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/29/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/28/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/29/2020 03:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/28/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/29/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/28/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/29/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/28/2020 22:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/29/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/28/2020 23:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/29/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/29/2020 00:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/29/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/29/2020 01:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 05/29/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 05/29/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/29/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/29/2020 03:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/29/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/29/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/29/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/29/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/29/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 05/29/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/29/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/29/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/29/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 05/29/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/29/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/29/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/29/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/29/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 05/29/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/29/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/29/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/29/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/29/2020 23:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/29/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/30/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/29/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/30/2020 01:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/29/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/30/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/29/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/30/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/29/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/30/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/29/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/30/2020 05:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/29/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/30/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/29/2020 23:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/30/2020 07:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/30/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/30/2020 08:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/30/2020 01:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/30/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/30/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/30/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/30/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/30/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/30/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/30/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 05/30/2020 05:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/30/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 05/30/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/30/2020 14:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 05/30/2020 07:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/30/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/30/2020 08:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 05/30/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/30/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/30/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/30/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 05/30/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/30/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/30/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/30/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 05/30/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/30/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 05/30/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/30/2020 14:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 05/30/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 05/30/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/30/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 05/30/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/31/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 05/30/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/31/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 05/30/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/31/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/30/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/31/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/30/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/31/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/30/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 05/31/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/30/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 05/31/2020 06:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/30/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 05/31/2020 07:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/31/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 05/31/2020 08:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/31/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 05/31/2020 09:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/31/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/31/2020 10:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 05/31/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/31/2020 11:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 05/31/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 05/31/2020 12:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 05/31/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 05/31/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/31/2020 06:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/31/2020 14:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/31/2020 07:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 05/31/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/31/2020 08:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/31/2020 16:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 05/31/2020 09:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 05/31/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/31/2020 10:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 05/31/2020 18:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 05/31/2020 11:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 05/31/2020 19:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 05/31/2020 12:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 05/31/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 05/31/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 05/31/2020 21:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 05/31/2020 14:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/31/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 05/31/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 05/31/2020 23:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 05/31/2020 16:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/01/2020 00:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 05/31/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/01/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 05/31/2020 18:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/01/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 05/31/2020 19:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/01/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/31/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/01/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/31/2020 21:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/01/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/31/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/01/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 05/31/2020 23:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/01/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/01/2020 00:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 06/01/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/01/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 06/01/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/01/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 06/01/2020 10:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 06/01/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 11:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 06/01/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 12:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/01/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 13:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/01/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 14:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/01/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/01/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/01/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/01/2020 17:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/01/2020 10:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 06/01/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/01/2020 11:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 06/01/2020 19:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/01/2020 12:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/01/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/01/2020 13:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/01/2020 21:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/01/2020 14:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/01/2020 22:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/01/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/01/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/01/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/02/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/01/2020 17:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/02/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/01/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/02/2020 02:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/01/2020 19:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/02/2020 03:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/01/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/02/2020 04:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/01/2020 21:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/02/2020 05:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/01/2020 22:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/02/2020 06:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 06/01/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/02/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/02/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/02/2020 08:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/02/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/02/2020 09:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/02/2020 02:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/02/2020 10:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/02/2020 03:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/02/2020 11:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/02/2020 04:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/02/2020 12:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/02/2020 05:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/02/2020 13:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/02/2020 06:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 06/02/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/02/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/02/2020 15:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/02/2020 08:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/02/2020 16:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/02/2020 09:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/02/2020 17:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/02/2020 10:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/02/2020 18:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/02/2020 11:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/02/2020 19:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/02/2020 12:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/02/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/02/2020 13:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/02/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/02/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/02/2020 22:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/02/2020 15:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/02/2020 23:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/02/2020 16:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/03/2020 00:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/02/2020 17:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/03/2020 01:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/02/2020 18:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/03/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/02/2020 19:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/03/2020 03:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/02/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/03/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/02/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/03/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/02/2020 22:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/03/2020 06:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/02/2020 23:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/03/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/03/2020 00:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/03/2020 08:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/03/2020 01:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/03/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/03/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/03/2020 10:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/03/2020 03:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/03/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/03/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/03/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/03/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/03/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/03/2020 06:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/03/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/03/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/03/2020 15:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/03/2020 08:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/03/2020 16:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/03/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/03/2020 17:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/03/2020 10:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/03/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/03/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/03/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/03/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/03/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/03/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/03/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/03/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/03/2020 22:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/03/2020 15:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/03/2020 23:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/03/2020 16:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/04/2020 00:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/03/2020 17:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/04/2020 01:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/03/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/04/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/03/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/04/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/03/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/04/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/03/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/04/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/03/2020 22:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/04/2020 06:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/03/2020 23:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/04/2020 07:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/04/2020 00:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/04/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/04/2020 01:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/04/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/04/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/04/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/04/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/04/2020 11:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/04/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/04/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/04/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 06:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/04/2020 14:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 07:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/04/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/04/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/04/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/04/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 11:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/04/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/04/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/04/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/04/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/04/2020 14:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/04/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/04/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/04/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/04/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/05/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/04/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/05/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/04/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/05/2020 02:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/04/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/05/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/04/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/05/2020 04:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/04/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/05/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/04/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/05/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/04/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/05/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/05/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/05/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/05/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/05/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/05/2020 02:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/05/2020 10:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/05/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/05/2020 11:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 04:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/05/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/05/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/05/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/05/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/05/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/05/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/05/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/05/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/05/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/05/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/05/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/05/2020 10:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/05/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/05/2020 11:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/05/2020 19:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/05/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/05/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/05/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/05/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/05/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/05/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/05/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/05/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/06/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/05/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/06/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/06/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 19:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/06/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/06/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/06/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/05/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/06/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/06/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/06/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/06/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/06/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/06/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/06/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/06/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/06/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/06/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/06/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/06/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/06/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/06/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/06/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/06/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/06/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/06/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/06/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/06/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/06/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 05:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/06/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 06:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/06/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/07/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/07/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/07/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/07/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/07/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/07/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/07/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/07/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/07/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/07/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/07/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/07/2020 05:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/07/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/07/2020 06:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/07/2020 14:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/07/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/07/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/07/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/07/2020 16:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/07/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/07/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/07/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/07/2020 18:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/07/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/07/2020 19:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/07/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/07/2020 20:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/07/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/07/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/07/2020 14:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/07/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/07/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/07/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/07/2020 16:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/08/2020 00:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/07/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/08/2020 01:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/07/2020 18:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/08/2020 02:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/07/2020 19:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/08/2020 03:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/07/2020 20:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/08/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/07/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/08/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/07/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/08/2020 06:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/07/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/08/2020 07:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 06/08/2020 00:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/08/2020 08:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 06/08/2020 01:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/08/2020 09:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/08/2020 02:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/08/2020 10:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/08/2020 03:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/08/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/08/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/08/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/08/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/08/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/08/2020 06:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/08/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/08/2020 07:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 06/08/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/08/2020 08:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 06/08/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/08/2020 09:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/08/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/08/2020 10:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/08/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/08/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/08/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/08/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/08/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/08/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/08/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/08/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/08/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/08/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/08/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/08/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/09/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/08/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/08/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/08/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/09/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/08/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/08/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/09/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/08/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/09/2020 06:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/08/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/09/2020 07:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/09/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/09/2020 08:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/09/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/09/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/09/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/09/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/09/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/09/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/09/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/09/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/09/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 06:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/09/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 07:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/09/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 08:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/09/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/09/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/09/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/09/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 20:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/09/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 01:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/09/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/09/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/09/2020 20:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/09/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/09/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 06:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/09/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/10/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/10/2020 01:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/10/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/10/2020 10:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/10/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/10/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/10/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/10/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/10/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/10/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/10/2020 06:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/10/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/10/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/10/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/10/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/10/2020 16:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/10/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/10/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/10/2020 10:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/10/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/10/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/10/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/10/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/10/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/10/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/10/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/10/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/10/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/10/2020 16:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/11/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/10/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/11/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/10/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/11/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/10/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/11/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/10/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/11/2020 04:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/10/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/11/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/10/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/11/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/10/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/11/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/11/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/11/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/11/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/11/2020 09:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/11/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/11/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/11/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/11/2020 11:00 EDT | 75.5 | 0 | 0 | 0
[14 empty] | 06/11/2020 04:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/11/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/11/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/11/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/11/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/11/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/11/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/11/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/11/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/11/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/11/2020 09:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/11/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/11/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 11:00 EDT | 75.5 | 0 | 0 | 0 | [26 empty] | 06/11/2020 19:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/11/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/11/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/11/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/11/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/11/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/11/2020 22:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/11/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/12/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 19:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/12/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/11/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/12/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/11/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/12/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/11/2020 22:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/11/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/12/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/12/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/12/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/12/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/12/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/12/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/12/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/12/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/12/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/12/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/12/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/12/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/12/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/12/2020 19:00 EDT | 81.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/12/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/12/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/12/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/12/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/12/2020 23:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/12/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/12/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/12/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/12/2020 19:00 EDT | 81.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/12/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 04:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/12/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/12/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/13/2020 06:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/12/2020 23:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/13/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/13/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/13/2020 08:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/13/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/13/2020 09:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/13/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/13/2020 10:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/13/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/13/2020 11:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/13/2020 04:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/13/2020 12:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/13/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/13/2020 13:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/13/2020 06:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/13/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/13/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/13/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/13/2020 08:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/13/2020 16:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/13/2020 09:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/13/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/13/2020 10:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/13/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/13/2020 11:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/13/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/13/2020 12:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/13/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/13/2020 13:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/13/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/13/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/13/2020 22:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/13/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/13/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/13/2020 16:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/14/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/13/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/14/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/13/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/14/2020 02:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/13/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/14/2020 03:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 06/13/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/14/2020 04:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 06/13/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/14/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 06/13/2020 22:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/14/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/13/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/14/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/14/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/14/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/14/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/14/2020 09:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 06/14/2020 02:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/14/2020 10:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/14/2020 03:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 06/14/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/14/2020 04:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 06/14/2020 12:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/14/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 06/14/2020 13:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/14/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/14/2020 14:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/14/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/14/2020 15:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/14/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/14/2020 16:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/14/2020 09:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 06/14/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/14/2020 10:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/14/2020 18:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/14/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/14/2020 19:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/14/2020 12:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/14/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/14/2020 13:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/14/2020 21:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/14/2020 14:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/14/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/14/2020 15:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/14/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/14/2020 16:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/15/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/14/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/15/2020 01:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/14/2020 18:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/15/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/14/2020 19:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/15/2020 03:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/14/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/15/2020 04:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/14/2020 21:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/15/2020 05:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 06/14/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/15/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/14/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/15/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/15/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/15/2020 08:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/15/2020 01:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/15/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/15/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/15/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/15/2020 03:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/15/2020 11:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/15/2020 04:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/15/2020 12:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/15/2020 05:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 06/15/2020 13:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/15/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/15/2020 14:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/15/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/15/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/15/2020 08:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/15/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/15/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/15/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/15/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/15/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/15/2020 11:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/15/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/15/2020 12:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/15/2020 20:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/15/2020 13:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/15/2020 21:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/15/2020 14:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/15/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/15/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/15/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 06/15/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/16/2020 00:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/15/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/16/2020 01:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 06/15/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/16/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/15/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/16/2020 03:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/15/2020 20:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/16/2020 04:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/15/2020 21:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/16/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/15/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/16/2020 06:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/15/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 06/16/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 06/16/2020 00:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/16/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/16/2020 01:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 06/16/2020 09:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/16/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/16/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/16/2020 03:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/16/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/16/2020 04:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/16/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/16/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/16/2020 13:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/16/2020 06:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/16/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/16/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 06/16/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/16/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/16/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/16/2020 09:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/16/2020 17:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/16/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/16/2020 18:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/16/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/16/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/16/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/16/2020 20:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/16/2020 13:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/16/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/16/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/16/2020 22:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/16/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/16/2020 23:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/16/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/17/2020 00:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/16/2020 17:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/17/2020 01:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/16/2020 18:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/17/2020 02:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/16/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/17/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/16/2020 20:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/17/2020 04:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/16/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/17/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/16/2020 22:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/17/2020 06:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/16/2020 23:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/17/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 06/17/2020 00:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/17/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 06/17/2020 01:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/17/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 06/17/2020 02:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/17/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/17/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/17/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/17/2020 04:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/17/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/17/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/17/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/17/2020 06:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/17/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/17/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 06/17/2020 15:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/17/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 06/17/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/17/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 06/17/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/17/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/17/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/17/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/17/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/17/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/17/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/17/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/17/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/17/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/17/2020 22:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/17/2020 15:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/17/2020 23:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/17/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/18/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/17/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/18/2020 01:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/17/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/18/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/17/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/18/2020 03:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/17/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/18/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/17/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/18/2020 05:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/17/2020 22:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/18/2020 06:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/17/2020 23:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/18/2020 07:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/18/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/18/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/18/2020 01:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/18/2020 09:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/18/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 03:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/18/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/18/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/18/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/18/2020 05:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/18/2020 13:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/18/2020 06:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/18/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/18/2020 07:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/18/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/18/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/18/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/18/2020 09:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/18/2020 17:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/18/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/18/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/18/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/18/2020 19:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/18/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/18/2020 20:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/18/2020 13:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/18/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/18/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/18/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/18/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/18/2020 23:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/18/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/19/2020 00:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 17:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/19/2020 01:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/19/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 19:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/19/2020 03:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 20:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/19/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/19/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/18/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/19/2020 06:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/18/2020 23:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/19/2020 07:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/19/2020 00:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/19/2020 08:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/19/2020 01:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/19/2020 09:00 EDT | 69.5 | 0 | 0 | 0
[14 empty] | 06/19/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/19/2020 10:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/19/2020 03:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/19/2020 11:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/19/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/19/2020 12:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/19/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/19/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/19/2020 06:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/19/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/19/2020 07:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/19/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/19/2020 08:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/19/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/19/2020 09:00 EDT | 69.5 | 0 | 0 | 0 | [26 empty] | 06/19/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/19/2020 10:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/19/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/19/2020 11:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/19/2020 19:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/19/2020 12:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/19/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/19/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/19/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/19/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/19/2020 22:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/19/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/19/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/19/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/19/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 01:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/19/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/19/2020 19:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/20/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/19/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/20/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/19/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/20/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/19/2020 22:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/20/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/19/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/20/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/20/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/20/2020 08:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/20/2020 01:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/20/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/20/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/20/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/20/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/20/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/20/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/20/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/20/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/20/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/20/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 08:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/20/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/20/2020 17:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/20/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/20/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/20/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/20/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/20/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/20/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/20/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/20/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/20/2020 17:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/20/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/20/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/20/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/21/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/20/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/21/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/20/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/21/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/20/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/21/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/21/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/21/2020 08:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/21/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/21/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/21/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/21/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/21/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/21/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/21/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/21/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/21/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/21/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/21/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 08:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/21/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/21/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/21/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/21/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/21/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 22:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/21/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/21/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/21/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/21/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 01:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/21/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/21/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/21/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/21/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 05:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/21/2020 22:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/22/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/21/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/22/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/22/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/22/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/22/2020 01:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/22/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/22/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/22/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/22/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/22/2020 12:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 05:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/22/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/22/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/22/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/22/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/22/2020 17:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 12:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/22/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/22/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 00:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/22/2020 17:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/22/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 02:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/22/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/22/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 04:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/22/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/22/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 06:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/22/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 07:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/23/2020 00:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/23/2020 08:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/23/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/23/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/23/2020 02:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/23/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/23/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 04:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/23/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/23/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 06:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/23/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 07:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/23/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 08:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/23/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/23/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 20:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/23/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/23/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/23/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/23/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/23/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 01:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/23/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/23/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/23/2020 20:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/23/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/23/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/24/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/23/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/24/2020 07:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/24/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/24/2020 08:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/24/2020 01:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/24/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/24/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/24/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/24/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/24/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/24/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/24/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 07:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/24/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 08:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/24/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/24/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 22:00 EDT | 79.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/24/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/24/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/24/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/24/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/24/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/24/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/24/2020 22:00 EDT | 79.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/24/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/25/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 08:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/25/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/25/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/25/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/25/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/25/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/25/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/25/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/25/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/25/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/25/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/25/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 08:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/25/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/25/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/25/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/25/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/25/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 21:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/25/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/25/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/25/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/25/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/25/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 01:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/25/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/25/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/25/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/25/2020 21:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/26/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/25/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/26/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/25/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/26/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/26/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/26/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/26/2020 01:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/26/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/26/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/26/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/26/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/26/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/26/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/26/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/26/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/26/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/26/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/26/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/26/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/26/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/26/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/26/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/26/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/26/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 02:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/26/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/26/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/26/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/26/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/26/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/27/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/27/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/27/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/27/2020 02:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/27/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/27/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/27/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/27/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/27/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/27/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/27/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/27/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/27/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/27/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/27/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/27/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/27/2020 17:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/27/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/27/2020 18:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/27/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/27/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/27/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/27/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 22:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/27/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/27/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 17:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/28/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 18:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/28/2020 02:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/27/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/27/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/27/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/27/2020 22:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 06/28/2020 06:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/27/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 07:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/28/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 08:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/28/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/28/2020 02:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/28/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/28/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/28/2020 13:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 06:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/28/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 07:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 06/28/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 08:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/28/2020 16:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/28/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/28/2020 13:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/28/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/28/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/28/2020 23:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/28/2020 16:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/28/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/28/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/28/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/28/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/28/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/29/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/28/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/29/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/28/2020 23:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/29/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 06/29/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/29/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/29/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/29/2020 09:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/29/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/29/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/29/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/29/2020 11:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/29/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/29/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/29/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/29/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 06/29/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/29/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 09:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/29/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/29/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 11:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 06/29/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/29/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 20:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 06/29/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/29/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/29/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/29/2020 23:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/29/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/30/2020 00:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/29/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/30/2020 01:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/29/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/30/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/29/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/30/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/29/2020 20:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 06/30/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/29/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/30/2020 05:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/29/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/30/2020 06:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/29/2020 23:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/30/2020 07:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/30/2020 00:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/30/2020 08:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/30/2020 01:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/30/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/30/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/30/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/30/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/30/2020 11:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/30/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 06/30/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/30/2020 05:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/30/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/30/2020 06:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/30/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/30/2020 07:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 06/30/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/30/2020 08:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 06/30/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 06/30/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/30/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 06/30/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 06/30/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 06/30/2020 11:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 06/30/2020 19:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 06/30/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 06/30/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 06/30/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/30/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 06/30/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 06/30/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 06/30/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 06/30/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/30/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/01/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/30/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/01/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 06/30/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/01/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/30/2020 19:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/01/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 06/30/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/01/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/30/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/01/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 06/30/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/01/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 06/30/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/01/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 07/01/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/01/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/01/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/01/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/01/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/01/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/01/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/01/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/01/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 07/01/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/01/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 07/01/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/01/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 07/01/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/01/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 07/01/2020 15:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/01/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/01/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/01/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/01/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/01/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/01/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/01/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/01/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/01/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/01/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/01/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/01/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/01/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/01/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/01/2020 15:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/01/2020 23:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/01/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/02/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/01/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/02/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/01/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/02/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/01/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/02/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/01/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/02/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/01/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/02/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/01/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/02/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/01/2020 23:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/02/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/02/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/02/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/02/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 09:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/02/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/02/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/02/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/02/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/02/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 09:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/02/2020 17:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/02/2020 18:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/02/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/02/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/02/2020 21:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/02/2020 22:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/02/2020 23:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 17:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 18:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 04:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 21:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 22:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/02/2020 23:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 07:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 04:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 13:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 14:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 07:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 18:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 20:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/03/2020 13:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/03/2020 14:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 22:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/03/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/03/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/03/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/03/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/03/2020 18:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/03/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/03/2020 20:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/03/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/04/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/03/2020 22:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/04/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 07/03/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/04/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/04/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/04/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/04/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/04/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/04/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/04/2020 10:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/04/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/04/2020 11:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/04/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/04/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/04/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/04/2020 13:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 07/04/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/04/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/04/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/04/2020 17:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 10:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/04/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 11:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/04/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/04/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/04/2020 13:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 21:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/04/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/04/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/04/2020 23:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/04/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/04/2020 17:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/04/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/04/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/04/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/04/2020 21:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/05/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/04/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/05/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/04/2020 23:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/05/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/05/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/05/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/05/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/05/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/05/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/05/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/05/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/05/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/05/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/05/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/05/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/05/2020 14:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/05/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/05/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/05/2020 17:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/05/2020 18:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/05/2020 19:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 14:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/05/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 17:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 18:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 19:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/05/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 06:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/05/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 07:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/06/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 08:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/06/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 10:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 11:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 13:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 06:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/06/2020 14:00 EDT | 94 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 07:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/06/2020 15:00 EDT | 95 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 08:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/06/2020 16:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/06/2020 10:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/06/2020 11:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 19:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/06/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 13:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/06/2020 14:00 EDT | 94 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 15:00 EDT | 95 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/06/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 16:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/07/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/07/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/07/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/06/2020 19:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/07/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/07/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/06/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/07/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/07/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/07/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/07/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/07/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 11:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/07/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/07/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 14:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/07/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/07/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/07/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/07/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 11:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/07/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/07/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/07/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/07/2020 21:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/07/2020 14:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/07/2020 22:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/07/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/07/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/07/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 04:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 21:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/08/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 22:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/08/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/07/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 07:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/08/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 08:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/08/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/08/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 11:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 04:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 12:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 07:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/08/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 08:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/08/2020 16:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/08/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 11:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 19:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 12:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/08/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/08/2020 23:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/08/2020 16:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/08/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/09/2020 02:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/08/2020 19:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/09/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 04:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/08/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/08/2020 23:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/09/2020 07:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/09/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/09/2020 08:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/09/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/09/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/09/2020 02:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/09/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/09/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 04:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/09/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/09/2020 13:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/09/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 07:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/09/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 08:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/09/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/09/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 13:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/09/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/09/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/09/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/09/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 02:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/09/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 03:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/09/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 04:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/09/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/09/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/09/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/10/2020 07:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/10/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 08:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/10/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/10/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/10/2020 02:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/10/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/10/2020 03:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/10/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/10/2020 04:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/10/2020 12:00 EDT | 75.5 | 0 | 0 | 0
[14 empty] | 07/10/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/10/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 14:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/10/2020 07:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 08:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 16:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/10/2020 18:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/10/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/10/2020 19:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/10/2020 12:00 EDT | 75.5 | 0 | 0 | 0 | [26 empty] | 07/10/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/10/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/10/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 14:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/10/2020 22:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/10/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 16:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/10/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 01:00 EDT | 73.5 | 0 | 0 | 0
[14 empty] | 07/10/2020 18:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/11/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 19:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/11/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/11/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/10/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/10/2020 22:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/10/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/11/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/11/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/11/2020 01:00 EDT | 73.5 | 0 | 0 | 0 | [26 empty] | 07/11/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/11/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/11/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/11/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/11/2020 14:00 EDT | 79.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/11/2020 15:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/11/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/11/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/11/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/11/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/11/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/11/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/11/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/11/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/11/2020 14:00 EDT | 79.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/11/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/11/2020 15:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/11/2020 23:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/11/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/11/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 01:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/11/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/11/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/11/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/11/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/12/2020 05:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/11/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/12/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/11/2020 23:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/12/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/12/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/12/2020 08:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/12/2020 01:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/12/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/12/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/12/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/12/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/12/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/12/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 05:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/12/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/12/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/12/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 08:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/12/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/12/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/12/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/12/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/12/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/12/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/12/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/12/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 02:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/12/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/12/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/12/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/12/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/12/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/13/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/13/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/13/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/13/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/13/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/13/2020 02:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/13/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/13/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/13/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/13/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/13/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/13/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/13/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/13/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/13/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/13/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 20:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 22:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/13/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/13/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/13/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/13/2020 20:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/13/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/13/2020 22:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/13/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/14/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/14/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 09:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/14/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/14/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/14/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/14/2020 11:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/14/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/14/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/14/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/14/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/14/2020 15:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/14/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 09:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/14/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/14/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 11:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/14/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 15:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/14/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/14/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 00:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/14/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/14/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 02:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/14/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/14/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/14/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/14/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/14/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 00:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/15/2020 08:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/15/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/15/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/15/2020 02:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/15/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/15/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/15/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/15/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/15/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/15/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/15/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/15/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/15/2020 14:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/15/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/15/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/15/2020 08:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/15/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/15/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/15/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/15/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/15/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/15/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/15/2020 19:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/15/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/15/2020 20:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/15/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/15/2020 14:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/15/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/15/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/15/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/15/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/16/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/15/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/16/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/16/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 19:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/16/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 20:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/16/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/16/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/16/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/15/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/16/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/16/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/16/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/16/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/16/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/16/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/16/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/16/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/16/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/16/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/16/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/16/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/16/2020 17:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/16/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/16/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/16/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/16/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/16/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/16/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/16/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/16/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/16/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/16/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/17/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 17:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/17/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/16/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/17/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/16/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/17/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/16/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/17/2020 04:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 05:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/16/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/17/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/17/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/17/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 07/17/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/17/2020 10:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 07/17/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/17/2020 11:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/17/2020 04:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/17/2020 05:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/17/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 14:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/17/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/17/2020 15:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/17/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/17/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 07/17/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 10:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 07/17/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 11:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/17/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/17/2020 20:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/17/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 14:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/17/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 15:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/17/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/17/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/17/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/17/2020 20:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 04:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/17/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/17/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/17/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/18/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/18/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/18/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/18/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/18/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 04:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/18/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/18/2020 13:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/18/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/18/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/18/2020 16:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/18/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 18:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 20:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 13:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/18/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 16:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 01:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 18:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 20:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/18/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 07:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/19/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 01:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 11:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 12:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 13:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 14:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 07:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/19/2020 15:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 16:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 11:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 12:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 20:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 13:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 14:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 22:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 15:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/19/2020 23:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 16:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 00:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 01:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 02:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 03:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 20:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 04:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 05:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 22:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 06:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/19/2020 23:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 07:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 00:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 08:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 01:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 09:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 02:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 10:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 03:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 11:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 04:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 12:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 05:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 13:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 06:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 14:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 07:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 15:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 08:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 16:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 09:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 17:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 10:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 18:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 11:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 19:00 EDT | 89.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 12:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 13:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 21:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 14:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 22:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 15:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/20/2020 23:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 16:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 00:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 17:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 01:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 18:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 02:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 19:00 EDT | 89.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 04:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 21:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 22:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/20/2020 23:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 07:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 00:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 08:00 EDT | 79.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 01:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 02:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 11:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 04:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 13:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 07:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 08:00 EDT | 79.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 16:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 17:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 18:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 11:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 20:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 13:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 21:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/21/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 16:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 00:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 17:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 18:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/21/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/21/2020 20:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/21/2020 21:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/21/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 06:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/21/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 07:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/22/2020 00:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/22/2020 11:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/22/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/22/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 06:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/22/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 07:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/22/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 16:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 11:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/22/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/22/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/22/2020 14:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/22/2020 15:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/22/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/22/2020 16:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/22/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/22/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/22/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/22/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/23/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/22/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/23/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/22/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/23/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/22/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/23/2020 07:00 EDT | 73.5 | 0 | 0 | 0
[14 empty] | 07/23/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/23/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/23/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/23/2020 09:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/23/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/23/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/23/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/23/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/23/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/23/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/23/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 07:00 EDT | 73.5 | 0 | 0 | 0 | [26 empty] | 07/23/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/23/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 09:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/23/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/23/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/23/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 00:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 18:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/23/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 05:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/23/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/23/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 07:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/24/2020 00:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 08:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/24/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/24/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 10:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/24/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/24/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/24/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/24/2020 05:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/24/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/24/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/24/2020 14:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/24/2020 07:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/24/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/24/2020 08:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/24/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/24/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/24/2020 17:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/24/2020 10:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/24/2020 18:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/24/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/24/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/24/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/24/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/24/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/24/2020 21:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/24/2020 14:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/24/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/24/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/24/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/24/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/25/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/24/2020 17:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/25/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/24/2020 18:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/25/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/24/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/24/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/25/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/24/2020 21:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/25/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/24/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/25/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/24/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/25/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/25/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/25/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/25/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/25/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/25/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/25/2020 11:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 07/25/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/25/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/25/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/25/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/25/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 07/25/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 11:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/25/2020 23:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 00:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/25/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 06:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/25/2020 23:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 07:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/26/2020 00:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 08:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/26/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 09:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 11:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 05:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 13:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 06:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/26/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 07:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/26/2020 15:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 08:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/26/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 09:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 11:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 19:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 12:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 20:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 13:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 21:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 22:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 15:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/26/2020 23:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 00:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 01:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 02:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 19:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 20:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 21:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 05:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 22:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/26/2020 23:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 07:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/27/2020 00:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 01:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 02:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 11:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 12:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 05:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 13:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 14:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 07:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/27/2020 15:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 16:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 17:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 10:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 18:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 11:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 19:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 12:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 13:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 21:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 14:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 22:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 15:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/27/2020 23:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 16:00 EDT | 93 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 00:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 17:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 01:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 18:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 02:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 19:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 03:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 04:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 21:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 05:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 22:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 06:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/27/2020 23:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 07:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 00:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 08:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 01:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 09:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 02:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 10:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 03:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 11:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 04:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 12:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 05:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 13:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 06:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 14:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 07:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 15:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 08:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 16:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 09:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 10:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 11:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 12:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 20:00 EDT | 85.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 13:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 14:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 22:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 15:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/28/2020 23:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 16:00 EDT | 92 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 20:00 EDT | 85.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 22:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/28/2020 23:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 09:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 17:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 21:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 22:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/29/2020 23:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 17:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 01:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 02:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 21:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 22:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/29/2020 23:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 08:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/30/2020 01:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 02:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 03:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 13:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 14:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 15:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 08:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 07/30/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 18:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 19:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 20:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 13:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 14:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 22:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 15:00 EDT | 91 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/30/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/30/2020 18:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/30/2020 19:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/30/2020 20:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/30/2020 21:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/30/2020 22:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/30/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/31/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/31/2020 01:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 07/31/2020 09:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/31/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/31/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/31/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 11:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/31/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/31/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/31/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 14:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 07/31/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/31/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 16:00 EDT | 76.5 | 0 | 0 | 0
[14 empty] | 07/31/2020 09:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/31/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/31/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/31/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/31/2020 11:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/31/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/31/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 07/31/2020 20:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/31/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 07/31/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 07/31/2020 14:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 07/31/2020 22:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/31/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 07/31/2020 23:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 07/31/2020 16:00 EDT | 76.5 | 0 | 0 | 0 | [26 empty] | 08/01/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/31/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 07/31/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 02:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/31/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 07/31/2020 20:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 04:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 07/31/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 05:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 07/31/2020 22:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/01/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 07/31/2020 23:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/01/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/01/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/01/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/01/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/01/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/01/2020 02:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/01/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/01/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 04:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/01/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 05:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/01/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/01/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/01/2020 15:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/01/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/01/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 21:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 15:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/01/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 16:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/01/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 03:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/01/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 04:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 21:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/01/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 06:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/01/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 07:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/02/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 08:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/02/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/02/2020 09:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 03:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/02/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 04:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 06:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/02/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 07:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/02/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 08:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/02/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 09:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 12:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 20:00 EDT | 85.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 22:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 15:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/02/2020 23:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 00:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 01:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 02:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 03:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 20:00 EDT | 85.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 04:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 05:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 22:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 06:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/02/2020 23:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 07:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 00:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 01:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/03/2020 02:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 10:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/03/2020 03:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 04:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 05:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 06:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 07:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 08:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 16:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/03/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 10:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/03/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 21:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 22:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/03/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/03/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/03/2020 16:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/03/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 01:00 EDT | 72.5 | 0 | 0 | 0
[14 empty] | 08/03/2020 18:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/03/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/03/2020 20:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/03/2020 21:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 05:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/03/2020 22:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/04/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/03/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/04/2020 07:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/04/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/04/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/04/2020 01:00 EDT | 72.5 | 0 | 0 | 0 | [26 empty] | 08/04/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/04/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/04/2020 10:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/04/2020 11:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/04/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 05:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/04/2020 13:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/04/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/04/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/04/2020 07:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/04/2020 15:00 EDT | 73.5 | 0 | 0 | 0
[14 empty] | 08/04/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/04/2020 16:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/04/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/04/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/04/2020 10:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/04/2020 18:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 11:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/04/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/04/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/04/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/04/2020 13:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/04/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/04/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/04/2020 22:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 15:00 EDT | 73.5 | 0 | 0 | 0 | [26 empty] | 08/04/2020 23:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 16:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/05/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/04/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/05/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/04/2020 18:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/05/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/04/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/04/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 04:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/04/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/04/2020 22:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/05/2020 06:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/04/2020 23:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/05/2020 07:00 EDT | 74.5 | 0 | 0 | 0
[14 empty] | 08/05/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/05/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/05/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/05/2020 09:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/05/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/05/2020 10:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/05/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/05/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 04:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/05/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/05/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 06:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/05/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 07:00 EDT | 74.5 | 0 | 0 | 0 | [26 empty] | 08/05/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/05/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 09:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/05/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 10:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/05/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/05/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/05/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 00:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/05/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/05/2020 18:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/05/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/05/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/05/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/05/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/05/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 00:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/06/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/06/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/06/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/06/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/06/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/06/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/06/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/06/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/06/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/06/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/06/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/06/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/06/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/06/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/06/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/06/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/06/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/06/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/06/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/06/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/06/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/06/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/06/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/06/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/06/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/06/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/06/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/06/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/06/2020 23:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/06/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/07/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/06/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/07/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/07/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/07/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/07/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/07/2020 05:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/07/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/06/2020 23:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/07/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/07/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/07/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/07/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/07/2020 09:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/07/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/07/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/07/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/07/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/07/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/07/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/07/2020 05:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/07/2020 13:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/07/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/07/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/07/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/07/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/07/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/07/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/07/2020 09:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/07/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/07/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/07/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/07/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/07/2020 19:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/07/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/07/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/07/2020 13:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/07/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/07/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/07/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/07/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/07/2020 23:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/07/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/08/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/07/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/08/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/07/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/08/2020 02:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/07/2020 19:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/08/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/07/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/08/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/07/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/08/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/07/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/08/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/07/2020 23:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/08/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/08/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/08/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/08/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/08/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/08/2020 02:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/08/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/08/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/08/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/08/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/08/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/08/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/08/2020 13:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/08/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/08/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/08/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/08/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/08/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/08/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/08/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/08/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/08/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/08/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/08/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/08/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/08/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/08/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/08/2020 13:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/08/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/08/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/08/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/08/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/08/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/08/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/08/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/08/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/08/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/08/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/09/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/08/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/09/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/08/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/09/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/08/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/09/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/09/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/09/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/09/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/09/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/09/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/09/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/09/2020 16:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/09/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/09/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 13:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/09/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 16:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 01:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 03:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/09/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 04:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/09/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/09/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 06:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/09/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 07:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/10/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 08:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/10/2020 01:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/10/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 03:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 04:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/10/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/10/2020 13:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 06:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/10/2020 14:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 07:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/10/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 08:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/10/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/10/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 10:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 11:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 13:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 14:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 22:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/10/2020 23:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 16:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 01:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 20:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 22:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/10/2020 23:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 00:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 01:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 02:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 06:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 10:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 11:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 12:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/11/2020 23:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 16:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 03:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 22:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/11/2020 23:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 10:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 03:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 11:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 04:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 12:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 13:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 06:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 07:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 08:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 16:00 EDT | 83.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 09:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 10:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 18:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/12/2020 11:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/12/2020 12:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 20:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 13:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/12/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 16:00 EDT | 83.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 18:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/13/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/13/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 20:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/12/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/12/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 07:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 08:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 09:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/13/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 10:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/13/2020 03:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 04:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/13/2020 05:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/13/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/13/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/13/2020 07:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/13/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/13/2020 08:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/13/2020 16:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/13/2020 09:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/13/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/13/2020 10:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/13/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/13/2020 19:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/13/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/13/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/13/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/13/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/13/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/13/2020 16:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/14/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/14/2020 01:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/14/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 19:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/14/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/14/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/13/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/14/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/14/2020 06:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/13/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/14/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/14/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/14/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/14/2020 01:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/14/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/14/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/14/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/14/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/14/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/14/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 06:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/14/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/14/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/14/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/14/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/14/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 11:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/14/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/14/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 13:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/14/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 14:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/14/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/14/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/14/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 00:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/14/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/14/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 02:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/14/2020 19:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/14/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/14/2020 21:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/14/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/14/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/15/2020 00:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/15/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/15/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/15/2020 09:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/15/2020 02:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/15/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/15/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/15/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/15/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/15/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/15/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/15/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/15/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/15/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 09:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/15/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/15/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/15/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/15/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/15/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/15/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/15/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/15/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/15/2020 23:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/15/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/16/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/15/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/16/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/15/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/16/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/15/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/16/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/15/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/16/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/15/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/16/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/15/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/16/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/15/2020 23:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/16/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/16/2020 08:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/16/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/16/2020 09:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/16/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/16/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/16/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/16/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/16/2020 12:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/16/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/16/2020 13:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/16/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/16/2020 14:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/16/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 08:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/16/2020 16:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 09:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/16/2020 17:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/16/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/16/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/16/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/16/2020 19:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/16/2020 12:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/16/2020 20:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/16/2020 13:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/16/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/16/2020 14:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/16/2020 22:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/16/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/16/2020 23:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/16/2020 16:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/17/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 17:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/17/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/16/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/17/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 19:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/17/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 20:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/17/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/16/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/17/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/16/2020 22:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/17/2020 06:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/16/2020 23:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/17/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/17/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/17/2020 08:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/17/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/17/2020 09:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/17/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/17/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/17/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/17/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/17/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/17/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/17/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/17/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/17/2020 06:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/17/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/17/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/17/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/17/2020 08:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/17/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/17/2020 09:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/17/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/17/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/17/2020 18:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/17/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/17/2020 19:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/17/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/17/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/17/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/17/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/17/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/17/2020 22:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/17/2020 15:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/17/2020 23:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/17/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/18/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/17/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/18/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/17/2020 18:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/18/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/17/2020 19:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/18/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/17/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/18/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/17/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/18/2020 05:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/17/2020 22:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/18/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/17/2020 23:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/18/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/18/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/18/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/18/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/18/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/18/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/18/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/18/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/18/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/18/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/18/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/18/2020 05:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/18/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/18/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/18/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/18/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/18/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/18/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/18/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/18/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/18/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/18/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/18/2020 14:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/18/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/18/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/18/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/18/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/19/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/18/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/19/2020 01:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/18/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/19/2020 02:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/18/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/19/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/18/2020 20:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/19/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/18/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/19/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/18/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/19/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/18/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/19/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/19/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/19/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/19/2020 01:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/19/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/19/2020 02:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/19/2020 10:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/19/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/19/2020 11:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/19/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/19/2020 12:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/19/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/19/2020 13:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/19/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/19/2020 14:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/19/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/19/2020 15:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/19/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/19/2020 16:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/19/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/19/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/19/2020 10:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/19/2020 18:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/19/2020 11:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/19/2020 19:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/19/2020 12:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/19/2020 20:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/19/2020 13:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/19/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/19/2020 14:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/19/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/19/2020 15:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/19/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/19/2020 16:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/20/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/19/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/20/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/19/2020 18:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/20/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/19/2020 19:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/20/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/19/2020 20:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/20/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/19/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/20/2020 05:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/19/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/20/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/19/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/20/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/20/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/20/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 08/20/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/20/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/20/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/20/2020 10:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/20/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/20/2020 11:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/20/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/20/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/20/2020 05:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/20/2020 13:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/20/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/20/2020 14:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/20/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/20/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/20/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 08/20/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/20/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/20/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/20/2020 10:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/20/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/20/2020 11:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/20/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/20/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/20/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/20/2020 13:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/20/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/20/2020 14:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/20/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/20/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/20/2020 23:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/20/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/20/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/20/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/20/2020 19:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/20/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/21/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/20/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/21/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/20/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/21/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/20/2020 23:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/21/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/21/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/21/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/21/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/21/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/21/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/21/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/21/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/21/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/21/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 16:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/21/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/21/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/21/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/21/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/21/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/21/2020 16:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 00:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/21/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/21/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/21/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/21/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/21/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/21/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 06:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/21/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 07:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/22/2020 00:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/22/2020 08:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/22/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/22/2020 09:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/22/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/22/2020 10:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/22/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/22/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/22/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/22/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 06:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/22/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 07:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/22/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 08:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/22/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 09:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/22/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 10:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/22/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 12:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 13:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 14:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 22:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/22/2020 23:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 17:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/22/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 02:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/22/2020 19:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 03:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/22/2020 20:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/22/2020 21:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 05:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/22/2020 22:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 06:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/22/2020 23:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 07:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/23/2020 00:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 08:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/23/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/23/2020 02:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/23/2020 10:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/23/2020 03:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/23/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/23/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 05:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/23/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 06:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/23/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 07:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/23/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 08:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/23/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/23/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 10:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/23/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 11:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 12:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 21:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 14:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/23/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/23/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 03:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/23/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 04:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/23/2020 21:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/23/2020 22:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/23/2020 23:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 07:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/24/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 08:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/24/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/24/2020 02:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 03:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/24/2020 11:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 04:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/24/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/24/2020 13:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/24/2020 14:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 07:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/24/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 08:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/24/2020 16:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/24/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 11:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 12:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 20:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 13:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 14:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 15:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/24/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 16:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 17:00 EDT | 89 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 19:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 03:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/24/2020 20:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 04:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/24/2020 21:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 05:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/24/2020 22:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/24/2020 23:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 07:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/25/2020 00:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 08:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/25/2020 01:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 09:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/25/2020 02:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 03:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 11:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 04:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/25/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 05:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/25/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/25/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 07:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/25/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 08:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/25/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 09:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/25/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 10:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 11:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 19:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/25/2020 12:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/25/2020 13:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/25/2020 14:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/25/2020 15:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/25/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/25/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/26/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/25/2020 17:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/26/2020 01:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/25/2020 18:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/26/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/25/2020 19:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/26/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/25/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/26/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/25/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/26/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/25/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/26/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/25/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/26/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/26/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/26/2020 08:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/26/2020 01:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/26/2020 09:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/26/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/26/2020 10:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/26/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/26/2020 11:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/26/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/26/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/26/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/26/2020 13:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/26/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/26/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/26/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/26/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/26/2020 08:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/26/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/26/2020 09:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/26/2020 17:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/26/2020 10:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/26/2020 18:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/26/2020 11:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/26/2020 19:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/26/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/26/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/26/2020 13:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/26/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/26/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/26/2020 22:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/26/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/26/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/26/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/27/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/26/2020 17:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/27/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/26/2020 18:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/27/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/26/2020 19:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/27/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/26/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/27/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/26/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/27/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/26/2020 22:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/27/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/26/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/27/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/27/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/27/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/27/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/27/2020 09:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/27/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/27/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/27/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/27/2020 11:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/27/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/27/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/27/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/27/2020 13:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/27/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/27/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/27/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 09:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/27/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/27/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 11:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/27/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/27/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 13:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/27/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/27/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/27/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/27/2020 15:00 EDT | 86 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/27/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/27/2020 16:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/27/2020 17:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/27/2020 18:00 EDT | 87 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/27/2020 19:00 EDT | 88 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 03:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/27/2020 20:00 EDT | 90 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/27/2020 21:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/27/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/28/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/27/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/28/2020 07:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/28/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/28/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/28/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/28/2020 09:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/28/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/28/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/28/2020 03:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/28/2020 11:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/28/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/28/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/28/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/28/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/28/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 07:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/28/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/28/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 09:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/28/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/28/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 11:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/28/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/28/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/28/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/28/2020 14:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/28/2020 15:00 EDT | 85 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/28/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/28/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/29/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/28/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/29/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/28/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/29/2020 02:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/28/2020 19:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/29/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/28/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/29/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/28/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/29/2020 05:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/28/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/29/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/28/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/29/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/29/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/29/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/29/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/29/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/29/2020 02:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/29/2020 10:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/29/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/29/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/29/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/29/2020 12:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/29/2020 05:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/29/2020 13:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/29/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/29/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/29/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/29/2020 15:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/29/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/29/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/29/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 10:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/29/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/29/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 12:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/29/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 13:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/29/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/29/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 15:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/29/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 16:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/29/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 01:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/29/2020 18:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/29/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/29/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/29/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 05:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/29/2020 22:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/29/2020 23:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/30/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 08:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/30/2020 01:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/30/2020 09:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/30/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/30/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/30/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/30/2020 11:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/30/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/30/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/30/2020 05:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/30/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/30/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/30/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/30/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/30/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/30/2020 08:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/30/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/30/2020 09:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 08/30/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/30/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/30/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 08/30/2020 11:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/30/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 08/30/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/30/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/30/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/30/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 08/30/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/30/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/30/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/30/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/30/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/31/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/30/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/31/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 08/30/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 08/31/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/30/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 08/31/2020 03:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 08/30/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 08/31/2020 04:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/30/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 08/31/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/30/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 08/31/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 08/30/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/31/2020 07:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/31/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 08/31/2020 08:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 08/31/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 08/31/2020 09:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/31/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/31/2020 10:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 08/31/2020 03:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 08/31/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 08/31/2020 04:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/31/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/31/2020 13:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 08/31/2020 14:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/31/2020 07:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/31/2020 15:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 08:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 08/31/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 08/31/2020 09:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/31/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 08/31/2020 10:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 08/31/2020 18:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 08/31/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/31/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/31/2020 13:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/31/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 14:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 08/31/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 15:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 08/31/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 08/31/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/01/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/31/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/01/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/31/2020 18:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/01/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 08/31/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/01/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/31/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/01/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 08/31/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/01/2020 05:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/31/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/01/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 08/31/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/01/2020 07:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/01/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/01/2020 08:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/01/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/01/2020 09:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/01/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/01/2020 10:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/01/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/01/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/01/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/01/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/01/2020 05:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/01/2020 13:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/01/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/01/2020 14:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/01/2020 07:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/01/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/01/2020 08:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/01/2020 16:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/01/2020 09:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/01/2020 17:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/01/2020 10:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/01/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/01/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/01/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/01/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/01/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/01/2020 13:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/01/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/01/2020 14:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/01/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/01/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/01/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/01/2020 16:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/02/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/01/2020 17:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/02/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/01/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/02/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/01/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/02/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/01/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/02/2020 04:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/01/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/02/2020 05:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/01/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/02/2020 06:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/01/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/02/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/02/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/02/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/02/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/02/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/02/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/02/2020 10:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/02/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/02/2020 11:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/02/2020 04:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/02/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/02/2020 05:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/02/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/02/2020 06:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/02/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/02/2020 15:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/02/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/02/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/02/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/02/2020 10:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/02/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/02/2020 11:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/02/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/02/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/02/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/02/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/02/2020 21:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/02/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/02/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 15:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/02/2020 23:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/02/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/02/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/02/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 02:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/03/2020 03:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/03/2020 04:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 21:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/03/2020 05:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 06:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/02/2020 23:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/03/2020 07:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/03/2020 00:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 08:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/03/2020 01:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/03/2020 02:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 10:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/03/2020 03:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/03/2020 04:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/03/2020 05:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 13:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 06:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 07:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/03/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 08:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/03/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/03/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 10:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/03/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/03/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/03/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/03/2020 13:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/03/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/03/2020 15:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/03/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/03/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 00:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/03/2020 17:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 01:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/03/2020 18:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/03/2020 19:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/03/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/03/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/04/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/03/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/04/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/03/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/04/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/04/2020 00:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/04/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/04/2020 01:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/04/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/04/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/04/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/04/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/04/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/04/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/04/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/04/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/04/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/04/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/04/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/04/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/04/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/04/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 12:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 13:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/04/2020 14:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/04/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/04/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/04/2020 16:00 EDT | 84 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 00:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/04/2020 17:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/04/2020 18:00 EDT | 82 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/04/2020 19:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 03:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/04/2020 20:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 04:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/04/2020 21:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/04/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/05/2020 06:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/04/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/05/2020 07:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/05/2020 00:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/05/2020 08:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/05/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/05/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/05/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/05/2020 10:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/05/2020 03:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/05/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/05/2020 04:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/05/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/05/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/05/2020 13:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/05/2020 06:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/05/2020 14:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/05/2020 07:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/05/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/05/2020 08:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/05/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/05/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/05/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/05/2020 10:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/05/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/05/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/05/2020 19:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/05/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/05/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/05/2020 13:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/05/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/05/2020 14:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/05/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/05/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/05/2020 23:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/05/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/06/2020 00:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/05/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/06/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/05/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/06/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/05/2020 19:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/06/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/05/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/06/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/05/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/06/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/05/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/06/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/05/2020 23:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/06/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/06/2020 00:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/06/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/06/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/06/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/06/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/06/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/06/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/06/2020 11:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/06/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/06/2020 12:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/06/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/06/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/06/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/06/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/06/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/06/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/06/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/06/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/06/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/06/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/06/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/06/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/06/2020 11:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/06/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/06/2020 12:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/06/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/06/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/06/2020 21:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/06/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/06/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/06/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/06/2020 23:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/06/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/07/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/06/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/07/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/06/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/07/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/06/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/07/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/06/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/07/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/06/2020 21:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/07/2020 05:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/06/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/07/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/06/2020 23:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/07/2020 07:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/07/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/07/2020 08:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/07/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/07/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/07/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/07/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/07/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/07/2020 11:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/07/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/07/2020 12:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/07/2020 05:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/07/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/07/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/07/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/07/2020 07:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/07/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/07/2020 08:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/07/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/07/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/07/2020 17:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/07/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/07/2020 18:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/07/2020 11:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/07/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/07/2020 12:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/07/2020 20:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/07/2020 13:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/07/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/07/2020 14:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/07/2020 22:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/07/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/07/2020 23:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/07/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/08/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/07/2020 17:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/08/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/07/2020 18:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/08/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/07/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/08/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/07/2020 20:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/08/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/07/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/07/2020 22:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/07/2020 23:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/08/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 08:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/08/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/08/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/08/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/08/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/08/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/08/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/08/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/08/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/08/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/08/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 08:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/08/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/08/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/08/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/08/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/08/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/08/2020 20:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/08/2020 13:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/08/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/08/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/08/2020 22:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/08/2020 15:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/08/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/08/2020 16:00 EDT | 83 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/09/2020 00:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/08/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/09/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/08/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/09/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/08/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/09/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/08/2020 20:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/09/2020 04:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/08/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/09/2020 05:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/08/2020 22:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/09/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/08/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/09/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/09/2020 00:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/09/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/09/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/09/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/09/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/09/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/09/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/09/2020 11:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/09/2020 04:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/09/2020 12:00 EDT | 75.5 | 0 | 0 | 0
[14 empty] | 09/09/2020 05:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/09/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/09/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/09/2020 14:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/09/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/09/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/09/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/09/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/09/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/09/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/09/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/09/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/09/2020 11:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/09/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/09/2020 12:00 EDT | 75.5 | 0 | 0 | 0 | [26 empty] | 09/09/2020 20:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/09/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/09/2020 21:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/09/2020 14:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/09/2020 22:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/09/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/09/2020 23:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/09/2020 16:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/10/2020 00:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/09/2020 17:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/10/2020 01:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/09/2020 18:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/10/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/09/2020 19:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/10/2020 03:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/09/2020 20:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/10/2020 04:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/09/2020 21:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/10/2020 05:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/09/2020 22:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/10/2020 06:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/09/2020 23:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/10/2020 07:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/10/2020 00:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/10/2020 08:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/10/2020 01:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/10/2020 09:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/10/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/10/2020 10:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/10/2020 03:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/10/2020 11:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/10/2020 04:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/10/2020 12:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/10/2020 05:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/10/2020 13:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/10/2020 06:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/10/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 07:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/10/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 08:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/10/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 09:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/10/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 10:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/10/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 11:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/10/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 12:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/10/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/10/2020 13:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/10/2020 21:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/10/2020 14:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/10/2020 22:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/10/2020 15:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/10/2020 23:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/10/2020 16:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/11/2020 00:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/10/2020 17:00 EDT | 81 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/11/2020 01:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/10/2020 18:00 EDT | 80 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/11/2020 02:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/10/2020 19:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/11/2020 03:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/10/2020 20:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/11/2020 04:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/10/2020 21:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/11/2020 05:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/10/2020 22:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/11/2020 06:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/10/2020 23:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/11/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/11/2020 00:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/11/2020 08:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/11/2020 01:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/11/2020 09:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/11/2020 02:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/11/2020 10:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/11/2020 03:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/11/2020 11:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/11/2020 04:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/11/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/11/2020 05:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/11/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/11/2020 06:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/11/2020 14:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/11/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/11/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/11/2020 08:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/11/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/11/2020 09:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/11/2020 17:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/11/2020 10:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/11/2020 18:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/11/2020 11:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/11/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/11/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/11/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/11/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/11/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/11/2020 14:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/11/2020 22:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/11/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/11/2020 23:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/11/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/12/2020 00:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/11/2020 17:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/12/2020 01:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/11/2020 18:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/12/2020 02:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/11/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/12/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/11/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/12/2020 04:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/11/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/12/2020 05:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/11/2020 22:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/12/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/11/2020 23:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/12/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/12/2020 00:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/12/2020 08:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/12/2020 01:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/12/2020 09:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/12/2020 02:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/12/2020 10:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/12/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/12/2020 11:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/12/2020 04:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/12/2020 12:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/12/2020 05:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/12/2020 13:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/12/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/12/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/12/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/12/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/12/2020 08:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/12/2020 16:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/12/2020 09:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/12/2020 17:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/12/2020 10:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/12/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/12/2020 11:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/12/2020 19:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/12/2020 12:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/12/2020 20:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/12/2020 13:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/12/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/12/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/12/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/12/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/12/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/12/2020 16:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/13/2020 00:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/12/2020 17:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/13/2020 01:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/12/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/13/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/12/2020 19:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/13/2020 03:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/12/2020 20:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/13/2020 04:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/12/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/13/2020 05:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/12/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/13/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/12/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/13/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/13/2020 00:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/13/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/13/2020 01:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/13/2020 09:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/13/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/13/2020 10:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/13/2020 03:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/13/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/13/2020 04:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/13/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 05:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/13/2020 13:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/13/2020 14:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/13/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/13/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/13/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/13/2020 16:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/13/2020 09:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/13/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/13/2020 10:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/13/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/13/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/13/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/13/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/13/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 13:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/13/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/13/2020 14:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/13/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/13/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 16:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/14/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/14/2020 01:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/14/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/14/2020 03:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 04:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/13/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/14/2020 05:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/13/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 06:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/13/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/14/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 08:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/14/2020 01:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/14/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 10:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/14/2020 03:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/14/2020 04:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/14/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/14/2020 05:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/14/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/14/2020 06:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/14/2020 14:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/14/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/14/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/14/2020 08:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/14/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/14/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/14/2020 17:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/14/2020 10:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/14/2020 18:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/14/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/14/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/14/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/14/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/14/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/14/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/14/2020 14:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/14/2020 22:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/14/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/14/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/14/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/15/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/14/2020 17:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/15/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/14/2020 18:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/15/2020 02:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/14/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/15/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/14/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/15/2020 04:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/14/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/15/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/14/2020 22:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/15/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/14/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/15/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/15/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/15/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/15/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/15/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/15/2020 02:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/15/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/15/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/15/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/15/2020 04:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/15/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/15/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/15/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/15/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/15/2020 14:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/15/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/15/2020 15:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/15/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/15/2020 16:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/15/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/15/2020 17:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/15/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/15/2020 18:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/15/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/15/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/15/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/15/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/15/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/15/2020 21:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/15/2020 14:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/15/2020 22:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/15/2020 15:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/15/2020 23:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/15/2020 16:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/16/2020 00:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/15/2020 17:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/16/2020 01:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/15/2020 18:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/16/2020 02:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/15/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/16/2020 03:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/15/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/16/2020 04:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/15/2020 21:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/16/2020 05:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/15/2020 22:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/16/2020 06:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/15/2020 23:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/16/2020 07:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/16/2020 00:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/16/2020 08:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/16/2020 01:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/16/2020 09:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/16/2020 02:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/16/2020 10:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/16/2020 03:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/16/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/16/2020 04:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/16/2020 12:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/16/2020 05:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/16/2020 13:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/16/2020 06:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/16/2020 14:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/16/2020 07:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/16/2020 15:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/16/2020 08:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/16/2020 16:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/16/2020 09:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/16/2020 17:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/16/2020 10:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/16/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/16/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/16/2020 19:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/16/2020 12:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/16/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/16/2020 13:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/16/2020 21:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 14:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/16/2020 22:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 15:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/16/2020 23:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 16:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/17/2020 00:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 17:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/17/2020 01:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/17/2020 02:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 19:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/17/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/16/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/17/2020 04:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/16/2020 21:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/16/2020 22:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 06:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/16/2020 23:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 07:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/17/2020 00:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 08:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/17/2020 01:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/17/2020 02:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/17/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/17/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/17/2020 04:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/17/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/17/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/17/2020 13:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/17/2020 06:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/17/2020 14:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/17/2020 07:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/17/2020 15:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/17/2020 08:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/17/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/17/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/17/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/17/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/17/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/17/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/17/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/17/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/17/2020 20:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/17/2020 13:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/17/2020 21:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/17/2020 14:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/17/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/17/2020 15:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/17/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/17/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/18/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/17/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/18/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/17/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/18/2020 02:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/17/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/18/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/17/2020 20:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/18/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/17/2020 21:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/18/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/17/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/18/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/17/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/18/2020 07:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/18/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/18/2020 08:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/18/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/18/2020 09:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/18/2020 02:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/18/2020 10:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/18/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/18/2020 11:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/18/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/18/2020 12:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/18/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/18/2020 13:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/18/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/18/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/18/2020 07:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/18/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/18/2020 08:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/18/2020 16:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/18/2020 09:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/18/2020 17:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/18/2020 10:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/18/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/18/2020 11:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/18/2020 19:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/18/2020 12:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/18/2020 20:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/18/2020 13:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/18/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/18/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/18/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/18/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/18/2020 23:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/18/2020 16:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/19/2020 00:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/18/2020 17:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/19/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/18/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/19/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/18/2020 19:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/19/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/18/2020 20:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/19/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/18/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/19/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/18/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/19/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/18/2020 23:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/19/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 00:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/19/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/19/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 12:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/19/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 13:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/19/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 14:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/19/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/19/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 16:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/19/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 17:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/19/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 18:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/19/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/19/2020 19:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/19/2020 12:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/19/2020 20:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/19/2020 13:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/19/2020 21:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/19/2020 14:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/19/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/19/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/19/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/19/2020 16:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/20/2020 00:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/19/2020 17:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/20/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 18:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/20/2020 02:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 19:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/20/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 20:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/20/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 21:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/20/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/20/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/19/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/20/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 00:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/20/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 02:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 03:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/20/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 12:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/20/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 13:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/20/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 14:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/20/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 15:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/20/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 16:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/20/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 17:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/20/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/20/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/20/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/20/2020 19:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/20/2020 12:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/20/2020 20:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/20/2020 13:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/20/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/20/2020 14:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/20/2020 22:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/20/2020 15:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/20/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/20/2020 16:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/21/2020 00:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 17:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/21/2020 01:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/20/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/21/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 19:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/21/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 20:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/21/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/21/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 22:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/21/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/20/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/21/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 00:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 08:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 01:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/21/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/21/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/21/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/21/2020 06:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 14:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/21/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/21/2020 08:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/21/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 17:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/21/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/21/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/21/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/21/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/21/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/21/2020 20:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/21/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/21/2020 21:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/21/2020 14:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/21/2020 22:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/21/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/21/2020 23:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/21/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/22/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 09/21/2020 17:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/22/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/22/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/22/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 20:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/22/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 21:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/22/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 22:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/22/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/21/2020 23:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/22/2020 07:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/22/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 09/22/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/22/2020 01:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 09:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/22/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/22/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 09/22/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 12:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/22/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/22/2020 06:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/22/2020 07:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 15:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/22/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 16:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/22/2020 09:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 17:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/22/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/22/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/22/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 09/22/2020 19:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/22/2020 12:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/22/2020 20:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/22/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/22/2020 21:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/22/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/22/2020 22:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/22/2020 15:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/22/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/22/2020 16:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/23/2020 00:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/22/2020 17:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/23/2020 01:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/22/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/23/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/22/2020 19:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/23/2020 03:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/22/2020 20:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/23/2020 04:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/22/2020 21:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/23/2020 05:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 09/22/2020 22:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/23/2020 06:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/22/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/23/2020 07:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/23/2020 00:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/23/2020 08:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 09/23/2020 01:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/23/2020 09:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/23/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 09/23/2020 10:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/23/2020 03:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/23/2020 11:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/23/2020 04:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/23/2020 12:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/23/2020 05:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 09/23/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/23/2020 06:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/23/2020 14:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/23/2020 07:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/23/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/23/2020 08:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 09/23/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/23/2020 09:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/23/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/23/2020 10:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/23/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/23/2020 11:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/23/2020 19:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/23/2020 12:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/23/2020 20:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/23/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/23/2020 21:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/23/2020 14:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/23/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/23/2020 15:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/23/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/23/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/24/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/23/2020 17:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/24/2020 01:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/23/2020 18:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/24/2020 02:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/23/2020 19:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/24/2020 03:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/23/2020 20:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/24/2020 04:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/23/2020 21:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/24/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/23/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/24/2020 06:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/23/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/24/2020 07:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/24/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/24/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/24/2020 01:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/24/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/24/2020 02:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/24/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/24/2020 03:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/24/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/24/2020 04:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/24/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/24/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/24/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/24/2020 06:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 09/24/2020 14:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/24/2020 07:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/24/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/24/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/24/2020 16:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/24/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/24/2020 17:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/24/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/24/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/24/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/24/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/24/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/24/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/24/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/24/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/24/2020 14:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/24/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/24/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/24/2020 23:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/24/2020 16:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/25/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/24/2020 17:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/25/2020 01:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/24/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/25/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/24/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/25/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/24/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/25/2020 04:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/24/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/25/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/24/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/25/2020 06:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/24/2020 23:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/25/2020 07:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/25/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/25/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/25/2020 01:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/25/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/25/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/25/2020 10:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/25/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/25/2020 11:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/25/2020 04:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/25/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/25/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/25/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/25/2020 06:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/25/2020 14:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/25/2020 07:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/25/2020 15:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/25/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/25/2020 16:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/25/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/25/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/25/2020 10:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/25/2020 18:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/25/2020 11:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/25/2020 19:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/25/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/25/2020 20:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/25/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/25/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/25/2020 14:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/25/2020 22:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/25/2020 15:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/25/2020 23:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/25/2020 16:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/26/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/25/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/26/2020 01:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/25/2020 18:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/26/2020 02:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/25/2020 19:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/26/2020 03:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/25/2020 20:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/26/2020 04:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/25/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/26/2020 05:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/25/2020 22:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/26/2020 06:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/25/2020 23:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/26/2020 07:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/26/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/26/2020 08:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/26/2020 01:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/26/2020 09:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/26/2020 02:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/26/2020 10:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/26/2020 03:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/26/2020 11:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/26/2020 04:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/26/2020 12:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/26/2020 05:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/26/2020 13:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/26/2020 06:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/26/2020 14:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/26/2020 07:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 09/26/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/26/2020 08:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/26/2020 16:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/26/2020 09:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/26/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/26/2020 10:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/26/2020 18:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/26/2020 11:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/26/2020 19:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/26/2020 12:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/26/2020 20:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/26/2020 13:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/26/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/26/2020 14:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/26/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/26/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/26/2020 23:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/26/2020 16:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/27/2020 00:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/26/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/27/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/26/2020 18:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/27/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/26/2020 19:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/27/2020 03:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/26/2020 20:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/27/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/26/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/27/2020 05:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/26/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/27/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/26/2020 23:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/27/2020 07:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/27/2020 00:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/27/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/27/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 10:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/27/2020 03:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 11:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/27/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/27/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/27/2020 05:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 09/27/2020 13:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/27/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/27/2020 14:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/27/2020 07:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/27/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/27/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/27/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 09/27/2020 10:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/27/2020 18:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/27/2020 11:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/27/2020 19:00 EDT | 75 | 0 | 0 | 0
[14 empty] | 09/27/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/27/2020 20:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/27/2020 13:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/27/2020 21:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/27/2020 14:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/27/2020 22:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/27/2020 15:00 EDT | 79 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/27/2020 23:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/27/2020 16:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/28/2020 00:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/27/2020 17:00 EDT | 78 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 09/28/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/27/2020 18:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/28/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/27/2020 19:00 EDT | 75 | 0 | 0 | 0 | [26 empty] | 09/28/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/27/2020 20:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/28/2020 04:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/27/2020 21:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/28/2020 05:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/27/2020 22:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/28/2020 06:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/27/2020 23:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/28/2020 07:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/28/2020 00:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/28/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/28/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/28/2020 09:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/28/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/28/2020 10:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/28/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/28/2020 11:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/28/2020 04:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/28/2020 12:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/28/2020 05:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/28/2020 13:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/28/2020 06:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/28/2020 14:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/28/2020 07:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/28/2020 15:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/28/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/28/2020 16:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/28/2020 09:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/28/2020 17:00 EDT | 77 | 0 | 0 | 0
[14 empty] | 09/28/2020 10:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/28/2020 18:00 EDT | 76 | 0 | 0 | 0
[14 empty] | 09/28/2020 11:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/28/2020 19:00 EDT | 74 | 0 | 0 | 0
[14 empty] | 09/28/2020 12:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/28/2020 20:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/28/2020 13:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/28/2020 21:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/28/2020 14:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/28/2020 22:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/28/2020 15:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/28/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/28/2020 16:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/29/2020 00:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/28/2020 17:00 EDT | 77 | 0 | 0 | 0 | [26 empty] | 09/29/2020 01:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/28/2020 18:00 EDT | 76 | 0 | 0 | 0 | [26 empty] | 09/29/2020 02:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/28/2020 19:00 EDT | 74 | 0 | 0 | 0 | [26 empty] | 09/29/2020 03:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/28/2020 20:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/29/2020 04:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/28/2020 21:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/29/2020 05:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/28/2020 22:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/29/2020 06:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/28/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/29/2020 07:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/29/2020 00:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/29/2020 08:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/29/2020 01:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/29/2020 09:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/29/2020 02:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/29/2020 10:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/29/2020 03:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/29/2020 11:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/29/2020 04:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/29/2020 12:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/29/2020 05:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/29/2020 13:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/29/2020 06:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/29/2020 14:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/29/2020 07:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/29/2020 15:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/29/2020 08:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/29/2020 16:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 09/29/2020 09:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/29/2020 17:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 09/29/2020 10:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/29/2020 18:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/29/2020 11:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/29/2020 19:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/29/2020 12:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/29/2020 20:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/29/2020 13:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/29/2020 21:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/29/2020 14:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/29/2020 22:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/29/2020 15:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/29/2020 23:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/29/2020 16:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 09/30/2020 00:00 EDT | 70.5 | 0 | 0 | 0
[14 empty] | 09/29/2020 17:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 09/30/2020 01:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/29/2020 18:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/30/2020 02:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/29/2020 19:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/30/2020 03:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 09/29/2020 20:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/30/2020 04:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 09/29/2020 21:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/30/2020 05:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 09/29/2020 22:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/30/2020 06:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/29/2020 23:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/30/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/30/2020 00:00 EDT | 70.5 | 0 | 0 | 0 | [26 empty] | 09/30/2020 08:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/30/2020 01:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/30/2020 09:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/30/2020 02:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/30/2020 10:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/30/2020 03:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 09/30/2020 11:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/30/2020 04:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 09/30/2020 12:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/30/2020 05:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 09/30/2020 13:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/30/2020 06:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/30/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/30/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/30/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/30/2020 08:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/30/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/30/2020 09:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/30/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/30/2020 10:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/30/2020 18:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 09/30/2020 11:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 09/30/2020 19:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 09/30/2020 12:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 09/30/2020 20:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 09/30/2020 13:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 09/30/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/30/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 09/30/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 09/30/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 09/30/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 09/30/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/01/2020 00:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/30/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/01/2020 01:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 09/30/2020 18:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/01/2020 02:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 09/30/2020 19:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/01/2020 03:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/30/2020 20:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/01/2020 04:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/30/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/01/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 09/30/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/01/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 09/30/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/01/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/01/2020 00:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/01/2020 08:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/01/2020 01:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/01/2020 09:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/01/2020 02:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/01/2020 10:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/01/2020 03:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/01/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/01/2020 04:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/01/2020 12:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/01/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/01/2020 13:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/01/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/01/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/01/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/01/2020 15:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/01/2020 08:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/01/2020 16:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/01/2020 09:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/01/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/01/2020 10:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/01/2020 18:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/01/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/01/2020 19:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/01/2020 12:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/01/2020 20:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/01/2020 13:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/01/2020 21:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/01/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/01/2020 22:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/01/2020 15:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/01/2020 23:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/01/2020 16:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/02/2020 00:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/01/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/02/2020 01:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/01/2020 18:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/02/2020 02:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/01/2020 19:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/02/2020 03:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/01/2020 20:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/02/2020 04:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/01/2020 21:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/02/2020 05:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/01/2020 22:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/02/2020 06:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/01/2020 23:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/02/2020 07:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/02/2020 00:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/02/2020 08:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/02/2020 01:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/02/2020 09:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/02/2020 02:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/02/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 03:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/02/2020 11:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/02/2020 04:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/02/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 05:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/02/2020 13:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/02/2020 06:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/02/2020 14:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/02/2020 07:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/02/2020 15:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/02/2020 08:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/02/2020 16:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/02/2020 09:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/02/2020 17:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/02/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/02/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/02/2020 11:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/02/2020 19:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/02/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/02/2020 20:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/02/2020 13:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/02/2020 21:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/02/2020 14:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/02/2020 22:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/02/2020 15:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/02/2020 23:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/02/2020 16:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/03/2020 00:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/02/2020 17:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/03/2020 01:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/02/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/03/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 19:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/03/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 20:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/03/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 21:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/03/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 22:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/03/2020 06:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/02/2020 23:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/03/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 00:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/03/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 01:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/03/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/03/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/03/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/03/2020 06:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 14:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/03/2020 07:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 15:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/03/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 16:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/03/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/03/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/03/2020 18:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/03/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/03/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/03/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/03/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/03/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/03/2020 21:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/03/2020 14:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/03/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/03/2020 15:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/03/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/03/2020 16:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/04/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/03/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/04/2020 01:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/03/2020 18:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/04/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/03/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/04/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/04/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 21:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/04/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/04/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/03/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/04/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/04/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/04/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/04/2020 01:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/04/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/04/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/04/2020 10:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/04/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 11:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/04/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 12:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/04/2020 05:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 13:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/04/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/04/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 15:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/04/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 16:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/04/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/04/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/04/2020 10:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/04/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/04/2020 11:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/04/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/04/2020 12:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/04/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/04/2020 13:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/04/2020 21:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/04/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/04/2020 22:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/04/2020 15:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/04/2020 23:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/04/2020 16:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/05/2020 00:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/04/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/05/2020 01:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/04/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/05/2020 02:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/04/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/05/2020 03:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/04/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/05/2020 04:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/04/2020 21:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/05/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/04/2020 22:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/05/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/04/2020 23:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/05/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/05/2020 00:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/05/2020 08:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/05/2020 01:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/05/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/05/2020 02:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/05/2020 10:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/05/2020 03:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/05/2020 11:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/05/2020 04:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/05/2020 12:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/05/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/05/2020 13:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/05/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/05/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/05/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/05/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/05/2020 08:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/05/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/05/2020 09:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/05/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/05/2020 10:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/05/2020 18:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/05/2020 11:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/05/2020 19:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/05/2020 12:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/05/2020 20:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/05/2020 13:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/05/2020 21:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/05/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/05/2020 22:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/05/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/05/2020 23:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/05/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/06/2020 00:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/05/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/06/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/05/2020 18:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/06/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/05/2020 19:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/06/2020 03:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/05/2020 20:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/06/2020 04:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/05/2020 21:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/06/2020 05:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/05/2020 22:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/06/2020 06:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/05/2020 23:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/06/2020 07:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/06/2020 00:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/06/2020 08:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/06/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/06/2020 09:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/06/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/06/2020 10:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/06/2020 03:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/06/2020 11:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/06/2020 04:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/06/2020 12:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/06/2020 05:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/06/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/06/2020 06:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/06/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/06/2020 07:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/06/2020 15:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/06/2020 08:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/06/2020 16:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/06/2020 09:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/06/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/06/2020 10:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/06/2020 18:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/06/2020 11:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/06/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/06/2020 12:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/06/2020 20:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/06/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/06/2020 21:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/06/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/06/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/06/2020 15:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/06/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/06/2020 16:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/07/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/06/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/07/2020 01:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/06/2020 18:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/07/2020 02:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/06/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/07/2020 03:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/06/2020 20:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/07/2020 04:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/06/2020 21:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/07/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/06/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/07/2020 06:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/06/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/07/2020 07:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/07/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/07/2020 08:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/07/2020 01:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 09:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/07/2020 02:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/07/2020 10:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/07/2020 03:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/07/2020 11:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/07/2020 04:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 12:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/07/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 13:00 EDT | 71 | 0 | 0 | 0
[14 empty] | 10/07/2020 06:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 14:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 10/07/2020 07:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 15:00 EDT | 72 | 0 | 0 | 0
[14 empty] | 10/07/2020 08:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 16:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 10/07/2020 09:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/07/2020 17:00 EDT | 73 | 0 | 0 | 0
[14 empty] | 10/07/2020 10:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/07/2020 18:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/07/2020 11:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/07/2020 19:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/07/2020 12:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/07/2020 20:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/07/2020 13:00 EDT | 71 | 0 | 0 | 0 | [26 empty] | 10/07/2020 21:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/07/2020 14:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 10/07/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/07/2020 15:00 EDT | 72 | 0 | 0 | 0 | [26 empty] | 10/07/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/07/2020 16:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 10/08/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/07/2020 17:00 EDT | 73 | 0 | 0 | 0 | [26 empty] | 10/08/2020 01:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/07/2020 18:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/08/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/07/2020 19:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/08/2020 03:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/07/2020 20:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/08/2020 04:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/07/2020 21:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/08/2020 05:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/07/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/08/2020 06:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/07/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/08/2020 07:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/08/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/08/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 01:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/08/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/08/2020 10:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/08/2020 03:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/08/2020 11:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/08/2020 04:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/08/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/08/2020 05:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/08/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/08/2020 06:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/08/2020 14:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/08/2020 07:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/08/2020 15:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/08/2020 08:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/08/2020 16:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/08/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/08/2020 17:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/08/2020 10:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/08/2020 18:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/08/2020 11:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/08/2020 19:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/08/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/08/2020 20:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/08/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/08/2020 21:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/08/2020 14:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/08/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/08/2020 15:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/08/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/08/2020 16:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/09/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 17:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/09/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 18:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/09/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 19:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/09/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 20:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/09/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 21:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/09/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/09/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/08/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/09/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/09/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/09/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/09/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/09/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 11:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/09/2020 04:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 12:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/09/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 13:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/09/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 14:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/09/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 15:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/09/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 16:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/09/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/09/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/09/2020 18:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/09/2020 11:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/09/2020 19:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/09/2020 12:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/09/2020 20:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/09/2020 13:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/09/2020 21:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/09/2020 14:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/09/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/09/2020 15:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/09/2020 23:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/09/2020 16:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/10/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/09/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/10/2020 01:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/09/2020 18:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/10/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/09/2020 19:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/10/2020 03:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/09/2020 20:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/10/2020 04:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/09/2020 21:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/10/2020 05:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/09/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/10/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/09/2020 23:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/10/2020 07:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/10/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/10/2020 08:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/10/2020 01:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/10/2020 09:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/10/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/10/2020 10:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/10/2020 03:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/10/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/10/2020 04:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/10/2020 12:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/10/2020 05:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/10/2020 13:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/10/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/10/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/10/2020 07:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/10/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/10/2020 08:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/10/2020 16:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/10/2020 09:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/10/2020 17:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/10/2020 10:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/10/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/10/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/10/2020 19:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/10/2020 12:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/10/2020 20:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/10/2020 13:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/10/2020 21:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/10/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/10/2020 22:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/10/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/10/2020 23:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/10/2020 16:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/11/2020 00:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/10/2020 17:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/11/2020 01:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/10/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/11/2020 02:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/10/2020 19:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/11/2020 03:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/10/2020 20:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/11/2020 04:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/10/2020 21:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/11/2020 05:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/10/2020 22:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/11/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/10/2020 23:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/11/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/11/2020 00:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/11/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/11/2020 01:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/11/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/11/2020 02:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/11/2020 10:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/11/2020 03:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/11/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/11/2020 04:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/11/2020 12:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/11/2020 05:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/11/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/11/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/11/2020 14:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/11/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/11/2020 15:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/11/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/11/2020 16:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/11/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/11/2020 17:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/11/2020 10:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/11/2020 18:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/11/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/11/2020 19:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/11/2020 12:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/11/2020 20:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/11/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/11/2020 21:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/11/2020 14:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/11/2020 22:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/11/2020 15:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/11/2020 23:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/11/2020 16:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/12/2020 00:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/11/2020 17:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/12/2020 01:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/11/2020 18:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/12/2020 02:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/11/2020 19:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/12/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/11/2020 20:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/12/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/11/2020 21:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/12/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/11/2020 22:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/12/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/11/2020 23:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/12/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 00:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/12/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 01:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/12/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 02:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/12/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 08:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 09:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 11:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 20:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 13:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/12/2020 23:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 01:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/12/2020 18:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 19:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 20:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 21:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 22:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/12/2020 23:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 07:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 08:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 01:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/13/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 12:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 13:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 06:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 14:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/13/2020 07:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 15:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 08:00 EDT | 54.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 16:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/13/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 17:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 10:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 18:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/13/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/13/2020 19:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 12:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/13/2020 20:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 13:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/13/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/13/2020 14:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/13/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 15:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/13/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 16:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/14/2020 00:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/13/2020 17:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/14/2020 01:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/13/2020 18:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/14/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 19:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/14/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 20:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/14/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/14/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/14/2020 06:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/13/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/14/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/14/2020 00:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/14/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/14/2020 01:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/14/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/14/2020 02:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/14/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/14/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 12:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/14/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/14/2020 06:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 14:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/14/2020 07:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 15:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/14/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/14/2020 09:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/14/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 18:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/14/2020 11:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/14/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/14/2020 12:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/14/2020 20:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/14/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/14/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/14/2020 14:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/14/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/14/2020 15:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/14/2020 23:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/14/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/15/2020 00:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/14/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/15/2020 01:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/14/2020 18:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/15/2020 02:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/14/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/15/2020 03:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/14/2020 20:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/15/2020 04:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/14/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/15/2020 05:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/14/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/15/2020 06:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/14/2020 23:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/15/2020 07:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/15/2020 00:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/15/2020 08:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/15/2020 01:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/15/2020 09:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/15/2020 02:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/15/2020 10:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/15/2020 03:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/15/2020 11:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/15/2020 04:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/15/2020 12:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/15/2020 05:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/15/2020 13:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/15/2020 06:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/15/2020 14:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/15/2020 07:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/15/2020 15:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/15/2020 08:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/15/2020 16:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/15/2020 09:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/15/2020 17:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/15/2020 10:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/15/2020 18:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/15/2020 11:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/15/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 12:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/15/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 13:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/15/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/15/2020 14:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/15/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/15/2020 15:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/15/2020 23:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 16:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/16/2020 00:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/15/2020 17:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/16/2020 01:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 18:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/16/2020 02:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 04:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/15/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/16/2020 05:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/16/2020 06:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/15/2020 23:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 07:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/16/2020 00:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/16/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/16/2020 01:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 09:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/16/2020 02:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 10:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/16/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 11:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/16/2020 04:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/16/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 05:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 06:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/16/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 07:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/16/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/16/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 09:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/16/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 10:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/16/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 11:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/16/2020 19:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/16/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/16/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/16/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/16/2020 23:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 16:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 17:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 01:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 18:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 19:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 20:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/16/2020 23:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 01:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 09:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 02:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 11:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 12:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 13:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 14:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/17/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 15:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/17/2020 08:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 16:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/17/2020 09:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 17:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/17/2020 10:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/17/2020 11:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/17/2020 12:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 13:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/17/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 14:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/17/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 15:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/17/2020 23:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 16:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/18/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 17:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/18/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/18/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/18/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 20:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 21:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 05:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 22:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/17/2020 23:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 01:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 03:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 04:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 12:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/18/2020 05:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 13:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/18/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 14:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/18/2020 07:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 15:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/18/2020 08:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 16:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/18/2020 09:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 17:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/18/2020 10:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 18:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/18/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/18/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/18/2020 12:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/18/2020 20:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/18/2020 13:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/18/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/18/2020 14:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/18/2020 22:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/18/2020 15:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/18/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/18/2020 16:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/19/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 17:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/19/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 18:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/19/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/19/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 20:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/19/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/19/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 22:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/19/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/18/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/19/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/19/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/19/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/19/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 10:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/19/2020 03:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 11:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/19/2020 04:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 12:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/19/2020 05:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 13:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/19/2020 06:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 14:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/19/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 15:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/19/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 16:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/19/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/19/2020 17:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/19/2020 10:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/19/2020 18:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/19/2020 11:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/19/2020 19:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/19/2020 12:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/19/2020 20:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/19/2020 13:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/19/2020 21:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/19/2020 14:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/19/2020 22:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/19/2020 15:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/19/2020 23:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/19/2020 16:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/20/2020 00:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/19/2020 17:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/20/2020 01:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/19/2020 18:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/20/2020 02:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/19/2020 19:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/20/2020 03:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/19/2020 20:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/20/2020 04:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/19/2020 21:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/20/2020 05:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/19/2020 22:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/20/2020 06:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/19/2020 23:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/20/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/20/2020 00:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/20/2020 08:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/20/2020 01:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/20/2020 09:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/20/2020 02:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/20/2020 10:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/20/2020 03:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/20/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/20/2020 04:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/20/2020 12:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/20/2020 05:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/20/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/20/2020 06:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/20/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/20/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/20/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/20/2020 08:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/20/2020 16:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/20/2020 09:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/20/2020 17:00 EDT | 70 | 0 | 0 | 0
[14 empty] | 10/20/2020 10:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/20/2020 18:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/20/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/20/2020 19:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/20/2020 12:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/20/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/20/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/20/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/20/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/20/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/20/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/20/2020 23:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/20/2020 16:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/21/2020 00:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/20/2020 17:00 EDT | 70 | 0 | 0 | 0 | [26 empty] | 10/21/2020 01:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/20/2020 18:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/21/2020 02:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/20/2020 19:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/21/2020 03:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/20/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/21/2020 04:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/20/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/21/2020 05:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/20/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/21/2020 06:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/20/2020 23:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/21/2020 07:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/21/2020 00:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/21/2020 08:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/21/2020 01:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/21/2020 09:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/21/2020 02:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/21/2020 10:00 EDT | 61 | 0 | 0 | 0
[14 empty] | 10/21/2020 03:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/21/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/21/2020 04:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/21/2020 12:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/21/2020 05:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/21/2020 13:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/21/2020 06:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/21/2020 14:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/21/2020 07:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/21/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/21/2020 08:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/21/2020 16:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/21/2020 09:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/21/2020 17:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/21/2020 10:00 EDT | 61 | 0 | 0 | 0 | [26 empty] | 10/21/2020 18:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/21/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/21/2020 19:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/21/2020 12:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/21/2020 20:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/21/2020 13:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/21/2020 21:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/21/2020 14:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/21/2020 22:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/21/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/21/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/21/2020 16:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/22/2020 00:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/21/2020 17:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/22/2020 01:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/21/2020 18:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/22/2020 02:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/21/2020 19:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/22/2020 03:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/21/2020 20:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/22/2020 04:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/21/2020 21:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/22/2020 05:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/21/2020 22:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/22/2020 06:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/21/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/22/2020 07:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/22/2020 00:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/22/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/22/2020 01:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/22/2020 09:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 02:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/22/2020 10:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 03:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/22/2020 11:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 04:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/22/2020 12:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/22/2020 05:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/22/2020 13:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/22/2020 06:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/22/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/22/2020 07:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/22/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/22/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/22/2020 16:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/22/2020 09:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/22/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/22/2020 10:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/22/2020 18:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/22/2020 11:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/22/2020 19:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/22/2020 12:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/22/2020 20:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/22/2020 13:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/22/2020 21:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/22/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/22/2020 22:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/22/2020 23:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 16:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/23/2020 00:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/23/2020 01:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 18:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/23/2020 02:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 19:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/23/2020 03:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/22/2020 20:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/23/2020 04:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/22/2020 21:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/23/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/22/2020 22:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/23/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/22/2020 23:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/23/2020 07:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 00:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/23/2020 08:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 01:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/23/2020 09:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 02:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/23/2020 10:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 03:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/23/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 04:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/23/2020 12:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/23/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/23/2020 13:00 EDT | 66 | 0 | 0 | 0
[14 empty] | 10/23/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/23/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/23/2020 07:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/23/2020 15:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/23/2020 08:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/23/2020 16:00 EDT | 68 | 0 | 0 | 0
[14 empty] | 10/23/2020 09:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/23/2020 17:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/23/2020 10:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/23/2020 18:00 EDT | 65 | 0 | 0 | 0
[14 empty] | 10/23/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/23/2020 19:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 12:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/23/2020 20:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 13:00 EDT | 66 | 0 | 0 | 0 | [26 empty] | 10/23/2020 21:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/23/2020 22:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 15:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/23/2020 23:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 16:00 EDT | 68 | 0 | 0 | 0 | [26 empty] | 10/24/2020 00:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 17:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/24/2020 01:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 18:00 EDT | 65 | 0 | 0 | 0 | [26 empty] | 10/24/2020 02:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/23/2020 19:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 03:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 20:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 04:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 21:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 05:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 22:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 06:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/23/2020 23:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 07:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/24/2020 00:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 08:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/24/2020 01:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 09:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/24/2020 02:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 10:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/24/2020 03:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 11:00 EDT | 63 | 0 | 0 | 0
[14 empty] | 10/24/2020 04:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 12:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/24/2020 05:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 13:00 EDT | 64 | 0 | 0 | 0
[14 empty] | 10/24/2020 06:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 14:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/24/2020 07:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 15:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/24/2020 08:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 16:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/24/2020 09:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 17:00 EDT | 69 | 0 | 0 | 0
[14 empty] | 10/24/2020 10:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 18:00 EDT | 67 | 0 | 0 | 0
[14 empty] | 10/24/2020 11:00 EDT | 63 | 0 | 0 | 0 | [26 empty] | 10/24/2020 19:00 EDT | 62 | 0 | 0 | 0
[14 empty] | 10/24/2020 12:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 20:00 EDT | 60 | 0 | 0 | 0
[14 empty] | 10/24/2020 13:00 EDT | 64 | 0 | 0 | 0 | [26 empty] | 10/24/2020 21:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/24/2020 14:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/24/2020 22:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/24/2020 15:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/24/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 16:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/25/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 17:00 EDT | 69 | 0 | 0 | 0 | [26 empty] | 10/25/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 18:00 EDT | 67 | 0 | 0 | 0 | [26 empty] | 10/25/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 19:00 EDT | 62 | 0 | 0 | 0 | [26 empty] | 10/25/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 20:00 EDT | 60 | 0 | 0 | 0 | [26 empty] | 10/25/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 21:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/25/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 22:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/25/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/24/2020 23:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 00:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 09:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 02:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 03:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 04:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 05:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 06:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 07:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 08:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 09:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 10:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 18:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 11:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 12:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 20:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 14:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 15:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/25/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 16:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 17:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 18:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 19:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 20:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 21:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 22:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/25/2020 23:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 00:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 01:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 02:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 03:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 04:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 05:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 13:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 14:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/26/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 15:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/26/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 16:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/26/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 17:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/26/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 18:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 11:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 19:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 12:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 20:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 13:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 21:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 14:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/26/2020 22:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 15:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/26/2020 23:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/26/2020 16:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/27/2020 00:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/26/2020 17:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/27/2020 01:00 EDT | 59 | 0 | 0 | 0
[14 empty] | 10/26/2020 18:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 02:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 19:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 03:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 20:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 04:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/26/2020 21:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 05:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 22:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 06:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/26/2020 23:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/27/2020 07:00 EDT | 58 | 0 | 0 | 0
[14 empty] | 10/27/2020 00:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/27/2020 08:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/27/2020 01:00 EDT | 59 | 0 | 0 | 0 | [26 empty] | 10/27/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 02:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 03:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 11:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 04:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/27/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 05:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 13:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 06:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 14:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 07:00 EDT | 58 | 0 | 0 | 0 | [26 empty] | 10/27/2020 15:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/27/2020 08:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/27/2020 16:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/27/2020 09:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/27/2020 17:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/27/2020 10:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/27/2020 18:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/27/2020 11:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/27/2020 19:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/27/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/27/2020 20:00 EDT | 56.5 | 0 | 0 | 0
[14 empty] | 10/27/2020 13:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/27/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/27/2020 14:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/27/2020 22:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/27/2020 15:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/27/2020 23:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/27/2020 16:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/28/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 17:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/28/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 18:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/28/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 19:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/28/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 20:00 EDT | 56.5 | 0 | 0 | 0 | [26 empty] | 10/28/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/28/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 22:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/28/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/27/2020 23:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/28/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 00:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 01:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 02:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 03:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 11:00 EDT | 53.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 04:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 05:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 06:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 07:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 08:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 09:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 17:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 10:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 18:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/28/2020 11:00 EDT | 53.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 19:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 12:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 20:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 13:00 EDT | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 21:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 14:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 22:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 15:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/28/2020 23:00 EDT | 57 | 0 | 0 | 0
[14 empty] | 10/28/2020 16:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 00:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 17:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 01:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 18:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/29/2020 02:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 19:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 20:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 21:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 05:00 EDT | 56 | 0 | 0 | 0
[14 empty] | 10/28/2020 22:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/28/2020 23:00 EDT | 57 | 0 | 0 | 0 | [26 empty] | 10/29/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 00:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 01:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 02:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 03:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 04:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 05:00 EDT | 56 | 0 | 0 | 0 | [26 empty] | 10/29/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 06:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 07:00 EDT | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 08:00 EDT | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 09:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 17:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 10:00 EDT | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 18:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 11:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 12:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 13:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 14:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 15:00 EDT | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/29/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 16:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 17:00 EDT | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 18:00 EDT | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 02:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 19:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 20:00 EDT | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 21:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 22:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 06:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/29/2020 23:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 00:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 01:00 EDT | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 09:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 02:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 10:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 03:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 11:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 04:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 12:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 05:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 13:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 06:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 14:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 07:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 15:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 08:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 16:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 09:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 17:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 10:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 18:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 11:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 19:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 12:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 20:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 13:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 21:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 14:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 22:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 15:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/30/2020 23:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 16:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 00:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 17:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 01:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 18:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 19:00 EDT | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 03:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 20:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 04:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 21:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 05:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 22:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 06:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/30/2020 23:00 EDT | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 07:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 00:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 08:00 EDT | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 01:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 09:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 02:00 EDT | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 10:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 03:00 EDT | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 11:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 04:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 12:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 05:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 13:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 06:00 EDT | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 14:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 07:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 15:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 08:00 EDT | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 09:00 EDT | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 10:00 EDT | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 18:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 11:00 EDT | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 19:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 12:00 EDT | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 20:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 13:00 EDT | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 14:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 15:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 10/31/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 16:00 EDT | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 17:00 EDT | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 01:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 18:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 19:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 20:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 21:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 22:00 EDT | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 10/31/2020 23:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 06:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 00:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 01:00 EDT | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 08:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 09:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 10:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 11:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 12:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 06:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 14:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 08:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 09:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 17:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 10:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 11:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 19:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 12:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 20:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 14:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/01/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 17:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 19:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 20:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/01/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 13:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 09:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 13:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/02/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 06:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/02/2020 23:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 07:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 10:00 | 46.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 06:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 07:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 16:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 09:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 17:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 10:00 | 46.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 19:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/03/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 16:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 17:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 19:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/03/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 12:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 13:00 | 60 | 0 | 0 | 0
[14 empty] | 11/04/2020 06:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 14:00 | 60 | 0 | 0 | 0
[14 empty] | 11/04/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 15:00 | 61 | 0 | 0 | 0
[14 empty] | 11/04/2020 08:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 16:00 | 61 | 0 | 0 | 0
[14 empty] | 11/04/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 17:00 | 61 | 0 | 0 | 0
[14 empty] | 11/04/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 18:00 | 59 | 0 | 0 | 0
[14 empty] | 11/04/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 19:00 | 58 | 0 | 0 | 0
[14 empty] | 11/04/2020 12:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/04/2020 20:00 | 59 | 0 | 0 | 0
[14 empty] | 11/04/2020 13:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/04/2020 21:00 | 56 | 0 | 0 | 0
[14 empty] | 11/04/2020 14:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/04/2020 22:00 | 57 | 0 | 0 | 0
[14 empty] | 11/04/2020 15:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/04/2020 23:00 | 57 | 0 | 0 | 0
[14 empty] | 11/04/2020 16:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/05/2020 00:00 | 56 | 0 | 0 | 0
[14 empty] | 11/04/2020 17:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/05/2020 01:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 18:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/05/2020 02:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 19:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/05/2020 03:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 20:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/05/2020 04:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 21:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/05/2020 05:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 22:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/05/2020 06:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/04/2020 23:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/05/2020 07:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/05/2020 00:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/05/2020 08:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/05/2020 01:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 09:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/05/2020 02:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 10:00 | 56 | 0 | 0 | 0
[14 empty] | 11/05/2020 03:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 11:00 | 56 | 0 | 0 | 0
[14 empty] | 11/05/2020 04:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 12:00 | 61 | 0 | 0 | 0
[14 empty] | 11/05/2020 05:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 13:00 | 64 | 0 | 0 | 0
[14 empty] | 11/05/2020 06:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 14:00 | 67 | 0 | 0 | 0
[14 empty] | 11/05/2020 07:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 15:00 | 67 | 0 | 0 | 0
[14 empty] | 11/05/2020 08:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 16:00 | 65 | 0 | 0 | 0
[14 empty] | 11/05/2020 09:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/05/2020 17:00 | 64 | 0 | 0 | 0
[14 empty] | 11/05/2020 10:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/05/2020 18:00 | 61 | 0 | 0 | 0
[14 empty] | 11/05/2020 11:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/05/2020 19:00 | 60 | 0 | 0 | 0
[14 empty] | 11/05/2020 12:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/05/2020 20:00 | 59 | 0 | 0 | 0
[14 empty] | 11/05/2020 13:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/05/2020 21:00 | 61 | 0 | 0 | 0
[14 empty] | 11/05/2020 14:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/05/2020 22:00 | 61 | 0 | 0 | 0
[14 empty] | 11/05/2020 15:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/05/2020 23:00 | 60 | 0 | 0 | 0
[14 empty] | 11/05/2020 16:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/06/2020 00:00 | 60 | 0 | 0 | 0
[14 empty] | 11/05/2020 17:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/06/2020 01:00 | 59 | 0 | 0 | 0
[14 empty] | 11/05/2020 18:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/06/2020 02:00 | 59 | 0 | 0 | 0
[14 empty] | 11/05/2020 19:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/06/2020 03:00 | 57 | 0 | 0 | 0
[14 empty] | 11/05/2020 20:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/06/2020 04:00 | 57 | 0 | 0 | 0
[14 empty] | 11/05/2020 21:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/06/2020 05:00 | 56 | 0 | 0 | 0
[14 empty] | 11/05/2020 22:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/06/2020 06:00 | 58 | 0 | 0 | 0
[14 empty] | 11/05/2020 23:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/06/2020 07:00 | 58 | 0 | 0 | 0
[14 empty] | 11/06/2020 00:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/06/2020 08:00 | 57 | 0 | 0 | 0
[14 empty] | 11/06/2020 01:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/06/2020 09:00 | 58 | 0 | 0 | 0
[14 empty] | 11/06/2020 02:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/06/2020 10:00 | 60 | 0 | 0 | 0
[14 empty] | 11/06/2020 03:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/06/2020 11:00 | 62 | 0 | 0 | 0
[14 empty] | 11/06/2020 04:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/06/2020 12:00 | 64 | 0 | 0 | 0
[14 empty] | 11/06/2020 05:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/06/2020 13:00 | 67 | 0 | 0 | 0
[14 empty] | 11/06/2020 06:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/06/2020 14:00 | 69 | 0 | 0 | 0
[14 empty] | 11/06/2020 07:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/06/2020 15:00 | 70 | 0 | 0 | 0
[14 empty] | 11/06/2020 08:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/06/2020 16:00 | 69 | 0 | 0 | 0
[14 empty] | 11/06/2020 09:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/06/2020 17:00 | 68 | 0 | 0 | 0
[14 empty] | 11/06/2020 10:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/06/2020 18:00 | 66 | 0 | 0 | 0
[14 empty] | 11/06/2020 11:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/06/2020 19:00 | 65 | 0 | 0 | 0
[14 empty] | 11/06/2020 12:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/06/2020 20:00 | 64 | 0 | 0 | 0
[14 empty] | 11/06/2020 13:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/06/2020 21:00 | 63 | 0 | 0 | 0
[14 empty] | 11/06/2020 14:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/06/2020 22:00 | 63 | 0 | 0 | 0
[14 empty] | 11/06/2020 15:00 | 70 | 0 | 0 | 0 | [26 empty] | 11/06/2020 23:00 | 63 | 0 | 0 | 0
[14 empty] | 11/06/2020 16:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/07/2020 00:00 | 62 | 0 | 0 | 0
[14 empty] | 11/06/2020 17:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/07/2020 01:00 | 61 | 0 | 0 | 0
[14 empty] | 11/06/2020 18:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/07/2020 02:00 | 59 | 0 | 0 | 0
[14 empty] | 11/06/2020 19:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/07/2020 03:00 | 61 | 0 | 0 | 0
[14 empty] | 11/06/2020 20:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/07/2020 04:00 | 59 | 0 | 0 | 0
[14 empty] | 11/06/2020 21:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/07/2020 05:00 | 59 | 0 | 0 | 0
[14 empty] | 11/06/2020 22:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/07/2020 06:00 | 57 | 0 | 0 | 0
[14 empty] | 11/06/2020 23:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/07/2020 07:00 | 56 | 0 | 0 | 0
[14 empty] | 11/07/2020 00:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/07/2020 08:00 | 57 | 0 | 0 | 0
[14 empty] | 11/07/2020 01:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/07/2020 09:00 | 59 | 0 | 0 | 0
[14 empty] | 11/07/2020 02:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/07/2020 10:00 | 62 | 0 | 0 | 0
[14 empty] | 11/07/2020 03:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/07/2020 11:00 | 64 | 0 | 0 | 0
[14 empty] | 11/07/2020 04:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/07/2020 12:00 | 67 | 0 | 0 | 0
[14 empty] | 11/07/2020 05:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/07/2020 13:00 | 70 | 0 | 0 | 0
[14 empty] | 11/07/2020 06:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/07/2020 14:00 | 72 | 0 | 0 | 0
[14 empty] | 11/07/2020 07:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/07/2020 15:00 | 73 | 0 | 0 | 0
[14 empty] | 11/07/2020 08:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/07/2020 16:00 | 73 | 0 | 0 | 0
[14 empty] | 11/07/2020 09:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/07/2020 17:00 | 72 | 0 | 0 | 0
[14 empty] | 11/07/2020 10:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/07/2020 18:00 | 70 | 0 | 0 | 0
[14 empty] | 11/07/2020 11:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/07/2020 19:00 | 69 | 0 | 0 | 0
[14 empty] | 11/07/2020 12:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/07/2020 20:00 | 69 | 0 | 0 | 0
[14 empty] | 11/07/2020 13:00 | 70 | 0 | 0 | 0 | [26 empty] | 11/07/2020 21:00 | 68 | 0 | 0 | 0
[14 empty] | 11/07/2020 14:00 | 72 | 0 | 0 | 0 | [26 empty] | 11/07/2020 22:00 | 67 | 0 | 0 | 0
[14 empty] | 11/07/2020 15:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/07/2020 23:00 | 65 | 0 | 0 | 0
[14 empty] | 11/07/2020 16:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/08/2020 00:00 | 64 | 0 | 0 | 0
[14 empty] | 11/07/2020 17:00 | 72 | 0 | 0 | 0 | [26 empty] | 11/08/2020 01:00 | 63 | 0 | 0 | 0
[14 empty] | 11/07/2020 18:00 | 70 | 0 | 0 | 0 | [26 empty] | 11/08/2020 02:00 | 63 | 0 | 0 | 0
[14 empty] | 11/07/2020 19:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/08/2020 03:00 | 63 | 0 | 0 | 0
[14 empty] | 11/07/2020 20:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/08/2020 04:00 | 62 | 0 | 0 | 0
[14 empty] | 11/07/2020 21:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/08/2020 05:00 | 61 | 0 | 0 | 0
[14 empty] | 11/07/2020 22:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/08/2020 06:00 | 59 | 0 | 0 | 0
[14 empty] | 11/07/2020 23:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/08/2020 07:00 | 56 | 0 | 0 | 0
[14 empty] | 11/08/2020 00:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/08/2020 08:00 | 56 | 0 | 0 | 0
[14 empty] | 11/08/2020 01:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/08/2020 09:00 | 58 | 0 | 0 | 0
[14 empty] | 11/08/2020 02:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/08/2020 10:00 | 60 | 0 | 0 | 0
[14 empty] | 11/08/2020 03:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/08/2020 11:00 | 63 | 0 | 0 | 0
[14 empty] | 11/08/2020 04:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/08/2020 12:00 | 67 | 0 | 0 | 0
[14 empty] | 11/08/2020 05:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/08/2020 13:00 | 71 | 0 | 0 | 0
[14 empty] | 11/08/2020 06:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/08/2020 14:00 | 73 | 0 | 0 | 0
[14 empty] | 11/08/2020 07:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/08/2020 15:00 | 73 | 0 | 0 | 0
[14 empty] | 11/08/2020 08:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/08/2020 16:00 | 74 | 0 | 0 | 0
[14 empty] | 11/08/2020 09:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/08/2020 17:00 | 73 | 0 | 0 | 0
[14 empty] | 11/08/2020 10:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/08/2020 18:00 | 69 | 0 | 0 | 0
[14 empty] | 11/08/2020 11:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/08/2020 19:00 | 67 | 0 | 0 | 0
[14 empty] | 11/08/2020 12:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/08/2020 20:00 | 65 | 0 | 0 | 0
[14 empty] | 11/08/2020 13:00 | 71 | 0 | 0 | 0 | [26 empty] | 11/08/2020 21:00 | 63 | 0 | 0 | 0
[14 empty] | 11/08/2020 14:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/08/2020 22:00 | 62 | 0 | 0 | 0
[14 empty] | 11/08/2020 15:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/08/2020 23:00 | 62 | 0 | 0 | 0
[14 empty] | 11/08/2020 16:00 | 74 | 0 | 0 | 0 | [26 empty] | 11/09/2020 00:00 | 59 | 0 | 0 | 0
[14 empty] | 11/08/2020 17:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/09/2020 01:00 | 58 | 0 | 0 | 0
[14 empty] | 11/08/2020 18:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/09/2020 02:00 | 58 | 0 | 0 | 0
[14 empty] | 11/08/2020 19:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/09/2020 03:00 | 58 | 0 | 0 | 0
[14 empty] | 11/08/2020 20:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/09/2020 04:00 | 57 | 0 | 0 | 0
[14 empty] | 11/08/2020 21:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/09/2020 05:00 | 57 | 0 | 0 | 0
[14 empty] | 11/08/2020 22:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/09/2020 06:00 | 56 | 0 | 0 | 0
[14 empty] | 11/08/2020 23:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/09/2020 07:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/09/2020 00:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/09/2020 08:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/09/2020 01:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/09/2020 09:00 | 57 | 0 | 0 | 0
[14 empty] | 11/09/2020 02:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/09/2020 10:00 | 60 | 0 | 0 | 0
[14 empty] | 11/09/2020 03:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/09/2020 11:00 | 64 | 0 | 0 | 0
[14 empty] | 11/09/2020 04:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/09/2020 12:00 | 68 | 0 | 0 | 0
[14 empty] | 11/09/2020 05:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/09/2020 13:00 | 72 | 0 | 0 | 0
[14 empty] | 11/09/2020 06:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/09/2020 14:00 | 74 | 0 | 0 | 0
[14 empty] | 11/09/2020 07:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/09/2020 15:00 | 74 | 0 | 0 | 0
[14 empty] | 11/09/2020 08:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/09/2020 16:00 | 74 | 0 | 0 | 0
[14 empty] | 11/09/2020 09:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/09/2020 17:00 | 74 | 0 | 0 | 0
[14 empty] | 11/09/2020 10:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/09/2020 18:00 | 69 | 0 | 0 | 0
[14 empty] | 11/09/2020 11:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/09/2020 19:00 | 67 | 0 | 0 | 0
[14 empty] | 11/09/2020 12:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/09/2020 20:00 | 65 | 0 | 0 | 0
[14 empty] | 11/09/2020 13:00 | 72 | 0 | 0 | 0 | [26 empty] | 11/09/2020 21:00 | 64 | 0 | 0 | 0
[14 empty] | 11/09/2020 14:00 | 74 | 0 | 0 | 0 | [26 empty] | 11/09/2020 22:00 | 62 | 0 | 0 | 0
[14 empty] | 11/09/2020 15:00 | 74 | 0 | 0 | 0 | [26 empty] | 11/09/2020 23:00 | 65 | 0 | 0 | 0
[14 empty] | 11/09/2020 16:00 | 74 | 0 | 0 | 0 | [26 empty] | 11/10/2020 00:00 | 65 | 0 | 0 | 0
[14 empty] | 11/09/2020 17:00 | 74 | 0 | 0 | 0 | [26 empty] | 11/10/2020 01:00 | 64 | 0 | 0 | 0
[14 empty] | 11/09/2020 18:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/10/2020 02:00 | 63 | 0 | 0 | 0
[14 empty] | 11/09/2020 19:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/10/2020 03:00 | 62 | 0 | 0 | 0
[14 empty] | 11/09/2020 20:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/10/2020 04:00 | 62 | 0 | 0 | 0
[14 empty] | 11/09/2020 21:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/10/2020 05:00 | 62 | 0 | 0 | 0
[14 empty] | 11/09/2020 22:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/10/2020 06:00 | 62 | 0 | 0 | 0
[14 empty] | 11/09/2020 23:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/10/2020 07:00 | 61 | 0 | 0 | 0
[14 empty] | 11/10/2020 00:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/10/2020 08:00 | 61 | 0 | 0 | 0
[14 empty] | 11/10/2020 01:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/10/2020 09:00 | 61 | 0 | 0 | 0
[14 empty] | 11/10/2020 02:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/10/2020 10:00 | 62 | 0 | 0 | 0
[14 empty] | 11/10/2020 03:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/10/2020 11:00 | 65 | 0 | 0 | 0
[14 empty] | 11/10/2020 04:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/10/2020 12:00 | 67 | 0 | 0 | 0
[14 empty] | 11/10/2020 05:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/10/2020 13:00 | 70 | 0 | 0 | 0
[14 empty] | 11/10/2020 06:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/10/2020 14:00 | 71 | 0 | 0 | 0
[14 empty] | 11/10/2020 07:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/10/2020 15:00 | 73 | 0 | 0 | 0
[14 empty] | 11/10/2020 08:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/10/2020 16:00 | 74 | 0 | 0 | 0
[14 empty] | 11/10/2020 09:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/10/2020 17:00 | 73 | 0 | 0 | 0
[14 empty] | 11/10/2020 10:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/10/2020 18:00 | 70 | 0 | 0 | 0
[14 empty] | 11/10/2020 11:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/10/2020 19:00 | 67 | 0 | 0 | 0
[14 empty] | 11/10/2020 12:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/10/2020 20:00 | 67 | 0 | 0 | 0
[14 empty] | 11/10/2020 13:00 | 70 | 0 | 0 | 0 | [26 empty] | 11/10/2020 21:00 | 68 | 0 | 0 | 0
[14 empty] | 11/10/2020 14:00 | 71 | 0 | 0 | 0 | [26 empty] | 11/10/2020 22:00 | 67 | 0 | 0 | 0
[14 empty] | 11/10/2020 15:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/10/2020 23:00 | 67 | 0 | 0 | 0
[14 empty] | 11/10/2020 16:00 | 74 | 0 | 0 | 0 | [26 empty] | 11/11/2020 00:00 | 67 | 0 | 0 | 0
[14 empty] | 11/10/2020 17:00 | 73 | 0 | 0 | 0 | [26 empty] | 11/11/2020 01:00 | 66 | 0 | 0 | 0
[14 empty] | 11/10/2020 18:00 | 70 | 0 | 0 | 0 | [26 empty] | 11/11/2020 02:00 | 65 | 0 | 0 | 0
[14 empty] | 11/10/2020 19:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/11/2020 03:00 | 65 | 0 | 0 | 0
[14 empty] | 11/10/2020 20:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/11/2020 04:00 | 64 | 0 | 0 | 0
[14 empty] | 11/10/2020 21:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/11/2020 05:00 | 65 | 0 | 0 | 0
[14 empty] | 11/10/2020 22:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/11/2020 06:00 | 66 | 0 | 0 | 0
[14 empty] | 11/10/2020 23:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/11/2020 07:00 | 66 | 0 | 0 | 0
[14 empty] | 11/11/2020 00:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/11/2020 08:00 | 66 | 0 | 0 | 0
[14 empty] | 11/11/2020 01:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/11/2020 09:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 02:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/11/2020 10:00 | 68 | 0 | 0 | 0
[14 empty] | 11/11/2020 03:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/11/2020 11:00 | 68 | 0 | 0 | 0
[14 empty] | 11/11/2020 04:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/11/2020 12:00 | 69 | 0 | 0 | 0
[14 empty] | 11/11/2020 05:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/11/2020 13:00 | 72 | 0 | 0 | 0
[14 empty] | 11/11/2020 06:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/11/2020 14:00 | 71 | 0 | 0 | 0
[14 empty] | 11/11/2020 07:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/11/2020 15:00 | 69 | 0 | 0 | 0
[14 empty] | 11/11/2020 08:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/11/2020 16:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 09:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/11/2020 17:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 10:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/11/2020 18:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 11:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/11/2020 19:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 12:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/11/2020 20:00 | 66 | 0 | 0 | 0
[14 empty] | 11/11/2020 13:00 | 72 | 0 | 0 | 0 | [26 empty] | 11/11/2020 21:00 | 66 | 0 | 0 | 0
[14 empty] | 11/11/2020 14:00 | 71 | 0 | 0 | 0 | [26 empty] | 11/11/2020 22:00 | 66 | 0 | 0 | 0
[14 empty] | 11/11/2020 15:00 | 69 | 0 | 0 | 0 | [26 empty] | 11/11/2020 23:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 16:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 00:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 17:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 01:00 | 68 | 0 | 0 | 0
[14 empty] | 11/11/2020 18:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 02:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 19:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 03:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 20:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/12/2020 04:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 21:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/12/2020 05:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 22:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/12/2020 06:00 | 67 | 0 | 0 | 0
[14 empty] | 11/11/2020 23:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 07:00 | 66 | 0 | 0 | 0
[14 empty] | 11/12/2020 00:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 08:00 | 66 | 0 | 0 | 0
[14 empty] | 11/12/2020 01:00 | 68 | 0 | 0 | 0 | [26 empty] | 11/12/2020 09:00 | 58 | 0 | 0 | 0
[14 empty] | 11/12/2020 02:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 10:00 | 56 | 0 | 0 | 0
[14 empty] | 11/12/2020 03:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 11:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 04:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 12:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 05:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 06:00 | 67 | 0 | 0 | 0 | [26 empty] | 11/12/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 07:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/12/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 08:00 | 66 | 0 | 0 | 0 | [26 empty] | 11/12/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 09:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/12/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 10:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/12/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 11:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/12/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 12:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/12/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/12/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/12/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 15:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/12/2020 23:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 00:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 01:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 02:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/12/2020 23:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 00:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 08:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 01:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 09:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 02:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 04:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 08:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 09:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 22:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/13/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 01:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 02:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 03:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 04:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 22:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/13/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 07:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 01:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 02:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 03:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 04:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 13:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 14:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 07:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 17:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 18:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 19:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 20:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 13:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 14:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/14/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 17:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 18:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 19:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 20:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/14/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 00:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 01:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 03:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 11:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 04:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 12:00 | 56 | 0 | 0 | 0
[14 empty] | 11/15/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 13:00 | 56 | 0 | 0 | 0
[14 empty] | 11/15/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 14:00 | 56 | 0 | 0 | 0
[14 empty] | 11/15/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 15:00 | 57 | 0 | 0 | 0
[14 empty] | 11/15/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 16:00 | 57 | 0 | 0 | 0
[14 empty] | 11/15/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 17:00 | 58 | 0 | 0 | 0
[14 empty] | 11/15/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 18:00 | 59 | 0 | 0 | 0
[14 empty] | 11/15/2020 11:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/15/2020 19:00 | 61 | 0 | 0 | 0
[14 empty] | 11/15/2020 12:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/15/2020 20:00 | 62 | 0 | 0 | 0
[14 empty] | 11/15/2020 13:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/15/2020 21:00 | 63 | 0 | 0 | 0
[14 empty] | 11/15/2020 14:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/15/2020 22:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 15:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/15/2020 23:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 16:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/16/2020 00:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 17:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/16/2020 01:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 18:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/16/2020 02:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 19:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/16/2020 03:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 20:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/16/2020 04:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 21:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/16/2020 05:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 22:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 06:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/15/2020 23:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 00:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 01:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 09:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 02:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 03:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 04:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 05:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 06:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 09:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 17:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 18:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/16/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 16:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 17:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 18:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 19:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 20:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 04:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/16/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 10:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 03:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 04:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 10:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/17/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 05:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/17/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 05:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 13:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 14:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 15:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 16:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 17:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 18:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 11:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 12:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 13:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 21:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 14:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 15:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/18/2020 23:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 16:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 17:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 01:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 18:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 02:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 03:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 20:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 21:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/18/2020 23:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 07:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 08:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 01:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 02:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 10:00 | 35.5 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 03:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 07:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 08:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 10:00 | 35.5 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 11:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 20:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 21:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/19/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 18:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 19:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 20:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 21:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/19/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 12:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 13:00 | 56 | 0 | 0 | 0
[14 empty] | 11/20/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 14:00 | 59 | 0 | 0 | 0
[14 empty] | 11/20/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 15:00 | 61 | 0 | 0 | 0
[14 empty] | 11/20/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 16:00 | 62 | 0 | 0 | 0
[14 empty] | 11/20/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 17:00 | 62 | 0 | 0 | 0
[14 empty] | 11/20/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 18:00 | 61 | 0 | 0 | 0
[14 empty] | 11/20/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 19:00 | 61 | 0 | 0 | 0
[14 empty] | 11/20/2020 12:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/20/2020 20:00 | 60 | 0 | 0 | 0
[14 empty] | 11/20/2020 13:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/20/2020 21:00 | 59 | 0 | 0 | 0
[14 empty] | 11/20/2020 14:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/20/2020 22:00 | 59 | 0 | 0 | 0
[14 empty] | 11/20/2020 15:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/20/2020 23:00 | 57 | 0 | 0 | 0
[14 empty] | 11/20/2020 16:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/21/2020 00:00 | 56 | 0 | 0 | 0
[14 empty] | 11/20/2020 17:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/21/2020 01:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 18:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/21/2020 02:00 | 56 | 0 | 0 | 0
[14 empty] | 11/20/2020 19:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/21/2020 03:00 | 56 | 0 | 0 | 0
[14 empty] | 11/20/2020 20:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/21/2020 04:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 21:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/21/2020 05:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 22:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/21/2020 06:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/20/2020 23:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/21/2020 07:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 00:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/21/2020 08:00 | 56 | 0 | 0 | 0
[14 empty] | 11/21/2020 01:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/21/2020 09:00 | 56 | 0 | 0 | 0
[14 empty] | 11/21/2020 02:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/21/2020 10:00 | 58 | 0 | 0 | 0
[14 empty] | 11/21/2020 03:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/21/2020 11:00 | 59 | 0 | 0 | 0
[14 empty] | 11/21/2020 04:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/21/2020 12:00 | 62 | 0 | 0 | 0
[14 empty] | 11/21/2020 05:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/21/2020 13:00 | 63 | 0 | 0 | 0
[14 empty] | 11/21/2020 06:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/21/2020 14:00 | 64 | 0 | 0 | 0
[14 empty] | 11/21/2020 07:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/21/2020 15:00 | 63 | 0 | 0 | 0
[14 empty] | 11/21/2020 08:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/21/2020 16:00 | 60 | 0 | 0 | 0
[14 empty] | 11/21/2020 09:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/21/2020 17:00 | 59 | 0 | 0 | 0
[14 empty] | 11/21/2020 10:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/21/2020 18:00 | 58 | 0 | 0 | 0
[14 empty] | 11/21/2020 11:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/21/2020 19:00 | 56 | 0 | 0 | 0
[14 empty] | 11/21/2020 12:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/21/2020 20:00 | 56 | 0 | 0 | 0
[14 empty] | 11/21/2020 13:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/21/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 14:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/21/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 15:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/21/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 16:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/22/2020 00:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 17:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/22/2020 01:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 18:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/22/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 19:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/22/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 20:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/22/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/21/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 00:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 08:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 01:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 02:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 03:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 13:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 06:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 07:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 08:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 09:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 10:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 12:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 20:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 13:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 21:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 22:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/22/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/22/2020 23:00 | 56 | 0 | 0 | 0
[14 empty] | 11/22/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 00:00 | 57 | 0 | 0 | 0
[14 empty] | 11/22/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 01:00 | 59 | 0 | 0 | 0
[14 empty] | 11/22/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 02:00 | 59 | 0 | 0 | 0
[14 empty] | 11/22/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 03:00 | 59 | 0 | 0 | 0
[14 empty] | 11/22/2020 20:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 04:00 | 60 | 0 | 0 | 0
[14 empty] | 11/22/2020 21:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 05:00 | 60 | 0 | 0 | 0
[14 empty] | 11/22/2020 22:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 06:00 | 60 | 0 | 0 | 0
[14 empty] | 11/22/2020 23:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/23/2020 07:00 | 59 | 0 | 0 | 0
[14 empty] | 11/23/2020 00:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/23/2020 08:00 | 59 | 0 | 0 | 0
[14 empty] | 11/23/2020 01:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/23/2020 09:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 02:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/23/2020 10:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 03:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/23/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 04:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/23/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 05:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/23/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 06:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/23/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 07:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/23/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 08:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/23/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 09:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 10:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 13:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 14:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/23/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 20:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 06:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/23/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 07:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 10:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 04:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 05:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 06:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 07:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 10:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 19:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 12:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/24/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 19:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/24/2020 23:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 01:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 10:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 12:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 05:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 13:00 | 56 | 0 | 0 | 0
[14 empty] | 11/25/2020 06:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 08:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 16:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 17:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 10:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 18:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 11:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 12:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 20:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 13:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/25/2020 21:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/25/2020 23:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 16:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 00:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 17:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 01:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/25/2020 18:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 02:00 | 56 | 0 | 0 | 0
[14 empty] | 11/25/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 03:00 | 56 | 0 | 0 | 0
[14 empty] | 11/25/2020 20:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 04:00 | 57 | 0 | 0 | 0
[14 empty] | 11/25/2020 21:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 05:00 | 56 | 0 | 0 | 0
[14 empty] | 11/25/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 06:00 | 56 | 0 | 0 | 0
[14 empty] | 11/25/2020 23:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 07:00 | 57 | 0 | 0 | 0
[14 empty] | 11/26/2020 00:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 08:00 | 58 | 0 | 0 | 0
[14 empty] | 11/26/2020 01:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/26/2020 09:00 | 60 | 0 | 0 | 0
[14 empty] | 11/26/2020 02:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/26/2020 10:00 | 60 | 0 | 0 | 0
[14 empty] | 11/26/2020 03:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/26/2020 11:00 | 61 | 0 | 0 | 0
[14 empty] | 11/26/2020 04:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/26/2020 12:00 | 62 | 0 | 0 | 0
[14 empty] | 11/26/2020 05:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/26/2020 13:00 | 63 | 0 | 0 | 0
[14 empty] | 11/26/2020 06:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/26/2020 14:00 | 64 | 0 | 0 | 0
[14 empty] | 11/26/2020 07:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/26/2020 15:00 | 63 | 0 | 0 | 0
[14 empty] | 11/26/2020 08:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/26/2020 16:00 | 65 | 0 | 0 | 0
[14 empty] | 11/26/2020 09:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/26/2020 17:00 | 65 | 0 | 0 | 0
[14 empty] | 11/26/2020 10:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/26/2020 18:00 | 62 | 0 | 0 | 0
[14 empty] | 11/26/2020 11:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/26/2020 19:00 | 60 | 0 | 0 | 0
[14 empty] | 11/26/2020 12:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/26/2020 20:00 | 61 | 0 | 0 | 0
[14 empty] | 11/26/2020 13:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/26/2020 21:00 | 59 | 0 | 0 | 0
[14 empty] | 11/26/2020 14:00 | 64 | 0 | 0 | 0 | [26 empty] | 11/26/2020 22:00 | 58 | 0 | 0 | 0
[14 empty] | 11/26/2020 15:00 | 63 | 0 | 0 | 0 | [26 empty] | 11/26/2020 23:00 | 56 | 0 | 0 | 0
[14 empty] | 11/26/2020 16:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/27/2020 00:00 | 56 | 0 | 0 | 0
[14 empty] | 11/26/2020 17:00 | 65 | 0 | 0 | 0 | [26 empty] | 11/27/2020 01:00 | 56 | 0 | 0 | 0
[14 empty] | 11/26/2020 18:00 | 62 | 0 | 0 | 0 | [26 empty] | 11/27/2020 02:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/26/2020 19:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/27/2020 03:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/26/2020 20:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/27/2020 04:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/26/2020 21:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/27/2020 05:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/26/2020 22:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/27/2020 06:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/26/2020 23:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/27/2020 07:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 00:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/27/2020 08:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 01:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/27/2020 09:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 02:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 10:00 | 56 | 0 | 0 | 0
[14 empty] | 11/27/2020 03:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 11:00 | 58 | 0 | 0 | 0
[14 empty] | 11/27/2020 04:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 12:00 | 60 | 0 | 0 | 0
[14 empty] | 11/27/2020 05:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 13:00 | 60 | 0 | 0 | 0
[14 empty] | 11/27/2020 06:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 14:00 | 61 | 0 | 0 | 0
[14 empty] | 11/27/2020 07:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 15:00 | 61 | 0 | 0 | 0
[14 empty] | 11/27/2020 08:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 16:00 | 60 | 0 | 0 | 0
[14 empty] | 11/27/2020 09:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/27/2020 17:00 | 59 | 0 | 0 | 0
[14 empty] | 11/27/2020 10:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/27/2020 18:00 | 58 | 0 | 0 | 0
[14 empty] | 11/27/2020 11:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/27/2020 19:00 | 57 | 0 | 0 | 0
[14 empty] | 11/27/2020 12:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/27/2020 20:00 | 56 | 0 | 0 | 0
[14 empty] | 11/27/2020 13:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/27/2020 21:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 14:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/27/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 15:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/27/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 16:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/28/2020 00:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 17:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/28/2020 01:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 18:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/28/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 19:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/28/2020 03:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 20:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/28/2020 04:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 21:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 05:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 06:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/27/2020 23:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 07:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 00:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 08:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 01:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 09:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 10:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 03:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 11:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 04:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 12:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 05:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 06:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 14:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 07:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 08:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 16:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 09:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 17:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 10:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 11:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 19:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 12:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 14:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 15:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/28/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 16:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 17:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 18:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 19:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 21:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 22:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/28/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 01:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 09:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 02:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 03:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 04:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 13:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 16:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 09:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 17:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 10:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 18:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 11:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 19:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 13:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 21:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 22:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 15:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/29/2020 23:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 16:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 00:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 17:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 01:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 18:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 19:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 03:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 04:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 21:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 05:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 22:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 06:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/29/2020 23:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 07:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/30/2020 00:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 08:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/30/2020 01:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 09:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/30/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 10:00 | 56 | 0 | 0 | 0
[14 empty] | 11/30/2020 03:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 11:00 | 57 | 0 | 0 | 0
[14 empty] | 11/30/2020 04:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 12:00 | 58 | 0 | 0 | 0
[14 empty] | 11/30/2020 05:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 13:00 | 59 | 0 | 0 | 0
[14 empty] | 11/30/2020 06:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 14:00 | 60 | 0 | 0 | 0
[14 empty] | 11/30/2020 07:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 15:00 | 61 | 0 | 0 | 0
[14 empty] | 11/30/2020 08:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 16:00 | 62 | 0 | 0 | 0
[14 empty] | 11/30/2020 09:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 11/30/2020 17:00 | 62 | 0 | 0 | 0
[14 empty] | 11/30/2020 10:00 | 56 | 0 | 0 | 0 | [26 empty] | 11/30/2020 18:00 | 63 | 0 | 0 | 0
[14 empty] | 11/30/2020 11:00 | 57 | 0 | 0 | 0 | [26 empty] | 11/30/2020 19:00 | 62 | 0 | 0 | 0
[14 empty] | 11/30/2020 12:00 | 58 | 0 | 0 | 0 | [26 empty] | 11/30/2020 20:00 | 63 | 0 | 0 | 0
[14 empty] | 11/30/2020 13:00 | 59 | 0 | 0 | 0 | [26 empty] | 11/30/2020 21:00 | 63 | 0 | 0 | 0
[14 empty] | 11/30/2020 14:00 | 60 | 0 | 0 | 0 | [26 empty] | 11/30/2020 22:00 | 61 | 0 | 0 | 0
[14 empty] | 11/30/2020 15:00 | 61 | 0 | 0 | 0 | [26 empty] | 11/30/2020 23:00 | 60 | 0 | 0 | 0
[14 empty] | 11/30/2020 16:00 | 62 | 0 | 0 | 0 | [26 empty] | 12/01/2020 00:00 | 61 | 0 | 0 | 0
[14 empty] | 11/30/2020 17:00 | 62 | 0 | 0 | 0 | [26 empty] | 12/01/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 11/30/2020 18:00 | 63 | 0 | 0 | 0 | [26 empty] | 12/01/2020 02:00 | 59 | 0 | 0 | 0
[14 empty] | 11/30/2020 19:00 | 62 | 0 | 0 | 0 | [26 empty] | 12/01/2020 03:00 | 59 | 0 | 0 | 0
[14 empty] | 11/30/2020 20:00 | 63 | 0 | 0 | 0 | [26 empty] | 12/01/2020 04:00 | 58 | 0 | 0 | 0
[14 empty] | 11/30/2020 21:00 | 63 | 0 | 0 | 0 | [26 empty] | 12/01/2020 05:00 | 56 | 0 | 0 | 0
[14 empty] | 11/30/2020 22:00 | 61 | 0 | 0 | 0 | [26 empty] | 12/01/2020 06:00 | 56 | 0 | 0 | 0
[14 empty] | 11/30/2020 23:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/01/2020 07:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 00:00 | 61 | 0 | 0 | 0 | [26 empty] | 12/01/2020 08:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 09:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 02:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/01/2020 10:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 03:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/01/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 04:00 | 58 | 0 | 0 | 0 | [26 empty] | 12/01/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 05:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/01/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 06:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/01/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 07:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 08:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 09:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 10:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 11:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 14:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 15:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/01/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 01:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 18:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 03:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 06:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/01/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 01:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 03:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 05:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 13:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 06:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 14:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 13:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 14:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 15:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/02/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 16:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 17:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 05:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 06:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/02/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 07:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 00:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 08:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 01:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 09:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 02:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 05:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 06:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 07:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 08:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 09:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 18:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 12:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 22:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/03/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 16:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 17:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 01:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 18:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 02:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 04:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 21:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 22:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/03/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 00:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 08:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 01:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 02:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 03:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 04:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 14:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 07:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 08:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 10:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 19:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 12:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 13:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 21:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 14:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/04/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 19:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 20:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 21:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 22:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 06:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/04/2020 23:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 07:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 00:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 01:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 09:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 04:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 05:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 06:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 07:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 08:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 09:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 17:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 10:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 11:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 12:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 13:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 14:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/05/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 17:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 22:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/05/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 01:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 02:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 10:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 03:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 10:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 15:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/06/2020 23:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 19:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 03:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 04:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 06:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/06/2020 23:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 07:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 03:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 11:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 04:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 12:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 06:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 07:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 08:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 09:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 11:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 12:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 14:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 15:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/07/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 17:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 01:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 18:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 20:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 04:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/07/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 07:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 00:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 01:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 10:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 11:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 04:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 12:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 13:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 06:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 14:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 07:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 15:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 16:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 10:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 11:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 12:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 13:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 21:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 14:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 15:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/08/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 16:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 04:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 21:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 22:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/08/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 07:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 00:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 01:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 02:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 10:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 04:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 06:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 14:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 07:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 15:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 08:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 09:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 17:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 10:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 18:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 12:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 14:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 15:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/09/2020 23:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 16:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 17:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 18:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 21:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 22:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/09/2020 23:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 08:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 02:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 10:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 03:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 11:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 08:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 10:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 11:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 14:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 15:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/10/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 16:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 17:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 18:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 19:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 21:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/10/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 00:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 10:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 03:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 05:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 06:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 15:00 | 56 | 0 | 0 | 0
[14 empty] | 12/11/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 16:00 | 56 | 0 | 0 | 0
[14 empty] | 12/11/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 17:00 | 56 | 0 | 0 | 0
[14 empty] | 12/11/2020 10:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 11:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 19:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 12:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 20:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 13:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 14:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/11/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 15:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/11/2020 23:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 16:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/12/2020 00:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 17:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/12/2020 01:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 19:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 03:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 20:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 04:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 21:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 05:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 22:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 06:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/11/2020 23:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 00:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 08:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 01:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 02:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 10:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 03:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 04:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 05:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 13:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 06:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 14:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 07:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 08:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 16:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 09:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 17:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 10:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 11:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 12:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 20:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 13:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 21:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 14:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 22:00 | 58 | 0 | 0 | 0
[14 empty] | 12/12/2020 15:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/12/2020 23:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 16:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 00:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 17:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 01:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 18:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 02:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 03:00 | 56 | 0 | 0 | 0
[14 empty] | 12/12/2020 20:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 04:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 21:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 05:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 22:00 | 58 | 0 | 0 | 0 | [26 empty] | 12/13/2020 06:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/12/2020 23:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 07:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 00:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 08:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 01:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 09:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 02:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 10:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 03:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/13/2020 11:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 04:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 12:00 | 58 | 0 | 0 | 0
[14 empty] | 12/13/2020 05:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 13:00 | 60 | 0 | 0 | 0
[14 empty] | 12/13/2020 06:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 14:00 | 60 | 0 | 0 | 0
[14 empty] | 12/13/2020 07:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 15:00 | 59 | 0 | 0 | 0
[14 empty] | 12/13/2020 08:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 16:00 | 57 | 0 | 0 | 0
[14 empty] | 12/13/2020 09:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 17:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 10:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 11:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/13/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 12:00 | 58 | 0 | 0 | 0 | [26 empty] | 12/13/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 13:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/13/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 14:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/13/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 15:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/13/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 16:00 | 57 | 0 | 0 | 0 | [26 empty] | 12/14/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 17:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 01:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 18:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 19:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 20:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 04:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 21:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 22:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/13/2020 23:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 00:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 01:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 02:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 04:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 12:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 05:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 06:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 07:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 15:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 08:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 16:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 09:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 12:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 13:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 15:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/14/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 16:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 19:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 20:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 21:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/14/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 00:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 01:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 10:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 03:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 04:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 05:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 06:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 15:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 17:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 10:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 13:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 14:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 22:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 15:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/15/2020 23:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 00:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 17:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 01:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 02:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 19:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 04:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 05:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 22:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/15/2020 23:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 00:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 08:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 01:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 09:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 02:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 10:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 04:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 12:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 05:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 13:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 07:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 15:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 08:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 16:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 09:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 17:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 10:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 18:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 19:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 12:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 20:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 13:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 21:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 22:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 15:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/16/2020 23:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 16:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 00:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 17:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 01:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 18:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 02:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 19:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 20:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 04:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 21:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 05:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 22:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 06:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/16/2020 23:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 07:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 00:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 08:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 01:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 09:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 02:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 11:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 04:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 12:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 05:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 06:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 07:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 15:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 08:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 09:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 17:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 11:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 19:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 12:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 20:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 21:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 22:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 15:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/17/2020 23:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 00:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 17:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 02:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 19:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 03:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 20:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 04:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 21:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 22:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/17/2020 23:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 00:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 08:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 09:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 02:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 03:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 11:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 04:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 12:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 08:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 09:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 11:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 12:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 20:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 21:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 22:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/18/2020 23:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 00:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 01:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 02:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 19:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 03:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 20:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 04:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 21:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 05:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 22:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 06:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/18/2020 23:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 07:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 00:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 01:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 02:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 10:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 03:00 | 23 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 11:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 04:00 | 22 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 12:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 05:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 06:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 14:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 07:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 08:00 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 16:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 09:00 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 17:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 10:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 18:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 11:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 19:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 12:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 20:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 13:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 21:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 14:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/19/2020 23:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 16:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 17:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 01:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 18:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 19:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 20:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 21:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 22:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 06:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/19/2020 23:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 01:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 02:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 10:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 03:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 11:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 04:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 05:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 13:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 06:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 14:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 07:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 08:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 09:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 17:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 10:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 11:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 19:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 13:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 14:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/20/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 17:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 01:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 18:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 19:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 21:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 22:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/20/2020 23:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 00:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 01:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 02:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 10:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 13:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 07:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 08:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 09:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 10:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 13:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/21/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 16:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 17:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 18:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 19:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 20:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 22:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/21/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 00:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 01:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 04:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 09:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 10:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 11:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 12:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 13:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 14:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/22/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 16:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 18:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 19:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 20:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 21:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 22:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/22/2020 23:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 01:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 02:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 03:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 04:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 05:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 06:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 07:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 08:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 16:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 10:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 11:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 19:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 12:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 13:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 14:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 15:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/23/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 16:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 02:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 19:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 21:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 05:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 06:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/23/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 07:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/24/2020 00:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 08:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/24/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 09:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/24/2020 02:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 10:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/24/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 11:00 | 56 | 0 | 0 | 0
[14 empty] | 12/24/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 12:00 | 57 | 0 | 0 | 0
[14 empty] | 12/24/2020 05:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 13:00 | 56 | 0 | 0 | 0
[14 empty] | 12/24/2020 06:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 14:00 | 57 | 0 | 0 | 0
[14 empty] | 12/24/2020 07:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 15:00 | 58 | 0 | 0 | 0
[14 empty] | 12/24/2020 08:00 | 52 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 16:00 | 58 | 0 | 0 | 0
[14 empty] | 12/24/2020 09:00 | 53 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 17:00 | 57 | 0 | 0 | 0
[14 empty] | 12/24/2020 10:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/24/2020 18:00 | 56 | 0 | 0 | 0
[14 empty] | 12/24/2020 11:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/24/2020 19:00 | 58 | 0 | 0 | 0
[14 empty] | 12/24/2020 12:00 | 57 | 0 | 0 | 0 | [26 empty] | 12/24/2020 20:00 | 57 | 0 | 0 | 0
[14 empty] | 12/24/2020 13:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/24/2020 21:00 | 59 | 0 | 0 | 0
[14 empty] | 12/24/2020 14:00 | 57 | 0 | 0 | 0 | [26 empty] | 12/24/2020 22:00 | 59 | 0 | 0 | 0
[14 empty] | 12/24/2020 15:00 | 58 | 0 | 0 | 0 | [26 empty] | 12/24/2020 23:00 | 59 | 0 | 0 | 0
[14 empty] | 12/24/2020 16:00 | 58 | 0 | 0 | 0 | [26 empty] | 12/25/2020 00:00 | 59 | 0 | 0 | 0
[14 empty] | 12/24/2020 17:00 | 57 | 0 | 0 | 0 | [26 empty] | 12/25/2020 01:00 | 59 | 0 | 0 | 0
[14 empty] | 12/24/2020 18:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/25/2020 02:00 | 60 | 0 | 0 | 0
[14 empty] | 12/24/2020 19:00 | 58 | 0 | 0 | 0 | [26 empty] | 12/25/2020 03:00 | 60 | 0 | 0 | 0
[14 empty] | 12/24/2020 20:00 | 57 | 0 | 0 | 0 | [26 empty] | 12/25/2020 04:00 | 60 | 0 | 0 | 0
[14 empty] | 12/24/2020 21:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/25/2020 05:00 | 60 | 0 | 0 | 0
[14 empty] | 12/24/2020 22:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/25/2020 06:00 | 59 | 0 | 0 | 0
[14 empty] | 12/24/2020 23:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/25/2020 07:00 | 56 | 0 | 0 | 0
[14 empty] | 12/25/2020 00:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/25/2020 08:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 01:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/25/2020 09:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 02:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/25/2020 10:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 03:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/25/2020 11:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 04:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/25/2020 12:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 05:00 | 60 | 0 | 0 | 0 | [26 empty] | 12/25/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 06:00 | 59 | 0 | 0 | 0 | [26 empty] | 12/25/2020 14:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 07:00 | 56 | 0 | 0 | 0 | [26 empty] | 12/25/2020 15:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 08:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 09:00 | 55 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 10:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 11:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 12:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 20:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 13:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 14:00 | 54 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 15:00 | 51 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/25/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 16:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 00:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 17:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 01:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 02:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 19:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 03:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 20:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 04:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 05:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 22:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/25/2020 23:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 00:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 08:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 01:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 09:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 02:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 10:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 03:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 11:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 04:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 12:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 05:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 13:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 06:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 08:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 09:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 10:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 11:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 19:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 12:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 20:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 13:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 21:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 14:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 22:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 15:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/26/2020 23:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 16:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 00:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 17:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 18:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 02:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 19:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 03:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 20:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 04:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 21:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 22:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 06:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/26/2020 23:00 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 00:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 08:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 01:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 09:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 02:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 03:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 04:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 12:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 05:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 13:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 06:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 07:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 08:00 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 09:00 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 10:00 | 26 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 11:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 12:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 13:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 22:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 15:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/27/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 01:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 18:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 03:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 20:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 21:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 22:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/27/2020 23:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 00:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 08:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 01:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 02:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 03:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 04:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 06:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 07:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 08:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 12:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 13:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 14:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 15:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/28/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 16:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 17:00 | 50 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 18:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 19:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 20:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 21:00 | 49 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 22:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/28/2020 23:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 00:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 02:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 03:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 04:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 05:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 06:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 07:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 15:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 08:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 09:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 10:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 11:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 13:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 14:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 22:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 15:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/29/2020 23:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 16:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 17:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 01:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 18:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 02:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 19:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 20:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 04:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 21:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 05:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 22:00 | 32 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 06:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/29/2020 23:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 07:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 00:00 | 31 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 01:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 02:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 03:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 11:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 04:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 05:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 13:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 06:00 | 29 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 14:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 07:00 | 28 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 15:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 08:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 09:00 | 30 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 10:00 | 33 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 11:00 | 34 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 19:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 12:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 13:00 | 35 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 14:00 | 36 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 15:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/30/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 16:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 17:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 18:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 02:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 19:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 20:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 21:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 22:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/30/2020 23:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 00:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 01:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 02:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 03:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 04:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 05:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 06:00 | 47 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 07:00 | 48 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 08:00 | 46 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 16:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 09:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 10:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 11:00 | 45 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 19:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 12:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 13:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 14:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 15:00 | 44 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 2020-12-31 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 16:00 | 43 | #DIV/0! | #DIV/0! | #DIV/0! | [26 empty] | 12/31/2020 24:00 PM | 36 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 17:00 | 42 | #DIV/0! | #DIV/0! | #DIV/0! | [30 empty] | #DIV/0!
[14 empty] | 12/31/2020 18:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 19:00 | 41 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 20:00 | 40 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 21:00 | 39 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 22:00 | 38 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 2020-12-31 23:00 | 37 | #DIV/0! | #DIV/0! | #DIV/0!
[14 empty] | 12/31/2020 24:00 PM | 36 | #DIV/0! | #DIV/0! | #DIV/0!

## Constants (hidden)
Physics Constants |  |  | Other constants
Specific Heat Air Cp | 1.005 | (kJ/(kg K) | HDD_TMY3_65 | 4884 | F.Days/yr | https://rredc.nrel.gov/solar/old_data/nsrdb/1991-2010/
Density of Air | 1.2 | kg/m^3 | HDD_TMY3_64 | 4633 | F.Days/yr
Cp(Steam) | 2.08 | J/g/K | HDD_TMY3_63 | 4398 | F.Days/yr
L(water) | 2260 | J/g | HDD_TMY3_62 | 4169 | F.Days/yr
Cp(Water) | 4.1813 | J/g/K | HDD_TMY3_61 | 3949 | F.Days/yr
Water Heat Content | 8.33 | BTU/Gal-F | HDD_TMY3_60 | 3735 | F.Days/yr
Specific Heat Capacity of Air | 0.24 | Btu/lb.F | HDD_TMY3_59 | 3530 | F.Days/yr
Density | 0.07636 | lb/sf^3 | HDD_TMY3_58 | 3332 | F.Days/yr
Volumetric Heat Capacity of Air | 0.018326 | Btu/sf^3.F | HDD_TMY3_57 | 3142 | F.Days/yr
Atmospheric Pressure | 1013 | hPa | HDD_TMY3_56 | 2957 | F.Days/yr
Atmospheric Pressure | 101300 | Pa | HDD_TMY3_55 | 2777 | F.Days/yr
Atmospheric Pressure | 1.013 | bar
Atmospheric Pressure | 14.6923 | psi |  |  |  | 59F – 3530 F.days/year
HDD | 4487.1325 | days.F/yr |  |  |  | 58F – 3332
CDD | 1374.01 | days.F/yr |  |  |  | 57F – 3142
EFLHheat | 1012 | hrs |  |  |  | 56 F – 2957
ESFheat | 6.8% | % |  |  |  | 55F – 2777
59F – 3530 F.days/year
58F – 3332
57F – 3142
56 F – 2957
55F – 2777

## TMY3 (hidden)
TMY3 Import
Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch | Don't Touch
Date (MM/DD/YYYY) |  |  | Time (HH:MM) | 725030TY.csv |  |  | Pre-Retrofit
HDD | Base | 65 |  | 4400.52 | Fahrenheit | Enthalpy | Heating Schedule 1 | Heating Schedule 2 | Cooling Schedule 1 | Cooling Schedule 2
CDD | Base | 65 |  | 1287.3975
1985-01-01 | 1 | 1 | 0.041667 | -2.2 | 28.04 | 8.0742 |  | 28.04
1985-01-01 | 1 | 1 | 0.083333 | -2.2 | 28.04 | 8.0742 |  | 28.04
1985-01-01 | 1 | 1 | 0.125 | -2.2 | 28.04 | 8.0742 |  | 28.04
1985-01-01 | 1 | 1 | 0.16667 | -2.8 | 26.96 | 7.8123 |  | 26.96
1985-01-01 | 1 | 1 | 0.20833 | -2.8 | 26.96 | 7.8763 |  | 26.96
1985-01-01 | 1 | 1 | 0.25 | -3.3 | 26.06 | 7.6631 | 26.06
1985-01-01 | 1 | 1 | 0.29167 | -2.8 | 26.96 | 8.0365 | 26.96
1985-01-01 | 1 | 1 | 0.33333 | -2.8 | 26.96 | 8.0365 | 26.96
1985-01-01 | 1 | 1 | 0.375 | -1.7 | 28.94 | 8.4184 | 28.94
1985-01-01 | 1 | 1 | 0.41667 | -0.6 | 30.92 | 8.882 | 30.92
1985-01-01 | 1 | 1 | 0.45833 | 0 | 32 | 9.2973 | 32
1985-01-01 | 1 | 1 | 0.5 | 2.2 | 35.96 | 10.4341 | 35.96
1985-01-01 | 1 | 1 | 0.54167 | 2.8 | 37.04 | 10.8725 | 37.04
1985-01-01 | 1 | 1 | 0.58333 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-01 | 1 | 1 | 0.625 | 2.2 | 35.96 | 10.8151 | 35.96
1985-01-01 | 1 | 1 | 0.66667 | 2.8 | 37.04 | 11.4199 | 37.04
1985-01-01 | 1 | 1 | 0.70833 | 1.7 | 35.06 | 10.9351 | 35.06
1985-01-01 | 1 | 1 | 0.75 | 2.2 | 35.96 | 11.1488 | 35.96
1985-01-01 | 1 | 1 | 0.79167 | 2.8 | 37.04 | 11.7188 | 37.04
1985-01-01 | 1 | 1 | 0.83333 | 2.2 | 35.96 | 11.5783 | 35.96
1985-01-01 | 1 | 1 | 0.875 | 3.3 | 37.94 | 12.5038 | 37.94
1985-01-01 | 1 | 1 | 0.91667 | 3.3 | 37.94 | 12.8144 |  | 37.94
1985-01-01 | 1 | 1 | 0.95833 | 3.3 | 37.94 | 12.8144 |  | 37.94
1985-01-01 | 1 | 1 | 1 | 3.9 | 39.02 | 13.2366 |  | 39.02
1985-01-02 | 2 | 1 | 0.041667 | 4.4 | 39.92 | 13.6493 |  | 39.92
1985-01-02 | 2 | 1 | 0.083333 | 4.4 | 39.92 | 13.8176 |  | 39.92
1985-01-02 | 2 | 1 | 0.125 | 5 | 41 | 14.2614 |  | 41
1985-01-02 | 2 | 1 | 0.16667 | 4.4 | 39.92 | 13.9859 |  | 39.92
1985-01-02 | 2 | 1 | 0.20833 | 4.4 | 39.92 | 13.8176 |  | 39.92
1985-01-02 | 2 | 1 | 0.25 | 3.9 | 39.02 | 13.7779 | 39.02
1985-01-02 | 2 | 1 | 0.29167 | 3.9 | 39.02 | 13.6154 | 39.02
1985-01-02 | 2 | 1 | 0.33333 | 3.3 | 37.94 | 13.3328 | 37.94
1985-01-02 | 2 | 1 | 0.375 | 4.4 | 39.92 | 13.8176 | 39.92
1985-01-02 | 2 | 1 | 0.41667 | 5 | 41 | 14.2614 | 41
1985-01-02 | 2 | 1 | 0.45833 | 5.6 | 42.08 | 14.1629 | 42.08
1985-01-02 | 2 | 1 | 0.5 | 6.7 | 44.06 | 14.4374 | 44.06
1985-01-02 | 2 | 1 | 0.54167 | 7.2 | 44.96 | 14.6542 | 44.96
1985-01-02 | 2 | 1 | 0.58333 | 7.8 | 46.04 | 14.9358 | 46.04
1985-01-02 | 2 | 1 | 0.625 | 8.3 | 46.94 | 14.7739 | 46.94
1985-01-02 | 2 | 1 | 0.66667 | 8.3 | 46.94 | 14.627 | 46.94
1985-01-02 | 2 | 1 | 0.70833 | 7.8 | 46.04 | 15.149 | 46.04
1985-01-02 | 2 | 1 | 0.75 | 7.2 | 44.96 | 14.0412 | 44.96
1985-01-02 | 2 | 1 | 0.79167 | 6.7 | 44.06 | 14.3057 | 44.06
1985-01-02 | 2 | 1 | 0.83333 | 6.1 | 42.98 | 14.3981 | 42.98
1985-01-02 | 2 | 1 | 0.875 | 6.1 | 42.98 | 14.3981 | 42.98
1985-01-02 | 2 | 1 | 0.91667 | 6.1 | 42.98 | 14.0191 |  | 42.98
1985-01-02 | 2 | 1 | 0.95833 | 5.6 | 42.08 | 13.6141 |  | 42.08
1985-01-02 | 2 | 1 | 1 | 4.4 | 39.92 | 12.6416 |  | 39.92
1985-01-03 | 3 | 1 | 0.041667 | 2.8 | 37.04 | 12.1178 |  | 37.04
1985-01-03 | 3 | 1 | 0.083333 | 2.2 | 35.96 | 11.865 |  | 35.96
1985-01-03 | 3 | 1 | 0.125 | 2.2 | 35.96 | 11.7216 |  | 35.96
1985-01-03 | 3 | 1 | 0.16667 | 2.2 | 35.96 | 11.7216 |  | 35.96
1985-01-03 | 3 | 1 | 0.20833 | 1.7 | 35.06 | 11.6259 |  | 35.06
1985-01-03 | 3 | 1 | 0.25 | 1.7 | 35.06 | 11.4876 | 35.06
1985-01-03 | 3 | 1 | 0.29167 | 1.7 | 35.06 | 11.4876 | 35.06
1985-01-03 | 3 | 1 | 0.33333 | 2.2 | 35.96 | 11.7216 | 35.96
1985-01-03 | 3 | 1 | 0.375 | 2.2 | 35.96 | 11.7216 | 35.96
1985-01-03 | 3 | 1 | 0.41667 | 2.8 | 37.04 | 11.9681 | 37.04
1985-01-03 | 3 | 1 | 0.45833 | 3.3 | 37.94 | 12.0383 | 37.94
1985-01-03 | 3 | 1 | 0.5 | 3.9 | 39.02 | 12.1566 | 39.02
1985-01-03 | 3 | 1 | 0.54167 | 4.4 | 39.92 | 12.2504 | 39.92
1985-01-03 | 3 | 1 | 0.58333 | 3.9 | 39.02 | 11.7794 | 39.02
1985-01-03 | 3 | 1 | 0.625 | 4.4 | 39.92 | 12.1388 | 39.92
1985-01-03 | 3 | 1 | 0.66667 | 4.4 | 39.92 | 12.0272 | 39.92
1985-01-03 | 3 | 1 | 0.70833 | 3.9 | 39.02 | 11.7794 | 39.02
1985-01-03 | 3 | 1 | 0.75 | 3.3 | 37.94 | 11.3157 | 37.94
1985-01-03 | 3 | 1 | 0.79167 | 3.3 | 37.94 | 11.3157 | 37.94
1985-01-03 | 3 | 1 | 0.83333 | 2.8 | 37.04 | 11.1709 | 37.04
1985-01-03 | 3 | 1 | 0.875 | 1.7 | 35.06 | 10.7052 | 35.06
1985-01-03 | 3 | 1 | 0.91667 | 1.7 | 35.06 | 10.7052 |  | 35.06
1985-01-03 | 3 | 1 | 0.95833 | 1.7 | 35.06 | 10.7052 |  | 35.06
1985-01-03 | 3 | 1 | 1 | 1.7 | 35.06 | 10.6133 |  | 35.06
1985-01-04 | 4 | 1 | 0.041667 | 1.7 | 35.06 | 10.7052 |  | 35.06
1985-01-04 | 4 | 1 | 0.083333 | 1.7 | 35.06 | 10.7052 |  | 35.06
1985-01-04 | 4 | 1 | 0.125 | 1.1 | 33.98 | 10.5682 |  | 33.98
1985-01-04 | 4 | 1 | 0.16667 | 0.6 | 33.08 | 10.2231 |  | 33.08
1985-01-04 | 4 | 1 | 0.20833 | 0 | 32 | 9.8652 |  | 32
1985-01-04 | 4 | 1 | 0.25 | -1.1 | 30.02 | 9.1978 | 30.02
1985-01-04 | 4 | 1 | 0.29167 | -1.7 | 28.94 | 8.6645 | 28.94
1985-01-04 | 4 | 1 | 0.33333 | -1.7 | 28.94 | 8.6645 | 28.94
1985-01-04 | 4 | 1 | 0.375 | -1.1 | 30.02 | 8.9388 | 30.02
1985-01-04 | 4 | 1 | 0.41667 | -1.1 | 30.02 | 8.9388 | 30.02
1985-01-04 | 4 | 1 | 0.45833 | 0 | 32 | 9.4189 | 32
1985-01-04 | 4 | 1 | 0.5 | 0.6 | 33.08 | 9.5024 | 33.08
1985-01-04 | 4 | 1 | 0.54167 | 1.1 | 33.98 | 9.7766 | 33.98
1985-01-04 | 4 | 1 | 0.58333 | 1.7 | 35.06 | 10.0622 | 35.06
1985-01-04 | 4 | 1 | 0.625 | 1.7 | 35.06 | 9.9704 | 35.06
1985-01-04 | 4 | 1 | 0.66667 | 2.2 | 35.96 | 10.1962 | 35.96
1985-01-04 | 4 | 1 | 0.70833 | 1.7 | 35.06 | 9.9704 | 35.06
1985-01-04 | 4 | 1 | 0.75 | 1.7 | 35.06 | 9.8787 | 35.06
1985-01-04 | 4 | 1 | 0.79167 | 1.7 | 35.06 | 10.0622 | 35.06
1985-01-04 | 4 | 1 | 0.83333 | 1.1 | 33.98 | 9.7766 | 33.98
1985-01-04 | 4 | 1 | 0.875 | 1.1 | 33.98 | 9.8644 | 33.98
1985-01-04 | 4 | 1 | 0.91667 | 0.6 | 33.08 | 9.6718 |  | 33.08
1985-01-04 | 4 | 1 | 0.95833 | 0.6 | 33.08 | 9.5871 |  | 33.08
1985-01-04 | 4 | 1 | 1 | 0 | 32 | 9.2973 |  | 32
1985-01-05 | 5 | 1 | 0.041667 | 0 | 32 | 9.4189 |  | 32
1985-01-05 | 5 | 1 | 0.083333 | 0 | 32 | 9.4189 |  | 32
1985-01-05 | 5 | 1 | 0.125 | -0.6 | 30.92 | 9.1519 |  | 30.92
1985-01-05 | 5 | 1 | 0.16667 | -0.6 | 30.92 | 8.9976 |  | 30.92
1985-01-05 | 5 | 1 | 0.20833 | -0.6 | 30.92 | 8.9976 |  | 30.92
1985-01-05 | 5 | 1 | 0.25 | -1.1 | 30.02 | 8.68 | 30.02
1985-01-05 | 5 | 1 | 0.29167 | -0.6 | 30.92 | 8.8435 | 30.92
1985-01-05 | 5 | 1 | 0.33333 | -0.6 | 30.92 | 8.8435 | 30.92
1985-01-05 | 5 | 1 | 0.375 | 0 | 32 | 9.0947 | 32
1985-01-05 | 5 | 1 | 0.41667 | 1.1 | 33.98 | 9.6448 | 33.98
1985-01-05 | 5 | 1 | 0.45833 | 2.2 | 35.96 | 10.1011 | 35.96
1985-01-05 | 5 | 1 | 0.5 | 2.2 | 35.96 | 10.1962 | 35.96
1985-01-05 | 5 | 1 | 0.54167 | 3.3 | 37.94 | 10.4402 | 37.94
1985-01-05 | 5 | 1 | 0.58333 | 3.9 | 39.02 | 11.1876 | 39.02
1985-01-05 | 5 | 1 | 0.625 | 3.3 | 37.94 | 11.3157 | 37.94
1985-01-05 | 5 | 1 | 0.66667 | 3.9 | 39.02 | 11.8872 | 39.02
1985-01-05 | 5 | 1 | 0.70833 | 4.4 | 39.92 | 12.1388 | 39.92
1985-01-05 | 5 | 1 | 0.75 | 4.4 | 39.92 | 11.8598 | 39.92
1985-01-05 | 5 | 1 | 0.79167 | 4.4 | 39.92 | 11.8598 | 39.92
1985-01-05 | 5 | 1 | 0.83333 | 4.4 | 39.92 | 12.0272 | 39.92
1985-01-05 | 5 | 1 | 0.875 | 3.9 | 39.02 | 12.1566 | 39.02
1985-01-05 | 5 | 1 | 0.91667 | 4.4 | 39.92 | 12.2504 |  | 39.92
1985-01-05 | 5 | 1 | 0.95833 | 4.4 | 39.92 | 11.8598 |  | 39.92
1985-01-05 | 5 | 1 | 1 | 4.4 | 39.92 | 11.6925 |  | 39.92
1985-01-06 | 6 | 1 | 0.041667 | 3.9 | 39.02 | 12.0488 |  | 39.02
1985-01-06 | 6 | 1 | 0.083333 | 4.4 | 39.92 | 12.418 |  | 39.92
1985-01-06 | 6 | 1 | 0.125 | 4.4 | 39.92 | 12.5298 |  | 39.92
1985-01-06 | 6 | 1 | 0.16667 | 3.9 | 39.02 | 12.4263 |  | 39.02
1985-01-06 | 6 | 1 | 0.20833 | 4.4 | 39.92 | 12.5298 |  | 39.92
1985-01-06 | 6 | 1 | 0.25 | 4.4 | 39.92 | 12.6416 | 39.92
1985-01-06 | 6 | 1 | 0.29167 | 4.4 | 39.92 | 12.9771 | 39.92
1985-01-06 | 6 | 1 | 0.33333 | 4.4 | 39.92 | 13.0891 | 39.92
1985-01-06 | 6 | 1 | 0.375 | 5.6 | 42.08 | 13.6141 | 42.08
1985-01-06 | 6 | 1 | 0.41667 | 5.6 | 42.08 | 13.7969 | 42.08
1985-01-06 | 6 | 1 | 0.45833 | 6.1 | 42.98 | 14.2086 | 42.98
1985-01-06 | 6 | 1 | 0.5 | 6.1 | 42.98 | 14.2086 | 42.98
1985-01-06 | 6 | 1 | 0.54167 | 6.7 | 44.06 | 14.635 | 44.06
1985-01-06 | 6 | 1 | 0.58333 | 5.6 | 42.08 | 14.7125 | 42.08
1985-01-06 | 6 | 1 | 0.625 | 5.6 | 42.08 | 14.8959 | 42.08
1985-01-06 | 6 | 1 | 0.66667 | 5 | 41 | 14.613 | 41
1985-01-06 | 6 | 1 | 0.70833 | 5.6 | 42.08 | 14.5292 | 42.08
1985-01-06 | 6 | 1 | 0.75 | 5 | 41 | 14.2614 | 41
1985-01-06 | 6 | 1 | 0.79167 | 5 | 41 | 14.0858 | 41
1985-01-06 | 6 | 1 | 0.83333 | 5 | 41 | 14.0858 | 41
1985-01-06 | 6 | 1 | 0.875 | 5 | 41 | 14.0858 | 41
1985-01-06 | 6 | 1 | 0.91667 | 4.4 | 39.92 | 13.4812 |  | 39.92
1985-01-06 | 6 | 1 | 0.95833 | 4.4 | 39.92 | 13.3131 |  | 39.92
1985-01-06 | 6 | 1 | 1 | 4.4 | 39.92 | 13.4812 |  | 39.92
1985-01-07 | 7 | 1 | 0.041667 | 3.9 | 39.02 | 13.2366 |  | 39.02
1985-01-07 | 7 | 1 | 0.083333 | 3.3 | 37.94 | 12.5038 |  | 37.94
1985-01-07 | 7 | 1 | 0.125 | 2.8 | 37.04 | 12.1178 |  | 37.04
1985-01-07 | 7 | 1 | 0.16667 | 2.8 | 37.04 | 11.8185 |  | 37.04
1985-01-07 | 7 | 1 | 0.20833 | 2.8 | 37.04 | 11.5693 |  | 37.04
1985-01-07 | 7 | 1 | 0.25 | 2.2 | 35.96 | 11.0534 | 35.96
1985-01-07 | 7 | 1 | 0.29167 | 2.2 | 35.96 | 10.9104 | 35.96
1985-01-07 | 7 | 1 | 0.33333 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-07 | 7 | 1 | 0.375 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-07 | 7 | 1 | 0.41667 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-07 | 7 | 1 | 0.45833 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-07 | 7 | 1 | 0.5 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-07 | 7 | 1 | 0.54167 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-07 | 7 | 1 | 0.58333 | 1.7 | 35.06 | 10.7052 | 35.06
1985-01-07 | 7 | 1 | 0.625 | 1.7 | 35.06 | 10.7052 | 35.06
1985-01-07 | 7 | 1 | 0.66667 | 1.7 | 35.06 | 10.8431 | 35.06
1985-01-07 | 7 | 1 | 0.70833 | 1.1 | 33.98 | 10.1721 | 33.98
1985-01-07 | 7 | 1 | 0.75 | 0 | 32 | 9.0947 | 32
1985-01-07 | 7 | 1 | 0.79167 | -0.6 | 30.92 | 8.6124 | 30.92
1985-01-07 | 7 | 1 | 0.83333 | -1.7 | 28.94 | 8.2076 | 28.94
1985-01-07 | 7 | 1 | 0.875 | -2.2 | 28.04 | 7.9395 | 28.04
1985-01-07 | 7 | 1 | 0.91667 | -2.8 | 26.96 | 7.8123 |  | 26.96
1985-01-07 | 7 | 1 | 0.95833 | -3.3 | 26.06 | 7.7245 |  | 26.06
1985-01-07 | 7 | 1 | 1 | -3.9 | 24.98 | 7.4792 |  | 24.98
1985-01-08 | 8 | 1 | 0.041667 | -4.4 | 24.08 | 7.1729 |  | 24.08
1985-01-08 | 8 | 1 | 0.083333 | -5 | 23 | 6.8435 |  | 23
1985-01-08 | 8 | 1 | 0.125 | -5.6 | 21.92 | 6.5425 |  | 21.92
1985-01-08 | 8 | 1 | 0.16667 | -5.6 | 21.92 | 6.4669 |  | 21.92
1985-01-08 | 8 | 1 | 0.20833 | -6.1 | 21.02 | 6.1273 |  | 21.02
1985-01-08 | 8 | 1 | 0.25 | -6.1 | 21.02 | 6.1273 | 21.02
1985-01-08 | 8 | 1 | 0.29167 | -6.1 | 21.02 | 6.1996 | 21.02
1985-01-08 | 8 | 1 | 0.33333 | -5.6 | 21.92 | 6.8195 | 21.92
1985-01-08 | 8 | 1 | 0.375 | -6.1 | 21.02 | 6.6579 | 21.02
1985-01-08 | 8 | 1 | 0.41667 | -5.6 | 21.92 | 6.9708 | 21.92
1985-01-08 | 8 | 1 | 0.45833 | -5 | 23 | 7.3212 | 23
1985-01-08 | 8 | 1 | 0.5 | -4.4 | 24.08 | 7.76 | 24.08
1985-01-08 | 8 | 1 | 0.54167 | -3.3 | 26.06 | 8.3389 | 26.06
1985-01-08 | 8 | 1 | 0.58333 | -2.8 | 26.96 | 8.5494 | 26.96
1985-01-08 | 8 | 1 | 0.625 | -2.2 | 28.04 | 9.0186 | 28.04
1985-01-08 | 8 | 1 | 0.66667 | -1.1 | 30.02 | 9.4941 | 30.02
1985-01-08 | 8 | 1 | 0.70833 | -1.1 | 30.02 | 9.42 | 30.02
1985-01-08 | 8 | 1 | 0.75 | -1.1 | 30.02 | 9.4941 | 30.02
1985-01-08 | 8 | 1 | 0.79167 | -1.1 | 30.02 | 9.6423 | 30.02
1985-01-08 | 8 | 1 | 0.83333 | -0.6 | 30.92 | 9.9628 | 30.92
1985-01-08 | 8 | 1 | 0.875 | -1.1 | 30.02 | 9.7165 | 30.02
1985-01-08 | 8 | 1 | 0.91667 | -1.1 | 30.02 | 10.0132 |  | 30.02
1985-01-08 | 8 | 1 | 0.95833 | -1.1 | 30.02 | 10.1245 |  | 30.02
1985-01-08 | 8 | 1 | 1 | -1.1 | 30.02 | 10.2731 |  | 30.02
1985-01-09 | 9 | 1 | 0.041667 | -1.7 | 28.94 | 10.0037 |  | 28.94
1985-01-09 | 9 | 1 | 0.083333 | -2.2 | 28.04 | 9.7963 |  | 28.04
1985-01-09 | 9 | 1 | 0.125 | -1.7 | 28.94 | 10.145 |  | 28.94
1985-01-09 | 9 | 1 | 0.16667 | -1.7 | 28.94 | 10.3217 |  | 28.94
1985-01-09 | 9 | 1 | 0.20833 | -1.7 | 28.94 | 10.145 |  | 28.94
1985-01-09 | 9 | 1 | 0.25 | -1.1 | 30.02 | 10.5703 | 30.02
1985-01-09 | 9 | 1 | 0.29167 | -0.6 | 30.92 | 10.8144 | 30.92
1985-01-09 | 9 | 1 | 0.33333 | -0.6 | 30.92 | 10.9307 | 30.92
1985-01-09 | 9 | 1 | 0.375 | -0.6 | 30.92 | 10.9307 | 30.92
1985-01-09 | 9 | 1 | 0.41667 | -0.6 | 30.92 | 11.1246 | 30.92
1985-01-09 | 9 | 1 | 0.45833 | 0.6 | 33.08 | 11.6265 | 33.08
1985-01-09 | 9 | 1 | 0.5 | 0.6 | 33.08 | 11.6265 | 33.08
1985-01-09 | 9 | 1 | 0.54167 | 0.6 | 33.08 | 11.797 | 33.08
1985-01-09 | 9 | 1 | 0.58333 | 1.1 | 33.98 | 12.2012 | 33.98
1985-01-09 | 9 | 1 | 0.625 | 1.1 | 33.98 | 12.2012 | 33.98
1985-01-09 | 9 | 1 | 0.66667 | 1.7 | 35.06 | 12.6416 | 35.06
1985-01-09 | 9 | 1 | 0.70833 | 1.7 | 35.06 | 12.6416 | 35.06
1985-01-09 | 9 | 1 | 0.75 | 1.7 | 35.06 | 12.2719 | 35.06
1985-01-09 | 9 | 1 | 0.79167 | 1.7 | 35.06 | 12.4567 | 35.06
1985-01-09 | 9 | 1 | 0.83333 | 1.1 | 33.98 | 12.2012 | 33.98
1985-01-09 | 9 | 1 | 0.875 | 1.1 | 33.98 | 12.2012 | 33.98
1985-01-09 | 9 | 1 | 0.91667 | 1.7 | 35.06 | 12.4567 |  | 35.06
1985-01-09 | 9 | 1 | 0.95833 | 2.8 | 37.04 | 12.9672 |  | 37.04
1985-01-09 | 9 | 1 | 1 | 3.9 | 39.02 | 12.7502 |  | 39.02
1985-01-10 | 10 | 1 | 0.041667 | 4.4 | 39.92 | 12.8093 |  | 39.92
1985-01-10 | 10 | 1 | 0.083333 | 3.9 | 39.02 | 12.9122 |  | 39.02
1985-01-10 | 10 | 1 | 0.125 | 3.9 | 39.02 | 13.2366 |  | 39.02
1985-01-10 | 10 | 1 | 0.16667 | 3.9 | 39.02 | 13.2366 |  | 39.02
1985-01-10 | 10 | 1 | 0.20833 | 3.3 | 37.94 | 12.8144 |  | 37.94
1985-01-10 | 10 | 1 | 0.25 | 3.3 | 37.94 | 12.8144 | 37.94
1985-01-10 | 10 | 1 | 0.29167 | 3.3 | 37.94 | 12.5038 | 37.94
1985-01-10 | 10 | 1 | 0.33333 | 3.3 | 37.94 | 12.5038 | 37.94
1985-01-10 | 10 | 1 | 0.375 | 3.9 | 39.02 | 12.7502 | 39.02
1985-01-10 | 10 | 1 | 0.41667 | 4.4 | 39.92 | 12.9771 | 39.92
1985-01-10 | 10 | 1 | 0.45833 | 4.4 | 39.92 | 12.8093 | 39.92
1985-01-10 | 10 | 1 | 0.5 | 4.4 | 39.92 | 12.8093 | 39.92
1985-01-10 | 10 | 1 | 0.54167 | 4.4 | 39.92 | 12.8093 | 39.92
1985-01-10 | 10 | 1 | 0.58333 | 4.4 | 39.92 | 12.6416 | 39.92
1985-01-10 | 10 | 1 | 0.625 | 4.4 | 39.92 | 12.5298 | 39.92
1985-01-10 | 10 | 1 | 0.66667 | 4.4 | 39.92 | 12.2504 | 39.92
1985-01-10 | 10 | 1 | 0.70833 | 4.4 | 39.92 | 12.1388 | 39.92
1985-01-10 | 10 | 1 | 0.75 | 2.8 | 37.04 | 11.4199 | 37.04
1985-01-10 | 10 | 1 | 0.79167 | 2.2 | 35.96 | 10.9104 | 35.96
1985-01-10 | 10 | 1 | 0.83333 | 1.1 | 33.98 | 10.7003 | 33.98
1985-01-10 | 10 | 1 | 0.875 | 0 | 32 | 9.6623 | 32
1985-01-10 | 10 | 1 | 0.91667 | -0.6 | 30.92 | 9.229 |  | 30.92
1985-01-10 | 10 | 1 | 0.95833 | -1.1 | 30.02 | 8.5322 |  | 30.02
1985-01-10 | 10 | 1 | 1 | -2.2 | 28.04 | 7.8048 |  | 28.04
1985-01-11 | 11 | 1 | 0.041667 | -2.8 | 26.96 | 7.4923 |  | 26.96
1985-01-11 | 11 | 1 | 0.083333 | -3.3 | 26.06 | 7.295 |  | 26.06
1985-01-11 | 11 | 1 | 0.125 | -3.3 | 26.06 | 7.1418 |  | 26.06
1985-01-11 | 11 | 1 | 0.16667 | -3.9 | 24.98 | 6.8091 |  | 24.98
1985-01-11 | 11 | 1 | 0.20833 | -4.4 | 24.08 | 6.7542 |  | 24.08
1985-01-11 | 11 | 1 | 0.25 | -4.4 | 24.08 | 6.8658 | 24.08
1985-01-11 | 11 | 1 | 0.29167 | -4.4 | 24.08 | 6.9216 | 24.08
1985-01-11 | 11 | 1 | 0.33333 | -3.9 | 24.98 | 7.1877 | 24.98
1985-01-11 | 11 | 1 | 0.375 | -3.9 | 24.98 | 7.0712 | 24.98
1985-01-11 | 11 | 1 | 0.41667 | -4.4 | 24.08 | 7.1171 | 24.08
1985-01-11 | 11 | 1 | 0.45833 | -5 | 23 | 7.7198 | 23
1985-01-11 | 11 | 1 | 0.5 | -6.1 | 21.02 | 7.1167 | 21.02
1985-01-11 | 11 | 1 | 0.54167 | -5 | 23 | 7.7996 | 23
1985-01-11 | 11 | 1 | 0.58333 | -4.4 | 24.08 | 8.2921 | 24.08
1985-01-11 | 11 | 1 | 0.625 | -4.4 | 24.08 | 8.4323 | 24.08
1985-01-11 | 11 | 1 | 0.66667 | -3.3 | 26.06 | 9.0469 | 26.06
1985-01-11 | 11 | 1 | 0.70833 | -2.2 | 28.04 | 9.7963 | 28.04
1985-01-11 | 11 | 1 | 0.75 | -1.7 | 28.94 | 10.145 | 28.94
1985-01-11 | 11 | 1 | 0.79167 | -1.1 | 30.02 | 10.719 | 30.02
1985-01-11 | 11 | 1 | 0.83333 | -1.7 | 28.94 | 10.3217 | 28.94
1985-01-11 | 11 | 1 | 0.875 | -0.6 | 30.92 | 11.2798 | 30.92
1985-01-11 | 11 | 1 | 0.91667 | -0.6 | 30.92 | 11.2798 |  | 30.92
1985-01-11 | 11 | 1 | 0.95833 | 0.6 | 33.08 | 11.797 |  | 33.08
1985-01-11 | 11 | 1 | 1 | 1.1 | 33.98 | 12.3783 |  | 33.98
1985-01-12 | 12 | 1 | 0.041667 | 1.7 | 35.06 | 12.8266 |  | 35.06
1985-01-12 | 12 | 1 | 0.083333 | 1.7 | 35.06 | 12.8266 |  | 35.06
1985-01-12 | 12 | 1 | 0.125 | 2.8 | 37.04 | 13.4679 |  | 37.04
1985-01-12 | 12 | 1 | 0.16667 | 3.3 | 37.94 | 13.8519 |  | 37.94
1985-01-12 | 12 | 1 | 0.20833 | 2.8 | 37.04 | 13.6684 |  | 37.04
1985-01-12 | 12 | 1 | 0.25 | 2.8 | 37.04 | 13.6684 | 37.04
1985-01-12 | 12 | 1 | 0.29167 | 2.8 | 37.04 | 13.6684 | 37.04
1985-01-12 | 12 | 1 | 0.33333 | 0.6 | 33.08 | 11.797 | 33.08
1985-01-12 | 12 | 1 | 0.375 | 0 | 32 | 11.3707 | 32
1985-01-12 | 12 | 1 | 0.41667 | 0 | 32 | 11.0446 | 32
1985-01-12 | 12 | 1 | 0.45833 | 0.6 | 33.08 | 11.456 | 33.08
1985-01-12 | 12 | 1 | 0.5 | 0 | 32 | 10.8817 | 32
1985-01-12 | 12 | 1 | 0.54167 | 0.6 | 33.08 | 11.3283 | 33.08
1985-01-12 | 12 | 1 | 0.58333 | 0.6 | 33.08 | 11.3283 | 33.08
1985-01-12 | 12 | 1 | 0.625 | 1.1 | 33.98 | 11.5382 | 33.98
1985-01-12 | 12 | 1 | 0.66667 | 1.1 | 33.98 | 11.8475 | 33.98
1985-01-12 | 12 | 1 | 0.70833 | 1.1 | 33.98 | 11.8475 | 33.98
1985-01-12 | 12 | 1 | 0.75 | 1.1 | 33.98 | 11.8475 | 33.98
1985-01-12 | 12 | 1 | 0.79167 | 1.1 | 33.98 | 12.0243 | 33.98
1985-01-12 | 12 | 1 | 0.83333 | 1.1 | 33.98 | 12.0243 | 33.98
1985-01-12 | 12 | 1 | 0.875 | 1.1 | 33.98 | 12.0243 | 33.98
1985-01-12 | 12 | 1 | 0.91667 | 1.7 | 35.06 | 12.2719 |  | 35.06
1985-01-12 | 12 | 1 | 0.95833 | 1.7 | 35.06 | 12.2719 |  | 35.06
1985-01-12 | 12 | 1 | 1 | 2.2 | 35.96 | 12.4869 |  | 35.96
1985-01-13 | 13 | 1 | 0.041667 | 2.2 | 35.96 | 12.6785 |  | 35.96
1985-01-13 | 13 | 1 | 0.083333 | 2.8 | 37.04 | 12.7672 |  | 37.04
1985-01-13 | 13 | 1 | 0.125 | 3.3 | 37.94 | 12.9698 |  | 37.94
1985-01-13 | 13 | 1 | 0.16667 | 3.3 | 37.94 | 13.1772 |  | 37.94
1985-01-13 | 13 | 1 | 0.20833 | 2.2 | 35.96 | 12.0084 |  | 35.96
1985-01-13 | 13 | 1 | 0.25 | 1.1 | 33.98 | 11.3616 | 33.98
1985-01-13 | 13 | 1 | 0.29167 | 0.6 | 33.08 | 10.8603 | 33.08
1985-01-13 | 13 | 1 | 0.33333 | 0 | 32 | 10.4747 | 32
1985-01-13 | 13 | 1 | 0.375 | -0.6 | 30.92 | 10.0788 | 30.92
1985-01-13 | 13 | 1 | 0.41667 | -0.6 | 30.92 | 9.9628 | 30.92
1985-01-13 | 13 | 1 | 0.45833 | -0.6 | 30.92 | 9.7309 | 30.92
1985-01-13 | 13 | 1 | 0.5 | 0 | 32 | 9.987 | 32
1985-01-13 | 13 | 1 | 0.54167 | 0 | 32 | 9.8652 | 32
1985-01-13 | 13 | 1 | 0.58333 | 0 | 32 | 9.987 | 32
1985-01-13 | 13 | 1 | 0.625 | 0 | 32 | 9.8652 | 32
1985-01-13 | 13 | 1 | 0.66667 | 0.6 | 33.08 | 10.1382 | 33.08
1985-01-13 | 13 | 1 | 0.70833 | 0 | 32 | 9.784 | 32
1985-01-13 | 13 | 1 | 0.75 | -0.6 | 30.92 | 9.422 | 30.92
1985-01-13 | 13 | 1 | 0.79167 | -0.6 | 30.92 | 9.422 | 30.92
1985-01-13 | 13 | 1 | 0.83333 | -1.1 | 30.02 | 9.1978 | 30.02
1985-01-13 | 13 | 1 | 0.875 | -1.7 | 28.94 | 8.946 | 28.94
1985-01-13 | 13 | 1 | 0.91667 | -2.2 | 28.04 | 8.7147 |  | 28.04
1985-01-13 | 13 | 1 | 0.95833 | -2.2 | 28.04 | 8.7147 |  | 28.04
1985-01-13 | 13 | 1 | 1 | -2.8 | 26.96 | 8.357 |  | 26.96
1985-01-14 | 14 | 1 | 0.041667 | -2.8 | 26.96 | 8.2928 |  | 26.96
1985-01-14 | 14 | 1 | 0.083333 | -2.8 | 26.96 | 8.2928 |  | 26.96
1985-01-14 | 14 | 1 | 0.125 | -2.8 | 26.96 | 8.2928 |  | 26.96
1985-01-14 | 14 | 1 | 0.16667 | -3.3 | 26.06 | 8.0623 |  | 26.06
1985-01-14 | 14 | 1 | 0.20833 | -3.3 | 26.06 | 7.9701 |  | 26.06
1985-01-14 | 14 | 1 | 0.25 | -3.3 | 26.06 | 8.0623 | 26.06
1985-01-14 | 14 | 1 | 0.29167 | -3.3 | 26.06 | 8.1545 | 26.06
1985-01-14 | 14 | 1 | 0.33333 | -2.8 | 26.96 | 8.4532 | 26.96
1985-01-14 | 14 | 1 | 0.375 | -1.1 | 30.02 | 9.3089 | 30.02
1985-01-14 | 14 | 1 | 0.41667 | -0.6 | 30.92 | 9.422 | 30.92
1985-01-14 | 14 | 1 | 0.45833 | 0 | 32 | 9.6623 | 32
1985-01-14 | 14 | 1 | 0.5 | 0.6 | 33.08 | 10.0109 | 33.08
1985-01-14 | 14 | 1 | 0.54167 | 0.6 | 33.08 | 10.1382 | 33.08
1985-01-14 | 14 | 1 | 0.58333 | 2.2 | 35.96 | 11.0534 | 35.96
1985-01-14 | 14 | 1 | 0.625 | 2.8 | 37.04 | 11.4199 | 37.04
1985-01-14 | 14 | 1 | 0.66667 | 2.8 | 37.04 | 11.4199 | 37.04
1985-01-14 | 14 | 1 | 0.70833 | 2.8 | 37.04 | 11.4199 | 37.04
1985-01-14 | 14 | 1 | 0.75 | 2.8 | 37.04 | 11.5693 | 37.04
1985-01-14 | 14 | 1 | 0.79167 | 2.8 | 37.04 | 11.7188 | 37.04
1985-01-14 | 14 | 1 | 0.83333 | 2.8 | 37.04 | 11.8185 | 37.04
1985-01-14 | 14 | 1 | 0.875 | 2.8 | 37.04 | 11.9681 | 37.04
1985-01-14 | 14 | 1 | 0.91667 | 2.2 | 35.96 | 11.7216 |  | 35.96
1985-01-14 | 14 | 1 | 0.95833 | 1.7 | 35.06 | 11.6259 |  | 35.06
1985-01-14 | 14 | 1 | 1 | 1.7 | 35.06 | 11.6259 |  | 35.06
1985-01-15 | 15 | 1 | 0.041667 | 1.7 | 35.06 | 11.6259 |  | 35.06
1985-01-15 | 15 | 1 | 0.083333 | 1.7 | 35.06 | 11.8103 |  | 35.06
1985-01-15 | 15 | 1 | 0.125 | 2.2 | 35.96 | 12.0084 |  | 35.96
1985-01-15 | 15 | 1 | 0.16667 | 1.7 | 35.06 | 11.8103 |  | 35.06
1985-01-15 | 15 | 1 | 0.20833 | 1.1 | 33.98 | 11.5382 |  | 33.98
1985-01-15 | 15 | 1 | 0.25 | 1.7 | 35.06 | 11.6259 | 35.06
1985-01-15 | 15 | 1 | 0.29167 | 1.7 | 35.06 | 11.6259 | 35.06
1985-01-15 | 15 | 1 | 0.33333 | 2.2 | 35.96 | 12.0084 | 35.96
1985-01-15 | 15 | 1 | 0.375 | 3.9 | 39.02 | 12.7502 | 39.02
1985-01-15 | 15 | 1 | 0.41667 | 5 | 41 | 13.5595 | 41
1985-01-15 | 15 | 1 | 0.45833 | 6.1 | 42.98 | 14.0191 | 42.98
1985-01-15 | 15 | 1 | 0.5 | 6.7 | 44.06 | 14.4374 | 44.06
1985-01-15 | 15 | 1 | 0.54167 | 7.8 | 46.04 | 15.2913 | 46.04
1985-01-15 | 15 | 1 | 0.58333 | 8.9 | 48.02 | 15.7943 | 48.02
1985-01-15 | 15 | 1 | 0.625 | 9.4 | 48.92 | 15.6038 | 48.92
1985-01-15 | 15 | 1 | 0.66667 | 9.4 | 48.92 | 15.4453 | 48.92
1985-01-15 | 15 | 1 | 0.70833 | 7.2 | 44.96 | 14.3135 | 44.96
1985-01-15 | 15 | 1 | 0.75 | 6.1 | 42.98 | 14.2086 | 42.98
1985-01-15 | 15 | 1 | 0.79167 | 5 | 41 | 13.9103 | 41
1985-01-15 | 15 | 1 | 0.83333 | 4.4 | 39.92 | 13.6493 | 39.92
1985-01-15 | 15 | 1 | 0.875 | 3.3 | 37.94 | 13.1772 | 37.94
1985-01-15 | 15 | 1 | 0.91667 | 2.8 | 37.04 | 13.1173 |  | 37.04
1985-01-15 | 15 | 1 | 0.95833 | 2.8 | 37.04 | 13.1173 |  | 37.04
1985-01-15 | 15 | 1 | 1 | 2.8 | 37.04 | 13.4679 |  | 37.04
1985-01-16 | 16 | 1 | 0.041667 | 2.8 | 37.04 | 13.6684 |  | 37.04
1985-01-16 | 16 | 1 | 0.083333 | 3.3 | 37.94 | 14.1118 |  | 37.94
1985-01-16 | 16 | 1 | 0.125 | 2.8 | 37.04 | 13.6684 |  | 37.04
1985-01-16 | 16 | 1 | 0.16667 | 3.3 | 37.94 | 14.1118 |  | 37.94
1985-01-16 | 16 | 1 | 0.20833 | 3.3 | 37.94 | 14.2678 |  | 37.94
1985-01-16 | 16 | 1 | 0.25 | 3.3 | 37.94 | 14.2678 | 37.94
1985-01-16 | 16 | 1 | 0.29167 | 3.3 | 37.94 | 14.2678 | 37.94
1985-01-16 | 16 | 1 | 0.33333 | 3.3 | 37.94 | 14.2678 | 37.94
1985-01-16 | 16 | 1 | 0.375 | 3.9 | 39.02 | 14.7544 | 39.02
1985-01-16 | 16 | 1 | 0.41667 | 4.4 | 39.92 | 15.1667 | 39.92
1985-01-16 | 16 | 1 | 0.45833 | 5.6 | 42.08 | 15.937 | 42.08
1985-01-16 | 16 | 1 | 0.5 | 10.6 | 51.08 | 20.8704 | 51.08
1985-01-16 | 16 | 1 | 0.54167 | 11.7 | 53.06 | 22.0145 | 53.06
1985-01-16 | 16 | 1 | 0.58333 | 11.7 | 53.06 | 22.0145 | 53.06
1985-01-16 | 16 | 1 | 0.625 | 11.1 | 51.98 | 21.1142 | 51.98
1985-01-16 | 16 | 1 | 0.66667 | 11.7 | 53.06 | 22.0145 | 53.06
1985-01-16 | 16 | 1 | 0.70833 | 11.1 | 51.98 | 21.1142 | 51.98
1985-01-16 | 16 | 1 | 0.75 | 11.7 | 53.06 | 22.0145 | 53.06
1985-01-16 | 16 | 1 | 0.79167 | 11.7 | 53.06 | 22.0145 | 53.06
1985-01-16 | 16 | 1 | 0.83333 | 11.1 | 51.98 | 21.3849 | 51.98
1985-01-16 | 16 | 1 | 0.875 | 10 | 50 | 20.2649 | 50
1985-01-16 | 16 | 1 | 0.91667 | 10.6 | 51.08 | 20.8704 |  | 51.08
1985-01-16 | 16 | 1 | 0.95833 | 10 | 50 | 20.2649 |  | 50
1985-01-16 | 16 | 1 | 1 | 10 | 50 | 19.6798 |  | 50
1985-01-17 | 17 | 1 | 0.041667 | 9.4 | 48.92 | 18.5503 |  | 48.92
1985-01-17 | 17 | 1 | 0.083333 | 8.3 | 46.94 | 17.8738 |  | 46.94
1985-01-17 | 17 | 1 | 0.125 | 8.3 | 46.94 | 17.5773 |  | 46.94
1985-01-17 | 17 | 1 | 0.16667 | 8.9 | 48.02 | 17.4093 |  | 48.02
1985-01-17 | 17 | 1 | 0.20833 | 8.3 | 46.94 | 16.6895 |  | 46.94
1985-01-17 | 17 | 1 | 0.25 | 8.3 | 46.94 | 16.4679 | 46.94
1985-01-17 | 17 | 1 | 0.29167 | 8.3 | 46.94 | 16.2465 | 46.94
1985-01-17 | 17 | 1 | 0.33333 | 7.8 | 46.04 | 15.8609 | 46.04
1985-01-17 | 17 | 1 | 0.375 | 7.8 | 46.04 | 15.8609 | 46.04
1985-01-17 | 17 | 1 | 0.41667 | 8.3 | 46.94 | 15.8777 | 46.94
1985-01-17 | 17 | 1 | 0.45833 | 8.3 | 46.94 | 15.6567 | 46.94
1985-01-17 | 17 | 1 | 0.5 | 7.8 | 46.04 | 15.2913 | 46.04
1985-01-17 | 17 | 1 | 0.54167 | 7.2 | 44.96 | 14.8588 | 44.96
1985-01-17 | 17 | 1 | 0.58333 | 7.2 | 44.96 | 14.3135 | 44.96
1985-01-17 | 17 | 1 | 0.625 | 7.2 | 44.96 | 14.1773 | 44.96
1985-01-17 | 17 | 1 | 0.66667 | 6.7 | 44.06 | 13.7795 | 44.06
1985-01-17 | 17 | 1 | 0.70833 | 6.7 | 44.06 | 13.7795 | 44.06
1985-01-17 | 17 | 1 | 0.75 | 6.1 | 42.98 | 13.5145 | 42.98
1985-01-17 | 17 | 1 | 0.79167 | 6.1 | 42.98 | 13.3885 | 42.98
1985-01-17 | 17 | 1 | 0.83333 | 5 | 41 | 13.0339 | 41
1985-01-17 | 17 | 1 | 0.875 | 5 | 41 | 12.5092 | 41
1985-01-17 | 17 | 1 | 0.91667 | 4.4 | 39.92 | 12.1388 |  | 39.92
1985-01-17 | 17 | 1 | 0.95833 | 4.4 | 39.92 | 12.1388 |  | 39.92
1985-01-17 | 17 | 1 | 1 | 4.4 | 39.92 | 12.1388 |  | 39.92
1985-01-18 | 18 | 1 | 0.041667 | 4.4 | 39.92 | 12.0272 |  | 39.92
1985-01-18 | 18 | 1 | 0.083333 | 3.9 | 39.02 | 11.8872 |  | 39.02
1985-01-18 | 18 | 1 | 0.125 | 3.3 | 37.94 | 11.7801 |  | 37.94
1985-01-18 | 18 | 1 | 0.16667 | 3.3 | 37.94 | 11.935 |  | 37.94
1985-01-18 | 18 | 1 | 0.20833 | 3.3 | 37.94 | 12.0383 |  | 37.94
1985-01-18 | 18 | 1 | 0.25 | 3.3 | 37.94 | 12.0383 | 37.94
1985-01-18 | 18 | 1 | 0.29167 | 3.3 | 37.94 | 12.1934 | 37.94
1985-01-18 | 18 | 1 | 0.33333 | 3.3 | 37.94 | 12.0383 | 37.94
1985-01-18 | 18 | 1 | 0.375 | 3.3 | 37.94 | 11.6252 | 37.94
1985-01-18 | 18 | 1 | 0.41667 | 3.3 | 37.94 | 11.1094 | 37.94
1985-01-18 | 18 | 1 | 0.45833 | 3.3 | 37.94 | 11.0064 | 37.94
1985-01-18 | 18 | 1 | 0.5 | 3.9 | 39.02 | 11.1876 | 39.02
1985-01-18 | 18 | 1 | 0.54167 | 3.9 | 39.02 | 11.3489 | 39.02
1985-01-18 | 18 | 1 | 0.58333 | 4.4 | 39.92 | 11.581 | 39.92
1985-01-18 | 18 | 1 | 0.625 | 4.4 | 39.92 | 11.581 | 39.92
1985-01-18 | 18 | 1 | 0.66667 | 5 | 41 | 11.869 | 41
1985-01-18 | 18 | 1 | 0.70833 | 3.9 | 39.02 | 11.1876 | 39.02
1985-01-18 | 18 | 1 | 0.75 | 3.9 | 39.02 | 11.2413 | 39.02
1985-01-18 | 18 | 1 | 0.79167 | 3.9 | 39.02 | 11.2413 | 39.02
1985-01-18 | 18 | 1 | 0.83333 | 3.9 | 39.02 | 11.5641 | 39.02
1985-01-18 | 18 | 1 | 0.875 | 3.9 | 39.02 | 11.6717 | 39.02
1985-01-18 | 18 | 1 | 0.91667 | 4.4 | 39.92 | 12.0272 |  | 39.92
1985-01-18 | 18 | 1 | 0.95833 | 3.9 | 39.02 | 11.5641 |  | 39.02
1985-01-18 | 18 | 1 | 1 | 3.3 | 37.94 | 11.3157 |  | 37.94
1985-01-19 | 19 | 1 | 0.041667 | 3.3 | 37.94 | 11.4188 |  | 37.94
1985-01-19 | 19 | 1 | 0.083333 | 3.3 | 37.94 | 11.3157 |  | 37.94
1985-01-19 | 19 | 1 | 0.125 | 3.3 | 37.94 | 11.4188 |  | 37.94
1985-01-19 | 19 | 1 | 0.16667 | 3.9 | 39.02 | 11.6717 |  | 39.02
1985-01-19 | 19 | 1 | 0.20833 | 3.3 | 37.94 | 11.4188 |  | 37.94
1985-01-19 | 19 | 1 | 0.25 | 3.3 | 37.94 | 11.6252 | 37.94
1985-01-19 | 19 | 1 | 0.29167 | 2.8 | 37.04 | 11.3203 | 37.04
1985-01-19 | 19 | 1 | 0.33333 | 3.3 | 37.94 | 11.522 | 37.94
1985-01-19 | 19 | 1 | 0.375 | 3.9 | 39.02 | 11.7794 | 39.02
1985-01-19 | 19 | 1 | 0.41667 | 4.4 | 39.92 | 12.0272 | 39.92
1985-01-19 | 19 | 1 | 0.45833 | 5.6 | 42.08 | 12.6408 | 42.08
1985-01-19 | 19 | 1 | 0.5 | 6.7 | 44.06 | 13.2542 | 44.06
1985-01-19 | 19 | 1 | 0.54167 | 7.2 | 44.96 | 13.4972 | 44.96
1985-01-19 | 19 | 1 | 0.58333 | 8.3 | 46.94 | 14.1866 | 46.94
1985-01-19 | 19 | 1 | 0.625 | 8.9 | 48.02 | 14.4925 | 48.02
1985-01-19 | 19 | 1 | 0.66667 | 9.4 | 48.92 | 14.6537 | 48.92
1985-01-19 | 19 | 1 | 0.70833 | 8.3 | 46.94 | 14.4801 | 46.94
1985-01-19 | 19 | 1 | 0.75 | 8.3 | 46.94 | 14.4801 | 46.94
1985-01-19 | 19 | 1 | 0.79167 | 8.9 | 48.02 | 14.9514 | 48.02
1985-01-19 | 19 | 1 | 0.83333 | 7.8 | 46.04 | 14.4387 | 46.04
1985-01-19 | 19 | 1 | 0.875 | 7.8 | 46.04 | 14.1549 | 46.04
1985-01-19 | 19 | 1 | 0.91667 | 7.2 | 44.96 | 14.0412 |  | 44.96
1985-01-19 | 19 | 1 | 0.95833 | 7.2 | 44.96 | 13.9051 |  | 44.96
1985-01-19 | 19 | 1 | 1 | 7.2 | 44.96 | 13.9051 |  | 44.96
1985-01-20 | 20 | 1 | 0.041667 | 7.2 | 44.96 | 14.0412 |  | 44.96
1985-01-20 | 20 | 1 | 0.083333 | 6.1 | 42.98 | 13.7037 |  | 42.98
1985-01-20 | 20 | 1 | 0.125 | 5.6 | 42.08 | 13.4923 |  | 42.08
1985-01-20 | 20 | 1 | 0.16667 | 5.6 | 42.08 | 13.4923 |  | 42.08
1985-01-20 | 20 | 1 | 0.20833 | 5.6 | 42.08 | 13.6141 |  | 42.08
1985-01-20 | 20 | 1 | 0.25 | 5.6 | 42.08 | 13.6141 | 42.08
1985-01-20 | 20 | 1 | 0.29167 | 5.6 | 42.08 | 13.4923 | 42.08
1985-01-20 | 20 | 1 | 0.33333 | 5 | 41 | 13.5595 | 41
1985-01-20 | 20 | 1 | 0.375 | 5.6 | 42.08 | 13.7969 | 42.08
1985-01-20 | 20 | 1 | 0.41667 | 7.2 | 44.96 | 14.0412 | 44.96
1985-01-20 | 20 | 1 | 0.45833 | 8.3 | 46.94 | 14.9944 | 46.94
1985-01-20 | 20 | 1 | 0.5 | 10 | 50 | 15.8594 | 50
1985-01-20 | 20 | 1 | 0.54167 | 10.6 | 51.08 | 16.3653 | 51.08
1985-01-20 | 20 | 1 | 0.58333 | 11.1 | 51.98 | 16.3667 | 51.98
1985-01-20 | 20 | 1 | 0.625 | 11.1 | 51.98 | 16.3667 | 51.98
1985-01-20 | 20 | 1 | 0.66667 | 10 | 50 | 15.8594 | 50
1985-01-20 | 20 | 1 | 0.70833 | 9.4 | 48.92 | 15.6038 | 48.92
1985-01-20 | 20 | 1 | 0.75 | 8.9 | 48.02 | 15.4109 | 48.02
1985-01-20 | 20 | 1 | 0.79167 | 8.3 | 46.94 | 15.1414 | 46.94
1985-01-20 | 20 | 1 | 0.83333 | 8.3 | 46.94 | 15.3622 | 46.94
1985-01-20 | 20 | 1 | 0.875 | 7.8 | 46.04 | 15.149 | 46.04
1985-01-20 | 20 | 1 | 0.91667 | 7.8 | 46.04 | 15.149 |  | 46.04
1985-01-20 | 20 | 1 | 0.95833 | 7.2 | 44.96 | 15.0635 |  | 44.96
1985-01-20 | 20 | 1 | 1 | 6.7 | 44.06 | 14.8327 |  | 44.06
1985-01-21 | 21 | 1 | 0.041667 | 5.6 | 42.08 | 14.7125 |  | 42.08
1985-01-21 | 21 | 1 | 0.083333 | 4.4 | 39.92 | 14.379 |  | 39.92
1985-01-21 | 21 | 1 | 0.125 | 3.9 | 39.02 | 14.1573 |  | 39.02
1985-01-21 | 21 | 1 | 0.16667 | 2.8 | 37.04 | 13.4679 |  | 37.04
1985-01-21 | 21 | 1 | 0.20833 | 2.2 | 35.96 | 13.0141 |  | 35.96
1985-01-21 | 21 | 1 | 0.25 | 1.7 | 35.06 | 12.8266 | 35.06
1985-01-21 | 21 | 1 | 0.29167 | 1.7 | 35.06 | 12.8266 | 35.06
1985-01-21 | 21 | 1 | 0.33333 | 2.2 | 35.96 | 13.0141 | 35.96
1985-01-21 | 21 | 1 | 0.375 | -1.1 | 30.02 | 10.719 | 30.02
1985-01-21 | 21 | 1 | 0.41667 | -2.8 | 26.96 | 9.3846 | 26.96
1985-01-21 | 21 | 1 | 0.45833 | -3.9 | 24.98 | 8.6478 | 24.98
1985-01-21 | 21 | 1 | 0.5 | -3.9 | 24.98 | 8.6478 | 24.98
1985-01-21 | 21 | 1 | 0.54167 | -4.4 | 24.08 | 8.068 | 24.08
1985-01-21 | 21 | 1 | 0.58333 | -3.3 | 26.06 | 8.3389 | 26.06
1985-01-21 | 21 | 1 | 0.625 | -3.9 | 24.98 | 8.063 | 24.98
1985-01-21 | 21 | 1 | 0.66667 | -3.9 | 24.98 | 8.063 | 24.98
1985-01-21 | 21 | 1 | 0.70833 | -3.9 | 24.98 | 7.9754 | 24.98
1985-01-21 | 21 | 1 | 0.75 | -4.4 | 24.08 | 7.5922 | 24.08
1985-01-21 | 21 | 1 | 0.79167 | -5 | 23 | 7.2415 | 23
1985-01-21 | 21 | 1 | 0.83333 | -5.6 | 21.92 | 6.8195 | 21.92
1985-01-21 | 21 | 1 | 0.875 | -7.2 | 19.04 | 5.8375 | 19.04
1985-01-21 | 21 | 1 | 0.91667 | -7.8 | 17.96 | 5.4507 |  | 17.96
1985-01-21 | 21 | 1 | 0.95833 | -8.3 | 17.06 | 5.0663 |  | 17.06
1985-01-21 | 21 | 1 | 1 | -8.9 | 15.98 | 4.7567 |  | 15.98
1985-01-22 | 22 | 1 | 0.041667 | -9.4 | 15.08 | 4.4465 |  | 15.08
1985-01-22 | 22 | 1 | 0.083333 | -10.6 | 12.92 | 3.9408 |  | 12.92
1985-01-22 | 22 | 1 | 0.125 | -10.6 | 12.92 | 3.9893 |  | 12.92
1985-01-22 | 22 | 1 | 0.16667 | -10.6 | 12.92 | 3.9408 |  | 12.92
1985-01-22 | 22 | 1 | 0.20833 | -11.7 | 10.94 | 3.4593 |  | 10.94
1985-01-22 | 22 | 1 | 0.25 | -11.7 | 10.94 | 3.4153 | 10.94
1985-01-22 | 22 | 1 | 0.29167 | -12.2 | 10.04 | 3.2902 | 10.04
1985-01-22 | 22 | 1 | 0.33333 | -12.2 | 10.04 | 3.1642 | 10.04
1985-01-22 | 22 | 1 | 0.375 | -11.7 | 10.94 | 3.3714 | 10.94
1985-01-22 | 22 | 1 | 0.41667 | -11.1 | 12.02 | 3.6877 | 12.02
1985-01-22 | 22 | 1 | 0.45833 | -10.6 | 12.92 | 3.8114 | 12.92
1985-01-22 | 22 | 1 | 0.5 | -9.4 | 15.08 | 4.4105 | 15.08
1985-01-22 | 22 | 1 | 0.54167 | -8.9 | 15.98 | 4.6249 | 15.98
1985-01-22 | 22 | 1 | 0.58333 | -7.8 | 17.96 | 5.0979 | 17.96
1985-01-22 | 22 | 1 | 0.625 | -7.2 | 19.04 | 5.3779 | 19.04
1985-01-22 | 22 | 1 | 0.66667 | -6.7 | 19.94 | 5.5387 | 19.94
1985-01-22 | 22 | 1 | 0.70833 | -6.7 | 19.94 | 5.5387 | 19.94
1985-01-22 | 22 | 1 | 0.75 | -6.7 | 19.94 | 5.5843 | 19.94
1985-01-22 | 22 | 1 | 0.79167 | -7.2 | 19.04 | 5.3779 | 19.04
1985-01-22 | 22 | 1 | 0.83333 | -7.8 | 17.96 | 5.0979 | 17.96
1985-01-22 | 22 | 1 | 0.875 | -7.8 | 17.96 | 5.0979 | 17.96
1985-01-22 | 22 | 1 | 0.91667 | -8.3 | 17.06 | 4.8875 |  | 17.06
1985-01-22 | 22 | 1 | 0.95833 | -8.3 | 17.06 | 4.8875 |  | 17.06
1985-01-22 | 22 | 1 | 1 | -8.3 | 17.06 | 4.9868 |  | 17.06
1985-01-23 | 23 | 1 | 0.041667 | -8.3 | 17.06 | 4.9868 |  | 17.06
1985-01-23 | 23 | 1 | 0.083333 | -8.3 | 17.06 | 4.9868 |  | 17.06
1985-01-23 | 23 | 1 | 0.125 | -8.3 | 17.06 | 4.9273 |  | 17.06
1985-01-23 | 23 | 1 | 0.16667 | -8.3 | 17.06 | 5.0265 |  | 17.06
1985-01-23 | 23 | 1 | 0.20833 | -8.3 | 17.06 | 5.0663 |  | 17.06
1985-01-23 | 23 | 1 | 0.25 | -7.8 | 17.96 | 5.3469 | 17.96
1985-01-23 | 23 | 1 | 0.29167 | -6.7 | 19.94 | 5.8815 | 19.94
1985-01-23 | 23 | 1 | 0.33333 | -6.1 | 21.02 | 6.1273 | 21.02
1985-01-23 | 23 | 1 | 0.375 | -4.4 | 24.08 | 6.7542 | 24.08
1985-01-23 | 23 | 1 | 0.41667 | -2.8 | 26.96 | 7.8763 | 26.96
1985-01-23 | 23 | 1 | 0.45833 | -1.1 | 30.02 | 8.6061 | 30.02
1985-01-23 | 23 | 1 | 0.5 | -0.6 | 30.92 | 8.9976 | 30.92
1985-01-23 | 23 | 1 | 0.54167 | 0.6 | 33.08 | 9.5871 | 33.08
1985-01-23 | 23 | 1 | 0.58333 | 1.1 | 33.98 | 9.8644 | 33.98
1985-01-23 | 23 | 1 | 0.625 | 1.7 | 35.06 | 10.154 | 35.06
1985-01-23 | 23 | 1 | 0.66667 | 1.7 | 35.06 | 10.154 | 35.06
1985-01-23 | 23 | 1 | 0.70833 | 1.7 | 35.06 | 10.2458 | 35.06
1985-01-23 | 23 | 1 | 0.75 | 1.7 | 35.06 | 10.4295 | 35.06
1985-01-23 | 23 | 1 | 0.79167 | 1.7 | 35.06 | 10.5213 | 35.06
1985-01-23 | 23 | 1 | 0.83333 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-23 | 23 | 1 | 0.875 | 1.7 | 35.06 | 10.6133 | 35.06
1985-01-23 | 23 | 1 | 0.91667 | 1.7 | 35.06 | 10.7052 |  | 35.06
1985-01-23 | 23 | 1 | 0.95833 | 1.7 | 35.06 | 10.8431 |  | 35.06
1985-01-23 | 23 | 1 | 1 | 1.7 | 35.06 | 10.9351 |  | 35.06
1985-01-24 | 24 | 1 | 0.041667 | 1.1 | 33.98 | 10.7003 |  | 33.98
1985-01-24 | 24 | 1 | 0.083333 | 1.1 | 33.98 | 10.7003 |  | 33.98
1985-01-24 | 24 | 1 | 0.125 | 1.7 | 35.06 | 11.0732 |  | 35.06
1985-01-24 | 24 | 1 | 0.16667 | 1.7 | 35.06 | 10.9351 |  | 35.06
1985-01-24 | 24 | 1 | 0.20833 | 1.7 | 35.06 | 10.9351 |  | 35.06
1985-01-24 | 24 | 1 | 0.25 | 1.7 | 35.06 | 10.9351 | 35.06
1985-01-24 | 24 | 1 | 0.29167 | 1.1 | 33.98 | 10.7003 | 33.98
1985-01-24 | 24 | 1 | 0.33333 | 1.7 | 35.06 | 10.9351 | 35.06
1985-01-24 | 24 | 1 | 0.375 | 2.2 | 35.96 | 11.0534 | 35.96
1985-01-24 | 24 | 1 | 0.41667 | 2.8 | 37.04 | 10.7731 | 37.04
1985-01-24 | 24 | 1 | 0.45833 | 3.9 | 39.02 | 11.0801 | 39.02
1985-01-24 | 24 | 1 | 0.5 | 3.9 | 39.02 | 10.9189 | 39.02
1985-01-24 | 24 | 1 | 0.54167 | 3.9 | 39.02 | 10.8652 | 39.02
1985-01-24 | 24 | 1 | 0.58333 | 3.9 | 39.02 | 10.9189 | 39.02
1985-01-24 | 24 | 1 | 0.625 | 3.9 | 39.02 | 10.8652 | 39.02
1985-01-24 | 24 | 1 | 0.66667 | 3.9 | 39.02 | 10.9189 | 39.02
1985-01-24 | 24 | 1 | 0.70833 | 3.9 | 39.02 | 10.9189 | 39.02
1985-01-24 | 24 | 1 | 0.75 | 2.8 | 37.04 | 10.2268 | 37.04
1985-01-24 | 24 | 1 | 0.79167 | 1.7 | 35.06 | 9.5578 | 35.06
1985-01-24 | 24 | 1 | 0.83333 | 0.6 | 33.08 | 9.0792 | 33.08
1985-01-24 | 24 | 1 | 0.875 | 0.6 | 33.08 | 9.3331 | 33.08
1985-01-24 | 24 | 1 | 0.91667 | -0.6 | 30.92 | 8.7664 |  | 30.92
1985-01-24 | 24 | 1 | 0.95833 | -2.2 | 28.04 | 8.3437 |  | 28.04
1985-01-24 | 24 | 1 | 1 | -3.3 | 26.06 | 7.7245 |  | 26.06
1985-01-25 | 25 | 1 | 0.041667 | -3.9 | 24.98 | 7.2751 |  | 24.98
1985-01-25 | 25 | 1 | 0.083333 | -4.4 | 24.08 | 6.7542 |  | 24.08
1985-01-25 | 25 | 1 | 0.125 | -5 | 23 | 6.4459 |  | 23
1985-01-25 | 25 | 1 | 0.16667 | -6.1 | 21.02 | 6.031 |  | 21.02
1985-01-25 | 25 | 1 | 0.20833 | -6.7 | 19.94 | 5.8129 |  | 19.94
1985-01-25 | 25 | 1 | 0.25 | -7.2 | 19.04 | 5.5966 | 19.04
1985-01-25 | 25 | 1 | 0.29167 | -7.2 | 19.04 | 5.5966 | 19.04
1985-01-25 | 25 | 1 | 0.33333 | -7.8 | 17.96 | 5.3469 | 17.96
1985-01-25 | 25 | 1 | 0.375 | -7.8 | 17.96 | 5.2431 | 17.96
1985-01-25 | 25 | 1 | 0.41667 | -7.2 | 19.04 | 5.4654 | 19.04
1985-01-25 | 25 | 1 | 0.45833 | -7.2 | 19.04 | 5.4654 | 19.04
1985-01-25 | 25 | 1 | 0.5 | -6.7 | 19.94 | 5.6758 | 19.94
1985-01-25 | 25 | 1 | 0.54167 | -6.1 | 21.02 | 5.9828 | 21.02
1985-01-25 | 25 | 1 | 0.58333 | -5.6 | 21.92 | 6.1398 | 21.92
1985-01-25 | 25 | 1 | 0.625 | -5 | 23 | 6.4194 | 23
1985-01-25 | 25 | 1 | 0.66667 | -4.4 | 24.08 | 6.6705 | 24.08
1985-01-25 | 25 | 1 | 0.70833 | -4.4 | 24.08 | 6.6147 | 24.08
1985-01-25 | 25 | 1 | 0.75 | -4.4 | 24.08 | 6.6147 | 24.08
1985-01-25 | 25 | 1 | 0.79167 | -4.4 | 24.08 | 6.6147 | 24.08
1985-01-25 | 25 | 1 | 0.83333 | -3.9 | 24.98 | 6.9256 | 24.98
1985-01-25 | 25 | 1 | 0.875 | -3.9 | 24.98 | 6.9256 | 24.98
1985-01-25 | 25 | 1 | 0.91667 | -3.9 | 24.98 | 6.9838 |  | 24.98
1985-01-25 | 25 | 1 | 0.95833 | -4.4 | 24.08 | 6.7542 |  | 24.08
1985-01-25 | 25 | 1 | 1 | -3.9 | 24.98 | 7.0129 |  | 24.98
1985-01-26 | 26 | 1 | 0.041667 | -3.9 | 24.98 | 7.0129 |  | 24.98
1985-01-26 | 26 | 1 | 0.083333 | -4.4 | 24.08 | 6.8658 |  | 24.08
1985-01-26 | 26 | 1 | 0.125 | -4.4 | 24.08 | 6.8658 |  | 24.08
1985-01-26 | 26 | 1 | 0.16667 | -5 | 23 | 6.5519 |  | 23
1985-01-26 | 26 | 1 | 0.20833 | -5 | 23 | 6.6049 |  | 23
1985-01-26 | 26 | 1 | 0.25 | -5.6 | 21.92 | 6.3411 | 21.92
1985-01-26 | 26 | 1 | 0.29167 | -5.6 | 21.92 | 6.4166 | 21.92
1985-01-26 | 26 | 1 | 0.33333 | -5 | 23 | 6.6579 | 23
1985-01-26 | 26 | 1 | 0.375 | -4.4 | 24.08 | 6.9216 | 24.08
1985-01-26 | 26 | 1 | 0.41667 | -3.3 | 26.06 | 7.3563 | 26.06
1985-01-26 | 26 | 1 | 0.45833 | -2.8 | 26.96 | 7.5563 | 26.96
1985-01-26 | 26 | 1 | 0.5 | -1.7 | 28.94 | 7.9619 | 28.94
1985-01-26 | 26 | 1 | 0.54167 | -1.1 | 30.02 | 8.3475 | 30.02
1985-01-26 | 26 | 1 | 0.58333 | -0.6 | 30.92 | 8.5739 | 30.92
1985-01-26 | 26 | 1 | 0.625 | 0 | 32 | 8.8922 | 32
1985-01-26 | 26 | 1 | 0.66667 | 0.6 | 33.08 | 9.1638 | 33.08
1985-01-26 | 26 | 1 | 0.70833 | 0 | 32 | 9.0947 | 32
1985-01-26 | 26 | 1 | 0.75 | 0 | 32 | 9.4189 | 32
1985-01-26 | 26 | 1 | 0.79167 | 0.6 | 33.08 | 9.8413 | 33.08
1985-01-26 | 26 | 1 | 0.83333 | 0.6 | 33.08 | 10.0109 | 33.08
1985-01-26 | 26 | 1 | 0.875 | 0.6 | 33.08 | 10.1382 | 33.08
1985-01-26 | 26 | 1 | 0.91667 | 1.1 | 33.98 | 10.5682 |  | 33.98
1985-01-26 | 26 | 1 | 0.95833 | 1.1 | 33.98 | 10.7003 |  | 33.98
1985-01-26 | 26 | 1 | 1 | 1.1 | 33.98 | 10.5682 |  | 33.98
1985-01-27 | 27 | 1 | 0.041667 | 0.6 | 33.08 | 10.4778 |  | 33.08
1985-01-27 | 27 | 1 | 0.083333 | 0.6 | 33.08 | 10.3504 |  | 33.08
1985-01-27 | 27 | 1 | 0.125 | 0 | 32 | 10.1901 |  | 32
1985-01-27 | 27 | 1 | 0.16667 | 0 | 32 | 10.4747 |  | 32
1985-01-27 | 27 | 1 | 0.20833 | -0.6 | 30.92 | 9.7309 |  | 30.92
1985-01-27 | 27 | 1 | 0.25 | -0.6 | 30.92 | 9.422 | 30.92
1985-01-27 | 27 | 1 | 0.29167 | -1.1 | 30.02 | 9.0868 | 30.02
1985-01-27 | 27 | 1 | 0.33333 | -1.1 | 30.02 | 9.0868 | 30.02
1985-01-27 | 27 | 1 | 0.375 | -0.6 | 30.92 | 9.422 | 30.92
1985-01-27 | 27 | 1 | 0.41667 | 0.6 | 33.08 | 9.6718 | 33.08
1985-01-27 | 27 | 1 | 0.45833 | 1.7 | 35.06 | 10.154 | 35.06
1985-01-27 | 27 | 1 | 0.5 | 2.2 | 35.96 | 10.3389 | 35.96
1985-01-27 | 27 | 1 | 0.54167 | 2.8 | 37.04 | 10.7234 | 37.04
1985-01-27 | 27 | 1 | 0.58333 | 3.3 | 37.94 | 10.7489 | 37.94
1985-01-27 | 27 | 1 | 0.625 | 3.9 | 39.02 | 10.8652 | 39.02
1985-01-27 | 27 | 1 | 0.66667 | 4.4 | 39.92 | 11.0799 | 39.92
1985-01-27 | 27 | 1 | 0.70833 | 3.9 | 39.02 | 10.9189 | 39.02
1985-01-27 | 27 | 1 | 0.75 | 2.8 | 37.04 | 10.3757 | 37.04
1985-01-27 | 27 | 1 | 0.79167 | 2.8 | 37.04 | 10.5246 | 37.04
1985-01-27 | 27 | 1 | 0.83333 | 2.8 | 37.04 | 10.8725 | 37.04
1985-01-27 | 27 | 1 | 0.875 | 3.9 | 39.02 | 11.4565 | 39.02
1985-01-27 | 27 | 1 | 0.91667 | 3.9 | 39.02 | 12.1566 |  | 39.02
1985-01-27 | 27 | 1 | 0.95833 | 4.4 | 39.92 | 12.9771 |  | 39.92
1985-01-27 | 27 | 1 | 1 | 4.4 | 39.92 | 13.6493 |  | 39.92
1985-01-28 | 28 | 1 | 0.041667 | 6.1 | 42.98 | 14.7142 |  | 42.98
1985-01-28 | 28 | 1 | 0.083333 | 7.2 | 44.96 | 15.5417 |  | 44.96
1985-01-28 | 28 | 1 | 0.125 | 6.7 | 44.06 | 14.9646 |  | 44.06
1985-01-28 | 28 | 1 | 0.16667 | 6.1 | 42.98 | 14.7142 |  | 42.98
1985-01-28 | 28 | 1 | 0.20833 | 6.1 | 42.98 | 14.904 |  | 42.98
1985-01-28 | 28 | 1 | 0.25 | 6.1 | 42.98 | 15.284 | 42.98
1985-01-28 | 28 | 1 | 0.29167 | 7.2 | 44.96 | 15.5417 | 44.96
1985-01-28 | 28 | 1 | 0.33333 | 6.7 | 44.06 | 15.1626 | 44.06
1985-01-28 | 28 | 1 | 0.375 | 6.1 | 42.98 | 14.7142 | 42.98
1985-01-28 | 28 | 1 | 0.41667 | 6.1 | 42.98 | 14.3981 | 42.98
1985-01-28 | 28 | 1 | 0.45833 | 6.7 | 44.06 | 14.3057 | 44.06
1985-01-28 | 28 | 1 | 0.5 | 7.2 | 44.96 | 14.5179 | 44.96
1985-01-28 | 28 | 1 | 0.54167 | 7.8 | 46.04 | 14.4387 | 46.04
1985-01-28 | 28 | 1 | 0.58333 | 8.9 | 48.02 | 14.0342 | 48.02
1985-01-28 | 28 | 1 | 0.625 | 8.3 | 46.94 | 13.9667 | 46.94
1985-01-28 | 28 | 1 | 0.66667 | 9.4 | 48.92 | 14.2586 | 48.92
1985-01-28 | 28 | 1 | 0.70833 | 7.8 | 46.04 | 13.5882 | 46.04
1985-01-28 | 28 | 1 | 0.75 | 7.2 | 44.96 | 13.0898 | 44.96
1985-01-28 | 28 | 1 | 0.79167 | 5.6 | 42.08 | 12.7623 | 42.08
1985-01-28 | 28 | 1 | 0.83333 | 6.1 | 42.98 | 13.3885 | 42.98
1985-01-28 | 28 | 1 | 0.875 | 5.6 | 42.08 | 13.3097 | 42.08
1985-01-28 | 28 | 1 | 0.91667 | 5.6 | 42.08 | 13.188 |  | 42.08
1985-01-28 | 28 | 1 | 0.95833 | 4.4 | 39.92 | 12.6416 |  | 39.92
1985-01-28 | 28 | 1 | 1 | 3.9 | 39.02 | 12.4263 |  | 39.02
1985-01-29 | 29 | 1 | 0.041667 | 3.3 | 37.94 | 12.1934 |  | 37.94
1985-01-29 | 29 | 1 | 0.083333 | 2.8 | 37.04 | 12.1178 |  | 37.04
1985-01-29 | 29 | 1 | 0.125 | 2.8 | 37.04 | 12.2675 |  | 37.04
1985-01-29 | 29 | 1 | 0.16667 | 3.9 | 39.02 | 12.9122 |  | 39.02
1985-01-29 | 29 | 1 | 0.20833 | 3.3 | 37.94 | 12.659 |  | 37.94
1985-01-29 | 29 | 1 | 0.25 | 1.7 | 35.06 | 11.8103 | 35.06
1985-01-29 | 29 | 1 | 0.29167 | 2.2 | 35.96 | 12.0084 | 35.96
1985-01-29 | 29 | 1 | 0.33333 | 3.3 | 37.94 | 12.3486 | 37.94
1985-01-29 | 29 | 1 | 0.375 | 5 | 41 | 13.0339 | 41
1985-01-29 | 29 | 1 | 0.41667 | 6.1 | 42.98 | 13.1365 | 42.98
1985-01-29 | 29 | 1 | 0.45833 | 7.2 | 44.96 | 13.2256 | 44.96
1985-01-29 | 29 | 1 | 0.5 | 7.8 | 46.04 | 13.7298 | 46.04
1985-01-29 | 29 | 1 | 0.54167 | 8.9 | 48.02 | 13.729 | 48.02
1985-01-29 | 29 | 1 | 0.58333 | 8.9 | 48.02 | 13.8053 | 48.02
1985-01-29 | 29 | 1 | 0.625 | 9.4 | 48.92 | 14.0218 | 48.92
1985-01-29 | 29 | 1 | 0.66667 | 8.9 | 48.02 | 13.9579 | 48.02
1985-01-29 | 29 | 1 | 0.70833 | 7.2 | 44.96 | 13.7011 | 44.96
1985-01-29 | 29 | 1 | 0.75 | 6.7 | 44.06 | 14.4374 | 44.06
1985-01-29 | 29 | 1 | 0.79167 | 6.7 | 44.06 | 14.4374 | 44.06
1985-01-29 | 29 | 1 | 0.83333 | 3.9 | 39.02 | 13.453 | 39.02
1985-01-29 | 29 | 1 | 0.875 | 6.7 | 44.06 | 14.9646 | 44.06
1985-01-29 | 29 | 1 | 0.91667 | 6.7 | 44.06 | 14.9646 |  | 44.06
1985-01-29 | 29 | 1 | 0.95833 | 7.2 | 44.96 | 15.5417 |  | 44.96
1985-01-29 | 29 | 1 | 1 | 7.8 | 46.04 | 16.2174 |  | 46.04
1985-01-30 | 30 | 1 | 0.041667 | 6.1 | 42.98 | 15.9182 |  | 42.98
1985-01-30 | 30 | 1 | 0.083333 | 5.6 | 42.08 | 15.937 |  | 42.08
1985-01-30 | 30 | 1 | 0.125 | 5.6 | 42.08 | 15.937 |  | 42.08
1985-01-30 | 30 | 1 | 0.16667 | 5 | 41 | 15.4347 |  | 41
1985-01-30 | 30 | 1 | 0.20833 | 5.6 | 42.08 | 15.6918 |  | 42.08
1985-01-30 | 30 | 1 | 0.25 | 5 | 41 | 15.4347 | 41
1985-01-30 | 30 | 1 | 0.29167 | 5 | 41 | 15.4347 | 41
1985-01-30 | 30 | 1 | 0.33333 | 6.1 | 42.98 | 16.1722 | 42.98
1985-01-30 | 30 | 1 | 0.375 | 6.1 | 42.98 | 15.9182 | 42.98
1985-01-30 | 30 | 1 | 0.41667 | 7.8 | 46.04 | 17.146 | 46.04
1985-01-30 | 30 | 1 | 0.45833 | 9.4 | 48.92 | 18.0708 | 48.92
1985-01-30 | 30 | 1 | 0.5 | 12.2 | 53.96 | 19.5448 | 53.96
1985-01-30 | 30 | 1 | 0.54167 | 12.2 | 53.96 | 19.5448 | 53.96
1985-01-30 | 30 | 1 | 0.58333 | 10.6 | 51.08 | 19.0439 | 51.08
1985-01-30 | 30 | 1 | 0.625 | 10.6 | 51.08 | 19.0439 | 51.08
1985-01-30 | 30 | 1 | 0.66667 | 10.6 | 51.08 | 19.0439 | 51.08
1985-01-30 | 30 | 1 | 0.70833 | 10 | 50 | 19.0956 | 50
1985-01-30 | 30 | 1 | 0.75 | 11.1 | 51.98 | 20.1234 | 51.98
1985-01-30 | 30 | 1 | 0.79167 | 10.6 | 51.08 | 19.6516 | 51.08
1985-01-30 | 30 | 1 | 0.83333 | 10.6 | 51.08 | 20.1734 | 51.08
1985-01-30 | 30 | 1 | 0.875 | 7.8 | 46.04 | 17.6471 | 46.04
1985-01-30 | 30 | 1 | 0.91667 | 8.3 | 46.94 | 18.3932 |  | 46.94
1985-01-30 | 30 | 1 | 0.95833 | 8.3 | 46.94 | 18.3932 |  | 46.94
1985-01-30 | 30 | 1 | 1 | 8.9 | 48.02 | 18.645 |  | 48.02
1985-01-31 | 31 | 1 | 0.041667 | 8.3 | 46.94 | 18.3932 |  | 46.94
1985-01-31 | 31 | 1 | 0.083333 | 7.8 | 46.04 | 17.6471 |  | 46.04
1985-01-31 | 31 | 1 | 0.125 | 7.2 | 44.96 | 16.9115 |  | 44.96
1985-01-31 | 31 | 1 | 0.16667 | 6.7 | 44.06 | 16.1539 |  | 44.06
1985-01-31 | 31 | 1 | 0.20833 | 5 | 41 | 13.5595 |  | 41
1985-01-31 | 31 | 1 | 0.25 | 2.8 | 37.04 | 11.5693 | 37.04
1985-01-31 | 31 | 1 | 0.29167 | 1.7 | 35.06 | 10.154 | 35.06
1985-01-31 | 31 | 1 | 0.33333 | 1.1 | 33.98 | 10.1721 | 33.98
1985-01-31 | 31 | 1 | 0.375 | 1.7 | 35.06 | 10.5213 | 35.06
1985-01-31 | 31 | 1 | 0.41667 | 2.2 | 35.96 | 10.7198 | 35.96
1985-01-31 | 31 | 1 | 0.45833 | 3.3 | 37.94 | 11.6252 | 37.94
1985-01-31 | 31 | 1 | 0.5 | 2.8 | 37.04 | 10.7731 | 37.04
1985-01-31 | 31 | 1 | 0.54167 | 2.2 | 35.96 | 10.1962 | 35.96
1985-01-31 | 31 | 1 | 0.58333 | 0 | 32 | 9.5 | 32
1985-01-31 | 31 | 1 | 0.625 | 1.1 | 33.98 | 10.0402 | 33.98
1985-01-31 | 31 | 1 | 0.66667 | 0.6 | 33.08 | 9.4177 | 33.08
1985-01-31 | 31 | 1 | 0.70833 | 0 | 32 | 9.4189 | 32
1985-01-31 | 31 | 1 | 0.75 | 0 | 32 | 8.9732 | 32
1985-01-31 | 31 | 1 | 0.79167 | -0.6 | 30.92 | 9.0362 | 30.92
1985-01-31 | 31 | 1 | 0.83333 | -1.7 | 28.94 | 8.6645 | 28.94
1985-01-31 | 31 | 1 | 0.875 | -2.2 | 28.04 | 7.9395 | 28.04
1985-01-31 | 31 | 1 | 0.91667 | -1.4 | 29.48 | 8.2975 |  | 29.48
1985-01-31 | 31 | 1 | 0.95833 | -0.7 | 30.74 | 8.7502 |  | 30.74
1985-01-31 | 31 | 1 | 1 | 0 | 32 | 8.9327 |  | 32
1985-02-01 | 1 | 2 | 0.041667 | 0.7 | 33.26 | 9.7278 |  | 33.26
1985-02-01 | 1 | 2 | 0.083333 | 1.4 | 34.52 | 10.0318 |  | 34.52
1985-02-01 | 1 | 2 | 0.125 | 2.1 | 35.78 | 10.7088 |  | 35.78
1985-02-01 | 1 | 2 | 0.16667 | 2.8 | 37.04 | 11.3203 |  | 37.04
1985-02-01 | 1 | 2 | 0.20833 | 2.2 | 35.96 | 11.0534 |  | 35.96
1985-02-01 | 1 | 2 | 0.25 | 1.7 | 35.06 | 10.8431 | 35.06
1985-02-01 | 1 | 2 | 0.29167 | 2.2 | 35.96 | 11.1488 | 35.96
1985-02-01 | 1 | 2 | 0.33333 | 3.3 | 37.94 | 11.7801 | 37.94
1985-02-01 | 1 | 2 | 0.375 | 4.4 | 39.92 | 12.5298 | 39.92
1985-02-01 | 1 | 2 | 0.41667 | 5 | 41 | 12.8006 | 41
1985-02-01 | 1 | 2 | 0.45833 | 6.7 | 44.06 | 13.6481 | 44.06
1985-02-01 | 1 | 2 | 0.5 | 7.2 | 44.96 | 14.0412 | 44.96
1985-02-01 | 1 | 2 | 0.54167 | 7.8 | 46.04 | 14.2968 | 46.04
1985-02-01 | 1 | 2 | 0.58333 | 7.8 | 46.04 | 14.2968 | 46.04
1985-02-01 | 1 | 2 | 0.625 | 8.3 | 46.94 | 14.4801 | 46.94
1985-02-01 | 1 | 2 | 0.66667 | 7.8 | 46.04 | 14.2968 | 46.04
1985-02-01 | 1 | 2 | 0.70833 | 7.2 | 44.96 | 14.1773 | 44.96
1985-02-01 | 1 | 2 | 0.75 | 7.2 | 44.96 | 14.0412 | 44.96
1985-02-01 | 1 | 2 | 0.79167 | 6.7 | 44.06 | 14.1083 | 44.06
1985-02-01 | 1 | 2 | 0.83333 | 6.7 | 44.06 | 14.1083 | 44.06
1985-02-01 | 1 | 2 | 0.875 | 6.7 | 44.06 | 14.3057 | 44.06
1985-02-01 | 1 | 2 | 0.91667 | 6.7 | 44.06 | 14.3057 |  | 44.06
1985-02-01 | 1 | 2 | 0.95833 | 6.1 | 42.98 | 14.0191 |  | 42.98
1985-02-01 | 1 | 2 | 1 | 6.1 | 42.98 | 14.0191 |  | 42.98
1985-02-02 | 2 | 2 | 0.041667 | 5.6 | 42.08 | 13.7969 |  | 42.08
1985-02-02 | 2 | 2 | 0.083333 | 5.6 | 42.08 | 13.7969 |  | 42.08
1985-02-02 | 2 | 2 | 0.125 | 5.6 | 42.08 | 13.7969 |  | 42.08
1985-02-02 | 2 | 2 | 0.16667 | 5 | 41 | 13.5595 |  | 41
1985-02-02 | 2 | 2 | 0.20833 | 5 | 41 | 13.0339 |  | 41
1985-02-02 | 2 | 2 | 0.25 | 4.4 | 39.92 | 12.5298 | 39.92
1985-02-02 | 2 | 2 | 0.29167 | 3.3 | 37.94 | 11.935 | 37.94
1985-02-02 | 2 | 2 | 0.33333 | 3.3 | 37.94 | 11.935 | 37.94
1985-02-02 | 2 | 2 | 0.375 | 3.3 | 37.94 | 11.7801 | 37.94
1985-02-02 | 2 | 2 | 0.41667 | 4.4 | 39.92 | 12.1388 | 39.92
1985-02-02 | 2 | 2 | 0.45833 | 4.4 | 39.92 | 12.0272 | 39.92
1985-02-02 | 2 | 2 | 0.5 | 5 | 41 | 12.1598 | 41
1985-02-02 | 2 | 2 | 0.54167 | 5 | 41 | 11.6365 | 41
1985-02-02 | 2 | 2 | 0.58333 | 5 | 41 | 11.6365 | 41
1985-02-02 | 2 | 2 | 0.625 | 3.9 | 39.02 | 10.7041 | 39.02
1985-02-02 | 2 | 2 | 0.66667 | 3.3 | 37.94 | 10.3887 | 37.94
1985-02-02 | 2 | 2 | 0.70833 | 2.8 | 37.04 | 9.9787 | 37.04
1985-02-02 | 2 | 2 | 0.75 | 1.7 | 35.06 | 9.3288 | 35.06
1985-02-02 | 2 | 2 | 0.79167 | 0.6 | 33.08 | 8.8255 | 33.08
1985-02-02 | 2 | 2 | 0.83333 | -0.6 | 30.92 | 8.4199 | 30.92
1985-02-02 | 2 | 2 | 0.875 | -1.7 | 28.94 | 7.8215 | 28.94
1985-02-02 | 2 | 2 | 0.91667 | -2.2 | 28.04 | 7.7712 |  | 28.04
1985-02-02 | 2 | 2 | 0.95833 | -3.3 | 26.06 | 7.4177 |  | 26.06
1985-02-02 | 2 | 2 | 1 | -4.4 | 24.08 | 7.1171 |  | 24.08
1985-02-03 | 3 | 2 | 0.041667 | -5 | 23 | 6.923 |  | 23
1985-02-03 | 3 | 2 | 0.083333 | -5.6 | 21.92 | 6.6684 |  | 21.92
1985-02-03 | 3 | 2 | 0.125 | -6.1 | 21.02 | 6.3202 |  | 21.02
1985-02-03 | 3 | 2 | 0.16667 | -6.7 | 19.94 | 6.1103 |  | 19.94
1985-02-03 | 3 | 2 | 0.20833 | -7.2 | 19.04 | 5.8375 |  | 19.04
1985-02-03 | 3 | 2 | 0.25 | -7.8 | 17.96 | 5.5131 | 17.96
1985-02-03 | 3 | 2 | 0.29167 | -7.8 | 17.96 | 5.5131 | 17.96
1985-02-03 | 3 | 2 | 0.33333 | -7.2 | 19.04 | 5.9032 | 19.04
1985-02-03 | 3 | 2 | 0.375 | -6.7 | 19.94 | 5.9273 | 19.94
1985-02-03 | 3 | 2 | 0.41667 | -5 | 23 | 6.6049 | 23
1985-02-03 | 3 | 2 | 0.45833 | -4.4 | 24.08 | 6.8658 | 24.08
1985-02-03 | 3 | 2 | 0.5 | -2.8 | 26.96 | 7.6203 | 26.96
1985-02-03 | 3 | 2 | 0.54167 | -1.1 | 30.02 | 8.4213 | 30.02
1985-02-03 | 3 | 2 | 0.58333 | -0.6 | 30.92 | 8.4969 | 30.92
1985-02-03 | 3 | 2 | 0.625 | 0 | 32 | 8.5685 | 32
1985-02-03 | 3 | 2 | 0.66667 | 0 | 32 | 8.4877 | 32
1985-02-03 | 3 | 2 | 0.70833 | -1.1 | 30.02 | 8.0891 | 30.02
1985-02-03 | 3 | 2 | 0.75 | -1.7 | 28.94 | 8.3482 | 28.94
1985-02-03 | 3 | 2 | 0.79167 | -2.2 | 28.04 | 8.3437 | 28.04
1985-02-03 | 3 | 2 | 0.83333 | -2.2 | 28.04 | 8.4449 | 28.04
1985-02-03 | 3 | 2 | 0.875 | -1.7 | 28.94 | 8.6645 | 28.94
1985-02-03 | 3 | 2 | 0.91667 | -1.7 | 28.94 | 8.7701 |  | 28.94
1985-02-03 | 3 | 2 | 0.95833 | -1.1 | 30.02 | 9.3089 |  | 30.02
1985-02-03 | 3 | 2 | 1 | -1.1 | 30.02 | 9.4941 |  | 30.02
1985-02-04 | 4 | 2 | 0.041667 | -2.2 | 28.04 | 9.6609 |  | 28.04
1985-02-04 | 4 | 2 | 0.083333 | -2.2 | 28.04 | 9.9318 |  | 28.04
1985-02-04 | 4 | 2 | 0.125 | -2.2 | 28.04 | 9.9318 |  | 28.04
1985-02-04 | 4 | 2 | 0.16667 | -1.7 | 28.94 | 10.3217 |  | 28.94
1985-02-04 | 4 | 2 | 0.20833 | -1.1 | 30.02 | 10.905 |  | 30.02
1985-02-04 | 4 | 2 | 0.25 | -0.6 | 30.92 | 11.2798 | 30.92
1985-02-04 | 4 | 2 | 0.29167 | 0 | 32 | 11.738 | 32
1985-02-04 | 4 | 2 | 0.33333 | 0 | 32 | 11.738 | 32
1985-02-04 | 4 | 2 | 0.375 | 0 | 32 | 11.738 | 32
1985-02-04 | 4 | 2 | 0.41667 | 1.1 | 33.98 | 12.3783 | 33.98
1985-02-04 | 4 | 2 | 0.45833 | 1.7 | 35.06 | 12.6416 | 35.06
1985-02-04 | 4 | 2 | 0.5 | 2.2 | 35.96 | 12.8702 | 35.96
1985-02-04 | 4 | 2 | 0.54167 | 2.2 | 35.96 | 12.8702 | 35.96
1985-02-04 | 4 | 2 | 0.58333 | 2.8 | 37.04 | 13.1173 | 37.04
1985-02-04 | 4 | 2 | 0.625 | 1.1 | 33.98 | 12.2012 | 33.98
1985-02-04 | 4 | 2 | 0.66667 | 0.6 | 33.08 | 10.4778 | 33.08
1985-02-04 | 4 | 2 | 0.70833 | 0 | 32 | 11.0446 | 32
1985-02-04 | 4 | 2 | 0.75 | 0 | 32 | 10.8817 | 32
1985-02-04 | 4 | 2 | 0.79167 | 0 | 32 | 10.7596 | 32
1985-02-04 | 4 | 2 | 0.83333 | 0 | 32 | 10.5968 | 32
1985-02-04 | 4 | 2 | 0.875 | -0.6 | 30.92 | 9.9628 | 30.92
1985-02-04 | 4 | 2 | 0.91667 | -0.6 | 30.92 | 9.8468 |  | 30.92
1985-02-04 | 4 | 2 | 0.95833 | -1.1 | 30.02 | 9.4941 |  | 30.02
1985-02-04 | 4 | 2 | 1 | -1.7 | 28.94 | 9.0164 |  | 28.94
1985-02-05 | 5 | 2 | 0.041667 | -1.7 | 28.94 | 8.946 |  | 28.94
1985-02-05 | 5 | 2 | 0.083333 | -1.7 | 28.94 | 8.946 |  | 28.94
1985-02-05 | 5 | 2 | 0.125 | -1.7 | 28.94 | 8.7701 |  | 28.94
1985-02-05 | 5 | 2 | 0.16667 | -2.2 | 28.04 | 8.546 |  | 28.04
1985-02-05 | 5 | 2 | 0.20833 | -2.8 | 26.96 | 8.0365 |  | 26.96
1985-02-05 | 5 | 2 | 0.25 | -3.3 | 26.06 | 7.7245 | 26.06
1985-02-05 | 5 | 2 | 0.29167 | -5 | 23 | 6.7904 | 23
1985-02-05 | 5 | 2 | 0.33333 | -5.6 | 21.92 | 6.3411 | 21.92
1985-02-05 | 5 | 2 | 0.375 | -6.1 | 21.02 | 6.031 | 21.02
1985-02-05 | 5 | 2 | 0.41667 | -6.1 | 21.02 | 6.1273 | 21.02
1985-02-05 | 5 | 2 | 0.45833 | -5.6 | 21.92 | 6.2908 | 21.92
1985-02-05 | 5 | 2 | 0.5 | -5.6 | 21.92 | 6.2404 | 21.92
1985-02-05 | 5 | 2 | 0.54167 | -5 | 23 | 6.5519 | 23
1985-02-05 | 5 | 2 | 0.58333 | -5.6 | 21.92 | 6.1398 | 21.92
1985-02-05 | 5 | 2 | 0.625 | -6.1 | 21.02 | 5.9828 | 21.02
1985-02-05 | 5 | 2 | 0.66667 | -6.7 | 19.94 | 5.8815 | 19.94
1985-02-05 | 5 | 2 | 0.70833 | -7.2 | 19.04 | 5.4872 | 19.04
1985-02-05 | 5 | 2 | 0.75 | -7.8 | 17.96 | 5.2846 | 17.96
1985-02-05 | 5 | 2 | 0.79167 | -8.9 | 15.98 | 4.6625 | 15.98
1985-02-05 | 5 | 2 | 0.83333 | -10.6 | 12.92 | 3.7791 | 12.92
1985-02-05 | 5 | 2 | 0.875 | -11.1 | 12.02 | 3.595 | 12.02
1985-02-05 | 5 | 2 | 0.91667 | -12.2 | 10.04 | 3.0803 |  | 10.04
1985-02-05 | 5 | 2 | 0.95833 | -13.9 | 6.98 | 2.2251 |  | 6.98
1985-02-05 | 5 | 2 | 1 | -14.4 | 6.08 | 1.9728 |  | 6.08
1985-02-06 | 6 | 2 | 0.041667 | -14.4 | 6.08 | 1.9728 |  | 6.08
1985-02-06 | 6 | 2 | 0.083333 | -15 | 5 | 1.6858 |  | 5
1985-02-06 | 6 | 2 | 0.125 | -14.4 | 6.08 | 1.95 |  | 6.08
1985-02-06 | 6 | 2 | 0.16667 | -15 | 5 | 1.7182 |  | 5
1985-02-06 | 6 | 2 | 0.20833 | -15 | 5 | 1.7182 |  | 5
1985-02-06 | 6 | 2 | 0.25 | -14.4 | 6.08 | 2.0985 | 6.08
1985-02-06 | 6 | 2 | 0.29167 | -14.4 | 6.08 | 2.03 | 6.08
1985-02-06 | 6 | 2 | 0.33333 | -13.9 | 6.98 | 2.3089 | 6.98
1985-02-06 | 6 | 2 | 0.375 | -12.8 | 8.96 | 2.7853 | 8.96
1985-02-06 | 6 | 2 | 0.41667 | -11.7 | 10.94 | 3.2982 | 10.94
1985-02-06 | 6 | 2 | 0.45833 | -10 | 14 | 4.0758 | 14
1985-02-06 | 6 | 2 | 0.5 | -9.4 | 15.08 | 4.4105 | 15.08
1985-02-06 | 6 | 2 | 0.54167 | -8.9 | 15.98 | 4.6249 | 15.98
1985-02-06 | 6 | 2 | 0.58333 | -8.3 | 17.06 | 4.9273 | 17.06
1985-02-06 | 6 | 2 | 0.625 | -7.2 | 19.04 | 5.4654 | 19.04
1985-02-06 | 6 | 2 | 0.66667 | -7.2 | 19.04 | 5.5529 | 19.04
1985-02-06 | 6 | 2 | 0.70833 | -6.7 | 19.94 | 5.9959 | 19.94
1985-02-06 | 6 | 2 | 0.75 | -8.3 | 17.06 | 5.802 | 17.06
1985-02-06 | 6 | 2 | 0.79167 | -8.3 | 17.06 | 5.424 | 17.06
1985-02-06 | 6 | 2 | 0.83333 | -8.3 | 17.06 | 5.1259 | 17.06
1985-02-06 | 6 | 2 | 0.875 | -8.3 | 17.06 | 5.1259 | 17.06
1985-02-06 | 6 | 2 | 0.91667 | -8.9 | 15.98 | 4.719 |  | 15.98
1985-02-06 | 6 | 2 | 0.95833 | -8.9 | 15.98 | 4.6625 |  | 15.98
1985-02-06 | 6 | 2 | 1 | -8.9 | 15.98 | 4.6249 |  | 15.98
1985-02-07 | 7 | 2 | 0.041667 | -9.4 | 15.08 | 4.4105 |  | 15.08
1985-02-07 | 7 | 2 | 0.083333 | -9.4 | 15.08 | 4.4465 |  | 15.08
1985-02-07 | 7 | 2 | 0.125 | -9.4 | 15.08 | 4.5005 |  | 15.08
1985-02-07 | 7 | 2 | 0.16667 | -9.4 | 15.08 | 4.6447 |  | 15.08
1985-02-07 | 7 | 2 | 0.20833 | -9.4 | 15.08 | 4.6987 |  | 15.08
1985-02-07 | 7 | 2 | 0.25 | -9.4 | 15.08 | 4.6987 | 15.08
1985-02-07 | 7 | 2 | 0.29167 | -9.4 | 15.08 | 4.879 | 15.08
1985-02-07 | 7 | 2 | 0.33333 | -8.3 | 17.06 | 5.3047 | 17.06
1985-02-07 | 7 | 2 | 0.375 | -7.2 | 19.04 | 5.7718 | 19.04
1985-02-07 | 7 | 2 | 0.41667 | -6.7 | 19.94 | 5.9273 | 19.94
1985-02-07 | 7 | 2 | 0.45833 | -5.6 | 21.92 | 6.4166 | 21.92
1985-02-07 | 7 | 2 | 0.5 | -5 | 23 | 6.7374 | 23
1985-02-07 | 7 | 2 | 0.54167 | -3.9 | 24.98 | 7.3334 | 24.98
1985-02-07 | 7 | 2 | 0.58333 | -3.9 | 24.98 | 7.2751 | 24.98
1985-02-07 | 7 | 2 | 0.625 | -2.8 | 26.96 | 7.6842 | 26.96
1985-02-07 | 7 | 2 | 0.66667 | -3.3 | 26.06 | 7.4483 | 26.06
1985-02-07 | 7 | 2 | 0.70833 | -3.9 | 24.98 | 7.1586 | 24.98
1985-02-07 | 7 | 2 | 0.75 | -4.4 | 24.08 | 6.9775 | 24.08
1985-02-07 | 7 | 2 | 0.79167 | -4.4 | 24.08 | 6.9775 | 24.08
1985-02-07 | 7 | 2 | 0.83333 | -4.4 | 24.08 | 6.9775 | 24.08
1985-02-07 | 7 | 2 | 0.875 | -5 | 23 | 6.6579 | 23
1985-02-07 | 7 | 2 | 0.91667 | -5 | 23 | 6.5519 |  | 23
1985-02-07 | 7 | 2 | 0.95833 | -4.4 | 24.08 | 6.81 |  | 24.08
1985-02-07 | 7 | 2 | 1 | -4.4 | 24.08 | 6.7542 |  | 24.08
1985-02-08 | 8 | 2 | 0.041667 | -4.4 | 24.08 | 6.9216 |  | 24.08
1985-02-08 | 8 | 2 | 0.083333 | -3.9 | 24.98 | 7.0712 |  | 24.98
1985-02-08 | 8 | 2 | 0.125 | -5 | 23 | 6.7904 |  | 23
1985-02-08 | 8 | 2 | 0.16667 | -5 | 23 | 6.7374 |  | 23
1985-02-08 | 8 | 2 | 0.20833 | -5.6 | 21.92 | 6.3411 |  | 21.92
1985-02-08 | 8 | 2 | 0.25 | -6.1 | 21.02 | 6.2478 | 21.02
1985-02-08 | 8 | 2 | 0.29167 | -6.7 | 19.94 | 5.8815 | 19.94
1985-02-08 | 8 | 2 | 0.33333 | -6.1 | 21.02 | 6.1996 | 21.02
1985-02-08 | 8 | 2 | 0.375 | -6.1 | 21.02 | 6.2478 | 21.02
1985-02-08 | 8 | 2 | 0.41667 | -5.6 | 21.92 | 6.5425 | 21.92
1985-02-08 | 8 | 2 | 0.45833 | -5 | 23 | 6.7374 | 23
1985-02-08 | 8 | 2 | 0.5 | -3.3 | 26.06 | 7.5404 | 26.06
1985-02-08 | 8 | 2 | 0.54167 | -2.8 | 26.96 | 7.4923 | 26.96
1985-02-08 | 8 | 2 | 0.58333 | -3.3 | 26.06 | 7.1724 | 26.06
1985-02-08 | 8 | 2 | 0.625 | -2.8 | 26.96 | 7.4923 | 26.96
1985-02-08 | 8 | 2 | 0.66667 | -2.8 | 26.96 | 7.4923 | 26.96
1985-02-08 | 8 | 2 | 0.70833 | -3.3 | 26.06 | 7.3563 | 26.06
1985-02-08 | 8 | 2 | 0.75 | -4.4 | 24.08 | 6.8658 | 24.08
1985-02-08 | 8 | 2 | 0.79167 | -4.4 | 24.08 | 6.8658 | 24.08
1985-02-08 | 8 | 2 | 0.83333 | -5 | 23 | 6.6049 | 23
1985-02-08 | 8 | 2 | 0.875 | -5.6 | 21.92 | 6.4166 | 21.92
1985-02-08 | 8 | 2 | 0.91667 | -6.1 | 21.02 | 6.1996 |  | 21.02
1985-02-08 | 8 | 2 | 0.95833 | -7.2 | 19.04 | 5.728 |  | 19.04
1985-02-08 | 8 | 2 | 1 | -7.2 | 19.04 | 5.5966 |  | 19.04
1985-02-09 | 9 | 2 | 0.041667 | -7.8 | 17.96 | 5.3469 |  | 17.96
1985-02-09 | 9 | 2 | 0.083333 | -8.3 | 17.06 | 5.1259 |  | 17.06
1985-02-09 | 9 | 2 | 0.125 | -8.3 | 17.06 | 5.1259 |  | 17.06
1985-02-09 | 9 | 2 | 0.16667 | -8.3 | 17.06 | 5.1855 |  | 17.06
1985-02-09 | 9 | 2 | 0.20833 | -7.8 | 17.96 | 5.3884 |  | 17.96
1985-02-09 | 9 | 2 | 0.25 | -7.8 | 17.96 | 5.4507 | 17.96
1985-02-09 | 9 | 2 | 0.29167 | -8.3 | 17.06 | 5.3047 | 17.06
1985-02-09 | 9 | 2 | 0.33333 | -7.8 | 17.96 | 5.5131 | 17.96
1985-02-09 | 9 | 2 | 0.375 | -7.2 | 19.04 | 5.6623 | 19.04
1985-02-09 | 9 | 2 | 0.41667 | -6.1 | 21.02 | 6.1273 | 21.02
1985-02-09 | 9 | 2 | 0.45833 | -4.4 | 24.08 | 6.9775 | 24.08
1985-02-09 | 9 | 2 | 0.5 | -2.8 | 26.96 | 7.8123 | 26.96
1985-02-09 | 9 | 2 | 0.54167 | -1.1 | 30.02 | 8.6061 | 30.02
1985-02-09 | 9 | 2 | 0.58333 | -1.1 | 30.02 | 8.6061 | 30.02
1985-02-09 | 9 | 2 | 0.625 | -0.6 | 30.92 | 8.7664 | 30.92
1985-02-09 | 9 | 2 | 0.66667 | -0.6 | 30.92 | 8.8435 | 30.92
1985-02-09 | 9 | 2 | 0.70833 | -2.2 | 28.04 | 8.0068 | 28.04
1985-02-09 | 9 | 2 | 0.75 | -2.2 | 28.04 | 8.0742 | 28.04
1985-02-09 | 9 | 2 | 0.79167 | -2.2 | 28.04 | 7.9395 | 28.04
1985-02-09 | 9 | 2 | 0.83333 | -1.7 | 28.94 | 8.1374 | 28.94
1985-02-09 | 9 | 2 | 0.875 | -1.7 | 28.94 | 8.2779 | 28.94
1985-02-09 | 9 | 2 | 0.91667 | -1.1 | 30.02 | 8.4213 |  | 30.02
1985-02-09 | 9 | 2 | 0.95833 | -0.6 | 30.92 | 8.6894 |  | 30.92
1985-02-09 | 9 | 2 | 1 | -1.1 | 30.02 | 8.6061 |  | 30.02
1985-02-10 | 10 | 2 | 0.041667 | -1.1 | 30.02 | 8.5322 |  | 30.02
1985-02-10 | 10 | 2 | 0.083333 | -1.7 | 28.94 | 8.4887 |  | 28.94
1985-02-10 | 10 | 2 | 0.125 | -1.1 | 30.02 | 8.7539 |  | 30.02
1985-02-10 | 10 | 2 | 0.16667 | -1.1 | 30.02 | 8.9388 |  | 30.02
1985-02-10 | 10 | 2 | 0.20833 | -1.1 | 30.02 | 9.0128 |  | 30.02
1985-02-10 | 10 | 2 | 0.25 | -1.7 | 28.94 | 8.8404 | 28.94
1985-02-10 | 10 | 2 | 0.29167 | -1.1 | 30.02 | 9.0868 | 30.02
1985-02-10 | 10 | 2 | 0.33333 | -1.1 | 30.02 | 9.1978 | 30.02
1985-02-10 | 10 | 2 | 0.375 | 0 | 32 | 9.5811 | 32
1985-02-10 | 10 | 2 | 0.41667 | 2.2 | 35.96 | 10.6246 | 35.96
1985-02-10 | 10 | 2 | 0.45833 | 2.8 | 37.04 | 10.972 | 37.04
1985-02-10 | 10 | 2 | 0.5 | 3.9 | 39.02 | 11.4565 | 39.02
1985-02-10 | 10 | 2 | 0.54167 | 5.6 | 42.08 | 11.9733 | 42.08
1985-02-10 | 10 | 2 | 0.58333 | 3.9 | 39.02 | 11.4565 | 39.02
1985-02-10 | 10 | 2 | 0.625 | 4.4 | 39.92 | 12.0272 | 39.92
1985-02-10 | 10 | 2 | 0.66667 | 3.9 | 39.02 | 12.0488 | 39.02
1985-02-10 | 10 | 2 | 0.70833 | 3.3 | 37.94 | 11.7801 | 37.94
1985-02-10 | 10 | 2 | 0.75 | 2.8 | 37.04 | 12.1178 | 37.04
1985-02-10 | 10 | 2 | 0.79167 | 3.3 | 37.94 | 11.935 | 37.94
1985-02-10 | 10 | 2 | 0.83333 | 3.9 | 39.02 | 11.6717 | 39.02
1985-02-10 | 10 | 2 | 0.875 | 3.3 | 37.94 | 11.522 | 37.94
1985-02-10 | 10 | 2 | 0.91667 | 2.8 | 37.04 | 11.5693 |  | 37.04
1985-02-10 | 10 | 2 | 0.95833 | 2.8 | 37.04 | 11.7188 |  | 37.04
1985-02-10 | 10 | 2 | 1 | 2.8 | 37.04 | 11.7188 |  | 37.04
1985-02-11 | 11 | 2 | 0.041667 | 3.3 | 37.94 | 11.935 |  | 37.94
1985-02-11 | 11 | 2 | 0.083333 | 2.8 | 37.04 | 11.7188 |  | 37.04
1985-02-11 | 11 | 2 | 0.125 | 2.2 | 35.96 | 11.4351 |  | 35.96
1985-02-11 | 11 | 2 | 0.16667 | 1.7 | 35.06 | 11.2113 |  | 35.06
1985-02-11 | 11 | 2 | 0.20833 | 2.2 | 35.96 | 11.4351 |  | 35.96
1985-02-11 | 11 | 2 | 0.25 | 1.7 | 35.06 | 11.3494 | 35.06
1985-02-11 | 11 | 2 | 0.29167 | 1.1 | 33.98 | 11.0969 | 33.98
1985-02-11 | 11 | 2 | 0.33333 | 2.8 | 37.04 | 11.9681 | 37.04
1985-02-11 | 11 | 2 | 0.375 | 4.4 | 39.92 | 12.5298 | 39.92
1985-02-11 | 11 | 2 | 0.41667 | 6.1 | 42.98 | 13.2625 | 42.98
1985-02-11 | 11 | 2 | 0.45833 | 5.6 | 42.08 | 12.7623 | 42.08
1985-02-11 | 11 | 2 | 0.5 | 6.7 | 44.06 | 12.7951 | 44.06
1985-02-11 | 11 | 2 | 0.54167 | 7.2 | 44.96 | 12.8185 | 44.96
1985-02-11 | 11 | 2 | 0.58333 | 7.2 | 44.96 | 13.0219 | 44.96
1985-02-11 | 11 | 2 | 0.625 | 7.8 | 46.04 | 13.3759 | 46.04
1985-02-11 | 11 | 2 | 0.66667 | 7.2 | 44.96 | 13.0219 | 44.96
1985-02-11 | 11 | 2 | 0.70833 | 7.2 | 44.96 | 12.8863 | 44.96
1985-02-11 | 11 | 2 | 0.75 | 6.1 | 42.98 | 12.3191 | 42.98
1985-02-11 | 11 | 2 | 0.79167 | 5.6 | 42.08 | 11.7309 | 42.08
1985-02-11 | 11 | 2 | 0.83333 | 4.4 | 39.92 | 10.913 | 39.92
1985-02-11 | 11 | 2 | 0.875 | 3.9 | 39.02 | 10.4358 | 39.02
1985-02-11 | 11 | 2 | 0.91667 | 2.2 | 35.96 | 9.721 |  | 35.96
1985-02-11 | 11 | 2 | 0.95833 | 0.6 | 33.08 | 8.9101 |  | 33.08
1985-02-11 | 11 | 2 | 1 | 0 | 32 | 8.609 |  | 32
1985-02-12 | 12 | 2 | 0.041667 | -1.7 | 28.94 | 7.8215 |  | 28.94
1985-02-12 | 12 | 2 | 0.083333 | -2.8 | 26.96 | 7.3964 |  | 26.96
1985-02-12 | 12 | 2 | 0.125 | -3.9 | 24.98 | 6.9256 |  | 24.98
1985-02-12 | 12 | 2 | 0.16667 | -5 | 23 | 6.4459 |  | 23
1985-02-12 | 12 | 2 | 0.20833 | -6.7 | 19.94 | 5.7215 |  | 19.94
1985-02-12 | 12 | 2 | 0.25 | -8.3 | 17.06 | 4.8478 | 17.06
1985-02-12 | 12 | 2 | 0.29167 | -10.6 | 12.92 | 3.7144 | 12.92
1985-02-12 | 12 | 2 | 0.33333 | -11.7 | 10.94 | 3.1958 | 10.94
1985-02-12 | 12 | 2 | 0.375 | -11.7 | 10.94 | 3.1958 | 10.94
1985-02-12 | 12 | 2 | 0.41667 | -11.1 | 12.02 | 3.4868 | 12.02
1985-02-12 | 12 | 2 | 0.45833 | -10 | 14 | 3.8712 | 14
1985-02-12 | 12 | 2 | 0.5 | -8.9 | 15.98 | 4.4367 | 15.98
1985-02-12 | 12 | 2 | 0.54167 | -7.2 | 19.04 | 5.2029 | 19.04
1985-02-12 | 12 | 2 | 0.58333 | -6.7 | 19.94 | 5.5158 | 19.94
1985-02-12 | 12 | 2 | 0.625 | -6.7 | 19.94 | 5.5843 | 19.94
1985-02-12 | 12 | 2 | 0.66667 | -5.6 | 21.92 | 6.0895 | 21.92
1985-02-12 | 12 | 2 | 0.70833 | -5 | 23 | 6.3664 | 23
1985-02-12 | 12 | 2 | 0.75 | -5.6 | 21.92 | 6.0141 | 21.92
1985-02-12 | 12 | 2 | 0.79167 | -6.1 | 21.02 | 5.8383 | 21.02
1985-02-12 | 12 | 2 | 0.83333 | -6.7 | 19.94 | 5.5387 | 19.94
1985-02-12 | 12 | 2 | 0.875 | -7.2 | 19.04 | 5.2904 | 19.04
1985-02-12 | 12 | 2 | 0.91667 | -7.2 | 19.04 | 5.3779 |  | 19.04
1985-02-12 | 12 | 2 | 0.95833 | -7.8 | 17.96 | 5.0979 |  | 17.96
1985-02-12 | 12 | 2 | 1 | -7.8 | 17.96 | 5.0979 |  | 17.96
1985-02-13 | 13 | 2 | 0.041667 | -8.3 | 17.06 | 4.8478 |  | 17.06
1985-02-13 | 13 | 2 | 0.083333 | -8.3 | 17.06 | 4.8478 |  | 17.06
1985-02-13 | 13 | 2 | 0.125 | -8.9 | 15.98 | 4.5872 |  | 15.98
1985-02-13 | 13 | 2 | 0.16667 | -9.4 | 15.08 | 4.3745 |  | 15.08
1985-02-13 | 13 | 2 | 0.20833 | -9.4 | 15.08 | 4.4105 |  | 15.08
1985-02-13 | 13 | 2 | 0.25 | -10 | 14 | 4.11 | 14
1985-02-13 | 13 | 2 | 0.29167 | -10 | 14 | 4.11 | 14
1985-02-13 | 13 | 2 | 0.33333 | -9.4 | 15.08 | 4.4105 | 15.08
1985-02-13 | 13 | 2 | 0.375 | -8.3 | 17.06 | 4.9868 | 17.06
1985-02-13 | 13 | 2 | 0.41667 | -7.8 | 17.96 | 5.2016 | 17.96
1985-02-13 | 13 | 2 | 0.45833 | -7.2 | 19.04 | 5.4654 | 19.04
1985-02-13 | 13 | 2 | 0.5 | -6.1 | 21.02 | 5.9828 | 21.02
1985-02-13 | 13 | 2 | 0.54167 | -5.6 | 21.92 | 6.1398 | 21.92
1985-02-13 | 13 | 2 | 0.58333 | -5 | 23 | 6.4459 | 23
1985-02-13 | 13 | 2 | 0.625 | -3.9 | 24.98 | 6.9838 | 24.98
1985-02-13 | 13 | 2 | 0.66667 | -3.3 | 26.06 | 7.295 | 26.06
1985-02-13 | 13 | 2 | 0.70833 | -3.3 | 26.06 | 7.295 | 26.06
1985-02-13 | 13 | 2 | 0.75 | -3.9 | 24.98 | 7.0129 | 24.98
1985-02-13 | 13 | 2 | 0.79167 | -3.9 | 24.98 | 7.0129 | 24.98
1985-02-13 | 13 | 2 | 0.83333 | -3.9 | 24.98 | 7.0712 | 24.98
1985-02-13 | 13 | 2 | 0.875 | -3.9 | 24.98 | 7.1586 | 24.98
1985-02-13 | 13 | 2 | 0.91667 | -3.9 | 24.98 | 7.1586 |  | 24.98
1985-02-13 | 13 | 2 | 0.95833 | -3.3 | 26.06 | 7.4483 |  | 26.06
1985-02-13 | 13 | 2 | 1 | -3.3 | 26.06 | 7.4483 |  | 26.06
1985-02-14 | 14 | 2 | 0.041667 | -3.3 | 26.06 | 7.4177 |  | 26.06
1985-02-14 | 14 | 2 | 0.083333 | -3.3 | 26.06 | 7.4177 |  | 26.06
1985-02-14 | 14 | 2 | 0.125 | -3.3 | 26.06 | 7.4177 |  | 26.06
1985-02-14 | 14 | 2 | 0.16667 | -3.9 | 24.98 | 7.0712 |  | 24.98
1985-02-14 | 14 | 2 | 0.20833 | -3.3 | 26.06 | 7.3563 |  | 26.06
1985-02-14 | 14 | 2 | 0.25 | -3.3 | 26.06 | 7.3563 | 26.06
1985-02-14 | 14 | 2 | 0.29167 | -3.9 | 24.98 | 7.1586 | 24.98
1985-02-14 | 14 | 2 | 0.33333 | -3.3 | 26.06 | 7.4177 | 26.06
1985-02-14 | 14 | 2 | 0.375 | -2.8 | 26.96 | 7.7483 | 26.96
1985-02-14 | 14 | 2 | 0.41667 | -2.8 | 26.96 | 7.8123 | 26.96
1985-02-14 | 14 | 2 | 0.45833 | -2.2 | 28.04 | 8.0068 | 28.04
1985-02-14 | 14 | 2 | 0.5 | -1.7 | 28.94 | 8.2076 | 28.94
1985-02-14 | 14 | 2 | 0.54167 | -0.6 | 30.92 | 8.7664 | 30.92
1985-02-14 | 14 | 2 | 0.58333 | -0.6 | 30.92 | 8.6894 | 30.92
1985-02-14 | 14 | 2 | 0.625 | 0.6 | 33.08 | 9.3331 | 33.08
1985-02-14 | 14 | 2 | 0.66667 | 0.6 | 33.08 | 9.2907 | 33.08
1985-02-14 | 14 | 2 | 0.70833 | 0.6 | 33.08 | 9.1638 | 33.08
1985-02-14 | 14 | 2 | 0.75 | 0 | 32 | 8.8518 | 32
1985-02-14 | 14 | 2 | 0.79167 | -0.6 | 30.92 | 8.6124 | 30.92
1985-02-14 | 14 | 2 | 0.83333 | -0.6 | 30.92 | 8.5739 | 30.92
1985-02-14 | 14 | 2 | 0.875 | -1.1 | 30.02 | 8.3475 | 30.02
1985-02-14 | 14 | 2 | 0.91667 | -1.7 | 28.94 | 8.1374 |  | 28.94
1985-02-14 | 14 | 2 | 0.95833 | -2.2 | 28.04 | 7.8721 |  | 28.04
1985-02-14 | 14 | 2 | 1 | -2.2 | 28.04 | 7.8721 |  | 28.04
1985-02-15 | 15 | 2 | 0.041667 | -2.8 | 26.96 | 7.8763 |  | 26.96
1985-02-15 | 15 | 2 | 0.083333 | -3.3 | 26.06 | 7.6017 |  | 26.06
1985-02-15 | 15 | 2 | 0.125 | -4.4 | 24.08 | 7.1729 |  | 24.08
1985-02-15 | 15 | 2 | 0.16667 | -4.4 | 24.08 | 7.3965 |  | 24.08
1985-02-15 | 15 | 2 | 0.20833 | -4.4 | 24.08 | 7.5922 |  | 24.08
1985-02-15 | 15 | 2 | 0.25 | -5 | 23 | 7.4009 | 23
1985-02-15 | 15 | 2 | 0.29167 | -5 | 23 | 7.2415 | 23
1985-02-15 | 15 | 2 | 0.33333 | -3.3 | 26.06 | 7.9701 | 26.06
1985-02-15 | 15 | 2 | 0.375 | -2.2 | 28.04 | 8.6135 | 28.04
1985-02-15 | 15 | 2 | 0.41667 | -0.6 | 30.92 | 9.422 | 30.92
1985-02-15 | 15 | 2 | 0.45833 | 0 | 32 | 9.784 | 32
1985-02-15 | 15 | 2 | 0.5 | 1.7 | 35.06 | 11.0732 | 35.06
1985-02-15 | 15 | 2 | 0.54167 | 2.8 | 37.04 | 11.8185 | 37.04
1985-02-15 | 15 | 2 | 0.58333 | 2.2 | 35.96 | 12.3433 | 35.96
1985-02-15 | 15 | 2 | 0.625 | 2.2 | 35.96 | 12.4869 | 35.96
1985-02-15 | 15 | 2 | 0.66667 | 2.2 | 35.96 | 12.6785 | 35.96
1985-02-15 | 15 | 2 | 0.70833 | 1.7 | 35.06 | 12.6416 | 35.06
1985-02-15 | 15 | 2 | 0.75 | 2.2 | 35.96 | 13.0141 | 35.96
1985-02-15 | 15 | 2 | 0.79167 | 2.8 | 37.04 | 13.6684 | 37.04
1985-02-15 | 15 | 2 | 0.83333 | 2.2 | 35.96 | 13.398 | 35.96
1985-02-15 | 15 | 2 | 0.875 | 1.7 | 35.06 | 13.0117 | 35.06
1985-02-15 | 15 | 2 | 0.91667 | 1.7 | 35.06 | 13.0117 |  | 35.06
1985-02-15 | 15 | 2 | 0.95833 | 2.2 | 35.96 | 13.206 |  | 35.96
1985-02-15 | 15 | 2 | 1 | 2.8 | 37.04 | 13.6684 |  | 37.04
1985-02-16 | 16 | 2 | 0.041667 | 3.9 | 39.02 | 14.5371 |  | 39.02
1985-02-16 | 16 | 2 | 0.083333 | 3.3 | 37.94 | 14.1118 |  | 37.94
1985-02-16 | 16 | 2 | 0.125 | 3.9 | 39.02 | 14.3743 |  | 39.02
1985-02-16 | 16 | 2 | 0.16667 | 3.3 | 37.94 | 13.8519 |  | 37.94
1985-02-16 | 16 | 2 | 0.20833 | 3.3 | 37.94 | 13.3328 |  | 37.94
1985-02-16 | 16 | 2 | 0.25 | 3.3 | 37.94 | 13.1772 | 37.94
1985-02-16 | 16 | 2 | 0.29167 | 2.8 | 37.04 | 13.1173 | 37.04
1985-02-16 | 16 | 2 | 0.33333 | 3.9 | 39.02 | 13.9946 | 39.02
1985-02-16 | 16 | 2 | 0.375 | 5 | 41 | 14.2614 | 41
1985-02-16 | 16 | 2 | 0.41667 | 6.1 | 42.98 | 14.7142 | 42.98
1985-02-16 | 16 | 2 | 0.45833 | 7.2 | 44.96 | 15.2001 | 44.96
1985-02-16 | 16 | 2 | 0.5 | 7.8 | 46.04 | 15.5048 | 46.04
1985-02-16 | 16 | 2 | 0.54167 | 6.7 | 44.06 | 14.9646 | 44.06
1985-02-16 | 16 | 2 | 0.58333 | 6.7 | 44.06 | 14.4374 | 44.06
1985-02-16 | 16 | 2 | 0.625 | 6.1 | 42.98 | 14.0191 | 42.98
1985-02-16 | 16 | 2 | 0.66667 | 6.1 | 42.98 | 13.7037 | 42.98
1985-02-16 | 16 | 2 | 0.70833 | 6.7 | 44.06 | 13.7795 | 44.06
1985-02-16 | 16 | 2 | 0.75 | 6.1 | 42.98 | 13.1365 | 42.98
1985-02-16 | 16 | 2 | 0.79167 | 6.1 | 42.98 | 13.1365 | 42.98
1985-02-16 | 16 | 2 | 0.83333 | 5 | 41 | 13.0339 | 41
1985-02-16 | 16 | 2 | 0.875 | 3.9 | 39.02 | 12.5882 | 39.02
1985-02-16 | 16 | 2 | 0.91667 | 3.9 | 39.02 | 12.3184 |  | 39.02
1985-02-16 | 16 | 2 | 0.95833 | 3.3 | 37.94 | 11.935 |  | 37.94
1985-02-16 | 16 | 2 | 1 | 3.3 | 37.94 | 11.935 |  | 37.94
1985-02-17 | 17 | 2 | 0.041667 | 3.3 | 37.94 | 11.7801 |  | 37.94
1985-02-17 | 17 | 2 | 0.083333 | 2.8 | 37.04 | 11.4199 |  | 37.04
1985-02-17 | 17 | 2 | 0.125 | 2.2 | 35.96 | 11.1488 |  | 35.96
1985-02-17 | 17 | 2 | 0.16667 | 2.2 | 35.96 | 11.0534 |  | 35.96
1985-02-17 | 17 | 2 | 0.20833 | 1.7 | 35.06 | 10.7052 |  | 35.06
1985-02-17 | 17 | 2 | 0.25 | 1.1 | 33.98 | 10.4361 | 33.98
1985-02-17 | 17 | 2 | 0.29167 | 0.6 | 33.08 | 10.2231 | 33.08
1985-02-17 | 17 | 2 | 0.33333 | 0.6 | 33.08 | 10.2231 | 33.08
1985-02-17 | 17 | 2 | 0.375 | 2.2 | 35.96 | 11.0534 | 35.96
1985-02-17 | 17 | 2 | 0.41667 | 3.3 | 37.94 | 11.522 | 37.94
1985-02-17 | 17 | 2 | 0.45833 | 4.4 | 39.92 | 11.8598 | 39.92
1985-02-17 | 17 | 2 | 0.5 | 5.6 | 42.08 | 12.5194 | 42.08
1985-02-17 | 17 | 2 | 0.54167 | 7.2 | 44.96 | 13.2256 | 44.96
1985-02-17 | 17 | 2 | 0.58333 | 7.8 | 46.04 | 13.3759 | 46.04
1985-02-17 | 17 | 2 | 0.625 | 7.8 | 46.04 | 13.0931 | 46.04
1985-02-17 | 17 | 2 | 0.66667 | 7.2 | 44.96 | 12.8185 | 44.96
1985-02-17 | 17 | 2 | 0.70833 | 7.2 | 44.96 | 12.6151 | 44.96
1985-02-17 | 17 | 2 | 0.75 | 6.1 | 42.98 | 12.1935 | 42.98
1985-02-17 | 17 | 2 | 0.79167 | 6.1 | 42.98 | 12.5075 | 42.98
1985-02-17 | 17 | 2 | 0.83333 | 6.1 | 42.98 | 12.3191 | 42.98
1985-02-17 | 17 | 2 | 0.875 | 5 | 41 | 12.2762 | 41
1985-02-17 | 17 | 2 | 0.91667 | 3.3 | 37.94 | 12.659 |  | 37.94
1985-02-17 | 17 | 2 | 0.95833 | 2.8 | 37.04 | 12.2675 |  | 37.04
1985-02-17 | 17 | 2 | 1 | 3.9 | 39.02 | 12.1566 |  | 39.02
1985-02-18 | 18 | 2 | 0.041667 | 3.9 | 39.02 | 12.0488 |  | 39.02
1985-02-18 | 18 | 2 | 0.083333 | 2.2 | 35.96 | 12.3433 |  | 35.96
1985-02-18 | 18 | 2 | 0.125 | 2.8 | 37.04 | 11.7188 |  | 37.04
1985-02-18 | 18 | 2 | 0.16667 | 1.7 | 35.06 | 11.4876 |  | 35.06
1985-02-18 | 18 | 2 | 0.20833 | 0.6 | 33.08 | 11.6265 |  | 33.08
1985-02-18 | 18 | 2 | 0.25 | 0 | 32 | 11.2076 | 32
1985-02-18 | 18 | 2 | 0.29167 | 0.6 | 33.08 | 12.0102 | 33.08
1985-02-18 | 18 | 2 | 0.33333 | 2.2 | 35.96 | 12.6785 | 35.96
1985-02-18 | 18 | 2 | 0.375 | 3.3 | 37.94 | 12.9698 | 37.94
1985-02-18 | 18 | 2 | 0.41667 | 5.6 | 42.08 | 13.7969 | 42.08
1985-02-18 | 18 | 2 | 0.45833 | 6.1 | 42.98 | 13.5145 | 42.98
1985-02-18 | 18 | 2 | 0.5 | 6.7 | 44.06 | 13.5168 | 44.06
1985-02-18 | 18 | 2 | 0.54167 | 7.8 | 46.04 | 13.5174 | 46.04
1985-02-18 | 18 | 2 | 0.58333 | 9.4 | 48.92 | 14.2586 | 48.92
1985-02-18 | 18 | 2 | 0.625 | 10 | 50 | 14.4584 | 50
1985-02-18 | 18 | 2 | 0.66667 | 9.4 | 48.92 | 14.1796 | 48.92
1985-02-18 | 18 | 2 | 0.70833 | 8.3 | 46.94 | 13.9667 | 46.94
1985-02-18 | 18 | 2 | 0.75 | 6.7 | 44.06 | 13.2542 | 44.06
1985-02-18 | 18 | 2 | 0.79167 | 5 | 41 | 13.0339 | 41
1985-02-18 | 18 | 2 | 0.83333 | 5 | 41 | 12.8006 | 41
1985-02-18 | 18 | 2 | 0.875 | 5 | 41 | 12.8006 | 41
1985-02-18 | 18 | 2 | 0.91667 | 3.9 | 39.02 | 12.3184 |  | 39.02
1985-02-18 | 18 | 2 | 0.95833 | 2.8 | 37.04 | 12.6172 |  | 37.04
1985-02-18 | 18 | 2 | 1 | 2.8 | 37.04 | 12.7672 |  | 37.04
1985-02-19 | 19 | 2 | 0.041667 | 1.7 | 35.06 | 12.2719 |  | 35.06
1985-02-19 | 19 | 2 | 0.083333 | 1.1 | 33.98 | 12.0243 |  | 33.98
1985-02-19 | 19 | 2 | 0.125 | 0 | 32 | 11.3707 |  | 32
1985-02-19 | 19 | 2 | 0.16667 | 0 | 32 | 11.3707 |  | 32
1985-02-19 | 19 | 2 | 0.20833 | -0.6 | 30.92 | 10.9307 |  | 30.92
1985-02-19 | 19 | 2 | 0.25 | 0 | 32 | 11.3707 | 32
1985-02-19 | 19 | 2 | 0.29167 | -0.6 | 30.92 | 10.9307 | 30.92
1985-02-19 | 19 | 2 | 0.33333 | 0.6 | 33.08 | 11.456 | 33.08
1985-02-19 | 19 | 2 | 0.375 | 2.2 | 35.96 | 12.3433 | 35.96
1985-02-19 | 19 | 2 | 0.41667 | 4.4 | 39.92 | 12.9771 | 39.92
1985-02-19 | 19 | 2 | 0.45833 | 6.1 | 42.98 | 14.0191 | 42.98
1985-02-19 | 19 | 2 | 0.5 | 8.9 | 48.02 | 15.4109 | 48.02
1985-02-19 | 19 | 2 | 0.54167 | 10.6 | 51.08 | 15.3341 | 51.08
1985-02-19 | 19 | 2 | 0.58333 | 11.7 | 53.06 | 14.9386 | 53.06
1985-02-19 | 19 | 2 | 0.625 | 12.2 | 53.96 | 15.0391 | 53.96
1985-02-19 | 19 | 2 | 0.66667 | 11.7 | 53.06 | 14.7543 | 53.06
1985-02-19 | 19 | 2 | 0.70833 | 11.1 | 51.98 | 14.5038 | 51.98
1985-02-19 | 19 | 2 | 0.75 | 10 | 50 | 14.1295 | 50
1985-02-19 | 19 | 2 | 0.79167 | 9.4 | 48.92 | 14.0218 | 48.92
1985-02-19 | 19 | 2 | 0.83333 | 8.9 | 48.02 | 14.1869 | 48.02
1985-02-19 | 19 | 2 | 0.875 | 8.9 | 48.02 | 14.1869 | 48.02
1985-02-19 | 19 | 2 | 0.91667 | 8.9 | 48.02 | 14.6454 |  | 48.02
1985-02-19 | 19 | 2 | 0.95833 | 8.3 | 46.94 | 14.4801 |  | 46.94
1985-02-19 | 19 | 2 | 1 | 7.2 | 44.96 | 14.1773 |  | 44.96
1985-02-20 | 20 | 2 | 0.041667 | 6.1 | 42.98 | 14.2086 |  | 42.98
1985-02-20 | 20 | 2 | 0.083333 | 5.6 | 42.08 | 13.7969 |  | 42.08
1985-02-20 | 20 | 2 | 0.125 | 4.4 | 39.92 | 13.3131 |  | 39.92
1985-02-20 | 20 | 2 | 0.16667 | 5 | 41 | 13.7348 |  | 41
1985-02-20 | 20 | 2 | 0.20833 | 3.9 | 39.02 | 13.2366 |  | 39.02
1985-02-20 | 20 | 2 | 0.25 | 2.8 | 37.04 | 12.9672 | 37.04
1985-02-20 | 20 | 2 | 0.29167 | 2.8 | 37.04 | 12.6172 | 37.04
1985-02-20 | 20 | 2 | 0.33333 | 4.4 | 39.92 | 12.9771 | 39.92
1985-02-20 | 20 | 2 | 0.375 | 5.6 | 42.08 | 13.0663 | 42.08
1985-02-20 | 20 | 2 | 0.41667 | 6.1 | 42.98 | 13.2625 | 42.98
1985-02-20 | 20 | 2 | 0.45833 | 6.7 | 44.06 | 13.7795 | 44.06
1985-02-20 | 20 | 2 | 0.5 | 6.7 | 44.06 | 14.3057 | 44.06
1985-02-20 | 20 | 2 | 0.54167 | 7.2 | 44.96 | 14.5179 | 44.96
1985-02-20 | 20 | 2 | 0.58333 | 6.7 | 44.06 | 14.4374 | 44.06
1985-02-20 | 20 | 2 | 0.625 | 6.7 | 44.06 | 14.635 | 44.06
1985-02-20 | 20 | 2 | 0.66667 | 7.2 | 44.96 | 14.8588 | 44.96
1985-02-20 | 20 | 2 | 0.70833 | 7.2 | 44.96 | 14.8588 | 44.96
1985-02-20 | 20 | 2 | 0.75 | 5 | 41 | 13.9103 | 41
1985-02-20 | 20 | 2 | 0.79167 | 4.4 | 39.92 | 13.6493 | 39.92
1985-02-20 | 20 | 2 | 0.83333 | 3.9 | 39.02 | 13.453 | 39.02
1985-02-20 | 20 | 2 | 0.875 | 3.3 | 37.94 | 13.3328 | 37.94
1985-02-20 | 20 | 2 | 0.91667 | 3.3 | 37.94 | 13.1772 |  | 37.94
1985-02-20 | 20 | 2 | 0.95833 | 3.9 | 39.02 | 13.6154 |  | 39.02
1985-02-20 | 20 | 2 | 1 | 3.3 | 37.94 | 13.1772 |  | 37.94
1985-02-21 | 21 | 2 | 0.041667 | 2.8 | 37.04 | 12.9672 |  | 37.04
1985-02-21 | 21 | 2 | 0.083333 | 2.8 | 37.04 | 13.1173 |  | 37.04
1985-02-21 | 21 | 2 | 0.125 | 2.8 | 37.04 | 13.1173 |  | 37.04
1985-02-21 | 21 | 2 | 0.16667 | 2.8 | 37.04 | 13.1173 |  | 37.04
1985-02-21 | 21 | 2 | 0.20833 | 2.8 | 37.04 | 13.1173 |  | 37.04
1985-02-21 | 21 | 2 | 0.25 | 2.8 | 37.04 | 13.1173 | 37.04
1985-02-21 | 21 | 2 | 0.29167 | 2.8 | 37.04 | 12.9672 | 37.04
1985-02-21 | 21 | 2 | 0.33333 | 2.8 | 37.04 | 13.1173 | 37.04
1985-02-21 | 21 | 2 | 0.375 | 1.7 | 35.06 | 12.6416 | 35.06
1985-02-21 | 21 | 2 | 0.41667 | 2.8 | 37.04 | 13.4679 | 37.04
1985-02-21 | 21 | 2 | 0.45833 | 3.3 | 37.94 | 13.4884 | 37.94
1985-02-21 | 21 | 2 | 0.5 | 3.9 | 39.02 | 14.1573 | 39.02
1985-02-21 | 21 | 2 | 0.54167 | 3.9 | 39.02 | 13.7779 | 39.02
1985-02-21 | 21 | 2 | 0.58333 | 4.4 | 39.92 | 13.8176 | 39.92
1985-02-21 | 21 | 2 | 0.625 | 3.9 | 39.02 | 13.453 | 39.02
1985-02-21 | 21 | 2 | 0.66667 | 4.4 | 39.92 | 13.8176 | 39.92
1985-02-21 | 21 | 2 | 0.70833 | 4.4 | 39.92 | 13.9859 | 39.92
1985-02-21 | 21 | 2 | 0.75 | 5.6 | 42.08 | 14.5292 | 42.08
1985-02-21 | 21 | 2 | 0.79167 | 5 | 41 | 14.0858 | 41
1985-02-21 | 21 | 2 | 0.83333 | 4.4 | 39.92 | 13.6493 | 39.92
1985-02-21 | 21 | 2 | 0.875 | 4.4 | 39.92 | 13.0891 | 39.92
1985-02-21 | 21 | 2 | 0.91667 | 3.9 | 39.02 | 12.5882 |  | 39.02
1985-02-21 | 21 | 2 | 0.95833 | 2.8 | 37.04 | 11.9681 |  | 37.04
1985-02-21 | 21 | 2 | 1 | 2.8 | 37.04 | 11.8185 |  | 37.04
1985-02-22 | 22 | 2 | 0.041667 | 2.8 | 37.04 | 11.8185 |  | 37.04
1985-02-22 | 22 | 2 | 0.083333 | 2.2 | 35.96 | 11.2919 |  | 35.96
1985-02-22 | 22 | 2 | 0.125 | 1.1 | 33.98 | 10.5682 |  | 33.98
1985-02-22 | 22 | 2 | 0.16667 | 0.6 | 33.08 | 10.3504 |  | 33.08
1985-02-22 | 22 | 2 | 0.20833 | 0 | 32 | 9.8652 |  | 32
1985-02-22 | 22 | 2 | 0.25 | -1.1 | 30.02 | 9.3089 | 30.02
1985-02-22 | 22 | 2 | 0.29167 | -1.7 | 28.94 | 8.7701 | 28.94
1985-02-22 | 22 | 2 | 0.33333 | -1.7 | 28.94 | 8.6645 | 28.94
1985-02-22 | 22 | 2 | 0.375 | -1.1 | 30.02 | 8.9388 | 30.02
1985-02-22 | 22 | 2 | 0.41667 | -1.1 | 30.02 | 8.9388 | 30.02
1985-02-22 | 22 | 2 | 0.45833 | 0.6 | 33.08 | 9.6718 | 33.08
1985-02-22 | 22 | 2 | 0.5 | 1.1 | 33.98 | 9.8644 | 33.98
1985-02-22 | 22 | 2 | 0.54167 | 2.2 | 35.96 | 10.2438 | 35.96
1985-02-22 | 22 | 2 | 0.58333 | 3.3 | 37.94 | 10.9034 | 37.94
1985-02-22 | 22 | 2 | 0.625 | 3.3 | 37.94 | 10.8519 | 37.94
1985-02-22 | 22 | 2 | 0.66667 | 4.4 | 39.92 | 11.3025 | 39.92
1985-02-22 | 22 | 2 | 0.70833 | 3.9 | 39.02 | 11.0264 | 39.02
1985-02-22 | 22 | 2 | 0.75 | 3.3 | 37.94 | 10.9034 | 37.94
1985-02-22 | 22 | 2 | 0.79167 | 3.3 | 37.94 | 11.1094 | 37.94
1985-02-22 | 22 | 2 | 0.83333 | 3.3 | 37.94 | 11.1094 | 37.94
1985-02-22 | 22 | 2 | 0.875 | 2.8 | 37.04 | 10.7731 | 37.04
1985-02-22 | 22 | 2 | 0.91667 | 3.3 | 37.94 | 10.9034 |  | 37.94
1985-02-22 | 22 | 2 | 0.95833 | 3.3 | 37.94 | 10.9034 |  | 37.94
1985-02-22 | 22 | 2 | 1 | 3.3 | 37.94 | 11.1094 |  | 37.94
1985-02-23 | 23 | 2 | 0.041667 | 3.3 | 37.94 | 11.2125 |  | 37.94
1985-02-23 | 23 | 2 | 0.083333 | 2.8 | 37.04 | 10.972 |  | 37.04
1985-02-23 | 23 | 2 | 0.125 | 3.3 | 37.94 | 11.2125 |  | 37.94
1985-02-23 | 23 | 2 | 0.16667 | 3.3 | 37.94 | 11.3157 |  | 37.94
1985-02-23 | 23 | 2 | 0.20833 | 3.3 | 37.94 | 11.3157 |  | 37.94
1985-02-23 | 23 | 2 | 0.25 | 3.9 | 39.02 | 11.7794 | 39.02
1985-02-23 | 23 | 2 | 0.29167 | 3.9 | 39.02 | 12.4263 | 39.02
1985-02-23 | 23 | 2 | 0.33333 | 4.4 | 39.92 | 12.8093 | 39.92
1985-02-23 | 23 | 2 | 0.375 | 5 | 41 | 13.209 | 41
1985-02-23 | 23 | 2 | 0.41667 | 5.6 | 42.08 | 13.6141 | 42.08
1985-02-23 | 23 | 2 | 0.45833 | 6.7 | 44.06 | 13.9768 | 44.06
1985-02-23 | 23 | 2 | 0.5 | 6.7 | 44.06 | 14.3057 | 44.06
1985-02-23 | 23 | 2 | 0.54167 | 7.8 | 46.04 | 14.7937 | 46.04
1985-02-23 | 23 | 2 | 0.58333 | 7.8 | 46.04 | 14.9358 | 46.04
1985-02-23 | 23 | 2 | 0.625 | 6.7 | 44.06 | 14.8327 | 44.06
1985-02-23 | 23 | 2 | 0.66667 | 5.6 | 42.08 | 14.1629 | 42.08
1985-02-23 | 23 | 2 | 0.70833 | 5.6 | 42.08 | 15.0794 | 42.08
1985-02-23 | 23 | 2 | 0.75 | 5.6 | 42.08 | 15.263 | 42.08
1985-02-23 | 23 | 2 | 0.79167 | 5.6 | 42.08 | 15.5079 | 42.08
1985-02-23 | 23 | 2 | 0.83333 | 5.6 | 42.08 | 15.5079 | 42.08
1985-02-23 | 23 | 2 | 0.875 | 6.1 | 42.98 | 15.7278 | 42.98
1985-02-23 | 23 | 2 | 0.91667 | 6.7 | 44.06 | 15.9554 |  | 44.06
1985-02-23 | 23 | 2 | 0.95833 | 6.7 | 44.06 | 15.9554 |  | 44.06
1985-02-23 | 23 | 2 | 1 | 5.6 | 42.08 | 15.5079 |  | 42.08
1985-02-24 | 24 | 2 | 0.041667 | 5.6 | 42.08 | 15.6918 |  | 42.08
1985-02-24 | 24 | 2 | 0.083333 | 6.7 | 44.06 | 16.1539 |  | 44.06
1985-02-24 | 24 | 2 | 0.125 | 6.1 | 42.98 | 15.9182 |  | 42.98
1985-02-24 | 24 | 2 | 0.16667 | 5 | 41 | 15.2584 |  | 41
1985-02-24 | 24 | 2 | 0.20833 | 4.4 | 39.92 | 14.9977 |  | 39.92
1985-02-24 | 24 | 2 | 0.25 | 6.1 | 42.98 | 16.1722 | 42.98
1985-02-24 | 24 | 2 | 0.29167 | 5.6 | 42.08 | 15.263 | 42.08
1985-02-24 | 24 | 2 | 0.33333 | 6.1 | 42.98 | 15.094 | 42.98
1985-02-24 | 24 | 2 | 0.375 | 6.7 | 44.06 | 15.3606 | 44.06
1985-02-24 | 24 | 2 | 0.41667 | 7.2 | 44.96 | 15.405 | 44.96
1985-02-24 | 24 | 2 | 0.45833 | 5.6 | 42.08 | 14.1629 | 42.08
1985-02-24 | 24 | 2 | 0.5 | 7.2 | 44.96 | 13.9051 | 44.96
1985-02-24 | 24 | 2 | 0.54167 | 7.8 | 46.04 | 13.5882 | 46.04
1985-02-24 | 24 | 2 | 0.58333 | 8.3 | 46.94 | 13.9667 | 46.94
1985-02-24 | 24 | 2 | 0.625 | 8.3 | 46.94 | 13.454 | 46.94
1985-02-24 | 24 | 2 | 0.66667 | 7.2 | 44.96 | 13.0219 | 44.96
1985-02-24 | 24 | 2 | 0.70833 | 5.6 | 42.08 | 12.3979 | 42.08
1985-02-24 | 24 | 2 | 0.75 | 4.4 | 39.92 | 11.6925 | 39.92
1985-02-24 | 24 | 2 | 0.79167 | 3.3 | 37.94 | 11.0064 | 37.94
1985-02-24 | 24 | 2 | 0.83333 | 1.7 | 35.06 | 10.4295 | 35.06
1985-02-24 | 24 | 2 | 0.875 | 1.1 | 33.98 | 10.0402 | 33.98
1985-02-24 | 24 | 2 | 0.91667 | 0 | 32 | 9.2568 |  | 32
1985-02-24 | 24 | 2 | 0.95833 | -1.1 | 30.02 | 8.5322 |  | 30.02
1985-02-24 | 24 | 2 | 1 | -2.2 | 28.04 | 8.0742 |  | 28.04
1985-02-25 | 25 | 2 | 0.041667 | -2.2 | 28.04 | 8.0068 |  | 28.04
1985-02-25 | 25 | 2 | 0.083333 | -2.8 | 26.96 | 7.7483 |  | 26.96
1985-02-25 | 25 | 2 | 0.125 | -3.3 | 26.06 | 7.6017 |  | 26.06
1985-02-25 | 25 | 2 | 0.16667 | -4.4 | 24.08 | 6.9216 |  | 24.08
1985-02-25 | 25 | 2 | 0.20833 | -4.4 | 24.08 | 6.8658 |  | 24.08
1985-02-25 | 25 | 2 | 0.25 | -4.4 | 24.08 | 6.9216 | 24.08
1985-02-25 | 25 | 2 | 0.29167 | -4.4 | 24.08 | 6.9775 | 24.08
1985-02-25 | 25 | 2 | 0.33333 | -3.3 | 26.06 | 7.4177 | 26.06
1985-02-25 | 25 | 2 | 0.375 | -2.8 | 26.96 | 7.6842 | 26.96
1985-02-25 | 25 | 2 | 0.41667 | -1.7 | 28.94 | 8.2779 | 28.94
1985-02-25 | 25 | 2 | 0.45833 | -0.6 | 30.92 | 8.7664 | 30.92
1985-02-25 | 25 | 2 | 0.5 | 1.1 | 33.98 | 9.4253 | 33.98
1985-02-25 | 25 | 2 | 0.54167 | 2.2 | 35.96 | 10.0536 | 35.96
1985-02-25 | 25 | 2 | 0.58333 | 3.3 | 37.94 | 10.646 | 37.94
1985-02-25 | 25 | 2 | 0.625 | 3.3 | 37.94 | 10.7489 | 37.94
1985-02-25 | 25 | 2 | 0.66667 | 3.9 | 39.02 | 11.0264 | 39.02
1985-02-25 | 25 | 2 | 0.70833 | 3.9 | 39.02 | 11.1876 | 39.02
1985-02-25 | 25 | 2 | 0.75 | 3.9 | 39.02 | 11.2413 | 39.02
1985-02-25 | 25 | 2 | 0.79167 | 3.9 | 39.02 | 11.2413 | 39.02
1985-02-25 | 25 | 2 | 0.83333 | 3.9 | 39.02 | 11.3489 | 39.02
1985-02-25 | 25 | 2 | 0.875 | 3.9 | 39.02 | 11.3489 | 39.02
1985-02-25 | 25 | 2 | 0.91667 | 3.9 | 39.02 | 11.3489 |  | 39.02
1985-02-25 | 25 | 2 | 0.95833 | 3.3 | 37.94 | 11.3157 |  | 37.94
1985-02-25 | 25 | 2 | 1 | 3.9 | 39.02 | 11.5641 |  | 39.02
1985-02-26 | 26 | 2 | 0.041667 | -1.1 | 30.02 | 9.42 |  | 30.02
1985-02-26 | 26 | 2 | 0.083333 | -1.7 | 28.94 | 8.946 |  | 28.94
1985-02-26 | 26 | 2 | 0.125 | -2.2 | 28.04 | 8.7147 |  | 28.04
1985-02-26 | 26 | 2 | 0.16667 | -2.8 | 26.96 | 8.7741 |  | 26.96
1985-02-26 | 26 | 2 | 0.20833 | -3.3 | 26.06 | 8.4619 |  | 26.06
1985-02-26 | 26 | 2 | 0.25 | -4.4 | 24.08 | 8.068 | 24.08
1985-02-26 | 26 | 2 | 0.29167 | -6.1 | 21.02 | 7.0442 | 21.02
1985-02-26 | 26 | 2 | 0.33333 | -6.7 | 19.94 | 6.6829 | 19.94
1985-02-26 | 26 | 2 | 0.375 | -7.2 | 19.04 | 6.3635 | 19.04
1985-02-26 | 26 | 2 | 0.41667 | -6.7 | 19.94 | 6.2476 | 19.94
1985-02-26 | 26 | 2 | 0.45833 | -6.1 | 21.02 | 7.0442 | 21.02
1985-02-26 | 26 | 2 | 0.5 | -5.6 | 21.92 | 6.9708 | 21.92
1985-02-26 | 26 | 2 | 0.54167 | -4.4 | 24.08 | 7.2567 | 24.08
1985-02-26 | 26 | 2 | 0.58333 | -3.3 | 26.06 | 7.5404 | 26.06
1985-02-26 | 26 | 2 | 0.625 | -2.8 | 26.96 | 7.4923 | 26.96
1985-02-26 | 26 | 2 | 0.66667 | -2.2 | 28.04 | 7.7712 | 28.04
1985-02-26 | 26 | 2 | 0.70833 | -1.7 | 28.94 | 8.1374 | 28.94
1985-02-26 | 26 | 2 | 0.75 | -1.1 | 30.02 | 8.4952 | 30.02
1985-02-26 | 26 | 2 | 0.79167 | -1.1 | 30.02 | 8.4213 | 30.02
1985-02-26 | 26 | 2 | 0.83333 | -1.1 | 30.02 | 8.3106 | 30.02
1985-02-26 | 26 | 2 | 0.875 | -1.1 | 30.02 | 8.3106 | 30.02
1985-02-26 | 26 | 2 | 0.91667 | -0.6 | 30.92 | 8.4199 |  | 30.92
1985-02-26 | 26 | 2 | 0.95833 | -0.6 | 30.92 | 8.4584 |  | 30.92
1985-02-26 | 26 | 2 | 1 | -1.1 | 30.02 | 8.3106 |  | 30.02
1985-02-27 | 27 | 2 | 0.041667 | -0.6 | 30.92 | 8.8435 |  | 30.92
1985-02-27 | 27 | 2 | 0.083333 | -0.6 | 30.92 | 8.9976 |  | 30.92
1985-02-27 | 27 | 2 | 0.125 | -1.1 | 30.02 | 9.3089 |  | 30.02
1985-02-27 | 27 | 2 | 0.16667 | -1.1 | 30.02 | 9.6423 |  | 30.02
1985-02-27 | 27 | 2 | 0.20833 | -1.7 | 28.94 | 9.7566 |  | 28.94
1985-02-27 | 27 | 2 | 0.25 | -1.7 | 28.94 | 10.0037 | 28.94
1985-02-27 | 27 | 2 | 0.29167 | -1.7 | 28.94 | 9.6155 | 28.94
1985-02-27 | 27 | 2 | 0.33333 | -1.1 | 30.02 | 10.0132 | 30.02
1985-02-27 | 27 | 2 | 0.375 | -0.6 | 30.92 | 10.6207 | 30.92
1985-02-27 | 27 | 2 | 0.41667 | -1.7 | 28.94 | 10.145 | 28.94
1985-02-27 | 27 | 2 | 0.45833 | -2.2 | 28.04 | 9.7963 | 28.04
1985-02-27 | 27 | 2 | 0.5 | -2.8 | 26.96 | 9.3846 | 26.96
1985-02-27 | 27 | 2 | 0.54167 | -2.2 | 28.04 | 9.7963 | 28.04
1985-02-27 | 27 | 2 | 0.58333 | -1.7 | 28.94 | 10.3217 | 28.94
1985-02-27 | 27 | 2 | 0.625 | -1.1 | 30.02 | 10.905 | 30.02
1985-02-27 | 27 | 2 | 0.66667 | -0.6 | 30.92 | 11.1246 | 30.92
1985-02-27 | 27 | 2 | 0.70833 | 0 | 32 | 11.5339 | 32
1985-02-27 | 27 | 2 | 0.75 | 0 | 32 | 11.5339 | 32
1985-02-27 | 27 | 2 | 0.79167 | 0 | 32 | 11.5339 | 32
1985-02-27 | 27 | 2 | 0.83333 | 0 | 32 | 11.5339 | 32
1985-02-27 | 27 | 2 | 0.875 | -0.6 | 30.92 | 11.1246 | 30.92
1985-02-27 | 27 | 2 | 0.91667 | 0 | 32 | 11.738 |  | 32
1985-02-27 | 27 | 2 | 0.95833 | 0.6 | 33.08 | 12.0102 |  | 33.08
1985-02-27 | 27 | 2 | 1 | 0.6 | 33.08 | 12.0102 |  | 33.08
1985-02-28 | 28 | 2 | 0.041667 | 0.6 | 33.08 | 12.0102 |  | 33.08
1985-02-28 | 28 | 2 | 0.083333 | 0.6 | 33.08 | 12.0102 |  | 33.08
1985-02-28 | 28 | 2 | 0.125 | 0.6 | 33.08 | 12.0102 |  | 33.08
1985-02-28 | 28 | 2 | 0.16667 | 1.1 | 33.98 | 12.2012 |  | 33.98
1985-02-28 | 28 | 2 | 0.20833 | 1.1 | 33.98 | 12.3783 |  | 33.98
1985-02-28 | 28 | 2 | 0.25 | 1.1 | 33.98 | 12.3783 | 33.98
1985-02-28 | 28 | 2 | 0.29167 | 1.1 | 33.98 | 12.3783 | 33.98
1985-02-28 | 28 | 2 | 0.33333 | 1.7 | 35.06 | 12.8266 | 35.06
1985-02-28 | 28 | 2 | 0.375 | 1.7 | 35.06 | 12.8266 | 35.06
1985-02-28 | 28 | 2 | 0.41667 | 3.3 | 37.94 | 14.1118 | 37.94
1985-02-28 | 28 | 2 | 0.45833 | 3.3 | 37.94 | 14.1118 | 37.94
1985-02-28 | 28 | 2 | 0.5 | 2.8 | 37.04 | 13.8689 | 37.04
1985-02-28 | 28 | 2 | 0.54167 | 3.3 | 37.94 | 14.2678 | 37.94
1985-02-28 | 28 | 2 | 0.58333 | 3.3 | 37.94 | 14.2678 | 37.94
1985-02-28 | 28 | 2 | 0.625 | 3.9 | 39.02 | 14.7544 | 39.02
1985-02-28 | 28 | 2 | 0.66667 | 4.4 | 39.92 | 14.9977 | 39.92
1985-02-28 | 28 | 2 | 0.70833 | 5 | 41 | 15.4347 | 41
1985-02-28 | 28 | 2 | 0.75 | 5.6 | 42.08 | 15.6918 | 42.08
1985-02-28 | 28 | 2 | 0.79167 | 5 | 41 | 15.2584 | 41
1985-02-28 | 28 | 2 | 0.83333 | 5.6 | 42.08 | 15.263 | 42.08
1985-02-28 | 28 | 2 | 0.875 | 5 | 41 | 15.0236 | 41
1985-02-28 | 28 | 2 | 0.91667 | 4.8 | 40.64 | 14.864 |  | 40.64
1985-02-28 | 28 | 2 | 0.95833 | 4.5 | 40.1 | 14.853 |  | 40.1
1985-02-28 | 28 | 2 | 1 | 4.3 | 39.74 | 14.4691 |  | 39.74
1988-03-01 | 1 | 3 | 0.041667 | 4 | 39.2 | 14.2349 |  | 39.2
1988-03-01 | 1 | 3 | 0.083333 | 3.8 | 38.84 | 14.0799 |  | 38.84
1988-03-01 | 1 | 3 | 0.125 | 3.5 | 38.3 | 13.6909 |  | 38.3
1988-03-01 | 1 | 3 | 0.16667 | 3.3 | 37.94 | 13.6961 |  | 37.94
1988-03-01 | 1 | 3 | 0.20833 | 3.3 | 37.94 | 13.4884 |  | 37.94
1988-03-01 | 1 | 3 | 0.25 | 3.3 | 37.94 | 13.6961 | 37.94
1988-03-01 | 1 | 3 | 0.29167 | 2.8 | 37.04 | 13.3176 | 37.04
1988-03-01 | 1 | 3 | 0.33333 | 2.8 | 37.04 | 13.1173 | 37.04
1988-03-01 | 1 | 3 | 0.375 | 3.3 | 37.94 | 13.3328 | 37.94
1988-03-01 | 1 | 3 | 0.41667 | 3.3 | 37.94 | 13.3328 | 37.94
1988-03-01 | 1 | 3 | 0.45833 | 4.4 | 39.92 | 13.6493 | 39.92
1988-03-01 | 1 | 3 | 0.5 | 5 | 41 | 13.5595 | 41
1988-03-01 | 1 | 3 | 0.54167 | 5.6 | 42.08 | 13.7969 | 42.08
1988-03-01 | 1 | 3 | 0.58333 | 5.6 | 42.08 | 13.7969 | 42.08
1988-03-01 | 1 | 3 | 0.625 | 5.6 | 42.08 | 14.1629 | 42.08
1988-03-01 | 1 | 3 | 0.66667 | 5.6 | 42.08 | 14.1629 | 42.08
1988-03-01 | 1 | 3 | 0.70833 | 5.6 | 42.08 | 14.1629 | 42.08
1988-03-01 | 1 | 3 | 0.75 | 5 | 41 | 14.0858 | 41
1988-03-01 | 1 | 3 | 0.79167 | 5 | 41 | 13.9103 | 41
1988-03-01 | 1 | 3 | 0.83333 | 4.4 | 39.92 | 13.4812 | 39.92
1988-03-01 | 1 | 3 | 0.875 | 3.9 | 39.02 | 13.2366 | 39.02
1988-03-01 | 1 | 3 | 0.91667 | 3.9 | 39.02 | 13.2366 |  | 39.02
1988-03-01 | 1 | 3 | 0.95833 | 2.8 | 37.04 | 12.4173 |  | 37.04
1988-03-01 | 1 | 3 | 1 | 2.2 | 35.96 | 11.865 |  | 35.96
1988-03-02 | 2 | 3 | 0.041667 | 1.7 | 35.06 | 11.4876 |  | 35.06
1988-03-02 | 2 | 3 | 0.083333 | 0.6 | 33.08 | 10.6052 |  | 33.08
1988-03-02 | 2 | 3 | 0.125 | 0 | 32 | 9.8652 |  | 32
1988-03-02 | 2 | 3 | 0.16667 | -0.6 | 30.92 | 9.615 |  | 30.92
1988-03-02 | 2 | 3 | 0.20833 | -0.6 | 30.92 | 9.4992 |  | 30.92
1988-03-02 | 2 | 3 | 0.25 | -1.1 | 30.02 | 9.42 | 30.02
1988-03-02 | 2 | 3 | 0.29167 | -1.1 | 30.02 | 9.42 | 30.02
1988-03-02 | 2 | 3 | 0.33333 | -0.6 | 30.92 | 9.615 | 30.92
1988-03-02 | 2 | 3 | 0.375 | -0.6 | 30.92 | 9.4992 | 30.92
1988-03-02 | 2 | 3 | 0.41667 | 1.1 | 33.98 | 10.3481 | 33.98
1988-03-02 | 2 | 3 | 0.45833 | 1.7 | 35.06 | 10.5213 | 35.06
1988-03-02 | 2 | 3 | 0.5 | 1.1 | 33.98 | 10.2601 | 33.98
1988-03-02 | 2 | 3 | 0.54167 | 2.8 | 37.04 | 10.8725 | 37.04
1988-03-02 | 2 | 3 | 0.58333 | 2.8 | 37.04 | 10.7731 | 37.04
1988-03-02 | 2 | 3 | 0.625 | 3.3 | 37.94 | 10.8519 | 37.94
1988-03-02 | 2 | 3 | 0.66667 | 2.8 | 37.04 | 10.475 | 37.04
1988-03-02 | 2 | 3 | 0.70833 | 2.8 | 37.04 | 10.5246 | 37.04
1988-03-02 | 2 | 3 | 0.75 | 2.2 | 35.96 | 10.1011 | 35.96
1988-03-02 | 2 | 3 | 0.79167 | 1.7 | 35.06 | 9.8328 | 35.06
1988-03-02 | 2 | 3 | 0.83333 | 1.1 | 33.98 | 9.557 | 33.98
1988-03-02 | 2 | 3 | 0.875 | 0 | 32 | 9.0947 | 32
1988-03-02 | 2 | 3 | 0.91667 | 0 | 32 | 9.0947 |  | 32
1988-03-02 | 2 | 3 | 0.95833 | -0.6 | 30.92 | 9.0362 |  | 30.92
1988-03-02 | 2 | 3 | 1 | -0.6 | 30.92 | 9.0362 |  | 30.92
1988-03-03 | 3 | 3 | 0.041667 | -1.1 | 30.02 | 9.0128 |  | 30.02
1988-03-03 | 3 | 3 | 0.083333 | -1.1 | 30.02 | 9.0128 |  | 30.02
1988-03-03 | 3 | 3 | 0.125 | -1.7 | 28.94 | 8.6645 |  | 28.94
1988-03-03 | 3 | 3 | 0.16667 | -1.7 | 28.94 | 8.6645 |  | 28.94
1988-03-03 | 3 | 3 | 0.20833 | -1.7 | 28.94 | 8.6645 |  | 28.94
1988-03-03 | 3 | 3 | 0.25 | -2.2 | 28.04 | 8.4449 | 28.04
1988-03-03 | 3 | 3 | 0.29167 | -2.2 | 28.04 | 8.4449 | 28.04
1988-03-03 | 3 | 3 | 0.33333 | -0.6 | 30.92 | 9.229 | 30.92
1988-03-03 | 3 | 3 | 0.375 | 0 | 32 | 9.5 | 32
1988-03-03 | 3 | 3 | 0.41667 | 0 | 32 | 9.5811 | 32
1988-03-03 | 3 | 3 | 0.45833 | 0.6 | 33.08 | 9.9261 | 33.08
1988-03-03 | 3 | 3 | 0.5 | 1.1 | 33.98 | 10.2601 | 33.98
1988-03-03 | 3 | 3 | 0.54167 | 2.2 | 35.96 | 10.8151 | 35.96
1988-03-03 | 3 | 3 | 0.58333 | 2.2 | 35.96 | 10.8151 | 35.96
1988-03-03 | 3 | 3 | 0.625 | 2.8 | 37.04 | 11.0714 | 37.04
1988-03-03 | 3 | 3 | 0.66667 | 2.8 | 37.04 | 11.0714 | 37.04
1988-03-03 | 3 | 3 | 0.70833 | 3.3 | 37.94 | 11.4188 | 37.94
1988-03-03 | 3 | 3 | 0.75 | 2.8 | 37.04 | 11.3203 | 37.04
1988-03-03 | 3 | 3 | 0.79167 | 2.2 | 35.96 | 11.1488 | 35.96
1988-03-03 | 3 | 3 | 0.83333 | 1.7 | 35.06 | 11.2113 | 35.06
1988-03-03 | 3 | 3 | 0.875 | 2.2 | 35.96 | 11.7216 | 35.96
1988-03-03 | 3 | 3 | 0.91667 | 1.1 | 33.98 | 11.3616 |  | 33.98
1988-03-03 | 3 | 3 | 0.95833 | 1.1 | 33.98 | 11.5382 |  | 33.98
1988-03-03 | 3 | 3 | 1 | 1.1 | 33.98 | 11.5382 |  | 33.98
1988-03-04 | 4 | 3 | 0.041667 | 1.1 | 33.98 | 11.6707 |  | 33.98
1988-03-04 | 4 | 3 | 0.083333 | 1.1 | 33.98 | 11.6707 |  | 33.98
1988-03-04 | 4 | 3 | 0.125 | 1.1 | 33.98 | 11.6707 |  | 33.98
1988-03-04 | 4 | 3 | 0.16667 | 1.1 | 33.98 | 12.2012 |  | 33.98
1988-03-04 | 4 | 3 | 0.20833 | 1.1 | 33.98 | 12.2012 |  | 33.98
1988-03-04 | 4 | 3 | 0.25 | 1.7 | 35.06 | 12.4567 | 35.06
1988-03-04 | 4 | 3 | 0.29167 | 1.7 | 35.06 | 12.6416 | 35.06
1988-03-04 | 4 | 3 | 0.33333 | 1.7 | 35.06 | 12.4567 | 35.06
1988-03-04 | 4 | 3 | 0.375 | 1.7 | 35.06 | 12.4567 | 35.06
1988-03-04 | 4 | 3 | 0.41667 | 1.7 | 35.06 | 12.4567 | 35.06
1988-03-04 | 4 | 3 | 0.45833 | 2.2 | 35.96 | 12.6785 | 35.96
1988-03-04 | 4 | 3 | 0.5 | 2.2 | 35.96 | 12.6785 | 35.96
1988-03-04 | 4 | 3 | 0.54167 | 2.8 | 37.04 | 12.9672 | 37.04
1988-03-04 | 4 | 3 | 0.58333 | 2.8 | 37.04 | 12.9672 | 37.04
1988-03-04 | 4 | 3 | 0.625 | 2.8 | 37.04 | 12.9672 | 37.04
1988-03-04 | 4 | 3 | 0.66667 | 3.3 | 37.94 | 12.8144 | 37.94
1988-03-04 | 4 | 3 | 0.70833 | 3.3 | 37.94 | 12.8144 | 37.94
1988-03-04 | 4 | 3 | 0.75 | 3.3 | 37.94 | 12.3486 | 37.94
1988-03-04 | 4 | 3 | 0.79167 | 3.3 | 37.94 | 12.0383 | 37.94
1988-03-04 | 4 | 3 | 0.83333 | 2.2 | 35.96 | 12.4869 | 35.96
1988-03-04 | 4 | 3 | 0.875 | 2.2 | 35.96 | 12.3433 | 35.96
1988-03-04 | 4 | 3 | 0.91667 | 2.2 | 35.96 | 12.4869 |  | 35.96
1988-03-04 | 4 | 3 | 0.95833 | 2.2 | 35.96 | 12.1519 |  | 35.96
1988-03-04 | 4 | 3 | 1 | 1.7 | 35.06 | 11.8103 |  | 35.06
1988-03-05 | 5 | 3 | 0.041667 | 1.7 | 35.06 | 11.6259 |  | 35.06
1988-03-05 | 5 | 3 | 0.083333 | 1.7 | 35.06 | 11.6259 |  | 35.06
1988-03-05 | 5 | 3 | 0.125 | 1.1 | 33.98 | 11.3616 |  | 33.98
1988-03-05 | 5 | 3 | 0.16667 | 0.6 | 33.08 | 11.158 |  | 33.08
1988-03-05 | 5 | 3 | 0.20833 | 0.6 | 33.08 | 11.158 |  | 33.08
1988-03-05 | 5 | 3 | 0.25 | 0.6 | 33.08 | 11.0304 | 33.08
1988-03-05 | 5 | 3 | 0.29167 | 1.1 | 33.98 | 11.0969 | 33.98
1988-03-05 | 5 | 3 | 0.33333 | 1.7 | 35.06 | 11.4876 | 35.06
1988-03-05 | 5 | 3 | 0.375 | 2.2 | 35.96 | 11.5783 | 35.96
1988-03-05 | 5 | 3 | 0.41667 | 2.8 | 37.04 | 11.8185 | 37.04
1988-03-05 | 5 | 3 | 0.45833 | 3.9 | 39.02 | 12.4263 | 39.02
1988-03-05 | 5 | 3 | 0.5 | 5 | 41 | 12.6257 | 41
1988-03-05 | 5 | 3 | 0.54167 | 5.6 | 42.08 | 13.0663 | 42.08
1988-03-05 | 5 | 3 | 0.58333 | 6.1 | 42.98 | 13.5145 | 42.98
1988-03-05 | 5 | 3 | 0.625 | 6.7 | 44.06 | 13.9768 | 44.06
1988-03-05 | 5 | 3 | 0.66667 | 6.7 | 44.06 | 13.9768 | 44.06
1988-03-05 | 5 | 3 | 0.70833 | 6.1 | 42.98 | 14.0191 | 42.98
1988-03-05 | 5 | 3 | 0.75 | 5.6 | 42.08 | 13.9798 | 42.08
1988-03-05 | 5 | 3 | 0.79167 | 6.1 | 42.98 | 14.3981 | 42.98
1988-03-05 | 5 | 3 | 0.83333 | 6.1 | 42.98 | 14.3981 | 42.98
1988-03-05 | 5 | 3 | 0.875 | 5.6 | 42.08 | 14.1629 | 42.08
1988-03-05 | 5 | 3 | 0.91667 | 4.4 | 39.92 | 13.9859 |  | 39.92
1988-03-05 | 5 | 3 | 0.95833 | 3.9 | 39.02 | 13.9946 |  | 39.02
1988-03-05 | 5 | 3 | 1 | 3.3 | 37.94 | 13.6961 |  | 37.94
1988-03-06 | 6 | 3 | 0.041667 | 3.3 | 37.94 | 13.8519 |  | 37.94
1988-03-06 | 6 | 3 | 0.083333 | 3.3 | 37.94 | 13.8519 |  | 37.94
1988-03-06 | 6 | 3 | 0.125 | 3.3 | 37.94 | 13.8519 |  | 37.94
1988-03-06 | 6 | 3 | 0.16667 | 3.3 | 37.94 | 13.8519 |  | 37.94
1988-03-06 | 6 | 3 | 0.20833 | 3.3 | 37.94 | 13.8519 |  | 37.94
1988-03-06 | 6 | 3 | 0.25 | 3.9 | 39.02 | 14.3743 | 39.02
1988-03-06 | 6 | 3 | 0.29167 | 5 | 41 | 15.2584 | 41
1988-03-06 | 6 | 3 | 0.33333 | 5.6 | 42.08 | 15.5079 | 42.08
1988-03-06 | 6 | 3 | 0.375 | 7.2 | 44.96 | 16.6371 | 44.96
1988-03-06 | 6 | 3 | 0.41667 | 7.8 | 46.04 | 17.146 | 46.04
1988-03-06 | 6 | 3 | 0.45833 | 7.8 | 46.04 | 17.3607 | 46.04
1988-03-06 | 6 | 3 | 0.5 | 10 | 50 | 19.0956 | 50
1988-03-06 | 6 | 3 | 0.54167 | 10.6 | 51.08 | 19.0439 | 51.08
1988-03-06 | 6 | 3 | 0.58333 | 11.7 | 53.06 | 18.8308 | 53.06
1988-03-06 | 6 | 3 | 0.625 | 12.2 | 53.96 | 19.5448 | 53.96
1988-03-06 | 6 | 3 | 0.66667 | 11.1 | 51.98 | 18.7769 | 51.98
1988-03-06 | 6 | 3 | 0.70833 | 12.8 | 55.04 | 19.372 | 55.04
1988-03-06 | 6 | 3 | 0.75 | 9.4 | 48.92 | 17.5919 | 48.92
1988-03-06 | 6 | 3 | 0.79167 | 10 | 50 | 17.8473 | 50
1988-03-06 | 6 | 3 | 0.83333 | 10.6 | 51.08 | 18.3506 | 51.08
1988-03-06 | 6 | 3 | 0.875 | 10 | 50 | 18.0966 | 50
1988-03-06 | 6 | 3 | 0.91667 | 9.4 | 48.92 | 17.5919 |  | 48.92
1988-03-06 | 6 | 3 | 0.95833 | 7.8 | 46.04 | 16.86 |  | 46.04
1988-03-06 | 6 | 3 | 1 | 5 | 41 | 15.0236 |  | 41
1988-03-07 | 7 | 3 | 0.041667 | 5 | 41 | 15.0236 |  | 41
1988-03-07 | 7 | 3 | 0.083333 | 5 | 41 | 15.0236 |  | 41
1988-03-07 | 7 | 3 | 0.125 | 5 | 41 | 15.0236 |  | 41
1988-03-07 | 7 | 3 | 0.16667 | 4.4 | 39.92 | 14.7726 |  | 39.92
1988-03-07 | 7 | 3 | 0.20833 | 4.4 | 39.92 | 14.5477 |  | 39.92
1988-03-07 | 7 | 3 | 0.25 | 3.9 | 39.02 | 14.3743 | 39.02
1988-03-07 | 7 | 3 | 0.29167 | 4.4 | 39.92 | 14.7726 | 39.92
1988-03-07 | 7 | 3 | 0.33333 | 5 | 41 | 14.8476 | 41
1988-03-07 | 7 | 3 | 0.375 | 6.1 | 42.98 | 15.4741 | 42.98
1988-03-07 | 7 | 3 | 0.41667 | 7.8 | 46.04 | 16.4315 | 46.04
1988-03-07 | 7 | 3 | 0.45833 | 11.1 | 51.98 | 18.5978 | 51.98
1988-03-07 | 7 | 3 | 0.5 | 10.6 | 51.08 | 18.8704 | 51.08
1988-03-07 | 7 | 3 | 0.54167 | 10 | 50 | 19.0956 | 50
1988-03-07 | 7 | 3 | 0.58333 | 10 | 50 | 19.6798 | 50
1988-03-07 | 7 | 3 | 0.625 | 10 | 50 | 19.9304 | 50
1988-03-07 | 7 | 3 | 0.66667 | 11.1 | 51.98 | 20.7536 | 51.98
1988-03-07 | 7 | 3 | 0.70833 | 10.6 | 51.08 | 20.1734 | 51.08
1988-03-07 | 7 | 3 | 0.75 | 10.6 | 51.08 | 20.5217 | 51.08
1988-03-07 | 7 | 3 | 0.79167 | 10.6 | 51.08 | 20.8704 | 51.08
1988-03-07 | 7 | 3 | 0.83333 | 10 | 50 | 20.2649 | 50
1988-03-07 | 7 | 3 | 0.875 | 8.9 | 48.02 | 19.1871 | 48.02
1988-03-07 | 7 | 3 | 0.91667 | 8.9 | 48.02 | 19.1871 |  | 48.02
1988-03-07 | 7 | 3 | 0.95833 | 8.9 | 48.02 | 19.1871 |  | 48.02
1988-03-07 | 7 | 3 | 1 | 8.9 | 48.02 | 19.1871 |  | 48.02
1988-03-08 | 8 | 3 | 0.041667 | 9.4 | 48.92 | 19.6719 |  | 48.92
1988-03-08 | 8 | 3 | 0.083333 | 9.4 | 48.92 | 19.6719 |  | 48.92
1988-03-08 | 8 | 3 | 0.125 | 10 | 50 | 19.9304 |  | 50
1988-03-08 | 8 | 3 | 0.16667 | 8.9 | 48.02 | 18.645 |  | 48.02
1988-03-08 | 8 | 3 | 0.20833 | 8.9 | 48.02 | 18.8772 |  | 48.02
1988-03-08 | 8 | 3 | 0.25 | 9.4 | 48.92 | 19.4313 | 48.92
1988-03-08 | 8 | 3 | 0.29167 | 10.6 | 51.08 | 20.1734 | 51.08
1988-03-08 | 8 | 3 | 0.33333 | 11.7 | 53.06 | 20.7 | 53.06
1988-03-08 | 8 | 3 | 0.375 | 12.2 | 53.96 | 21.1894 | 53.96
1988-03-08 | 8 | 3 | 0.41667 | 13.3 | 55.94 | 22.4004 | 55.94
1988-03-08 | 8 | 3 | 0.45833 | 15.6 | 60.08 | 23.7771 | 60.08
1988-03-08 | 8 | 3 | 0.5 | 15.6 | 60.08 | 23.4124 | 60.08
1988-03-08 | 8 | 3 | 0.54167 | 16.1 | 60.98 | 23.9281 | 60.98
1988-03-08 | 8 | 3 | 0.58333 | 15 | 59 | 23.7401 | 59
1988-03-08 | 8 | 3 | 0.625 | 14.4 | 57.92 | 23.8959 | 57.92
1988-03-08 | 8 | 3 | 0.66667 | 14.4 | 57.92 | 23.8959 | 57.92
1988-03-08 | 8 | 3 | 0.70833 | 14.4 | 57.92 | 23.8959 | 57.92
1988-03-08 | 8 | 3 | 0.75 | 13.9 | 57.02 | 23.68 | 57.02
1988-03-08 | 8 | 3 | 0.79167 | 14.4 | 57.92 | 24.2342 | 57.92
1988-03-08 | 8 | 3 | 0.83333 | 6.7 | 44.06 | 16.6838 | 44.06
1988-03-08 | 8 | 3 | 0.875 | 6.1 | 42.98 | 16.1722 | 42.98
1988-03-08 | 8 | 3 | 0.91667 | 5.6 | 42.08 | 15.5079 |  | 42.08
1988-03-08 | 8 | 3 | 0.95833 | 5 | 41 | 15.0236 |  | 41
1988-03-08 | 8 | 3 | 1 | 4.4 | 39.92 | 14.7726 |  | 39.92
1988-03-09 | 9 | 3 | 0.041667 | 2.8 | 37.04 | 13.4679 |  | 37.04
1988-03-09 | 9 | 3 | 0.083333 | 2.8 | 37.04 | 13.3176 |  | 37.04
1988-03-09 | 9 | 3 | 0.125 | 1.1 | 33.98 | 11.3616 |  | 33.98
1988-03-09 | 9 | 3 | 0.16667 | 0 | 32 | 10.4747 |  | 32
1988-03-09 | 9 | 3 | 0.20833 | 0 | 32 | 10.4747 |  | 32
1988-03-09 | 9 | 3 | 0.25 | 0 | 32 | 10.1901 | 32
1988-03-09 | 9 | 3 | 0.29167 | -1.1 | 30.02 | 9.4941 | 30.02
1988-03-09 | 9 | 3 | 0.33333 | -2.2 | 28.04 | 8.816 | 28.04
1988-03-09 | 9 | 3 | 0.375 | -2.2 | 28.04 | 8.7147 | 28.04
1988-03-09 | 9 | 3 | 0.41667 | -1.7 | 28.94 | 8.946 | 28.94
1988-03-09 | 9 | 3 | 0.45833 | -0.6 | 30.92 | 9.422 | 30.92
1988-03-09 | 9 | 3 | 0.5 | -0.6 | 30.92 | 9.422 | 30.92
1988-03-09 | 9 | 3 | 0.54167 | 0 | 32 | 9.784 | 32
1988-03-09 | 9 | 3 | 0.58333 | 0.6 | 33.08 | 9.8413 | 33.08
1988-03-09 | 9 | 3 | 0.625 | 1.1 | 33.98 | 10.1721 | 33.98
1988-03-09 | 9 | 3 | 0.66667 | 0.6 | 33.08 | 9.9261 | 33.08
1988-03-09 | 9 | 3 | 0.70833 | 0.6 | 33.08 | 9.8413 | 33.08
1988-03-09 | 9 | 3 | 0.75 | -0.6 | 30.92 | 9.229 | 30.92
1988-03-09 | 9 | 3 | 0.79167 | -1.7 | 28.94 | 8.6645 | 28.94
1988-03-09 | 9 | 3 | 0.83333 | -2.8 | 26.96 | 8.1005 | 26.96
1988-03-09 | 9 | 3 | 0.875 | -3.3 | 26.06 | 7.7245 | 26.06
1988-03-09 | 9 | 3 | 0.91667 | -3.9 | 24.98 | 7.4792 |  | 24.98
1988-03-09 | 9 | 3 | 0.95833 | -3.9 | 24.98 | 7.5376 |  | 24.98
1988-03-09 | 9 | 3 | 1 | -4.4 | 24.08 | 7.3406 |  | 24.08
1988-03-10 | 10 | 3 | 0.041667 | -4.4 | 24.08 | 7.3406 |  | 24.08
1988-03-10 | 10 | 3 | 0.083333 | -4.4 | 24.08 | 7.3406 |  | 24.08
1988-03-10 | 10 | 3 | 0.125 | -5 | 23 | 6.8435 |  | 23
1988-03-10 | 10 | 3 | 0.16667 | -5 | 23 | 6.7904 |  | 23
1988-03-10 | 10 | 3 | 0.20833 | -5.6 | 21.92 | 6.6684 |  | 21.92
1988-03-10 | 10 | 3 | 0.25 | -5.6 | 21.92 | 6.6684 | 21.92
1988-03-10 | 10 | 3 | 0.29167 | -5 | 23 | 6.7904 | 23
1988-03-10 | 10 | 3 | 0.33333 | -5 | 23 | 6.7374 | 23
1988-03-10 | 10 | 3 | 0.375 | -3.9 | 24.98 | 7.1586 | 24.98
1988-03-10 | 10 | 3 | 0.41667 | -2.2 | 28.04 | 7.8048 | 28.04
1988-03-10 | 10 | 3 | 0.45833 | -1.1 | 30.02 | 8.1998 | 30.02
1988-03-10 | 10 | 3 | 0.5 | 0 | 32 | 8.7304 | 32
1988-03-10 | 10 | 3 | 0.54167 | 1.1 | 33.98 | 9.0745 | 33.98
1988-03-10 | 10 | 3 | 0.58333 | 1.7 | 35.06 | 9.4662 | 35.06
1988-03-10 | 10 | 3 | 0.625 | 2.8 | 37.04 | 9.9292 | 37.04
1988-03-10 | 10 | 3 | 0.66667 | 3.3 | 37.94 | 10.3373 | 37.94
1988-03-10 | 10 | 3 | 0.70833 | 3.3 | 37.94 | 10.1831 | 37.94
1988-03-10 | 10 | 3 | 0.75 | 2.8 | 37.04 | 9.9787 | 37.04
1988-03-10 | 10 | 3 | 0.79167 | 2.2 | 35.96 | 9.8635 | 35.96
1988-03-10 | 10 | 3 | 0.83333 | 1.7 | 35.06 | 9.6953 | 35.06
1988-03-10 | 10 | 3 | 0.875 | 1.7 | 35.06 | 9.512 | 35.06
1988-03-10 | 10 | 3 | 0.91667 | 1.1 | 33.98 | 9.206 |  | 33.98
1988-03-10 | 10 | 3 | 0.95833 | 1.1 | 33.98 | 9.3814 |  | 33.98
1988-03-10 | 10 | 3 | 1 | 1.1 | 33.98 | 9.1621 |  | 33.98
1988-03-11 | 11 | 3 | 0.041667 | 1.1 | 33.98 | 9.1621 |  | 33.98
1988-03-11 | 11 | 3 | 0.083333 | 0.6 | 33.08 | 8.9101 |  | 33.08
1988-03-11 | 11 | 3 | 0.125 | 0.6 | 33.08 | 8.9101 |  | 33.08
1988-03-11 | 11 | 3 | 0.16667 | 0 | 32 | 8.7708 |  | 32
1988-03-11 | 11 | 3 | 0.20833 | 0 | 32 | 8.6494 |  | 32
1988-03-11 | 11 | 3 | 0.25 | 0 | 32 | 8.7708 | 32
1988-03-11 | 11 | 3 | 0.29167 | 0.6 | 33.08 | 8.9101 | 33.08
1988-03-11 | 11 | 3 | 0.33333 | 1.1 | 33.98 | 9.206 | 33.98
1988-03-11 | 11 | 3 | 0.375 | 1.7 | 35.06 | 9.6037 | 35.06
1988-03-11 | 11 | 3 | 0.41667 | 2.8 | 37.04 | 10.2268 | 37.04
1988-03-11 | 11 | 3 | 0.45833 | 3.9 | 39.02 | 10.8652 | 39.02
1988-03-11 | 11 | 3 | 0.5 | 4.4 | 39.92 | 11.1912 | 39.92
1988-03-11 | 11 | 3 | 0.54167 | 5 | 41 | 11.4622 | 41
1988-03-11 | 11 | 3 | 0.58333 | 6.1 | 42.98 | 12.3191 | 42.98
1988-03-11 | 11 | 3 | 0.625 | 6.7 | 44.06 | 12.5986 | 44.06
1988-03-11 | 11 | 3 | 0.66667 | 5.6 | 42.08 | 12.2159 | 42.08
1988-03-11 | 11 | 3 | 0.70833 | 5 | 41 | 11.9271 | 41
1988-03-11 | 11 | 3 | 0.75 | 4.4 | 39.92 | 11.581 | 39.92
1988-03-11 | 11 | 3 | 0.79167 | 3.9 | 39.02 | 11.7794 | 39.02
1988-03-11 | 11 | 3 | 0.83333 | 3.9 | 39.02 | 11.7794 | 39.02
1988-03-11 | 11 | 3 | 0.875 | 3.9 | 39.02 | 11.8872 | 39.02
1988-03-11 | 11 | 3 | 0.91667 | 3.9 | 39.02 | 12.0488 |  | 39.02
1988-03-11 | 11 | 3 | 0.95833 | 3.3 | 37.94 | 12.3486 |  | 37.94
1988-03-11 | 11 | 3 | 1 | 2.8 | 37.04 | 12.4173 |  | 37.04
1988-03-12 | 12 | 3 | 0.041667 | 2.8 | 37.04 | 12.4173 |  | 37.04
1988-03-12 | 12 | 3 | 0.083333 | 2.8 | 37.04 | 12.4173 |  | 37.04
1988-03-12 | 12 | 3 | 0.125 | 2.2 | 35.96 | 12.1519 |  | 35.96
1988-03-12 | 12 | 3 | 0.16667 | 2.2 | 35.96 | 12.4869 |  | 35.96
1988-03-12 | 12 | 3 | 0.20833 | 2.2 | 35.96 | 12.4869 |  | 35.96
1988-03-12 | 12 | 3 | 0.25 | 1.7 | 35.06 | 12.1334 | 35.06
1988-03-12 | 12 | 3 | 0.29167 | 1.7 | 35.06 | 12.1334 | 35.06
1988-03-12 | 12 | 3 | 0.33333 | 3.3 | 37.94 | 12.9698 | 37.94
1988-03-12 | 12 | 3 | 0.375 | 4.4 | 39.92 | 13.6493 | 39.92
1988-03-12 | 12 | 3 | 0.41667 | 5.6 | 42.08 | 14.1629 | 42.08
1988-03-12 | 12 | 3 | 0.45833 | 8.3 | 46.94 | 15.3622 | 46.94
1988-03-12 | 12 | 3 | 0.5 | 9.4 | 48.92 | 16.1593 | 48.92
1988-03-12 | 12 | 3 | 0.54167 | 7.2 | 44.96 | 15.2001 | 44.96
1988-03-12 | 12 | 3 | 0.58333 | 6.7 | 44.06 | 14.9646 | 44.06
1988-03-12 | 12 | 3 | 0.625 | 6.7 | 44.06 | 14.9646 | 44.06
1988-03-12 | 12 | 3 | 0.66667 | 5.6 | 42.08 | 13.6141 | 42.08
1988-03-12 | 12 | 3 | 0.70833 | 5.6 | 42.08 | 14.5292 | 42.08
1988-03-12 | 12 | 3 | 0.75 | 5 | 41 | 14.613 | 41
1988-03-12 | 12 | 3 | 0.79167 | 5.6 | 42.08 | 14.8959 | 42.08
1988-03-12 | 12 | 3 | 0.83333 | 5 | 41 | 14.613 | 41
1988-03-12 | 12 | 3 | 0.875 | 4.4 | 39.92 | 14.379 | 39.92
1988-03-12 | 12 | 3 | 0.91667 | 4.4 | 39.92 | 14.5477 |  | 39.92
1988-03-12 | 12 | 3 | 0.95833 | 3.9 | 39.02 | 14.1573 |  | 39.02
1988-03-12 | 12 | 3 | 1 | 3.9 | 39.02 | 14.1573 |  | 39.02
1988-03-13 | 13 | 3 | 0.041667 | 3.9 | 39.02 | 14.1573 |  | 39.02
1988-03-13 | 13 | 3 | 0.083333 | 3.3 | 37.94 | 13.6961 |  | 37.94
1988-03-13 | 13 | 3 | 0.125 | 3.3 | 37.94 | 13.6961 |  | 37.94
1988-03-13 | 13 | 3 | 0.16667 | 3.3 | 37.94 | 13.6961 |  | 37.94
1988-03-13 | 13 | 3 | 0.20833 | 3.3 | 37.94 | 13.6961 |  | 37.94
1988-03-13 | 13 | 3 | 0.25 | 3.9 | 39.02 | 13.7779 | 39.02
1988-03-13 | 13 | 3 | 0.29167 | 3.9 | 39.02 | 13.9946 | 39.02
1988-03-13 | 13 | 3 | 0.33333 | 5 | 41 | 14.4372 | 41
1988-03-13 | 13 | 3 | 0.375 | 7.2 | 44.96 | 16.2259 | 44.96
1988-03-13 | 13 | 3 | 0.41667 | 8.9 | 48.02 | 17.1011 | 48.02
1988-03-13 | 13 | 3 | 0.45833 | 12.2 | 53.96 | 18.5811 | 53.96
1988-03-13 | 13 | 3 | 0.5 | 15.6 | 60.08 | 20.0271 | 60.08
1988-03-13 | 13 | 3 | 0.54167 | 17.2 | 62.96 | 20.5321 | 62.96
1988-03-13 | 13 | 3 | 0.58333 | 19.4 | 66.92 | 21.6888 | 66.92
1988-03-13 | 13 | 3 | 0.625 | 21.7 | 71.06 | 22.1424 | 71.06
1988-03-13 | 13 | 3 | 0.66667 | 22.2 | 71.96 | 22.7016 | 71.96
1988-03-13 | 13 | 3 | 0.70833 | 21.7 | 71.06 | 22.4961 | 71.06
1988-03-13 | 13 | 3 | 0.75 | 20 | 68 | 21.5291 | 68
1988-03-13 | 13 | 3 | 0.79167 | 17.8 | 64.04 | 20.1744 | 64.04
1988-03-13 | 13 | 3 | 0.83333 | 15.6 | 60.08 | 19.4261 | 60.08
1988-03-13 | 13 | 3 | 0.875 | 14.4 | 57.92 | 18.7506 | 57.92
1988-03-13 | 13 | 3 | 0.91667 | 15.6 | 60.08 | 19.186 |  | 60.08
1988-03-13 | 13 | 3 | 0.95833 | 10.6 | 51.08 | 17.6587 |  | 51.08
1988-03-13 | 13 | 3 | 1 | 9.4 | 48.92 | 17.3527 |  | 48.92
1988-03-14 | 14 | 3 | 0.041667 | 10 | 50 | 17.4322 |  | 50
1988-03-14 | 14 | 3 | 0.083333 | 9.4 | 48.92 | 16.9545 |  | 48.92
1988-03-14 | 14 | 3 | 0.125 | 8.3 | 46.94 | 16.6895 |  | 46.94
1988-03-14 | 14 | 3 | 0.16667 | 6.7 | 44.06 | 15.9554 |  | 44.06
1988-03-14 | 14 | 3 | 0.20833 | 6.1 | 42.98 | 15.4741 |  | 42.98
1988-03-14 | 14 | 3 | 0.25 | 5.6 | 42.08 | 15.5079 | 42.08
1988-03-14 | 14 | 3 | 0.29167 | 6.1 | 42.98 | 15.7278 | 42.98
1988-03-14 | 14 | 3 | 0.33333 | 7.8 | 46.04 | 16.4315 | 46.04
1988-03-14 | 14 | 3 | 0.375 | 8.3 | 46.94 | 16.6895 | 46.94
1988-03-14 | 14 | 3 | 0.41667 | 8.9 | 48.02 | 16.7162 | 48.02
1988-03-14 | 14 | 3 | 0.45833 | 10 | 50 | 17.1834 | 50
1988-03-14 | 14 | 3 | 0.5 | 11.7 | 53.06 | 16.1385 | 53.06
1988-03-14 | 14 | 3 | 0.54167 | 13.3 | 55.94 | 18.6579 | 55.94
1988-03-14 | 14 | 3 | 0.58333 | 15 | 59 | 20.2463 | 59
1988-03-14 | 14 | 3 | 0.625 | 12.2 | 53.96 | 18.5811 | 53.96
1988-03-14 | 14 | 3 | 0.66667 | 10.6 | 51.08 | 17.8316 | 51.08
1988-03-14 | 14 | 3 | 0.70833 | 9.4 | 48.92 | 17.3527 | 48.92
1988-03-14 | 14 | 3 | 0.75 | 7.2 | 44.96 | 16.3629 | 44.96
1988-03-14 | 14 | 3 | 0.79167 | 7.2 | 44.96 | 16.6371 | 44.96
1988-03-14 | 14 | 3 | 0.83333 | 7.2 | 44.96 | 16.6371 | 44.96
1988-03-14 | 14 | 3 | 0.875 | 6.7 | 44.06 | 16.1539 | 44.06
1988-03-14 | 14 | 3 | 0.91667 | 6.7 | 44.06 | 16.1539 |  | 44.06
1988-03-14 | 14 | 3 | 0.95833 | 6.7 | 44.06 | 16.1539 |  | 44.06
1988-03-14 | 14 | 3 | 1 | 7.2 | 44.96 | 16.6371 |  | 44.96
1988-03-15 | 15 | 3 | 0.041667 | 7.2 | 44.96 | 16.3629 |  | 44.96
1988-03-15 | 15 | 3 | 0.083333 | 6.7 | 44.06 | 16.1539 |  | 44.06
1988-03-15 | 15 | 3 | 0.125 | 7.2 | 44.96 | 16.3629 |  | 44.96
1988-03-15 | 15 | 3 | 0.16667 | 7.2 | 44.96 | 16.6371 |  | 44.96
1988-03-15 | 15 | 3 | 0.20833 | 7.2 | 44.96 | 17.1175 |  | 44.96
1988-03-15 | 15 | 3 | 0.25 | 7.2 | 44.96 | 17.1175 | 44.96
1988-03-15 | 15 | 3 | 0.29167 | 7.2 | 44.96 | 17.1175 | 44.96
1988-03-15 | 15 | 3 | 0.33333 | 7.8 | 46.04 | 17.3607 | 46.04
1988-03-15 | 15 | 3 | 0.375 | 8.9 | 48.02 | 17.6407 | 48.02
1988-03-15 | 15 | 3 | 0.41667 | 11.1 | 51.98 | 18.7769 | 51.98
1988-03-15 | 15 | 3 | 0.45833 | 11.7 | 53.06 | 19.0172 | 53.06
1988-03-15 | 15 | 3 | 0.5 | 15 | 59 | 20.4781 | 59
1988-03-15 | 15 | 3 | 0.54167 | 18.9 | 66.02 | 22.189 | 66.02
1988-03-15 | 15 | 3 | 0.58333 | 21.1 | 69.98 | 23.2314 | 69.98
1988-03-15 | 15 | 3 | 0.625 | 20.6 | 69.08 | 22.982 | 69.08
1988-03-15 | 15 | 3 | 0.66667 | 20 | 68 | 22.6444 | 68
1988-03-15 | 15 | 3 | 0.70833 | 17.8 | 64.04 | 23.0902 | 64.04
1988-03-15 | 15 | 3 | 0.75 | 13.3 | 55.94 | 19.7971 | 55.94
1988-03-15 | 15 | 3 | 0.79167 | 12.2 | 53.96 | 19.0626 | 53.96
1988-03-15 | 15 | 3 | 0.83333 | 11.7 | 53.06 | 19.0172 | 53.06
1988-03-15 | 15 | 3 | 0.875 | 11.1 | 51.98 | 18.5978 | 51.98
1988-03-15 | 15 | 3 | 0.91667 | 10 | 50 | 18.0966 |  | 50
1988-03-15 | 15 | 3 | 0.95833 | 10 | 50 | 18.0966 |  | 50
1988-03-15 | 15 | 3 | 1 | 7.8 | 46.04 | 16.86 |  | 46.04
1988-03-16 | 16 | 3 | 0.041667 | 7.8 | 46.04 | 16.86 |  | 46.04
1988-03-16 | 16 | 3 | 0.083333 | 7.2 | 44.96 | 16.6371 |  | 44.96
1988-03-16 | 16 | 3 | 0.125 | 6.7 | 44.06 | 16.4187 |  | 44.06
1988-03-16 | 16 | 3 | 0.16667 | 6.1 | 42.98 | 15.9182 |  | 42.98
1988-03-16 | 16 | 3 | 0.20833 | 6.1 | 42.98 | 16.1722 |  | 42.98
1988-03-16 | 16 | 3 | 0.25 | 5.6 | 42.08 | 15.6918 | 42.08
1988-03-16 | 16 | 3 | 0.29167 | 5.6 | 42.08 | 15.6918 | 42.08
1988-03-16 | 16 | 3 | 0.33333 | 7.2 | 44.96 | 16.6371 | 44.96
1988-03-16 | 16 | 3 | 0.375 | 8.9 | 48.02 | 18.1039 | 48.02
1988-03-16 | 16 | 3 | 0.41667 | 10.6 | 51.08 | 18.8704 | 51.08
1988-03-16 | 16 | 3 | 0.45833 | 15.6 | 60.08 | 20.9909 | 60.08
1988-03-16 | 16 | 3 | 0.5 | 15 | 59 | 21.0583 | 59
1988-03-16 | 16 | 3 | 0.54167 | 13.9 | 57.02 | 20.5316 | 57.02
1988-03-16 | 16 | 3 | 0.58333 | 13.3 | 55.94 | 20.524 | 55.94
1988-03-16 | 16 | 3 | 0.625 | 12.2 | 53.96 | 19.7379 | 53.96
1988-03-16 | 16 | 3 | 0.66667 | 12.2 | 53.96 | 19.7379 | 53.96
1988-03-16 | 16 | 3 | 0.70833 | 11.1 | 51.98 | 19.3149 | 51.98
1988-03-16 | 16 | 3 | 0.75 | 11.1 | 51.98 | 19.3149 | 51.98
1988-03-16 | 16 | 3 | 0.79167 | 11.1 | 51.98 | 19.3149 | 51.98
1988-03-16 | 16 | 3 | 0.83333 | 10.6 | 51.08 | 19.0439 | 51.08
1988-03-16 | 16 | 3 | 0.875 | 10.6 | 51.08 | 19.391 | 51.08
1988-03-16 | 16 | 3 | 0.91667 | 10.6 | 51.08 | 19.6516 |  | 51.08
1988-03-16 | 16 | 3 | 0.95833 | 8.3 | 46.94 | 18.0963 |  | 46.94
1988-03-16 | 16 | 3 | 1 | 6.7 | 44.06 | 16.8827 |  | 44.06
1988-03-17 | 17 | 3 | 0.041667 | 7.8 | 46.04 | 17.8621 |  | 46.04
1988-03-17 | 17 | 3 | 0.083333 | 7.8 | 46.04 | 17.6471 |  | 46.04
1988-03-17 | 17 | 3 | 0.125 | 7.2 | 44.96 | 17.3923 |  | 44.96
1988-03-17 | 17 | 3 | 0.16667 | 6.7 | 44.06 | 16.8827 |  | 44.06
1988-03-17 | 17 | 3 | 0.20833 | 6.7 | 44.06 | 17.1481 |  | 44.06
1988-03-17 | 17 | 3 | 0.25 | 6.7 | 44.06 | 17.1481 | 44.06
1988-03-17 | 17 | 3 | 0.29167 | 6.7 | 44.06 | 17.1481 | 44.06
1988-03-17 | 17 | 3 | 0.33333 | 7.2 | 44.96 | 17.3923 | 44.96
1988-03-17 | 17 | 3 | 0.375 | 7.2 | 44.96 | 17.5986 | 44.96
1988-03-17 | 17 | 3 | 0.41667 | 7.8 | 46.04 | 18.1489 | 46.04
1988-03-17 | 17 | 3 | 0.45833 | 8.9 | 48.02 | 19.1871 | 48.02
1988-03-17 | 17 | 3 | 0.5 | 10.6 | 51.08 | 19.6516 | 51.08
1988-03-17 | 17 | 3 | 0.54167 | 13.3 | 55.94 | 21.1483 | 55.94
1988-03-17 | 17 | 3 | 0.58333 | 15 | 59 | 21.8723 | 59
1988-03-17 | 17 | 3 | 0.625 | 13.3 | 55.94 | 20.836 | 55.94
1988-03-17 | 17 | 3 | 0.66667 | 12.8 | 55.04 | 20.5777 | 55.04
1988-03-17 | 17 | 3 | 0.70833 | 12.2 | 53.96 | 20.608 | 53.96
1988-03-17 | 17 | 3 | 0.75 | 12.8 | 55.04 | 20.8798 | 55.04
1988-03-17 | 17 | 3 | 0.79167 | 10.6 | 51.08 | 19.391 | 51.08
1988-03-17 | 17 | 3 | 0.83333 | 12.2 | 53.96 | 18.7737 | 53.96
1988-03-17 | 17 | 3 | 0.875 | 10.6 | 51.08 | 16.3653 | 51.08
1988-03-17 | 17 | 3 | 0.91667 | 9.4 | 48.92 | 15.8418 |  | 48.92
1988-03-17 | 17 | 3 | 0.95833 | 8.3 | 46.94 | 15.3622 |  | 46.94
1988-03-17 | 17 | 3 | 1 | 6.7 | 44.06 | 14.4374 |  | 44.06
1988-03-18 | 18 | 3 | 0.041667 | 6.1 | 42.98 | 14.2086 |  | 42.98
1988-03-18 | 18 | 3 | 0.083333 | 5.6 | 42.08 | 13.7969 |  | 42.08
1988-03-18 | 18 | 3 | 0.125 | 5.6 | 42.08 | 13.7969 |  | 42.08
1988-03-18 | 18 | 3 | 0.16667 | 5.6 | 42.08 | 13.7969 |  | 42.08
1988-03-18 | 18 | 3 | 0.20833 | 5 | 41 | 13.3842 |  | 41
1988-03-18 | 18 | 3 | 0.25 | 5 | 41 | 13.209 | 41
1988-03-18 | 18 | 3 | 0.29167 | 5 | 41 | 13.209 | 41
1988-03-18 | 18 | 3 | 0.33333 | 6.1 | 42.98 | 13.7037 | 42.98
1988-03-18 | 18 | 3 | 0.375 | 7.2 | 44.96 | 14.5179 | 44.96
1988-03-18 | 18 | 3 | 0.41667 | 8.3 | 46.94 | 14.9944 | 46.94
1988-03-18 | 18 | 3 | 0.45833 | 9.4 | 48.92 | 15.6038 | 48.92
1988-03-18 | 18 | 3 | 0.5 | 10.6 | 51.08 | 16.3653 | 51.08
1988-03-18 | 18 | 3 | 0.54167 | 11.7 | 53.06 | 16.9718 | 53.06
1988-03-18 | 18 | 3 | 0.58333 | 12.8 | 55.04 | 17.6711 | 55.04
1988-03-18 | 18 | 3 | 0.625 | 12.8 | 55.04 | 17.4716 | 55.04
1988-03-18 | 18 | 3 | 0.66667 | 12.8 | 55.04 | 17.4716 | 55.04
1988-03-18 | 18 | 3 | 0.70833 | 12.8 | 55.04 | 17.4716 | 55.04
1988-03-18 | 18 | 3 | 0.75 | 12.2 | 53.96 | 17.0449 | 53.96
1988-03-18 | 18 | 3 | 0.79167 | 10.6 | 51.08 | 16.7097 | 51.08
1988-03-18 | 18 | 3 | 0.83333 | 10 | 50 | 16.438 | 50
1988-03-18 | 18 | 3 | 0.875 | 8.9 | 48.02 | 16.1781 | 48.02
1988-03-18 | 18 | 3 | 0.91667 | 8.9 | 48.02 | 15.9478 |  | 48.02
1988-03-18 | 18 | 3 | 0.95833 | 8.9 | 48.02 | 15.7943 |  | 48.02
1988-03-18 | 18 | 3 | 1 | 8.3 | 46.94 | 15.6567 |  | 46.94
1988-03-19 | 19 | 3 | 0.041667 | 7.8 | 46.04 | 15.2913 |  | 46.04
1988-03-19 | 19 | 3 | 0.083333 | 7.2 | 44.96 | 15.2001 |  | 44.96
1988-03-19 | 19 | 3 | 0.125 | 6.1 | 42.98 | 14.5877 |  | 42.98
1988-03-19 | 19 | 3 | 0.16667 | 5.6 | 42.08 | 14.346 |  | 42.08
1988-03-19 | 19 | 3 | 0.20833 | 6.1 | 42.98 | 14.3981 |  | 42.98
1988-03-19 | 19 | 3 | 0.25 | 5 | 41 | 13.9103 | 41
1988-03-19 | 19 | 3 | 0.29167 | 5.6 | 42.08 | 14.346 | 42.08
1988-03-19 | 19 | 3 | 0.33333 | 6.1 | 42.98 | 14.5877 | 42.98
1988-03-19 | 19 | 3 | 0.375 | 7.2 | 44.96 | 14.8588 | 44.96
1988-03-19 | 19 | 3 | 0.41667 | 8.3 | 46.94 | 15.5094 | 46.94
1988-03-19 | 19 | 3 | 0.45833 | 8.3 | 46.94 | 15.5094 | 46.94
1988-03-19 | 19 | 3 | 0.5 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-19 | 19 | 3 | 0.54167 | 9.4 | 48.92 | 15.8418 | 48.92
1988-03-19 | 19 | 3 | 0.58333 | 9.4 | 48.92 | 16.0005 | 48.92
1988-03-19 | 19 | 3 | 0.625 | 10 | 50 | 16.2726 | 50
1988-03-19 | 19 | 3 | 0.66667 | 9.4 | 48.92 | 15.4453 | 48.92
1988-03-19 | 19 | 3 | 0.70833 | 8.3 | 46.94 | 14.7739 | 46.94
1988-03-19 | 19 | 3 | 0.75 | 7.2 | 44.96 | 14.8588 | 44.96
1988-03-19 | 19 | 3 | 0.79167 | 6.1 | 42.98 | 14.5877 | 42.98
1988-03-19 | 19 | 3 | 0.83333 | 6.1 | 42.98 | 14.7142 | 42.98
1988-03-19 | 19 | 3 | 0.875 | 5.6 | 42.08 | 14.5292 | 42.08
1988-03-19 | 19 | 3 | 0.91667 | 6.1 | 42.98 | 14.7142 |  | 42.98
1988-03-19 | 19 | 3 | 0.95833 | 6.1 | 42.98 | 14.7142 |  | 42.98
1988-03-19 | 19 | 3 | 1 | 5.6 | 42.08 | 14.5292 |  | 42.08
1988-03-20 | 20 | 3 | 0.041667 | 5.6 | 42.08 | 14.5292 |  | 42.08
1988-03-20 | 20 | 3 | 0.083333 | 5 | 41 | 14.2614 |  | 41
1988-03-20 | 20 | 3 | 0.125 | 5 | 41 | 14.2614 |  | 41
1988-03-20 | 20 | 3 | 0.16667 | 4.4 | 39.92 | 14.2105 |  | 39.92
1988-03-20 | 20 | 3 | 0.20833 | 5 | 41 | 14.4372 |  | 41
1988-03-20 | 20 | 3 | 0.25 | 5.6 | 42.08 | 14.8959 | 42.08
1988-03-20 | 20 | 3 | 0.29167 | 5.6 | 42.08 | 14.8959 | 42.08
1988-03-20 | 20 | 3 | 0.33333 | 7.2 | 44.96 | 15.8152 | 44.96
1988-03-20 | 20 | 3 | 0.375 | 8.3 | 46.94 | 16.2465 | 46.94
1988-03-20 | 20 | 3 | 0.41667 | 10 | 50 | 16.7691 | 50
1988-03-20 | 20 | 3 | 0.45833 | 10 | 50 | 16.7691 | 50
1988-03-20 | 20 | 3 | 0.5 | 10.6 | 51.08 | 17.227 | 51.08
1988-03-20 | 20 | 3 | 0.54167 | 11.1 | 51.98 | 17.525 | 51.98
1988-03-20 | 20 | 3 | 0.58333 | 11.1 | 51.98 | 17.525 | 51.98
1988-03-20 | 20 | 3 | 0.625 | 11.1 | 51.98 | 17.525 | 51.98
1988-03-20 | 20 | 3 | 0.66667 | 11.7 | 53.06 | 18.179 | 53.06
1988-03-20 | 20 | 3 | 0.70833 | 10.6 | 51.08 | 17.8316 | 51.08
1988-03-20 | 20 | 3 | 0.75 | 10 | 50 | 17.8473 | 50
1988-03-20 | 20 | 3 | 0.79167 | 9.4 | 48.92 | 17.8313 | 48.92
1988-03-20 | 20 | 3 | 0.83333 | 9.4 | 48.92 | 18.0708 | 48.92
1988-03-20 | 20 | 3 | 0.875 | 9.4 | 48.92 | 18.3105 | 48.92
1988-03-20 | 20 | 3 | 0.91667 | 9.4 | 48.92 | 18.3105 |  | 48.92
1988-03-20 | 20 | 3 | 0.95833 | 10 | 50 | 18.8456 |  | 50
1988-03-20 | 20 | 3 | 1 | 10 | 50 | 18.8456 |  | 50
1988-03-21 | 21 | 3 | 0.041667 | 9.4 | 48.92 | 18.8704 |  | 48.92
1988-03-21 | 21 | 3 | 0.083333 | 9.4 | 48.92 | 19.1107 |  | 48.92
1988-03-21 | 21 | 3 | 0.125 | 9.4 | 48.92 | 19.1107 |  | 48.92
1988-03-21 | 21 | 3 | 0.16667 | 8.9 | 48.02 | 18.8772 |  | 48.02
1988-03-21 | 21 | 3 | 0.20833 | 9.4 | 48.92 | 19.4313 |  | 48.92
1988-03-21 | 21 | 3 | 0.25 | 9.4 | 48.92 | 19.1107 | 48.92
1988-03-21 | 21 | 3 | 0.29167 | 9.4 | 48.92 | 18.5503 | 48.92
1988-03-21 | 21 | 3 | 0.33333 | 10.6 | 51.08 | 19.0439 | 51.08
1988-03-21 | 21 | 3 | 0.375 | 10 | 50 | 18.8456 | 50
1988-03-21 | 21 | 3 | 0.41667 | 10 | 50 | 19.3458 | 50
1988-03-21 | 21 | 3 | 0.45833 | 10 | 50 | 19.9304 | 50
1988-03-21 | 21 | 3 | 0.5 | 10.6 | 51.08 | 20.5217 | 51.08
1988-03-21 | 21 | 3 | 0.54167 | 11.1 | 51.98 | 19.8537 | 51.98
1988-03-21 | 21 | 3 | 0.58333 | 13.3 | 55.94 | 21.1483 | 55.94
1988-03-21 | 21 | 3 | 0.625 | 15.6 | 60.08 | 21.8365 | 60.08
1988-03-21 | 21 | 3 | 0.66667 | 14.4 | 57.92 | 20.5315 | 57.92
1988-03-21 | 21 | 3 | 0.70833 | 14.4 | 57.92 | 19.974 | 57.92
1988-03-21 | 21 | 3 | 0.75 | 14.4 | 57.92 | 19.5286 | 57.92
1988-03-21 | 21 | 3 | 0.79167 | 13.9 | 57.02 | 19.1297 | 57.02
1988-03-21 | 21 | 3 | 0.83333 | 12.8 | 55.04 | 18.2705 | 55.04
1988-03-21 | 21 | 3 | 0.875 | 11.7 | 53.06 | 17.7141 | 53.06
1988-03-21 | 21 | 3 | 0.91667 | 10.6 | 51.08 | 17.0545 |  | 51.08
1988-03-21 | 21 | 3 | 0.95833 | 10 | 50 | 16.6035 |  | 50
1988-03-21 | 21 | 3 | 1 | 10 | 50 | 16.438 |  | 50
1988-03-22 | 22 | 3 | 0.041667 | 10 | 50 | 16.438 |  | 50
1988-03-22 | 22 | 3 | 0.083333 | 9.4 | 48.92 | 16.0005 |  | 48.92
1988-03-22 | 22 | 3 | 0.125 | 8.9 | 48.02 | 15.7943 |  | 48.02
1988-03-22 | 22 | 3 | 0.16667 | 8.9 | 48.02 | 15.7943 |  | 48.02
1988-03-22 | 22 | 3 | 0.20833 | 8.3 | 46.94 | 15.5094 |  | 46.94
1988-03-22 | 22 | 3 | 0.25 | 8.3 | 46.94 | 15.5094 | 46.94
1988-03-22 | 22 | 3 | 0.29167 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-22 | 22 | 3 | 0.33333 | 8.9 | 48.02 | 16.5624 | 48.02
1988-03-22 | 22 | 3 | 0.375 | 8.9 | 48.02 | 16.5624 | 48.02
1988-03-22 | 22 | 3 | 0.41667 | 8.9 | 48.02 | 15.9478 | 48.02
1988-03-22 | 22 | 3 | 0.45833 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-22 | 22 | 3 | 0.5 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-22 | 22 | 3 | 0.54167 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-22 | 22 | 3 | 0.58333 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-22 | 22 | 3 | 0.625 | 10 | 50 | 15.8594 | 50
1988-03-22 | 22 | 3 | 0.66667 | 10 | 50 | 15.8594 | 50
1988-03-22 | 22 | 3 | 0.70833 | 8.3 | 46.94 | 15.8777 | 46.94
1988-03-22 | 22 | 3 | 0.75 | 8.3 | 46.94 | 15.8777 | 46.94
1988-03-22 | 22 | 3 | 0.79167 | 7.8 | 46.04 | 15.5048 | 46.04
1988-03-22 | 22 | 3 | 0.83333 | 7.8 | 46.04 | 15.5048 | 46.04
1988-03-22 | 22 | 3 | 0.875 | 7.8 | 46.04 | 15.6472 | 46.04
1988-03-22 | 22 | 3 | 0.91667 | 7.2 | 44.96 | 15.0635 |  | 44.96
1988-03-22 | 22 | 3 | 0.95833 | 6.7 | 44.06 | 14.635 |  | 44.06
1988-03-22 | 22 | 3 | 1 | 6.7 | 44.06 | 14.4374 |  | 44.06
1988-03-23 | 23 | 3 | 0.041667 | 6.7 | 44.06 | 14.4374 |  | 44.06
1988-03-23 | 23 | 3 | 0.083333 | 7.2 | 44.96 | 14.8588 |  | 44.96
1988-03-23 | 23 | 3 | 0.125 | 6.7 | 44.06 | 14.635 |  | 44.06
1988-03-23 | 23 | 3 | 0.16667 | 6.7 | 44.06 | 14.635 |  | 44.06
1988-03-23 | 23 | 3 | 0.20833 | 6.7 | 44.06 | 14.635 |  | 44.06
1988-03-23 | 23 | 3 | 0.25 | 6.7 | 44.06 | 14.635 | 44.06
1988-03-23 | 23 | 3 | 0.29167 | 6.7 | 44.06 | 14.8327 | 44.06
1988-03-23 | 23 | 3 | 0.33333 | 7.2 | 44.96 | 14.8588 | 44.96
1988-03-23 | 23 | 3 | 0.375 | 8.3 | 46.94 | 15.5094 | 46.94
1988-03-23 | 23 | 3 | 0.41667 | 8.9 | 48.02 | 15.9478 | 48.02
1988-03-23 | 23 | 3 | 0.45833 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-23 | 23 | 3 | 0.5 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-23 | 23 | 3 | 0.54167 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-23 | 23 | 3 | 0.58333 | 9.4 | 48.92 | 16.0005 | 48.92
1988-03-23 | 23 | 3 | 0.625 | 9.4 | 48.92 | 16.0005 | 48.92
1988-03-23 | 23 | 3 | 0.66667 | 9.4 | 48.92 | 16.0005 | 48.92
1988-03-23 | 23 | 3 | 0.70833 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-23 | 23 | 3 | 0.75 | 8.9 | 48.02 | 15.7943 | 48.02
1988-03-23 | 23 | 3 | 0.79167 | 8.3 | 46.94 | 15.3622 | 46.94
1988-03-23 | 23 | 3 | 0.83333 | 8.3 | 46.94 | 15.3622 | 46.94
1988-03-23 | 23 | 3 | 0.875 | 7.8 | 46.04 | 15.2913 | 46.04
1988-03-23 | 23 | 3 | 0.91667 | 7.2 | 44.96 | 15.0635 |  | 44.96
1988-03-23 | 23 | 3 | 0.95833 | 7.2 | 44.96 | 14.8588 |  | 44.96
1988-03-23 | 23 | 3 | 1 | 7.2 | 44.96 | 14.8588 |  | 44.96
1988-03-24 | 24 | 3 | 0.041667 | 6.7 | 44.06 | 14.635 |  | 44.06
1988-03-24 | 24 | 3 | 0.083333 | 6.7 | 44.06 | 14.635 |  | 44.06
1988-03-24 | 24 | 3 | 0.125 | 5.6 | 42.08 | 14.5292 |  | 42.08
1988-03-24 | 24 | 3 | 0.16667 | 5 | 41 | 13.7348 |  | 41
1988-03-24 | 24 | 3 | 0.20833 | 5 | 41 | 13.5595 |  | 41
1988-03-24 | 24 | 3 | 0.25 | 4.4 | 39.92 | 13.3131 | 39.92
1988-03-24 | 24 | 3 | 0.29167 | 4.4 | 39.92 | 13.4812 | 39.92
1988-03-24 | 24 | 3 | 0.33333 | 5.6 | 42.08 | 13.7969 | 42.08
1988-03-24 | 24 | 3 | 0.375 | 6.1 | 42.98 | 13.8298 | 42.98
1988-03-24 | 24 | 3 | 0.41667 | 7.2 | 44.96 | 13.9051 | 44.96
1988-03-24 | 24 | 3 | 0.45833 | 6.7 | 44.06 | 13.5168 | 44.06
1988-03-24 | 24 | 3 | 0.5 | 6.7 | 44.06 | 13.3854 | 44.06
1988-03-24 | 24 | 3 | 0.54167 | 5.6 | 42.08 | 13.188 | 42.08
1988-03-24 | 24 | 3 | 0.58333 | 6.1 | 42.98 | 13.2625 | 42.98
1988-03-24 | 24 | 3 | 0.625 | 6.7 | 44.06 | 12.6641 | 44.06
1988-03-24 | 24 | 3 | 0.66667 | 6.7 | 44.06 | 12.9918 | 44.06
1988-03-24 | 24 | 3 | 0.70833 | 6.7 | 44.06 | 12.7951 | 44.06
1988-03-24 | 24 | 3 | 0.75 | 6.1 | 42.98 | 12.6332 | 42.98
1988-03-24 | 24 | 3 | 0.79167 | 5.6 | 42.08 | 12.3979 | 42.08
1988-03-24 | 24 | 3 | 0.83333 | 5 | 41 | 12.0435 | 41
1988-03-24 | 24 | 3 | 0.875 | 4.4 | 39.92 | 11.6925 | 39.92
1988-03-24 | 24 | 3 | 0.91667 | 4.4 | 39.92 | 11.8598 |  | 39.92
1988-03-24 | 24 | 3 | 0.95833 | 3.3 | 37.94 | 11.3157 |  | 37.94
1988-03-24 | 24 | 3 | 1 | 2.8 | 37.04 | 11.0714 |  | 37.04
1988-03-25 | 25 | 3 | 0.041667 | 2.8 | 37.04 | 10.972 |  | 37.04
1988-03-25 | 25 | 3 | 0.083333 | 2.2 | 35.96 | 10.7198 |  | 35.96
1988-03-25 | 25 | 3 | 0.125 | 2.2 | 35.96 | 10.6246 |  | 35.96
1988-03-25 | 25 | 3 | 0.16667 | 1.7 | 35.06 | 10.4295 |  | 35.06
1988-03-25 | 25 | 3 | 0.20833 | 1.7 | 35.06 | 10.2458 |  | 35.06
1988-03-25 | 25 | 3 | 0.25 | 1.7 | 35.06 | 10.2917 | 35.06
1988-03-25 | 25 | 3 | 0.29167 | 1.7 | 35.06 | 10.2458 | 35.06
1988-03-25 | 25 | 3 | 0.33333 | 2.8 | 37.04 | 10.624 | 37.04
1988-03-25 | 25 | 3 | 0.375 | 1.1 | 33.98 | 9.7326 | 33.98
1988-03-25 | 25 | 3 | 0.41667 | 5 | 41 | 11.3461 | 41
1988-03-25 | 25 | 3 | 0.45833 | 6.7 | 44.06 | 12.2059 | 44.06
1988-03-25 | 25 | 3 | 0.5 | 7.8 | 46.04 | 12.6693 | 46.04
1988-03-25 | 25 | 3 | 0.54167 | 9.4 | 48.92 | 13.4698 | 48.92
1988-03-25 | 25 | 3 | 0.58333 | 10.6 | 51.08 | 13.964 | 51.08
1988-03-25 | 25 | 3 | 0.625 | 11.1 | 51.98 | 14.1501 | 51.98
1988-03-25 | 25 | 3 | 0.66667 | 11.7 | 53.06 | 14.5702 | 53.06
1988-03-25 | 25 | 3 | 0.70833 | 12.2 | 53.96 | 14.5632 | 53.96
1988-03-25 | 25 | 3 | 0.75 | 11.1 | 51.98 | 14.4153 | 51.98
1988-03-25 | 25 | 3 | 0.79167 | 10 | 50 | 14.1295 | 50
1988-03-25 | 25 | 3 | 0.83333 | 9.4 | 48.92 | 13.7851 | 48.92
1988-03-25 | 25 | 3 | 0.875 | 8.3 | 46.94 | 13.3077 | 46.94
1988-03-25 | 25 | 3 | 0.91667 | 8.3 | 46.94 | 13.3077 |  | 46.94
1988-03-25 | 25 | 3 | 0.95833 | 7.8 | 46.04 | 12.8811 |  | 46.04
1988-03-25 | 25 | 3 | 1 | 7.2 | 44.96 | 12.8185 |  | 44.96
1988-03-26 | 26 | 3 | 0.041667 | 7.2 | 44.96 | 13.0219 |  | 44.96
1988-03-26 | 26 | 3 | 0.083333 | 6.7 | 44.06 | 12.8607 |  | 44.06
1988-03-26 | 26 | 3 | 0.125 | 6.7 | 44.06 | 12.8607 |  | 44.06
1988-03-26 | 26 | 3 | 0.16667 | 6.1 | 42.98 | 12.6332 |  | 42.98
1988-03-26 | 26 | 3 | 0.20833 | 5.6 | 42.08 | 12.5194 |  | 42.08
1988-03-26 | 26 | 3 | 0.25 | 5 | 41 | 12.3927 | 41
1988-03-26 | 26 | 3 | 0.29167 | 6.1 | 42.98 | 12.759 | 42.98
1988-03-26 | 26 | 3 | 0.33333 | 6.7 | 44.06 | 12.9918 | 44.06
1988-03-26 | 26 | 3 | 0.375 | 7.8 | 46.04 | 13.5174 | 46.04
1988-03-26 | 26 | 3 | 0.41667 | 8.3 | 46.94 | 13.6004 | 46.94
1988-03-26 | 26 | 3 | 0.45833 | 10 | 50 | 14.5406 | 50
1988-03-26 | 26 | 3 | 0.5 | 10.6 | 51.08 | 15.0768 | 51.08
1988-03-26 | 26 | 3 | 0.54167 | 12.2 | 53.96 | 15.6109 | 53.96
1988-03-26 | 26 | 3 | 0.58333 | 13.9 | 57.02 | 16.1295 | 57.02
1988-03-26 | 26 | 3 | 0.625 | 15 | 59 | 16.4439 | 59
1988-03-26 | 26 | 3 | 0.66667 | 15 | 59 | 16.3293 | 59
1988-03-26 | 26 | 3 | 0.70833 | 15 | 59 | 16.2148 | 59
1988-03-26 | 26 | 3 | 0.75 | 14.4 | 57.92 | 15.8765 | 57.92
1988-03-26 | 26 | 3 | 0.79167 | 13.3 | 55.94 | 15.4679 | 55.94
1988-03-26 | 26 | 3 | 0.83333 | 12.2 | 53.96 | 15.5156 | 53.96
1988-03-26 | 26 | 3 | 0.875 | 11.7 | 53.06 | 15.3073 | 53.06
1988-03-26 | 26 | 3 | 0.91667 | 10.6 | 51.08 | 14.4771 |  | 51.08
1988-03-26 | 26 | 3 | 0.95833 | 10 | 50 | 14.2117 |  | 50
1988-03-26 | 26 | 3 | 1 | 8.9 | 48.02 | 13.9579 |  | 48.02
1988-03-27 | 27 | 3 | 0.041667 | 7.8 | 46.04 | 13.7298 |  | 46.04
1988-03-27 | 27 | 3 | 0.083333 | 7.2 | 44.96 | 13.4972 |  | 44.96
1988-03-27 | 27 | 3 | 0.125 | 6.7 | 44.06 | 13.5168 |  | 44.06
1988-03-27 | 27 | 3 | 0.16667 | 6.1 | 42.98 | 13.1365 |  | 42.98
1988-03-27 | 27 | 3 | 0.20833 | 5.6 | 42.08 | 12.7623 |  | 42.08
1988-03-27 | 27 | 3 | 0.25 | 5 | 41 | 12.8006 | 41
1988-03-27 | 27 | 3 | 0.29167 | 6.1 | 42.98 | 13.2625 | 42.98
1988-03-27 | 27 | 3 | 0.33333 | 6.7 | 44.06 | 13.3854 | 44.06
1988-03-27 | 27 | 3 | 0.375 | 7.8 | 46.04 | 13.8715 | 46.04
1988-03-27 | 27 | 3 | 0.41667 | 7.8 | 46.04 | 13.8715 | 46.04
1988-03-27 | 27 | 3 | 0.45833 | 8.3 | 46.94 | 13.9667 | 46.94
1988-03-27 | 27 | 3 | 0.5 | 9.4 | 48.92 | 14.0218 | 48.92
1988-03-27 | 27 | 3 | 0.54167 | 10 | 50 | 14.4584 | 50
1988-03-27 | 27 | 3 | 0.58333 | 11.1 | 51.98 | 15.1236 | 51.98
1988-03-27 | 27 | 3 | 0.625 | 11.7 | 53.06 | 15.5842 | 53.06
1988-03-27 | 27 | 3 | 0.66667 | 11.7 | 53.06 | 15.3996 | 53.06
1988-03-27 | 27 | 3 | 0.70833 | 11.7 | 53.06 | 15.5842 | 53.06
1988-03-27 | 27 | 3 | 0.75 | 11.1 | 51.98 | 14.9464 | 51.98
1988-03-27 | 27 | 3 | 0.79167 | 10 | 50 | 14.4584 | 50
1988-03-27 | 27 | 3 | 0.83333 | 10 | 50 | 14.2939 | 50
1988-03-27 | 27 | 3 | 0.875 | 9.4 | 48.92 | 14.1796 | 48.92
1988-03-27 | 27 | 3 | 0.91667 | 9.4 | 48.92 | 13.8639 |  | 48.92
1988-03-27 | 27 | 3 | 0.95833 | 8.9 | 48.02 | 13.9579 |  | 48.02
1988-03-27 | 27 | 3 | 1 | 8.3 | 46.94 | 13.6004 |  | 46.94
1988-03-28 | 28 | 3 | 0.041667 | 7.8 | 46.04 | 13.5174 |  | 46.04
1988-03-28 | 28 | 3 | 0.083333 | 6.7 | 44.06 | 13.2542 |  | 44.06
1988-03-28 | 28 | 3 | 0.125 | 6.1 | 42.98 | 12.8848 |  | 42.98
1988-03-28 | 28 | 3 | 0.16667 | 5.6 | 42.08 | 12.8839 |  | 42.08
1988-03-28 | 28 | 3 | 0.20833 | 5 | 41 | 12.3927 |  | 41
1988-03-28 | 28 | 3 | 0.25 | 4.4 | 39.92 | 12.1388 | 39.92
1988-03-28 | 28 | 3 | 0.29167 | 3.9 | 39.02 | 11.8872 | 39.02
1988-03-28 | 28 | 3 | 0.33333 | 6.1 | 42.98 | 12.759 | 42.98
1988-03-28 | 28 | 3 | 0.375 | 6.1 | 42.98 | 12.759 | 42.98
1988-03-28 | 28 | 3 | 0.41667 | 7.2 | 44.96 | 13.0898 | 44.96
1988-03-28 | 28 | 3 | 0.45833 | 8.3 | 46.94 | 13.6004 | 46.94
1988-03-28 | 28 | 3 | 0.5 | 8.9 | 48.02 | 13.9579 | 48.02
1988-03-28 | 28 | 3 | 0.54167 | 10 | 50 | 14.1295 | 50
1988-03-28 | 28 | 3 | 0.58333 | 11.1 | 51.98 | 14.7693 | 51.98
1988-03-28 | 28 | 3 | 0.625 | 11.1 | 51.98 | 14.6808 | 51.98
1988-03-28 | 28 | 3 | 0.66667 | 11.1 | 51.98 | 14.9464 | 51.98
1988-03-28 | 28 | 3 | 0.70833 | 11.1 | 51.98 | 14.9464 | 51.98
1988-03-28 | 28 | 3 | 0.75 | 10.6 | 51.08 | 14.8197 | 51.08
1988-03-28 | 28 | 3 | 0.79167 | 10 | 50 | 14.5406 | 50
1988-03-28 | 28 | 3 | 0.83333 | 10 | 50 | 14.7052 | 50
1988-03-28 | 28 | 3 | 0.875 | 8.3 | 46.94 | 14.7739 | 46.94
1988-03-28 | 28 | 3 | 0.91667 | 7.8 | 46.04 | 14.4387 |  | 46.04
1988-03-28 | 28 | 3 | 0.95833 | 8.3 | 46.94 | 13.9667 |  | 46.94
1988-03-28 | 28 | 3 | 1 | 8.3 | 46.94 | 14.1866 |  | 46.94
1988-03-29 | 29 | 3 | 0.041667 | 7.8 | 46.04 | 13.8715 |  | 46.04
1988-03-29 | 29 | 3 | 0.083333 | 7.2 | 44.96 | 13.6331 |  | 44.96
1988-03-29 | 29 | 3 | 0.125 | 6.1 | 42.98 | 13.1365 |  | 42.98
1988-03-29 | 29 | 3 | 0.16667 | 6.7 | 44.06 | 13.2542 |  | 44.06
1988-03-29 | 29 | 3 | 0.20833 | 5.6 | 42.08 | 12.6408 |  | 42.08
1988-03-29 | 29 | 3 | 0.25 | 5 | 41 | 12.6257 | 41
1988-03-29 | 29 | 3 | 0.29167 | 6.7 | 44.06 | 12.9918 | 44.06
1988-03-29 | 29 | 3 | 0.33333 | 7.8 | 46.04 | 13.3759 | 46.04
1988-03-29 | 29 | 3 | 0.375 | 8.3 | 46.94 | 13.454 | 46.94
1988-03-29 | 29 | 3 | 0.41667 | 9.4 | 48.92 | 14.2586 | 48.92
1988-03-29 | 29 | 3 | 0.45833 | 10.6 | 51.08 | 14.9053 | 51.08
1988-03-29 | 29 | 3 | 0.5 | 11.1 | 51.98 | 14.9464 | 51.98
1988-03-29 | 29 | 3 | 0.54167 | 12.2 | 53.96 | 15.5156 | 53.96
1988-03-29 | 29 | 3 | 0.58333 | 14.4 | 57.92 | 16.979 | 57.92
1988-03-29 | 29 | 3 | 0.625 | 12.8 | 55.04 | 15.7802 | 55.04
1988-03-29 | 29 | 3 | 0.66667 | 12.2 | 53.96 | 15.6109 | 53.96
1988-03-29 | 29 | 3 | 0.70833 | 10.6 | 51.08 | 14.9053 | 51.08
1988-03-29 | 29 | 3 | 0.75 | 9.4 | 48.92 | 14.8119 | 48.92
1988-03-29 | 29 | 3 | 0.79167 | 7.8 | 46.04 | 14.4387 | 46.04
1988-03-29 | 29 | 3 | 0.83333 | 7.8 | 46.04 | 14.7937 | 46.04
1988-03-29 | 29 | 3 | 0.875 | 7.2 | 44.96 | 14.5179 | 44.96
1988-03-29 | 29 | 3 | 0.91667 | 7.2 | 44.96 | 14.5179 |  | 44.96
1988-03-29 | 29 | 3 | 0.95833 | 6.7 | 44.06 | 15.3606 |  | 44.06
1988-03-29 | 29 | 3 | 1 | 6.7 | 44.06 | 15.757 |  | 44.06
1988-03-30 | 30 | 3 | 0.041667 | 6.7 | 44.06 | 15.9554 |  | 44.06
1988-03-30 | 30 | 3 | 0.083333 | 7.2 | 44.96 | 16.3629 |  | 44.96
1988-03-30 | 30 | 3 | 0.125 | 7.2 | 44.96 | 16.3629 |  | 44.96
1988-03-30 | 30 | 3 | 0.16667 | 7.8 | 46.04 | 16.6457 |  | 46.04
1988-03-30 | 30 | 3 | 0.20833 | 7.8 | 46.04 | 16.6457 |  | 46.04
1988-03-30 | 30 | 3 | 0.25 | 7.8 | 46.04 | 16.6457 | 46.04
1988-03-30 | 30 | 3 | 0.29167 | 8.3 | 46.94 | 16.4679 | 46.94
1988-03-30 | 30 | 3 | 0.33333 | 8.9 | 48.02 | 16.3318 | 48.02
1988-03-30 | 30 | 3 | 0.375 | 8.9 | 48.02 | 16.7162 | 48.02
1988-03-30 | 30 | 3 | 0.41667 | 8.9 | 48.02 | 17.1011 | 48.02
1988-03-30 | 30 | 3 | 0.45833 | 8.9 | 48.02 | 17.6407 | 48.02
1988-03-30 | 30 | 3 | 0.5 | 9.4 | 48.92 | 17.8313 | 48.92
1988-03-30 | 30 | 3 | 0.54167 | 9.4 | 48.92 | 17.3527 | 48.92
1988-03-30 | 30 | 3 | 0.58333 | 10 | 50 | 17.5982 | 50
1988-03-30 | 30 | 3 | 0.625 | 9.4 | 48.92 | 17.5919 | 48.92
1988-03-30 | 30 | 3 | 0.66667 | 9.4 | 48.92 | 17.8313 | 48.92
1988-03-30 | 30 | 3 | 0.70833 | 9.4 | 48.92 | 17.8313 | 48.92
1988-03-30 | 30 | 3 | 0.75 | 8.9 | 48.02 | 17.6407 | 48.02
1988-03-30 | 30 | 3 | 0.79167 | 8.9 | 48.02 | 17.8722 | 48.02
1988-03-30 | 30 | 3 | 0.83333 | 8.9 | 48.02 | 18.1039 | 48.02
1988-03-30 | 30 | 3 | 0.875 | 9.4 | 48.92 | 17.8313 | 48.92
1988-03-30 | 30 | 3 | 0.91667 | 9.4 | 48.92 | 17.8313 |  | 48.92
1988-03-30 | 30 | 3 | 0.95833 | 9.4 | 48.92 | 18.0708 |  | 48.92
1988-03-30 | 30 | 3 | 1 | 9.4 | 48.92 | 16.9545 |  | 48.92
1988-03-31 | 31 | 3 | 0.041667 | 8.9 | 48.02 | 16.7162 |  | 48.02
1988-03-31 | 31 | 3 | 0.083333 | 8.3 | 46.94 | 16.4679 |  | 46.94
1988-03-31 | 31 | 3 | 0.125 | 7.8 | 46.04 | 15.8609 |  | 46.04
1988-03-31 | 31 | 3 | 0.16667 | 7.2 | 44.96 | 15.2001 |  | 44.96
1988-03-31 | 31 | 3 | 0.20833 | 6.7 | 44.06 | 14.8327 |  | 44.06
1988-03-31 | 31 | 3 | 0.25 | 6.7 | 44.06 | 14.9646 | 44.06
1988-03-31 | 31 | 3 | 0.29167 | 6.7 | 44.06 | 14.9646 | 44.06
1988-03-31 | 31 | 3 | 0.33333 | 7.2 | 44.96 | 14.8588 | 44.96
1988-03-31 | 31 | 3 | 0.375 | 7.8 | 46.04 | 14.7937 | 46.04
1988-03-31 | 31 | 3 | 0.41667 | 8.3 | 46.94 | 14.9944 | 46.94
1988-03-31 | 31 | 3 | 0.45833 | 8.9 | 48.02 | 14.9514 | 48.02
1988-03-31 | 31 | 3 | 0.5 | 10 | 50 | 15.3643 | 50
1988-03-31 | 31 | 3 | 0.54167 | 9.4 | 48.92 | 14.9701 | 48.92
1988-03-31 | 31 | 3 | 0.58333 | 10 | 50 | 15.117 | 50
1988-03-31 | 31 | 3 | 0.625 | 10.6 | 51.08 | 15.5057 | 51.08
1988-03-31 | 31 | 3 | 0.66667 | 10.6 | 51.08 | 15.5057 | 51.08
1988-03-31 | 31 | 3 | 0.70833 | 10 | 50 | 14.9522 | 50
1988-03-31 | 31 | 3 | 0.75 | 10 | 50 | 15.117 | 50
1988-03-31 | 31 | 3 | 0.79167 | 10 | 50 | 14.9522 | 50
1988-03-31 | 31 | 3 | 0.83333 | 9.4 | 48.92 | 14.8119 | 48.92
1988-03-31 | 31 | 3 | 0.875 | 8.3 | 46.94 | 14.4801 | 46.94
1988-03-31 | 31 | 3 | 0.91667 | 8.2 | 46.76 | 14.8525 |  | 46.76
1988-03-31 | 31 | 3 | 0.95833 | 8.2 | 46.76 | 14.9985 |  | 46.76
1988-03-31 | 31 | 3 | 1 | 8.1 | 46.58 | 15.2921 |  | 46.58
2003-04-01 | 1 | 4 | 0.041667 | 8 | 46.4 | 16.2314 |  | 46.4
2003-04-01 | 1 | 4 | 0.083333 | 7.9 | 46.22 | 16.3684 |  | 46.22
2003-04-01 | 1 | 4 | 0.125 | 7.9 | 46.22 | 16.5122 |  | 46.22
2003-04-01 | 1 | 4 | 0.16667 | 7.8 | 46.04 | 16.0747 |  | 46.04
2003-04-01 | 1 | 4 | 0.20833 | 6.7 | 44.06 | 15.757 |  | 44.06
2003-04-01 | 1 | 4 | 0.25 | 7.8 | 46.04 | 16.4315 | 46.04
2003-04-01 | 1 | 4 | 0.29167 | 6.7 | 44.06 | 15.3606 | 44.06
2003-04-01 | 1 | 4 | 0.33333 | 8.3 | 46.94 | 15.8777 | 46.94
2003-04-01 | 1 | 4 | 0.375 | 9.4 | 48.92 | 16.0005 | 48.92
2003-04-01 | 1 | 4 | 0.41667 | 10.6 | 51.08 | 16.0212 | 51.08
2003-04-01 | 1 | 4 | 0.45833 | 11.7 | 53.06 | 17.3428 | 53.06
2003-04-01 | 1 | 4 | 0.5 | 12.8 | 55.04 | 17.4716 | 55.04
2003-04-01 | 1 | 4 | 0.54167 | 14.4 | 57.92 | 17.6423 | 57.92
2003-04-01 | 1 | 4 | 0.58333 | 13.9 | 57.02 | 16.6633 | 57.02
2003-04-01 | 1 | 4 | 0.625 | 14.4 | 57.92 | 17.2 | 57.92
2003-04-01 | 1 | 4 | 0.66667 | 14.4 | 57.92 | 17.3105 | 57.92
2003-04-01 | 1 | 4 | 0.70833 | 14.4 | 57.92 | 18.196 | 57.92
2003-04-01 | 1 | 4 | 0.75 | 13.3 | 55.94 | 17.0077 | 55.94
2003-04-01 | 1 | 4 | 0.79167 | 12.8 | 55.04 | 16.5751 | 55.04
2003-04-01 | 1 | 4 | 0.83333 | 12.2 | 53.96 | 16.4706 | 53.96
2003-04-01 | 1 | 4 | 0.875 | 13.3 | 55.94 | 16.802 | 55.94
2003-04-01 | 1 | 4 | 0.91667 | 13.3 | 55.94 | 16.802 |  | 55.94
2003-04-01 | 1 | 4 | 0.95833 | 12.8 | 55.04 | 16.5751 |  | 55.04
2003-04-01 | 1 | 4 | 1 | 12.2 | 53.96 | 16.4706 |  | 53.96
2003-04-02 | 2 | 4 | 0.041667 | 11.1 | 51.98 | 16.9008 |  | 51.98
2003-04-02 | 2 | 4 | 0.083333 | 10.6 | 51.08 | 16.3653 |  | 51.08
2003-04-02 | 2 | 4 | 0.125 | 9.4 | 48.92 | 16.1593 |  | 48.92
2003-04-02 | 2 | 4 | 0.16667 | 7.2 | 44.96 | 14.8588 |  | 44.96
2003-04-02 | 2 | 4 | 0.20833 | 6.7 | 44.06 | 14.635 |  | 44.06
2003-04-02 | 2 | 4 | 0.25 | 6.1 | 42.98 | 14.7142 | 42.98
2003-04-02 | 2 | 4 | 0.29167 | 6.1 | 42.98 | 14.7142 | 42.98
2003-04-02 | 2 | 4 | 0.33333 | 7.2 | 44.96 | 15.0635 | 44.96
2003-04-02 | 2 | 4 | 0.375 | 6.7 | 44.06 | 14.8327 | 44.06
2003-04-02 | 2 | 4 | 0.41667 | 6.7 | 44.06 | 15.1626 | 44.06
2003-04-02 | 2 | 4 | 0.45833 | 7.2 | 44.96 | 15.5417 | 44.96
2003-04-02 | 2 | 4 | 0.5 | 7.2 | 44.96 | 15.5417 | 44.96
2003-04-02 | 2 | 4 | 0.54167 | 9.4 | 48.92 | 16.3977 | 48.92
2003-04-02 | 2 | 4 | 0.58333 | 8.9 | 48.02 | 16.1781 | 48.02
2003-04-02 | 2 | 4 | 0.625 | 7.2 | 44.96 | 15.405 | 44.96
2003-04-02 | 2 | 4 | 0.66667 | 7.2 | 44.96 | 15.5417 | 44.96
2003-04-02 | 2 | 4 | 0.70833 | 6.7 | 44.06 | 15.5587 | 44.06
2003-04-02 | 2 | 4 | 0.75 | 6.1 | 42.98 | 15.4741 | 42.98
2003-04-02 | 2 | 4 | 0.79167 | 6.1 | 42.98 | 15.9182 | 42.98
2003-04-02 | 2 | 4 | 0.83333 | 6.7 | 44.06 | 16.4187 | 44.06
2003-04-02 | 2 | 4 | 0.875 | 6.1 | 42.98 | 15.9182 | 42.98
2003-04-02 | 2 | 4 | 0.91667 | 6.1 | 42.98 | 15.9182 |  | 42.98
2003-04-02 | 2 | 4 | 0.95833 | 5.6 | 42.08 | 15.6918 |  | 42.08
2003-04-02 | 2 | 4 | 1 | 4.4 | 39.92 | 14.9977 |  | 39.92
2003-04-03 | 3 | 4 | 0.041667 | 4.4 | 39.92 | 14.9977 |  | 39.92
2003-04-03 | 3 | 4 | 0.083333 | 4.7 | 40.46 | 15.2445 |  | 40.46
2003-04-03 | 3 | 4 | 0.125 | 5 | 41 | 15.4347 |  | 41
2003-04-03 | 3 | 4 | 0.16667 | 7.8 | 46.04 | 16.6457 |  | 46.04
2003-04-03 | 3 | 4 | 0.20833 | 7.8 | 46.04 | 16.6457 |  | 46.04
2003-04-03 | 3 | 4 | 0.25 | 8.9 | 48.02 | 17.1011 | 48.02
2003-04-03 | 3 | 4 | 0.29167 | 9.4 | 48.92 | 17.5919 | 48.92
2003-04-03 | 3 | 4 | 0.33333 | 10.6 | 51.08 | 18.3506 | 51.08
2003-04-03 | 3 | 4 | 0.375 | 12.2 | 53.96 | 19.2554 | 53.96
2003-04-03 | 3 | 4 | 0.41667 | 14.4 | 57.92 | 19.974 | 57.92
2003-04-03 | 3 | 4 | 0.45833 | 12.8 | 55.04 | 20.0748 | 55.04
2003-04-03 | 3 | 4 | 0.5 | 13.3 | 55.94 | 20.3162 | 55.94
2003-04-03 | 3 | 4 | 0.54167 | 13.3 | 55.94 | 20.3162 | 55.94
2003-04-03 | 3 | 4 | 0.58333 | 12.8 | 55.04 | 20.0748 | 55.04
2003-04-03 | 3 | 4 | 0.625 | 12.8 | 55.04 | 20.3765 | 55.04
2003-04-03 | 3 | 4 | 0.66667 | 12.2 | 53.96 | 19.7379 | 53.96
2003-04-03 | 3 | 4 | 0.70833 | 11.1 | 51.98 | 19.0458 | 51.98
2003-04-03 | 3 | 4 | 0.75 | 11.1 | 51.98 | 19.0458 | 51.98
2003-04-03 | 3 | 4 | 0.79167 | 11.1 | 51.98 | 19.3149 | 51.98
2003-04-03 | 3 | 4 | 0.83333 | 11.1 | 51.98 | 19.5842 | 51.98
2003-04-03 | 3 | 4 | 0.875 | 10.6 | 51.08 | 19.6516 | 51.08
2003-04-03 | 3 | 4 | 0.91667 | 11.1 | 51.98 | 19.8537 |  | 51.98
2003-04-03 | 3 | 4 | 0.95833 | 10.6 | 51.08 | 19.391 |  | 51.08
2003-04-03 | 3 | 4 | 1 | 10 | 50 | 19.0956 |  | 50
2003-04-04 | 4 | 4 | 0.041667 | 10 | 50 | 18.8456 |  | 50
2003-04-04 | 4 | 4 | 0.083333 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-04 | 4 | 4 | 0.125 | 8.3 | 46.94 | 17.5773 |  | 46.94
2003-04-04 | 4 | 4 | 0.16667 | 7.2 | 44.96 | 16.3629 |  | 44.96
2003-04-04 | 4 | 4 | 0.20833 | 5.6 | 42.08 | 15.5079 |  | 42.08
2003-04-04 | 4 | 4 | 0.25 | 4.4 | 39.92 | 14.379 | 39.92
2003-04-04 | 4 | 4 | 0.29167 | 3.9 | 39.02 | 13.6154 | 39.02
2003-04-04 | 4 | 4 | 0.33333 | 4.4 | 39.92 | 13.4812 | 39.92
2003-04-04 | 4 | 4 | 0.375 | 5.6 | 42.08 | 13.6141 | 42.08
2003-04-04 | 4 | 4 | 0.41667 | 7.2 | 44.96 | 14.3135 | 44.96
2003-04-04 | 4 | 4 | 0.45833 | 7.8 | 46.04 | 14.7937 | 46.04
2003-04-04 | 4 | 4 | 0.5 | 9.4 | 48.92 | 15.4453 | 48.92
2003-04-04 | 4 | 4 | 0.54167 | 10.6 | 51.08 | 16.3653 | 51.08
2003-04-04 | 4 | 4 | 0.58333 | 11.7 | 53.06 | 16.5086 | 53.06
2003-04-04 | 4 | 4 | 0.625 | 13.3 | 55.94 | 17.0077 | 55.94
2003-04-04 | 4 | 4 | 0.66667 | 15 | 59 | 17.5916 | 59
2003-04-04 | 4 | 4 | 0.70833 | 15 | 59 | 17.3618 | 59
2003-04-04 | 4 | 4 | 0.75 | 13.9 | 57.02 | 16.7702 | 57.02
2003-04-04 | 4 | 4 | 0.79167 | 12.8 | 55.04 | 16.4756 | 55.04
2003-04-04 | 4 | 4 | 0.83333 | 12.8 | 55.04 | 16.7741 | 55.04
2003-04-04 | 4 | 4 | 0.875 | 12.2 | 53.96 | 16.6619 | 53.96
2003-04-04 | 4 | 4 | 0.91667 | 10 | 50 | 16.438 |  | 50
2003-04-04 | 4 | 4 | 0.95833 | 9.4 | 48.92 | 16.0005 |  | 48.92
2003-04-04 | 4 | 4 | 1 | 8.9 | 48.02 | 15.9478 |  | 48.02
2003-04-05 | 5 | 4 | 0.041667 | 8.3 | 46.94 | 15.8777 |  | 46.94
2003-04-05 | 5 | 4 | 0.083333 | 7.8 | 46.04 | 15.5048 |  | 46.04
2003-04-05 | 5 | 4 | 0.125 | 7.2 | 44.96 | 15.405 |  | 44.96
2003-04-05 | 5 | 4 | 0.16667 | 6.7 | 44.06 | 15.3606 |  | 44.06
2003-04-05 | 5 | 4 | 0.20833 | 6.1 | 42.98 | 14.904 |  | 42.98
2003-04-05 | 5 | 4 | 0.25 | 6.7 | 44.06 | 15.1626 | 44.06
2003-04-05 | 5 | 4 | 0.29167 | 7.8 | 46.04 | 16.2174 | 46.04
2003-04-05 | 5 | 4 | 0.33333 | 11.1 | 51.98 | 17.525 | 51.98
2003-04-05 | 5 | 4 | 0.375 | 12.8 | 55.04 | 17.9707 | 55.04
2003-04-05 | 5 | 4 | 0.41667 | 13.9 | 57.02 | 18.9145 | 57.02
2003-04-05 | 5 | 4 | 0.45833 | 13.9 | 57.02 | 18.6995 | 57.02
2003-04-05 | 5 | 4 | 0.5 | 13.9 | 57.02 | 19.1297 | 57.02
2003-04-05 | 5 | 4 | 0.54167 | 13.3 | 55.94 | 19.0717 | 55.94
2003-04-05 | 5 | 4 | 0.58333 | 13.3 | 55.94 | 18.6579 | 55.94
2003-04-05 | 5 | 4 | 0.625 | 12.8 | 55.04 | 17.8708 | 55.04
2003-04-05 | 5 | 4 | 0.66667 | 12.2 | 53.96 | 17.7161 | 53.96
2003-04-05 | 5 | 4 | 0.70833 | 11.7 | 53.06 | 17.7141 | 53.06
2003-04-05 | 5 | 4 | 0.75 | 10.6 | 51.08 | 17.0545 | 51.08
2003-04-05 | 5 | 4 | 0.79167 | 9.4 | 48.92 | 16.5567 | 48.92
2003-04-05 | 5 | 4 | 0.83333 | 9.4 | 48.92 | 17.1137 | 48.92
2003-04-05 | 5 | 4 | 0.875 | 9.4 | 48.92 | 17.5919 | 48.92
2003-04-05 | 5 | 4 | 0.91667 | 10 | 50 | 17.0176 |  | 50
2003-04-05 | 5 | 4 | 0.95833 | 9.4 | 48.92 | 17.1137 |  | 48.92
2003-04-05 | 5 | 4 | 1 | 8.9 | 48.02 | 17.1011 |  | 48.02
2003-04-06 | 6 | 4 | 0.041667 | 8.3 | 46.94 | 16.8373 |  | 46.94
2003-04-06 | 6 | 4 | 0.083333 | 7.8 | 46.04 | 16.86 |  | 46.04
2003-04-06 | 6 | 4 | 0.125 | 7.2 | 44.96 | 16.6371 |  | 44.96
2003-04-06 | 6 | 4 | 0.16667 | 7.2 | 44.96 | 16.3629 |  | 44.96
2003-04-06 | 6 | 4 | 0.20833 | 6.7 | 44.06 | 16.4187 |  | 44.06
2003-04-06 | 6 | 4 | 0.25 | 7.2 | 44.96 | 16.9115 | 44.96
2003-04-06 | 6 | 4 | 0.29167 | 6.7 | 44.06 | 16.8827 | 44.06
2003-04-06 | 6 | 4 | 0.33333 | 7.2 | 44.96 | 17.1175 | 44.96
2003-04-06 | 6 | 4 | 0.375 | 7.2 | 44.96 | 17.1175 | 44.96
2003-04-06 | 6 | 4 | 0.41667 | 7.2 | 44.96 | 17.3923 | 44.96
2003-04-06 | 6 | 4 | 0.45833 | 10 | 50 | 19.6798 | 50
2003-04-06 | 6 | 4 | 0.5 | 11.1 | 51.98 | 20.7536 | 51.98
2003-04-06 | 6 | 4 | 0.54167 | 10.6 | 51.08 | 20.5217 | 51.08
2003-04-06 | 6 | 4 | 0.58333 | 10.6 | 51.08 | 20.5217 | 51.08
2003-04-06 | 6 | 4 | 0.625 | 11.1 | 51.98 | 20.7536 | 51.98
2003-04-06 | 6 | 4 | 0.66667 | 11.7 | 53.06 | 21.3566 | 53.06
2003-04-06 | 6 | 4 | 0.70833 | 12.2 | 53.96 | 21.8688 | 53.96
2003-04-06 | 6 | 4 | 0.75 | 13.9 | 57.02 | 23.244 | 57.02
2003-04-06 | 6 | 4 | 0.79167 | 12.8 | 55.04 | 22.4956 | 55.04
2003-04-06 | 6 | 4 | 0.83333 | 12.2 | 53.96 | 21.8688 | 53.96
2003-04-06 | 6 | 4 | 0.875 | 11.7 | 53.06 | 20.9812 | 53.06
2003-04-06 | 6 | 4 | 0.91667 | 11.1 | 51.98 | 20.3933 |  | 51.98
2003-04-06 | 6 | 4 | 0.95833 | 11.1 | 51.98 | 20.7536 |  | 51.98
2003-04-06 | 6 | 4 | 1 | 11.7 | 53.06 | 21.6384 |  | 53.06
2003-04-07 | 7 | 4 | 0.041667 | 12.2 | 53.96 | 22.2577 |  | 53.96
2003-04-07 | 7 | 4 | 0.083333 | 11.7 | 53.06 | 21.6384 |  | 53.06
2003-04-07 | 7 | 4 | 0.125 | 11.1 | 51.98 | 21.1142 |  | 51.98
2003-04-07 | 7 | 4 | 0.16667 | 12.8 | 55.04 | 22.7994 |  | 55.04
2003-04-07 | 7 | 4 | 0.20833 | 13.3 | 55.94 | 23.4473 |  | 55.94
2003-04-07 | 7 | 4 | 0.25 | 13.9 | 57.02 | 23.0263 | 57.02
2003-04-07 | 7 | 4 | 0.29167 | 12.2 | 53.96 | 20.8986 | 53.96
2003-04-07 | 7 | 4 | 0.33333 | 12.8 | 55.04 | 20.8798 | 55.04
2003-04-07 | 7 | 4 | 0.375 | 14.4 | 57.92 | 22.8831 | 57.92
2003-04-07 | 7 | 4 | 0.41667 | 11.1 | 51.98 | 19.0458 | 51.98
2003-04-07 | 7 | 4 | 0.45833 | 10 | 50 | 17.5982 | 50
2003-04-07 | 7 | 4 | 0.5 | 10 | 50 | 16.7691 | 50
2003-04-07 | 7 | 4 | 0.54167 | 9.4 | 48.92 | 15.6038 | 48.92
2003-04-07 | 7 | 4 | 0.58333 | 8.9 | 48.02 | 15.2576 | 48.02
2003-04-07 | 7 | 4 | 0.625 | 8.3 | 46.94 | 14.9944 | 46.94
2003-04-07 | 7 | 4 | 0.66667 | 9.4 | 48.92 | 15.6038 | 48.92
2003-04-07 | 7 | 4 | 0.70833 | 8.3 | 46.94 | 14.7739 | 46.94
2003-04-07 | 7 | 4 | 0.75 | 7.8 | 46.04 | 14.5806 | 46.04
2003-04-07 | 7 | 4 | 0.79167 | 6.7 | 44.06 | 13.7795 | 44.06
2003-04-07 | 7 | 4 | 0.83333 | 6.7 | 44.06 | 13.5168 | 44.06
2003-04-07 | 7 | 4 | 0.875 | 6.1 | 42.98 | 12.759 | 42.98
2003-04-07 | 7 | 4 | 0.91667 | 5 | 41 | 12.3927 |  | 41
2003-04-07 | 7 | 4 | 0.95833 | 4.4 | 39.92 | 12.1388 |  | 39.92
2003-04-07 | 7 | 4 | 1 | 3.9 | 39.02 | 11.8872 |  | 39.02
2003-04-08 | 8 | 4 | 0.041667 | 3.9 | 39.02 | 11.7794 |  | 39.02
2003-04-08 | 8 | 4 | 0.083333 | 3.9 | 39.02 | 11.4565 |  | 39.02
2003-04-08 | 8 | 4 | 0.125 | 3.3 | 37.94 | 11.3157 |  | 37.94
2003-04-08 | 8 | 4 | 0.16667 | 2.8 | 37.04 | 11.0714 |  | 37.04
2003-04-08 | 8 | 4 | 0.20833 | 2.2 | 35.96 | 10.9104 |  | 35.96
2003-04-08 | 8 | 4 | 0.25 | 2.2 | 35.96 | 10.9104 | 35.96
2003-04-08 | 8 | 4 | 0.29167 | 2.8 | 37.04 | 11.3203 | 37.04
2003-04-08 | 8 | 4 | 0.33333 | 5 | 41 | 12.1598 | 41
2003-04-08 | 8 | 4 | 0.375 | 7.2 | 44.96 | 13.0219 | 44.96
2003-04-08 | 8 | 4 | 0.41667 | 8.9 | 48.02 | 13.5003 | 48.02
2003-04-08 | 8 | 4 | 0.45833 | 10 | 50 | 13.8831 | 50
2003-04-08 | 8 | 4 | 0.5 | 11.1 | 51.98 | 14.3269 | 51.98
2003-04-08 | 8 | 4 | 0.54167 | 12.2 | 53.96 | 14.9438 | 53.96
2003-04-08 | 8 | 4 | 0.58333 | 12.8 | 55.04 | 15.0862 | 55.04
2003-04-08 | 8 | 4 | 0.625 | 13.9 | 57.02 | 15.5966 | 57.02
2003-04-08 | 8 | 4 | 0.66667 | 13.9 | 57.02 | 15.7031 | 57.02
2003-04-08 | 8 | 4 | 0.70833 | 13.9 | 57.02 | 15.4901 | 57.02
2003-04-08 | 8 | 4 | 0.75 | 10.6 | 51.08 | 15.5057 | 51.08
2003-04-08 | 8 | 4 | 0.79167 | 9.4 | 48.92 | 14.5746 | 48.92
2003-04-08 | 8 | 4 | 0.83333 | 8.9 | 48.02 | 13.9579 | 48.02
2003-04-08 | 8 | 4 | 0.875 | 7.8 | 46.04 | 13.8715 | 46.04
2003-04-08 | 8 | 4 | 0.91667 | 7.2 | 44.96 | 14.3135 |  | 44.96
2003-04-08 | 8 | 4 | 0.95833 | 6.7 | 44.06 | 14.3057 |  | 44.06
2003-04-08 | 8 | 4 | 1 | 6.7 | 44.06 | 14.1083 |  | 44.06
2003-04-09 | 9 | 4 | 0.041667 | 6.1 | 42.98 | 13.7037 |  | 42.98
2003-04-09 | 9 | 4 | 0.083333 | 6.1 | 42.98 | 13.5145 |  | 42.98
2003-04-09 | 9 | 4 | 0.125 | 6.1 | 42.98 | 13.7037 |  | 42.98
2003-04-09 | 9 | 4 | 0.16667 | 5.6 | 42.08 | 13.6141 |  | 42.08
2003-04-09 | 9 | 4 | 0.20833 | 5 | 41 | 13.5595 |  | 41
2003-04-09 | 9 | 4 | 0.25 | 5.6 | 42.08 | 13.9798 | 42.08
2003-04-09 | 9 | 4 | 0.29167 | 6.1 | 42.98 | 14.3981 | 42.98
2003-04-09 | 9 | 4 | 0.33333 | 8.9 | 48.02 | 15.4109 | 48.02
2003-04-09 | 9 | 4 | 0.375 | 11.1 | 51.98 | 15.567 | 51.98
2003-04-09 | 9 | 4 | 0.41667 | 11.1 | 51.98 | 16.3667 | 51.98
2003-04-09 | 9 | 4 | 0.45833 | 12.2 | 53.96 | 16.1838 | 53.96
2003-04-09 | 9 | 4 | 0.5 | 10.6 | 51.08 | 15.6775 | 51.08
2003-04-09 | 9 | 4 | 0.54167 | 10 | 50 | 15.8594 | 50
2003-04-09 | 9 | 4 | 0.58333 | 10 | 50 | 16.6035 | 50
2003-04-09 | 9 | 4 | 0.625 | 11.1 | 51.98 | 17.7036 | 51.98
2003-04-09 | 9 | 4 | 0.66667 | 11.7 | 53.06 | 18.3651 | 53.06
2003-04-09 | 9 | 4 | 0.70833 | 11.7 | 53.06 | 18.5513 | 53.06
2003-04-09 | 9 | 4 | 0.75 | 12.8 | 55.04 | 19.372 | 55.04
2003-04-09 | 9 | 4 | 0.79167 | 11.7 | 53.06 | 19.5772 | 53.06
2003-04-09 | 9 | 4 | 0.83333 | 11.1 | 51.98 | 19.3149 | 51.98
2003-04-09 | 9 | 4 | 0.875 | 10.6 | 51.08 | 19.391 | 51.08
2003-04-09 | 9 | 4 | 0.91667 | 11.1 | 51.98 | 19.3149 |  | 51.98
2003-04-09 | 9 | 4 | 0.95833 | 10.6 | 51.08 | 19.0439 |  | 51.08
2003-04-09 | 9 | 4 | 1 | 10.6 | 51.08 | 19.391 |  | 51.08
2003-04-10 | 10 | 4 | 0.041667 | 10.6 | 51.08 | 19.0439 |  | 51.08
2003-04-10 | 10 | 4 | 0.083333 | 10 | 50 | 18.8456 |  | 50
2003-04-10 | 10 | 4 | 0.125 | 10.6 | 51.08 | 19.0439 |  | 51.08
2003-04-10 | 10 | 4 | 0.16667 | 11.1 | 51.98 | 19.5842 |  | 51.98
2003-04-10 | 10 | 4 | 0.20833 | 11.7 | 53.06 | 20.1381 |  | 53.06
2003-04-10 | 10 | 4 | 0.25 | 12.8 | 55.04 | 20.8798 | 55.04
2003-04-10 | 10 | 4 | 0.29167 | 12.2 | 53.96 | 20.8986 | 53.96
2003-04-10 | 10 | 4 | 0.33333 | 12.8 | 55.04 | 21.1822 | 55.04
2003-04-10 | 10 | 4 | 0.375 | 15 | 59 | 22.1052 | 59
2003-04-10 | 10 | 4 | 0.41667 | 17.2 | 62.96 | 24.4197 | 62.96
2003-04-10 | 10 | 4 | 0.45833 | 17.2 | 62.96 | 25.0945 | 62.96
2003-04-10 | 10 | 4 | 0.5 | 17.2 | 62.96 | 25.0945 | 62.96
2003-04-10 | 10 | 4 | 0.54167 | 17.8 | 64.04 | 25.4688 | 64.04
2003-04-10 | 10 | 4 | 0.58333 | 16.1 | 60.98 | 24.9345 | 60.98
2003-04-10 | 10 | 4 | 0.625 | 15.6 | 60.08 | 25.2398 | 60.08
2003-04-10 | 10 | 4 | 0.66667 | 15.6 | 60.08 | 25.2398 | 60.08
2003-04-10 | 10 | 4 | 0.70833 | 15.6 | 60.08 | 25.6064 | 60.08
2003-04-10 | 10 | 4 | 0.75 | 13.9 | 57.02 | 24.0074 | 57.02
2003-04-10 | 10 | 4 | 0.79167 | 12.8 | 55.04 | 21.4848 | 55.04
2003-04-10 | 10 | 4 | 0.83333 | 12.8 | 55.04 | 20.8798 | 55.04
2003-04-10 | 10 | 4 | 0.875 | 12.2 | 53.96 | 20.3177 | 53.96
2003-04-10 | 10 | 4 | 0.91667 | 12.2 | 53.96 | 19.2554 |  | 53.96
2003-04-10 | 10 | 4 | 0.95833 | 10.6 | 51.08 | 16.8821 |  | 51.08
2003-04-10 | 10 | 4 | 1 | 10.6 | 51.08 | 16.8821 |  | 51.08
2003-04-11 | 11 | 4 | 0.041667 | 10 | 50 | 16.6035 |  | 50
2003-04-11 | 11 | 4 | 0.083333 | 10 | 50 | 16.6035 |  | 50
2003-04-11 | 11 | 4 | 0.125 | 8.9 | 48.02 | 15.9478 |  | 48.02
2003-04-11 | 11 | 4 | 0.16667 | 8.3 | 46.94 | 15.5094 |  | 46.94
2003-04-11 | 11 | 4 | 0.20833 | 8.3 | 46.94 | 15.3622 |  | 46.94
2003-04-11 | 11 | 4 | 0.25 | 7.8 | 46.04 | 15.149 | 46.04
2003-04-11 | 11 | 4 | 0.29167 | 8.3 | 46.94 | 15.5094 | 46.94
2003-04-11 | 11 | 4 | 0.33333 | 9.4 | 48.92 | 16.0005 | 48.92
2003-04-11 | 11 | 4 | 0.375 | 10.6 | 51.08 | 16.1932 | 51.08
2003-04-11 | 11 | 4 | 0.41667 | 12.2 | 53.96 | 16.6619 | 53.96
2003-04-11 | 11 | 4 | 0.45833 | 13.3 | 55.94 | 17.2135 | 55.94
2003-04-11 | 11 | 4 | 0.5 | 15 | 59 | 17.3618 | 59
2003-04-11 | 11 | 4 | 0.54167 | 16.7 | 62.06 | 18.0855 | 62.06
2003-04-11 | 11 | 4 | 0.58333 | 17.2 | 62.96 | 18.0089 | 62.96
2003-04-11 | 11 | 4 | 0.625 | 17.8 | 64.04 | 17.9695 | 64.04
2003-04-11 | 11 | 4 | 0.66667 | 18.3 | 64.94 | 18.1281 | 64.94
2003-04-11 | 11 | 4 | 0.70833 | 17.2 | 62.96 | 17.7443 | 62.96
2003-04-11 | 11 | 4 | 0.75 | 17.2 | 62.96 | 17.6122 | 62.96
2003-04-11 | 11 | 4 | 0.79167 | 16.7 | 62.06 | 18.5989 | 62.06
2003-04-11 | 11 | 4 | 0.83333 | 14.4 | 57.92 | 17.6423 | 57.92
2003-04-11 | 11 | 4 | 0.875 | 14.4 | 57.92 | 17.9744 | 57.92
2003-04-11 | 11 | 4 | 0.91667 | 12.8 | 55.04 | 17.8708 |  | 55.04
2003-04-11 | 11 | 4 | 0.95833 | 13.3 | 55.94 | 17.7287 |  | 55.94
2003-04-11 | 11 | 4 | 1 | 12.8 | 55.04 | 18.2705 |  | 55.04
2003-04-12 | 12 | 4 | 0.041667 | 12.2 | 53.96 | 18.0042 |  | 53.96
2003-04-12 | 12 | 4 | 0.083333 | 11.7 | 53.06 | 17.9 |  | 53.06
2003-04-12 | 12 | 4 | 0.125 | 10.6 | 51.08 | 17.8316 |  | 51.08
2003-04-12 | 12 | 4 | 0.16667 | 9.4 | 48.92 | 17.5919 |  | 48.92
2003-04-12 | 12 | 4 | 0.20833 | 10 | 50 | 17.4322 |  | 50
2003-04-12 | 12 | 4 | 0.25 | 10 | 50 | 17.4322 | 50
2003-04-12 | 12 | 4 | 0.29167 | 9.4 | 48.92 | 17.3527 | 48.92
2003-04-12 | 12 | 4 | 0.33333 | 10 | 50 | 17.4322 | 50
2003-04-12 | 12 | 4 | 0.375 | 10 | 50 | 19.0956 | 50
2003-04-12 | 12 | 4 | 0.41667 | 10.6 | 51.08 | 18.8704 | 51.08
2003-04-12 | 12 | 4 | 0.45833 | 9.4 | 48.92 | 17.8313 | 48.92
2003-04-12 | 12 | 4 | 0.5 | 8.9 | 48.02 | 17.8722 | 48.02
2003-04-12 | 12 | 4 | 0.54167 | 7.8 | 46.04 | 17.146 | 46.04
2003-04-12 | 12 | 4 | 0.58333 | 7.2 | 44.96 | 16.9115 | 44.96
2003-04-12 | 12 | 4 | 0.625 | 7.2 | 44.96 | 16.9115 | 44.96
2003-04-12 | 12 | 4 | 0.66667 | 7.8 | 46.04 | 17.146 | 46.04
2003-04-12 | 12 | 4 | 0.70833 | 7.8 | 46.04 | 17.146 | 46.04
2003-04-12 | 12 | 4 | 0.75 | 7.2 | 44.96 | 17.1175 | 44.96
2003-04-12 | 12 | 4 | 0.79167 | 6.7 | 44.06 | 16.8827 | 44.06
2003-04-12 | 12 | 4 | 0.83333 | 6.7 | 44.06 | 16.8827 | 44.06
2003-04-12 | 12 | 4 | 0.875 | 6.7 | 44.06 | 17.1481 | 44.06
2003-04-12 | 12 | 4 | 0.91667 | 6.7 | 44.06 | 17.1481 |  | 44.06
2003-04-12 | 12 | 4 | 0.95833 | 6.7 | 44.06 | 17.1481 |  | 44.06
2003-04-12 | 12 | 4 | 1 | 6.7 | 44.06 | 17.1481 |  | 44.06
2003-04-13 | 13 | 4 | 0.041667 | 6.7 | 44.06 | 17.1481 |  | 44.06
2003-04-13 | 13 | 4 | 0.083333 | 6.1 | 42.98 | 16.6172 |  | 42.98
2003-04-13 | 13 | 4 | 0.125 | 6.1 | 42.98 | 16.6172 |  | 42.98
2003-04-13 | 13 | 4 | 0.16667 | 6.1 | 42.98 | 16.6172 |  | 42.98
2003-04-13 | 13 | 4 | 0.20833 | 6.1 | 42.98 | 16.6172 |  | 42.98
2003-04-13 | 13 | 4 | 0.25 | 6.7 | 44.06 | 17.1481 | 44.06
2003-04-13 | 13 | 4 | 0.29167 | 6.7 | 44.06 | 17.1481 | 44.06
2003-04-13 | 13 | 4 | 0.33333 | 6.7 | 44.06 | 17.1481 | 44.06
2003-04-13 | 13 | 4 | 0.375 | 6.7 | 44.06 | 17.1481 | 44.06
2003-04-13 | 13 | 4 | 0.41667 | 7.2 | 44.96 | 17.5986 | 44.96
2003-04-13 | 13 | 4 | 0.45833 | 7.8 | 46.04 | 18.1489 | 46.04
2003-04-13 | 13 | 4 | 0.5 | 7.2 | 44.96 | 17.5986 | 44.96
2003-04-13 | 13 | 4 | 0.54167 | 7.2 | 44.96 | 17.5986 | 44.96
2003-04-13 | 13 | 4 | 0.58333 | 7.8 | 46.04 | 18.1489 | 46.04
2003-04-13 | 13 | 4 | 0.625 | 8.3 | 46.94 | 18.616 | 46.94
2003-04-13 | 13 | 4 | 0.66667 | 12.8 | 55.04 | 22.7994 | 55.04
2003-04-13 | 13 | 4 | 0.70833 | 13.9 | 57.02 | 23.68 | 57.02
2003-04-13 | 13 | 4 | 0.75 | 13.3 | 55.94 | 23.0282 | 55.94
2003-04-13 | 13 | 4 | 0.79167 | 12.8 | 55.04 | 22.4956 | 55.04
2003-04-13 | 13 | 4 | 0.83333 | 12.2 | 53.96 | 22.2577 | 53.96
2003-04-13 | 13 | 4 | 0.875 | 12.8 | 55.04 | 22.7994 | 55.04
2003-04-13 | 13 | 4 | 0.91667 | 12.2 | 53.96 | 22.2577 |  | 53.96
2003-04-13 | 13 | 4 | 0.95833 | 12.2 | 53.96 | 22.2577 |  | 53.96
2003-04-13 | 13 | 4 | 1 | 12.8 | 55.04 | 22.7994 |  | 55.04
2003-04-14 | 14 | 4 | 0.041667 | 12.2 | 53.96 | 22.2577 |  | 53.96
2003-04-14 | 14 | 4 | 0.083333 | 12.8 | 55.04 | 22.4956 |  | 55.04
2003-04-14 | 14 | 4 | 0.125 | 12.8 | 55.04 | 22.4956 |  | 55.04
2003-04-14 | 14 | 4 | 0.16667 | 12.8 | 55.04 | 22.0909 |  | 55.04
2003-04-14 | 14 | 4 | 0.20833 | 12.8 | 55.04 | 21.4848 |  | 55.04
2003-04-14 | 14 | 4 | 0.25 | 13.3 | 55.94 | 21.6695 | 55.94
2003-04-14 | 14 | 4 | 0.29167 | 14.4 | 57.92 | 20.7548 | 57.92
2003-04-14 | 14 | 4 | 0.33333 | 15.6 | 60.08 | 20.9909 | 60.08
2003-04-14 | 14 | 4 | 0.375 | 16.1 | 60.98 | 20.8023 | 60.98
2003-04-14 | 14 | 4 | 0.41667 | 16.7 | 62.06 | 20.2727 | 62.06
2003-04-14 | 14 | 4 | 0.45833 | 17.2 | 62.96 | 20.5321 | 62.96
2003-04-14 | 14 | 4 | 0.5 | 17.8 | 64.04 | 21.0049 | 64.04
2003-04-14 | 14 | 4 | 0.54167 | 18.9 | 66.02 | 21.7425 | 66.02
2003-04-14 | 14 | 4 | 0.58333 | 19.4 | 66.92 | 22.4565 | 66.92
2003-04-14 | 14 | 4 | 0.625 | 20 | 68 | 22.9637 | 68
2003-04-14 | 14 | 4 | 0.66667 | 20.6 | 69.08 | 22.982 | 69.08
2003-04-14 | 14 | 4 | 0.70833 | 21.7 | 71.06 | 23.3819 | 71.06
2003-04-14 | 14 | 4 | 0.75 | 19.4 | 66.92 | 22.9179 | 66.92
2003-04-14 | 14 | 4 | 0.79167 | 18.3 | 64.94 | 22.4081 | 64.94
2003-04-14 | 14 | 4 | 0.83333 | 17.2 | 62.96 | 22.2694 | 62.96
2003-04-14 | 14 | 4 | 0.875 | 16.7 | 62.06 | 22.8639 | 62.06
2003-04-14 | 14 | 4 | 0.91667 | 17.2 | 62.96 | 22.8057 |  | 62.96
2003-04-14 | 14 | 4 | 0.95833 | 16.7 | 62.06 | 22.8639 |  | 62.06
2003-04-14 | 14 | 4 | 1 | 14.4 | 57.92 | 21.6493 |  | 57.92
2003-04-15 | 15 | 4 | 0.041667 | 13.9 | 57.02 | 21.3973 |  | 57.02
2003-04-15 | 15 | 4 | 0.083333 | 11.7 | 53.06 | 20.1381 |  | 53.06
2003-04-15 | 15 | 4 | 0.125 | 10.6 | 51.08 | 19.391 |  | 51.08
2003-04-15 | 15 | 4 | 0.16667 | 9.4 | 48.92 | 19.1107 |  | 48.92
2003-04-15 | 15 | 4 | 0.20833 | 9.4 | 48.92 | 18.8704 |  | 48.92
2003-04-15 | 15 | 4 | 0.25 | 8.9 | 48.02 | 18.645 | 48.02
2003-04-15 | 15 | 4 | 0.29167 | 11.1 | 51.98 | 19.5842 | 51.98
2003-04-15 | 15 | 4 | 0.33333 | 11.7 | 53.06 | 19.5772 | 53.06
2003-04-15 | 15 | 4 | 0.375 | 13.9 | 57.02 | 21.0724 | 57.02
2003-04-15 | 15 | 4 | 0.41667 | 15.6 | 60.08 | 21.8365 | 60.08
2003-04-15 | 15 | 4 | 0.45833 | 18.3 | 64.94 | 23.2706 | 64.94
2003-04-15 | 15 | 4 | 0.5 | 18.3 | 64.94 | 23.2706 | 64.94
2003-04-15 | 15 | 4 | 0.54167 | 19.4 | 66.92 | 23.9971 | 66.92
2003-04-15 | 15 | 4 | 0.58333 | 23.9 | 75.02 | 25.4601 | 75.02
2003-04-15 | 15 | 4 | 0.625 | 23.3 | 73.94 | 25.1265 | 73.94
2003-04-15 | 15 | 4 | 0.66667 | 20 | 68 | 24.244 | 68
2003-04-15 | 15 | 4 | 0.70833 | 20.6 | 69.08 | 23.4795 | 69.08
2003-04-15 | 15 | 4 | 0.75 | 20 | 68 | 22.9637 | 68
2003-04-15 | 15 | 4 | 0.79167 | 19.4 | 66.92 | 22.4565 | 66.92
2003-04-15 | 15 | 4 | 0.83333 | 16.7 | 62.06 | 22.0845 | 62.06
2003-04-15 | 15 | 4 | 0.875 | 14.4 | 57.92 | 21.6493 | 57.92
2003-04-15 | 15 | 4 | 0.91667 | 14.4 | 57.92 | 21.3136 |  | 57.92
2003-04-15 | 15 | 4 | 0.95833 | 13.9 | 57.02 | 21.0724 |  | 57.02
2003-04-15 | 15 | 4 | 1 | 13.9 | 57.02 | 21.0724 |  | 57.02
2003-04-16 | 16 | 4 | 0.041667 | 14.4 | 57.92 | 21.6493 |  | 57.92
2003-04-16 | 16 | 4 | 0.083333 | 13.9 | 57.02 | 21.3973 |  | 57.02
2003-04-16 | 16 | 4 | 0.125 | 12.8 | 55.04 | 21.1822 |  | 55.04
2003-04-16 | 16 | 4 | 0.16667 | 12.2 | 53.96 | 21.1894 |  | 53.96
2003-04-16 | 16 | 4 | 0.20833 | 12.8 | 55.04 | 22.0909 |  | 55.04
2003-04-16 | 16 | 4 | 0.25 | 13.9 | 57.02 | 24.0074 | 57.02
2003-04-16 | 16 | 4 | 0.29167 | 13.9 | 57.02 | 24.0074 | 57.02
2003-04-16 | 16 | 4 | 0.33333 | 13.3 | 55.94 | 23.4473 | 55.94
2003-04-16 | 16 | 4 | 0.375 | 13.3 | 55.94 | 23.762 | 55.94
2003-04-16 | 16 | 4 | 0.41667 | 12.2 | 53.96 | 22.2577 | 53.96
2003-04-16 | 16 | 4 | 0.45833 | 11.7 | 53.06 | 20.9812 | 53.06
2003-04-16 | 16 | 4 | 0.5 | 12.8 | 55.04 | 21.1822 | 55.04
2003-04-16 | 16 | 4 | 0.54167 | 13.9 | 57.02 | 21.3973 | 57.02
2003-04-16 | 16 | 4 | 0.58333 | 15 | 59 | 21.5232 | 59
2003-04-16 | 16 | 4 | 0.625 | 16.7 | 62.06 | 21.048 | 62.06
2003-04-16 | 16 | 4 | 0.66667 | 18.9 | 66.02 | 20.5548 | 66.02
2003-04-16 | 16 | 4 | 0.70833 | 18.9 | 66.02 | 19.8145 | 66.02
2003-04-16 | 16 | 4 | 0.75 | 17.2 | 62.96 | 18.6711 | 62.96
2003-04-16 | 16 | 4 | 0.79167 | 16.7 | 62.06 | 18.3421 | 62.06
2003-04-16 | 16 | 4 | 0.83333 | 16.1 | 60.98 | 17.8281 | 60.98
2003-04-16 | 16 | 4 | 0.875 | 15.6 | 60.08 | 17.6294 | 60.08
2003-04-16 | 16 | 4 | 0.91667 | 15 | 59 | 17.7066 |  | 59
2003-04-16 | 16 | 4 | 0.95833 | 13.9 | 57.02 | 17.4121 |  | 57.02
2003-04-16 | 16 | 4 | 1 | 13.3 | 55.94 | 17.2135 |  | 55.94
2003-04-17 | 17 | 4 | 0.041667 | 12.8 | 55.04 | 17.2722 |  | 55.04
2003-04-17 | 17 | 4 | 0.083333 | 12.2 | 53.96 | 17.2365 |  | 53.96
2003-04-17 | 17 | 4 | 0.125 | 11.7 | 53.06 | 16.9718 |  | 53.06
2003-04-17 | 17 | 4 | 0.16667 | 11.1 | 51.98 | 16.9008 |  | 51.98
2003-04-17 | 17 | 4 | 0.20833 | 11.1 | 51.98 | 16.5446 |  | 51.98
2003-04-17 | 17 | 4 | 0.25 | 10 | 50 | 16.6035 | 50
2003-04-17 | 17 | 4 | 0.29167 | 11.7 | 53.06 | 17.1572 | 53.06
2003-04-17 | 17 | 4 | 0.33333 | 12.8 | 55.04 | 17.8708 | 55.04
2003-04-17 | 17 | 4 | 0.375 | 14.4 | 57.92 | 18.3069 | 57.92
2003-04-17 | 17 | 4 | 0.41667 | 14.4 | 57.92 | 17.4211 | 57.92
2003-04-17 | 17 | 4 | 0.45833 | 15.6 | 60.08 | 17.8684 | 60.08
2003-04-17 | 17 | 4 | 0.5 | 15.6 | 60.08 | 17.988 | 60.08
2003-04-17 | 17 | 4 | 0.54167 | 14.4 | 57.92 | 17.6423 | 57.92
2003-04-17 | 17 | 4 | 0.58333 | 14.4 | 57.92 | 17.9744 | 57.92
2003-04-17 | 17 | 4 | 0.625 | 16.1 | 60.98 | 18.1985 | 60.98
2003-04-17 | 17 | 4 | 0.66667 | 15 | 59 | 17.3618 | 59
2003-04-17 | 17 | 4 | 0.70833 | 16.7 | 62.06 | 18.4705 | 62.06
2003-04-17 | 17 | 4 | 0.75 | 15.6 | 60.08 | 17.6294 | 60.08
2003-04-17 | 17 | 4 | 0.79167 | 16.1 | 60.98 | 17.3349 | 60.98
2003-04-17 | 17 | 4 | 0.83333 | 15.6 | 60.08 | 17.0326 | 60.08
2003-04-17 | 17 | 4 | 0.875 | 16.1 | 60.98 | 16.9655 | 60.98
2003-04-17 | 17 | 4 | 0.91667 | 13.3 | 55.94 | 16.4936 |  | 55.94
2003-04-17 | 17 | 4 | 0.95833 | 12.2 | 53.96 | 15.8973 |  | 53.96
2003-04-17 | 17 | 4 | 1 | 12.2 | 53.96 | 15.6109 |  | 53.96
2003-04-18 | 18 | 4 | 0.041667 | 12.8 | 55.04 | 15.7802 |  | 55.04
2003-04-18 | 18 | 4 | 0.083333 | 11.1 | 51.98 | 15.3009 |  | 51.98
2003-04-18 | 18 | 4 | 0.125 | 11.1 | 51.98 | 14.9464 |  | 51.98
2003-04-18 | 18 | 4 | 0.16667 | 11.1 | 51.98 | 14.9464 |  | 51.98
2003-04-18 | 18 | 4 | 0.20833 | 11.1 | 51.98 | 14.7693 |  | 51.98
2003-04-18 | 18 | 4 | 0.25 | 11.1 | 51.98 | 14.7693 | 51.98
2003-04-18 | 18 | 4 | 0.29167 | 10.6 | 51.08 | 14.9053 | 51.08
2003-04-18 | 18 | 4 | 0.33333 | 12.2 | 53.96 | 15.2296 | 53.96
2003-04-18 | 18 | 4 | 0.375 | 12.8 | 55.04 | 15.2843 | 55.04
2003-04-18 | 18 | 4 | 0.41667 | 13.3 | 55.94 | 15.4679 | 55.94
2003-04-18 | 18 | 4 | 0.45833 | 14.4 | 57.92 | 15.9865 | 57.92
2003-04-18 | 18 | 4 | 0.5 | 16.1 | 60.98 | 16.5965 | 60.98
2003-04-18 | 18 | 4 | 0.54167 | 16.1 | 60.98 | 16.9655 | 60.98
2003-04-18 | 18 | 4 | 0.58333 | 17.2 | 62.96 | 17.6122 | 62.96
2003-04-18 | 18 | 4 | 0.625 | 17.8 | 64.04 | 17.8322 | 64.04
2003-04-18 | 18 | 4 | 0.66667 | 18.3 | 64.94 | 17.9863 | 64.94
2003-04-18 | 18 | 4 | 0.70833 | 18.9 | 66.02 | 18.0445 | 66.02
2003-04-18 | 18 | 4 | 0.75 | 18.9 | 66.02 | 17.8974 | 66.02
2003-04-18 | 18 | 4 | 0.79167 | 18.9 | 66.02 | 18.3389 | 66.02
2003-04-18 | 18 | 4 | 0.83333 | 17.8 | 64.04 | 17.9695 | 64.04
2003-04-18 | 18 | 4 | 0.875 | 17.2 | 62.96 | 17.7443 | 62.96
2003-04-18 | 18 | 4 | 0.91667 | 17.2 | 62.96 | 18.2736 |  | 62.96
2003-04-18 | 18 | 4 | 0.95833 | 16.7 | 62.06 | 18.5989 |  | 62.06
2003-04-18 | 18 | 4 | 1 | 16.7 | 62.06 | 18.8559 |  | 62.06
2003-04-19 | 19 | 4 | 0.041667 | 16.1 | 60.98 | 19.3119 |  | 60.98
2003-04-19 | 19 | 4 | 0.083333 | 13.9 | 57.02 | 19.9917 |  | 57.02
2003-04-19 | 19 | 4 | 0.125 | 12.8 | 55.04 | 20.5777 |  | 55.04
2003-04-19 | 19 | 4 | 0.16667 | 12.2 | 53.96 | 19.7379 |  | 53.96
2003-04-19 | 19 | 4 | 0.20833 | 11.7 | 53.06 | 20.1381 |  | 53.06
2003-04-19 | 19 | 4 | 0.25 | 11.1 | 51.98 | 19.8537 | 51.98
2003-04-19 | 19 | 4 | 0.29167 | 13.3 | 55.94 | 20.3162 | 55.94
2003-04-19 | 19 | 4 | 0.33333 | 16.7 | 62.06 | 22.0845 | 62.06
2003-04-19 | 19 | 4 | 0.375 | 20.6 | 69.08 | 23.9777 | 69.08
2003-04-19 | 19 | 4 | 0.41667 | 21.1 | 69.98 | 24.2588 | 69.98
2003-04-19 | 19 | 4 | 0.45833 | 24.4 | 75.92 | 25.6984 | 75.92
2003-04-19 | 19 | 4 | 0.5 | 26.1 | 78.98 | 26.3173 | 78.98
2003-04-19 | 19 | 4 | 0.54167 | 26.7 | 80.06 | 26.6069 | 80.06
2003-04-19 | 19 | 4 | 0.58333 | 27.2 | 80.96 | 26.8 | 80.96
2003-04-19 | 19 | 4 | 0.625 | 27.2 | 80.96 | 26.8 | 80.96
2003-04-19 | 19 | 4 | 0.66667 | 26.7 | 80.06 | 27.5724 | 80.06
2003-04-19 | 19 | 4 | 0.70833 | 23.3 | 73.94 | 26.1096 | 73.94
2003-04-19 | 19 | 4 | 0.75 | 20 | 68 | 26.6574 | 68
2003-04-19 | 19 | 4 | 0.79167 | 19.4 | 66.92 | 27.255 | 66.92
2003-04-19 | 19 | 4 | 0.83333 | 19.4 | 66.92 | 27.7229 | 66.92
2003-04-19 | 19 | 4 | 0.875 | 19.4 | 66.92 | 27.7229 | 66.92
2003-04-19 | 19 | 4 | 0.91667 | 19.4 | 66.92 | 27.7229 |  | 66.92
2003-04-19 | 19 | 4 | 0.95833 | 18.3 | 64.94 | 26.4517 |  | 64.94
2003-04-19 | 19 | 4 | 1 | 16.1 | 60.98 | 24.6826 |  | 60.98
2003-04-20 | 20 | 4 | 0.041667 | 15.6 | 60.08 | 23.0481 |  | 60.08
2003-04-20 | 20 | 4 | 0.083333 | 13.9 | 57.02 | 20.5316 |  | 57.02
2003-04-20 | 20 | 4 | 0.125 | 12.8 | 55.04 | 19.5727 |  | 55.04
2003-04-20 | 20 | 4 | 0.16667 | 12.2 | 53.96 | 20.8986 |  | 53.96
2003-04-20 | 20 | 4 | 0.20833 | 12.2 | 53.96 | 18.3887 |  | 53.96
2003-04-20 | 20 | 4 | 0.25 | 12.8 | 55.04 | 17.4716 | 55.04
2003-04-20 | 20 | 4 | 0.29167 | 12.2 | 53.96 | 17.6202 | 53.96
2003-04-20 | 20 | 4 | 0.33333 | 12.8 | 55.04 | 17.6711 | 55.04
2003-04-20 | 20 | 4 | 0.375 | 13.3 | 55.94 | 17.0077 | 55.94
2003-04-20 | 20 | 4 | 0.41667 | 13.9 | 57.02 | 16.5565 | 57.02
2003-04-20 | 20 | 4 | 0.45833 | 15 | 59 | 16.5585 | 59
2003-04-20 | 20 | 4 | 0.5 | 15.6 | 60.08 | 16.9134 | 60.08
2003-04-20 | 20 | 4 | 0.54167 | 15.6 | 60.08 | 16.4369 | 60.08
2003-04-20 | 20 | 4 | 0.58333 | 15.6 | 60.08 | 16.1989 | 60.08
2003-04-20 | 20 | 4 | 0.625 | 15 | 59 | 16.1003 | 59
2003-04-20 | 20 | 4 | 0.66667 | 15.6 | 60.08 | 16.08 | 60.08
2003-04-20 | 20 | 4 | 0.70833 | 16.1 | 60.98 | 16.3507 | 60.98
2003-04-20 | 20 | 4 | 0.75 | 15 | 59 | 16.3293 | 59
2003-04-20 | 20 | 4 | 0.79167 | 13.9 | 57.02 | 15.9162 | 57.02
2003-04-20 | 20 | 4 | 0.83333 | 13.3 | 55.94 | 15.7753 | 55.94
2003-04-20 | 20 | 4 | 0.875 | 12.8 | 55.04 | 15.3835 | 55.04
2003-04-20 | 20 | 4 | 0.91667 | 11.1 | 51.98 | 15.3009 |  | 51.98
2003-04-20 | 20 | 4 | 0.95833 | 11.1 | 51.98 | 14.7693 |  | 51.98
2003-04-20 | 20 | 4 | 1 | 10.6 | 51.08 | 14.9053 |  | 51.08
2003-04-21 | 21 | 4 | 0.041667 | 10 | 50 | 14.9522 |  | 50
2003-04-21 | 21 | 4 | 0.083333 | 10 | 50 | 15.117 |  | 50
2003-04-21 | 21 | 4 | 0.125 | 10 | 50 | 14.7052 |  | 50
2003-04-21 | 21 | 4 | 0.16667 | 9.4 | 48.92 | 14.1796 |  | 48.92
2003-04-21 | 21 | 4 | 0.20833 | 8.9 | 48.02 | 14.3397 |  | 48.02
2003-04-21 | 21 | 4 | 0.25 | 9.4 | 48.92 | 14.9701 | 48.92
2003-04-21 | 21 | 4 | 0.29167 | 10 | 50 | 15.3643 | 50
2003-04-21 | 21 | 4 | 0.33333 | 10 | 50 | 15.1994 | 50
2003-04-21 | 21 | 4 | 0.375 | 12.2 | 53.96 | 16.0883 | 53.96
2003-04-21 | 21 | 4 | 0.41667 | 13.3 | 55.94 | 16.3909 | 55.94
2003-04-21 | 21 | 4 | 0.45833 | 13.9 | 57.02 | 16.7702 | 57.02
2003-04-21 | 21 | 4 | 0.5 | 15 | 59 | 17.2469 | 59
2003-04-21 | 21 | 4 | 0.54167 | 16.7 | 62.06 | 18.0855 | 62.06
2003-04-21 | 21 | 4 | 0.58333 | 16.1 | 60.98 | 18.1985 | 60.98
2003-04-21 | 21 | 4 | 0.625 | 15 | 59 | 18.0518 | 59
2003-04-21 | 21 | 4 | 0.66667 | 15 | 59 | 17.9367 | 59
2003-04-21 | 21 | 4 | 0.70833 | 14.4 | 57.92 | 17.3105 | 57.92
2003-04-21 | 21 | 4 | 0.75 | 13.3 | 55.94 | 16.2882 | 55.94
2003-04-21 | 21 | 4 | 0.79167 | 12.2 | 53.96 | 16.0883 | 53.96
2003-04-21 | 21 | 4 | 0.83333 | 11.7 | 53.06 | 15.6765 | 53.06
2003-04-21 | 21 | 4 | 0.875 | 11.1 | 51.98 | 16.5446 | 51.98
2003-04-21 | 21 | 4 | 0.91667 | 11.1 | 51.98 | 16.011 |  | 51.98
2003-04-21 | 21 | 4 | 0.95833 | 10 | 50 | 14.9522 |  | 50
2003-04-21 | 21 | 4 | 1 | 9.4 | 48.92 | 14.6537 |  | 48.92
2003-04-22 | 22 | 4 | 0.041667 | 8.3 | 46.94 | 14.3333 |  | 46.94
2003-04-22 | 22 | 4 | 0.083333 | 7.8 | 46.04 | 14.2968 |  | 46.04
2003-04-22 | 22 | 4 | 0.125 | 7.2 | 44.96 | 14.0412 |  | 44.96
2003-04-22 | 22 | 4 | 0.16667 | 6.7 | 44.06 | 14.3057 |  | 44.06
2003-04-22 | 22 | 4 | 0.20833 | 7.2 | 44.96 | 14.0412 |  | 44.96
2003-04-22 | 22 | 4 | 0.25 | 7.8 | 46.04 | 13.8715 | 46.04
2003-04-22 | 22 | 4 | 0.29167 | 8.3 | 46.94 | 14.1133 | 46.94
2003-04-22 | 22 | 4 | 0.33333 | 9.4 | 48.92 | 14.5746 | 48.92
2003-04-22 | 22 | 4 | 0.375 | 10 | 50 | 14.7875 | 50
2003-04-22 | 22 | 4 | 0.41667 | 10.6 | 51.08 | 14.734 | 51.08
2003-04-22 | 22 | 4 | 0.45833 | 11.1 | 51.98 | 14.6808 | 51.98
2003-04-22 | 22 | 4 | 0.5 | 12.2 | 53.96 | 15.1343 | 53.96
2003-04-22 | 22 | 4 | 0.54167 | 13.3 | 55.94 | 15.7753 | 55.94
2003-04-22 | 22 | 4 | 0.58333 | 13.9 | 57.02 | 15.5966 | 57.02
2003-04-22 | 22 | 4 | 0.625 | 13.9 | 57.02 | 15.9162 | 57.02
2003-04-22 | 22 | 4 | 0.66667 | 13.9 | 57.02 | 15.7031 | 57.02
2003-04-22 | 22 | 4 | 0.70833 | 13.9 | 57.02 | 15.7031 | 57.02
2003-04-22 | 22 | 4 | 0.75 | 13.3 | 55.94 | 15.2631 | 55.94
2003-04-22 | 22 | 4 | 0.79167 | 12.2 | 53.96 | 15.0391 | 53.96
2003-04-22 | 22 | 4 | 0.83333 | 11.7 | 53.06 | 15.2151 | 53.06
2003-04-22 | 22 | 4 | 0.875 | 11.1 | 51.98 | 14.6808 | 51.98
2003-04-22 | 22 | 4 | 0.91667 | 10.6 | 51.08 | 14.306 |  | 51.08
2003-04-22 | 22 | 4 | 0.95833 | 10 | 50 | 14.2939 |  | 50
2003-04-22 | 22 | 4 | 1 | 9.4 | 48.92 | 14.0218 |  | 48.92
2003-04-23 | 23 | 4 | 0.041667 | 8.9 | 48.02 | 14.0342 |  | 48.02
2003-04-23 | 23 | 4 | 0.083333 | 8.3 | 46.94 | 13.6736 |  | 46.94
2003-04-23 | 23 | 4 | 0.125 | 7.8 | 46.04 | 13.7298 |  | 46.04
2003-04-23 | 23 | 4 | 0.16667 | 7.8 | 46.04 | 13.8715 |  | 46.04
2003-04-23 | 23 | 4 | 0.20833 | 7.8 | 46.04 | 13.7298 |  | 46.04
2003-04-23 | 23 | 4 | 0.25 | 7.2 | 44.96 | 13.3614 | 44.96
2003-04-23 | 23 | 4 | 0.29167 | 8.3 | 46.94 | 13.6736 | 46.94
2003-04-23 | 23 | 4 | 0.33333 | 9.4 | 48.92 | 14.1796 | 48.92
2003-04-23 | 23 | 4 | 0.375 | 10 | 50 | 14.2939 | 50
2003-04-23 | 23 | 4 | 0.41667 | 12.2 | 53.96 | 15.1343 | 53.96
2003-04-23 | 23 | 4 | 0.45833 | 13.3 | 55.94 | 15.7753 | 55.94
2003-04-23 | 23 | 4 | 0.5 | 13.9 | 57.02 | 15.9162 | 57.02
2003-04-23 | 23 | 4 | 0.54167 | 15.6 | 60.08 | 16.7942 | 60.08
2003-04-23 | 23 | 4 | 0.58333 | 15.6 | 60.08 | 16.7942 | 60.08
2003-04-23 | 23 | 4 | 0.625 | 15.6 | 60.08 | 17.1519 | 60.08
2003-04-23 | 23 | 4 | 0.66667 | 13.9 | 57.02 | 16.7702 | 57.02
2003-04-23 | 23 | 4 | 0.70833 | 13.3 | 55.94 | 16.6992 | 55.94
2003-04-23 | 23 | 4 | 0.75 | 11.7 | 53.06 | 16.9718 | 53.06
2003-04-23 | 23 | 4 | 0.79167 | 11.1 | 51.98 | 17.525 | 51.98
2003-04-23 | 23 | 4 | 0.83333 | 11.7 | 53.06 | 18.179 | 53.06
2003-04-23 | 23 | 4 | 0.875 | 11.7 | 53.06 | 17.9 | 53.06
2003-04-23 | 23 | 4 | 0.91667 | 11.7 | 53.06 | 17.3428 |  | 53.06
2003-04-23 | 23 | 4 | 0.95833 | 12.2 | 53.96 | 17.4283 |  | 53.96
2003-04-23 | 23 | 4 | 1 | 11.7 | 53.06 | 17.1572 |  | 53.06
2003-04-24 | 24 | 4 | 0.041667 | 11.7 | 53.06 | 17.1572 |  | 53.06
2003-04-24 | 24 | 4 | 0.083333 | 11.7 | 53.06 | 17.5284 |  | 53.06
2003-04-24 | 24 | 4 | 0.125 | 11.7 | 53.06 | 17.7141 |  | 53.06
2003-04-24 | 24 | 4 | 0.16667 | 11.1 | 51.98 | 17.7036 |  | 51.98
2003-04-24 | 24 | 4 | 0.20833 | 10.6 | 51.08 | 17.8316 |  | 51.08
2003-04-24 | 24 | 4 | 0.25 | 10.6 | 51.08 | 17.8316 | 51.08
2003-04-24 | 24 | 4 | 0.29167 | 12.2 | 53.96 | 18.7737 | 53.96
2003-04-24 | 24 | 4 | 0.33333 | 13.9 | 57.02 | 19.345 | 57.02
2003-04-24 | 24 | 4 | 0.375 | 16.7 | 62.06 | 20.1436 | 62.06
2003-04-24 | 24 | 4 | 0.41667 | 18.9 | 66.02 | 20.8513 | 66.02
2003-04-24 | 24 | 4 | 0.45833 | 21.1 | 69.98 | 21.5258 | 69.98
2003-04-24 | 24 | 4 | 0.5 | 23.3 | 73.94 | 21.6104 | 73.94
2003-04-24 | 24 | 4 | 0.54167 | 23.9 | 75.02 | 21.8129 | 75.02
2003-04-24 | 24 | 4 | 0.58333 | 25 | 77 | 22.3366 | 77
2003-04-24 | 24 | 4 | 0.625 | 26.1 | 78.98 | 23.3073 | 78.98
2003-04-24 | 24 | 4 | 0.66667 | 26.1 | 78.98 | 23.3073 | 78.98
2003-04-24 | 24 | 4 | 0.70833 | 26.7 | 80.06 | 23.4874 | 80.06
2003-04-24 | 24 | 4 | 0.75 | 25.6 | 78.08 | 23.6336 | 78.08
2003-04-24 | 24 | 4 | 0.79167 | 23.9 | 75.02 | 22.8221 | 75.02
2003-04-24 | 24 | 4 | 0.83333 | 23.3 | 73.94 | 22.5835 | 73.94
2003-04-24 | 24 | 4 | 0.875 | 22.8 | 73.04 | 22.2206 | 73.04
2003-04-24 | 24 | 4 | 0.91667 | 22.8 | 73.04 | 22.4096 |  | 73.04
2003-04-24 | 24 | 4 | 0.95833 | 22.2 | 71.96 | 22.3368 |  | 71.96
2003-04-24 | 24 | 4 | 1 | 21.7 | 71.06 | 22.1424 |  | 71.06
2003-04-25 | 25 | 4 | 0.041667 | 22.8 | 73.04 | 22.5987 |  | 73.04
2003-04-25 | 25 | 4 | 0.083333 | 22.2 | 71.96 | 22.3368 |  | 71.96
2003-04-25 | 25 | 4 | 0.125 | 20.6 | 69.08 | 21.8239 |  | 69.08
2003-04-25 | 25 | 4 | 0.16667 | 18.3 | 64.94 | 20.9755 |  | 64.94
2003-04-25 | 25 | 4 | 0.20833 | 18.9 | 66.02 | 21.2966 |  | 66.02
2003-04-25 | 25 | 4 | 0.25 | 19.4 | 66.92 | 21.5354 | 66.92
2003-04-25 | 25 | 4 | 0.29167 | 19.4 | 66.92 | 21.9956 | 66.92
2003-04-25 | 25 | 4 | 0.33333 | 22.2 | 71.96 | 23.2495 | 71.96
2003-04-25 | 25 | 4 | 0.375 | 23.9 | 75.02 | 23.6316 | 75.02
2003-04-25 | 25 | 4 | 0.41667 | 21.7 | 71.06 | 23.9146 | 71.06
2003-04-25 | 25 | 4 | 0.45833 | 23.3 | 73.94 | 24.1462 | 73.94
2003-04-25 | 25 | 4 | 0.5 | 12.8 | 55.04 | 20.0748 | 55.04
2003-04-25 | 25 | 4 | 0.54167 | 12.2 | 53.96 | 20.0277 | 53.96
2003-04-25 | 25 | 4 | 0.58333 | 12.8 | 55.04 | 20.3765 | 55.04
2003-04-25 | 25 | 4 | 0.625 | 13.9 | 57.02 | 21.0724 | 57.02
2003-04-25 | 25 | 4 | 0.66667 | 11.1 | 51.98 | 19.5842 | 51.98
2003-04-25 | 25 | 4 | 0.70833 | 11.1 | 51.98 | 19.5842 | 51.98
2003-04-25 | 25 | 4 | 0.75 | 12.8 | 55.04 | 20.0748 | 55.04
2003-04-25 | 25 | 4 | 0.79167 | 12.2 | 53.96 | 19.5448 | 53.96
2003-04-25 | 25 | 4 | 0.83333 | 11.7 | 53.06 | 19.2971 | 53.06
2003-04-25 | 25 | 4 | 0.875 | 10.6 | 51.08 | 18.8704 | 51.08
2003-04-25 | 25 | 4 | 0.91667 | 10 | 50 | 18.3461 |  | 50
2003-04-25 | 25 | 4 | 0.95833 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-25 | 25 | 4 | 1 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-26 | 26 | 4 | 0.041667 | 8.3 | 46.94 | 17.5773 |  | 46.94
2003-04-26 | 26 | 4 | 0.083333 | 8.9 | 48.02 | 18.1039 |  | 48.02
2003-04-26 | 26 | 4 | 0.125 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-26 | 26 | 4 | 0.16667 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-26 | 26 | 4 | 0.20833 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-26 | 26 | 4 | 0.25 | 7.8 | 46.04 | 17.8621 | 46.04
2003-04-26 | 26 | 4 | 0.29167 | 7.8 | 46.04 | 18.1489 | 46.04
2003-04-26 | 26 | 4 | 0.33333 | 7.8 | 46.04 | 18.1489 | 46.04
2003-04-26 | 26 | 4 | 0.375 | 8.9 | 48.02 | 18.8772 | 48.02
2003-04-26 | 26 | 4 | 0.41667 | 8.3 | 46.94 | 18.3932 | 46.94
2003-04-26 | 26 | 4 | 0.45833 | 8.9 | 48.02 | 18.645 | 48.02
2003-04-26 | 26 | 4 | 0.5 | 9.4 | 48.92 | 18.8704 | 48.92
2003-04-26 | 26 | 4 | 0.54167 | 10 | 50 | 19.0956 | 50
2003-04-26 | 26 | 4 | 0.58333 | 10.6 | 51.08 | 19.391 | 51.08
2003-04-26 | 26 | 4 | 0.625 | 10.6 | 51.08 | 19.391 | 51.08
2003-04-26 | 26 | 4 | 0.66667 | 10.6 | 51.08 | 19.6516 | 51.08
2003-04-26 | 26 | 4 | 0.70833 | 11.7 | 53.06 | 20.4189 | 53.06
2003-04-26 | 26 | 4 | 0.75 | 11.1 | 51.98 | 20.1234 | 51.98
2003-04-26 | 26 | 4 | 0.79167 | 10 | 50 | 19.0956 | 50
2003-04-26 | 26 | 4 | 0.83333 | 8.9 | 48.02 | 18.645 | 48.02
2003-04-26 | 26 | 4 | 0.875 | 8.9 | 48.02 | 18.645 | 48.02
2003-04-26 | 26 | 4 | 0.91667 | 9.4 | 48.92 | 18.8704 |  | 48.92
2003-04-26 | 26 | 4 | 0.95833 | 8.9 | 48.02 | 18.645 |  | 48.02
2003-04-26 | 26 | 4 | 1 | 8.3 | 46.94 | 18.616 |  | 46.94
2003-04-27 | 27 | 4 | 0.041667 | 8.3 | 46.94 | 18.616 |  | 46.94
2003-04-27 | 27 | 4 | 0.083333 | 8.9 | 48.02 | 19.1871 |  | 48.02
2003-04-27 | 27 | 4 | 0.125 | 10 | 50 | 19.9304 |  | 50
2003-04-27 | 27 | 4 | 0.16667 | 10 | 50 | 19.9304 |  | 50
2003-04-27 | 27 | 4 | 0.20833 | 9.4 | 48.92 | 19.4313 |  | 48.92
2003-04-27 | 27 | 4 | 0.25 | 9.4 | 48.92 | 19.4313 | 48.92
2003-04-27 | 27 | 4 | 0.29167 | 11.1 | 51.98 | 20.3933 | 51.98
2003-04-27 | 27 | 4 | 0.33333 | 12.2 | 53.96 | 21.1894 | 53.96
2003-04-27 | 27 | 4 | 0.375 | 13.9 | 57.02 | 21.614 | 57.02
2003-04-27 | 27 | 4 | 0.41667 | 17.2 | 62.96 | 23.7463 | 62.96
2003-04-27 | 27 | 4 | 0.45833 | 21.7 | 71.06 | 26.4111 | 71.06
2003-04-27 | 27 | 4 | 0.5 | 24.4 | 75.92 | 28.2276 | 75.92
2003-04-27 | 27 | 4 | 0.54167 | 26.7 | 80.06 | 29.7549 | 80.06
2003-04-27 | 27 | 4 | 0.58333 | 23.9 | 75.02 | 28.3237 | 75.02
2003-04-27 | 27 | 4 | 0.625 | 25.6 | 78.08 | 29.5092 | 78.08
2003-04-27 | 27 | 4 | 0.66667 | 26.7 | 80.06 | 30.4854 | 80.06
2003-04-27 | 27 | 4 | 0.70833 | 22.2 | 71.96 | 32.6996 | 71.96
2003-04-27 | 27 | 4 | 0.75 | 25 | 77 | 32.8375 | 77
2003-04-27 | 27 | 4 | 0.79167 | 22.8 | 73.04 | 32.5774 | 73.04
2003-04-27 | 27 | 4 | 0.83333 | 21.7 | 71.06 | 31.096 | 71.06
2003-04-27 | 27 | 4 | 0.875 | 22.2 | 71.96 | 30.6394 | 71.96
2003-04-27 | 27 | 4 | 0.91667 | 22.2 | 71.96 | 30.2661 |  | 71.96
2003-04-27 | 27 | 4 | 0.95833 | 22.2 | 71.96 | 30.2661 |  | 71.96
2003-04-27 | 27 | 4 | 1 | 21.7 | 71.06 | 30.0092 |  | 71.06
2003-04-28 | 28 | 4 | 0.041667 | 20.6 | 69.08 | 28.1581 |  | 69.08
2003-04-28 | 28 | 4 | 0.083333 | 19.4 | 66.92 | 25.0796 |  | 66.92
2003-04-28 | 28 | 4 | 0.125 | 18.3 | 64.94 | 23.2706 |  | 64.94
2003-04-28 | 28 | 4 | 0.16667 | 17.2 | 62.96 | 22.2694 |  | 62.96
2003-04-28 | 28 | 4 | 0.20833 | 15.6 | 60.08 | 20.9909 |  | 60.08
2003-04-28 | 28 | 4 | 0.25 | 15 | 59 | 20.4781 | 59
2003-04-28 | 28 | 4 | 0.29167 | 14.4 | 57.92 | 19.974 | 57.92
2003-04-28 | 28 | 4 | 0.33333 | 15 | 59 | 20.4781 | 59
2003-04-28 | 28 | 4 | 0.375 | 16.7 | 62.06 | 21.3068 | 62.06
2003-04-28 | 28 | 4 | 0.41667 | 18.3 | 64.94 | 22.2646 | 64.94
2003-04-28 | 28 | 4 | 0.45833 | 18.9 | 66.02 | 22.487 | 66.02
2003-04-28 | 28 | 4 | 0.5 | 20 | 68 | 22.9637 | 68
2003-04-28 | 28 | 4 | 0.54167 | 21.7 | 71.06 | 23.7369 | 71.06
2003-04-28 | 28 | 4 | 0.58333 | 21.7 | 71.06 | 23.7369 | 71.06
2003-04-28 | 28 | 4 | 0.625 | 21.1 | 69.98 | 22.8896 | 69.98
2003-04-28 | 28 | 4 | 0.66667 | 21.1 | 69.98 | 22.3776 | 69.98
2003-04-28 | 28 | 4 | 0.70833 | 21.7 | 71.06 | 21.789 | 71.06
2003-04-28 | 28 | 4 | 0.75 | 21.1 | 69.98 | 21.1858 | 69.98
2003-04-28 | 28 | 4 | 0.79167 | 18.3 | 64.94 | 22.2646 | 64.94
2003-04-28 | 28 | 4 | 0.83333 | 17.8 | 64.04 | 21.9765 | 64.04
2003-04-28 | 28 | 4 | 0.875 | 13.9 | 57.02 | 21.3973 | 57.02
2003-04-28 | 28 | 4 | 0.91667 | 12.8 | 55.04 | 20.5777 |  | 55.04
2003-04-28 | 28 | 4 | 0.95833 | 12.2 | 53.96 | 20.0277 |  | 53.96
2003-04-28 | 28 | 4 | 1 | 11.1 | 51.98 | 19.3149 |  | 51.98
2003-04-29 | 29 | 4 | 0.041667 | 10.6 | 51.08 | 19.0439 |  | 51.08
2003-04-29 | 29 | 4 | 0.083333 | 10 | 50 | 18.8456 |  | 50
2003-04-29 | 29 | 4 | 0.125 | 9.4 | 48.92 | 18.5503 |  | 48.92
2003-04-29 | 29 | 4 | 0.16667 | 9.4 | 48.92 | 18.3105 |  | 48.92
2003-04-29 | 29 | 4 | 0.20833 | 8.9 | 48.02 | 18.3357 |  | 48.02
2003-04-29 | 29 | 4 | 0.25 | 9.4 | 48.92 | 18.3105 | 48.92
2003-04-29 | 29 | 4 | 0.29167 | 9.4 | 48.92 | 18.5503 | 48.92
2003-04-29 | 29 | 4 | 0.33333 | 9.4 | 48.92 | 18.0708 | 48.92
2003-04-29 | 29 | 4 | 0.375 | 10.6 | 51.08 | 18.6104 | 51.08
2003-04-29 | 29 | 4 | 0.41667 | 11.7 | 53.06 | 19.0172 | 53.06
2003-04-29 | 29 | 4 | 0.45833 | 10.6 | 51.08 | 18.8704 | 51.08
2003-04-29 | 29 | 4 | 0.5 | 11.1 | 51.98 | 18.7769 | 51.98
2003-04-29 | 29 | 4 | 0.54167 | 10.6 | 51.08 | 19.0439 | 51.08
2003-04-29 | 29 | 4 | 0.58333 | 11.1 | 51.98 | 19.8537 | 51.98
2003-04-29 | 29 | 4 | 0.625 | 13.9 | 57.02 | 21.9394 | 57.02
2003-04-29 | 29 | 4 | 0.66667 | 11.7 | 53.06 | 20.4189 | 53.06
2003-04-29 | 29 | 4 | 0.70833 | 11.1 | 51.98 | 19.8537 | 51.98
2003-04-29 | 29 | 4 | 0.75 | 11.7 | 53.06 | 20.4189 | 53.06
2003-04-29 | 29 | 4 | 0.79167 | 11.7 | 53.06 | 20.9812 | 53.06
2003-04-29 | 29 | 4 | 0.83333 | 12.2 | 53.96 | 21.8688 | 53.96
2003-04-29 | 29 | 4 | 0.875 | 12.2 | 53.96 | 21.8688 | 53.96
2003-04-29 | 29 | 4 | 0.91667 | 11.1 | 51.98 | 20.7536 |  | 51.98
2003-04-29 | 29 | 4 | 0.95833 | 11.7 | 53.06 | 21.6384 |  | 53.06
2003-04-29 | 29 | 4 | 1 | 12.8 | 55.04 | 22.4956 |  | 55.04
2003-04-30 | 30 | 4 | 0.041667 | 12.2 | 53.96 | 21.8688 |  | 53.96
2003-04-30 | 30 | 4 | 0.083333 | 12.8 | 55.04 | 22.4956 |  | 55.04
2003-04-30 | 30 | 4 | 0.125 | 14.4 | 57.92 | 24.6857 |  | 57.92
2003-04-30 | 30 | 4 | 0.16667 | 15.6 | 60.08 | 25.6064 |  | 60.08
2003-04-30 | 30 | 4 | 0.20833 | 13.9 | 57.02 | 23.68 |  | 57.02
2003-04-30 | 30 | 4 | 0.25 | 15 | 59 | 24.9127 | 59
2003-04-30 | 30 | 4 | 0.29167 | 16.1 | 60.98 | 25.8174 | 60.98
2003-04-30 | 30 | 4 | 0.33333 | 17.8 | 64.04 | 26.4531 | 64.04
2003-04-30 | 30 | 4 | 0.375 | 19.4 | 66.92 | 25.3896 | 66.92
2003-04-30 | 30 | 4 | 0.41667 | 20 | 68 | 26.3346 | 68
2003-04-30 | 30 | 4 | 0.45833 | 21.7 | 71.06 | 26.7692 | 71.06
2003-04-30 | 30 | 4 | 0.5 | 22.2 | 71.96 | 27.2943 | 71.96
2003-04-30 | 30 | 4 | 0.54167 | 25.6 | 78.08 | 28.3715 | 78.08
2003-04-30 | 30 | 4 | 0.58333 | 26.1 | 78.98 | 27.7154 | 78.98
2003-04-30 | 30 | 4 | 0.625 | 25 | 77 | 28.8622 | 77
2003-04-30 | 30 | 4 | 0.66667 | 23.9 | 75.02 | 29.1463 | 75.02
2003-04-30 | 30 | 4 | 0.70833 | 21.7 | 71.06 | 28.2055 | 71.06
2003-04-30 | 30 | 4 | 0.75 | 20.6 | 69.08 | 26.6473 | 69.08
2003-04-30 | 30 | 4 | 0.79167 | 19.4 | 66.92 | 26.4765 | 66.92
2003-04-30 | 30 | 4 | 0.83333 | 18.3 | 64.94 | 26.4517 | 64.94
2003-04-30 | 30 | 4 | 0.875 | 17.8 | 64.04 | 27.4402 | 64.04
2003-04-30 | 30 | 4 | 0.91667 | 17.5 | 63.5 | 27.4933 |  | 63.5
2003-04-30 | 30 | 4 | 0.95833 | 17.2 | 62.96 | 27.5346 |  | 62.96
2003-04-30 | 30 | 4 | 1 | 16.9 | 62.42 | 26.7643 |  | 62.42
1985-05-01 | 1 | 5 | 0.041667 | 16.5 | 61.7 | 26.6767 |  | 61.7
1985-05-01 | 1 | 5 | 0.083333 | 16.2 | 61.16 | 26.698 |  | 61.16
1985-05-01 | 1 | 5 | 0.125 | 15.9 | 60.62 | 25.9592 |  | 60.62
1985-05-01 | 1 | 5 | 0.16667 | 15.6 | 60.08 | 25.6064 |  | 60.08
1985-05-01 | 1 | 5 | 0.20833 | 15.6 | 60.08 | 25.2398 |  | 60.08
1985-05-01 | 1 | 5 | 0.25 | 15.6 | 60.08 | 25.2398 | 60.08
1985-05-01 | 1 | 5 | 0.29167 | 16.1 | 60.98 | 25.4387 | 60.98
1985-05-01 | 1 | 5 | 0.33333 | 17.8 | 64.04 | 26.4531 | 64.04
1985-05-01 | 1 | 5 | 0.375 | 17.8 | 64.04 | 27.0168 | 64.04
1985-05-01 | 1 | 5 | 0.41667 | 19.4 | 66.92 | 28.1915 | 66.92
1985-05-01 | 1 | 5 | 0.45833 | 19.4 | 66.92 | 27.255 | 66.92
1985-05-01 | 1 | 5 | 0.5 | 20 | 68 | 26.6574 | 68
1985-05-01 | 1 | 5 | 0.54167 | 18.3 | 64.94 | 26.7424 | 64.94
1985-05-01 | 1 | 5 | 0.58333 | 21.7 | 71.06 | 28.2055 | 71.06
1985-05-01 | 1 | 5 | 0.625 | 23.3 | 73.94 | 28.4806 | 73.94
1985-05-01 | 1 | 5 | 0.66667 | 22.8 | 73.04 | 27.552 | 73.04
1985-05-01 | 1 | 5 | 0.70833 | 23.9 | 75.02 | 25.6638 | 75.02
1985-05-01 | 1 | 5 | 0.75 | 21.1 | 69.98 | 23.4024 | 69.98
1985-05-01 | 1 | 5 | 0.79167 | 18.3 | 64.94 | 21.4046 | 64.94
1985-05-01 | 1 | 5 | 0.83333 | 15.6 | 60.08 | 20.5087 | 60.08
1985-05-01 | 1 | 5 | 0.875 | 14.4 | 57.92 | 19.3062 | 57.92
1985-05-01 | 1 | 5 | 0.91667 | 13.3 | 55.94 | 17.8318 |  | 55.94
1985-05-01 | 1 | 5 | 0.95833 | 12.2 | 53.96 | 17.6202 |  | 53.96
1985-05-01 | 1 | 5 | 1 | 10.6 | 51.08 | 16.7097 |  | 51.08
1985-05-02 | 2 | 5 | 0.041667 | 10 | 50 | 16.1073 |  | 50
1985-05-02 | 2 | 5 | 0.083333 | 9.4 | 48.92 | 15.8418 |  | 48.92
1985-05-02 | 2 | 5 | 0.125 | 8.9 | 48.02 | 15.4109 |  | 48.02
1985-05-02 | 2 | 5 | 0.16667 | 8.3 | 46.94 | 15.1414 |  | 46.94
1985-05-02 | 2 | 5 | 0.20833 | 8.3 | 46.94 | 15.3622 |  | 46.94
1985-05-02 | 2 | 5 | 0.25 | 8.3 | 46.94 | 14.7739 | 46.94
1985-05-02 | 2 | 5 | 0.29167 | 8.9 | 48.02 | 15.1045 | 48.02
1985-05-02 | 2 | 5 | 0.33333 | 9.4 | 48.92 | 15.2868 | 48.92
1985-05-02 | 2 | 5 | 0.375 | 11.1 | 51.98 | 16.1888 | 51.98
1985-05-02 | 2 | 5 | 0.41667 | 11.7 | 53.06 | 16.6012 | 53.06
1985-05-02 | 2 | 5 | 0.45833 | 12.8 | 55.04 | 17.2722 | 55.04
1985-05-02 | 2 | 5 | 0.5 | 13.9 | 57.02 | 17.6263 | 57.02
1985-05-02 | 2 | 5 | 0.54167 | 15 | 59 | 17.9367 | 59
1985-05-02 | 2 | 5 | 0.58333 | 15.6 | 60.08 | 17.8684 | 60.08
1985-05-02 | 2 | 5 | 0.625 | 16.1 | 60.98 | 17.7047 | 60.98
1985-05-02 | 2 | 5 | 0.66667 | 16.7 | 62.06 | 18.0855 | 62.06
1985-05-02 | 2 | 5 | 0.70833 | 16.1 | 60.98 | 17.8281 | 60.98
1985-05-02 | 2 | 5 | 0.75 | 15.6 | 60.08 | 17.6294 | 60.08
1985-05-02 | 2 | 5 | 0.79167 | 15 | 59 | 17.7066 | 59
1985-05-02 | 2 | 5 | 0.83333 | 14.4 | 57.92 | 17.4211 | 57.92
1985-05-02 | 2 | 5 | 0.875 | 13.9 | 57.02 | 17.4121 | 57.02
1985-05-02 | 2 | 5 | 0.91667 | 12.8 | 55.04 | 17.2722 |  | 55.04
1985-05-02 | 2 | 5 | 0.95833 | 12.2 | 53.96 | 17.0449 |  | 53.96
1985-05-02 | 2 | 5 | 1 | 11.7 | 53.06 | 16.5086 |  | 53.06
1985-05-03 | 3 | 5 | 0.041667 | 11.1 | 51.98 | 16.5446 |  | 51.98
1985-05-03 | 3 | 5 | 0.083333 | 10.6 | 51.08 | 16.0212 |  | 51.08
1985-05-03 | 3 | 5 | 0.125 | 10 | 50 | 15.8594 |  | 50
1985-05-03 | 3 | 5 | 0.16667 | 10 | 50 | 15.5292 |  | 50
1985-05-03 | 3 | 5 | 0.20833 | 9.4 | 48.92 | 15.2868 |  | 48.92
1985-05-03 | 3 | 5 | 0.25 | 10 | 50 | 15.3643 | 50
1985-05-03 | 3 | 5 | 0.29167 | 11.1 | 51.98 | 15.9222 | 51.98
1985-05-03 | 3 | 5 | 0.33333 | 12.2 | 53.96 | 16.1838 | 53.96
1985-05-03 | 3 | 5 | 0.375 | 12.8 | 55.04 | 16.4756 | 55.04
1985-05-03 | 3 | 5 | 0.41667 | 14.4 | 57.92 | 16.7582 | 57.92
1985-05-03 | 3 | 5 | 0.45833 | 15 | 59 | 17.1321 | 59
1985-05-03 | 3 | 5 | 0.5 | 15.6 | 60.08 | 17.2712 | 60.08
1985-05-03 | 3 | 5 | 0.54167 | 16.1 | 60.98 | 17.4582 | 60.98
1985-05-03 | 3 | 5 | 0.58333 | 17.2 | 62.96 | 17.7443 | 62.96
1985-05-03 | 3 | 5 | 0.625 | 17.2 | 62.96 | 18.406 | 62.96
1985-05-03 | 3 | 5 | 0.66667 | 16.7 | 62.06 | 18.4705 | 62.06
1985-05-03 | 3 | 5 | 0.70833 | 15 | 59 | 18.0518 | 59
1985-05-03 | 3 | 5 | 0.75 | 13.9 | 57.02 | 17.198 | 57.02
1985-05-03 | 3 | 5 | 0.79167 | 13.9 | 57.02 | 17.4121 | 57.02
1985-05-03 | 3 | 5 | 0.83333 | 13.9 | 57.02 | 17.4121 | 57.02
1985-05-03 | 3 | 5 | 0.875 | 13.9 | 57.02 | 17.6263 | 57.02
1985-05-03 | 3 | 5 | 0.91667 | 13.3 | 55.94 | 17.5225 |  | 55.94
1985-05-03 | 3 | 5 | 0.95833 | 12.8 | 55.04 | 17.2722 |  | 55.04
1985-05-03 | 3 | 5 | 1 | 12.8 | 55.04 | 17.0729 |  | 55.04
1985-05-04 | 4 | 5 | 0.041667 | 12.8 | 55.04 | 17.2722 |  | 55.04
1985-05-04 | 4 | 5 | 0.083333 | 12.8 | 55.04 | 17.6711 |  | 55.04
1985-05-04 | 4 | 5 | 0.125 | 12.8 | 55.04 | 17.8708 |  | 55.04
1985-05-04 | 4 | 5 | 0.16667 | 11.1 | 51.98 | 18.5978 |  | 51.98
1985-05-04 | 4 | 5 | 0.20833 | 10.6 | 51.08 | 19.0439 |  | 51.08
1985-05-04 | 4 | 5 | 0.25 | 10.6 | 51.08 | 19.391 | 51.08
1985-05-04 | 4 | 5 | 0.29167 | 12.2 | 53.96 | 18.5811 | 53.96
1985-05-04 | 4 | 5 | 0.33333 | 14.4 | 57.92 | 18.196 | 57.92
1985-05-04 | 4 | 5 | 0.375 | 15.6 | 60.08 | 17.6294 | 60.08
1985-05-04 | 4 | 5 | 0.41667 | 16.1 | 60.98 | 17.7047 | 60.98
1985-05-04 | 4 | 5 | 0.45833 | 16.7 | 62.06 | 18.0855 | 62.06
1985-05-04 | 4 | 5 | 0.5 | 15.6 | 60.08 | 18.4667 | 60.08
1985-05-04 | 4 | 5 | 0.54167 | 16.1 | 60.98 | 19.3119 | 60.98
1985-05-04 | 4 | 5 | 0.58333 | 14.4 | 57.92 | 19.3062 | 57.92
1985-05-04 | 4 | 5 | 0.625 | 13.9 | 57.02 | 18.6995 | 57.02
1985-05-04 | 4 | 5 | 0.66667 | 12.8 | 55.04 | 18.8709 | 55.04
1985-05-04 | 4 | 5 | 0.70833 | 12.8 | 55.04 | 19.372 | 55.04
1985-05-04 | 4 | 5 | 0.75 | 12.8 | 55.04 | 19.372 | 55.04
1985-05-04 | 4 | 5 | 0.79167 | 11.7 | 53.06 | 19.0172 | 53.06
1985-05-04 | 4 | 5 | 0.83333 | 11.1 | 51.98 | 19.0458 | 51.98
1985-05-04 | 4 | 5 | 0.875 | 10.6 | 51.08 | 19.0439 | 51.08
1985-05-04 | 4 | 5 | 0.91667 | 10.6 | 51.08 | 19.391 |  | 51.08
1985-05-04 | 4 | 5 | 0.95833 | 10.6 | 51.08 | 19.6516 |  | 51.08
1985-05-04 | 4 | 5 | 1 | 10.6 | 51.08 | 19.9124 |  | 51.08
1985-05-05 | 5 | 5 | 0.041667 | 10.6 | 51.08 | 19.9124 |  | 51.08
1985-05-05 | 5 | 5 | 0.083333 | 11.1 | 51.98 | 20.1234 |  | 51.98
1985-05-05 | 5 | 5 | 0.125 | 11.1 | 51.98 | 20.1234 |  | 51.98
1985-05-05 | 5 | 5 | 0.16667 | 11.1 | 51.98 | 20.3933 |  | 51.98
1985-05-05 | 5 | 5 | 0.20833 | 11.7 | 53.06 | 20.7 |  | 53.06
1985-05-05 | 5 | 5 | 0.25 | 12.2 | 53.96 | 20.608 | 53.96
1985-05-05 | 5 | 5 | 0.29167 | 13.3 | 55.94 | 20.3162 | 55.94
1985-05-05 | 5 | 5 | 0.33333 | 13.3 | 55.94 | 19.7971 | 55.94
1985-05-05 | 5 | 5 | 0.375 | 14.4 | 57.92 | 20.1969 | 57.92
1985-05-05 | 5 | 5 | 0.41667 | 16.1 | 60.98 | 21.3005 | 60.98
1985-05-05 | 5 | 5 | 0.45833 | 17.2 | 62.96 | 22.0015 | 62.96
1985-05-05 | 5 | 5 | 0.5 | 17.8 | 64.04 | 22.2545 | 64.04
1985-05-05 | 5 | 5 | 0.54167 | 18.9 | 66.02 | 22.487 | 66.02
1985-05-05 | 5 | 5 | 0.58333 | 20 | 68 | 22.9637 | 68
1985-05-05 | 5 | 5 | 0.625 | 20.6 | 69.08 | 23.1477 | 69.08
1985-05-05 | 5 | 5 | 0.66667 | 21.7 | 71.06 | 23.7369 | 71.06
1985-05-05 | 5 | 5 | 0.70833 | 22.2 | 71.96 | 23.4323 | 71.96
1985-05-05 | 5 | 5 | 0.75 | 21.7 | 71.06 | 23.2046 | 71.06
1985-05-05 | 5 | 5 | 0.79167 | 18.9 | 66.02 | 22.9344 | 66.02
1985-05-05 | 5 | 5 | 0.83333 | 16.7 | 62.06 | 22.3441 | 62.06
1985-05-05 | 5 | 5 | 0.875 | 15.6 | 60.08 | 22.6841 | 60.08
1985-05-05 | 5 | 5 | 0.91667 | 15 | 59 | 22.4549 |  | 59
1985-05-05 | 5 | 5 | 0.95833 | 13.9 | 57.02 | 22.2651 |  | 57.02
1985-05-05 | 5 | 5 | 1 | 13.3 | 55.94 | 22.087 |  | 55.94
1985-05-06 | 6 | 5 | 0.041667 | 14.4 | 57.92 | 21.3136 |  | 57.92
1985-05-06 | 6 | 5 | 0.083333 | 15.6 | 60.08 | 20.9909 |  | 60.08
1985-05-06 | 6 | 5 | 0.125 | 14.4 | 57.92 | 19.7512 |  | 57.92
1985-05-06 | 6 | 5 | 0.16667 | 15 | 59 | 19.205 |  | 59
1985-05-06 | 6 | 5 | 0.20833 | 15.6 | 60.08 | 19.186 |  | 60.08
1985-05-06 | 6 | 5 | 0.25 | 16.1 | 60.98 | 19.6839 | 60.98
1985-05-06 | 6 | 5 | 0.29167 | 15 | 59 | 20.8261 | 59
1985-05-06 | 6 | 5 | 0.33333 | 13.3 | 55.94 | 22.087 | 55.94
1985-05-06 | 6 | 5 | 0.375 | 13.3 | 55.94 | 22.4004 | 55.94
1985-05-06 | 6 | 5 | 0.41667 | 14.4 | 57.92 | 22.8831 | 57.92
1985-05-06 | 6 | 5 | 0.45833 | 16.1 | 60.98 | 22.0492 | 60.98
1985-05-06 | 6 | 5 | 0.5 | 17.2 | 62.96 | 21.7339 | 62.96
1985-05-06 | 6 | 5 | 0.54167 | 14.4 | 57.92 | 20.1969 | 57.92
1985-05-06 | 6 | 5 | 0.58333 | 16.7 | 62.06 | 19.7568 | 62.06
1985-05-06 | 6 | 5 | 0.625 | 16.1 | 60.98 | 19.3119 | 60.98
1985-05-06 | 6 | 5 | 0.66667 | 15.6 | 60.08 | 19.9068 | 60.08
1985-05-06 | 6 | 5 | 0.70833 | 15 | 59 | 19.5518 | 59
1985-05-06 | 6 | 5 | 0.75 | 14.4 | 57.92 | 19.0839 | 57.92
1985-05-06 | 6 | 5 | 0.79167 | 13.3 | 55.94 | 18.8648 | 55.94
1985-05-06 | 6 | 5 | 0.83333 | 12.2 | 53.96 | 18.5811 | 53.96
1985-05-06 | 6 | 5 | 0.875 | 11.7 | 53.06 | 18.179 | 53.06
1985-05-06 | 6 | 5 | 0.91667 | 11.1 | 51.98 | 18.061 |  | 51.98
1985-05-06 | 6 | 5 | 0.95833 | 10.6 | 51.08 | 17.8316 |  | 51.08
1985-05-06 | 6 | 5 | 1 | 10.6 | 51.08 | 17.8316 |  | 51.08
1985-05-07 | 7 | 5 | 0.041667 | 10.6 | 51.08 | 18.091 |  | 51.08
1985-05-07 | 7 | 5 | 0.083333 | 10 | 50 | 18.0966 |  | 50
1985-05-07 | 7 | 5 | 0.125 | 10.6 | 51.08 | 18.3506 |  | 51.08
1985-05-07 | 7 | 5 | 0.16667 | 10 | 50 | 18.0966 |  | 50
1985-05-07 | 7 | 5 | 0.20833 | 9.4 | 48.92 | 17.8313 |  | 48.92
1985-05-07 | 7 | 5 | 0.25 | 10 | 50 | 18.5957 | 50
1985-05-07 | 7 | 5 | 0.29167 | 11.7 | 53.06 | 19.0172 | 53.06
1985-05-07 | 7 | 5 | 0.33333 | 13.9 | 57.02 | 20.3156 | 57.02
1985-05-07 | 7 | 5 | 0.375 | 15.6 | 60.08 | 20.9909 | 60.08
1985-05-07 | 7 | 5 | 0.41667 | 16.7 | 62.06 | 21.5659 | 62.06
1985-05-07 | 7 | 5 | 0.45833 | 17.2 | 62.96 | 21.4665 | 62.96
1985-05-07 | 7 | 5 | 0.5 | 19.4 | 66.92 | 22.1492 | 66.92
1985-05-07 | 7 | 5 | 0.54167 | 20 | 68 | 22.6444 | 68
1985-05-07 | 7 | 5 | 0.58333 | 18.3 | 64.94 | 21.9777 | 64.94
1985-05-07 | 7 | 5 | 0.625 | 16.7 | 62.06 | 21.5659 | 62.06
1985-05-07 | 7 | 5 | 0.66667 | 15.6 | 60.08 | 20.7497 | 60.08
1985-05-07 | 7 | 5 | 0.70833 | 14.4 | 57.92 | 21.8733 | 57.92
1985-05-07 | 7 | 5 | 0.75 | 13.9 | 57.02 | 21.9394 | 57.02
1985-05-07 | 7 | 5 | 0.79167 | 13.3 | 55.94 | 22.4004 | 55.94
1985-05-07 | 7 | 5 | 0.83333 | 11.7 | 53.06 | 20.7 | 53.06
1985-05-07 | 7 | 5 | 0.875 | 11.1 | 51.98 | 20.3933 | 51.98
1985-05-07 | 7 | 5 | 0.91667 | 10.6 | 51.08 | 20.5217 |  | 51.08
1985-05-07 | 7 | 5 | 0.95833 | 10.6 | 51.08 | 20.5217 |  | 51.08
1985-05-07 | 7 | 5 | 1 | 11.1 | 51.98 | 21.1142 |  | 51.98
1985-05-08 | 8 | 5 | 0.041667 | 11.1 | 51.98 | 21.3849 |  | 51.98
1985-05-08 | 8 | 5 | 0.083333 | 11.7 | 53.06 | 21.6384 |  | 53.06
1985-05-08 | 8 | 5 | 0.125 | 12.8 | 55.04 | 22.7994 |  | 55.04
1985-05-08 | 8 | 5 | 0.16667 | 12.2 | 53.96 | 22.2577 |  | 53.96
1985-05-08 | 8 | 5 | 0.20833 | 11.7 | 53.06 | 22.0145 |  | 53.06
1985-05-08 | 8 | 5 | 0.25 | 12.2 | 53.96 | 22.2577 | 53.96
1985-05-08 | 8 | 5 | 0.29167 | 12.2 | 53.96 | 22.2577 | 53.96
1985-05-08 | 8 | 5 | 0.33333 | 12.8 | 55.04 | 22.7994 | 55.04
1985-05-08 | 8 | 5 | 0.375 | 13.9 | 57.02 | 23.244 | 57.02
1985-05-08 | 8 | 5 | 0.41667 | 15 | 59 | 23.7401 | 59
1985-05-08 | 8 | 5 | 0.45833 | 15 | 59 | 23.5061 | 59
1985-05-08 | 8 | 5 | 0.5 | 16.1 | 60.98 | 23.5515 | 60.98
1985-05-08 | 8 | 5 | 0.54167 | 16.7 | 62.06 | 23.2543 | 62.06
1985-05-08 | 8 | 5 | 0.58333 | 16.1 | 60.98 | 22.9247 | 60.98
1985-05-08 | 8 | 5 | 0.625 | 16.1 | 60.98 | 23.3007 | 60.98
1985-05-08 | 8 | 5 | 0.66667 | 15 | 59 | 22.8049 | 59
1985-05-08 | 8 | 5 | 0.70833 | 13.9 | 57.02 | 22.5911 | 57.02
1985-05-08 | 8 | 5 | 0.75 | 15 | 59 | 23.0385 | 59
1985-05-08 | 8 | 5 | 0.79167 | 14.4 | 57.92 | 22.2096 | 57.92
1985-05-08 | 8 | 5 | 0.83333 | 14.4 | 57.92 | 22.2096 | 57.92
1985-05-08 | 8 | 5 | 0.875 | 13.9 | 57.02 | 21.614 | 57.02
1985-05-08 | 8 | 5 | 0.91667 | 13.9 | 57.02 | 21.3973 |  | 57.02
1985-05-08 | 8 | 5 | 0.95833 | 13.3 | 55.94 | 20.836 |  | 55.94
1985-05-08 | 8 | 5 | 1 | 13.3 | 55.94 | 20.836 |  | 55.94
1985-05-09 | 9 | 5 | 0.041667 | 12.8 | 55.04 | 20.3765 |  | 55.04
1985-05-09 | 9 | 5 | 0.083333 | 12.2 | 53.96 | 20.0277 |  | 53.96
1985-05-09 | 9 | 5 | 0.125 | 12.2 | 53.96 | 19.7379 |  | 53.96
1985-05-09 | 9 | 5 | 0.16667 | 11.1 | 51.98 | 19.3149 |  | 51.98
1985-05-09 | 9 | 5 | 0.20833 | 10.6 | 51.08 | 19.0439 |  | 51.08
1985-05-09 | 9 | 5 | 0.25 | 12.2 | 53.96 | 19.7379 | 53.96
1985-05-09 | 9 | 5 | 0.29167 | 13.9 | 57.02 | 20.3156 | 57.02
1985-05-09 | 9 | 5 | 0.33333 | 15.6 | 60.08 | 20.7497 | 60.08
1985-05-09 | 9 | 5 | 0.375 | 17.8 | 64.04 | 21.2822 | 64.04
1985-05-09 | 9 | 5 | 0.41667 | 20 | 68 | 22.0067 | 68
1985-05-09 | 9 | 5 | 0.45833 | 21.1 | 69.98 | 21.8663 | 69.98
1985-05-09 | 9 | 5 | 0.5 | 22.8 | 73.04 | 22.9772 | 73.04
1985-05-09 | 9 | 5 | 0.54167 | 23.9 | 75.02 | 23.0243 | 75.02
1985-05-09 | 9 | 5 | 0.58333 | 23.3 | 73.94 | 22.9735 | 73.94
1985-05-09 | 9 | 5 | 0.625 | 23.9 | 75.02 | 23.4291 | 75.02
1985-05-09 | 9 | 5 | 0.66667 | 23.9 | 75.02 | 23.4291 | 75.02
1985-05-09 | 9 | 5 | 0.70833 | 23.3 | 73.94 | 23.5593 | 73.94
1985-05-09 | 9 | 5 | 0.75 | 22.8 | 73.04 | 23.9252 | 73.04
1985-05-09 | 9 | 5 | 0.79167 | 21.7 | 71.06 | 23.7369 | 71.06
1985-05-09 | 9 | 5 | 0.83333 | 21.1 | 69.98 | 23.4024 | 69.98
1985-05-09 | 9 | 5 | 0.875 | 19.4 | 66.92 | 23.2259 | 66.92
1985-05-09 | 9 | 5 | 0.91667 | 18.9 | 66.02 | 22.9344 |  | 66.02
1985-05-09 | 9 | 5 | 0.95833 | 18.3 | 64.94 | 22.9829 |  | 64.94
1985-05-09 | 9 | 5 | 1 | 17.8 | 64.04 | 22.8114 |  | 64.04
1985-05-10 | 10 | 5 | 0.041667 | 16.7 | 62.06 | 22.6039 |  | 62.06
1985-05-10 | 10 | 5 | 0.083333 | 16.7 | 62.06 | 22.6039 |  | 62.06
1985-05-10 | 10 | 5 | 0.125 | 16.7 | 62.06 | 22.8639 |  | 62.06
1985-05-10 | 10 | 5 | 0.16667 | 15.6 | 60.08 | 20.9909 |  | 60.08
1985-05-10 | 10 | 5 | 0.20833 | 15 | 59 | 21.0583 |  | 59
1985-05-10 | 10 | 5 | 0.25 | 14.4 | 57.92 | 20.7548 | 57.92
1985-05-10 | 10 | 5 | 0.29167 | 15.6 | 60.08 | 21.2323 | 60.08
1985-05-10 | 10 | 5 | 0.33333 | 16.1 | 60.98 | 21.3005 | 60.98
1985-05-10 | 10 | 5 | 0.375 | 17.8 | 64.04 | 21.9765 | 64.04
1985-05-10 | 10 | 5 | 0.41667 | 18.9 | 66.02 | 22.189 | 66.02
1985-05-10 | 10 | 5 | 0.45833 | 20 | 68 | 21.8474 | 68
1985-05-10 | 10 | 5 | 0.5 | 21.1 | 69.98 | 21.696 | 69.98
1985-05-10 | 10 | 5 | 0.54167 | 18.9 | 66.02 | 20.5548 | 66.02
1985-05-10 | 10 | 5 | 0.58333 | 21.1 | 69.98 | 21.1858 | 69.98
1985-05-10 | 10 | 5 | 0.625 | 21.7 | 71.06 | 21.4361 | 71.06
1985-05-10 | 10 | 5 | 0.66667 | 17.8 | 64.04 | 20.5894 | 64.04
1985-05-10 | 10 | 5 | 0.70833 | 17.2 | 62.96 | 20.7988 | 62.96
1985-05-10 | 10 | 5 | 0.75 | 17.8 | 64.04 | 20.5894 | 64.04
1985-05-10 | 10 | 5 | 0.79167 | 17.2 | 62.96 | 20.1325 | 62.96
1985-05-10 | 10 | 5 | 0.83333 | 15.6 | 60.08 | 19.6664 | 60.08
1985-05-10 | 10 | 5 | 0.875 | 15 | 59 | 19.205 | 59
1985-05-10 | 10 | 5 | 0.91667 | 15 | 59 | 18.9741 |  | 59
1985-05-10 | 10 | 5 | 0.95833 | 13.9 | 57.02 | 18.6995 |  | 57.02
1985-05-10 | 10 | 5 | 1 | 13.3 | 55.94 | 19.0717 |  | 55.94
1985-05-11 | 11 | 5 | 0.041667 | 12.8 | 55.04 | 19.0712 |  | 55.04
1985-05-11 | 11 | 5 | 0.083333 | 12.8 | 55.04 | 18.8709 |  | 55.04
1985-05-11 | 11 | 5 | 0.125 | 12.2 | 53.96 | 18.5811 |  | 53.96
1985-05-11 | 11 | 5 | 0.16667 | 11.1 | 51.98 | 18.3293 |  | 51.98
1985-05-11 | 11 | 5 | 0.20833 | 10 | 50 | 17.5982 |  | 50
1985-05-11 | 11 | 5 | 0.25 | 12.2 | 53.96 | 19.0626 | 53.96
1985-05-11 | 11 | 5 | 0.29167 | 15.6 | 60.08 | 20.5087 | 60.08
1985-05-11 | 11 | 5 | 0.33333 | 16.7 | 62.06 | 20.2727 | 62.06
1985-05-11 | 11 | 5 | 0.375 | 18.3 | 64.94 | 20.6897 | 64.94
1985-05-11 | 11 | 5 | 0.41667 | 20 | 68 | 21.0523 | 68
1985-05-11 | 11 | 5 | 0.45833 | 20.6 | 69.08 | 21.6587 | 69.08
1985-05-11 | 11 | 5 | 0.5 | 21.7 | 71.06 | 22.4961 | 71.06
1985-05-11 | 11 | 5 | 0.54167 | 20.6 | 69.08 | 21.9891 | 69.08
1985-05-11 | 11 | 5 | 0.58333 | 19.4 | 66.92 | 21.229 | 66.92
1985-05-11 | 11 | 5 | 0.625 | 18.9 | 66.02 | 21.2966 | 66.02
1985-05-11 | 11 | 5 | 0.66667 | 17.8 | 64.04 | 20.451 | 64.04
1985-05-11 | 11 | 5 | 0.70833 | 16.7 | 62.06 | 21.048 | 62.06
1985-05-11 | 11 | 5 | 0.75 | 16.1 | 60.98 | 21.5499 | 60.98
1985-05-11 | 11 | 5 | 0.79167 | 15.6 | 60.08 | 22.0785 | 60.08
1985-05-11 | 11 | 5 | 0.83333 | 16.7 | 62.06 | 21.5659 | 62.06
1985-05-11 | 11 | 5 | 0.875 | 16.7 | 62.06 | 20.7894 | 62.06
1985-05-11 | 11 | 5 | 0.91667 | 15.6 | 60.08 | 20.9909 |  | 60.08
1985-05-11 | 11 | 5 | 0.95833 | 15.6 | 60.08 | 20.9909 |  | 60.08
1985-05-11 | 11 | 5 | 1 | 15 | 59 | 20.4781 |  | 59
1985-05-12 | 12 | 5 | 0.041667 | 14.4 | 57.92 | 21.09 |  | 57.92
1985-05-12 | 12 | 5 | 0.083333 | 14.4 | 57.92 | 21.8733 |  | 57.92
1985-05-12 | 12 | 5 | 0.125 | 15 | 59 | 22.1052 |  | 59
1985-05-12 | 12 | 5 | 0.16667 | 16.7 | 62.06 | 22.6039 |  | 62.06
1985-05-12 | 12 | 5 | 0.20833 | 16.7 | 62.06 | 22.8639 |  | 62.06
1985-05-12 | 12 | 5 | 0.25 | 17.2 | 62.96 | 23.7463 | 62.96
1985-05-12 | 12 | 5 | 0.29167 | 17.2 | 62.96 | 24.0155 | 62.96
1985-05-12 | 12 | 5 | 0.33333 | 17.2 | 62.96 | 24.4197 | 62.96
1985-05-12 | 12 | 5 | 0.375 | 17.8 | 64.04 | 24.6274 | 64.04
1985-05-12 | 12 | 5 | 0.41667 | 15.6 | 60.08 | 24.3858 | 60.08
1985-05-12 | 12 | 5 | 0.45833 | 17.8 | 64.04 | 25.7498 | 64.04
1985-05-12 | 12 | 5 | 0.5 | 19.4 | 66.92 | 26.1656 | 66.92
1985-05-12 | 12 | 5 | 0.54167 | 21.1 | 69.98 | 26.1504 | 69.98
1985-05-12 | 12 | 5 | 0.58333 | 15 | 59 | 22.4549 | 59
1985-05-12 | 12 | 5 | 0.625 | 17.2 | 62.96 | 24.0155 | 62.96
1985-05-12 | 12 | 5 | 0.66667 | 16.7 | 62.06 | 22.3441 | 62.06
1985-05-12 | 12 | 5 | 0.70833 | 16.1 | 60.98 | 20.9267 | 60.98
1985-05-12 | 12 | 5 | 0.75 | 13.9 | 57.02 | 19.5604 | 57.02
1985-05-12 | 12 | 5 | 0.79167 | 13.3 | 55.94 | 19.0717 | 55.94
1985-05-12 | 12 | 5 | 0.83333 | 12.2 | 53.96 | 18.3887 | 53.96
1985-05-12 | 12 | 5 | 0.875 | 12.2 | 53.96 | 18.3887 | 53.96
1985-05-12 | 12 | 5 | 0.91667 | 11.7 | 53.06 | 18.179 |  | 53.06
1985-05-12 | 12 | 5 | 0.95833 | 11.1 | 51.98 | 17.7036 |  | 51.98
1985-05-12 | 12 | 5 | 1 | 10 | 50 | 16.7691 |  | 50
1985-05-13 | 13 | 5 | 0.041667 | 10.6 | 51.08 | 16.7097 |  | 51.08
1985-05-13 | 13 | 5 | 0.083333 | 10 | 50 | 16.1073 |  | 50
1985-05-13 | 13 | 5 | 0.125 | 9.4 | 48.92 | 15.6038 |  | 48.92
1985-05-13 | 13 | 5 | 0.16667 | 8.9 | 48.02 | 15.2576 |  | 48.02
1985-05-13 | 13 | 5 | 0.20833 | 8.9 | 48.02 | 15.2576 |  | 48.02
1985-05-13 | 13 | 5 | 0.25 | 8.9 | 48.02 | 15.2576 | 48.02
1985-05-13 | 13 | 5 | 0.29167 | 9.4 | 48.92 | 15.2868 | 48.92
1985-05-13 | 13 | 5 | 0.33333 | 10.6 | 51.08 | 15.5057 | 51.08
1985-05-13 | 13 | 5 | 0.375 | 11.7 | 53.06 | 16.1385 | 53.06
1985-05-13 | 13 | 5 | 0.41667 | 12.8 | 55.04 | 16.4756 | 55.04
1985-05-13 | 13 | 5 | 0.45833 | 13.9 | 57.02 | 17.198 | 57.02
1985-05-13 | 13 | 5 | 0.5 | 15.6 | 60.08 | 18.1076 | 60.08
1985-05-13 | 13 | 5 | 0.54167 | 16.1 | 60.98 | 18.322 | 60.98
1985-05-13 | 13 | 5 | 0.58333 | 17.2 | 62.96 | 18.5385 | 62.96
1985-05-13 | 13 | 5 | 0.625 | 17.2 | 62.96 | 18.8037 | 62.96
1985-05-13 | 13 | 5 | 0.66667 | 17.2 | 62.96 | 18.2736 | 62.96
1985-05-13 | 13 | 5 | 0.70833 | 16.7 | 62.06 | 17.4449 | 62.06
1985-05-13 | 13 | 5 | 0.75 | 16.1 | 60.98 | 17.5814 | 60.98
1985-05-13 | 13 | 5 | 0.79167 | 14.4 | 57.92 | 17.2 | 57.92
1985-05-13 | 13 | 5 | 0.83333 | 13.3 | 55.94 | 16.802 | 55.94
1985-05-13 | 13 | 5 | 0.875 | 12.8 | 55.04 | 16.7741 | 55.04
1985-05-13 | 13 | 5 | 0.91667 | 12.2 | 53.96 | 16.4706 |  | 53.96
1985-05-13 | 13 | 5 | 0.95833 | 12.2 | 53.96 | 16.1838 |  | 53.96
1985-05-13 | 13 | 5 | 1 | 11.7 | 53.06 | 15.9537 |  | 53.06
1985-05-14 | 14 | 5 | 0.041667 | 11.7 | 53.06 | 15.9537 |  | 53.06
1985-05-14 | 14 | 5 | 0.083333 | 11.1 | 51.98 | 15.567 |  | 51.98
1985-05-14 | 14 | 5 | 0.125 | 10.6 | 51.08 | 15.2483 |  | 51.08
1985-05-14 | 14 | 5 | 0.16667 | 10.6 | 51.08 | 15.5057 |  | 51.08
1985-05-14 | 14 | 5 | 0.20833 | 10.6 | 51.08 | 15.8493 |  | 51.08
1985-05-14 | 14 | 5 | 0.25 | 10.6 | 51.08 | 15.6775 | 51.08
1985-05-14 | 14 | 5 | 0.29167 | 11.1 | 51.98 | 16.011 | 51.98
1985-05-14 | 14 | 5 | 0.33333 | 12.8 | 55.04 | 16.5751 | 55.04
1985-05-14 | 14 | 5 | 0.375 | 14.4 | 57.92 | 17.4211 | 57.92
1985-05-14 | 14 | 5 | 0.41667 | 16.7 | 62.06 | 18.4705 | 62.06
1985-05-14 | 14 | 5 | 0.45833 | 17.2 | 62.96 | 18.2736 | 62.96
1985-05-14 | 14 | 5 | 0.5 | 18.9 | 66.02 | 19.6667 | 66.02
1985-05-14 | 14 | 5 | 0.54167 | 20.6 | 69.08 | 20.1762 | 69.08
1985-05-14 | 14 | 5 | 0.58333 | 21.7 | 71.06 | 20.3793 | 71.06
1985-05-14 | 14 | 5 | 0.625 | 23.3 | 73.94 | 21.4161 | 73.94
1985-05-14 | 14 | 5 | 0.66667 | 23.3 | 73.94 | 21.4161 | 73.94
1985-05-14 | 14 | 5 | 0.70833 | 24.4 | 75.92 | 21.9392 | 75.92
1985-05-14 | 14 | 5 | 0.75 | 24.4 | 75.92 | 21.9392 | 75.92
1985-05-14 | 14 | 5 | 0.79167 | 23.3 | 73.94 | 21.4161 | 73.94
1985-05-14 | 14 | 5 | 0.83333 | 21.7 | 71.06 | 21.789 | 71.06
1985-05-14 | 14 | 5 | 0.875 | 21.1 | 69.98 | 21.5258 | 69.98
1985-05-14 | 14 | 5 | 0.91667 | 20.6 | 69.08 | 21.1639 |  | 69.08
1985-05-14 | 14 | 5 | 0.95833 | 20 | 68 | 20.7347 |  | 68
1985-05-14 | 14 | 5 | 1 | 17.8 | 64.04 | 20.0362 |  | 64.04
1985-05-15 | 15 | 5 | 0.041667 | 16.7 | 62.06 | 19.8857 |  | 62.06
1985-05-15 | 15 | 5 | 0.083333 | 15.6 | 60.08 | 19.6664 |  | 60.08
1985-05-15 | 15 | 5 | 0.125 | 15 | 59 | 19.5518 |  | 59
1985-05-15 | 15 | 5 | 0.16667 | 14.4 | 57.92 | 19.3062 |  | 57.92
1985-05-15 | 15 | 5 | 0.20833 | 14.4 | 57.92 | 19.5286 |  | 57.92
1985-05-15 | 15 | 5 | 0.25 | 15 | 59 | 20.0146 | 59
1985-05-15 | 15 | 5 | 0.29167 | 17.2 | 62.96 | 20.9323 | 62.96
1985-05-15 | 15 | 5 | 0.33333 | 20.6 | 69.08 | 22.982 | 69.08
1985-05-15 | 15 | 5 | 0.375 | 19.4 | 66.92 | 22.764 | 66.92
1985-05-15 | 15 | 5 | 0.41667 | 22.8 | 73.04 | 23.9252 | 73.04
1985-05-15 | 15 | 5 | 0.45833 | 23.3 | 73.94 | 23.9505 | 73.94
1985-05-15 | 15 | 5 | 0.5 | 22.8 | 73.04 | 24.1152 | 73.04
1985-05-15 | 15 | 5 | 0.54167 | 21.7 | 71.06 | 24.9823 | 71.06
1985-05-15 | 15 | 5 | 0.58333 | 21.1 | 69.98 | 25.4613 | 69.98
1985-05-15 | 15 | 5 | 0.625 | 21.1 | 69.98 | 26.1504 | 69.98
1985-05-15 | 15 | 5 | 0.66667 | 21.1 | 69.98 | 27.1866 | 69.98
1985-05-15 | 15 | 5 | 0.70833 | 18.3 | 64.94 | 27.1788 | 64.94
1985-05-15 | 15 | 5 | 0.75 | 18.9 | 66.02 | 27.4412 | 66.02
1985-05-15 | 15 | 5 | 0.79167 | 17.8 | 64.04 | 26.4531 | 64.04
1985-05-15 | 15 | 5 | 0.83333 | 17.2 | 62.96 | 26.3124 | 62.96
1985-05-15 | 15 | 5 | 0.875 | 16.7 | 62.06 | 25.9995 | 62.06
1985-05-15 | 15 | 5 | 0.91667 | 15 | 59 | 24.9127 |  | 59
1985-05-15 | 15 | 5 | 0.95833 | 13.9 | 57.02 | 23.68 |  | 57.02
1985-05-15 | 15 | 5 | 1 | 13.9 | 57.02 | 24.0074 |  | 57.02
1985-05-16 | 16 | 5 | 0.041667 | 12.8 | 55.04 | 23.2049 |  | 55.04
1985-05-16 | 16 | 5 | 0.083333 | 12.8 | 55.04 | 23.2049 |  | 55.04
1985-05-16 | 16 | 5 | 0.125 | 12.8 | 55.04 | 23.2049 |  | 55.04
1985-05-16 | 16 | 5 | 0.16667 | 12.8 | 55.04 | 23.2049 |  | 55.04
1985-05-16 | 16 | 5 | 0.20833 | 13.3 | 55.94 | 23.4473 |  | 55.94
1985-05-16 | 16 | 5 | 0.25 | 13.3 | 55.94 | 23.4473 | 55.94
1985-05-16 | 16 | 5 | 0.29167 | 12.8 | 55.04 | 22.7994 | 55.04
1985-05-16 | 16 | 5 | 0.33333 | 13.9 | 57.02 | 24.0074 | 57.02
1985-05-16 | 16 | 5 | 0.375 | 15 | 59 | 24.9127 | 59
1985-05-16 | 16 | 5 | 0.41667 | 17.8 | 64.04 | 26.1716 | 64.04
1985-05-16 | 16 | 5 | 0.45833 | 20 | 68 | 27.9515 | 68
1985-05-16 | 16 | 5 | 0.5 | 22.8 | 73.04 | 29.0905 | 73.04
1985-05-16 | 16 | 5 | 0.54167 | 20 | 68 | 27.9515 | 68
1985-05-16 | 16 | 5 | 0.58333 | 20 | 68 | 27.9515 | 68
1985-05-16 | 16 | 5 | 0.625 | 21.1 | 69.98 | 28.0524 | 69.98
1985-05-16 | 16 | 5 | 0.66667 | 21.7 | 71.06 | 28.2055 | 71.06
1985-05-16 | 16 | 5 | 0.70833 | 20.6 | 69.08 | 27.318 | 69.08
1985-05-16 | 16 | 5 | 0.75 | 17.2 | 62.96 | 25.9059 | 62.96
1985-05-16 | 16 | 5 | 0.79167 | 16.7 | 62.06 | 25.7371 | 62.06
1985-05-16 | 16 | 5 | 0.83333 | 14.4 | 57.92 | 24.2342 | 57.92
1985-05-16 | 16 | 5 | 0.875 | 13.9 | 57.02 | 23.68 | 57.02
1985-05-16 | 16 | 5 | 0.91667 | 13.3 | 55.94 | 23.0282 |  | 55.94
1985-05-16 | 16 | 5 | 0.95833 | 12.2 | 53.96 | 22.5497 |  | 53.96
1985-05-16 | 16 | 5 | 1 | 12.2 | 53.96 | 21.8688 |  | 53.96
1985-05-17 | 17 | 5 | 0.041667 | 11.7 | 53.06 | 21.6384 |  | 53.06
1985-05-17 | 17 | 5 | 0.083333 | 11.7 | 53.06 | 22.0145 |  | 53.06
1985-05-17 | 17 | 5 | 0.125 | 11.1 | 51.98 | 21.1142 |  | 51.98
1985-05-17 | 17 | 5 | 0.16667 | 10.6 | 51.08 | 20.5217 |  | 51.08
1985-05-17 | 17 | 5 | 0.20833 | 10 | 50 | 19.6798 |  | 50
1985-05-17 | 17 | 5 | 0.25 | 10.6 | 51.08 | 19.9124 | 51.08
1985-05-17 | 17 | 5 | 0.29167 | 10.6 | 51.08 | 19.9124 | 51.08
1985-05-17 | 17 | 5 | 0.33333 | 11.1 | 51.98 | 20.1234 | 51.98
1985-05-17 | 17 | 5 | 0.375 | 11.1 | 51.98 | 19.8537 | 51.98
1985-05-17 | 17 | 5 | 0.41667 | 11.1 | 51.98 | 20.1234 | 51.98
1985-05-17 | 17 | 5 | 0.45833 | 12.2 | 53.96 | 20.3177 | 53.96
1985-05-17 | 17 | 5 | 0.5 | 13.9 | 57.02 | 21.0724 | 57.02
1985-05-17 | 17 | 5 | 0.54167 | 14.4 | 57.92 | 21.3136 | 57.92
1985-05-17 | 17 | 5 | 0.58333 | 14.4 | 57.92 | 21.3136 | 57.92
1985-05-17 | 17 | 5 | 0.625 | 14.4 | 57.92 | 21.3136 | 57.92
1985-05-17 | 17 | 5 | 0.66667 | 15 | 59 | 21.5232 | 59
1985-05-17 | 17 | 5 | 0.70833 | 15 | 59 | 21.5232 | 59
1985-05-17 | 17 | 5 | 0.75 | 15 | 59 | 21.5232 | 59
1985-05-17 | 17 | 5 | 0.79167 | 14.4 | 57.92 | 21.3136 | 57.92
1985-05-17 | 17 | 5 | 0.83333 | 14.4 | 57.92 | 21.3136 | 57.92
1985-05-17 | 17 | 5 | 0.875 | 14.4 | 57.92 | 21.3136 | 57.92
1985-05-17 | 17 | 5 | 0.91667 | 13.9 | 57.02 | 21.3973 |  | 57.02
1985-05-17 | 17 | 5 | 0.95833 | 13.3 | 55.94 | 20.836 |  | 55.94
1985-05-17 | 17 | 5 | 1 | 13.3 | 55.94 | 21.1483 |  | 55.94
1985-05-18 | 18 | 5 | 0.041667 | 11.7 | 53.06 | 20.7 |  | 53.06
1985-05-18 | 18 | 5 | 0.083333 | 11.1 | 51.98 | 20.3933 |  | 51.98
1985-05-18 | 18 | 5 | 0.125 | 11.1 | 51.98 | 20.1234 |  | 51.98
1985-05-18 | 18 | 5 | 0.16667 | 12.2 | 53.96 | 20.3177 |  | 53.96
1985-05-18 | 18 | 5 | 0.20833 | 12.2 | 53.96 | 20.3177 |  | 53.96
1985-05-18 | 18 | 5 | 0.25 | 11.7 | 53.06 | 19.8575 | 53.06
1985-05-18 | 18 | 5 | 0.29167 | 12.8 | 55.04 | 20.0748 | 55.04
1985-05-18 | 18 | 5 | 0.33333 | 13.9 | 57.02 | 20.856 | 57.02
1985-05-18 | 18 | 5 | 0.375 | 15 | 59 | 21.2907 | 59
1985-05-18 | 18 | 5 | 0.41667 | 16.1 | 60.98 | 22.0492 | 60.98
1985-05-18 | 18 | 5 | 0.45833 | 16.1 | 60.98 | 21.7994 | 60.98
1985-05-18 | 18 | 5 | 0.5 | 15.6 | 60.08 | 21.8365 | 60.08
1985-05-18 | 18 | 5 | 0.54167 | 16.1 | 60.98 | 22.2991 | 60.98
1985-05-18 | 18 | 5 | 0.58333 | 16.7 | 62.06 | 22.3441 | 62.06
1985-05-18 | 18 | 5 | 0.625 | 15.6 | 60.08 | 22.4417 | 60.08
1985-05-18 | 18 | 5 | 0.66667 | 17.2 | 62.96 | 22.5374 | 62.96
1985-05-18 | 18 | 5 | 0.70833 | 16.1 | 60.98 | 22.2991 | 60.98
1985-05-18 | 18 | 5 | 0.75 | 12.8 | 55.04 | 22.0909 | 55.04
1985-05-18 | 18 | 5 | 0.79167 | 12.8 | 55.04 | 22.4956 | 55.04
1985-05-18 | 18 | 5 | 0.83333 | 12.8 | 55.04 | 21.1822 | 55.04
1985-05-18 | 18 | 5 | 0.875 | 11.7 | 53.06 | 20.9812 | 53.06
1985-05-18 | 18 | 5 | 0.91667 | 11.7 | 53.06 | 20.9812 |  | 53.06
1985-05-18 | 18 | 5 | 0.95833 | 12.2 | 53.96 | 21.1894 |  | 53.96
1985-05-18 | 18 | 5 | 1 | 11.7 | 53.06 | 20.9812 |  | 53.06
1985-05-19 | 19 | 5 | 0.041667 | 12.2 | 53.96 | 21.1894 |  | 53.96
1985-05-19 | 19 | 5 | 0.083333 | 10.6 | 51.08 | 20.1734 |  | 51.08
1985-05-19 | 19 | 5 | 0.125 | 10 | 50 | 19.9304 |  | 50
1985-05-19 | 19 | 5 | 0.16667 | 10.6 | 51.08 | 20.1734 |  | 51.08
1985-05-19 | 19 | 5 | 0.20833 | 10 | 50 | 19.9304 |  | 50
1985-05-19 | 19 | 5 | 0.25 | 10.6 | 51.08 | 20.1734 | 51.08
1985-05-19 | 19 | 5 | 0.29167 | 11.1 | 51.98 | 20.3933 | 51.98
1985-05-19 | 19 | 5 | 0.33333 | 11.1 | 51.98 | 20.3933 | 51.98
1985-05-19 | 19 | 5 | 0.375 | 11.7 | 53.06 | 20.4189 | 53.06
1985-05-19 | 19 | 5 | 0.41667 | 11.7 | 53.06 | 20.4189 | 53.06
1985-05-19 | 19 | 5 | 0.45833 | 11.7 | 53.06 | 20.1381 | 53.06
1985-05-19 | 19 | 5 | 0.5 | 11.7 | 53.06 | 20.1381 | 53.06
1985-05-19 | 19 | 5 | 0.54167 | 12.2 | 53.96 | 20.3177 | 53.96
1985-05-19 | 19 | 5 | 0.58333 | 12.2 | 53.96 | 20.608 | 53.96
1985-05-19 | 19 | 5 | 0.625 | 11.7 | 53.06 | 20.4189 | 53.06
1985-05-19 | 19 | 5 | 0.66667 | 11.1 | 51.98 | 20.1234 | 51.98
1985-05-19 | 19 | 5 | 0.70833 | 11.1 | 51.98 | 20.3933 | 51.98
1985-05-19 | 19 | 5 | 0.75 | 10.6 | 51.08 | 20.1734 | 51.08
1985-05-19 | 19 | 5 | 0.79167 | 10.6 | 51.08 | 20.1734 | 51.08
1985-05-19 | 19 | 5 | 0.83333 | 10.6 | 51.08 | 19.391 | 51.08
1985-05-19 | 19 | 5 | 0.875 | 10 | 50 | 19.0956 | 50
1985-05-19 | 19 | 5 | 0.91667 | 10 | 50 | 19.3458 |  | 50
1985-05-19 | 19 | 5 | 0.95833 | 9.4 | 48.92 | 19.1107 |  | 48.92
1985-05-19 | 19 | 5 | 1 | 9.4 | 48.92 | 18.5503 |  | 48.92
1985-05-20 | 20 | 5 | 0.041667 | 9.4 | 48.92 | 18.8704 |  | 48.92
1985-05-20 | 20 | 5 | 0.083333 | 8.9 | 48.02 | 18.645 |  | 48.02
1985-05-20 | 20 | 5 | 0.125 | 8.3 | 46.94 | 18.0963 |  | 46.94
1985-05-20 | 20 | 5 | 0.16667 | 8.9 | 48.02 | 18.645 |  | 48.02
1985-05-20 | 20 | 5 | 0.20833 | 9.4 | 48.92 | 18.3105 |  | 48.92
1985-05-20 | 20 | 5 | 0.25 | 8.9 | 48.02 | 17.6407 | 48.02
1985-05-20 | 20 | 5 | 0.29167 | 8.9 | 48.02 | 17.6407 | 48.02
1985-05-20 | 20 | 5 | 0.33333 | 9.4 | 48.92 | 17.8313 | 48.92
1985-05-20 | 20 | 5 | 0.375 | 10.6 | 51.08 | 18.091 | 51.08
1985-05-20 | 20 | 5 | 0.41667 | 11.1 | 51.98 | 18.3293 | 51.98
1985-05-20 | 20 | 5 | 0.45833 | 12.2 | 53.96 | 18.7737 | 53.96
1985-05-20 | 20 | 5 | 0.5 | 12.8 | 55.04 | 18.8709 | 55.04
1985-05-20 | 20 | 5 | 0.54167 | 13.3 | 55.94 | 19.2788 | 55.94
1985-05-20 | 20 | 5 | 0.58333 | 13.9 | 57.02 | 19.776 | 57.02
1985-05-20 | 20 | 5 | 0.625 | 15.6 | 60.08 | 20.7497 | 60.08
1985-05-20 | 20 | 5 | 0.66667 | 15.6 | 60.08 | 20.7497 | 60.08
1985-05-20 | 20 | 5 | 0.70833 | 16.1 | 60.98 | 21.3005 | 60.98
1985-05-20 | 20 | 5 | 0.75 | 13.3 | 55.94 | 20.524 | 55.94
1985-05-20 | 20 | 5 | 0.79167 | 12.2 | 53.96 | 19.7379 | 53.96
1985-05-20 | 20 | 5 | 0.83333 | 11.1 | 51.98 | 19.3149 | 51.98
1985-05-20 | 20 | 5 | 0.875 | 10.6 | 51.08 | 19.0439 | 51.08
1985-05-20 | 20 | 5 | 0.91667 | 10 | 50 | 18.8456 |  | 50
1985-05-20 | 20 | 5 | 0.95833 | 10 | 50 | 18.8456 |  | 50
1985-05-20 | 20 | 5 | 1 | 10 | 50 | 18.8456 |  | 50
1985-05-21 | 21 | 5 | 0.041667 | 9.4 | 48.92 | 18.5503 |  | 48.92
1985-05-21 | 21 | 5 | 0.083333 | 9.4 | 48.92 | 18.5503 |  | 48.92
1985-05-21 | 21 | 5 | 0.125 | 9.4 | 48.92 | 18.8704 |  | 48.92
1985-05-21 | 21 | 5 | 0.16667 | 8.9 | 48.02 | 18.645 |  | 48.02
1985-05-21 | 21 | 5 | 0.20833 | 10 | 50 | 19.3458 |  | 50
1985-05-21 | 21 | 5 | 0.25 | 11.1 | 51.98 | 19.8537 | 51.98
1985-05-21 | 21 | 5 | 0.29167 | 12.8 | 55.04 | 20.5777 | 55.04
1985-05-21 | 21 | 5 | 0.33333 | 13.9 | 57.02 | 20.5316 | 57.02
1985-05-21 | 21 | 5 | 0.375 | 15.6 | 60.08 | 20.2678 | 60.08
1985-05-21 | 21 | 5 | 0.41667 | 16.7 | 62.06 | 20.5309 | 62.06
1985-05-21 | 21 | 5 | 0.45833 | 17.8 | 64.04 | 21.5598 | 64.04
1985-05-21 | 21 | 5 | 0.5 | 19.4 | 66.92 | 22.4565 | 66.92
1985-05-21 | 21 | 5 | 0.54167 | 21.1 | 69.98 | 23.7447 | 69.98
1985-05-21 | 21 | 5 | 0.58333 | 21.7 | 71.06 | 24.9823 | 71.06
1985-05-21 | 21 | 5 | 0.625 | 20.6 | 69.08 | 23.9777 | 69.08
1985-05-21 | 21 | 5 | 0.66667 | 20.6 | 69.08 | 24.6432 | 69.08
1985-05-21 | 21 | 5 | 0.70833 | 19.4 | 66.92 | 24.306 | 66.92
1985-05-21 | 21 | 5 | 0.75 | 17.8 | 64.04 | 23.3691 | 64.04
1985-05-21 | 21 | 5 | 0.79167 | 15.6 | 60.08 | 22.4417 | 60.08
1985-05-21 | 21 | 5 | 0.83333 | 14.4 | 57.92 | 21.6493 | 57.92
1985-05-21 | 21 | 5 | 0.875 | 13.9 | 57.02 | 21.3973 | 57.02
1985-05-21 | 21 | 5 | 0.91667 | 13.3 | 55.94 | 21.3567 |  | 55.94
1985-05-21 | 21 | 5 | 0.95833 | 12.8 | 55.04 | 21.4848 |  | 55.04
1985-05-21 | 21 | 5 | 1 | 12.8 | 55.04 | 21.4848 |  | 55.04
1985-05-22 | 22 | 5 | 0.041667 | 12.8 | 55.04 | 21.1822 |  | 55.04
1985-05-22 | 22 | 5 | 0.083333 | 12.8 | 55.04 | 21.1822 |  | 55.04
1985-05-22 | 22 | 5 | 0.125 | 12.8 | 55.04 | 21.1822 |  | 55.04
1985-05-22 | 22 | 5 | 0.16667 | 12.2 | 53.96 | 20.8986 |  | 53.96
1985-05-22 | 22 | 5 | 0.20833 | 12.2 | 53.96 | 21.5775 |  | 53.96
1985-05-22 | 22 | 5 | 0.25 | 14.4 | 57.92 | 22.2096 | 57.92
1985-05-22 | 22 | 5 | 0.29167 | 15.6 | 60.08 | 22.6841 | 60.08
1985-05-22 | 22 | 5 | 0.33333 | 19.4 | 66.92 | 24.306 | 66.92
1985-05-22 | 22 | 5 | 0.375 | 22.8 | 73.04 | 26.9768 | 73.04
1985-05-22 | 22 | 5 | 0.41667 | 23.9 | 75.02 | 27.0935 | 75.02
1985-05-22 | 22 | 5 | 0.45833 | 23.9 | 75.02 | 27.0935 | 75.02
1985-05-22 | 22 | 5 | 0.5 | 24.4 | 75.92 | 26.5394 | 75.92
1985-05-22 | 22 | 5 | 0.54167 | 25.6 | 78.08 | 27.0111 | 78.08
1985-05-22 | 22 | 5 | 0.58333 | 23.3 | 73.94 | 27.4907 | 73.94
1985-05-22 | 22 | 5 | 0.625 | 23.9 | 75.02 | 27.2983 | 75.02
1985-05-22 | 22 | 5 | 0.66667 | 23.3 | 73.94 | 26.1096 | 73.94
1985-05-22 | 22 | 5 | 0.70833 | 23.9 | 75.02 | 25.6638 | 75.02
1985-05-22 | 22 | 5 | 0.75 | 22.8 | 73.04 | 24.8759 | 73.04
1985-05-22 | 22 | 5 | 0.79167 | 19.4 | 66.92 | 22.764 | 66.92
1985-05-22 | 22 | 5 | 0.83333 | 17.8 | 64.04 | 21.9765 | 64.04
1985-05-22 | 22 | 5 | 0.875 | 17.8 | 64.04 | 21.5598 | 64.04
1985-05-22 | 22 | 5 | 0.91667 | 17.2 | 62.96 | 20.7988 |  | 62.96
1985-05-22 | 22 | 5 | 0.95833 | 17.2 | 62.96 | 20.7988 |  | 62.96
1985-05-22 | 22 | 5 | 1 | 16.1 | 60.98 | 20.8023 |  | 60.98
1985-05-23 | 23 | 5 | 0.041667 | 15.6 | 60.08 | 20.9909 |  | 60.08
1985-05-23 | 23 | 5 | 0.083333 | 15.6 | 60.08 | 20.9909 |  | 60.08
1985-05-23 | 23 | 5 | 0.125 | 15 | 59 | 20.4781 |  | 59
1985-05-23 | 23 | 5 | 0.16667 | 14.4 | 57.92 | 20.1969 |  | 57.92
1985-05-23 | 23 | 5 | 0.20833 | 14.4 | 57.92 | 21.09 |  | 57.92
1985-05-23 | 23 | 5 | 0.25 | 16.1 | 60.98 | 22.0492 | 60.98
1985-05-23 | 23 | 5 | 0.29167 | 18.3 | 64.94 | 23.2706 | 64.94
1985-05-23 | 23 | 5 | 0.33333 | 20.6 | 69.08 | 23.9777 | 69.08
1985-05-23 | 23 | 5 | 0.375 | 22.2 | 71.96 | 25.2659 | 71.96
1985-05-23 | 23 | 5 | 0.41667 | 25 | 77 | 27.7659 | 77
1985-05-23 | 23 | 5 | 0.45833 | 27.2 | 80.96 | 29.5423 | 80.96
1985-05-23 | 23 | 5 | 0.5 | 29.4 | 84.92 | 30.772 | 84.92
1985-05-23 | 23 | 5 | 0.54167 | 31.7 | 89.06 | 32.6174 | 89.06
1985-05-23 | 23 | 5 | 0.58333 | 31.7 | 89.06 | 32.9441 | 89.06
1985-05-23 | 23 | 5 | 0.625 | 27.8 | 82.04 | 30.4325 | 82.04
1985-05-23 | 23 | 5 | 0.66667 | 27.2 | 80.96 | 31.5504 | 80.96
1985-05-23 | 23 | 5 | 0.70833 | 28.9 | 84.02 | 32.1941 | 84.02
1985-05-23 | 23 | 5 | 0.75 | 26.7 | 80.06 | 30.9733 | 80.06
1985-05-23 | 23 | 5 | 0.79167 | 25.6 | 78.08 | 30.4221 | 78.08
1985-05-23 | 23 | 5 | 0.83333 | 24.4 | 75.92 | 29.4992 | 75.92
1985-05-23 | 23 | 5 | 0.875 | 23.9 | 75.02 | 28.9405 | 75.02
1985-05-23 | 23 | 5 | 0.91667 | 24.4 | 75.92 | 29.0748 |  | 75.92
1985-05-23 | 23 | 5 | 0.95833 | 23.3 | 73.94 | 28.0843 |  | 73.94
1985-05-23 | 23 | 5 | 1 | 21.1 | 69.98 | 28.0524 |  | 69.98
1985-05-24 | 24 | 5 | 0.041667 | 21.1 | 69.98 | 28.9205 |  | 69.98
1985-05-24 | 24 | 5 | 0.083333 | 19.4 | 66.92 | 27.7229 |  | 66.92
1985-05-24 | 24 | 5 | 0.125 | 19.4 | 66.92 | 26.7877 |  | 66.92
1985-05-24 | 24 | 5 | 0.16667 | 17.8 | 64.04 | 25.4688 |  | 64.04
1985-05-24 | 24 | 5 | 0.20833 | 18.3 | 64.94 | 25.2916 |  | 64.94
1985-05-24 | 24 | 5 | 0.25 | 18.9 | 66.02 | 25.481 | 66.02
1985-05-24 | 24 | 5 | 0.29167 | 20.6 | 69.08 | 26.6473 | 69.08
1985-05-24 | 24 | 5 | 0.33333 | 21.7 | 71.06 | 26.0533 | 71.06
1985-05-24 | 24 | 5 | 0.375 | 23.3 | 73.94 | 26.7008 | 73.94
1985-05-24 | 24 | 5 | 0.41667 | 23.9 | 75.02 | 27.0935 | 75.02
1985-05-24 | 24 | 5 | 0.45833 | 24.4 | 75.92 | 27.8048 | 75.92
1985-05-24 | 24 | 5 | 0.5 | 25.6 | 78.08 | 28.3715 | 78.08
1985-05-24 | 24 | 5 | 0.54167 | 26.7 | 80.06 | 29.2687 | 80.06
1985-05-24 | 24 | 5 | 0.58333 | 27.8 | 82.04 | 29.9133 | 82.04
1985-05-24 | 24 | 5 | 0.625 | 26.1 | 78.98 | 29.3538 | 78.98
1985-05-24 | 24 | 5 | 0.66667 | 25.6 | 78.08 | 28.3715 | 78.08
1985-05-24 | 24 | 5 | 0.70833 | 24.4 | 75.92 | 26.9607 | 75.92
1985-05-24 | 24 | 5 | 0.75 | 23.3 | 73.94 | 27.0955 | 73.94
1985-05-24 | 24 | 5 | 0.79167 | 21.1 | 69.98 | 28.0524 | 69.98
1985-05-24 | 24 | 5 | 0.83333 | 20 | 68 | 27.9515 | 68
1985-05-24 | 24 | 5 | 0.875 | 19.4 | 66.92 | 27.255 | 66.92
1985-05-24 | 24 | 5 | 0.91667 | 18.9 | 66.02 | 26.9878 |  | 66.02
1985-05-24 | 24 | 5 | 0.95833 | 17.2 | 62.96 | 26.3124 |  | 62.96
1985-05-24 | 24 | 5 | 1 | 17.2 | 62.96 | 26.3124 |  | 62.96
1985-05-25 | 25 | 5 | 0.041667 | 16.7 | 62.06 | 25.9995 |  | 62.06
1985-05-25 | 25 | 5 | 0.083333 | 17.2 | 62.96 | 26.7193 |  | 62.96
1985-05-25 | 25 | 5 | 0.125 | 17.8 | 64.04 | 27.0168 |  | 64.04
1985-05-25 | 25 | 5 | 0.16667 | 19.4 | 66.92 | 27.7229 |  | 66.92
1985-05-25 | 25 | 5 | 0.20833 | 19.4 | 66.92 | 28.1915 |  | 66.92
1985-05-25 | 25 | 5 | 0.25 | 20 | 68 | 28.438 | 68
1985-05-25 | 25 | 5 | 0.29167 | 21.7 | 71.06 | 29.4671 | 71.06
1985-05-25 | 25 | 5 | 0.33333 | 23.9 | 75.02 | 30.1773 | 75.02
1985-05-25 | 25 | 5 | 0.375 | 23.9 | 75.02 | 31.0043 | 75.02
1985-05-25 | 25 | 5 | 0.41667 | 24.4 | 75.92 | 31.2019 | 75.92
1985-05-25 | 25 | 5 | 0.45833 | 26.7 | 80.06 | 32.6863 | 80.06
1985-05-25 | 25 | 5 | 0.5 | 27.8 | 82.04 | 33.3023 | 82.04
1985-05-25 | 25 | 5 | 0.54167 | 29.4 | 84.92 | 33.3475 | 84.92
1985-05-25 | 25 | 5 | 0.58333 | 29.4 | 84.92 | 33.0604 | 84.92
1985-05-25 | 25 | 5 | 0.625 | 28.9 | 84.02 | 32.1941 | 84.02
1985-05-25 | 25 | 5 | 0.66667 | 28.3 | 82.94 | 32.0482 | 82.94
1985-05-25 | 25 | 5 | 0.70833 | 22.2 | 71.96 | 33.2636 | 71.96
1985-05-25 | 25 | 5 | 0.75 | 21.7 | 71.06 | 32.5504 | 71.06
1985-05-25 | 25 | 5 | 0.79167 | 22.2 | 71.96 | 32.3241 | 71.96
1985-05-25 | 25 | 5 | 0.83333 | 19.4 | 66.92 | 29.9151 | 66.92
1985-05-25 | 25 | 5 | 0.875 | 19.4 | 66.92 | 29.9151 | 66.92
1985-05-25 | 25 | 5 | 0.91667 | 18.3 | 64.94 | 28.4915 |  | 64.94
1985-05-25 | 25 | 5 | 0.95833 | 18.9 | 66.02 | 29.7169 |  | 66.02
1985-05-25 | 25 | 5 | 1 | 18.9 | 66.02 | 29.2605 |  | 66.02
1985-05-26 | 26 | 5 | 0.041667 | 18.3 | 64.94 | 28.4915 |  | 64.94
1985-05-26 | 26 | 5 | 0.083333 | 18.3 | 64.94 | 28.4915 |  | 64.94
1985-05-26 | 26 | 5 | 0.125 | 18.3 | 64.94 | 28.4915 |  | 64.94
1985-05-26 | 26 | 5 | 0.16667 | 17.8 | 64.04 | 27.8641 |  | 64.04
1985-05-26 | 26 | 5 | 0.20833 | 17.8 | 64.04 | 27.4402 |  | 64.04
1985-05-26 | 26 | 5 | 0.25 | 18.3 | 64.94 | 28.0534 | 64.94
1985-05-26 | 26 | 5 | 0.29167 | 18.3 | 64.94 | 28.0534 | 64.94
1985-05-26 | 26 | 5 | 0.33333 | 20.6 | 69.08 | 30.0137 | 69.08
1985-05-26 | 26 | 5 | 0.375 | 22.2 | 71.96 | 30.2661 | 71.96
1985-05-26 | 26 | 5 | 0.41667 | 22.2 | 71.96 | 30.2661 | 71.96
1985-05-26 | 26 | 5 | 0.45833 | 20.6 | 69.08 | 29.5066 | 69.08
1985-05-26 | 26 | 5 | 0.5 | 21.1 | 69.98 | 29.2683 | 69.98
1985-05-26 | 26 | 5 | 0.54167 | 20 | 68 | 29.2504 | 68
1985-05-26 | 26 | 5 | 0.58333 | 21.7 | 71.06 | 30.0092 | 71.06
1985-05-26 | 26 | 5 | 0.625 | 22.2 | 71.96 | 30.6394 | 71.96
1985-05-26 | 26 | 5 | 0.66667 | 22.8 | 73.04 | 31.0233 | 73.04
1985-05-26 | 26 | 5 | 0.70833 | 23.3 | 73.94 | 31.2674 | 73.94
1985-05-26 | 26 | 5 | 0.75 | 24.4 | 75.92 | 30.7754 | 75.92
1985-05-26 | 26 | 5 | 0.79167 | 20 | 68 | 29.7388 | 68
1985-05-26 | 26 | 5 | 0.83333 | 20 | 68 | 28.7628 | 68
1985-05-26 | 26 | 5 | 0.875 | 19.4 | 66.92 | 28.9739 | 66.92
1985-05-26 | 26 | 5 | 0.91667 | 18.9 | 66.02 | 28.3496 |  | 66.02
1985-05-26 | 26 | 5 | 0.95833 | 18.9 | 66.02 | 27.8951 |  | 66.02
1985-05-26 | 26 | 5 | 1 | 18.9 | 66.02 | 27.8951 |  | 66.02
1985-05-27 | 27 | 5 | 0.041667 | 18.9 | 66.02 | 27.8951 |  | 66.02
1985-05-27 | 27 | 5 | 0.083333 | 17.8 | 64.04 | 26.4531 |  | 64.04
1985-05-27 | 27 | 5 | 0.125 | 15.6 | 60.08 | 22.6841 |  | 60.08
1985-05-27 | 27 | 5 | 0.16667 | 13.3 | 55.94 | 20.836 |  | 55.94
1985-05-27 | 27 | 5 | 0.20833 | 11.1 | 51.98 | 18.5978 |  | 51.98
1985-05-27 | 27 | 5 | 0.25 | 10.6 | 51.08 | 17.8316 | 51.08
1985-05-27 | 27 | 5 | 0.29167 | 10 | 50 | 17.4322 | 50
1985-05-27 | 27 | 5 | 0.33333 | 10 | 50 | 17.1834 | 50
1985-05-27 | 27 | 5 | 0.375 | 11.1 | 51.98 | 17.8823 | 51.98
1985-05-27 | 27 | 5 | 0.41667 | 12.8 | 55.04 | 18.3705 | 55.04
1985-05-27 | 27 | 5 | 0.45833 | 13.3 | 55.94 | 18.6579 | 55.94
1985-05-27 | 27 | 5 | 0.5 | 15 | 59 | 19.205 | 59
1985-05-27 | 27 | 5 | 0.54167 | 15.6 | 60.08 | 19.066 | 60.08
1985-05-27 | 27 | 5 | 0.58333 | 16.1 | 60.98 | 18.9404 | 60.98
1985-05-27 | 27 | 5 | 0.625 | 17.2 | 62.96 | 19.2018 | 62.96
1985-05-27 | 27 | 5 | 0.66667 | 17.8 | 64.04 | 19.3459 | 64.04
1985-05-27 | 27 | 5 | 0.70833 | 17.8 | 64.04 | 19.4838 | 64.04
1985-05-27 | 27 | 5 | 0.75 | 18.3 | 64.94 | 19.4064 | 64.94
1985-05-27 | 27 | 5 | 0.79167 | 17.2 | 62.96 | 18.8037 | 62.96
1985-05-27 | 27 | 5 | 0.83333 | 16.7 | 62.06 | 18.3421 | 62.06
1985-05-27 | 27 | 5 | 0.875 | 15.6 | 60.08 | 17.988 | 60.08
1985-05-27 | 27 | 5 | 0.91667 | 14.4 | 57.92 | 17.6423 |  | 57.92
1985-05-27 | 27 | 5 | 0.95833 | 13.9 | 57.02 | 17.091 |  | 57.02
1985-05-27 | 27 | 5 | 1 | 13.3 | 55.94 | 16.6992 |  | 55.94
1985-05-28 | 28 | 5 | 0.041667 | 12.8 | 55.04 | 16.5751 |  | 55.04
1985-05-28 | 28 | 5 | 0.083333 | 12.2 | 53.96 | 16.8533 |  | 53.96
1985-05-28 | 28 | 5 | 0.125 | 11.7 | 53.06 | 16.6012 |  | 53.06
1985-05-28 | 28 | 5 | 0.16667 | 11.1 | 51.98 | 16.1888 |  | 51.98
1985-05-28 | 28 | 5 | 0.20833 | 10.6 | 51.08 | 16.3653 |  | 51.08
1985-05-28 | 28 | 5 | 0.25 | 11.1 | 51.98 | 16.3667 | 51.98
1985-05-28 | 28 | 5 | 0.29167 | 13.3 | 55.94 | 17.8318 | 55.94
1985-05-28 | 28 | 5 | 0.33333 | 15 | 59 | 18.6279 | 59
1985-05-28 | 28 | 5 | 0.375 | 16.1 | 60.98 | 19.4359 | 60.98
1985-05-28 | 28 | 5 | 0.41667 | 17.2 | 62.96 | 19.4674 | 62.96
1985-05-28 | 28 | 5 | 0.45833 | 18.3 | 64.94 | 19.6912 | 64.94
1985-05-28 | 28 | 5 | 0.5 | 18.9 | 66.02 | 19.9625 | 66.02
1985-05-28 | 28 | 5 | 0.54167 | 20 | 68 | 20.5761 | 68
1985-05-28 | 28 | 5 | 0.58333 | 21.1 | 69.98 | 21.1858 | 69.98
1985-05-28 | 28 | 5 | 0.625 | 21.1 | 69.98 | 23.2314 | 69.98
1985-05-28 | 28 | 5 | 0.66667 | 20.6 | 69.08 | 23.1477 | 69.08
1985-05-28 | 28 | 5 | 0.70833 | 22.2 | 71.96 | 22.1546 | 71.96
1985-05-28 | 28 | 5 | 0.75 | 21.1 | 69.98 | 21.5258 | 69.98
1985-05-28 | 28 | 5 | 0.79167 | 20.6 | 69.08 | 21.1639 | 69.08
1985-05-28 | 28 | 5 | 0.83333 | 19.4 | 66.92 | 20.9228 | 66.92
1985-05-28 | 28 | 5 | 0.875 | 18.3 | 64.94 | 20.4041 | 64.94
1985-05-28 | 28 | 5 | 0.91667 | 17.8 | 64.04 | 20.5894 |  | 64.04
1985-05-28 | 28 | 5 | 0.95833 | 17.2 | 62.96 | 20.2656 |  | 62.96
1985-05-28 | 28 | 5 | 1 | 16.7 | 62.06 | 20.2727 |  | 62.06
1985-05-29 | 29 | 5 | 0.041667 | 16.7 | 62.06 | 20.5309 |  | 62.06
1985-05-29 | 29 | 5 | 0.083333 | 15.6 | 60.08 | 20.2678 |  | 60.08
1985-05-29 | 29 | 5 | 0.125 | 16.1 | 60.98 | 23.3007 |  | 60.98
1985-05-29 | 29 | 5 | 0.16667 | 15 | 59 | 20.2463 |  | 59
1985-05-29 | 29 | 5 | 0.20833 | 14.4 | 57.92 | 19.974 |  | 57.92
1985-05-29 | 29 | 5 | 0.25 | 15.6 | 60.08 | 21.2323 | 60.08
1985-05-29 | 29 | 5 | 0.29167 | 17.8 | 64.04 | 22.5329 | 64.04
1985-05-29 | 29 | 5 | 0.33333 | 18.9 | 66.02 | 22.9344 | 66.02
1985-05-29 | 29 | 5 | 0.375 | 20.6 | 69.08 | 23.4795 | 69.08
1985-05-29 | 29 | 5 | 0.41667 | 22.8 | 73.04 | 24.1152 | 73.04
1985-05-29 | 29 | 5 | 0.45833 | 24.4 | 75.92 | 24.4408 | 75.92
1985-05-29 | 29 | 5 | 0.5 | 25 | 77 | 24.7149 | 77
1985-05-29 | 29 | 5 | 0.54167 | 25.6 | 78.08 | 24.9806 | 78.08
1985-05-29 | 29 | 5 | 0.58333 | 25 | 77 | 26.8915 | 77
1985-05-29 | 29 | 5 | 0.625 | 24.4 | 75.92 | 25.9085 | 75.92
1985-05-29 | 29 | 5 | 0.66667 | 24.4 | 75.92 | 26.5394 | 75.92
1985-05-29 | 29 | 5 | 0.70833 | 23.3 | 73.94 | 25.716 | 73.94
1985-05-29 | 29 | 5 | 0.75 | 21.1 | 69.98 | 25.4613 | 69.98
1985-05-29 | 29 | 5 | 0.79167 | 20 | 68 | 25.3681 | 68
1985-05-29 | 29 | 5 | 0.83333 | 20 | 68 | 25.3681 | 68
1985-05-29 | 29 | 5 | 0.875 | 20.6 | 69.08 | 24.6432 | 69.08
1985-05-29 | 29 | 5 | 0.91667 | 20 | 68 | 22.9637 |  | 68
1985-05-29 | 29 | 5 | 0.95833 | 19.4 | 66.92 | 22.1492 |  | 66.92
1985-05-29 | 29 | 5 | 1 | 18.9 | 66.02 | 22.189 |  | 66.02
1985-05-30 | 30 | 5 | 0.041667 | 18.3 | 64.94 | 21.9777 |  | 64.94
1985-05-30 | 30 | 5 | 0.083333 | 17.8 | 64.04 | 21.9765 |  | 64.04
1985-05-30 | 30 | 5 | 0.125 | 17.8 | 64.04 | 21.9765 |  | 64.04
1985-05-30 | 30 | 5 | 0.16667 | 17.2 | 62.96 | 22.2694 |  | 62.96
1985-05-30 | 30 | 5 | 0.20833 | 16.1 | 60.98 | 20.9267 |  | 60.98
1985-05-30 | 30 | 5 | 0.25 | 17.2 | 62.96 | 23.4773 | 62.96
1985-05-30 | 30 | 5 | 0.29167 | 19.4 | 66.92 | 25.0796 | 66.92
1985-05-30 | 30 | 5 | 0.33333 | 20.6 | 69.08 | 26.3125 | 69.08
1985-05-30 | 30 | 5 | 0.375 | 22.8 | 73.04 | 27.552 | 73.04
1985-05-30 | 30 | 5 | 0.41667 | 24.4 | 75.92 | 28.6509 | 75.92
1985-05-30 | 30 | 5 | 0.45833 | 26.1 | 78.98 | 29.8233 | 78.98
1985-05-30 | 30 | 5 | 0.5 | 26.7 | 80.06 | 30.9733 | 80.06
1985-05-30 | 30 | 5 | 0.54167 | 27.2 | 80.96 | 31.0473 | 80.96
1985-05-30 | 30 | 5 | 0.58333 | 26.7 | 80.06 | 31.4619 | 80.06
1985-05-30 | 30 | 5 | 0.625 | 25 | 77 | 30.6234 | 77
1985-05-30 | 30 | 5 | 0.66667 | 25 | 77 | 30.1822 | 77
1985-05-30 | 30 | 5 | 0.70833 | 21.1 | 69.98 | 27.5326 | 69.98
1985-05-30 | 30 | 5 | 0.75 | 22.8 | 73.04 | 27.936 | 73.04
1985-05-30 | 30 | 5 | 0.79167 | 22.2 | 71.96 | 26.9246 | 71.96
1985-05-30 | 30 | 5 | 0.83333 | 22.2 | 71.96 | 26.1864 | 71.96
1985-05-30 | 30 | 5 | 0.875 | 21.7 | 71.06 | 25.6959 | 71.06
1985-05-30 | 30 | 5 | 0.91667 | 21.1 | 69.98 | 25.8057 |  | 69.98
1985-05-30 | 30 | 5 | 0.95833 | 20.6 | 69.08 | 25.4768 |  | 69.08
1985-05-30 | 30 | 5 | 1 | 20 | 68 | 26.0121 |  | 68
1985-05-31 | 31 | 5 | 0.041667 | 19.4 | 66.92 | 26.4765 |  | 66.92
1985-05-31 | 31 | 5 | 0.083333 | 18.9 | 66.02 | 25.481 |  | 66.02
1985-05-31 | 31 | 5 | 0.125 | 18.9 | 66.02 | 25.9323 |  | 66.02
1985-05-31 | 31 | 5 | 0.16667 | 18.3 | 64.94 | 25.5812 |  | 64.94
1985-05-31 | 31 | 5 | 0.20833 | 17.8 | 64.04 | 25.7498 |  | 64.04
1985-05-31 | 31 | 5 | 0.25 | 18.3 | 64.94 | 26.0162 | 64.94
1985-05-31 | 31 | 5 | 0.29167 | 20 | 68 | 27.1421 | 68
1985-05-31 | 31 | 5 | 0.33333 | 21.1 | 69.98 | 28.0524 | 69.98
1985-05-31 | 31 | 5 | 0.375 | 23.3 | 73.94 | 29.4733 | 73.94
1985-05-31 | 31 | 5 | 0.41667 | 24.4 | 75.92 | 29.9241 | 75.92
1985-05-31 | 31 | 5 | 0.45833 | 26.1 | 78.98 | 30.0583 | 78.98
1985-05-31 | 31 | 5 | 0.5 | 24.4 | 75.92 | 30.3495 | 75.92
1985-05-31 | 31 | 5 | 0.54167 | 25.6 | 78.08 | 30.8795 | 78.08
1985-05-31 | 31 | 5 | 0.58333 | 26.1 | 78.98 | 30.9999 | 78.98
1985-05-31 | 31 | 5 | 0.625 | 25.6 | 78.08 | 30.4221 | 78.08
1985-05-31 | 31 | 5 | 0.66667 | 25.6 | 78.08 | 30.4221 | 78.08
1985-05-31 | 31 | 5 | 0.70833 | 24.4 | 75.92 | 29.9241 | 75.92
1985-05-31 | 31 | 5 | 0.75 | 23.3 | 73.94 | 29.4733 | 73.94
1985-05-31 | 31 | 5 | 0.79167 | 22.2 | 71.96 | 28.9628 | 71.96
1985-05-31 | 31 | 5 | 0.83333 | 21.7 | 71.06 | 28.2055 | 71.06
1985-05-31 | 31 | 5 | 0.875 | 21.1 | 69.98 | 28.0524 | 69.98
1985-05-31 | 31 | 5 | 0.91667 | 20.1 | 68.18 | 27.2544 |  | 68.18
1985-05-31 | 31 | 5 | 0.95833 | 19 | 66.2 | 26.0404 |  | 66.2
1985-05-31 | 31 | 5 | 1 | 18 | 64.4 | 24.9761 |  | 64.4
1999-06-01 | 1 | 6 | 0.041667 | 17 | 62.6 | 27.6901 |  |  |  | 62.6
1999-06-01 | 1 | 6 | 0.083333 | 16 | 60.8 | 26.0776 |  |  |  | 60.8
1999-06-01 | 1 | 6 | 0.125 | 14.9 | 58.82 | 25.2656 |  |  |  | 58.82
1999-06-01 | 1 | 6 | 0.16667 | 13.9 | 57.02 | 23.68 |  |  |  | 57.02
1999-06-01 | 1 | 6 | 0.20833 | 13.9 | 57.02 | 23.244 |  |  |  | 57.02
1999-06-01 | 1 | 6 | 0.25 | 13.3 | 55.94 | 22.7141 |  |  | 55.94
1999-06-01 | 1 | 6 | 0.29167 | 13.9 | 57.02 | 23.0263 |  |  | 57.02
1999-06-01 | 1 | 6 | 0.33333 | 13.9 | 57.02 | 23.0263 |  |  | 57.02
1999-06-01 | 1 | 6 | 0.375 | 13.9 | 57.02 | 22.5911 |  |  | 57.02
1999-06-01 | 1 | 6 | 0.41667 | 15 | 59 | 23.5061 |  |  | 59
1999-06-01 | 1 | 6 | 0.45833 | 16.1 | 60.98 | 24.3052 |  |  | 60.98
1999-06-01 | 1 | 6 | 0.5 | 17.8 | 64.04 | 24.6274 |  |  | 64.04
1999-06-01 | 1 | 6 | 0.54167 | 17.8 | 64.04 | 25.0479 |  |  | 64.04
1999-06-01 | 1 | 6 | 0.58333 | 18.9 | 66.02 | 25.9323 |  |  | 66.02
1999-06-01 | 1 | 6 | 0.625 | 18.9 | 66.02 | 26.2336 |  |  | 66.02
1999-06-01 | 1 | 6 | 0.66667 | 18.9 | 66.02 | 26.2336 |  |  | 66.02
1999-06-01 | 1 | 6 | 0.70833 | 16.1 | 60.98 | 25.4387 |  |  | 60.98
1999-06-01 | 1 | 6 | 0.75 | 16.7 | 62.06 | 25.9995 |  |  | 62.06
1999-06-01 | 1 | 6 | 0.79167 | 16.1 | 60.98 | 25.8174 |  |  | 60.98
1999-06-01 | 1 | 6 | 0.83333 | 15.6 | 60.08 | 25.6064 |  |  | 60.08
1999-06-01 | 1 | 6 | 0.875 | 15.6 | 60.08 | 25.6064 |  |  | 60.08
1999-06-01 | 1 | 6 | 0.91667 | 15.6 | 60.08 | 25.6064 |  |  |  | 60.08
1999-06-01 | 1 | 6 | 0.95833 | 15.6 | 60.08 | 25.6064 |  |  |  | 60.08
1999-06-01 | 1 | 6 | 1 | 15.6 | 60.08 | 25.9735 |  |  |  | 60.08
1999-06-02 | 2 | 6 | 0.041667 | 16.7 | 62.06 | 25.9995 |  |  |  | 62.06
1999-06-02 | 2 | 6 | 0.083333 | 16.7 | 62.06 | 25.2129 |  |  |  | 62.06
1999-06-02 | 2 | 6 | 0.125 | 16.7 | 62.06 | 24.9511 |  |  |  | 62.06
1999-06-02 | 2 | 6 | 0.16667 | 16.1 | 60.98 | 24.3052 |  |  |  | 60.98
1999-06-02 | 2 | 6 | 0.20833 | 16.7 | 62.06 | 24.1669 |  |  |  | 62.06
1999-06-02 | 2 | 6 | 0.25 | 17.2 | 62.96 | 24.6895 |  |  | 62.96
1999-06-02 | 2 | 6 | 0.29167 | 18.3 | 64.94 | 25.2916 |  |  | 64.94
1999-06-02 | 2 | 6 | 0.33333 | 20 | 68 | 25.3681 |  |  | 68
1999-06-02 | 2 | 6 | 0.375 | 21.7 | 71.06 | 26.4111 |  |  | 71.06
1999-06-02 | 2 | 6 | 0.41667 | 23.3 | 73.94 | 27.0955 |  |  | 73.94
1999-06-02 | 2 | 6 | 0.45833 | 24.4 | 75.92 | 27.1715 |  |  | 75.92
1999-06-02 | 2 | 6 | 0.5 | 25 | 77 | 27.5471 |  |  | 77
1999-06-02 | 2 | 6 | 0.54167 | 25.6 | 78.08 | 28.1444 |  |  | 78.08
1999-06-02 | 2 | 6 | 0.58333 | 26.1 | 78.98 | 28.4166 |  |  | 78.98
1999-06-02 | 2 | 6 | 0.625 | 26.7 | 80.06 | 28.2984 |  |  | 80.06
1999-06-02 | 2 | 6 | 0.66667 | 26.7 | 80.06 | 27.5724 |  |  | 80.06
1999-06-02 | 2 | 6 | 0.70833 | 21.1 | 69.98 | 28.0524 |  |  | 69.98
1999-06-02 | 2 | 6 | 0.75 | 22.2 | 71.96 | 26.9246 |  |  | 71.96
1999-06-02 | 2 | 6 | 0.79167 | 22.8 | 73.04 | 27.936 |  |  | 73.04
1999-06-02 | 2 | 6 | 0.83333 | 19.4 | 66.92 | 26.1656 |  |  | 66.92
1999-06-02 | 2 | 6 | 0.875 | 20 | 68 | 26.0121 |  |  | 68
1999-06-02 | 2 | 6 | 0.91667 | 20 | 68 | 26.0121 |  |  |  | 68
1999-06-02 | 2 | 6 | 0.95833 | 20 | 68 | 26.0121 |  |  |  | 68
1999-06-02 | 2 | 6 | 1 | 19.4 | 66.92 | 26.1656 |  |  |  | 66.92
1999-06-03 | 3 | 6 | 0.041667 | 19.4 | 66.92 | 26.1656 |  |  |  | 66.92
1999-06-03 | 3 | 6 | 0.083333 | 18.9 | 66.02 | 26.2336 |  |  |  | 66.02
1999-06-03 | 3 | 6 | 0.125 | 17.8 | 64.04 | 26.1716 |  |  |  | 64.04
1999-06-03 | 3 | 6 | 0.16667 | 17.2 | 62.96 | 26.3124 |  |  |  | 62.96
1999-06-03 | 3 | 6 | 0.20833 | 17.2 | 62.96 | 25.9059 |  |  |  | 62.96
1999-06-03 | 3 | 6 | 0.25 | 16.7 | 62.06 | 25.7371 |  |  | 62.06
1999-06-03 | 3 | 6 | 0.29167 | 17.2 | 62.96 | 25.5 |  |  | 62.96
1999-06-03 | 3 | 6 | 0.33333 | 17.8 | 64.04 | 25.0479 |  |  | 64.04
1999-06-03 | 3 | 6 | 0.375 | 18.9 | 66.02 | 25.1804 |  |  | 66.02
1999-06-03 | 3 | 6 | 0.41667 | 20 | 68 | 25.3681 |  |  | 68
1999-06-03 | 3 | 6 | 0.45833 | 21.1 | 69.98 | 25.1173 |  |  | 69.98
1999-06-03 | 3 | 6 | 0.5 | 22.2 | 71.96 | 25.0821 |  |  | 71.96
1999-06-03 | 3 | 6 | 0.54167 | 22.8 | 73.04 | 25.257 |  |  | 73.04
1999-06-03 | 3 | 6 | 0.58333 | 22.8 | 73.04 | 25.257 |  |  | 73.04
1999-06-03 | 3 | 6 | 0.625 | 23.9 | 75.02 | 25.2564 |  |  | 75.02
1999-06-03 | 3 | 6 | 0.66667 | 25 | 77 | 25.5839 |  |  | 77
1999-06-03 | 3 | 6 | 0.70833 | 24.4 | 75.92 | 24.8595 |  |  | 75.92
1999-06-03 | 3 | 6 | 0.75 | 23.3 | 73.94 | 25.1265 |  |  | 73.94
1999-06-03 | 3 | 6 | 0.79167 | 22.2 | 71.96 | 25.2659 |  |  | 71.96
1999-06-03 | 3 | 6 | 0.83333 | 22.8 | 73.04 | 25.257 |  |  | 73.04
1999-06-03 | 3 | 6 | 0.875 | 20.6 | 69.08 | 25.3099 |  |  | 69.08
1999-06-03 | 3 | 6 | 0.91667 | 21.1 | 69.98 | 24.7736 |  |  |  | 69.98
1999-06-03 | 3 | 6 | 0.95833 | 20 | 68 | 24.0837 |  |  |  | 68
1999-06-03 | 3 | 6 | 1 | 19.4 | 66.92 | 23.9971 |  |  |  | 66.92
1999-06-04 | 4 | 6 | 0.041667 | 18.9 | 66.02 | 23.233 |  |  |  | 66.02
1999-06-04 | 4 | 6 | 0.083333 | 17.8 | 64.04 | 22.5329 |  |  |  | 64.04
1999-06-04 | 4 | 6 | 0.125 | 16.7 | 62.06 | 22.0845 |  |  |  | 62.06
1999-06-04 | 4 | 6 | 0.16667 | 16.1 | 60.98 | 21.5499 |  |  |  | 60.98
1999-06-04 | 4 | 6 | 0.20833 | 15.6 | 60.08 | 21.2323 |  |  |  | 60.08
1999-06-04 | 4 | 6 | 0.25 | 16.1 | 60.98 | 21.5499 |  |  | 60.98
1999-06-04 | 4 | 6 | 0.29167 | 16.7 | 62.06 | 21.5659 |  |  | 62.06
1999-06-04 | 4 | 6 | 0.33333 | 17.2 | 62.96 | 21.7339 |  |  | 62.96
1999-06-04 | 4 | 6 | 0.375 | 18.3 | 64.94 | 21.6911 |  |  | 64.94
1999-06-04 | 4 | 6 | 0.41667 | 18.9 | 66.02 | 22.487 |  |  | 66.02
1999-06-04 | 4 | 6 | 0.45833 | 20 | 68 | 22.9637 |  |  | 68
1999-06-04 | 4 | 6 | 0.5 | 21.1 | 69.98 | 23.4024 |  |  | 69.98
1999-06-04 | 4 | 6 | 0.54167 | 22.2 | 71.96 | 23.9814 |  |  | 71.96
1999-06-04 | 4 | 6 | 0.58333 | 21.1 | 69.98 | 23.4024 |  |  | 69.98
1999-06-04 | 4 | 6 | 0.625 | 20.6 | 69.08 | 23.1477 |  |  | 69.08
1999-06-04 | 4 | 6 | 0.66667 | 20 | 68 | 22.9637 |  |  | 68
1999-06-04 | 4 | 6 | 0.70833 | 19.4 | 66.92 | 23.2259 |  |  | 66.92
1999-06-04 | 4 | 6 | 0.75 | 17.8 | 64.04 | 23.0902 |  |  | 64.04
1999-06-04 | 4 | 6 | 0.79167 | 18.3 | 64.94 | 22.4081 |  |  | 64.94
1999-06-04 | 4 | 6 | 0.83333 | 17.8 | 64.04 | 22.8114 |  |  | 64.04
1999-06-04 | 4 | 6 | 0.875 | 17.2 | 62.96 | 23.0742 |  |  | 62.96
1999-06-04 | 4 | 6 | 0.91667 | 17.2 | 62.96 | 23.0742 |  |  |  | 62.96
1999-06-04 | 4 | 6 | 0.95833 | 17.2 | 62.96 | 23.4773 |  |  |  | 62.96
1999-06-04 | 4 | 6 | 1 | 16.7 | 62.06 | 23.5148 |  |  |  | 62.06
1999-06-05 | 5 | 6 | 0.041667 | 16.1 | 60.98 | 23.9281 |  |  |  | 60.98
1999-06-05 | 5 | 6 | 0.083333 | 16.1 | 60.98 | 24.3052 |  |  |  | 60.98
1999-06-05 | 5 | 6 | 0.125 | 16.1 | 60.98 | 24.6826 |  |  |  | 60.98
1999-06-05 | 5 | 6 | 0.16667 | 15.6 | 60.08 | 24.3858 |  |  |  | 60.08
1999-06-05 | 5 | 6 | 0.20833 | 15.6 | 60.08 | 24.3858 |  |  |  | 60.08
1999-06-05 | 5 | 6 | 0.25 | 15.6 | 60.08 | 23.7771 |  |  | 60.08
1999-06-05 | 5 | 6 | 0.29167 | 16.1 | 60.98 | 23.5515 |  |  | 60.98
1999-06-05 | 5 | 6 | 0.33333 | 16.7 | 62.06 | 23.9059 |  |  | 62.06
1999-06-05 | 5 | 6 | 0.375 | 17.2 | 62.96 | 23.4773 |  |  | 62.96
1999-06-05 | 5 | 6 | 0.41667 | 18.3 | 64.94 | 24.8575 |  |  | 64.94
1999-06-05 | 5 | 6 | 0.45833 | 18.9 | 66.02 | 22.487 |  |  | 66.02
1999-06-05 | 5 | 6 | 0.5 | 17.2 | 62.96 | 24.6895 |  |  | 62.96
1999-06-05 | 5 | 6 | 0.54167 | 16.7 | 62.06 | 24.1669 |  |  | 62.06
1999-06-05 | 5 | 6 | 0.58333 | 16.7 | 62.06 | 24.1669 |  |  | 62.06
1999-06-05 | 5 | 6 | 0.625 | 16.7 | 62.06 | 23.9059 |  |  | 62.06
1999-06-05 | 5 | 6 | 0.66667 | 16.7 | 62.06 | 23.5148 |  |  | 62.06
1999-06-05 | 5 | 6 | 0.70833 | 16.1 | 60.98 | 23.3007 |  |  | 60.98
1999-06-05 | 5 | 6 | 0.75 | 16.1 | 60.98 | 22.9247 |  |  | 60.98
1999-06-05 | 5 | 6 | 0.79167 | 16.1 | 60.98 | 23.3007 |  |  | 60.98
1999-06-05 | 5 | 6 | 0.83333 | 16.1 | 60.98 | 23.9281 |  |  | 60.98
1999-06-05 | 5 | 6 | 0.875 | 16.1 | 60.98 | 23.9281 |  |  | 60.98
1999-06-05 | 5 | 6 | 0.91667 | 15.6 | 60.08 | 24.0204 |  |  |  | 60.08
1999-06-05 | 5 | 6 | 0.95833 | 15.6 | 60.08 | 24.0204 |  |  |  | 60.08
1999-06-05 | 5 | 6 | 1 | 15 | 59 | 24.2087 |  |  |  | 59
1999-06-06 | 6 | 6 | 0.041667 | 15 | 59 | 23.5061 |  |  |  | 59
1999-06-06 | 6 | 6 | 0.083333 | 15 | 59 | 23.7401 |  |  |  | 59
1999-06-06 | 6 | 6 | 0.125 | 14.4 | 57.92 | 22.8831 |  |  |  | 57.92
1999-06-06 | 6 | 6 | 0.16667 | 14.4 | 57.92 | 22.8831 |  |  |  | 57.92
1999-06-06 | 6 | 6 | 0.20833 | 13.9 | 57.02 | 22.5911 |  |  |  | 57.02
1999-06-06 | 6 | 6 | 0.25 | 13.9 | 57.02 | 23.0263 |  |  | 57.02
1999-06-06 | 6 | 6 | 0.29167 | 13.3 | 55.94 | 23.0282 |  |  | 55.94
1999-06-06 | 6 | 6 | 0.33333 | 13.3 | 55.94 | 23.4473 |  |  | 55.94
1999-06-06 | 6 | 6 | 0.375 | 13.3 | 55.94 | 23.4473 |  |  | 55.94
1999-06-06 | 6 | 6 | 0.41667 | 13.9 | 57.02 | 24.0074 |  |  | 57.02
1999-06-06 | 6 | 6 | 0.45833 | 13.9 | 57.02 | 23.68 |  |  | 57.02
1999-06-06 | 6 | 6 | 0.5 | 14.4 | 57.92 | 24.2342 |  |  | 57.92
1999-06-06 | 6 | 6 | 0.54167 | 15.6 | 60.08 | 24.3858 |  |  | 60.08
1999-06-06 | 6 | 6 | 0.58333 | 15 | 59 | 24.2087 |  |  | 59
1999-06-06 | 6 | 6 | 0.625 | 15.6 | 60.08 | 24.3858 |  |  | 60.08
1999-06-06 | 6 | 6 | 0.66667 | 15.6 | 60.08 | 24.3858 |  |  | 60.08
1999-06-06 | 6 | 6 | 0.70833 | 14.4 | 57.92 | 24.2342 |  |  | 57.92
1999-06-06 | 6 | 6 | 0.75 | 15 | 59 | 24.5605 |  |  | 59
1999-06-06 | 6 | 6 | 0.79167 | 15 | 59 | 24.5605 |  |  | 59
1999-06-06 | 6 | 6 | 0.83333 | 15 | 59 | 24.5605 |  |  | 59
1999-06-06 | 6 | 6 | 0.875 | 15 | 59 | 24.2087 |  |  | 59
1999-06-06 | 6 | 6 | 0.91667 | 15 | 59 | 24.2087 |  |  |  | 59
1999-06-06 | 6 | 6 | 0.95833 | 15.6 | 60.08 | 24.3858 |  |  |  | 60.08
1999-06-06 | 6 | 6 | 1 | 15 | 59 | 24.2087 |  |  |  | 59
1999-06-07 | 7 | 6 | 0.041667 | 15.6 | 60.08 | 24.3858 |  |  |  | 60.08
1999-06-07 | 7 | 6 | 0.083333 | 16.1 | 60.98 | 24.6826 |  |  |  | 60.98
1999-06-07 | 7 | 6 | 0.125 | 15.6 | 60.08 | 24.3858 |  |  |  | 60.08
1999-06-07 | 7 | 6 | 0.16667 | 16.1 | 60.98 | 24.9345 |  |  |  | 60.98
1999-06-07 | 7 | 6 | 0.20833 | 16.1 | 60.98 | 24.9345 |  |  |  | 60.98
1999-06-07 | 7 | 6 | 0.25 | 16.1 | 60.98 | 25.4387 |  |  | 60.98
1999-06-07 | 7 | 6 | 0.29167 | 17.2 | 62.96 | 25.5 |  |  | 62.96
1999-06-07 | 7 | 6 | 0.33333 | 17.8 | 64.04 | 25.7498 |  |  | 64.04
1999-06-07 | 7 | 6 | 0.375 | 19.4 | 66.92 | 26.7877 |  |  | 66.92
1999-06-07 | 7 | 6 | 0.41667 | 20.6 | 69.08 | 28.1581 |  |  | 69.08
1999-06-07 | 7 | 6 | 0.45833 | 22.8 | 73.04 | 30.0556 |  |  | 73.04
1999-06-07 | 7 | 6 | 0.5 | 23.3 | 73.94 | 29.8712 |  |  | 73.94
1999-06-07 | 7 | 6 | 0.54167 | 25.6 | 78.08 | 31.3374 |  |  | 78.08
1999-06-07 | 7 | 6 | 0.58333 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1999-06-07 | 7 | 6 | 0.625 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1999-06-07 | 7 | 6 | 0.66667 | 25 | 77 | 31.5074 |  |  | 77
1999-06-07 | 7 | 6 | 0.70833 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1999-06-07 | 7 | 6 | 0.75 | 25 | 77 | 31.5074 |  |  | 77
1999-06-07 | 7 | 6 | 0.79167 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1999-06-07 | 7 | 6 | 0.83333 | 26.1 | 78.98 | 30.9999 |  |  | 78.98
1999-06-07 | 7 | 6 | 0.875 | 25.6 | 78.08 | 30.8795 |  |  | 78.08
1999-06-07 | 7 | 6 | 0.91667 | 25 | 77 | 30.6234 |  |  |  | 77
1999-06-07 | 7 | 6 | 0.95833 | 24.4 | 75.92 | 29.9241 |  |  |  | 75.92
1999-06-07 | 7 | 6 | 1 | 23.3 | 73.94 | 29.8712 |  |  |  | 73.94
1999-06-08 | 8 | 6 | 0.041667 | 22.8 | 73.04 | 28.7052 |  |  |  | 73.04
1999-06-08 | 8 | 6 | 0.083333 | 22.2 | 71.96 | 28.9628 |  |  |  | 71.96
1999-06-08 | 8 | 6 | 0.125 | 22.2 | 71.96 | 29.3347 |  |  |  | 71.96
1999-06-08 | 8 | 6 | 0.16667 | 21.7 | 71.06 | 29.4671 |  |  |  | 71.06
1999-06-08 | 8 | 6 | 0.20833 | 21.1 | 69.98 | 29.2683 |  |  |  | 69.98
1999-06-08 | 8 | 6 | 0.25 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1999-06-08 | 8 | 6 | 0.29167 | 22.2 | 71.96 | 30.6394 |  |  | 71.96
1999-06-08 | 8 | 6 | 0.33333 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1999-06-08 | 8 | 6 | 0.375 | 26.1 | 78.98 | 31.9441 |  |  | 78.98
1999-06-08 | 8 | 6 | 0.41667 | 27.8 | 82.04 | 32.7787 |  |  | 82.04
1999-06-08 | 8 | 6 | 0.45833 | 28.9 | 84.02 | 33.5879 |  |  | 84.02
1999-06-08 | 8 | 6 | 0.5 | 29.4 | 84.92 | 33.3475 |  |  | 84.92
1999-06-08 | 8 | 6 | 0.54167 | 30.6 | 87.08 | 32.9736 |  |  | 87.08
1999-06-08 | 8 | 6 | 0.58333 | 30.6 | 87.08 | 32.6665 |  |  | 87.08
1999-06-08 | 8 | 6 | 0.625 | 30.6 | 87.08 | 32.9736 |  |  | 87.08
1999-06-08 | 8 | 6 | 0.66667 | 31.1 | 87.98 | 33.5498 |  |  | 87.98
1999-06-08 | 8 | 6 | 0.70833 | 30.6 | 87.08 | 33.8964 |  |  | 87.08
1999-06-08 | 8 | 6 | 0.75 | 28.9 | 84.02 | 33.5879 |  |  | 84.02
1999-06-08 | 8 | 6 | 0.79167 | 28.9 | 84.02 | 32.1941 |  |  | 84.02
1999-06-08 | 8 | 6 | 0.83333 | 27.8 | 82.04 | 31.734 |  |  | 82.04
1999-06-08 | 8 | 6 | 0.875 | 27.8 | 82.04 | 31.4733 |  |  | 82.04
1999-06-08 | 8 | 6 | 0.91667 | 26.7 | 80.06 | 32.6863 |  |  |  | 80.06
1999-06-08 | 8 | 6 | 0.95833 | 25 | 77 | 31.9502 |  |  |  | 77
1999-06-08 | 8 | 6 | 1 | 24.4 | 75.92 | 32.2704 |  |  |  | 75.92
1999-06-09 | 9 | 6 | 0.041667 | 24.4 | 75.92 | 31.6289 |  |  |  | 75.92
1999-06-09 | 9 | 6 | 0.083333 | 23.3 | 73.94 | 31.2674 |  |  |  | 73.94
1999-06-09 | 9 | 6 | 0.125 | 22.8 | 73.04 | 31.4112 |  |  |  | 73.04
1999-06-09 | 9 | 6 | 0.16667 | 22.8 | 73.04 | 31.9938 |  |  |  | 73.04
1999-06-09 | 9 | 6 | 0.20833 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
1999-06-09 | 9 | 6 | 0.25 | 22.8 | 73.04 | 32.5774 |  |  | 73.04
1999-06-09 | 9 | 6 | 0.29167 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1999-06-09 | 9 | 6 | 0.33333 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
1999-06-09 | 9 | 6 | 0.375 | 28.3 | 82.94 | 35.5585 |  |  | 82.94
1999-06-09 | 9 | 6 | 0.41667 | 30 | 86 | 36.768 |  |  | 86
1999-06-09 | 9 | 6 | 0.45833 | 31.1 | 87.98 | 37.3688 |  |  | 87.98
1999-06-09 | 9 | 6 | 0.5 | 32.8 | 91.04 | 38.0415 |  |  | 91.04
1999-06-09 | 9 | 6 | 0.54167 | 32.8 | 91.04 | 38.0415 |  |  | 91.04
1999-06-09 | 9 | 6 | 0.58333 | 33.9 | 93.02 | 36.9594 |  |  | 93.02
1999-06-09 | 9 | 6 | 0.625 | 34.4 | 93.92 | 37.2183 |  |  | 93.92
1999-06-09 | 9 | 6 | 0.66667 | 34.4 | 93.92 | 37.6029 |  |  | 93.92
1999-06-09 | 9 | 6 | 0.70833 | 33.9 | 93.02 | 36.5859 |  |  | 93.02
1999-06-09 | 9 | 6 | 0.75 | 33.3 | 91.94 | 36.5624 |  |  | 91.94
1999-06-09 | 9 | 6 | 0.79167 | 32.2 | 89.96 | 36.5451 |  |  | 89.96
1999-06-09 | 9 | 6 | 0.83333 | 31.7 | 89.06 | 36.8881 |  |  | 89.06
1999-06-09 | 9 | 6 | 0.875 | 31.1 | 87.98 | 37.3688 |  |  | 87.98
1999-06-09 | 9 | 6 | 0.91667 | 31.1 | 87.98 | 36.7294 |  |  |  | 87.98
1999-06-09 | 9 | 6 | 0.95833 | 30 | 86 | 36.1682 |  |  |  | 86
1999-06-09 | 9 | 6 | 1 | 26.7 | 80.06 | 33.669 |  |  |  | 80.06
1999-06-10 | 10 | 6 | 0.041667 | 25 | 77 | 32.8375 |  |  |  | 77
1999-06-10 | 10 | 6 | 0.083333 | 24.4 | 75.92 | 32.6987 |  |  |  | 75.92
1999-06-10 | 10 | 6 | 0.125 | 24.4 | 75.92 | 32.6987 |  |  |  | 75.92
1999-06-10 | 10 | 6 | 0.16667 | 24.4 | 75.92 | 33.1275 |  |  |  | 75.92
1999-06-10 | 10 | 6 | 0.20833 | 23.9 | 75.02 | 33.0805 |  |  |  | 75.02
1999-06-10 | 10 | 6 | 0.25 | 25 | 77 | 33.9499 |  |  | 77
1999-06-10 | 10 | 6 | 0.29167 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1999-06-10 | 10 | 6 | 0.33333 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1999-06-10 | 10 | 6 | 0.375 | 26.1 | 78.98 | 35.0304 |  |  | 78.98
1999-06-10 | 10 | 6 | 0.41667 | 26.7 | 80.06 | 35.3954 |  |  | 80.06
1999-06-10 | 10 | 6 | 0.45833 | 26.1 | 78.98 | 35.7466 |  |  | 78.98
1999-06-10 | 10 | 6 | 0.5 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
1999-06-10 | 10 | 6 | 0.54167 | 25 | 77 | 34.6191 |  |  | 77
1999-06-10 | 10 | 6 | 0.58333 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1999-06-10 | 10 | 6 | 0.625 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1999-06-10 | 10 | 6 | 0.66667 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1999-06-10 | 10 | 6 | 0.70833 | 21.7 | 71.06 | 30.5522 |  |  | 71.06
1999-06-10 | 10 | 6 | 0.75 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1999-06-10 | 10 | 6 | 0.79167 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1999-06-10 | 10 | 6 | 0.83333 | 19.4 | 66.92 | 28.9739 |  |  | 66.92
1999-06-10 | 10 | 6 | 0.875 | 19.4 | 66.92 | 28.5043 |  |  | 66.92
1999-06-10 | 10 | 6 | 0.91667 | 19.4 | 66.92 | 27.7229 |  |  |  | 66.92
1999-06-10 | 10 | 6 | 0.95833 | 20 | 68 | 27.4656 |  |  |  | 68
1999-06-10 | 10 | 6 | 1 | 18.9 | 66.02 | 25.9323 |  |  |  | 66.02
1999-06-11 | 11 | 6 | 0.041667 | 18.9 | 66.02 | 25.1804 |  |  |  | 66.02
1999-06-11 | 11 | 6 | 0.083333 | 18.9 | 66.02 | 26.6859 |  |  |  | 66.02
1999-06-11 | 11 | 6 | 0.125 | 18.3 | 64.94 | 26.7424 |  |  |  | 64.94
1999-06-11 | 11 | 6 | 0.16667 | 18.3 | 64.94 | 25.2916 |  |  |  | 64.94
1999-06-11 | 11 | 6 | 0.20833 | 17.8 | 64.04 | 23.3691 |  |  |  | 64.04
1999-06-11 | 11 | 6 | 0.25 | 17.8 | 64.04 | 22.5329 |  |  | 64.04
1999-06-11 | 11 | 6 | 0.29167 | 17.2 | 62.96 | 21.4665 |  |  | 62.96
1999-06-11 | 11 | 6 | 0.33333 | 17.8 | 64.04 | 21.9765 |  |  | 64.04
1999-06-11 | 11 | 6 | 0.375 | 18.9 | 66.02 | 22.487 |  |  | 66.02
1999-06-11 | 11 | 6 | 0.41667 | 18.9 | 66.02 | 21.2966 |  |  | 66.02
1999-06-11 | 11 | 6 | 0.45833 | 18.9 | 66.02 | 22.0401 |  |  | 66.02
1999-06-11 | 11 | 6 | 0.5 | 20 | 68 | 21.0523 |  |  | 68
1999-06-11 | 11 | 6 | 0.54167 | 20.6 | 69.08 | 22.1544 |  |  | 69.08
1999-06-11 | 11 | 6 | 0.58333 | 20 | 68 | 22.166 |  |  | 68
1999-06-11 | 11 | 6 | 0.625 | 21.1 | 69.98 | 22.7188 |  |  | 69.98
1999-06-11 | 11 | 6 | 0.66667 | 21.1 | 69.98 | 23.2314 |  |  | 69.98
1999-06-11 | 11 | 6 | 0.70833 | 21.1 | 69.98 | 22.8896 |  |  | 69.98
1999-06-11 | 11 | 6 | 0.75 | 21.1 | 69.98 | 23.4024 |  |  | 69.98
1999-06-11 | 11 | 6 | 0.79167 | 19.4 | 66.92 | 23.5342 |  |  | 66.92
1999-06-11 | 11 | 6 | 0.83333 | 18.9 | 66.02 | 23.5319 |  |  | 66.02
1999-06-11 | 11 | 6 | 0.875 | 18.3 | 64.94 | 23.8468 |  |  | 64.94
1999-06-11 | 11 | 6 | 0.91667 | 18.3 | 64.94 | 24.2796 |  |  |  | 64.94
1999-06-11 | 11 | 6 | 0.95833 | 18.3 | 64.94 | 24.8575 |  |  |  | 64.94
1999-06-11 | 11 | 6 | 1 | 18.3 | 64.94 | 25.2916 |  |  |  | 64.94
1999-06-12 | 12 | 6 | 0.041667 | 17.8 | 64.04 | 24.6274 |  |  |  | 64.04
1999-06-12 | 12 | 6 | 0.083333 | 16.1 | 60.98 | 23.9281 |  |  |  | 60.98
1999-06-12 | 12 | 6 | 0.125 | 16.1 | 60.98 | 22.2991 |  |  |  | 60.98
1999-06-12 | 12 | 6 | 0.16667 | 15.6 | 60.08 | 20.7497 |  |  |  | 60.08
1999-06-12 | 12 | 6 | 0.20833 | 15.6 | 60.08 | 20.7497 |  |  |  | 60.08
1999-06-12 | 12 | 6 | 0.25 | 16.1 | 60.98 | 20.3048 |  |  | 60.98
1999-06-12 | 12 | 6 | 0.29167 | 17.2 | 62.96 | 20.5321 |  |  | 62.96
1999-06-12 | 12 | 6 | 0.33333 | 18.3 | 64.94 | 21.2615 |  |  | 64.94
1999-06-12 | 12 | 6 | 0.375 | 20 | 68 | 21.3701 |  |  | 68
1999-06-12 | 12 | 6 | 0.41667 | 21.1 | 69.98 | 21.5258 |  |  | 69.98
1999-06-12 | 12 | 6 | 0.45833 | 21.7 | 71.06 | 22.4961 |  |  | 71.06
1999-06-12 | 12 | 6 | 0.5 | 22.2 | 71.96 | 22.8841 |  |  | 71.96
1999-06-12 | 12 | 6 | 0.54167 | 23.3 | 73.94 | 22.9735 |  |  | 73.94
1999-06-12 | 12 | 6 | 0.58333 | 23.9 | 75.02 | 22.4181 |  |  | 75.02
1999-06-12 | 12 | 6 | 0.625 | 24.4 | 75.92 | 22.9793 |  |  | 75.92
1999-06-12 | 12 | 6 | 0.66667 | 24.4 | 75.92 | 22.9793 |  |  | 75.92
1999-06-12 | 12 | 6 | 0.70833 | 23.9 | 75.02 | 23.0243 |  |  | 75.02
1999-06-12 | 12 | 6 | 0.75 | 22.2 | 71.96 | 23.9814 |  |  | 71.96
1999-06-12 | 12 | 6 | 0.79167 | 20.6 | 69.08 | 23.4795 |  |  | 69.08
1999-06-12 | 12 | 6 | 0.83333 | 19.4 | 66.92 | 23.5342 |  |  | 66.92
1999-06-12 | 12 | 6 | 0.875 | 19.4 | 66.92 | 22.4565 |  |  | 66.92
1999-06-12 | 12 | 6 | 0.91667 | 19.4 | 66.92 | 22.764 |  |  |  | 66.92
1999-06-12 | 12 | 6 | 0.95833 | 18.9 | 66.02 | 21.7425 |  |  |  | 66.02
1999-06-12 | 12 | 6 | 1 | 18.3 | 64.94 | 22.2646 |  |  |  | 64.94
1999-06-13 | 13 | 6 | 0.041667 | 18.3 | 64.94 | 21.9777 |  |  |  | 64.94
1999-06-13 | 13 | 6 | 0.083333 | 17.8 | 64.04 | 22.2545 |  |  |  | 64.04
1999-06-13 | 13 | 6 | 0.125 | 17.2 | 62.96 | 22.5374 |  |  |  | 62.96
1999-06-13 | 13 | 6 | 0.16667 | 17.2 | 62.96 | 22.8057 |  |  |  | 62.96
1999-06-13 | 13 | 6 | 0.20833 | 16.7 | 62.06 | 22.8639 |  |  |  | 62.06
1999-06-13 | 13 | 6 | 0.25 | 17.2 | 62.96 | 23.4773 |  |  | 62.96
1999-06-13 | 13 | 6 | 0.29167 | 18.3 | 64.94 | 24.5684 |  |  | 64.94
1999-06-13 | 13 | 6 | 0.33333 | 18.9 | 66.02 | 24.58 |  |  | 66.02
1999-06-13 | 13 | 6 | 0.375 | 20 | 68 | 24.7253 |  |  | 68
1999-06-13 | 13 | 6 | 0.41667 | 21.7 | 71.06 | 24.8041 |  |  | 71.06
1999-06-13 | 13 | 6 | 0.45833 | 22.2 | 71.96 | 26.1864 |  |  | 71.96
1999-06-13 | 13 | 6 | 0.5 | 23.3 | 73.94 | 25.5194 |  |  | 73.94
1999-06-13 | 13 | 6 | 0.54167 | 23.3 | 73.94 | 23.5593 |  |  | 73.94
1999-06-13 | 13 | 6 | 0.58333 | 22.8 | 73.04 | 23.3561 |  |  | 73.04
1999-06-13 | 13 | 6 | 0.625 | 22.2 | 71.96 | 24.1646 |  |  | 71.96
1999-06-13 | 13 | 6 | 0.66667 | 21.1 | 69.98 | 24.7736 |  |  | 69.98
1999-06-13 | 13 | 6 | 0.70833 | 19.4 | 66.92 | 23.8427 |  |  | 66.92
1999-06-13 | 13 | 6 | 0.75 | 18.9 | 66.02 | 24.1304 |  |  | 66.02
1999-06-13 | 13 | 6 | 0.79167 | 18.3 | 64.94 | 23.8468 |  |  | 64.94
1999-06-13 | 13 | 6 | 0.83333 | 18.3 | 64.94 | 24.8575 |  |  | 64.94
1999-06-13 | 13 | 6 | 0.875 | 17.8 | 64.04 | 24.6274 |  |  | 64.04
1999-06-13 | 13 | 6 | 0.91667 | 17.8 | 64.04 | 26.1716 |  |  |  | 64.04
1999-06-13 | 13 | 6 | 0.95833 | 18.3 | 64.94 | 26.0162 |  |  |  | 64.94
1999-06-13 | 13 | 6 | 1 | 18.3 | 64.94 | 26.7424 |  |  |  | 64.94
1999-06-14 | 14 | 6 | 0.041667 | 18.3 | 64.94 | 27.1788 |  |  |  | 64.94
1999-06-14 | 14 | 6 | 0.083333 | 18.3 | 64.94 | 27.6159 |  |  |  | 64.94
1999-06-14 | 14 | 6 | 0.125 | 18.3 | 64.94 | 27.6159 |  |  |  | 64.94
1999-06-14 | 14 | 6 | 0.16667 | 18.9 | 66.02 | 27.4412 |  |  |  | 66.02
1999-06-14 | 14 | 6 | 0.20833 | 20 | 68 | 27.4656 |  |  |  | 68
1999-06-14 | 14 | 6 | 0.25 | 20 | 68 | 27.9515 |  |  | 68
1999-06-14 | 14 | 6 | 0.29167 | 20.6 | 69.08 | 29.0003 |  |  | 69.08
1999-06-14 | 14 | 6 | 0.33333 | 21.7 | 71.06 | 31.096 |  |  | 71.06
1999-06-14 | 14 | 6 | 0.375 | 21.7 | 71.06 | 31.459 |  |  | 71.06
1999-06-14 | 14 | 6 | 0.41667 | 23.3 | 73.94 | 32.6693 |  |  | 73.94
1999-06-14 | 14 | 6 | 0.45833 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1999-06-14 | 14 | 6 | 0.5 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1999-06-14 | 14 | 6 | 0.54167 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1999-06-14 | 14 | 6 | 0.58333 | 25 | 77 | 33.9499 |  |  | 77
1999-06-14 | 14 | 6 | 0.625 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
1999-06-14 | 14 | 6 | 0.66667 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
1999-06-14 | 14 | 6 | 0.70833 | 25 | 77 | 33.9499 |  |  | 77
1999-06-14 | 14 | 6 | 0.75 | 25 | 77 | 33.9499 |  |  | 77
1999-06-14 | 14 | 6 | 0.79167 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1999-06-14 | 14 | 6 | 0.83333 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1999-06-14 | 14 | 6 | 0.875 | 22.8 | 73.04 | 31.9938 |  |  | 73.04
1999-06-14 | 14 | 6 | 0.91667 | 22.2 | 71.96 | 32.3241 |  |  |  | 71.96
1999-06-14 | 14 | 6 | 0.95833 | 21.1 | 69.98 | 31.1876 |  |  |  | 69.98
1999-06-14 | 14 | 6 | 1 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
1999-06-15 | 15 | 6 | 0.041667 | 22.2 | 71.96 | 32.6996 |  |  |  | 71.96
1999-06-15 | 15 | 6 | 0.083333 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1999-06-15 | 15 | 6 | 0.125 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1999-06-15 | 15 | 6 | 0.16667 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1999-06-15 | 15 | 6 | 0.20833 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
1999-06-15 | 15 | 6 | 0.25 | 23.3 | 73.94 | 33.8754 |  |  | 73.94
1999-06-15 | 15 | 6 | 0.29167 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1999-06-15 | 15 | 6 | 0.33333 | 25 | 77 | 33.5046 |  |  | 77
1999-06-15 | 15 | 6 | 0.375 | 26.1 | 78.98 | 33.3652 |  |  | 78.98
1999-06-15 | 15 | 6 | 0.41667 | 27.2 | 80.96 | 33.3171 |  |  | 80.96
1999-06-15 | 15 | 6 | 0.45833 | 28.3 | 82.94 | 33.3941 |  |  | 82.94
1999-06-15 | 15 | 6 | 0.5 | 30 | 86 | 34.6732 |  |  | 86
1999-06-15 | 15 | 6 | 0.54167 | 31.7 | 89.06 | 35.8979 |  |  | 89.06
1999-06-15 | 15 | 6 | 0.58333 | 31.7 | 89.06 | 36.5577 |  |  | 89.06
1999-06-15 | 15 | 6 | 0.625 | 31.1 | 87.98 | 38.0093 |  |  | 87.98
1999-06-15 | 15 | 6 | 0.66667 | 31.1 | 87.98 | 37.3688 |  |  | 87.98
1999-06-15 | 15 | 6 | 0.70833 | 31.1 | 87.98 | 37.3688 |  |  | 87.98
1999-06-15 | 15 | 6 | 0.75 | 30.6 | 87.08 | 37.6121 |  |  | 87.08
1999-06-15 | 15 | 6 | 0.79167 | 28.9 | 84.02 | 37.5205 |  |  | 84.02
1999-06-15 | 15 | 6 | 0.83333 | 28.9 | 84.02 | 38.0859 |  |  | 84.02
1999-06-15 | 15 | 6 | 0.875 | 29.4 | 84.92 | 38.8481 |  |  | 84.92
1999-06-15 | 15 | 6 | 0.91667 | 28.3 | 82.94 | 37.7364 |  |  |  | 82.94
1999-06-15 | 15 | 6 | 0.95833 | 28.3 | 82.94 | 37.1906 |  |  |  | 82.94
1999-06-15 | 15 | 6 | 1 | 27.2 | 80.96 | 36.622 |  |  |  | 80.96
1999-06-16 | 16 | 6 | 0.041667 | 26.1 | 78.98 | 36.2248 |  |  |  | 78.98
1999-06-16 | 16 | 6 | 0.083333 | 25.6 | 78.08 | 35.9504 |  |  |  | 78.08
1999-06-16 | 16 | 6 | 0.125 | 24.4 | 75.92 | 35.4956 |  |  |  | 75.92
1999-06-16 | 16 | 6 | 0.16667 | 23.9 | 75.02 | 35.1691 |  |  |  | 75.02
1999-06-16 | 16 | 6 | 0.20833 | 23.9 | 75.02 | 32.0408 |  |  |  | 75.02
1999-06-16 | 16 | 6 | 0.25 | 23.3 | 73.94 | 30.2695 |  |  | 73.94
1999-06-16 | 16 | 6 | 0.29167 | 23.9 | 75.02 | 31.0043 |  |  | 75.02
1999-06-16 | 16 | 6 | 0.33333 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1999-06-16 | 16 | 6 | 0.375 | 25.6 | 78.08 | 30.4221 |  |  | 78.08
1999-06-16 | 16 | 6 | 0.41667 | 26.7 | 80.06 | 30.9733 |  |  | 80.06
1999-06-16 | 16 | 6 | 0.45833 | 27.2 | 80.96 | 32.0543 |  |  | 80.96
1999-06-16 | 16 | 6 | 0.5 | 27.8 | 82.04 | 31.734 |  |  | 82.04
1999-06-16 | 16 | 6 | 0.54167 | 29.4 | 84.92 | 31.6284 |  |  | 84.92
1999-06-16 | 16 | 6 | 0.58333 | 29.4 | 84.92 | 32.2005 |  |  | 84.92
1999-06-16 | 16 | 6 | 0.625 | 29.4 | 84.92 | 31.3427 |  |  | 84.92
1999-06-16 | 16 | 6 | 0.66667 | 29.4 | 84.92 | 30.487 |  |  | 84.92
1999-06-16 | 16 | 6 | 0.70833 | 27.2 | 80.96 | 29.5423 |  |  | 80.96
1999-06-16 | 16 | 6 | 0.75 | 26.7 | 80.06 | 29.7549 |  |  | 80.06
1999-06-16 | 16 | 6 | 0.79167 | 25 | 77 | 29.7417 |  |  | 77
1999-06-16 | 16 | 6 | 0.83333 | 25 | 77 | 31.9502 |  |  | 77
1999-06-16 | 16 | 6 | 0.875 | 25 | 77 | 34.6191 |  |  | 77
1999-06-16 | 16 | 6 | 0.91667 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
1999-06-16 | 16 | 6 | 0.95833 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
1999-06-16 | 16 | 6 | 1 | 23.9 | 75.02 | 34.1232 |  |  |  | 75.02
1999-06-17 | 17 | 6 | 0.041667 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
1999-06-17 | 17 | 6 | 0.083333 | 24.4 | 75.92 | 34.8482 |  |  |  | 75.92
1999-06-17 | 17 | 6 | 0.125 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
1999-06-17 | 17 | 6 | 0.16667 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1999-06-17 | 17 | 6 | 0.20833 | 22.2 | 71.96 | 33.2636 |  |  |  | 71.96
1999-06-17 | 17 | 6 | 0.25 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
1999-06-17 | 17 | 6 | 0.29167 | 25 | 77 | 35.2895 |  |  | 77
1999-06-17 | 17 | 6 | 0.33333 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
1999-06-17 | 17 | 6 | 0.375 | 27.8 | 82.04 | 36.9892 |  |  | 82.04
1999-06-17 | 17 | 6 | 0.41667 | 28.3 | 82.94 | 37.1906 |  |  | 82.94
1999-06-17 | 17 | 6 | 0.45833 | 29.4 | 84.92 | 38.265 |  |  | 84.92
1999-06-17 | 17 | 6 | 0.5 | 30.6 | 87.08 | 38.2353 |  |  | 87.08
1999-06-17 | 17 | 6 | 0.54167 | 30.6 | 87.08 | 38.2353 |  |  | 87.08
1999-06-17 | 17 | 6 | 0.58333 | 30 | 86 | 39.7824 |  |  | 86
1999-06-17 | 17 | 6 | 0.625 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
1999-06-17 | 17 | 6 | 0.66667 | 22.8 | 73.04 | 33.5522 |  |  | 73.04
1999-06-17 | 17 | 6 | 0.70833 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
1999-06-17 | 17 | 6 | 0.75 | 25 | 77 | 36.8589 |  |  | 77
1999-06-17 | 17 | 6 | 0.79167 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
1999-06-17 | 17 | 6 | 0.83333 | 23.9 | 75.02 | 35.1691 |  |  | 75.02
1999-06-17 | 17 | 6 | 0.875 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
1999-06-17 | 17 | 6 | 0.91667 | 23.9 | 75.02 | 36.008 |  |  |  | 75.02
1999-06-17 | 17 | 6 | 0.95833 | 23.3 | 73.94 | 35.0857 |  |  |  | 73.94
1999-06-17 | 17 | 6 | 1 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1999-06-18 | 18 | 6 | 0.041667 | 23.9 | 75.02 | 34.1232 |  |  |  | 75.02
1999-06-18 | 18 | 6 | 0.083333 | 23.9 | 75.02 | 34.1232 |  |  |  | 75.02
1999-06-18 | 18 | 6 | 0.125 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
1999-06-18 | 18 | 6 | 0.16667 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
1999-06-18 | 18 | 6 | 0.20833 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
1999-06-18 | 18 | 6 | 0.25 | 22.8 | 73.04 | 32.967 |  |  | 73.04
1999-06-18 | 18 | 6 | 0.29167 | 23.3 | 73.94 | 32.87 |  |  | 73.94
1999-06-18 | 18 | 6 | 0.33333 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
1999-06-18 | 18 | 6 | 0.375 | 25.6 | 78.08 | 36.1827 |  |  | 78.08
1999-06-18 | 18 | 6 | 0.41667 | 26.7 | 80.06 | 36.6337 |  |  | 80.06
1999-06-18 | 18 | 6 | 0.45833 | 28.9 | 84.02 | 37.5205 |  |  | 84.02
1999-06-18 | 18 | 6 | 0.5 | 28.9 | 84.02 | 37.5205 |  |  | 84.02
1999-06-18 | 18 | 6 | 0.54167 | 30.6 | 87.08 | 38.8595 |  |  | 87.08
1999-06-18 | 18 | 6 | 0.58333 | 31.7 | 89.06 | 39.5423 |  |  | 89.06
1999-06-18 | 18 | 6 | 0.625 | 32.2 | 89.96 | 38.9303 |  |  | 89.96
1999-06-18 | 18 | 6 | 0.66667 | 32.8 | 91.04 | 39.8092 |  |  | 91.04
1999-06-18 | 18 | 6 | 0.70833 | 29.4 | 84.92 | 39.7245 |  |  | 84.92
1999-06-18 | 18 | 6 | 0.75 | 27.8 | 82.04 | 40.9831 |  |  | 82.04
1999-06-18 | 18 | 6 | 0.79167 | 27.2 | 80.96 | 39.9585 |  |  | 80.96
1999-06-18 | 18 | 6 | 0.83333 | 27.8 | 82.04 | 40.1807 |  |  | 82.04
1999-06-18 | 18 | 6 | 0.875 | 23.3 | 73.94 | 36.9091 |  |  | 73.94
1999-06-18 | 18 | 6 | 0.91667 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1999-06-18 | 18 | 6 | 0.95833 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
1999-06-18 | 18 | 6 | 1 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1999-06-19 | 19 | 6 | 0.041667 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1999-06-19 | 19 | 6 | 0.083333 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1999-06-19 | 19 | 6 | 0.125 | 22.2 | 71.96 | 34.3944 |  |  |  | 71.96
1999-06-19 | 19 | 6 | 0.16667 | 22.2 | 71.96 | 34.3944 |  |  |  | 71.96
1999-06-19 | 19 | 6 | 0.20833 | 21.1 | 69.98 | 33.4697 |  |  |  | 69.98
1999-06-19 | 19 | 6 | 0.25 | 21.1 | 69.98 | 32.7659 |  |  | 69.98
1999-06-19 | 19 | 6 | 0.29167 | 23.3 | 73.94 | 34.48 |  |  | 73.94
1999-06-19 | 19 | 6 | 0.33333 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1999-06-19 | 19 | 6 | 0.375 | 26.7 | 80.06 | 33.669 |  |  | 80.06
1999-06-19 | 19 | 6 | 0.41667 | 25.6 | 78.08 | 32.2552 |  |  | 78.08
1999-06-19 | 19 | 6 | 0.45833 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
1999-06-19 | 19 | 6 | 0.5 | 25.6 | 78.08 | 31.796 |  |  | 78.08
1999-06-19 | 19 | 6 | 0.54167 | 26.7 | 80.06 | 30.9733 |  |  | 80.06
1999-06-19 | 19 | 6 | 0.58333 | 26.7 | 80.06 | 31.4619 |  |  | 80.06
1999-06-19 | 19 | 6 | 0.625 | 26.7 | 80.06 | 31.4619 |  |  | 80.06
1999-06-19 | 19 | 6 | 0.66667 | 26.1 | 78.98 | 30.9999 |  |  | 78.98
1999-06-19 | 19 | 6 | 0.70833 | 25.6 | 78.08 | 29.9654 |  |  | 78.08
1999-06-19 | 19 | 6 | 0.75 | 25 | 77 | 29.3016 |  |  | 77
1999-06-19 | 19 | 6 | 0.79167 | 24.4 | 75.92 | 29.0748 |  |  | 75.92
1999-06-19 | 19 | 6 | 0.83333 | 22.8 | 73.04 | 24.8759 |  |  | 73.04
1999-06-19 | 19 | 6 | 0.875 | 21.7 | 71.06 | 24.8041 |  |  | 71.06
1999-06-19 | 19 | 6 | 0.91667 | 20 | 68 | 23.4433 |  |  |  | 68
1999-06-19 | 19 | 6 | 0.95833 | 19.4 | 66.92 | 23.2259 |  |  |  | 66.92
1999-06-19 | 19 | 6 | 1 | 18.3 | 64.94 | 22.6954 |  |  |  | 64.94
1999-06-20 | 20 | 6 | 0.041667 | 17.2 | 62.96 | 22.5374 |  |  |  | 62.96
1999-06-20 | 20 | 6 | 0.083333 | 16.7 | 62.06 | 22.6039 |  |  |  | 62.06
1999-06-20 | 20 | 6 | 0.125 | 16.1 | 60.98 | 22.0492 |  |  |  | 60.98
1999-06-20 | 20 | 6 | 0.16667 | 15.6 | 60.08 | 21.8365 |  |  |  | 60.08
1999-06-20 | 20 | 6 | 0.20833 | 15 | 59 | 21.5232 |  |  |  | 59
1999-06-20 | 20 | 6 | 0.25 | 15.6 | 60.08 | 21.5947 |  |  | 60.08
1999-06-20 | 20 | 6 | 0.29167 | 16.1 | 60.98 | 21.7994 |  |  | 60.98
1999-06-20 | 20 | 6 | 0.33333 | 17.2 | 62.96 | 21.4665 |  |  | 62.96
1999-06-20 | 20 | 6 | 0.375 | 17.8 | 64.04 | 21.2822 |  |  | 64.04
1999-06-20 | 20 | 6 | 0.41667 | 18.3 | 64.94 | 21.6911 |  |  | 64.94
1999-06-20 | 20 | 6 | 0.45833 | 20 | 68 | 22.6444 |  |  | 68
1999-06-20 | 20 | 6 | 0.5 | 20.6 | 69.08 | 23.1477 |  |  | 69.08
1999-06-20 | 20 | 6 | 0.54167 | 21.1 | 69.98 | 23.4024 |  |  | 69.98
1999-06-20 | 20 | 6 | 0.58333 | 22.2 | 71.96 | 23.6152 |  |  | 71.96
1999-06-20 | 20 | 6 | 0.625 | 22.8 | 73.04 | 24.1152 |  |  | 73.04
1999-06-20 | 20 | 6 | 0.66667 | 22.8 | 73.04 | 24.1152 |  |  | 73.04
1999-06-20 | 20 | 6 | 0.70833 | 23.3 | 73.94 | 24.1462 |  |  | 73.94
1999-06-20 | 20 | 6 | 0.75 | 22.2 | 71.96 | 24.5313 |  |  | 71.96
1999-06-20 | 20 | 6 | 0.79167 | 22.2 | 71.96 | 24.7148 |  |  | 71.96
1999-06-20 | 20 | 6 | 0.83333 | 21.1 | 69.98 | 24.2588 |  |  | 69.98
1999-06-20 | 20 | 6 | 0.875 | 21.1 | 69.98 | 23.916 |  |  | 69.98
1999-06-20 | 20 | 6 | 0.91667 | 21.1 | 69.98 | 23.916 |  |  |  | 69.98
1999-06-20 | 20 | 6 | 0.95833 | 20.6 | 69.08 | 23.8116 |  |  |  | 69.08
1999-06-20 | 20 | 6 | 1 | 20 | 68 | 23.7633 |  |  |  | 68
1999-06-21 | 21 | 6 | 0.041667 | 20 | 68 | 23.7633 |  |  |  | 68
1999-06-21 | 21 | 6 | 0.083333 | 19.4 | 66.92 | 23.8427 |  |  |  | 66.92
1999-06-21 | 21 | 6 | 0.125 | 18.9 | 66.02 | 23.5319 |  |  |  | 66.02
1999-06-21 | 21 | 6 | 0.16667 | 18.3 | 64.94 | 23.2706 |  |  |  | 64.94
1999-06-21 | 21 | 6 | 0.20833 | 17.8 | 64.04 | 23.6484 |  |  |  | 64.04
1999-06-21 | 21 | 6 | 0.25 | 19.4 | 66.92 | 24.306 |  |  | 66.92
1999-06-21 | 21 | 6 | 0.29167 | 20.6 | 69.08 | 24.3103 |  |  | 69.08
1999-06-21 | 21 | 6 | 0.33333 | 21.7 | 71.06 | 24.9823 |  |  | 71.06
1999-06-21 | 21 | 6 | 0.375 | 22.2 | 71.96 | 26.0021 |  |  | 71.96
1999-06-21 | 21 | 6 | 0.41667 | 23.9 | 75.02 | 25.6638 |  |  | 75.02
1999-06-21 | 21 | 6 | 0.45833 | 24.4 | 75.92 | 25.6984 |  |  | 75.92
1999-06-21 | 21 | 6 | 0.5 | 26.1 | 78.98 | 26.7827 |  |  | 78.98
1999-06-21 | 21 | 6 | 0.54167 | 26.7 | 80.06 | 27.5724 |  |  | 80.06
1999-06-21 | 21 | 6 | 0.58333 | 26.7 | 80.06 | 27.8142 |  |  | 80.06
1999-06-21 | 21 | 6 | 0.625 | 26.1 | 78.98 | 29.1192 |  |  | 78.98
1999-06-21 | 21 | 6 | 0.66667 | 26.1 | 78.98 | 29.1192 |  |  | 78.98
1999-06-21 | 21 | 6 | 0.70833 | 25 | 77 | 29.7417 |  |  | 77
1999-06-21 | 21 | 6 | 0.75 | 25 | 77 | 30.6234 |  |  | 77
1999-06-21 | 21 | 6 | 0.79167 | 23.3 | 73.94 | 30.6683 |  |  | 73.94
1999-06-21 | 21 | 6 | 0.83333 | 22.8 | 73.04 | 30.4423 |  |  | 73.04
1999-06-21 | 21 | 6 | 0.875 | 22.2 | 71.96 | 29.3347 |  |  | 71.96
1999-06-21 | 21 | 6 | 0.91667 | 21.7 | 71.06 | 28.7456 |  |  |  | 71.06
1999-06-21 | 21 | 6 | 0.95833 | 21.1 | 69.98 | 27.1866 |  |  |  | 69.98
1999-06-21 | 21 | 6 | 1 | 21.1 | 69.98 | 27.5326 |  |  |  | 69.98
1999-06-22 | 22 | 6 | 0.041667 | 21.1 | 69.98 | 28.0524 |  |  |  | 69.98
1999-06-22 | 22 | 6 | 0.083333 | 21.1 | 69.98 | 28.0524 |  |  |  | 69.98
1999-06-22 | 22 | 6 | 0.125 | 21.1 | 69.98 | 28.0524 |  |  |  | 69.98
1999-06-22 | 22 | 6 | 0.16667 | 20.6 | 69.08 | 27.8218 |  |  |  | 69.08
1999-06-22 | 22 | 6 | 0.20833 | 20.6 | 69.08 | 28.1581 |  |  |  | 69.08
1999-06-22 | 22 | 6 | 0.25 | 21.7 | 71.06 | 29.1062 |  |  | 71.06
1999-06-22 | 22 | 6 | 0.29167 | 22.2 | 71.96 | 29.7069 |  |  | 71.96
1999-06-22 | 22 | 6 | 0.33333 | 23.3 | 73.94 | 30.6683 |  |  | 73.94
1999-06-22 | 22 | 6 | 0.375 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1999-06-22 | 22 | 6 | 0.41667 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
1999-06-22 | 22 | 6 | 0.45833 | 21.1 | 69.98 | 33.4697 |  |  | 69.98
1999-06-22 | 22 | 6 | 0.5 | 21.7 | 71.06 | 33.6452 |  |  | 71.06
1999-06-22 | 22 | 6 | 0.54167 | 23.3 | 73.94 | 34.48 |  |  | 73.94
1999-06-22 | 22 | 6 | 0.58333 | 22.8 | 73.04 | 34.7256 |  |  | 73.04
1999-06-22 | 22 | 6 | 0.625 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
1999-06-22 | 22 | 6 | 0.66667 | 23.9 | 75.02 | 35.1691 |  |  | 75.02
1999-06-22 | 22 | 6 | 0.70833 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1999-06-22 | 22 | 6 | 0.75 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1999-06-22 | 22 | 6 | 0.79167 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1999-06-22 | 22 | 6 | 0.83333 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1999-06-22 | 22 | 6 | 0.875 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1999-06-22 | 22 | 6 | 0.91667 | 25 | 77 | 35.7372 |  |  |  | 77
1999-06-22 | 22 | 6 | 0.95833 | 24.4 | 75.92 | 34.8482 |  |  |  | 75.92
1999-06-22 | 22 | 6 | 1 | 24.4 | 75.92 | 34.8482 |  |  |  | 75.92
1999-06-23 | 23 | 6 | 0.041667 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1999-06-23 | 23 | 6 | 0.083333 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
1999-06-23 | 23 | 6 | 0.125 | 22.8 | 73.04 | 30.4423 |  |  |  | 73.04
1999-06-23 | 23 | 6 | 0.16667 | 22.2 | 71.96 | 29.7069 |  |  |  | 71.96
1999-06-23 | 23 | 6 | 0.20833 | 21.7 | 71.06 | 29.4671 |  |  |  | 71.06
1999-06-23 | 23 | 6 | 0.25 | 21.7 | 71.06 | 29.1062 |  |  | 71.06
1999-06-23 | 23 | 6 | 0.29167 | 21.7 | 71.06 | 29.4671 |  |  | 71.06
1999-06-23 | 23 | 6 | 0.33333 | 21.7 | 71.06 | 29.4671 |  |  | 71.06
1999-06-23 | 23 | 6 | 0.375 | 22.2 | 71.96 | 29.3347 |  |  | 71.96
1999-06-23 | 23 | 6 | 0.41667 | 23.3 | 73.94 | 29.8712 |  |  | 73.94
1999-06-23 | 23 | 6 | 0.45833 | 24.4 | 75.92 | 28.6509 |  |  | 75.92
1999-06-23 | 23 | 6 | 0.5 | 25.6 | 78.08 | 29.2814 |  |  | 78.08
1999-06-23 | 23 | 6 | 0.54167 | 26.7 | 80.06 | 29.7549 |  |  | 80.06
1999-06-23 | 23 | 6 | 0.58333 | 27.8 | 82.04 | 30.4325 |  |  | 82.04
1999-06-23 | 23 | 6 | 0.625 | 28.3 | 82.94 | 29.6386 |  |  | 82.94
1999-06-23 | 23 | 6 | 0.66667 | 28.3 | 82.94 | 30.44 |  |  | 82.94
1999-06-23 | 23 | 6 | 0.70833 | 28.3 | 82.94 | 30.44 |  |  | 82.94
1999-06-23 | 23 | 6 | 0.75 | 26.7 | 80.06 | 30.4854 |  |  | 80.06
1999-06-23 | 23 | 6 | 0.79167 | 25 | 77 | 31.5074 |  |  | 77
1999-06-23 | 23 | 6 | 0.83333 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1999-06-23 | 23 | 6 | 0.875 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1999-06-23 | 23 | 6 | 0.91667 | 22.8 | 73.04 | 31.9938 |  |  |  | 73.04
1999-06-23 | 23 | 6 | 0.95833 | 23.3 | 73.94 | 31.2674 |  |  |  | 73.94
1999-06-23 | 23 | 6 | 1 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1999-06-24 | 24 | 6 | 0.041667 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1999-06-24 | 24 | 6 | 0.083333 | 20 | 68 | 30.7176 |  |  |  | 68
1999-06-24 | 24 | 6 | 0.125 | 19.4 | 66.92 | 29.9151 |  |  |  | 66.92
1999-06-24 | 24 | 6 | 0.16667 | 19.4 | 66.92 | 29.9151 |  |  |  | 66.92
1999-06-24 | 24 | 6 | 0.20833 | 18.3 | 64.94 | 28.9302 |  |  |  | 64.94
1999-06-24 | 24 | 6 | 0.25 | 18.9 | 66.02 | 29.7169 |  |  | 66.02
1999-06-24 | 24 | 6 | 0.29167 | 20 | 68 | 29.7388 |  |  | 68
1999-06-24 | 24 | 6 | 0.33333 | 20.6 | 69.08 | 29.5066 |  |  | 69.08
1999-06-24 | 24 | 6 | 0.375 | 22.8 | 73.04 | 31.4112 |  |  | 73.04
1999-06-24 | 24 | 6 | 0.41667 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
1999-06-24 | 24 | 6 | 0.45833 | 27.2 | 80.96 | 32.8114 |  |  | 80.96
1999-06-24 | 24 | 6 | 0.5 | 27.2 | 80.96 | 33.3171 |  |  | 80.96
1999-06-24 | 24 | 6 | 0.54167 | 27.2 | 80.96 | 34.5845 |  |  | 80.96
1999-06-24 | 24 | 6 | 0.58333 | 26.7 | 80.06 | 31.4619 |  |  | 80.06
1999-06-24 | 24 | 6 | 0.625 | 27.2 | 80.96 | 30.294 |  |  | 80.96
1999-06-24 | 24 | 6 | 0.66667 | 26.1 | 78.98 | 29.1192 |  |  | 78.98
1999-06-24 | 24 | 6 | 0.70833 | 25.6 | 78.08 | 28.3715 |  |  | 78.08
1999-06-24 | 24 | 6 | 0.75 | 25 | 77 | 29.3016 |  |  | 77
1999-06-24 | 24 | 6 | 0.79167 | 23.9 | 75.02 | 28.9405 |  |  | 75.02
1999-06-24 | 24 | 6 | 0.83333 | 22.8 | 73.04 | 29.6692 |  |  | 73.04
1999-06-24 | 24 | 6 | 0.875 | 22.8 | 73.04 | 30.4423 |  |  | 73.04
1999-06-24 | 24 | 6 | 0.91667 | 21.7 | 71.06 | 31.459 |  |  |  | 71.06
1999-06-24 | 24 | 6 | 0.95833 | 21.1 | 69.98 | 31.1876 |  |  |  | 69.98
1999-06-24 | 24 | 6 | 1 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1999-06-25 | 25 | 6 | 0.041667 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1999-06-25 | 25 | 6 | 0.083333 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1999-06-25 | 25 | 6 | 0.125 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1999-06-25 | 25 | 6 | 0.16667 | 20 | 68 | 31.2081 |  |  |  | 68
1999-06-25 | 25 | 6 | 0.20833 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1999-06-25 | 25 | 6 | 0.25 | 21.1 | 69.98 | 31.7129 |  |  | 69.98
1999-06-25 | 25 | 6 | 0.29167 | 22.2 | 71.96 | 31.2 |  |  | 71.96
1999-06-25 | 25 | 6 | 0.33333 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1999-06-25 | 25 | 6 | 0.375 | 23.9 | 75.02 | 32.4563 |  |  | 75.02
1999-06-25 | 25 | 6 | 0.41667 | 25 | 77 | 33.5046 |  |  | 77
1999-06-25 | 25 | 6 | 0.45833 | 25 | 77 | 33.9499 |  |  | 77
1999-06-25 | 25 | 6 | 0.5 | 26.1 | 78.98 | 34.5538 |  |  | 78.98
1999-06-25 | 25 | 6 | 0.54167 | 27.2 | 80.96 | 35.6018 |  |  | 80.96
1999-06-25 | 25 | 6 | 0.58333 | 27.8 | 82.04 | 34.6146 |  |  | 82.04
1999-06-25 | 25 | 6 | 0.625 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1999-06-25 | 25 | 6 | 0.66667 | 25.6 | 78.08 | 31.796 |  |  | 78.08
1999-06-25 | 25 | 6 | 0.70833 | 24.4 | 75.92 | 32.6987 |  |  | 75.92
1999-06-25 | 25 | 6 | 0.75 | 21.1 | 69.98 | 32.239 |  |  | 69.98
1999-06-25 | 25 | 6 | 0.79167 | 21.7 | 71.06 | 32.5504 |  |  | 71.06
1999-06-25 | 25 | 6 | 0.83333 | 20.6 | 69.08 | 31.5393 |  |  | 69.08
1999-06-25 | 25 | 6 | 0.875 | 20 | 68 | 30.7176 |  |  | 68
1999-06-25 | 25 | 6 | 0.91667 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
1999-06-25 | 25 | 6 | 0.95833 | 21.1 | 69.98 | 30.6631 |  |  |  | 69.98
1999-06-25 | 25 | 6 | 1 | 21.1 | 69.98 | 31.1876 |  |  |  | 69.98
1999-06-26 | 26 | 6 | 0.041667 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1999-06-26 | 26 | 6 | 0.083333 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
1999-06-26 | 26 | 6 | 0.125 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
1999-06-26 | 26 | 6 | 0.16667 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
1999-06-26 | 26 | 6 | 0.20833 | 21.1 | 69.98 | 32.7659 |  |  |  | 69.98
1999-06-26 | 26 | 6 | 0.25 | 21.1 | 69.98 | 32.239 |  |  | 69.98
1999-06-26 | 26 | 6 | 0.29167 | 21.7 | 71.06 | 32.5504 |  |  | 71.06
1999-06-26 | 26 | 6 | 0.33333 | 22.2 | 71.96 | 33.2636 |  |  | 71.96
1999-06-26 | 26 | 6 | 0.375 | 22.8 | 73.04 | 33.5522 |  |  | 73.04
1999-06-26 | 26 | 6 | 0.41667 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1999-06-26 | 26 | 6 | 0.45833 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1999-06-26 | 26 | 6 | 0.5 | 25.6 | 78.08 | 33.867 |  |  | 78.08
1999-06-26 | 26 | 6 | 0.54167 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
1999-06-26 | 26 | 6 | 0.58333 | 25 | 77 | 31.5074 |  |  | 77
1999-06-26 | 26 | 6 | 0.625 | 25.6 | 78.08 | 30.8795 |  |  | 78.08
1999-06-26 | 26 | 6 | 0.66667 | 25.6 | 78.08 | 29.2814 |  |  | 78.08
1999-06-26 | 26 | 6 | 0.70833 | 24.4 | 75.92 | 27.1715 |  |  | 75.92
1999-06-26 | 26 | 6 | 0.75 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1999-06-26 | 26 | 6 | 0.79167 | 23.3 | 73.94 | 25.5194 |  |  | 73.94
1999-06-26 | 26 | 6 | 0.83333 | 22.8 | 73.04 | 25.4476 |  |  | 73.04
1999-06-26 | 26 | 6 | 0.875 | 22.2 | 71.96 | 26.0021 |  |  | 71.96
1999-06-26 | 26 | 6 | 0.91667 | 21.7 | 71.06 | 25.3389 |  |  |  | 71.06
1999-06-26 | 26 | 6 | 0.95833 | 20.6 | 69.08 | 24.9764 |  |  |  | 69.08
1999-06-26 | 26 | 6 | 1 | 20 | 68 | 24.7253 |  |  |  | 68
1999-06-27 | 27 | 6 | 0.041667 | 19.4 | 66.92 | 25.0796 |  |  |  | 66.92
1999-06-27 | 27 | 6 | 0.083333 | 18.9 | 66.02 | 24.8801 |  |  |  | 66.02
1999-06-27 | 27 | 6 | 0.125 | 18.3 | 64.94 | 24.5684 |  |  |  | 64.94
1999-06-27 | 27 | 6 | 0.16667 | 17.8 | 64.04 | 24.3474 |  |  |  | 64.04
1999-06-27 | 27 | 6 | 0.20833 | 17.8 | 64.04 | 24.3474 |  |  |  | 64.04
1999-06-27 | 27 | 6 | 0.25 | 17.8 | 64.04 | 24.0676 |  |  | 64.04
1999-06-27 | 27 | 6 | 0.29167 | 18.3 | 64.94 | 23.8468 |  |  | 64.94
1999-06-27 | 27 | 6 | 0.33333 | 19.4 | 66.92 | 23.9971 |  |  | 66.92
1999-06-27 | 27 | 6 | 0.375 | 20.6 | 69.08 | 23.9777 |  |  | 69.08
1999-06-27 | 27 | 6 | 0.41667 | 22.2 | 71.96 | 24.7148 |  |  | 71.96
1999-06-27 | 27 | 6 | 0.45833 | 23.3 | 73.94 | 25.1265 |  |  | 73.94
1999-06-27 | 27 | 6 | 0.5 | 24.4 | 75.92 | 25.6984 |  |  | 75.92
1999-06-27 | 27 | 6 | 0.54167 | 25 | 77 | 26.4551 |  |  | 77
1999-06-27 | 27 | 6 | 0.58333 | 25.6 | 78.08 | 26.5589 |  |  | 78.08
1999-06-27 | 27 | 6 | 0.625 | 26.1 | 78.98 | 26.7827 |  |  | 78.98
1999-06-27 | 27 | 6 | 0.66667 | 26.1 | 78.98 | 27.0156 |  |  | 78.98
1999-06-27 | 27 | 6 | 0.70833 | 26.1 | 78.98 | 27.7154 |  |  | 78.98
1999-06-27 | 27 | 6 | 0.75 | 26.1 | 78.98 | 27.0156 |  |  | 78.98
1999-06-27 | 27 | 6 | 0.79167 | 25.6 | 78.08 | 26.5589 |  |  | 78.08
1999-06-27 | 27 | 6 | 0.83333 | 25 | 77 | 26.4551 |  |  | 77
1999-06-27 | 27 | 6 | 0.875 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1999-06-27 | 27 | 6 | 0.91667 | 23.9 | 75.02 | 26.2758 |  |  |  | 75.02
1999-06-27 | 27 | 6 | 0.95833 | 23.3 | 73.94 | 26.1096 |  |  |  | 73.94
1999-06-27 | 27 | 6 | 1 | 23.3 | 73.94 | 26.1096 |  |  |  | 73.94
1999-06-28 | 28 | 6 | 0.041667 | 22.2 | 71.96 | 26.0021 |  |  |  | 71.96
1999-06-28 | 28 | 6 | 0.083333 | 21.1 | 69.98 | 25.8057 |  |  |  | 69.98
1999-06-28 | 28 | 6 | 0.125 | 21.1 | 69.98 | 25.8057 |  |  |  | 69.98
1999-06-28 | 28 | 6 | 0.16667 | 21.1 | 69.98 | 25.8057 |  |  |  | 69.98
1999-06-28 | 28 | 6 | 0.20833 | 20 | 68 | 26.3346 |  |  |  | 68
1999-06-28 | 28 | 6 | 0.25 | 20.6 | 69.08 | 25.978 |  |  | 69.08
1999-06-28 | 28 | 6 | 0.29167 | 21.1 | 69.98 | 26.4954 |  |  | 69.98
1999-06-28 | 28 | 6 | 0.33333 | 22.2 | 71.96 | 26.1864 |  |  | 71.96
1999-06-28 | 28 | 6 | 0.375 | 23.9 | 75.02 | 26.6844 |  |  | 75.02
1999-06-28 | 28 | 6 | 0.41667 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1999-06-28 | 28 | 6 | 0.45833 | 24.4 | 75.92 | 26.9607 |  |  | 75.92
1999-06-28 | 28 | 6 | 0.5 | 26.1 | 78.98 | 27.2488 |  |  | 78.98
1999-06-28 | 28 | 6 | 0.54167 | 25 | 77 | 27.7659 |  |  | 77
1999-06-28 | 28 | 6 | 0.58333 | 25 | 77 | 27.7659 |  |  | 77
1999-06-28 | 28 | 6 | 0.625 | 24.4 | 75.92 | 27.5936 |  |  | 75.92
1999-06-28 | 28 | 6 | 0.66667 | 24.4 | 75.92 | 27.1715 |  |  | 75.92
1999-06-28 | 28 | 6 | 0.70833 | 24.4 | 75.92 | 27.1715 |  |  | 75.92
1999-06-28 | 28 | 6 | 0.75 | 23.9 | 75.02 | 27.7081 |  |  | 75.02
1999-06-28 | 28 | 6 | 0.79167 | 23.3 | 73.94 | 27.8863 |  |  | 73.94
1999-06-28 | 28 | 6 | 0.83333 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1999-06-28 | 28 | 6 | 0.875 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1999-06-28 | 28 | 6 | 0.91667 | 21.7 | 71.06 | 32.5504 |  |  |  | 71.06
1999-06-28 | 28 | 6 | 0.95833 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
1999-06-28 | 28 | 6 | 1 | 21.1 | 69.98 | 30.6631 |  |  |  | 69.98
1999-06-29 | 29 | 6 | 0.041667 | 22.2 | 71.96 | 29.7069 |  |  |  | 71.96
1999-06-29 | 29 | 6 | 0.083333 | 17.8 | 64.04 | 27.8641 |  |  |  | 64.04
1999-06-29 | 29 | 6 | 0.125 | 18.3 | 64.94 | 28.0534 |  |  |  | 64.94
1999-06-29 | 29 | 6 | 0.16667 | 18.3 | 64.94 | 28.0534 |  |  |  | 64.94
1999-06-29 | 29 | 6 | 0.20833 | 17.8 | 64.04 | 27.0168 |  |  |  | 64.04
1999-06-29 | 29 | 6 | 0.25 | 18.3 | 64.94 | 26.7424 |  |  | 64.94
1999-06-29 | 29 | 6 | 0.29167 | 18.3 | 64.94 | 26.7424 |  |  | 64.94
1999-06-29 | 29 | 6 | 0.33333 | 19.4 | 66.92 | 26.7877 |  |  | 66.92
1999-06-29 | 29 | 6 | 0.375 | 20 | 68 | 26.6574 |  |  | 68
1999-06-29 | 29 | 6 | 0.41667 | 21.7 | 71.06 | 27.8458 |  |  | 71.06
1999-06-29 | 29 | 6 | 0.45833 | 22.2 | 71.96 | 28.0348 |  |  | 71.96
1999-06-29 | 29 | 6 | 0.5 | 23.3 | 73.94 | 28.0843 |  |  | 73.94
1999-06-29 | 29 | 6 | 0.54167 | 25 | 77 | 28.204 |  |  | 77
1999-06-29 | 29 | 6 | 0.58333 | 25 | 77 | 28.204 |  |  | 77
1999-06-29 | 29 | 6 | 0.625 | 26.1 | 78.98 | 27.2488 |  |  | 78.98
1999-06-29 | 29 | 6 | 0.66667 | 26.1 | 78.98 | 27.949 |  |  | 78.98
1999-06-29 | 29 | 6 | 0.70833 | 26.7 | 80.06 | 27.8142 |  |  | 80.06
1999-06-29 | 29 | 6 | 0.75 | 25 | 77 | 28.204 |  |  | 77
1999-06-29 | 29 | 6 | 0.79167 | 25.6 | 78.08 | 27.6907 |  |  | 78.08
1999-06-29 | 29 | 6 | 0.83333 | 25 | 77 | 27.5471 |  |  | 77
1999-06-29 | 29 | 6 | 0.875 | 24.4 | 75.92 | 27.1715 |  |  | 75.92
1999-06-29 | 29 | 6 | 0.91667 | 24.4 | 75.92 | 27.5936 |  |  |  | 75.92
1999-06-29 | 29 | 6 | 0.95833 | 23.9 | 75.02 | 27.2983 |  |  |  | 75.02
1999-06-29 | 29 | 6 | 1 | 22.8 | 73.04 | 27.1684 |  |  |  | 73.04
1999-06-30 | 30 | 6 | 0.041667 | 22.2 | 71.96 | 26.9246 |  |  |  | 71.96
1999-06-30 | 30 | 6 | 0.083333 | 22.2 | 71.96 | 26.9246 |  |  |  | 71.96
1999-06-30 | 30 | 6 | 0.125 | 22.2 | 71.96 | 26.5553 |  |  |  | 71.96
1999-06-30 | 30 | 6 | 0.16667 | 21.7 | 71.06 | 26.7692 |  |  |  | 71.06
1999-06-30 | 30 | 6 | 0.20833 | 20.6 | 69.08 | 26.6473 |  |  |  | 69.08
1999-06-30 | 30 | 6 | 0.25 | 20.6 | 69.08 | 26.6473 |  |  | 69.08
1999-06-30 | 30 | 6 | 0.29167 | 21.7 | 71.06 | 27.8458 |  |  | 71.06
1999-06-30 | 30 | 6 | 0.33333 | 23.3 | 73.94 | 28.0843 |  |  | 73.94
1999-06-30 | 30 | 6 | 0.375 | 24.4 | 75.92 | 29.0748 |  |  | 75.92
1999-06-30 | 30 | 6 | 0.41667 | 25.6 | 78.08 | 29.5092 |  |  | 78.08
1999-06-30 | 30 | 6 | 0.45833 | 26.7 | 80.06 | 29.7549 |  |  | 80.06
1999-06-30 | 30 | 6 | 0.5 | 28.3 | 82.94 | 30.7075 |  |  | 82.94
1999-06-30 | 30 | 6 | 0.54167 | 28.3 | 82.94 | 30.7075 |  |  | 82.94
1999-06-30 | 30 | 6 | 0.58333 | 28.9 | 84.02 | 31.083 |  |  | 84.02
1999-06-30 | 30 | 6 | 0.625 | 28.3 | 82.94 | 32.586 |  |  | 82.94
1999-06-30 | 30 | 6 | 0.66667 | 27.8 | 82.04 | 32.256 |  |  | 82.04
1999-06-30 | 30 | 6 | 0.70833 | 29.4 | 84.92 | 30.487 |  |  | 84.92
1999-06-30 | 30 | 6 | 0.75 | 28.3 | 82.94 | 30.7075 |  |  | 82.94
1999-06-30 | 30 | 6 | 0.79167 | 26.1 | 78.98 | 30.5288 |  |  | 78.98
1999-06-30 | 30 | 6 | 0.83333 | 25.6 | 78.08 | 30.8795 |  |  | 78.08
1999-06-30 | 30 | 6 | 0.875 | 26.1 | 78.98 | 30.9999 |  |  | 78.98
1999-06-30 | 30 | 6 | 0.91667 | 25.3 | 77.54 | 29.4079 |  |  |  | 77.54
1999-06-30 | 30 | 6 | 0.95833 | 24.5 | 76.1 | 28.3325 |  |  |  | 76.1
1999-06-30 | 30 | 6 | 1 | 23.7 | 74.66 | 28.9229 |  |  |  | 74.66
2003-07-01 | 1 | 7 | 0.041667 | 23 | 73.4 | 34.4347 |  |  |  | 73.4
2003-07-01 | 1 | 7 | 0.083333 | 22.2 | 71.96 | 33.8285 |  |  |  | 71.96
2003-07-01 | 1 | 7 | 0.125 | 21.4 | 70.52 | 32.6656 |  |  |  | 70.52
2003-07-01 | 1 | 7 | 0.16667 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
2003-07-01 | 1 | 7 | 0.20833 | 20 | 68 | 31.2081 |  |  |  | 68
2003-07-01 | 1 | 7 | 0.25 | 22.2 | 71.96 | 32.3241 |  |  | 71.96
2003-07-01 | 1 | 7 | 0.29167 | 22.8 | 73.04 | 31.9938 |  |  | 73.04
2003-07-01 | 1 | 7 | 0.33333 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
2003-07-01 | 1 | 7 | 0.375 | 25 | 77 | 32.3936 |  |  | 77
2003-07-01 | 1 | 7 | 0.41667 | 26.7 | 80.06 | 32.6863 |  |  | 80.06
2003-07-01 | 1 | 7 | 0.45833 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
2003-07-01 | 1 | 7 | 0.5 | 28.9 | 84.02 | 33.3087 |  |  | 84.02
2003-07-01 | 1 | 7 | 0.54167 | 31.1 | 87.98 | 33.5498 |  |  | 87.98
2003-07-01 | 1 | 7 | 0.58333 | 29.4 | 84.92 | 34.4984 |  |  | 84.92
2003-07-01 | 1 | 7 | 0.625 | 28.9 | 84.02 | 33.5879 |  |  | 84.02
2003-07-01 | 1 | 7 | 0.66667 | 28.9 | 84.02 | 34.147 |  |  | 84.02
2003-07-01 | 1 | 7 | 0.70833 | 28.3 | 82.94 | 34.4746 |  |  | 82.94
2003-07-01 | 1 | 7 | 0.75 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
2003-07-01 | 1 | 7 | 0.79167 | 25 | 77 | 33.5046 |  |  | 77
2003-07-01 | 1 | 7 | 0.83333 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
2003-07-01 | 1 | 7 | 0.875 | 23.3 | 73.94 | 32.6693 |  |  | 73.94
2003-07-01 | 1 | 7 | 0.91667 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
2003-07-01 | 1 | 7 | 0.95833 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
2003-07-01 | 1 | 7 | 1 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
2003-07-02 | 2 | 7 | 0.041667 | 22.2 | 71.96 | 32.6996 |  |  |  | 71.96
2003-07-02 | 2 | 7 | 0.083333 | 22.2 | 71.96 | 32.3241 |  |  |  | 71.96
2003-07-02 | 2 | 7 | 0.125 | 22.2 | 71.96 | 32.3241 |  |  |  | 71.96
2003-07-02 | 2 | 7 | 0.16667 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
2003-07-02 | 2 | 7 | 0.20833 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
2003-07-02 | 2 | 7 | 0.25 | 22.2 | 71.96 | 32.3241 |  |  | 71.96
2003-07-02 | 2 | 7 | 0.29167 | 25 | 77 | 33.9499 |  |  | 77
2003-07-02 | 2 | 7 | 0.33333 | 27.8 | 82.04 | 34.6146 |  |  | 82.04
2003-07-02 | 2 | 7 | 0.375 | 28.3 | 82.94 | 34.4746 |  |  | 82.94
2003-07-02 | 2 | 7 | 0.41667 | 30 | 86 | 33.7792 |  |  | 86
2003-07-02 | 2 | 7 | 0.45833 | 30 | 86 | 35.5694 |  |  | 86
2003-07-02 | 2 | 7 | 0.5 | 31.1 | 87.98 | 36.0911 |  |  | 87.98
2003-07-02 | 2 | 7 | 0.54167 | 31.1 | 87.98 | 35.7724 |  |  | 87.98
2003-07-02 | 2 | 7 | 0.58333 | 31.1 | 87.98 | 36.0911 |  |  | 87.98
2003-07-02 | 2 | 7 | 0.625 | 30 | 86 | 34.6732 |  |  | 86
2003-07-02 | 2 | 7 | 0.66667 | 28.9 | 84.02 | 34.707 |  |  | 84.02
2003-07-02 | 2 | 7 | 0.70833 | 28.9 | 84.02 | 34.147 |  |  | 84.02
2003-07-02 | 2 | 7 | 0.75 | 27.2 | 80.96 | 33.3171 |  |  | 80.96
2003-07-02 | 2 | 7 | 0.79167 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
2003-07-02 | 2 | 7 | 0.83333 | 25 | 77 | 34.6191 |  |  | 77
2003-07-02 | 2 | 7 | 0.875 | 26.1 | 78.98 | 35.0304 |  |  | 78.98
2003-07-02 | 2 | 7 | 0.91667 | 26.7 | 80.06 | 35.3954 |  |  |  | 80.06
2003-07-02 | 2 | 7 | 0.95833 | 26.7 | 80.06 | 35.3954 |  |  |  | 80.06
2003-07-02 | 2 | 7 | 1 | 26.1 | 78.98 | 35.0304 |  |  |  | 78.98
2003-07-03 | 3 | 7 | 0.041667 | 25.6 | 78.08 | 34.7915 |  |  |  | 78.08
2003-07-03 | 3 | 7 | 0.083333 | 25.6 | 78.08 | 35.4864 |  |  |  | 78.08
2003-07-03 | 3 | 7 | 0.125 | 25 | 77 | 35.2895 |  |  |  | 77
2003-07-03 | 3 | 7 | 0.16667 | 25.6 | 78.08 | 35.4864 |  |  |  | 78.08
2003-07-03 | 3 | 7 | 0.20833 | 26.1 | 78.98 | 35.7466 |  |  |  | 78.98
2003-07-03 | 3 | 7 | 0.25 | 25.6 | 78.08 | 34.7915 |  |  | 78.08
2003-07-03 | 3 | 7 | 0.29167 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
2003-07-03 | 3 | 7 | 0.33333 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
2003-07-03 | 3 | 7 | 0.375 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
2003-07-03 | 3 | 7 | 0.41667 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
2003-07-03 | 3 | 7 | 0.45833 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
2003-07-03 | 3 | 7 | 0.5 | 27.2 | 80.96 | 34.8385 |  |  | 80.96
2003-07-03 | 3 | 7 | 0.54167 | 27.2 | 80.96 | 34.8385 |  |  | 80.96
2003-07-03 | 3 | 7 | 0.58333 | 27.2 | 80.96 | 33.8235 |  |  | 80.96
2003-07-03 | 3 | 7 | 0.625 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
2003-07-03 | 3 | 7 | 0.66667 | 28.3 | 82.94 | 33.934 |  |  | 82.94
2003-07-03 | 3 | 7 | 0.70833 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
2003-07-03 | 3 | 7 | 0.75 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
2003-07-03 | 3 | 7 | 0.79167 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
2003-07-03 | 3 | 7 | 0.83333 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
2003-07-03 | 3 | 7 | 0.875 | 25 | 77 | 33.9499 |  |  | 77
2003-07-03 | 3 | 7 | 0.91667 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
2003-07-03 | 3 | 7 | 0.95833 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
2003-07-03 | 3 | 7 | 1 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
2003-07-04 | 4 | 7 | 0.041667 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
2003-07-04 | 4 | 7 | 0.083333 | 21.7 | 71.06 | 33.6452 |  |  |  | 71.06
2003-07-04 | 4 | 7 | 0.125 | 21.7 | 71.06 | 33.6452 |  |  |  | 71.06
2003-07-04 | 4 | 7 | 0.16667 | 21.7 | 71.06 | 33.0973 |  |  |  | 71.06
2003-07-04 | 4 | 7 | 0.20833 | 21.1 | 69.98 | 32.7659 |  |  |  | 69.98
2003-07-04 | 4 | 7 | 0.25 | 20.6 | 69.08 | 32.0493 |  |  | 69.08
2003-07-04 | 4 | 7 | 0.29167 | 20.6 | 69.08 | 32.0493 |  |  | 69.08
2003-07-04 | 4 | 7 | 0.33333 | 21.7 | 71.06 | 32.0043 |  |  | 71.06
2003-07-04 | 4 | 7 | 0.375 | 23.3 | 73.94 | 32.2682 |  |  | 73.94
2003-07-04 | 4 | 7 | 0.41667 | 24.4 | 75.92 | 32.2704 |  |  | 75.92
2003-07-04 | 4 | 7 | 0.45833 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
2003-07-04 | 4 | 7 | 0.5 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
2003-07-04 | 4 | 7 | 0.54167 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
2003-07-04 | 4 | 7 | 0.58333 | 26.7 | 80.06 | 32.6863 |  |  | 80.06
2003-07-04 | 4 | 7 | 0.625 | 27.2 | 80.96 | 32.8114 |  |  | 80.96
2003-07-04 | 4 | 7 | 0.66667 | 28.3 | 82.94 | 30.44 |  |  | 82.94
2003-07-04 | 4 | 7 | 0.70833 | 27.8 | 82.04 | 30.1728 |  |  | 82.04
2003-07-04 | 4 | 7 | 0.75 | 26.7 | 80.06 | 29.7549 |  |  | 80.06
2003-07-04 | 4 | 7 | 0.79167 | 26.1 | 78.98 | 29.3538 |  |  | 78.98
2003-07-04 | 4 | 7 | 0.83333 | 24.4 | 75.92 | 28.6509 |  |  | 75.92
2003-07-04 | 4 | 7 | 0.875 | 23.9 | 75.02 | 28.9405 |  |  | 75.02
2003-07-04 | 4 | 7 | 0.91667 | 22.8 | 73.04 | 29.0905 |  |  |  | 73.04
2003-07-04 | 4 | 7 | 0.95833 | 22.2 | 71.96 | 30.2661 |  |  |  | 71.96
2003-07-04 | 4 | 7 | 1 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
2003-07-05 | 5 | 7 | 0.041667 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
2003-07-05 | 5 | 7 | 0.083333 | 21.1 | 69.98 | 31.7129 |  |  |  | 69.98
2003-07-05 | 5 | 7 | 0.125 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
2003-07-05 | 5 | 7 | 0.16667 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
2003-07-05 | 5 | 7 | 0.20833 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
2003-07-05 | 5 | 7 | 0.25 | 21.1 | 69.98 | 31.7129 |  |  | 69.98
2003-07-05 | 5 | 7 | 0.29167 | 21.7 | 71.06 | 32.5504 |  |  | 71.06
2003-07-05 | 5 | 7 | 0.33333 | 22.8 | 73.04 | 32.967 |  |  | 73.04
2003-07-05 | 5 | 7 | 0.375 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
2003-07-05 | 5 | 7 | 0.41667 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
2003-07-05 | 5 | 7 | 0.45833 | 25.6 | 78.08 | 34.7915 |  |  | 78.08
2003-07-05 | 5 | 7 | 0.5 | 27.2 | 80.96 | 35.6018 |  |  | 80.96
2003-07-05 | 5 | 7 | 0.54167 | 28.9 | 84.02 | 36.3924 |  |  | 84.02
2003-07-05 | 5 | 7 | 0.58333 | 30 | 86 | 36.768 |  |  | 86
2003-07-05 | 5 | 7 | 0.625 | 28.9 | 84.02 | 36.956 |  |  | 84.02
2003-07-05 | 5 | 7 | 0.66667 | 29.4 | 84.92 | 37.1017 |  |  | 84.92
2003-07-05 | 5 | 7 | 0.70833 | 28.3 | 82.94 | 36.6457 |  |  | 82.94
2003-07-05 | 5 | 7 | 0.75 | 27.2 | 80.96 | 36.622 |  |  | 80.96
2003-07-05 | 5 | 7 | 0.79167 | 25.6 | 78.08 | 35.9504 |  |  | 78.08
2003-07-05 | 5 | 7 | 0.83333 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
2003-07-05 | 5 | 7 | 0.875 | 25 | 77 | 35.7372 |  |  | 77
2003-07-05 | 5 | 7 | 0.91667 | 25 | 77 | 36.4098 |  |  |  | 77
2003-07-05 | 5 | 7 | 0.95833 | 25.6 | 78.08 | 36.6477 |  |  |  | 78.08
2003-07-05 | 5 | 7 | 1 | 25 | 77 | 35.7372 |  |  |  | 77
2003-07-06 | 6 | 7 | 0.041667 | 25 | 77 | 35.7372 |  |  |  | 77
2003-07-06 | 6 | 7 | 0.083333 | 24.4 | 75.92 | 35.4956 |  |  |  | 75.92
2003-07-06 | 6 | 7 | 0.125 | 24.4 | 75.92 | 34.8482 |  |  |  | 75.92
2003-07-06 | 6 | 7 | 0.16667 | 25 | 77 | 36.4098 |  |  |  | 77
2003-07-06 | 6 | 7 | 0.20833 | 24.4 | 75.92 | 35.4956 |  |  |  | 75.92
2003-07-06 | 6 | 7 | 0.25 | 25 | 77 | 35.7372 |  |  | 77
2003-07-06 | 6 | 7 | 0.29167 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
2003-07-06 | 6 | 7 | 0.33333 | 28.3 | 82.94 | 37.7364 |  |  | 82.94
2003-07-06 | 6 | 7 | 0.375 | 28.3 | 82.94 | 38.5566 |  |  | 82.94
2003-07-06 | 6 | 7 | 0.41667 | 30 | 86 | 39.7824 |  |  | 86
2003-07-06 | 6 | 7 | 0.45833 | 31.1 | 87.98 | 39.6159 |  |  | 87.98
2003-07-06 | 6 | 7 | 0.5 | 32.2 | 89.96 | 39.6148 |  |  | 89.96
2003-07-06 | 6 | 7 | 0.54167 | 33.9 | 93.02 | 41.0941 |  |  | 93.02
2003-07-06 | 6 | 7 | 0.58333 | 36.1 | 96.98 | 40.7267 |  |  | 96.98
2003-07-06 | 6 | 7 | 0.625 | 35.6 | 96.08 | 40.4339 |  |  | 96.08
2003-07-06 | 6 | 7 | 0.66667 | 32.2 | 89.96 | 41.3318 |  |  | 89.96
2003-07-06 | 6 | 7 | 0.70833 | 32.8 | 91.04 | 41.2298 |  |  | 91.04
2003-07-06 | 6 | 7 | 0.75 | 32.8 | 91.04 | 41.2298 |  |  | 91.04
2003-07-06 | 6 | 7 | 0.79167 | 32.8 | 91.04 | 41.2298 |  |  | 91.04
2003-07-06 | 6 | 7 | 0.83333 | 31.7 | 89.06 | 40.5429 |  |  | 89.06
2003-07-06 | 6 | 7 | 0.875 | 31.7 | 89.06 | 40.5429 |  |  | 89.06
2003-07-06 | 6 | 7 | 0.91667 | 30 | 86 | 37.9706 |  |  |  | 86
2003-07-06 | 6 | 7 | 0.95833 | 29.4 | 84.92 | 36.5215 |  |  |  | 84.92
2003-07-06 | 6 | 7 | 1 | 27.8 | 82.04 | 35.9318 |  |  |  | 82.04
2003-07-07 | 7 | 7 | 0.041667 | 27.8 | 82.04 | 35.9318 |  |  |  | 82.04
2003-07-07 | 7 | 7 | 0.083333 | 26.7 | 80.06 | 35.3954 |  |  |  | 80.06
2003-07-07 | 7 | 7 | 0.125 | 26.7 | 80.06 | 34.6544 |  |  |  | 80.06
2003-07-07 | 7 | 7 | 0.16667 | 25.6 | 78.08 | 34.3289 |  |  |  | 78.08
2003-07-07 | 7 | 7 | 0.20833 | 26.7 | 80.06 | 34.6544 |  |  |  | 80.06
2003-07-07 | 7 | 7 | 0.25 | 26.1 | 78.98 | 34.5538 |  |  | 78.98
2003-07-07 | 7 | 7 | 0.29167 | 25.6 | 78.08 | 33.867 |  |  | 78.08
2003-07-07 | 7 | 7 | 0.33333 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
2003-07-07 | 7 | 7 | 0.375 | 27.8 | 82.04 | 35.1409 |  |  | 82.04
2003-07-07 | 7 | 7 | 0.41667 | 31.7 | 89.06 | 36.5577 |  |  | 89.06
2003-07-07 | 7 | 7 | 0.45833 | 32.8 | 91.04 | 37.3369 |  |  | 91.04
2003-07-07 | 7 | 7 | 0.5 | 32.8 | 91.04 | 36.9851 |  |  | 91.04
2003-07-07 | 7 | 7 | 0.54167 | 33.9 | 93.02 | 39.5849 |  |  | 93.02
2003-07-07 | 7 | 7 | 0.58333 | 33.9 | 93.02 | 40.3387 |  |  | 93.02
2003-07-07 | 7 | 7 | 0.625 | 33.9 | 93.02 | 40.3387 |  |  | 93.02
2003-07-07 | 7 | 7 | 0.66667 | 36.1 | 96.98 | 40.3009 |  |  | 96.98
2003-07-07 | 7 | 7 | 0.70833 | 33.9 | 93.02 | 38.4573 |  |  | 93.02
2003-07-07 | 7 | 7 | 0.75 | 32.2 | 89.96 | 37.9061 |  |  | 89.96
2003-07-07 | 7 | 7 | 0.79167 | 32.2 | 89.96 | 38.2472 |  |  | 89.96
2003-07-07 | 7 | 7 | 0.83333 | 31.7 | 89.06 | 38.8769 |  |  | 89.06
2003-07-07 | 7 | 7 | 0.875 | 31.1 | 87.98 | 38.9724 |  |  | 87.98
2003-07-07 | 7 | 7 | 0.91667 | 27.8 | 82.04 | 36.9892 |  |  |  | 82.04
2003-07-07 | 7 | 7 | 0.95833 | 26.1 | 78.98 | 35.7466 |  |  |  | 78.98
2003-07-07 | 7 | 7 | 1 | 26.1 | 78.98 | 35.7466 |  |  |  | 78.98
2003-07-08 | 8 | 7 | 0.041667 | 26.7 | 80.06 | 36.3857 |  |  |  | 80.06
2003-07-08 | 8 | 7 | 0.083333 | 27.2 | 80.96 | 36.622 |  |  |  | 80.96
2003-07-08 | 8 | 7 | 0.125 | 26.7 | 80.06 | 35.8902 |  |  |  | 80.06
2003-07-08 | 8 | 7 | 0.16667 | 26.1 | 78.98 | 36.2248 |  |  |  | 78.98
2003-07-08 | 8 | 7 | 0.20833 | 25 | 77 | 35.7372 |  |  |  | 77
2003-07-08 | 8 | 7 | 0.25 | 26.1 | 78.98 | 37.4233 |  |  | 78.98
2003-07-08 | 8 | 7 | 0.29167 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
2003-07-08 | 8 | 7 | 0.33333 | 27.2 | 80.96 | 37.3891 |  |  | 80.96
2003-07-08 | 8 | 7 | 0.375 | 27.8 | 82.04 | 38.3155 |  |  | 82.04
2003-07-08 | 8 | 7 | 0.41667 | 29.4 | 84.92 | 39.7245 |  |  | 84.92
2003-07-08 | 8 | 7 | 0.45833 | 31.7 | 89.06 | 41.2115 |  |  | 89.06
2003-07-08 | 8 | 7 | 0.5 | 35.6 | 96.08 | 44.6013 |  |  | 96.08
2003-07-08 | 8 | 7 | 0.54167 | 35 | 95 | 43.6102 |  |  | 95
2003-07-08 | 8 | 7 | 0.58333 | 31.1 | 87.98 | 42.5264 |  |  | 87.98
2003-07-08 | 8 | 7 | 0.625 | 23.9 | 75.02 | 37.2703 |  |  | 75.02
2003-07-08 | 8 | 7 | 0.66667 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
2003-07-08 | 8 | 7 | 0.70833 | 25 | 77 | 37.7589 |  |  | 77
2003-07-08 | 8 | 7 | 0.75 | 25.6 | 78.08 | 38.0464 |  |  | 78.08
2003-07-08 | 8 | 7 | 0.79167 | 25 | 77 | 37.7589 |  |  | 77
2003-07-08 | 8 | 7 | 0.83333 | 25.6 | 78.08 | 38.0464 |  |  | 78.08
2003-07-08 | 8 | 7 | 0.875 | 25 | 77 | 37.7589 |  |  | 77
2003-07-08 | 8 | 7 | 0.91667 | 25 | 77 | 37.7589 |  |  |  | 77
2003-07-08 | 8 | 7 | 0.95833 | 25 | 77 | 37.7589 |  |  |  | 77
2003-07-08 | 8 | 7 | 1 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
2003-07-09 | 9 | 7 | 0.041667 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
2003-07-09 | 9 | 7 | 0.083333 | 23.3 | 73.94 | 36.9091 |  |  |  | 73.94
2003-07-09 | 9 | 7 | 0.125 | 23.3 | 73.94 | 36.9091 |  |  |  | 73.94
2003-07-09 | 9 | 7 | 0.16667 | 23.3 | 73.94 | 36.9091 |  |  |  | 73.94
2003-07-09 | 9 | 7 | 0.20833 | 23.3 | 73.94 | 36.9091 |  |  |  | 73.94
2003-07-09 | 9 | 7 | 0.25 | 22.8 | 73.04 | 36.6901 |  |  | 73.04
2003-07-09 | 9 | 7 | 0.29167 | 23.3 | 73.94 | 37.519 |  |  | 73.94
2003-07-09 | 9 | 7 | 0.33333 | 24.4 | 75.92 | 38.7509 |  |  | 75.92
2003-07-09 | 9 | 7 | 0.375 | 25.6 | 78.08 | 39.2162 |  |  | 78.08
2003-07-09 | 9 | 7 | 0.41667 | 27.8 | 82.04 | 40.1807 |  |  | 82.04
2003-07-09 | 9 | 7 | 0.45833 | 29.4 | 84.92 | 40.8966 |  |  | 84.92
2003-07-09 | 9 | 7 | 0.5 | 31.1 | 87.98 | 41.8775 |  |  | 87.98
2003-07-09 | 9 | 7 | 0.54167 | 33.9 | 93.02 | 41.4724 |  |  | 93.02
2003-07-09 | 9 | 7 | 0.58333 | 33.9 | 93.02 | 41.4724 |  |  | 93.02
2003-07-09 | 9 | 7 | 0.625 | 33.3 | 91.94 | 41.2878 |  |  | 91.94
2003-07-09 | 9 | 7 | 0.66667 | 31.1 | 87.98 | 40.2606 |  |  | 87.98
2003-07-09 | 9 | 7 | 0.70833 | 31.7 | 89.06 | 41.2115 |  |  | 89.06
2003-07-09 | 9 | 7 | 0.75 | 30.6 | 87.08 | 40.1114 |  |  | 87.08
2003-07-09 | 9 | 7 | 0.79167 | 30.6 | 87.08 | 40.1114 |  |  | 87.08
2003-07-09 | 9 | 7 | 0.83333 | 30.6 | 87.08 | 40.739 |  |  | 87.08
2003-07-09 | 9 | 7 | 0.875 | 30 | 86 | 41.2994 |  |  | 86
2003-07-09 | 9 | 7 | 0.91667 | 30 | 86 | 41.2994 |  |  |  | 86
2003-07-09 | 9 | 7 | 0.95833 | 30 | 86 | 40.3884 |  |  |  | 86
2003-07-09 | 9 | 7 | 1 | 29.4 | 84.92 | 36.5215 |  |  |  | 84.92
2003-07-10 | 10 | 7 | 0.041667 | 28.3 | 82.94 | 35.5585 |  |  |  | 82.94
2003-07-10 | 10 | 7 | 0.083333 | 27.2 | 80.96 | 34.8385 |  |  |  | 80.96
2003-07-10 | 10 | 7 | 0.125 | 26.7 | 80.06 | 35.3954 |  |  |  | 80.06
2003-07-10 | 10 | 7 | 0.16667 | 25.6 | 78.08 | 34.7915 |  |  |  | 78.08
2003-07-10 | 10 | 7 | 0.20833 | 25.6 | 78.08 | 33.867 |  |  |  | 78.08
2003-07-10 | 10 | 7 | 0.25 | 25 | 77 | 33.9499 |  |  | 77
2003-07-10 | 10 | 7 | 0.29167 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
2003-07-10 | 10 | 7 | 0.33333 | 26.7 | 80.06 | 33.669 |  |  | 80.06
2003-07-10 | 10 | 7 | 0.375 | 27.8 | 82.04 | 32.7787 |  |  | 82.04
2003-07-10 | 10 | 7 | 0.41667 | 28.9 | 84.02 | 32.7509 |  |  | 84.02
2003-07-10 | 10 | 7 | 0.45833 | 30 | 86 | 32.2944 |  |  | 86
2003-07-10 | 10 | 7 | 0.5 | 30 | 86 | 31.9982 |  |  | 86
2003-07-10 | 10 | 7 | 0.54167 | 30.6 | 87.08 | 32.6665 |  |  | 87.08
2003-07-10 | 10 | 7 | 0.58333 | 30.6 | 87.08 | 32.9736 |  |  | 87.08
2003-07-10 | 10 | 7 | 0.625 | 31.1 | 87.98 | 33.2334 |  |  | 87.98
2003-07-10 | 10 | 7 | 0.66667 | 31.1 | 87.98 | 38.0093 |  |  | 87.98
2003-07-10 | 10 | 7 | 0.70833 | 31.1 | 87.98 | 33.2334 |  |  | 87.98
2003-07-10 | 10 | 7 | 0.75 | 30 | 86 | 33.1846 |  |  | 86
2003-07-10 | 10 | 7 | 0.79167 | 28.9 | 84.02 | 33.3087 |  |  | 84.02
2003-07-10 | 10 | 7 | 0.83333 | 28.3 | 82.94 | 32.8552 |  |  | 82.94
2003-07-10 | 10 | 7 | 0.875 | 27.8 | 82.04 | 32.7787 |  |  | 82.04
2003-07-10 | 10 | 7 | 0.91667 | 27.2 | 80.96 | 32.8114 |  |  |  | 80.96
2003-07-10 | 10 | 7 | 0.95833 | 25 | 77 | 31.0651 |  |  |  | 77
2003-07-10 | 10 | 7 | 1 | 23.3 | 73.94 | 28.8773 |  |  |  | 73.94
2003-07-11 | 11 | 7 | 0.041667 | 22.2 | 71.96 | 28.0348 |  |  |  | 71.96
2003-07-11 | 11 | 7 | 0.083333 | 21.7 | 71.06 | 27.1277 |  |  |  | 71.06
2003-07-11 | 11 | 7 | 0.125 | 21.1 | 69.98 | 26.8408 |  |  |  | 69.98
2003-07-11 | 11 | 7 | 0.16667 | 20 | 68 | 26.3346 |  |  |  | 68
2003-07-11 | 11 | 7 | 0.20833 | 19.4 | 66.92 | 26.4765 |  |  |  | 66.92
2003-07-11 | 11 | 7 | 0.25 | 20 | 68 | 26.6574 |  |  | 68
2003-07-11 | 11 | 7 | 0.29167 | 21.1 | 69.98 | 27.1866 |  |  | 69.98
2003-07-11 | 11 | 7 | 0.33333 | 22.2 | 71.96 | 27.2943 |  |  | 71.96
2003-07-11 | 11 | 7 | 0.375 | 23.3 | 73.94 | 27.8863 |  |  | 73.94
2003-07-11 | 11 | 7 | 0.41667 | 24.4 | 75.92 | 28.6509 |  |  | 75.92
2003-07-11 | 11 | 7 | 0.45833 | 25 | 77 | 28.8622 |  |  | 77
2003-07-11 | 11 | 7 | 0.5 | 26.1 | 78.98 | 29.3538 |  |  | 78.98
2003-07-11 | 11 | 7 | 0.54167 | 26.1 | 78.98 | 28.6507 |  |  | 78.98
2003-07-11 | 11 | 7 | 0.58333 | 27.2 | 80.96 | 29.0421 |  |  | 80.96
2003-07-11 | 11 | 7 | 0.625 | 27.2 | 80.96 | 28.7923 |  |  | 80.96
2003-07-11 | 11 | 7 | 0.66667 | 27.8 | 82.04 | 28.3603 |  |  | 82.04
2003-07-11 | 11 | 7 | 0.70833 | 27.8 | 82.04 | 28.6186 |  |  | 82.04
2003-07-11 | 11 | 7 | 0.75 | 27.8 | 82.04 | 28.6186 |  |  | 82.04
2003-07-11 | 11 | 7 | 0.79167 | 26.7 | 80.06 | 27.8142 |  |  | 80.06
2003-07-11 | 11 | 7 | 0.83333 | 26.1 | 78.98 | 27.0156 |  |  | 78.98
2003-07-11 | 11 | 7 | 0.875 | 25 | 77 | 30.6234 |  |  | 77
2003-07-11 | 11 | 7 | 0.91667 | 24.4 | 75.92 | 31.2019 |  |  |  | 75.92
2003-07-11 | 11 | 7 | 0.95833 | 23.9 | 75.02 | 31.4185 |  |  |  | 75.02
2003-07-11 | 11 | 7 | 1 | 23.9 | 75.02 | 31.0043 |  |  |  | 75.02
2003-07-12 | 12 | 7 | 0.041667 | 23.3 | 73.94 | 30.6683 |  |  |  | 73.94
2003-07-12 | 12 | 7 | 0.083333 | 23.3 | 73.94 | 29.8712 |  |  |  | 73.94
2003-07-12 | 12 | 7 | 0.125 | 22.8 | 73.04 | 29.0905 |  |  |  | 73.04
2003-07-12 | 12 | 7 | 0.16667 | 22.8 | 73.04 | 28.7052 |  |  |  | 73.04
2003-07-12 | 12 | 7 | 0.20833 | 22.2 | 71.96 | 28.9628 |  |  |  | 71.96
2003-07-12 | 12 | 7 | 0.25 | 22.8 | 73.04 | 28.7052 |  |  | 73.04
2003-07-12 | 12 | 7 | 0.29167 | 23.9 | 75.02 | 30.1773 |  |  | 75.02
2003-07-12 | 12 | 7 | 0.33333 | 26.1 | 78.98 | 30.5288 |  |  | 78.98
2003-07-12 | 12 | 7 | 0.375 | 26.7 | 80.06 | 29.0259 |  |  | 80.06
2003-07-12 | 12 | 7 | 0.41667 | 27.2 | 80.96 | 28.7923 |  |  | 80.96
2003-07-12 | 12 | 7 | 0.45833 | 28.3 | 82.94 | 29.6386 |  |  | 82.94
2003-07-12 | 12 | 7 | 0.5 | 28.3 | 82.94 | 29.6386 |  |  | 82.94
2003-07-12 | 12 | 7 | 0.54167 | 29.4 | 84.92 | 29.9177 |  |  | 84.92
2003-07-12 | 12 | 7 | 0.58333 | 29.4 | 84.92 | 30.2022 |  |  | 84.92
2003-07-12 | 12 | 7 | 0.625 | 31.1 | 87.98 | 31.3412 |  |  | 87.98
2003-07-12 | 12 | 7 | 0.66667 | 31.7 | 89.06 | 32.2911 |  |  | 89.06
2003-07-12 | 12 | 7 | 0.70833 | 29.4 | 84.92 | 32.2005 |  |  | 84.92
2003-07-12 | 12 | 7 | 0.75 | 28.3 | 82.94 | 33.3941 |  |  | 82.94
2003-07-12 | 12 | 7 | 0.79167 | 29.4 | 84.92 | 34.7867 |  |  | 84.92
2003-07-12 | 12 | 7 | 0.83333 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
2003-07-12 | 12 | 7 | 0.875 | 28.3 | 82.94 | 32.0482 |  |  | 82.94
2003-07-12 | 12 | 7 | 0.91667 | 28.9 | 84.02 | 31.3605 |  |  |  | 84.02
2003-07-12 | 12 | 7 | 0.95833 | 28.3 | 82.94 | 31.2432 |  |  |  | 82.94
2003-07-12 | 12 | 7 | 1 | 28.3 | 82.94 | 30.7075 |  |  |  | 82.94
2003-07-13 | 13 | 7 | 0.041667 | 26.7 | 80.06 | 31.4619 |  |  |  | 80.06
2003-07-13 | 13 | 7 | 0.083333 | 26.1 | 78.98 | 30.9999 |  |  |  | 78.98
2003-07-13 | 13 | 7 | 0.125 | 25.6 | 78.08 | 30.8795 |  |  |  | 78.08
2003-07-13 | 13 | 7 | 0.16667 | 25 | 77 | 30.6234 |  |  |  | 77
2003-07-13 | 13 | 7 | 0.20833 | 25 | 77 | 30.6234 |  |  |  | 77
2003-07-13 | 13 | 7 | 0.25 | 26.1 | 78.98 | 31.4717 |  |  | 78.98
2003-07-13 | 13 | 7 | 0.29167 | 27.8 | 82.04 | 32.7787 |  |  | 82.04
2003-07-13 | 13 | 7 | 0.33333 | 27.8 | 82.04 | 32.7787 |  |  | 82.04
2003-07-13 | 13 | 7 | 0.375 | 28.9 | 84.02 | 33.5879 |  |  | 84.02
2003-07-13 | 13 | 7 | 0.41667 | 30.6 | 87.08 | 34.5129 |  |  | 87.08
2003-07-13 | 13 | 7 | 0.45833 | 32.8 | 91.04 | 35.2316 |  |  | 91.04
2003-07-13 | 13 | 7 | 0.5 | 33.3 | 91.94 | 35.4809 |  |  | 91.94
2003-07-13 | 13 | 7 | 0.54167 | 36.1 | 96.98 | 36.4916 |  |  | 96.98
2003-07-13 | 13 | 7 | 0.58333 | 36.7 | 98.06 | 35.902 |  |  | 98.06
2003-07-13 | 13 | 7 | 0.625 | 35 | 95 | 37.9914 |  |  | 95
2003-07-13 | 13 | 7 | 0.66667 | 33.9 | 93.02 | 39.2086 |  |  | 93.02
2003-07-13 | 13 | 7 | 0.70833 | 32.8 | 91.04 | 38.7475 |  |  | 91.04
2003-07-13 | 13 | 7 | 0.75 | 32.2 | 89.96 | 38.9303 |  |  | 89.96
2003-07-13 | 13 | 7 | 0.79167 | 31.7 | 89.06 | 38.8769 |  |  | 89.06
2003-07-13 | 13 | 7 | 0.83333 | 30 | 86 | 38.5735 |  |  | 86
2003-07-13 | 13 | 7 | 0.875 | 30.6 | 87.08 | 38.2353 |  |  | 87.08
2003-07-13 | 13 | 7 | 0.91667 | 30 | 86 | 37.9706 |  |  |  | 86
2003-07-13 | 13 | 7 | 0.95833 | 30.6 | 87.08 | 37.6121 |  |  |  | 87.08
2003-07-13 | 13 | 7 | 1 | 27.8 | 82.04 | 35.1409 |  |  |  | 82.04
2003-07-14 | 14 | 7 | 0.041667 | 27.2 | 80.96 | 34.8385 |  |  |  | 80.96
2003-07-14 | 14 | 7 | 0.083333 | 26.7 | 80.06 | 34.6544 |  |  |  | 80.06
2003-07-14 | 14 | 7 | 0.125 | 25 | 77 | 34.6191 |  |  |  | 77
2003-07-14 | 14 | 7 | 0.16667 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
2003-07-14 | 14 | 7 | 0.20833 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
2003-07-14 | 14 | 7 | 0.25 | 25 | 77 | 32.8375 |  |  | 77
2003-07-14 | 14 | 7 | 0.29167 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
2003-07-14 | 14 | 7 | 0.33333 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
2003-07-14 | 14 | 7 | 0.375 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
2003-07-14 | 14 | 7 | 0.41667 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
2003-07-14 | 14 | 7 | 0.45833 | 27.2 | 80.96 | 34.5845 |  |  | 80.96
2003-07-14 | 14 | 7 | 0.5 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
2003-07-14 | 14 | 7 | 0.54167 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
2003-07-14 | 14 | 7 | 0.58333 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
2003-07-14 | 14 | 7 | 0.625 | 26.1 | 78.98 | 35.0304 |  |  | 78.98
2003-07-14 | 14 | 7 | 0.66667 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
2003-07-14 | 14 | 7 | 0.70833 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
2003-07-14 | 14 | 7 | 0.75 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
2003-07-14 | 14 | 7 | 0.79167 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
2003-07-14 | 14 | 7 | 0.83333 | 22.2 | 71.96 | 34.017 |  |  | 71.96
2003-07-14 | 14 | 7 | 0.875 | 22.2 | 71.96 | 34.017 |  |  | 71.96
2003-07-14 | 14 | 7 | 0.91667 | 22.2 | 71.96 | 33.2636 |  |  |  | 71.96
2003-07-14 | 14 | 7 | 0.95833 | 21.1 | 69.98 | 32.7659 |  |  |  | 69.98
2003-07-14 | 14 | 7 | 1 | 21.1 | 69.98 | 32.7659 |  |  |  | 69.98
2003-07-15 | 15 | 7 | 0.041667 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
2003-07-15 | 15 | 7 | 0.083333 | 20.6 | 69.08 | 32.5601 |  |  |  | 69.08
2003-07-15 | 15 | 7 | 0.125 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
2003-07-15 | 15 | 7 | 0.16667 | 20 | 68 | 31.6992 |  |  |  | 68
2003-07-15 | 15 | 7 | 0.20833 | 20 | 68 | 31.6992 |  |  |  | 68
2003-07-15 | 15 | 7 | 0.25 | 20 | 68 | 31.6992 |  |  | 68
2003-07-15 | 15 | 7 | 0.29167 | 19.4 | 66.92 | 31.0164 |  |  | 66.92
2003-07-15 | 15 | 7 | 0.33333 | 20 | 68 | 31.2081 |  |  | 68
2003-07-15 | 15 | 7 | 0.375 | 20.6 | 69.08 | 31.5393 |  |  | 69.08
2003-07-15 | 15 | 7 | 0.41667 | 21.1 | 69.98 | 31.7129 |  |  | 69.98
2003-07-15 | 15 | 7 | 0.45833 | 21.7 | 71.06 | 32.0043 |  |  | 71.06
2003-07-15 | 15 | 7 | 0.5 | 22.8 | 73.04 | 32.967 |  |  | 73.04
2003-07-15 | 15 | 7 | 0.54167 | 22.8 | 73.04 | 32.967 |  |  | 73.04
2003-07-15 | 15 | 7 | 0.58333 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
2003-07-15 | 15 | 7 | 0.625 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
2003-07-15 | 15 | 7 | 0.66667 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
2003-07-15 | 15 | 7 | 0.70833 | 21.7 | 71.06 | 33.0973 |  |  | 71.06
2003-07-15 | 15 | 7 | 0.75 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
2003-07-15 | 15 | 7 | 0.79167 | 23.9 | 75.02 | 34.1232 |  |  | 75.02
2003-07-15 | 15 | 7 | 0.83333 | 23.9 | 75.02 | 34.1232 |  |  | 75.02
2003-07-15 | 15 | 7 | 0.875 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
2003-07-15 | 15 | 7 | 0.91667 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
2003-07-15 | 15 | 7 | 0.95833 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
2003-07-15 | 15 | 7 | 1 | 23.9 | 75.02 | 35.1691 |  |  |  | 75.02
2003-07-16 | 16 | 7 | 0.041667 | 23.9 | 75.02 | 36.008 |  |  |  | 75.02
2003-07-16 | 16 | 7 | 0.083333 | 22.8 | 73.04 | 34.7256 |  |  |  | 73.04
2003-07-16 | 16 | 7 | 0.125 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
2003-07-16 | 16 | 7 | 0.16667 | 21.7 | 71.06 | 33.6452 |  |  |  | 71.06
2003-07-16 | 16 | 7 | 0.20833 | 21.7 | 71.06 | 33.0973 |  |  |  | 71.06
2003-07-16 | 16 | 7 | 0.25 | 21.7 | 71.06 | 33.0973 |  |  | 71.06
2003-07-16 | 16 | 7 | 0.29167 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
2003-07-16 | 16 | 7 | 0.33333 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
2003-07-16 | 16 | 7 | 0.375 | 27.2 | 80.96 | 37.3891 |  |  | 80.96
2003-07-16 | 16 | 7 | 0.41667 | 28.3 | 82.94 | 36.6457 |  |  | 82.94
2003-07-16 | 16 | 7 | 0.45833 | 30 | 86 | 36.768 |  |  | 86
2003-07-16 | 16 | 7 | 0.5 | 30 | 86 | 36.1682 |  |  | 86
2003-07-16 | 16 | 7 | 0.54167 | 29.4 | 84.92 | 34.7867 |  |  | 84.92
2003-07-16 | 16 | 7 | 0.58333 | 28.9 | 84.02 | 34.707 |  |  | 84.02
2003-07-16 | 16 | 7 | 0.625 | 30 | 86 | 35.2704 |  |  | 86
2003-07-16 | 16 | 7 | 0.66667 | 30.6 | 87.08 | 35.4398 |  |  | 87.08
2003-07-16 | 16 | 7 | 0.70833 | 29.4 | 84.92 | 34.7867 |  |  | 84.92
2003-07-16 | 16 | 7 | 0.75 | 29.4 | 84.92 | 34.4984 |  |  | 84.92
2003-07-16 | 16 | 7 | 0.79167 | 28.3 | 82.94 | 34.4746 |  |  | 82.94
2003-07-16 | 16 | 7 | 0.83333 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
2003-07-16 | 16 | 7 | 0.875 | 26.1 | 78.98 | 32.8908 |  |  | 78.98
2003-07-16 | 16 | 7 | 0.91667 | 26.1 | 78.98 | 32.8908 |  |  |  | 78.98
2003-07-16 | 16 | 7 | 0.95833 | 25.6 | 78.08 | 32.2552 |  |  |  | 78.08
2003-07-16 | 16 | 7 | 1 | 25.6 | 78.08 | 31.796 |  |  |  | 78.08
2003-07-17 | 17 | 7 | 0.041667 | 24.4 | 75.92 | 32.2704 |  |  |  | 75.92
2003-07-17 | 17 | 7 | 0.083333 | 24.4 | 75.92 | 32.2704 |  |  |  | 75.92
2003-07-17 | 17 | 7 | 0.125 | 22.8 | 73.04 | 31.9938 |  |  |  | 73.04
2003-07-17 | 17 | 7 | 0.16667 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
2003-07-17 | 17 | 7 | 0.20833 | 21.7 | 71.06 | 31.459 |  |  |  | 71.06
2003-07-17 | 17 | 7 | 0.25 | 23.3 | 73.94 | 32.2682 |  |  | 73.94
2003-07-17 | 17 | 7 | 0.29167 | 24.4 | 75.92 | 32.6987 |  |  | 75.92
2003-07-17 | 17 | 7 | 0.33333 | 25 | 77 | 32.8375 |  |  | 77
2003-07-17 | 17 | 7 | 0.375 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
2003-07-17 | 17 | 7 | 0.41667 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
2003-07-17 | 17 | 7 | 0.45833 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
2003-07-17 | 17 | 7 | 0.5 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
2003-07-17 | 17 | 7 | 0.54167 | 28.9 | 84.02 | 34.707 |  |  | 84.02
2003-07-17 | 17 | 7 | 0.58333 | 31.7 | 89.06 | 34.582 |  |  | 89.06
2003-07-17 | 17 | 7 | 0.625 | 28.9 | 84.02 | 34.707 |  |  | 84.02
2003-07-17 | 17 | 7 | 0.66667 | 30 | 86 | 34.077 |  |  | 86
2003-07-17 | 17 | 7 | 0.70833 | 29.4 | 84.92 | 33.0604 |  |  | 84.92
2003-07-17 | 17 | 7 | 0.75 | 28.9 | 84.02 | 32.7509 |  |  | 84.02
2003-07-17 | 17 | 7 | 0.79167 | 28.3 | 82.94 | 33.3941 |  |  | 82.94
2003-07-17 | 17 | 7 | 0.83333 | 27.2 | 80.96 | 33.8235 |  |  | 80.96
2003-07-17 | 17 | 7 | 0.875 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
2003-07-17 | 17 | 7 | 0.91667 | 26.1 | 78.98 | 34.5538 |  |  |  | 78.98
2003-07-17 | 17 | 7 | 0.95833 | 26.1 | 78.98 | 35.0304 |  |  |  | 78.98
2003-07-17 | 17 | 7 | 1 | 25.6 | 78.08 | 35.4864 |  |  |  | 78.08
2003-07-18 | 18 | 7 | 0.041667 | 25 | 77 | 35.7372 |  |  |  | 77
2003-07-18 | 18 | 7 | 0.083333 | 23.9 | 75.02 | 35.1691 |  |  |  | 75.02
2003-07-18 | 18 | 7 | 0.125 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
2003-07-18 | 18 | 7 | 0.16667 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
2003-07-18 | 18 | 7 | 0.20833 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
2003-07-18 | 18 | 7 | 0.25 | 23.3 | 73.94 | 36.3002 |  |  | 73.94
2003-07-18 | 18 | 7 | 0.29167 | 23.3 | 73.94 | 36.3002 |  |  | 73.94
2003-07-18 | 18 | 7 | 0.33333 | 22.8 | 73.04 | 35.5101 |  |  | 73.04
2003-07-18 | 18 | 7 | 0.375 | 22.2 | 71.96 | 34.3944 |  |  | 71.96
2003-07-18 | 18 | 7 | 0.41667 | 22.2 | 71.96 | 35.1502 |  |  | 71.96
2003-07-18 | 18 | 7 | 0.45833 | 22.2 | 71.96 | 35.1502 |  |  | 71.96
2003-07-18 | 18 | 7 | 0.5 | 22.8 | 73.04 | 34.7256 |  |  | 73.04
2003-07-18 | 18 | 7 | 0.54167 | 22.8 | 73.04 | 34.7256 |  |  | 73.04
2003-07-18 | 18 | 7 | 0.58333 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
2003-07-18 | 18 | 7 | 0.625 | 23.9 | 75.02 | 34.7504 |  |  | 75.02
2003-07-18 | 18 | 7 | 0.66667 | 23.3 | 73.94 | 33.8754 |  |  | 73.94
2003-07-18 | 18 | 7 | 0.70833 | 23.3 | 73.94 | 33.8754 |  |  | 73.94
2003-07-18 | 18 | 7 | 0.75 | 23.3 | 73.94 | 33.8754 |  |  | 73.94
2003-07-18 | 18 | 7 | 0.79167 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
2003-07-18 | 18 | 7 | 0.83333 | 21.1 | 69.98 | 32.7659 |  |  | 69.98
2003-07-18 | 18 | 7 | 0.875 | 22.8 | 73.04 | 32.967 |  |  | 73.04
2003-07-18 | 18 | 7 | 0.91667 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
2003-07-18 | 18 | 7 | 0.95833 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
2003-07-18 | 18 | 7 | 1 | 23.3 | 73.94 | 34.48 |  |  |  | 73.94
2003-07-19 | 19 | 7 | 0.041667 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
2003-07-19 | 19 | 7 | 0.083333 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
2003-07-19 | 19 | 7 | 0.125 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
2003-07-19 | 19 | 7 | 0.16667 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
2003-07-19 | 19 | 7 | 0.20833 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
2003-07-19 | 19 | 7 | 0.25 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
2003-07-19 | 19 | 7 | 0.29167 | 24.4 | 75.92 | 36.7941 |  |  | 75.92
2003-07-19 | 19 | 7 | 0.33333 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
2003-07-19 | 19 | 7 | 0.375 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
2003-07-19 | 19 | 7 | 0.41667 | 28.3 | 82.94 | 37.7364 |  |  | 82.94
2003-07-19 | 19 | 7 | 0.45833 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
2003-07-19 | 19 | 7 | 0.5 | 29.4 | 84.92 | 38.8481 |  |  | 84.92
2003-07-19 | 19 | 7 | 0.54167 | 28.9 | 84.02 | 38.0859 |  |  | 84.02
2003-07-19 | 19 | 7 | 0.58333 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
2003-07-19 | 19 | 7 | 0.625 | 30.6 | 87.08 | 40.1114 |  |  | 87.08
2003-07-19 | 19 | 7 | 0.66667 | 30.6 | 87.08 | 40.1114 |  |  | 87.08
2003-07-19 | 19 | 7 | 0.70833 | 29.4 | 84.92 | 39.7245 |  |  | 84.92
2003-07-19 | 19 | 7 | 0.75 | 28.3 | 82.94 | 38.5566 |  |  | 82.94
2003-07-19 | 19 | 7 | 0.79167 | 28.3 | 82.94 | 38.5566 |  |  | 82.94
2003-07-19 | 19 | 7 | 0.83333 | 26.7 | 80.06 | 38.3749 |  |  | 80.06
2003-07-19 | 19 | 7 | 0.875 | 26.7 | 80.06 | 39.1237 |  |  | 80.06
2003-07-19 | 19 | 7 | 0.91667 | 26.7 | 80.06 | 39.8742 |  |  |  | 80.06
2003-07-19 | 19 | 7 | 0.95833 | 26.7 | 80.06 | 39.8742 |  |  |  | 80.06
2003-07-19 | 19 | 7 | 1 | 26.7 | 80.06 | 39.8742 |  |  |  | 80.06
2003-07-20 | 20 | 7 | 0.041667 | 26.7 | 80.06 | 39.8742 |  |  |  | 80.06
2003-07-20 | 20 | 7 | 0.083333 | 25.6 | 78.08 | 38.5138 |  |  |  | 78.08
2003-07-20 | 20 | 7 | 0.125 | 25.6 | 78.08 | 38.5138 |  |  |  | 78.08
2003-07-20 | 20 | 7 | 0.16667 | 25.6 | 78.08 | 38.5138 |  |  |  | 78.08
2003-07-20 | 20 | 7 | 0.20833 | 25.6 | 78.08 | 38.5138 |  |  |  | 78.08
2003-07-20 | 20 | 7 | 0.25 | 25.6 | 78.08 | 38.5138 |  |  | 78.08
2003-07-20 | 20 | 7 | 0.29167 | 27.2 | 80.96 | 39.1857 |  |  | 80.96
2003-07-20 | 20 | 7 | 0.33333 | 28.3 | 82.94 | 40.4779 |  |  | 82.94
2003-07-20 | 20 | 7 | 0.375 | 29.4 | 84.92 | 40.8966 |  |  | 84.92
2003-07-20 | 20 | 7 | 0.41667 | 30.6 | 87.08 | 40.1114 |  |  | 87.08
2003-07-20 | 20 | 7 | 0.45833 | 32.2 | 89.96 | 40.3006 |  |  | 89.96
2003-07-20 | 20 | 7 | 0.5 | 32.8 | 91.04 | 39.8092 |  |  | 91.04
2003-07-20 | 20 | 7 | 0.54167 | 32.8 | 91.04 | 39.101 |  |  | 91.04
2003-07-20 | 20 | 7 | 0.58333 | 33.3 | 91.94 | 39.4628 |  |  | 91.94
2003-07-20 | 20 | 7 | 0.625 | 31.7 | 89.06 | 41.2115 |  |  | 89.06
2003-07-20 | 20 | 7 | 0.66667 | 31.7 | 89.06 | 41.8814 |  |  | 89.06
2003-07-20 | 20 | 7 | 0.70833 | 31.7 | 89.06 | 41.2115 |  |  | 89.06
2003-07-20 | 20 | 7 | 0.75 | 30.6 | 87.08 | 40.739 |  |  | 87.08
2003-07-20 | 20 | 7 | 0.79167 | 29.4 | 84.92 | 41.7782 |  |  | 84.92
2003-07-20 | 20 | 7 | 0.83333 | 29.4 | 84.92 | 42.3671 |  |  | 84.92
2003-07-20 | 20 | 7 | 0.875 | 29.4 | 84.92 | 42.3671 |  |  | 84.92
2003-07-20 | 20 | 7 | 0.91667 | 29.4 | 84.92 | 41.7782 |  |  |  | 84.92
2003-07-20 | 20 | 7 | 0.95833 | 28.9 | 84.02 | 40.6417 |  |  |  | 84.02
2003-07-20 | 20 | 7 | 1 | 28.3 | 82.94 | 39.6532 |  |  |  | 82.94
2003-07-21 | 21 | 7 | 0.041667 | 27.8 | 82.04 | 38.8474 |  |  |  | 82.04
2003-07-21 | 21 | 7 | 0.083333 | 27.2 | 80.96 | 39.1857 |  |  |  | 80.96
2003-07-21 | 21 | 7 | 0.125 | 26.7 | 80.06 | 39.1237 |  |  |  | 80.06
2003-07-21 | 21 | 7 | 0.16667 | 26.7 | 80.06 | 38.3749 |  |  |  | 80.06
2003-07-21 | 21 | 7 | 0.20833 | 26.1 | 78.98 | 38.1444 |  |  |  | 78.98
2003-07-21 | 21 | 7 | 0.25 | 26.7 | 80.06 | 39.1237 |  |  | 80.06
2003-07-21 | 21 | 7 | 0.29167 | 27.2 | 80.96 | 39.1857 |  |  | 80.96
2003-07-21 | 21 | 7 | 0.33333 | 28.3 | 82.94 | 39.6532 |  |  | 82.94
2003-07-21 | 21 | 7 | 0.375 | 30 | 86 | 40.3884 |  |  | 86
2003-07-21 | 21 | 7 | 0.41667 | 32.2 | 89.96 | 41.3318 |  |  | 89.96
2003-07-21 | 21 | 7 | 0.45833 | 32.8 | 91.04 | 40.5188 |  |  | 91.04
2003-07-21 | 21 | 7 | 0.5 | 33.3 | 91.94 | 41.2878 |  |  | 91.94
2003-07-21 | 21 | 7 | 0.54167 | 32.2 | 89.96 | 41.3318 |  |  | 89.96
2003-07-21 | 21 | 7 | 0.58333 | 31.1 | 87.98 | 40.9065 |  |  | 87.98
2003-07-21 | 21 | 7 | 0.625 | 31.1 | 87.98 | 40.2606 |  |  | 87.98
2003-07-21 | 21 | 7 | 0.66667 | 30 | 86 | 39.7824 |  |  | 86
2003-07-21 | 21 | 7 | 0.70833 | 31.1 | 87.98 | 40.9065 |  |  | 87.98
2003-07-21 | 21 | 7 | 0.75 | 31.1 | 87.98 | 40.9065 |  |  | 87.98
2003-07-21 | 21 | 7 | 0.79167 | 28.9 | 84.02 | 40.0722 |  |  | 84.02
2003-07-21 | 21 | 7 | 0.83333 | 27.8 | 82.04 | 38.8474 |  |  | 82.04
2003-07-21 | 21 | 7 | 0.875 | 27.2 | 80.96 | 39.1857 |  |  | 80.96
2003-07-21 | 21 | 7 | 0.91667 | 27.2 | 80.96 | 38.6714 |  |  |  | 80.96
2003-07-21 | 21 | 7 | 0.95833 | 27.8 | 82.04 | 38.8474 |  |  |  | 82.04
2003-07-21 | 21 | 7 | 1 | 27.8 | 82.04 | 39.6468 |  |  |  | 82.04
2003-07-22 | 22 | 7 | 0.041667 | 27.2 | 80.96 | 39.1857 |  |  |  | 80.96
2003-07-22 | 22 | 7 | 0.083333 | 27.2 | 80.96 | 38.6714 |  |  |  | 80.96
2003-07-22 | 22 | 7 | 0.125 | 27.2 | 80.96 | 38.6714 |  |  |  | 80.96
2003-07-22 | 22 | 7 | 0.16667 | 27.2 | 80.96 | 38.6714 |  |  |  | 80.96
2003-07-22 | 22 | 7 | 0.20833 | 26.7 | 80.06 | 37.6276 |  |  |  | 80.06
2003-07-22 | 22 | 7 | 0.25 | 26.7 | 80.06 | 38.3749 |  |  | 80.06
2003-07-22 | 22 | 7 | 0.29167 | 27.2 | 80.96 | 38.6714 |  |  | 80.96
2003-07-22 | 22 | 7 | 0.33333 | 27.8 | 82.04 | 38.8474 |  |  | 82.04
2003-07-22 | 22 | 7 | 0.375 | 28.3 | 82.94 | 39.1044 |  |  | 82.94
2003-07-22 | 22 | 7 | 0.41667 | 29.4 | 84.92 | 39.7245 |  |  | 84.92
2003-07-22 | 22 | 7 | 0.45833 | 30 | 86 | 39.7824 |  |  | 86
2003-07-22 | 22 | 7 | 0.5 | 31.7 | 89.06 | 39.8755 |  |  | 89.06
2003-07-22 | 22 | 7 | 0.54167 | 32.2 | 89.96 | 40.3006 |  |  | 89.96
2003-07-22 | 22 | 7 | 0.58333 | 32.2 | 89.96 | 41.3318 |  |  | 89.96
2003-07-22 | 22 | 7 | 0.625 | 31.7 | 89.06 | 40.5429 |  |  | 89.06
2003-07-22 | 22 | 7 | 0.66667 | 30.6 | 87.08 | 40.739 |  |  | 87.08
2003-07-22 | 22 | 7 | 0.70833 | 30.6 | 87.08 | 40.739 |  |  | 87.08
2003-07-22 | 22 | 7 | 0.75 | 30 | 86 | 40.3884 |  |  | 86
2003-07-22 | 22 | 7 | 0.79167 | 28.9 | 84.02 | 39.5035 |  |  | 84.02
2003-07-22 | 22 | 7 | 0.83333 | 28.3 | 82.94 | 39.1044 |  |  | 82.94
2003-07-22 | 22 | 7 | 0.875 | 28.3 | 82.94 | 38.5566 |  |  | 82.94
2003-07-22 | 22 | 7 | 0.91667 | 27.8 | 82.04 | 38.3155 |  |  |  | 82.04
2003-07-22 | 22 | 7 | 0.95833 | 27.8 | 82.04 | 38.3155 |  |  |  | 82.04
2003-07-22 | 22 | 7 | 1 | 26.7 | 80.06 | 36.3857 |  |  |  | 80.06
2003-07-23 | 23 | 7 | 0.041667 | 25.6 | 78.08 | 36.6477 |  |  |  | 78.08
2003-07-23 | 23 | 7 | 0.083333 | 25.6 | 78.08 | 37.3463 |  |  |  | 78.08
2003-07-23 | 23 | 7 | 0.125 | 25.6 | 78.08 | 37.3463 |  |  |  | 78.08
2003-07-23 | 23 | 7 | 0.16667 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-23 | 23 | 7 | 0.20833 | 25.6 | 78.08 | 38.0464 |  |  |  | 78.08
2003-07-23 | 23 | 7 | 0.25 | 25.6 | 78.08 | 37.3463 |  |  | 78.08
2003-07-23 | 23 | 7 | 0.29167 | 26.1 | 78.98 | 37.4233 |  |  | 78.98
2003-07-23 | 23 | 7 | 0.33333 | 26.7 | 80.06 | 37.6276 |  |  | 80.06
2003-07-23 | 23 | 7 | 0.375 | 26.7 | 80.06 | 37.6276 |  |  | 80.06
2003-07-23 | 23 | 7 | 0.41667 | 27.2 | 80.96 | 37.9015 |  |  | 80.96
2003-07-23 | 23 | 7 | 0.45833 | 28.9 | 84.02 | 39.5035 |  |  | 84.02
2003-07-23 | 23 | 7 | 0.5 | 30.6 | 87.08 | 38.8595 |  |  | 87.08
2003-07-23 | 23 | 7 | 0.54167 | 27.2 | 80.96 | 38.6714 |  |  | 80.96
2003-07-23 | 23 | 7 | 0.58333 | 28.3 | 82.94 | 39.6532 |  |  | 82.94
2003-07-23 | 23 | 7 | 0.625 | 23.9 | 75.02 | 36.008 |  |  | 75.02
2003-07-23 | 23 | 7 | 0.66667 | 23.9 | 75.02 | 36.008 |  |  | 75.02
2003-07-23 | 23 | 7 | 0.70833 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
2003-07-23 | 23 | 7 | 0.75 | 24.4 | 75.92 | 36.7941 |  |  | 75.92
2003-07-23 | 23 | 7 | 0.79167 | 25 | 77 | 36.8589 |  |  | 77
2003-07-23 | 23 | 7 | 0.83333 | 24.4 | 75.92 | 36.7941 |  |  | 75.92
2003-07-23 | 23 | 7 | 0.875 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
2003-07-23 | 23 | 7 | 0.91667 | 24.4 | 75.92 | 36.7941 |  |  |  | 75.92
2003-07-23 | 23 | 7 | 0.95833 | 25 | 77 | 37.7589 |  |  |  | 77
2003-07-23 | 23 | 7 | 1 | 24.4 | 75.92 | 36.7941 |  |  |  | 75.92
2003-07-24 | 24 | 7 | 0.041667 | 23.9 | 75.02 | 36.008 |  |  |  | 75.02
2003-07-24 | 24 | 7 | 0.083333 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
2003-07-24 | 24 | 7 | 0.125 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
2003-07-24 | 24 | 7 | 0.16667 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
2003-07-24 | 24 | 7 | 0.20833 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
2003-07-24 | 24 | 7 | 0.25 | 23.3 | 73.94 | 35.6924 |  |  | 73.94
2003-07-24 | 24 | 7 | 0.29167 | 23.9 | 75.02 | 36.008 |  |  | 75.02
2003-07-24 | 24 | 7 | 0.33333 | 25 | 77 | 35.7372 |  |  | 77
2003-07-24 | 24 | 7 | 0.375 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
2003-07-24 | 24 | 7 | 0.41667 | 27.2 | 80.96 | 36.622 |  |  | 80.96
2003-07-24 | 24 | 7 | 0.45833 | 28.3 | 82.94 | 37.7364 |  |  | 82.94
2003-07-24 | 24 | 7 | 0.5 | 28.9 | 84.02 | 37.5205 |  |  | 84.02
2003-07-24 | 24 | 7 | 0.54167 | 28.9 | 84.02 | 38.0859 |  |  | 84.02
2003-07-24 | 24 | 7 | 0.58333 | 31.7 | 89.06 | 39.5423 |  |  | 89.06
2003-07-24 | 24 | 7 | 0.625 | 31.7 | 89.06 | 39.8755 |  |  | 89.06
2003-07-24 | 24 | 7 | 0.66667 | 30.6 | 87.08 | 39.4849 |  |  | 87.08
2003-07-24 | 24 | 7 | 0.70833 | 29.4 | 84.92 | 38.265 |  |  | 84.92
2003-07-24 | 24 | 7 | 0.75 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
2003-07-24 | 24 | 7 | 0.79167 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
2003-07-24 | 24 | 7 | 0.83333 | 26.1 | 78.98 | 36.9434 |  |  | 78.98
2003-07-24 | 24 | 7 | 0.875 | 26.1 | 78.98 | 36.9434 |  |  | 78.98
2003-07-24 | 24 | 7 | 0.91667 | 26.1 | 78.98 | 36.9434 |  |  |  | 78.98
2003-07-24 | 24 | 7 | 0.95833 | 26.7 | 80.06 | 37.6276 |  |  |  | 80.06
2003-07-24 | 24 | 7 | 1 | 26.1 | 78.98 | 35.7466 |  |  |  | 78.98
2003-07-25 | 25 | 7 | 0.041667 | 26.1 | 78.98 | 35.7466 |  |  |  | 78.98
2003-07-25 | 25 | 7 | 0.083333 | 26.1 | 78.98 | 36.9434 |  |  |  | 78.98
2003-07-25 | 25 | 7 | 0.125 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-25 | 25 | 7 | 0.16667 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-25 | 25 | 7 | 0.20833 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-25 | 25 | 7 | 0.25 | 25.6 | 78.08 | 37.3463 |  |  | 78.08
2003-07-25 | 25 | 7 | 0.29167 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
2003-07-25 | 25 | 7 | 0.33333 | 28.3 | 82.94 | 36.6457 |  |  | 82.94
2003-07-25 | 25 | 7 | 0.375 | 29.4 | 84.92 | 37.1017 |  |  | 84.92
2003-07-25 | 25 | 7 | 0.41667 | 31.1 | 87.98 | 37.3688 |  |  | 87.98
2003-07-25 | 25 | 7 | 0.45833 | 32.2 | 89.96 | 37.225 |  |  | 89.96
2003-07-25 | 25 | 7 | 0.5 | 32.8 | 91.04 | 37.3369 |  |  | 91.04
2003-07-25 | 25 | 7 | 0.54167 | 32.2 | 89.96 | 37.225 |  |  | 89.96
2003-07-25 | 25 | 7 | 0.58333 | 32.2 | 89.96 | 36.2057 |  |  | 89.96
2003-07-25 | 25 | 7 | 0.625 | 28.9 | 84.02 | 35.8297 |  |  | 84.02
2003-07-25 | 25 | 7 | 0.66667 | 31.1 | 87.98 | 34.5006 |  |  | 87.98
2003-07-25 | 25 | 7 | 0.70833 | 28.9 | 84.02 | 34.147 |  |  | 84.02
2003-07-25 | 25 | 7 | 0.75 | 26.7 | 80.06 | 35.8902 |  |  | 80.06
2003-07-25 | 25 | 7 | 0.79167 | 26.1 | 78.98 | 34.5538 |  |  | 78.98
2003-07-25 | 25 | 7 | 0.83333 | 26.1 | 78.98 | 32.8908 |  |  | 78.98
2003-07-25 | 25 | 7 | 0.875 | 25 | 77 | 33.9499 |  |  | 77
2003-07-25 | 25 | 7 | 0.91667 | 25 | 77 | 33.9499 |  |  |  | 77
2003-07-25 | 25 | 7 | 0.95833 | 25 | 77 | 33.9499 |  |  |  | 77
2003-07-25 | 25 | 7 | 1 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
2003-07-26 | 26 | 7 | 0.041667 | 23.9 | 75.02 | 33.4972 |  |  |  | 75.02
2003-07-26 | 26 | 7 | 0.083333 | 23.9 | 75.02 | 33.0805 |  |  |  | 75.02
2003-07-26 | 26 | 7 | 0.125 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
2003-07-26 | 26 | 7 | 0.16667 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
2003-07-26 | 26 | 7 | 0.20833 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
2003-07-26 | 26 | 7 | 0.25 | 23.9 | 75.02 | 34.7504 |  |  | 75.02
2003-07-26 | 26 | 7 | 0.29167 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
2003-07-26 | 26 | 7 | 0.33333 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
2003-07-26 | 26 | 7 | 0.375 | 26.7 | 80.06 | 35.8902 |  |  | 80.06
2003-07-26 | 26 | 7 | 0.41667 | 27.2 | 80.96 | 36.622 |  |  | 80.96
2003-07-26 | 26 | 7 | 0.45833 | 27.8 | 82.04 | 36.4601 |  |  | 82.04
2003-07-26 | 26 | 7 | 0.5 | 28.9 | 84.02 | 36.956 |  |  | 84.02
2003-07-26 | 26 | 7 | 0.54167 | 30.6 | 87.08 | 38.2353 |  |  | 87.08
2003-07-26 | 26 | 7 | 0.58333 | 30 | 86 | 37.9706 |  |  | 86
2003-07-26 | 26 | 7 | 0.625 | 29.4 | 84.92 | 36.5215 |  |  | 84.92
2003-07-26 | 26 | 7 | 0.66667 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
2003-07-26 | 26 | 7 | 0.70833 | 25 | 77 | 38.2097 |  |  | 77
2003-07-26 | 26 | 7 | 0.75 | 23.9 | 75.02 | 36.008 |  |  | 75.02
2003-07-26 | 26 | 7 | 0.79167 | 23.9 | 75.02 | 36.008 |  |  | 75.02
2003-07-26 | 26 | 7 | 0.83333 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
2003-07-26 | 26 | 7 | 0.875 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
2003-07-26 | 26 | 7 | 0.91667 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
2003-07-26 | 26 | 7 | 0.95833 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
2003-07-26 | 26 | 7 | 1 | 23.9 | 75.02 | 35.1691 |  |  |  | 75.02
2003-07-27 | 27 | 7 | 0.041667 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
2003-07-27 | 27 | 7 | 0.083333 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
2003-07-27 | 27 | 7 | 0.125 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
2003-07-27 | 27 | 7 | 0.16667 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
2003-07-27 | 27 | 7 | 0.20833 | 23.3 | 73.94 | 34.48 |  |  |  | 73.94
2003-07-27 | 27 | 7 | 0.25 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
2003-07-27 | 27 | 7 | 0.29167 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
2003-07-27 | 27 | 7 | 0.33333 | 25.6 | 78.08 | 33.867 |  |  | 78.08
2003-07-27 | 27 | 7 | 0.375 | 26.1 | 78.98 | 33.3652 |  |  | 78.98
2003-07-27 | 27 | 7 | 0.41667 | 26.1 | 78.98 | 32.8908 |  |  | 78.98
2003-07-27 | 27 | 7 | 0.45833 | 27.2 | 80.96 | 32.5588 |  |  | 80.96
2003-07-27 | 27 | 7 | 0.5 | 28.3 | 82.94 | 32.8552 |  |  | 82.94
2003-07-27 | 27 | 7 | 0.54167 | 28.3 | 82.94 | 33.3941 |  |  | 82.94
2003-07-27 | 27 | 7 | 0.58333 | 28.9 | 84.02 | 33.5879 |  |  | 84.02
2003-07-27 | 27 | 7 | 0.625 | 29.4 | 84.92 | 33.9225 |  |  | 84.92
2003-07-27 | 27 | 7 | 0.66667 | 28.9 | 84.02 | 32.7509 |  |  | 84.02
2003-07-27 | 27 | 7 | 0.70833 | 28.3 | 82.94 | 32.8552 |  |  | 82.94
2003-07-27 | 27 | 7 | 0.75 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
2003-07-27 | 27 | 7 | 0.79167 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
2003-07-27 | 27 | 7 | 0.83333 | 25 | 77 | 35.2895 |  |  | 77
2003-07-27 | 27 | 7 | 0.875 | 25 | 77 | 35.7372 |  |  | 77
2003-07-27 | 27 | 7 | 0.91667 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
2003-07-27 | 27 | 7 | 0.95833 | 22.2 | 71.96 | 34.3944 |  |  |  | 71.96
2003-07-27 | 27 | 7 | 1 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
2003-07-28 | 28 | 7 | 0.041667 | 25 | 77 | 39.1131 |  |  |  | 77
2003-07-28 | 28 | 7 | 0.083333 | 24.4 | 75.92 | 38.0974 |  |  |  | 75.92
2003-07-28 | 28 | 7 | 0.125 | 23.9 | 75.02 | 37.6921 |  |  |  | 75.02
2003-07-28 | 28 | 7 | 0.16667 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
2003-07-28 | 28 | 7 | 0.20833 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
2003-07-28 | 28 | 7 | 0.25 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
2003-07-28 | 28 | 7 | 0.29167 | 24.4 | 75.92 | 36.7941 |  |  | 75.92
2003-07-28 | 28 | 7 | 0.33333 | 25.6 | 78.08 | 36.6477 |  |  | 78.08
2003-07-28 | 28 | 7 | 0.375 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
2003-07-28 | 28 | 7 | 0.41667 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
2003-07-28 | 28 | 7 | 0.45833 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
2003-07-28 | 28 | 7 | 0.5 | 28.9 | 84.02 | 38.0859 |  |  | 84.02
2003-07-28 | 28 | 7 | 0.54167 | 25.6 | 78.08 | 38.0464 |  |  | 78.08
2003-07-28 | 28 | 7 | 0.58333 | 26.7 | 80.06 | 39.1237 |  |  | 80.06
2003-07-28 | 28 | 7 | 0.625 | 27.8 | 82.04 | 38.8474 |  |  | 82.04
2003-07-28 | 28 | 7 | 0.66667 | 28.3 | 82.94 | 37.1906 |  |  | 82.94
2003-07-28 | 28 | 7 | 0.70833 | 27.8 | 82.04 | 36.9892 |  |  | 82.04
2003-07-28 | 28 | 7 | 0.75 | 27.2 | 80.96 | 36.1115 |  |  | 80.96
2003-07-28 | 28 | 7 | 0.79167 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
2003-07-28 | 28 | 7 | 0.83333 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
2003-07-28 | 28 | 7 | 0.875 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
2003-07-28 | 28 | 7 | 0.91667 | 25 | 77 | 33.9499 |  |  |  | 77
2003-07-28 | 28 | 7 | 0.95833 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
2003-07-28 | 28 | 7 | 1 | 23.9 | 75.02 | 33.0805 |  |  |  | 75.02
2003-07-29 | 29 | 7 | 0.041667 | 22.8 | 73.04 | 31.9938 |  |  |  | 73.04
2003-07-29 | 29 | 7 | 0.083333 | 22.8 | 73.04 | 31.9938 |  |  |  | 73.04
2003-07-29 | 29 | 7 | 0.125 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
2003-07-29 | 29 | 7 | 0.16667 | 22.2 | 71.96 | 32.3241 |  |  |  | 71.96
2003-07-29 | 29 | 7 | 0.20833 | 21.7 | 71.06 | 31.459 |  |  |  | 71.06
2003-07-29 | 29 | 7 | 0.25 | 21.7 | 71.06 | 31.459 |  |  | 71.06
2003-07-29 | 29 | 7 | 0.29167 | 22.2 | 71.96 | 31.7616 |  |  | 71.96
2003-07-29 | 29 | 7 | 0.33333 | 23.9 | 75.02 | 32.4563 |  |  | 75.02
2003-07-29 | 29 | 7 | 0.375 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
2003-07-29 | 29 | 7 | 0.41667 | 24.4 | 75.92 | 32.2704 |  |  | 75.92
2003-07-29 | 29 | 7 | 0.45833 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
2003-07-29 | 29 | 7 | 0.5 | 26.1 | 78.98 | 33.3652 |  |  | 78.98
2003-07-29 | 29 | 7 | 0.54167 | 26.1 | 78.98 | 33.3652 |  |  | 78.98
2003-07-29 | 29 | 7 | 0.58333 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
2003-07-29 | 29 | 7 | 0.625 | 28.3 | 82.94 | 33.934 |  |  | 82.94
2003-07-29 | 29 | 7 | 0.66667 | 30 | 86 | 35.2704 |  |  | 86
2003-07-29 | 29 | 7 | 0.70833 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
2003-07-29 | 29 | 7 | 0.75 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
2003-07-29 | 29 | 7 | 0.79167 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
2003-07-29 | 29 | 7 | 0.83333 | 25 | 77 | 35.7372 |  |  | 77
2003-07-29 | 29 | 7 | 0.875 | 25 | 77 | 36.8589 |  |  | 77
2003-07-29 | 29 | 7 | 0.91667 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-29 | 29 | 7 | 0.95833 | 24.4 | 75.92 | 36.7941 |  |  |  | 75.92
2003-07-29 | 29 | 7 | 1 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
2003-07-30 | 30 | 7 | 0.041667 | 24.4 | 75.92 | 36.7941 |  |  |  | 75.92
2003-07-30 | 30 | 7 | 0.083333 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
2003-07-30 | 30 | 7 | 0.125 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
2003-07-30 | 30 | 7 | 0.16667 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
2003-07-30 | 30 | 7 | 0.20833 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
2003-07-30 | 30 | 7 | 0.25 | 23.9 | 75.02 | 37.2703 |  |  | 75.02
2003-07-30 | 30 | 7 | 0.29167 | 24.4 | 75.92 | 36.1442 |  |  | 75.92
2003-07-30 | 30 | 7 | 0.33333 | 27.2 | 80.96 | 37.9015 |  |  | 80.96
2003-07-30 | 30 | 7 | 0.375 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
2003-07-30 | 30 | 7 | 0.41667 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
2003-07-30 | 30 | 7 | 0.45833 | 30 | 86 | 38.5735 |  |  | 86
2003-07-30 | 30 | 7 | 0.5 | 31.7 | 89.06 | 39.8755 |  |  | 89.06
2003-07-30 | 30 | 7 | 0.54167 | 31.7 | 89.06 | 39.8755 |  |  | 89.06
2003-07-30 | 30 | 7 | 0.58333 | 31.1 | 87.98 | 38.9724 |  |  | 87.98
2003-07-30 | 30 | 7 | 0.625 | 30.6 | 87.08 | 38.8595 |  |  | 87.08
2003-07-30 | 30 | 7 | 0.66667 | 30 | 86 | 39.1775 |  |  | 86
2003-07-30 | 30 | 7 | 0.70833 | 29.4 | 84.92 | 36.5215 |  |  | 84.92
2003-07-30 | 30 | 7 | 0.75 | 28.9 | 84.02 | 36.956 |  |  | 84.02
2003-07-30 | 30 | 7 | 0.79167 | 27.2 | 80.96 | 36.1115 |  |  | 80.96
2003-07-30 | 30 | 7 | 0.83333 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
2003-07-30 | 30 | 7 | 0.875 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
2003-07-30 | 30 | 7 | 0.91667 | 25.6 | 78.08 | 35.4864 |  |  |  | 78.08
2003-07-30 | 30 | 7 | 0.95833 | 25.6 | 78.08 | 35.9504 |  |  |  | 78.08
2003-07-30 | 30 | 7 | 1 | 26.1 | 78.98 | 36.9434 |  |  |  | 78.98
2003-07-31 | 31 | 7 | 0.041667 | 25.6 | 78.08 | 36.6477 |  |  |  | 78.08
2003-07-31 | 31 | 7 | 0.083333 | 25.6 | 78.08 | 37.3463 |  |  |  | 78.08
2003-07-31 | 31 | 7 | 0.125 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-31 | 31 | 7 | 0.16667 | 25 | 77 | 36.8589 |  |  |  | 77
2003-07-31 | 31 | 7 | 0.20833 | 25.6 | 78.08 | 33.867 |  |  |  | 78.08
2003-07-31 | 31 | 7 | 0.25 | 25.6 | 78.08 | 33.867 |  |  | 78.08
2003-07-31 | 31 | 7 | 0.29167 | 25 | 77 | 33.5046 |  |  | 77
2003-07-31 | 31 | 7 | 0.33333 | 25 | 77 | 33.9499 |  |  | 77
2003-07-31 | 31 | 7 | 0.375 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
2003-07-31 | 31 | 7 | 0.41667 | 26.7 | 80.06 | 33.669 |  |  | 80.06
2003-07-31 | 31 | 7 | 0.45833 | 27.2 | 80.96 | 34.5845 |  |  | 80.96
2003-07-31 | 31 | 7 | 0.5 | 27.8 | 82.04 | 35.1409 |  |  | 82.04
2003-07-31 | 31 | 7 | 0.54167 | 28.9 | 84.02 | 35.8297 |  |  | 84.02
2003-07-31 | 31 | 7 | 0.58333 | 28.3 | 82.94 | 36.1017 |  |  | 82.94
2003-07-31 | 31 | 7 | 0.625 | 28.3 | 82.94 | 34.4746 |  |  | 82.94
2003-07-31 | 31 | 7 | 0.66667 | 28.9 | 84.02 | 34.707 |  |  | 84.02
2003-07-31 | 31 | 7 | 0.70833 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
2003-07-31 | 31 | 7 | 0.75 | 27.8 | 82.04 | 34.6146 |  |  | 82.04
2003-07-31 | 31 | 7 | 0.79167 | 27.2 | 80.96 | 33.8235 |  |  | 80.96
2003-07-31 | 31 | 7 | 0.83333 | 26.7 | 80.06 | 35.3954 |  |  | 80.06
2003-07-31 | 31 | 7 | 0.875 | 26.7 | 80.06 | 35.3954 |  |  | 80.06
2003-07-31 | 31 | 7 | 0.91667 | 25.7 | 78.26 | 33.3073 |  |  |  | 78.26
2003-07-31 | 31 | 7 | 0.95833 | 24.6 | 76.28 | 35.1422 |  |  |  | 76.28
2003-07-31 | 31 | 7 | 1 | 23.6 | 74.48 | 33.695 |  |  |  | 74.48
1987-08-01 | 1 | 8 | 0.041667 | 22.5 | 72.5 | 28.7463 |  |  |  | 72.5
1987-08-01 | 1 | 8 | 0.083333 | 21.5 | 70.7 | 27.9796 |  |  |  | 70.7
1987-08-01 | 1 | 8 | 0.125 | 20.4 | 68.72 | 26.7651 |  |  |  | 68.72
1987-08-01 | 1 | 8 | 0.16667 | 19.4 | 66.92 | 25.6998 |  |  |  | 66.92
1987-08-01 | 1 | 8 | 0.20833 | 18.9 | 66.02 | 25.1804 |  |  |  | 66.02
1987-08-01 | 1 | 8 | 0.25 | 19.4 | 66.92 | 25.3896 |  |  | 66.92
1987-08-01 | 1 | 8 | 0.29167 | 20 | 68 | 25.3681 |  |  | 68
1987-08-01 | 1 | 8 | 0.33333 | 21.1 | 69.98 | 26.1504 |  |  | 69.98
1987-08-01 | 1 | 8 | 0.375 | 22.2 | 71.96 | 26.5553 |  |  | 71.96
1987-08-01 | 1 | 8 | 0.41667 | 23.9 | 75.02 | 27.0935 |  |  | 75.02
1987-08-01 | 1 | 8 | 0.45833 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1987-08-01 | 1 | 8 | 0.5 | 25.6 | 78.08 | 27.0111 |  |  | 78.08
1987-08-01 | 1 | 8 | 0.54167 | 25.6 | 78.08 | 27.6907 |  |  | 78.08
1987-08-01 | 1 | 8 | 0.58333 | 26.1 | 78.98 | 27.949 |  |  | 78.98
1987-08-01 | 1 | 8 | 0.625 | 26.1 | 78.98 | 27.7154 |  |  | 78.98
1987-08-01 | 1 | 8 | 0.66667 | 26.7 | 80.06 | 28.2984 |  |  | 80.06
1987-08-01 | 1 | 8 | 0.70833 | 26.7 | 80.06 | 28.2984 |  |  | 80.06
1987-08-01 | 1 | 8 | 0.75 | 26.1 | 78.98 | 27.949 |  |  | 78.98
1987-08-01 | 1 | 8 | 0.79167 | 24.4 | 75.92 | 28.6509 |  |  | 75.92
1987-08-01 | 1 | 8 | 0.83333 | 23.3 | 73.94 | 27.8863 |  |  | 73.94
1987-08-01 | 1 | 8 | 0.875 | 23.3 | 73.94 | 28.0843 |  |  | 73.94
1987-08-01 | 1 | 8 | 0.91667 | 22.8 | 73.04 | 28.3204 |  |  |  | 73.04
1987-08-01 | 1 | 8 | 0.95833 | 22.8 | 73.04 | 28.3204 |  |  |  | 73.04
1987-08-01 | 1 | 8 | 1 | 22.2 | 71.96 | 28.0348 |  |  |  | 71.96
1987-08-02 | 2 | 8 | 0.041667 | 22.2 | 71.96 | 28.0348 |  |  |  | 71.96
1987-08-02 | 2 | 8 | 0.083333 | 21.7 | 71.06 | 28.7456 |  |  |  | 71.06
1987-08-02 | 2 | 8 | 0.125 | 21.7 | 71.06 | 28.2055 |  |  |  | 71.06
1987-08-02 | 2 | 8 | 0.16667 | 21.1 | 69.98 | 27.5326 |  |  |  | 69.98
1987-08-02 | 2 | 8 | 0.20833 | 21.1 | 69.98 | 27.5326 |  |  |  | 69.98
1987-08-02 | 2 | 8 | 0.25 | 20.6 | 69.08 | 26.9825 |  |  | 69.08
1987-08-02 | 2 | 8 | 0.29167 | 22.2 | 71.96 | 27.2943 |  |  | 71.96
1987-08-02 | 2 | 8 | 0.33333 | 23.3 | 73.94 | 27.8863 |  |  | 73.94
1987-08-02 | 2 | 8 | 0.375 | 24.4 | 75.92 | 28.2276 |  |  | 75.92
1987-08-02 | 2 | 8 | 0.41667 | 25 | 77 | 28.204 |  |  | 77
1987-08-02 | 2 | 8 | 0.45833 | 26.7 | 80.06 | 28.5407 |  |  | 80.06
1987-08-02 | 2 | 8 | 0.5 | 27.2 | 80.96 | 28.7923 |  |  | 80.96
1987-08-02 | 2 | 8 | 0.54167 | 28.3 | 82.94 | 28.5731 |  |  | 82.94
1987-08-02 | 2 | 8 | 0.58333 | 27.8 | 82.04 | 28.3603 |  |  | 82.04
1987-08-02 | 2 | 8 | 0.625 | 28.9 | 84.02 | 28.8715 |  |  | 84.02
1987-08-02 | 2 | 8 | 0.66667 | 27.8 | 82.04 | 28.6186 |  |  | 82.04
1987-08-02 | 2 | 8 | 0.70833 | 27.2 | 80.96 | 28.5426 |  |  | 80.96
1987-08-02 | 2 | 8 | 0.75 | 26.1 | 78.98 | 27.949 |  |  | 78.98
1987-08-02 | 2 | 8 | 0.79167 | 25.6 | 78.08 | 29.2814 |  |  | 78.08
1987-08-02 | 2 | 8 | 0.83333 | 23.9 | 75.02 | 29.1463 |  |  | 75.02
1987-08-02 | 2 | 8 | 0.875 | 24.4 | 75.92 | 28.6509 |  |  | 75.92
1987-08-02 | 2 | 8 | 0.91667 | 23.3 | 73.94 | 28.4806 |  |  |  | 73.94
1987-08-02 | 2 | 8 | 0.95833 | 22.8 | 73.04 | 28.7052 |  |  |  | 73.04
1987-08-02 | 2 | 8 | 1 | 22.2 | 71.96 | 28.9628 |  |  |  | 71.96
1987-08-03 | 3 | 8 | 0.041667 | 21.7 | 71.06 | 28.7456 |  |  |  | 71.06
1987-08-03 | 3 | 8 | 0.083333 | 21.1 | 69.98 | 28.9205 |  |  |  | 69.98
1987-08-03 | 3 | 8 | 0.125 | 21.1 | 69.98 | 29.2683 |  |  |  | 69.98
1987-08-03 | 3 | 8 | 0.16667 | 20.6 | 69.08 | 29.0003 |  |  |  | 69.08
1987-08-03 | 3 | 8 | 0.20833 | 20.6 | 69.08 | 29.0003 |  |  |  | 69.08
1987-08-03 | 3 | 8 | 0.25 | 21.7 | 71.06 | 29.1062 |  |  | 71.06
1987-08-03 | 3 | 8 | 0.29167 | 22.2 | 71.96 | 29.7069 |  |  | 71.96
1987-08-03 | 3 | 8 | 0.33333 | 23.3 | 73.94 | 29.8712 |  |  | 73.94
1987-08-03 | 3 | 8 | 0.375 | 23.9 | 75.02 | 30.5905 |  |  | 75.02
1987-08-03 | 3 | 8 | 0.41667 | 25.6 | 78.08 | 31.3374 |  |  | 78.08
1987-08-03 | 3 | 8 | 0.45833 | 26.7 | 80.06 | 31.4619 |  |  | 80.06
1987-08-03 | 3 | 8 | 0.5 | 28.3 | 82.94 | 30.7075 |  |  | 82.94
1987-08-03 | 3 | 8 | 0.54167 | 28.9 | 84.02 | 31.3605 |  |  | 84.02
1987-08-03 | 3 | 8 | 0.58333 | 29.4 | 84.92 | 31.6284 |  |  | 84.92
1987-08-03 | 3 | 8 | 0.625 | 29.4 | 84.92 | 31.6284 |  |  | 84.92
1987-08-03 | 3 | 8 | 0.66667 | 28.9 | 84.02 | 31.3605 |  |  | 84.02
1987-08-03 | 3 | 8 | 0.70833 | 28.3 | 82.94 | 33.3941 |  |  | 82.94
1987-08-03 | 3 | 8 | 0.75 | 26.7 | 80.06 | 33.669 |  |  | 80.06
1987-08-03 | 3 | 8 | 0.79167 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
1987-08-03 | 3 | 8 | 0.83333 | 25 | 77 | 32.3936 |  |  | 77
1987-08-03 | 3 | 8 | 0.875 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
1987-08-03 | 3 | 8 | 0.91667 | 24.4 | 75.92 | 32.6987 |  |  |  | 75.92
1987-08-03 | 3 | 8 | 0.95833 | 24.4 | 75.92 | 30.7754 |  |  |  | 75.92
1987-08-03 | 3 | 8 | 1 | 23.9 | 75.02 | 31.4185 |  |  |  | 75.02
1987-08-04 | 4 | 8 | 0.041667 | 23.3 | 73.94 | 31.2674 |  |  |  | 73.94
1987-08-04 | 4 | 8 | 0.083333 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1987-08-04 | 4 | 8 | 0.125 | 23.3 | 73.94 | 30.2695 |  |  |  | 73.94
1987-08-04 | 4 | 8 | 0.16667 | 23.3 | 73.94 | 30.2695 |  |  |  | 73.94
1987-08-04 | 4 | 8 | 0.20833 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1987-08-04 | 4 | 8 | 0.25 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1987-08-04 | 4 | 8 | 0.29167 | 23.3 | 73.94 | 31.2674 |  |  | 73.94
1987-08-04 | 4 | 8 | 0.33333 | 25 | 77 | 31.9502 |  |  | 77
1987-08-04 | 4 | 8 | 0.375 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
1987-08-04 | 4 | 8 | 0.41667 | 25 | 77 | 33.5046 |  |  | 77
1987-08-04 | 4 | 8 | 0.45833 | 26.1 | 78.98 | 33.3652 |  |  | 78.98
1987-08-04 | 4 | 8 | 0.5 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-04 | 4 | 8 | 0.54167 | 28.3 | 82.94 | 33.934 |  |  | 82.94
1987-08-04 | 4 | 8 | 0.58333 | 28.9 | 84.02 | 33.3087 |  |  | 84.02
1987-08-04 | 4 | 8 | 0.625 | 29.4 | 84.92 | 33.3475 |  |  | 84.92
1987-08-04 | 4 | 8 | 0.66667 | 29.4 | 84.92 | 33.9225 |  |  | 84.92
1987-08-04 | 4 | 8 | 0.70833 | 28.3 | 82.94 | 33.3941 |  |  | 82.94
1987-08-04 | 4 | 8 | 0.75 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1987-08-04 | 4 | 8 | 0.79167 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
1987-08-04 | 4 | 8 | 0.83333 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
1987-08-04 | 4 | 8 | 0.875 | 25 | 77 | 32.3936 |  |  | 77
1987-08-04 | 4 | 8 | 0.91667 | 25 | 77 | 31.9502 |  |  |  | 77
1987-08-04 | 4 | 8 | 0.95833 | 24.4 | 75.92 | 32.2704 |  |  |  | 75.92
1987-08-04 | 4 | 8 | 1 | 24.4 | 75.92 | 31.2019 |  |  |  | 75.92
1987-08-05 | 5 | 8 | 0.041667 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1987-08-05 | 5 | 8 | 0.083333 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
1987-08-05 | 5 | 8 | 0.125 | 22.8 | 73.04 | 32.967 |  |  |  | 73.04
1987-08-05 | 5 | 8 | 0.16667 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
1987-08-05 | 5 | 8 | 0.20833 | 21.7 | 71.06 | 33.6452 |  |  |  | 71.06
1987-08-05 | 5 | 8 | 0.25 | 22.2 | 71.96 | 34.017 |  |  | 71.96
1987-08-05 | 5 | 8 | 0.29167 | 22.8 | 73.04 | 34.7256 |  |  | 73.04
1987-08-05 | 5 | 8 | 0.33333 | 23.9 | 75.02 | 34.1232 |  |  | 75.02
1987-08-05 | 5 | 8 | 0.375 | 25.6 | 78.08 | 32.2552 |  |  | 78.08
1987-08-05 | 5 | 8 | 0.41667 | 26.7 | 80.06 | 32.6863 |  |  | 80.06
1987-08-05 | 5 | 8 | 0.45833 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-05 | 5 | 8 | 0.5 | 28.3 | 82.94 | 33.934 |  |  | 82.94
1987-08-05 | 5 | 8 | 0.54167 | 28.9 | 84.02 | 31.3605 |  |  | 84.02
1987-08-05 | 5 | 8 | 0.58333 | 28.9 | 84.02 | 31.3605 |  |  | 84.02
1987-08-05 | 5 | 8 | 0.625 | 29.4 | 84.92 | 32.2005 |  |  | 84.92
1987-08-05 | 5 | 8 | 0.66667 | 28.9 | 84.02 | 32.1941 |  |  | 84.02
1987-08-05 | 5 | 8 | 0.70833 | 28.3 | 82.94 | 31.5113 |  |  | 82.94
1987-08-05 | 5 | 8 | 0.75 | 27.2 | 80.96 | 32.0543 |  |  | 80.96
1987-08-05 | 5 | 8 | 0.79167 | 25.6 | 78.08 | 30.8795 |  |  | 78.08
1987-08-05 | 5 | 8 | 0.83333 | 25 | 77 | 29.3016 |  |  | 77
1987-08-05 | 5 | 8 | 0.875 | 25 | 77 | 29.7417 |  |  | 77
1987-08-05 | 5 | 8 | 0.91667 | 24.4 | 75.92 | 30.3495 |  |  |  | 75.92
1987-08-05 | 5 | 8 | 0.95833 | 24.4 | 75.92 | 29.9241 |  |  |  | 75.92
1987-08-05 | 5 | 8 | 1 | 24.4 | 75.92 | 29.4992 |  |  |  | 75.92
1987-08-06 | 6 | 8 | 0.041667 | 24.4 | 75.92 | 28.6509 |  |  |  | 75.92
1987-08-06 | 6 | 8 | 0.083333 | 23.9 | 75.02 | 28.3237 |  |  |  | 75.02
1987-08-06 | 6 | 8 | 0.125 | 23.9 | 75.02 | 30.1773 |  |  |  | 75.02
1987-08-06 | 6 | 8 | 0.16667 | 23.3 | 73.94 | 29.8712 |  |  |  | 73.94
1987-08-06 | 6 | 8 | 0.20833 | 23.3 | 73.94 | 31.2674 |  |  |  | 73.94
1987-08-06 | 6 | 8 | 0.25 | 22.8 | 73.04 | 31.9938 |  |  | 73.04
1987-08-06 | 6 | 8 | 0.29167 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1987-08-06 | 6 | 8 | 0.33333 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1987-08-06 | 6 | 8 | 0.375 | 26.1 | 78.98 | 29.8233 |  |  | 78.98
1987-08-06 | 6 | 8 | 0.41667 | 27.8 | 82.04 | 30.1728 |  |  | 82.04
1987-08-06 | 6 | 8 | 0.45833 | 28.3 | 82.94 | 31.2432 |  |  | 82.94
1987-08-06 | 6 | 8 | 0.5 | 30.6 | 87.08 | 33.8964 |  |  | 87.08
1987-08-06 | 6 | 8 | 0.54167 | 30 | 86 | 32.8876 |  |  | 86
1987-08-06 | 6 | 8 | 0.58333 | 30 | 86 | 33.1846 |  |  | 86
1987-08-06 | 6 | 8 | 0.625 | 28.9 | 84.02 | 31.083 |  |  | 84.02
1987-08-06 | 6 | 8 | 0.66667 | 27.8 | 82.04 | 30.9526 |  |  | 82.04
1987-08-06 | 6 | 8 | 0.70833 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1987-08-06 | 6 | 8 | 0.75 | 26.7 | 80.06 | 32.6863 |  |  | 80.06
1987-08-06 | 6 | 8 | 0.79167 | 25.6 | 78.08 | 31.3374 |  |  | 78.08
1987-08-06 | 6 | 8 | 0.83333 | 25 | 77 | 31.0651 |  |  | 77
1987-08-06 | 6 | 8 | 0.875 | 25 | 77 | 31.9502 |  |  | 77
1987-08-06 | 6 | 8 | 0.91667 | 24.4 | 75.92 | 31.6289 |  |  |  | 75.92
1987-08-06 | 6 | 8 | 0.95833 | 24.4 | 75.92 | 31.6289 |  |  |  | 75.92
1987-08-06 | 6 | 8 | 1 | 23.9 | 75.02 | 32.4563 |  |  |  | 75.02
1987-08-07 | 7 | 8 | 0.041667 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1987-08-07 | 7 | 8 | 0.083333 | 22.8 | 73.04 | 32.967 |  |  |  | 73.04
1987-08-07 | 7 | 8 | 0.125 | 22.2 | 71.96 | 32.6996 |  |  |  | 71.96
1987-08-07 | 7 | 8 | 0.16667 | 21.7 | 71.06 | 31.459 |  |  |  | 71.06
1987-08-07 | 7 | 8 | 0.20833 | 21.1 | 69.98 | 31.7129 |  |  |  | 69.98
1987-08-07 | 7 | 8 | 0.25 | 21.7 | 71.06 | 32.0043 |  |  | 71.06
1987-08-07 | 7 | 8 | 0.29167 | 22.2 | 71.96 | 32.3241 |  |  | 71.96
1987-08-07 | 7 | 8 | 0.33333 | 23.3 | 73.94 | 32.6693 |  |  | 73.94
1987-08-07 | 7 | 8 | 0.375 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
1987-08-07 | 7 | 8 | 0.41667 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
1987-08-07 | 7 | 8 | 0.45833 | 27.2 | 80.96 | 33.3171 |  |  | 80.96
1987-08-07 | 7 | 8 | 0.5 | 28.3 | 82.94 | 31.2432 |  |  | 82.94
1987-08-07 | 7 | 8 | 0.54167 | 28.3 | 82.94 | 30.7075 |  |  | 82.94
1987-08-07 | 7 | 8 | 0.58333 | 28.9 | 84.02 | 30.5288 |  |  | 84.02
1987-08-07 | 7 | 8 | 0.625 | 28.9 | 84.02 | 30.2521 |  |  | 84.02
1987-08-07 | 7 | 8 | 0.66667 | 27.8 | 82.04 | 29.9133 |  |  | 82.04
1987-08-07 | 7 | 8 | 0.70833 | 27.2 | 80.96 | 29.7927 |  |  | 80.96
1987-08-07 | 7 | 8 | 0.75 | 26.1 | 78.98 | 30.5288 |  |  | 78.98
1987-08-07 | 7 | 8 | 0.79167 | 25.6 | 78.08 | 31.3374 |  |  | 78.08
1987-08-07 | 7 | 8 | 0.83333 | 24.4 | 75.92 | 32.2704 |  |  | 75.92
1987-08-07 | 7 | 8 | 0.875 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
1987-08-07 | 7 | 8 | 0.91667 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1987-08-07 | 7 | 8 | 0.95833 | 22.8 | 73.04 | 31.9938 |  |  |  | 73.04
1987-08-07 | 7 | 8 | 1 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
1987-08-08 | 8 | 8 | 0.041667 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
1987-08-08 | 8 | 8 | 0.083333 | 21.7 | 71.06 | 32.5504 |  |  |  | 71.06
1987-08-08 | 8 | 8 | 0.125 | 21.1 | 69.98 | 32.239 |  |  |  | 69.98
1987-08-08 | 8 | 8 | 0.16667 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
1987-08-08 | 8 | 8 | 0.20833 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1987-08-08 | 8 | 8 | 0.25 | 20.6 | 69.08 | 32.0493 |  |  | 69.08
1987-08-08 | 8 | 8 | 0.29167 | 21.7 | 71.06 | 33.0973 |  |  | 71.06
1987-08-08 | 8 | 8 | 0.33333 | 22.8 | 73.04 | 33.5522 |  |  | 73.04
1987-08-08 | 8 | 8 | 0.375 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1987-08-08 | 8 | 8 | 0.41667 | 25 | 77 | 33.5046 |  |  | 77
1987-08-08 | 8 | 8 | 0.45833 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
1987-08-08 | 8 | 8 | 0.5 | 27.2 | 80.96 | 33.8235 |  |  | 80.96
1987-08-08 | 8 | 8 | 0.54167 | 27.2 | 80.96 | 33.8235 |  |  | 80.96
1987-08-08 | 8 | 8 | 0.58333 | 28.3 | 82.94 | 35.0162 |  |  | 82.94
1987-08-08 | 8 | 8 | 0.625 | 28.3 | 82.94 | 35.0162 |  |  | 82.94
1987-08-08 | 8 | 8 | 0.66667 | 28.3 | 82.94 | 35.5585 |  |  | 82.94
1987-08-08 | 8 | 8 | 0.70833 | 27.2 | 80.96 | 35.6018 |  |  | 80.96
1987-08-08 | 8 | 8 | 0.75 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
1987-08-08 | 8 | 8 | 0.79167 | 25.6 | 78.08 | 36.6477 |  |  | 78.08
1987-08-08 | 8 | 8 | 0.83333 | 25.6 | 78.08 | 35.9504 |  |  | 78.08
1987-08-08 | 8 | 8 | 0.875 | 25 | 77 | 35.7372 |  |  | 77
1987-08-08 | 8 | 8 | 0.91667 | 23.9 | 75.02 | 35.1691 |  |  |  | 75.02
1987-08-08 | 8 | 8 | 0.95833 | 23.9 | 75.02 | 35.1691 |  |  |  | 75.02
1987-08-08 | 8 | 8 | 1 | 23.9 | 75.02 | 36.008 |  |  |  | 75.02
1987-08-09 | 9 | 8 | 0.041667 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1987-08-09 | 9 | 8 | 0.083333 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1987-08-09 | 9 | 8 | 0.125 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
1987-08-09 | 9 | 8 | 0.16667 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1987-08-09 | 9 | 8 | 0.20833 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1987-08-09 | 9 | 8 | 0.25 | 22.8 | 73.04 | 35.5101 |  |  | 73.04
1987-08-09 | 9 | 8 | 0.29167 | 23.9 | 75.02 | 35.1691 |  |  | 75.02
1987-08-09 | 9 | 8 | 0.33333 | 25 | 77 | 33.9499 |  |  | 77
1987-08-09 | 9 | 8 | 0.375 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
1987-08-09 | 9 | 8 | 0.41667 | 27.2 | 80.96 | 34.8385 |  |  | 80.96
1987-08-09 | 9 | 8 | 0.45833 | 28.3 | 82.94 | 35.0162 |  |  | 82.94
1987-08-09 | 9 | 8 | 0.5 | 28.9 | 84.02 | 34.147 |  |  | 84.02
1987-08-09 | 9 | 8 | 0.54167 | 28.3 | 82.94 | 35.5585 |  |  | 82.94
1987-08-09 | 9 | 8 | 0.58333 | 28.9 | 84.02 | 35.2679 |  |  | 84.02
1987-08-09 | 9 | 8 | 0.625 | 29.4 | 84.92 | 35.364 |  |  | 84.92
1987-08-09 | 9 | 8 | 0.66667 | 27.8 | 82.04 | 35.1409 |  |  | 82.04
1987-08-09 | 9 | 8 | 0.70833 | 27.8 | 82.04 | 35.9318 |  |  | 82.04
1987-08-09 | 9 | 8 | 0.75 | 26.7 | 80.06 | 35.8902 |  |  | 80.06
1987-08-09 | 9 | 8 | 0.79167 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
1987-08-09 | 9 | 8 | 0.83333 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
1987-08-09 | 9 | 8 | 0.875 | 25 | 77 | 35.7372 |  |  | 77
1987-08-09 | 9 | 8 | 0.91667 | 24.4 | 75.92 | 35.4956 |  |  |  | 75.92
1987-08-09 | 9 | 8 | 0.95833 | 24.4 | 75.92 | 36.1442 |  |  |  | 75.92
1987-08-09 | 9 | 8 | 1 | 24.4 | 75.92 | 36.1442 |  |  |  | 75.92
1987-08-10 | 10 | 8 | 0.041667 | 24.4 | 75.92 | 36.1442 |  |  |  | 75.92
1987-08-10 | 10 | 8 | 0.083333 | 24.4 | 75.92 | 35.4956 |  |  |  | 75.92
1987-08-10 | 10 | 8 | 0.125 | 24.4 | 75.92 | 36.1442 |  |  |  | 75.92
1987-08-10 | 10 | 8 | 0.16667 | 23.9 | 75.02 | 36.008 |  |  |  | 75.02
1987-08-10 | 10 | 8 | 0.20833 | 24 | 75.2 | 35.1089 |  |  |  | 75.2
1987-08-10 | 10 | 8 | 0.25 | 23.9 | 75.02 | 34.7504 |  |  | 75.02
1987-08-10 | 10 | 8 | 0.29167 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
1987-08-10 | 10 | 8 | 0.33333 | 25 | 77 | 35.7372 |  |  | 77
1987-08-10 | 10 | 8 | 0.375 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
1987-08-10 | 10 | 8 | 0.41667 | 27.2 | 80.96 | 36.622 |  |  | 80.96
1987-08-10 | 10 | 8 | 0.45833 | 28.3 | 82.94 | 36.1017 |  |  | 82.94
1987-08-10 | 10 | 8 | 0.5 | 28.3 | 82.94 | 37.7364 |  |  | 82.94
1987-08-10 | 10 | 8 | 0.54167 | 29.4 | 84.92 | 38.265 |  |  | 84.92
1987-08-10 | 10 | 8 | 0.58333 | 29.4 | 84.92 | 38.265 |  |  | 84.92
1987-08-10 | 10 | 8 | 0.625 | 28.3 | 82.94 | 38.5566 |  |  | 82.94
1987-08-10 | 10 | 8 | 0.66667 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
1987-08-10 | 10 | 8 | 0.70833 | 27.2 | 80.96 | 37.9015 |  |  | 80.96
1987-08-10 | 10 | 8 | 0.75 | 26.7 | 80.06 | 37.6276 |  |  | 80.06
1987-08-10 | 10 | 8 | 0.79167 | 26.1 | 78.98 | 37.4233 |  |  | 78.98
1987-08-10 | 10 | 8 | 0.83333 | 26.1 | 78.98 | 38.1444 |  |  | 78.98
1987-08-10 | 10 | 8 | 0.875 | 26.1 | 78.98 | 37.4233 |  |  | 78.98
1987-08-10 | 10 | 8 | 0.91667 | 26.1 | 78.98 | 36.9434 |  |  |  | 78.98
1987-08-10 | 10 | 8 | 0.95833 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1987-08-10 | 10 | 8 | 1 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1987-08-11 | 11 | 8 | 0.041667 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
1987-08-11 | 11 | 8 | 0.083333 | 24.4 | 75.92 | 36.7941 |  |  |  | 75.92
1987-08-11 | 11 | 8 | 0.125 | 23.3 | 73.94 | 36.9091 |  |  |  | 73.94
1987-08-11 | 11 | 8 | 0.16667 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
1987-08-11 | 11 | 8 | 0.20833 | 23.9 | 75.02 | 36.008 |  |  |  | 75.02
1987-08-11 | 11 | 8 | 0.25 | 23.9 | 75.02 | 36.008 |  |  | 75.02
1987-08-11 | 11 | 8 | 0.29167 | 23.9 | 75.02 | 36.008 |  |  | 75.02
1987-08-11 | 11 | 8 | 0.33333 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1987-08-11 | 11 | 8 | 0.375 | 25.6 | 78.08 | 35.9504 |  |  | 78.08
1987-08-11 | 11 | 8 | 0.41667 | 26.1 | 78.98 | 36.9434 |  |  | 78.98
1987-08-11 | 11 | 8 | 0.45833 | 26.7 | 80.06 | 36.3857 |  |  | 80.06
1987-08-11 | 11 | 8 | 0.5 | 27.8 | 82.04 | 36.4601 |  |  | 82.04
1987-08-11 | 11 | 8 | 0.54167 | 27.8 | 82.04 | 35.9318 |  |  | 82.04
1987-08-11 | 11 | 8 | 0.58333 | 29.4 | 84.92 | 37.1017 |  |  | 84.92
1987-08-11 | 11 | 8 | 0.625 | 30.6 | 87.08 | 36.3691 |  |  | 87.08
1987-08-11 | 11 | 8 | 0.66667 | 31.1 | 87.98 | 37.3688 |  |  | 87.98
1987-08-11 | 11 | 8 | 0.70833 | 31.1 | 87.98 | 36.0911 |  |  | 87.98
1987-08-11 | 11 | 8 | 0.75 | 30.6 | 87.08 | 36.3691 |  |  | 87.08
1987-08-11 | 11 | 8 | 0.79167 | 30 | 86 | 36.1682 |  |  | 86
1987-08-11 | 11 | 8 | 0.83333 | 25.6 | 78.08 | 34.7915 |  |  | 78.08
1987-08-11 | 11 | 8 | 0.875 | 25 | 77 | 33.9499 |  |  | 77
1987-08-11 | 11 | 8 | 0.91667 | 24.4 | 75.92 | 34.2019 |  |  |  | 75.92
1987-08-11 | 11 | 8 | 0.95833 | 23.9 | 75.02 | 34.1232 |  |  |  | 75.02
1987-08-11 | 11 | 8 | 1 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1987-08-12 | 12 | 8 | 0.041667 | 23.9 | 75.02 | 34.1232 |  |  |  | 75.02
1987-08-12 | 12 | 8 | 0.083333 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1987-08-12 | 12 | 8 | 0.125 | 22.8 | 73.04 | 32.967 |  |  |  | 73.04
1987-08-12 | 12 | 8 | 0.16667 | 22.2 | 71.96 | 32.3241 |  |  |  | 71.96
1987-08-12 | 12 | 8 | 0.20833 | 21.7 | 71.06 | 30.0092 |  |  |  | 71.06
1987-08-12 | 12 | 8 | 0.25 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1987-08-12 | 12 | 8 | 0.29167 | 22.2 | 71.96 | 30.2661 |  |  | 71.96
1987-08-12 | 12 | 8 | 0.33333 | 22.8 | 73.04 | 30.4423 |  |  | 73.04
1987-08-12 | 12 | 8 | 0.375 | 23.9 | 75.02 | 31.0043 |  |  | 75.02
1987-08-12 | 12 | 8 | 0.41667 | 25.6 | 78.08 | 31.796 |  |  | 78.08
1987-08-12 | 12 | 8 | 0.45833 | 26.7 | 80.06 | 32.6863 |  |  | 80.06
1987-08-12 | 12 | 8 | 0.5 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1987-08-12 | 12 | 8 | 0.54167 | 28.3 | 82.94 | 32.8552 |  |  | 82.94
1987-08-12 | 12 | 8 | 0.58333 | 28.9 | 84.02 | 32.7509 |  |  | 84.02
1987-08-12 | 12 | 8 | 0.625 | 28.3 | 82.94 | 32.0482 |  |  | 82.94
1987-08-12 | 12 | 8 | 0.66667 | 28.9 | 84.02 | 32.7509 |  |  | 84.02
1987-08-12 | 12 | 8 | 0.70833 | 28.3 | 82.94 | 32.0482 |  |  | 82.94
1987-08-12 | 12 | 8 | 0.75 | 27.8 | 82.04 | 31.734 |  |  | 82.04
1987-08-12 | 12 | 8 | 0.79167 | 27.2 | 80.96 | 31.5504 |  |  | 80.96
1987-08-12 | 12 | 8 | 0.83333 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1987-08-12 | 12 | 8 | 0.875 | 24.4 | 75.92 | 32.6987 |  |  | 75.92
1987-08-12 | 12 | 8 | 0.91667 | 23.9 | 75.02 | 33.0805 |  |  |  | 75.02
1987-08-12 | 12 | 8 | 0.95833 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
1987-08-12 | 12 | 8 | 1 | 21.7 | 71.06 | 31.096 |  |  |  | 71.06
1987-08-13 | 13 | 8 | 0.041667 | 21.1 | 69.98 | 30.6631 |  |  |  | 69.98
1987-08-13 | 13 | 8 | 0.083333 | 20.6 | 69.08 | 30.0137 |  |  |  | 69.08
1987-08-13 | 13 | 8 | 0.125 | 20.6 | 69.08 | 30.0137 |  |  |  | 69.08
1987-08-13 | 13 | 8 | 0.16667 | 20 | 68 | 29.7388 |  |  |  | 68
1987-08-13 | 13 | 8 | 0.20833 | 20 | 68 | 29.2504 |  |  |  | 68
1987-08-13 | 13 | 8 | 0.25 | 20.6 | 69.08 | 29.5066 |  |  | 69.08
1987-08-13 | 13 | 8 | 0.29167 | 20 | 68 | 29.7388 |  |  | 68
1987-08-13 | 13 | 8 | 0.33333 | 20 | 68 | 29.7388 |  |  | 68
1987-08-13 | 13 | 8 | 0.375 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1987-08-13 | 13 | 8 | 0.41667 | 22 | 71.6 | 30.3859 |  |  | 71.6
1987-08-13 | 13 | 8 | 0.45833 | 22.2 | 71.96 | 30.6394 |  |  | 71.96
1987-08-13 | 13 | 8 | 0.5 | 23.3 | 73.94 | 31.2674 |  |  | 73.94
1987-08-13 | 13 | 8 | 0.54167 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1987-08-13 | 13 | 8 | 0.58333 | 24.4 | 75.92 | 31.6289 |  |  | 75.92
1987-08-13 | 13 | 8 | 0.625 | 25.6 | 78.08 | 31.796 |  |  | 78.08
1987-08-13 | 13 | 8 | 0.66667 | 24.4 | 75.92 | 31.6289 |  |  | 75.92
1987-08-13 | 13 | 8 | 0.70833 | 24.4 | 75.92 | 31.6289 |  |  | 75.92
1987-08-13 | 13 | 8 | 0.75 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
1987-08-13 | 13 | 8 | 0.79167 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1987-08-13 | 13 | 8 | 0.83333 | 22.8 | 73.04 | 31.4112 |  |  | 73.04
1987-08-13 | 13 | 8 | 0.875 | 22.8 | 73.04 | 31.4112 |  |  | 73.04
1987-08-13 | 13 | 8 | 0.91667 | 22.8 | 73.04 | 31.4112 |  |  |  | 73.04
1987-08-13 | 13 | 8 | 0.95833 | 22.8 | 73.04 | 31.4112 |  |  |  | 73.04
1987-08-13 | 13 | 8 | 1 | 22.8 | 73.04 | 31.4112 |  |  |  | 73.04
1987-08-14 | 14 | 8 | 0.041667 | 22.2 | 71.96 | 31.2 |  |  |  | 71.96
1987-08-14 | 14 | 8 | 0.083333 | 22.2 | 71.96 | 31.2 |  |  |  | 71.96
1987-08-14 | 14 | 8 | 0.125 | 22.2 | 71.96 | 31.2 |  |  |  | 71.96
1987-08-14 | 14 | 8 | 0.16667 | 21.7 | 71.06 | 31.096 |  |  |  | 71.06
1987-08-14 | 14 | 8 | 0.20833 | 21.7 | 71.06 | 31.096 |  |  |  | 71.06
1987-08-14 | 14 | 8 | 0.25 | 22.2 | 71.96 | 31.2 |  |  | 71.96
1987-08-14 | 14 | 8 | 0.29167 | 22.8 | 73.04 | 31.4112 |  |  | 73.04
1987-08-14 | 14 | 8 | 0.33333 | 23.3 | 73.94 | 31.2674 |  |  | 73.94
1987-08-14 | 14 | 8 | 0.375 | 23.3 | 73.94 | 31.2674 |  |  | 73.94
1987-08-14 | 14 | 8 | 0.41667 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1987-08-14 | 14 | 8 | 0.45833 | 24.4 | 75.92 | 31.2019 |  |  | 75.92
1987-08-14 | 14 | 8 | 0.5 | 25 | 77 | 31.5074 |  |  | 77
1987-08-14 | 14 | 8 | 0.54167 | 25 | 77 | 31.5074 |  |  | 77
1987-08-14 | 14 | 8 | 0.58333 | 24.4 | 75.92 | 30.7754 |  |  | 75.92
1987-08-14 | 14 | 8 | 0.625 | 25 | 77 | 31.0651 |  |  | 77
1987-08-14 | 14 | 8 | 0.66667 | 24.4 | 75.92 | 30.3495 |  |  | 75.92
1987-08-14 | 14 | 8 | 0.70833 | 24.4 | 75.92 | 30.3495 |  |  | 75.92
1987-08-14 | 14 | 8 | 0.75 | 23.9 | 75.02 | 30.1773 |  |  | 75.02
1987-08-14 | 14 | 8 | 0.79167 | 23.3 | 73.94 | 29.8712 |  |  | 73.94
1987-08-14 | 14 | 8 | 0.83333 | 22.8 | 73.04 | 29.6692 |  |  | 73.04
1987-08-14 | 14 | 8 | 0.875 | 22.8 | 73.04 | 29.6692 |  |  | 73.04
1987-08-14 | 14 | 8 | 0.91667 | 22.8 | 73.04 | 30.0556 |  |  |  | 73.04
1987-08-14 | 14 | 8 | 0.95833 | 22.8 | 73.04 | 29.6692 |  |  |  | 73.04
1987-08-14 | 14 | 8 | 1 | 22.8 | 73.04 | 30.0556 |  |  |  | 73.04
1987-08-15 | 15 | 8 | 0.041667 | 22.8 | 73.04 | 30.0556 |  |  |  | 73.04
1987-08-15 | 15 | 8 | 0.083333 | 22.8 | 73.04 | 30.0556 |  |  |  | 73.04
1987-08-15 | 15 | 8 | 0.125 | 22.2 | 71.96 | 29.7069 |  |  |  | 71.96
1987-08-15 | 15 | 8 | 0.16667 | 22.8 | 73.04 | 30.0556 |  |  |  | 73.04
1987-08-15 | 15 | 8 | 0.20833 | 22.8 | 73.04 | 30.4423 |  |  |  | 73.04
1987-08-15 | 15 | 8 | 0.25 | 22.8 | 73.04 | 30.4423 |  |  | 73.04
1987-08-15 | 15 | 8 | 0.29167 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1987-08-15 | 15 | 8 | 0.33333 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1987-08-15 | 15 | 8 | 0.375 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
1987-08-15 | 15 | 8 | 0.41667 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
1987-08-15 | 15 | 8 | 0.45833 | 26.7 | 80.06 | 32.6863 |  |  | 80.06
1987-08-15 | 15 | 8 | 0.5 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-15 | 15 | 8 | 0.54167 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-15 | 15 | 8 | 0.58333 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1987-08-15 | 15 | 8 | 0.625 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1987-08-15 | 15 | 8 | 0.66667 | 27.8 | 82.04 | 33.3023 |  |  | 82.04
1987-08-15 | 15 | 8 | 0.70833 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
1987-08-15 | 15 | 8 | 0.75 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1987-08-15 | 15 | 8 | 0.79167 | 24.4 | 75.92 | 32.6987 |  |  | 75.92
1987-08-15 | 15 | 8 | 0.83333 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1987-08-15 | 15 | 8 | 0.875 | 23.9 | 75.02 | 34.1232 |  |  | 75.02
1987-08-15 | 15 | 8 | 0.91667 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
1987-08-15 | 15 | 8 | 0.95833 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
1987-08-15 | 15 | 8 | 1 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
1987-08-16 | 16 | 8 | 0.041667 | 23.3 | 73.94 | 34.48 |  |  |  | 73.94
1987-08-16 | 16 | 8 | 0.083333 | 23.3 | 73.94 | 34.48 |  |  |  | 73.94
1987-08-16 | 16 | 8 | 0.125 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
1987-08-16 | 16 | 8 | 0.16667 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
1987-08-16 | 16 | 8 | 0.20833 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
1987-08-16 | 16 | 8 | 0.25 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
1987-08-16 | 16 | 8 | 0.29167 | 23.9 | 75.02 | 35.1691 |  |  | 75.02
1987-08-16 | 16 | 8 | 0.33333 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1987-08-16 | 16 | 8 | 0.375 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
1987-08-16 | 16 | 8 | 0.41667 | 27.8 | 82.04 | 34.6146 |  |  | 82.04
1987-08-16 | 16 | 8 | 0.45833 | 28.3 | 82.94 | 35.0162 |  |  | 82.94
1987-08-16 | 16 | 8 | 0.5 | 29.4 | 84.92 | 35.364 |  |  | 84.92
1987-08-16 | 16 | 8 | 0.54167 | 30 | 86 | 36.768 |  |  | 86
1987-08-16 | 16 | 8 | 0.58333 | 30 | 86 | 35.5694 |  |  | 86
1987-08-16 | 16 | 8 | 0.625 | 28.9 | 84.02 | 36.956 |  |  | 84.02
1987-08-16 | 16 | 8 | 0.66667 | 28.9 | 84.02 | 35.2679 |  |  | 84.02
1987-08-16 | 16 | 8 | 0.70833 | 28.3 | 82.94 | 36.1017 |  |  | 82.94
1987-08-16 | 16 | 8 | 0.75 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
1987-08-16 | 16 | 8 | 0.79167 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
1987-08-16 | 16 | 8 | 0.83333 | 26.1 | 78.98 | 38.1444 |  |  | 78.98
1987-08-16 | 16 | 8 | 0.875 | 25.6 | 78.08 | 38.0464 |  |  | 78.08
1987-08-16 | 16 | 8 | 0.91667 | 25 | 77 | 37.7589 |  |  |  | 77
1987-08-16 | 16 | 8 | 0.95833 | 25 | 77 | 37.7589 |  |  |  | 77
1987-08-16 | 16 | 8 | 1 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1987-08-17 | 17 | 8 | 0.041667 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1987-08-17 | 17 | 8 | 0.083333 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1987-08-17 | 17 | 8 | 0.125 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
1987-08-17 | 17 | 8 | 0.16667 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
1987-08-17 | 17 | 8 | 0.20833 | 23.9 | 75.02 | 37.2703 |  |  |  | 75.02
1987-08-17 | 17 | 8 | 0.25 | 24 | 75.2 | 37.4343 |  |  | 75.2
1987-08-17 | 17 | 8 | 0.29167 | 25 | 77 | 38.2097 |  |  | 77
1987-08-17 | 17 | 8 | 0.33333 | 23.9 | 75.02 | 37.6921 |  |  | 75.02
1987-08-17 | 17 | 8 | 0.375 | 25 | 77 | 38.2097 |  |  | 77
1987-08-17 | 17 | 8 | 0.41667 | 25.6 | 78.08 | 38.5138 |  |  | 78.08
1987-08-17 | 17 | 8 | 0.45833 | 25 | 77 | 38.2097 |  |  | 77
1987-08-17 | 17 | 8 | 0.5 | 25 | 77 | 37.9842 |  |  | 77
1987-08-17 | 17 | 8 | 0.54167 | 23.9 | 75.02 | 37.2703 |  |  | 75.02
1987-08-17 | 17 | 8 | 0.58333 | 22.8 | 73.04 | 36.6901 |  |  | 73.04
1987-08-17 | 17 | 8 | 0.625 | 23.3 | 73.94 | 37.519 |  |  | 73.94
1987-08-17 | 17 | 8 | 0.66667 | 23.3 | 73.94 | 36.9091 |  |  | 73.94
1987-08-17 | 17 | 8 | 0.70833 | 23.3 | 73.94 | 36.9091 |  |  | 73.94
1987-08-17 | 17 | 8 | 0.75 | 23.3 | 73.94 | 36.9091 |  |  | 73.94
1987-08-17 | 17 | 8 | 0.79167 | 23.3 | 73.94 | 36.9091 |  |  | 73.94
1987-08-17 | 17 | 8 | 0.83333 | 23.3 | 73.94 | 36.9091 |  |  | 73.94
1987-08-17 | 17 | 8 | 0.875 | 23 | 73.4 | 37.0196 |  |  | 73.4
1987-08-17 | 17 | 8 | 0.91667 | 23.3 | 73.94 | 36.9091 |  |  |  | 73.94
1987-08-17 | 17 | 8 | 0.95833 | 23 | 73.4 | 37.0196 |  |  |  | 73.4
1987-08-17 | 17 | 8 | 1 | 23 | 73.4 | 37.0196 |  |  |  | 73.4
1987-08-18 | 18 | 8 | 0.041667 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
1987-08-18 | 18 | 8 | 0.083333 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
1987-08-18 | 18 | 8 | 0.125 | 23.3 | 73.94 | 36.3002 |  |  |  | 73.94
1987-08-18 | 18 | 8 | 0.16667 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1987-08-18 | 18 | 8 | 0.20833 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
1987-08-18 | 18 | 8 | 0.25 | 22.2 | 71.96 | 34.017 |  |  | 71.96
1987-08-18 | 18 | 8 | 0.29167 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
1987-08-18 | 18 | 8 | 0.33333 | 23.9 | 75.02 | 34.7504 |  |  | 75.02
1987-08-18 | 18 | 8 | 0.375 | 25 | 77 | 35.2895 |  |  | 77
1987-08-18 | 18 | 8 | 0.41667 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
1987-08-18 | 18 | 8 | 0.45833 | 27.8 | 82.04 | 36.9892 |  |  | 82.04
1987-08-18 | 18 | 8 | 0.5 | 29.4 | 84.92 | 37.6829 |  |  | 84.92
1987-08-18 | 18 | 8 | 0.54167 | 30 | 86 | 36.768 |  |  | 86
1987-08-18 | 18 | 8 | 0.58333 | 30 | 86 | 36.1682 |  |  | 86
1987-08-18 | 18 | 8 | 0.625 | 30.6 | 87.08 | 36.9901 |  |  | 87.08
1987-08-18 | 18 | 8 | 0.66667 | 28.3 | 82.94 | 35.5585 |  |  | 82.94
1987-08-18 | 18 | 8 | 0.70833 | 27.2 | 80.96 | 35.6018 |  |  | 80.96
1987-08-18 | 18 | 8 | 0.75 | 25 | 77 | 35.7372 |  |  | 77
1987-08-18 | 18 | 8 | 0.79167 | 25 | 77 | 35.7372 |  |  | 77
1987-08-18 | 18 | 8 | 0.83333 | 23.3 | 73.94 | 33.8754 |  |  | 73.94
1987-08-18 | 18 | 8 | 0.875 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
1987-08-18 | 18 | 8 | 0.91667 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1987-08-18 | 18 | 8 | 0.95833 | 20.6 | 69.08 | 30.0137 |  |  |  | 69.08
1987-08-18 | 18 | 8 | 1 | 19.4 | 66.92 | 27.7229 |  |  |  | 66.92
1987-08-19 | 19 | 8 | 0.041667 | 19.4 | 66.92 | 26.7877 |  |  |  | 66.92
1987-08-19 | 19 | 8 | 0.083333 | 17.8 | 64.04 | 25.0479 |  |  |  | 64.04
1987-08-19 | 19 | 8 | 0.125 | 17.2 | 62.96 | 24.4197 |  |  |  | 62.96
1987-08-19 | 19 | 8 | 0.16667 | 16.7 | 62.06 | 23.9059 |  |  |  | 62.06
1987-08-19 | 19 | 8 | 0.20833 | 16.1 | 60.98 | 22.9247 |  |  |  | 60.98
1987-08-19 | 19 | 8 | 0.25 | 16.1 | 60.98 | 22.5492 |  |  | 60.98
1987-08-19 | 19 | 8 | 0.29167 | 16.7 | 62.06 | 23.2543 |  |  | 62.06
1987-08-19 | 19 | 8 | 0.33333 | 16.7 | 62.06 | 22.8639 |  |  | 62.06
1987-08-19 | 19 | 8 | 0.375 | 17.8 | 64.04 | 23.3691 |  |  | 64.04
1987-08-19 | 19 | 8 | 0.41667 | 18.3 | 64.94 | 23.2706 |  |  | 64.94
1987-08-19 | 19 | 8 | 0.45833 | 19.4 | 66.92 | 23.9971 |  |  | 66.92
1987-08-19 | 19 | 8 | 0.5 | 20.6 | 69.08 | 24.9764 |  |  | 69.08
1987-08-19 | 19 | 8 | 0.54167 | 21.1 | 69.98 | 24.7736 |  |  | 69.98
1987-08-19 | 19 | 8 | 0.58333 | 21.7 | 71.06 | 24.448 |  |  | 71.06
1987-08-19 | 19 | 8 | 0.625 | 22.2 | 71.96 | 24.7148 |  |  | 71.96
1987-08-19 | 19 | 8 | 0.66667 | 22.2 | 71.96 | 24.7148 |  |  | 71.96
1987-08-19 | 19 | 8 | 0.70833 | 22.2 | 71.96 | 24.7148 |  |  | 71.96
1987-08-19 | 19 | 8 | 0.75 | 21.7 | 71.06 | 24.9823 |  |  | 71.06
1987-08-19 | 19 | 8 | 0.79167 | 21.1 | 69.98 | 24.6019 |  |  | 69.98
1987-08-19 | 19 | 8 | 0.83333 | 20.6 | 69.08 | 23.9777 |  |  | 69.08
1987-08-19 | 19 | 8 | 0.875 | 20 | 68 | 23.4433 |  |  | 68
1987-08-19 | 19 | 8 | 0.91667 | 20 | 68 | 23.7633 |  |  |  | 68
1987-08-19 | 19 | 8 | 0.95833 | 19.4 | 66.92 | 23.2259 |  |  |  | 66.92
1987-08-19 | 19 | 8 | 1 | 18.9 | 66.02 | 22.9344 |  |  |  | 66.02
1987-08-20 | 20 | 8 | 0.041667 | 18.9 | 66.02 | 22.9344 |  |  |  | 66.02
1987-08-20 | 20 | 8 | 0.083333 | 18.3 | 64.94 | 23.2706 |  |  |  | 64.94
1987-08-20 | 20 | 8 | 0.125 | 17.8 | 64.04 | 22.8114 |  |  |  | 64.04
1987-08-20 | 20 | 8 | 0.16667 | 17.8 | 64.04 | 23.0902 |  |  |  | 64.04
1987-08-20 | 20 | 8 | 0.20833 | 17.2 | 62.96 | 22.5374 |  |  |  | 62.96
1987-08-20 | 20 | 8 | 0.25 | 16.7 | 62.06 | 22.3441 |  |  | 62.06
1987-08-20 | 20 | 8 | 0.29167 | 17.8 | 64.04 | 23.0902 |  |  | 64.04
1987-08-20 | 20 | 8 | 0.33333 | 19.4 | 66.92 | 23.8427 |  |  | 66.92
1987-08-20 | 20 | 8 | 0.375 | 20.6 | 69.08 | 24.3103 |  |  | 69.08
1987-08-20 | 20 | 8 | 0.41667 | 21.7 | 71.06 | 24.9823 |  |  | 71.06
1987-08-20 | 20 | 8 | 0.45833 | 22.2 | 71.96 | 25.2659 |  |  | 71.96
1987-08-20 | 20 | 8 | 0.5 | 22.2 | 71.96 | 25.0821 |  |  | 71.96
1987-08-20 | 20 | 8 | 0.54167 | 24.4 | 75.92 | 25.9085 |  |  | 75.92
1987-08-20 | 20 | 8 | 0.58333 | 25 | 77 | 26.2371 |  |  | 77
1987-08-20 | 20 | 8 | 0.625 | 25.6 | 78.08 | 27.0111 |  |  | 78.08
1987-08-20 | 20 | 8 | 0.66667 | 25.6 | 78.08 | 27.0111 |  |  | 78.08
1987-08-20 | 20 | 8 | 0.70833 | 26.1 | 78.98 | 27.7154 |  |  | 78.98
1987-08-20 | 20 | 8 | 0.75 | 25 | 77 | 28.204 |  |  | 77
1987-08-20 | 20 | 8 | 0.79167 | 25 | 77 | 29.3016 |  |  | 77
1987-08-20 | 20 | 8 | 0.83333 | 22.8 | 73.04 | 28.7052 |  |  | 73.04
1987-08-20 | 20 | 8 | 0.875 | 22.2 | 71.96 | 28.0348 |  |  | 71.96
1987-08-20 | 20 | 8 | 0.91667 | 21.7 | 71.06 | 27.8458 |  |  |  | 71.06
1987-08-20 | 20 | 8 | 0.95833 | 21.1 | 69.98 | 27.5326 |  |  |  | 69.98
1987-08-20 | 20 | 8 | 1 | 21.1 | 69.98 | 27.5326 |  |  |  | 69.98
1987-08-21 | 21 | 8 | 0.041667 | 20.6 | 69.08 | 26.9825 |  |  |  | 69.08
1987-08-21 | 21 | 8 | 0.083333 | 21.1 | 69.98 | 26.8408 |  |  |  | 69.98
1987-08-21 | 21 | 8 | 0.125 | 21.1 | 69.98 | 26.4954 |  |  |  | 69.98
1987-08-21 | 21 | 8 | 0.16667 | 20.6 | 69.08 | 25.978 |  |  |  | 69.08
1987-08-21 | 21 | 8 | 0.20833 | 20.6 | 69.08 | 26.3125 |  |  |  | 69.08
1987-08-21 | 21 | 8 | 0.25 | 20 | 68 | 26.0121 |  |  | 68
1987-08-21 | 21 | 8 | 0.29167 | 21.1 | 69.98 | 26.8408 |  |  | 69.98
1987-08-21 | 21 | 8 | 0.33333 | 21.7 | 71.06 | 26.7692 |  |  | 71.06
1987-08-21 | 21 | 8 | 0.375 | 22.8 | 73.04 | 27.552 |  |  | 73.04
1987-08-21 | 21 | 8 | 0.41667 | 23.9 | 75.02 | 28.3237 |  |  | 75.02
1987-08-21 | 21 | 8 | 0.45833 | 25 | 77 | 28.8622 |  |  | 77
1987-08-21 | 21 | 8 | 0.5 | 26.1 | 78.98 | 29.8233 |  |  | 78.98
1987-08-21 | 21 | 8 | 0.54167 | 27.2 | 80.96 | 31.5504 |  |  | 80.96
1987-08-21 | 21 | 8 | 0.58333 | 28.9 | 84.02 | 32.7509 |  |  | 84.02
1987-08-21 | 21 | 8 | 0.625 | 28.3 | 82.94 | 32.8552 |  |  | 82.94
1987-08-21 | 21 | 8 | 0.66667 | 28.9 | 84.02 | 33.3087 |  |  | 84.02
1987-08-21 | 21 | 8 | 0.70833 | 28.9 | 84.02 | 33.3087 |  |  | 84.02
1987-08-21 | 21 | 8 | 0.75 | 28.3 | 82.94 | 33.934 |  |  | 82.94
1987-08-21 | 21 | 8 | 0.79167 | 27.2 | 80.96 | 32.8114 |  |  | 80.96
1987-08-21 | 21 | 8 | 0.83333 | 26.7 | 80.06 | 33.669 |  |  | 80.06
1987-08-21 | 21 | 8 | 0.875 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1987-08-21 | 21 | 8 | 0.91667 | 24.4 | 75.92 | 34.2019 |  |  |  | 75.92
1987-08-21 | 21 | 8 | 0.95833 | 23.9 | 75.02 | 34.1232 |  |  |  | 75.02
1987-08-21 | 21 | 8 | 1 | 22.8 | 73.04 | 33.5522 |  |  |  | 73.04
1987-08-22 | 22 | 8 | 0.041667 | 22.8 | 73.04 | 32.967 |  |  |  | 73.04
1987-08-22 | 22 | 8 | 0.083333 | 22.2 | 71.96 | 31.7616 |  |  |  | 71.96
1987-08-22 | 22 | 8 | 0.125 | 22.2 | 71.96 | 31.3871 |  |  |  | 71.96
1987-08-22 | 22 | 8 | 0.16667 | 21.7 | 71.06 | 31.096 |  |  |  | 71.06
1987-08-22 | 22 | 8 | 0.20833 | 21.1 | 69.98 | 30.8379 |  |  |  | 69.98
1987-08-22 | 22 | 8 | 0.25 | 21.7 | 71.06 | 30.5522 |  |  | 71.06
1987-08-22 | 22 | 8 | 0.29167 | 21.1 | 69.98 | 28.9205 |  |  | 69.98
1987-08-22 | 22 | 8 | 0.33333 | 22.2 | 71.96 | 29.3347 |  |  | 71.96
1987-08-22 | 22 | 8 | 0.375 | 22.8 | 73.04 | 31.4112 |  |  | 73.04
1987-08-22 | 22 | 8 | 0.41667 | 23.9 | 75.02 | 29.5583 |  |  | 75.02
1987-08-22 | 22 | 8 | 0.45833 | 25 | 77 | 28.8622 |  |  | 77
1987-08-22 | 22 | 8 | 0.5 | 25.6 | 78.08 | 28.3715 |  |  | 78.08
1987-08-22 | 22 | 8 | 0.54167 | 26.1 | 78.98 | 31.4717 |  |  | 78.98
1987-08-22 | 22 | 8 | 0.58333 | 27.8 | 82.04 | 32.256 |  |  | 82.04
1987-08-22 | 22 | 8 | 0.625 | 27.8 | 82.04 | 33.0404 |  |  | 82.04
1987-08-22 | 22 | 8 | 0.66667 | 26.1 | 78.98 | 30.2935 |  |  | 78.98
1987-08-22 | 22 | 8 | 0.70833 | 27.2 | 80.96 | 29.7927 |  |  | 80.96
1987-08-22 | 22 | 8 | 0.75 | 26.1 | 78.98 | 28.4166 |  |  | 78.98
1987-08-22 | 22 | 8 | 0.79167 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1987-08-22 | 22 | 8 | 0.83333 | 23.9 | 75.02 | 30.5905 |  |  | 75.02
1987-08-22 | 22 | 8 | 0.875 | 23.9 | 75.02 | 31.4185 |  |  | 75.02
1987-08-22 | 22 | 8 | 0.91667 | 23.3 | 73.94 | 32.2682 |  |  |  | 73.94
1987-08-22 | 22 | 8 | 0.95833 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1987-08-22 | 22 | 8 | 1 | 23.3 | 73.94 | 32.2682 |  |  |  | 73.94
1987-08-23 | 23 | 8 | 0.041667 | 22.8 | 73.04 | 32.967 |  |  |  | 73.04
1987-08-23 | 23 | 8 | 0.083333 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
1987-08-23 | 23 | 8 | 0.125 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
1987-08-23 | 23 | 8 | 0.16667 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
1987-08-23 | 23 | 8 | 0.20833 | 23.3 | 73.94 | 32.2682 |  |  |  | 73.94
1987-08-23 | 23 | 8 | 0.25 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
1987-08-23 | 23 | 8 | 0.29167 | 22.8 | 73.04 | 32.5774 |  |  | 73.04
1987-08-23 | 23 | 8 | 0.33333 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1987-08-23 | 23 | 8 | 0.375 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
1987-08-23 | 23 | 8 | 0.41667 | 26.7 | 80.06 | 35.8902 |  |  | 80.06
1987-08-23 | 23 | 8 | 0.45833 | 26.7 | 80.06 | 35.8902 |  |  | 80.06
1987-08-23 | 23 | 8 | 0.5 | 27.2 | 80.96 | 36.622 |  |  | 80.96
1987-08-23 | 23 | 8 | 0.54167 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
1987-08-23 | 23 | 8 | 0.58333 | 28.3 | 82.94 | 37.1906 |  |  | 82.94
1987-08-23 | 23 | 8 | 0.625 | 29.4 | 84.92 | 37.1017 |  |  | 84.92
1987-08-23 | 23 | 8 | 0.66667 | 29.4 | 84.92 | 40.3101 |  |  | 84.92
1987-08-23 | 23 | 8 | 0.70833 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
1987-08-23 | 23 | 8 | 0.75 | 28.3 | 82.94 | 38.5566 |  |  | 82.94
1987-08-23 | 23 | 8 | 0.79167 | 27.8 | 82.04 | 38.3155 |  |  | 82.04
1987-08-23 | 23 | 8 | 0.83333 | 27.8 | 82.04 | 38.3155 |  |  | 82.04
1987-08-23 | 23 | 8 | 0.875 | 28.3 | 82.94 | 39.1044 |  |  | 82.94
1987-08-23 | 23 | 8 | 0.91667 | 28.3 | 82.94 | 38.5566 |  |  |  | 82.94
1987-08-23 | 23 | 8 | 0.95833 | 27.8 | 82.04 | 38.8474 |  |  |  | 82.04
1987-08-23 | 23 | 8 | 1 | 27.8 | 82.04 | 38.3155 |  |  |  | 82.04
1987-08-24 | 24 | 8 | 0.041667 | 27.2 | 80.96 | 37.9015 |  |  |  | 80.96
1987-08-24 | 24 | 8 | 0.083333 | 26.7 | 80.06 | 37.1303 |  |  |  | 80.06
1987-08-24 | 24 | 8 | 0.125 | 26.1 | 78.98 | 36.9434 |  |  |  | 78.98
1987-08-24 | 24 | 8 | 0.16667 | 26.1 | 78.98 | 37.4233 |  |  |  | 78.98
1987-08-24 | 24 | 8 | 0.20833 | 25.6 | 78.08 | 37.3463 |  |  |  | 78.08
1987-08-24 | 24 | 8 | 0.25 | 25 | 77 | 36.8589 |  |  | 77
1987-08-24 | 24 | 8 | 0.29167 | 25.6 | 78.08 | 37.3463 |  |  | 78.08
1987-08-24 | 24 | 8 | 0.33333 | 26.7 | 80.06 | 37.1303 |  |  | 80.06
1987-08-24 | 24 | 8 | 0.375 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
1987-08-24 | 24 | 8 | 0.41667 | 29.4 | 84.92 | 38.265 |  |  | 84.92
1987-08-24 | 24 | 8 | 0.45833 | 30.6 | 87.08 | 38.2353 |  |  | 87.08
1987-08-24 | 24 | 8 | 0.5 | 32.2 | 89.96 | 38.2472 |  |  | 89.96
1987-08-24 | 24 | 8 | 0.54167 | 32.8 | 91.04 | 38.0415 |  |  | 91.04
1987-08-24 | 24 | 8 | 0.58333 | 33.3 | 91.94 | 36.5624 |  |  | 91.94
1987-08-24 | 24 | 8 | 0.625 | 32.2 | 89.96 | 36.2057 |  |  | 89.96
1987-08-24 | 24 | 8 | 0.66667 | 32.8 | 91.04 | 36.9851 |  |  | 91.04
1987-08-24 | 24 | 8 | 0.70833 | 32.2 | 89.96 | 37.225 |  |  | 89.96
1987-08-24 | 24 | 8 | 0.75 | 31.7 | 89.06 | 36.5577 |  |  | 89.06
1987-08-24 | 24 | 8 | 0.79167 | 31.1 | 87.98 | 36.7294 |  |  | 87.98
1987-08-24 | 24 | 8 | 0.83333 | 30.6 | 87.08 | 36.3691 |  |  | 87.08
1987-08-24 | 24 | 8 | 0.875 | 30 | 86 | 36.1682 |  |  | 86
1987-08-24 | 24 | 8 | 0.91667 | 29.4 | 84.92 | 35.9423 |  |  |  | 84.92
1987-08-24 | 24 | 8 | 0.95833 | 28.9 | 84.02 | 36.3924 |  |  |  | 84.02
1987-08-24 | 24 | 8 | 1 | 28.3 | 82.94 | 36.6457 |  |  |  | 82.94
1987-08-25 | 25 | 8 | 0.041667 | 28.3 | 82.94 | 36.1017 |  |  |  | 82.94
1987-08-25 | 25 | 8 | 0.083333 | 28.3 | 82.94 | 34.4746 |  |  |  | 82.94
1987-08-25 | 25 | 8 | 0.125 | 27.8 | 82.04 | 34.0891 |  |  |  | 82.04
1987-08-25 | 25 | 8 | 0.16667 | 27.2 | 80.96 | 33.8235 |  |  |  | 80.96
1987-08-25 | 25 | 8 | 0.20833 | 26.7 | 80.06 | 33.1773 |  |  |  | 80.06
1987-08-25 | 25 | 8 | 0.25 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
1987-08-25 | 25 | 8 | 0.29167 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
1987-08-25 | 25 | 8 | 0.33333 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-25 | 25 | 8 | 0.375 | 29.4 | 84.92 | 34.4984 |  |  | 84.92
1987-08-25 | 25 | 8 | 0.41667 | 30.6 | 87.08 | 34.5129 |  |  | 87.08
1987-08-25 | 25 | 8 | 0.45833 | 32.2 | 89.96 | 35.1894 |  |  | 89.96
1987-08-25 | 25 | 8 | 0.5 | 32.8 | 91.04 | 35.2316 |  |  | 91.04
1987-08-25 | 25 | 8 | 0.54167 | 33.3 | 91.94 | 37.2852 |  |  | 91.94
1987-08-25 | 25 | 8 | 0.58333 | 31.1 | 87.98 | 36.0911 |  |  | 87.98
1987-08-25 | 25 | 8 | 0.625 | 31.1 | 87.98 | 35.7724 |  |  | 87.98
1987-08-25 | 25 | 8 | 0.66667 | 30.6 | 87.08 | 33.8964 |  |  | 87.08
1987-08-25 | 25 | 8 | 0.70833 | 30 | 86 | 35.2704 |  |  | 86
1987-08-25 | 25 | 8 | 0.75 | 30 | 86 | 35.2704 |  |  | 86
1987-08-25 | 25 | 8 | 0.79167 | 29.4 | 84.92 | 35.9423 |  |  | 84.92
1987-08-25 | 25 | 8 | 0.83333 | 28.3 | 82.94 | 35.5585 |  |  | 82.94
1987-08-25 | 25 | 8 | 0.875 | 27.2 | 80.96 | 36.622 |  |  | 80.96
1987-08-25 | 25 | 8 | 0.91667 | 27.8 | 82.04 | 35.9318 |  |  |  | 82.04
1987-08-25 | 25 | 8 | 0.95833 | 27.2 | 80.96 | 35.6018 |  |  |  | 80.96
1987-08-25 | 25 | 8 | 1 | 26.7 | 80.06 | 37.1303 |  |  |  | 80.06
1987-08-26 | 26 | 8 | 0.041667 | 25.6 | 78.08 | 35.9504 |  |  |  | 78.08
1987-08-26 | 26 | 8 | 0.083333 | 24.4 | 75.92 | 34.8482 |  |  |  | 75.92
1987-08-26 | 26 | 8 | 0.125 | 22.8 | 73.04 | 34.7256 |  |  |  | 73.04
1987-08-26 | 26 | 8 | 0.16667 | 22.2 | 71.96 | 34.3944 |  |  |  | 71.96
1987-08-26 | 26 | 8 | 0.20833 | 22.2 | 71.96 | 34.3944 |  |  |  | 71.96
1987-08-26 | 26 | 8 | 0.25 | 22.8 | 73.04 | 34.7256 |  |  | 73.04
1987-08-26 | 26 | 8 | 0.29167 | 25 | 77 | 35.7372 |  |  | 77
1987-08-26 | 26 | 8 | 0.33333 | 23.9 | 75.02 | 36.008 |  |  | 75.02
1987-08-26 | 26 | 8 | 0.375 | 26.1 | 78.98 | 37.4233 |  |  | 78.98
1987-08-26 | 26 | 8 | 0.41667 | 28.9 | 84.02 | 38.6523 |  |  | 84.02
1987-08-26 | 26 | 8 | 0.45833 | 30 | 86 | 39.1775 |  |  | 86
1987-08-26 | 26 | 8 | 0.5 | 31.1 | 87.98 | 38.9724 |  |  | 87.98
1987-08-26 | 26 | 8 | 0.54167 | 31.1 | 87.98 | 38.9724 |  |  | 87.98
1987-08-26 | 26 | 8 | 0.58333 | 29.4 | 84.92 | 40.8966 |  |  | 84.92
1987-08-26 | 26 | 8 | 0.625 | 29.4 | 84.92 | 41.7782 |  |  | 84.92
1987-08-26 | 26 | 8 | 0.66667 | 30 | 86 | 41.2994 |  |  | 86
1987-08-26 | 26 | 8 | 0.70833 | 29.4 | 84.92 | 41.7782 |  |  | 84.92
1987-08-26 | 26 | 8 | 0.75 | 24 | 75.2 | 36.3754 |  |  | 75.2
1987-08-26 | 26 | 8 | 0.79167 | 26.1 | 78.98 | 38.1444 |  |  | 78.98
1987-08-26 | 26 | 8 | 0.83333 | 26.7 | 80.06 | 38.3749 |  |  | 80.06
1987-08-26 | 26 | 8 | 0.875 | 26.7 | 80.06 | 39.8742 |  |  | 80.06
1987-08-26 | 26 | 8 | 0.91667 | 26.7 | 80.06 | 40.3754 |  |  |  | 80.06
1987-08-26 | 26 | 8 | 0.95833 | 26.7 | 80.06 | 41.1285 |  |  |  | 80.06
1987-08-26 | 26 | 8 | 1 | 25.6 | 78.08 | 39.92 |  |  |  | 78.08
1987-08-27 | 27 | 8 | 0.041667 | 26.1 | 78.98 | 39.591 |  |  |  | 78.98
1987-08-27 | 27 | 8 | 0.083333 | 25 | 77 | 37.7589 |  |  |  | 77
1987-08-27 | 27 | 8 | 0.125 | 24.4 | 75.92 | 32.2704 |  |  |  | 75.92
1987-08-27 | 27 | 8 | 0.16667 | 24.4 | 75.92 | 31.6289 |  |  |  | 75.92
1987-08-27 | 27 | 8 | 0.20833 | 23.9 | 75.02 | 31.4185 |  |  |  | 75.02
1987-08-27 | 27 | 8 | 0.25 | 23.3 | 73.94 | 30.6683 |  |  | 73.94
1987-08-27 | 27 | 8 | 0.29167 | 23.3 | 73.94 | 30.6683 |  |  | 73.94
1987-08-27 | 27 | 8 | 0.33333 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1987-08-27 | 27 | 8 | 0.375 | 24.4 | 75.92 | 31.6289 |  |  | 75.92
1987-08-27 | 27 | 8 | 0.41667 | 24.4 | 75.92 | 32.6987 |  |  | 75.92
1987-08-27 | 27 | 8 | 0.45833 | 25 | 77 | 33.5046 |  |  | 77
1987-08-27 | 27 | 8 | 0.5 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
1987-08-27 | 27 | 8 | 0.54167 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
1987-08-27 | 27 | 8 | 0.58333 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
1987-08-27 | 27 | 8 | 0.625 | 28.9 | 84.02 | 32.1941 |  |  | 84.02
1987-08-27 | 27 | 8 | 0.66667 | 28.9 | 84.02 | 33.3087 |  |  | 84.02
1987-08-27 | 27 | 8 | 0.70833 | 28.3 | 82.94 | 34.4746 |  |  | 82.94
1987-08-27 | 27 | 8 | 0.75 | 27.8 | 82.04 | 35.1409 |  |  | 82.04
1987-08-27 | 27 | 8 | 0.79167 | 26.7 | 80.06 | 35.3954 |  |  | 80.06
1987-08-27 | 27 | 8 | 0.83333 | 26.1 | 78.98 | 36.9434 |  |  | 78.98
1987-08-27 | 27 | 8 | 0.875 | 25 | 77 | 36.8589 |  |  | 77
1987-08-27 | 27 | 8 | 0.91667 | 24.4 | 75.92 | 37.4451 |  |  |  | 75.92
1987-08-27 | 27 | 8 | 0.95833 | 24.4 | 75.92 | 36.7941 |  |  |  | 75.92
1987-08-27 | 27 | 8 | 1 | 23.9 | 75.02 | 36.4283 |  |  |  | 75.02
1987-08-28 | 28 | 8 | 0.041667 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1987-08-28 | 28 | 8 | 0.083333 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1987-08-28 | 28 | 8 | 0.125 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1987-08-28 | 28 | 8 | 0.16667 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1987-08-28 | 28 | 8 | 0.20833 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1987-08-28 | 28 | 8 | 0.25 | 22.8 | 73.04 | 35.5101 |  |  | 73.04
1987-08-28 | 28 | 8 | 0.29167 | 23.3 | 73.94 | 35.6924 |  |  | 73.94
1987-08-28 | 28 | 8 | 0.33333 | 23.3 | 73.94 | 34.8837 |  |  | 73.94
1987-08-28 | 28 | 8 | 0.375 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
1987-08-28 | 28 | 8 | 0.41667 | 25 | 77 | 34.6191 |  |  | 77
1987-08-28 | 28 | 8 | 0.45833 | 25 | 77 | 34.6191 |  |  | 77
1987-08-28 | 28 | 8 | 0.5 | 26.1 | 78.98 | 34.5538 |  |  | 78.98
1987-08-28 | 28 | 8 | 0.54167 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
1987-08-28 | 28 | 8 | 0.58333 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
1987-08-28 | 28 | 8 | 0.625 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1987-08-28 | 28 | 8 | 0.66667 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
1987-08-28 | 28 | 8 | 0.70833 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1987-08-28 | 28 | 8 | 0.75 | 25 | 77 | 33.9499 |  |  | 77
1987-08-28 | 28 | 8 | 0.79167 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1987-08-28 | 28 | 8 | 0.83333 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1987-08-28 | 28 | 8 | 0.875 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1987-08-28 | 28 | 8 | 0.91667 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1987-08-28 | 28 | 8 | 0.95833 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1987-08-28 | 28 | 8 | 1 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1987-08-29 | 29 | 8 | 0.041667 | 23.9 | 75.02 | 32.4563 |  |  |  | 75.02
1987-08-29 | 29 | 8 | 0.083333 | 23.9 | 75.02 | 32.0408 |  |  |  | 75.02
1987-08-29 | 29 | 8 | 0.125 | 23.3 | 73.94 | 32.2682 |  |  |  | 73.94
1987-08-29 | 29 | 8 | 0.16667 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1987-08-29 | 29 | 8 | 0.20833 | 23.3 | 73.94 | 32.2682 |  |  |  | 73.94
1987-08-29 | 29 | 8 | 0.25 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1987-08-29 | 29 | 8 | 0.29167 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
1987-08-29 | 29 | 8 | 0.33333 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
1987-08-29 | 29 | 8 | 0.375 | 26.7 | 80.06 | 32.196 |  |  | 80.06
1987-08-29 | 29 | 8 | 0.41667 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-29 | 29 | 8 | 0.45833 | 29.4 | 84.92 | 34.7867 |  |  | 84.92
1987-08-29 | 29 | 8 | 0.5 | 30 | 86 | 36.1682 |  |  | 86
1987-08-29 | 29 | 8 | 0.54167 | 30.6 | 87.08 | 36.9901 |  |  | 87.08
1987-08-29 | 29 | 8 | 0.58333 | 30.6 | 87.08 | 36.3691 |  |  | 87.08
1987-08-29 | 29 | 8 | 0.625 | 29.4 | 84.92 | 37.1017 |  |  | 84.92
1987-08-29 | 29 | 8 | 0.66667 | 30.6 | 87.08 | 36.0591 |  |  | 87.08
1987-08-29 | 29 | 8 | 0.70833 | 30.6 | 87.08 | 36.0591 |  |  | 87.08
1987-08-29 | 29 | 8 | 0.75 | 30 | 86 | 35.5694 |  |  | 86
1987-08-29 | 29 | 8 | 0.79167 | 28.3 | 82.94 | 34.4746 |  |  | 82.94
1987-08-29 | 29 | 8 | 0.83333 | 27.2 | 80.96 | 34.8385 |  |  | 80.96
1987-08-29 | 29 | 8 | 0.875 | 26.7 | 80.06 | 34.6544 |  |  | 80.06
1987-08-29 | 29 | 8 | 0.91667 | 26.1 | 78.98 | 35.7466 |  |  |  | 78.98
1987-08-29 | 29 | 8 | 0.95833 | 26.1 | 78.98 | 35.0304 |  |  |  | 78.98
1987-08-29 | 29 | 8 | 1 | 25.6 | 78.08 | 34.3289 |  |  |  | 78.08
1987-08-30 | 30 | 8 | 0.041667 | 25 | 77 | 33.9499 |  |  |  | 77
1987-08-30 | 30 | 8 | 0.083333 | 25 | 77 | 33.9499 |  |  |  | 77
1987-08-30 | 30 | 8 | 0.125 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
1987-08-30 | 30 | 8 | 0.16667 | 24.3 | 75.74 | 33.6324 |  |  |  | 75.74
1987-08-30 | 30 | 8 | 0.20833 | 23.9 | 75.02 | 33.4972 |  |  |  | 75.02
1987-08-30 | 30 | 8 | 0.25 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1987-08-30 | 30 | 8 | 0.29167 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1987-08-30 | 30 | 8 | 0.33333 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
1987-08-30 | 30 | 8 | 0.375 | 26.7 | 80.06 | 34.1614 |  |  | 80.06
1987-08-30 | 30 | 8 | 0.41667 | 27.2 | 80.96 | 34.5845 |  |  | 80.96
1987-08-30 | 30 | 8 | 0.45833 | 28.3 | 82.94 | 35.5585 |  |  | 82.94
1987-08-30 | 30 | 8 | 0.5 | 29.4 | 84.92 | 34.7867 |  |  | 84.92
1987-08-30 | 30 | 8 | 0.54167 | 29.4 | 84.92 | 34.7867 |  |  | 84.92
1987-08-30 | 30 | 8 | 0.58333 | 30 | 86 | 35.2704 |  |  | 86
1987-08-30 | 30 | 8 | 0.625 | 31.1 | 87.98 | 34.1834 |  |  | 87.98
1987-08-30 | 30 | 8 | 0.66667 | 30.6 | 87.08 | 33.8964 |  |  | 87.08
1987-08-30 | 30 | 8 | 0.70833 | 30 | 86 | 34.077 |  |  | 86
1987-08-30 | 30 | 8 | 0.75 | 28.9 | 84.02 | 35.2679 |  |  | 84.02
1987-08-30 | 30 | 8 | 0.79167 | 28.3 | 82.94 | 36.6457 |  |  | 82.94
1987-08-30 | 30 | 8 | 0.83333 | 28.3 | 82.94 | 35.0162 |  |  | 82.94
1987-08-30 | 30 | 8 | 0.875 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1987-08-30 | 30 | 8 | 0.91667 | 28.3 | 82.94 | 33.934 |  |  |  | 82.94
1987-08-30 | 30 | 8 | 0.95833 | 27.8 | 82.04 | 33.8266 |  |  |  | 82.04
1987-08-30 | 30 | 8 | 1 | 27.2 | 80.96 | 33.8235 |  |  |  | 80.96
1987-08-31 | 31 | 8 | 0.041667 | 26.7 | 80.06 | 33.669 |  |  |  | 80.06
1987-08-31 | 31 | 8 | 0.083333 | 25.6 | 78.08 | 33.867 |  |  |  | 78.08
1987-08-31 | 31 | 8 | 0.125 | 24.4 | 75.92 | 33.7718 |  |  |  | 75.92
1987-08-31 | 31 | 8 | 0.16667 | 23.3 | 73.94 | 33.2718 |  |  |  | 73.94
1987-08-31 | 31 | 8 | 0.20833 | 23.3 | 73.94 | 32.6693 |  |  |  | 73.94
1987-08-31 | 31 | 8 | 0.25 | 23.3 | 73.94 | 32.6693 |  |  | 73.94
1987-08-31 | 31 | 8 | 0.29167 | 23.3 | 73.94 | 32.2682 |  |  | 73.94
1987-08-31 | 31 | 8 | 0.33333 | 23.9 | 75.02 | 31.0043 |  |  | 75.02
1987-08-31 | 31 | 8 | 0.375 | 23.3 | 73.94 | 30.2695 |  |  | 73.94
1987-08-31 | 31 | 8 | 0.41667 | 24.4 | 75.92 | 30.7754 |  |  | 75.92
1987-08-31 | 31 | 8 | 0.45833 | 25 | 77 | 31.0651 |  |  | 77
1987-08-31 | 31 | 8 | 0.5 | 25.6 | 78.08 | 31.3374 |  |  | 78.08
1987-08-31 | 31 | 8 | 0.54167 | 26.7 | 80.06 | 31.7064 |  |  | 80.06
1987-08-31 | 31 | 8 | 0.58333 | 27.2 | 80.96 | 32.5588 |  |  | 80.96
1987-08-31 | 31 | 8 | 0.625 | 27.2 | 80.96 | 32.5588 |  |  | 80.96
1987-08-31 | 31 | 8 | 0.66667 | 26.7 | 80.06 | 32.196 |  |  | 80.06
1987-08-31 | 31 | 8 | 0.70833 | 26.1 | 78.98 | 32.8908 |  |  | 78.98
1987-08-31 | 31 | 8 | 0.75 | 26.1 | 78.98 | 32.8908 |  |  | 78.98
1987-08-31 | 31 | 8 | 0.79167 | 26.1 | 78.98 | 32.4171 |  |  | 78.98
1987-08-31 | 31 | 8 | 0.83333 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1987-08-31 | 31 | 8 | 0.875 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1987-08-31 | 31 | 8 | 0.91667 | 23.8 | 74.84 | 30.8807 |  |  |  | 74.84
1987-08-31 | 31 | 8 | 0.95833 | 23.7 | 74.66 | 28.3135 |  |  |  | 74.66
1987-08-31 | 31 | 8 | 1 | 23.6 | 74.48 | 30.6349 |  |  |  | 74.48
1995-09-01 | 1 | 9 | 0.041667 | 23.6 | 74.48 | 34.3103 |  |  |  | 74.48
1995-09-01 | 1 | 9 | 0.083333 | 23.5 | 74.3 | 34.1647 |  |  |  | 74.3
1995-09-01 | 1 | 9 | 0.125 | 23.4 | 74.12 | 34.6283 |  |  |  | 74.12
1995-09-01 | 1 | 9 | 0.16667 | 23.3 | 73.94 | 34.48 |  |  |  | 73.94
1995-09-01 | 1 | 9 | 0.20833 | 23.3 | 73.94 | 33.8754 |  |  |  | 73.94
1995-09-01 | 1 | 9 | 0.25 | 22.8 | 73.04 | 31.9938 |  |  | 73.04
1995-09-01 | 1 | 9 | 0.29167 | 22.2 | 71.96 | 31.2 |  |  | 71.96
1995-09-01 | 1 | 9 | 0.33333 | 22.8 | 73.04 | 31.4112 |  |  | 73.04
1995-09-01 | 1 | 9 | 0.375 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1995-09-01 | 1 | 9 | 0.41667 | 23.3 | 73.94 | 30.6683 |  |  | 73.94
1995-09-01 | 1 | 9 | 0.45833 | 24.4 | 75.92 | 30.7754 |  |  | 75.92
1995-09-01 | 1 | 9 | 0.5 | 26.1 | 78.98 | 30.9999 |  |  | 78.98
1995-09-01 | 1 | 9 | 0.54167 | 26.1 | 78.98 | 29.8233 |  |  | 78.98
1995-09-01 | 1 | 9 | 0.58333 | 26.1 | 78.98 | 29.8233 |  |  | 78.98
1995-09-01 | 1 | 9 | 0.625 | 26.7 | 80.06 | 29.2687 |  |  | 80.06
1995-09-01 | 1 | 9 | 0.66667 | 26.7 | 80.06 | 28.2984 |  |  | 80.06
1995-09-01 | 1 | 9 | 0.70833 | 26.1 | 78.98 | 28.6507 |  |  | 78.98
1995-09-01 | 1 | 9 | 0.75 | 25.6 | 78.08 | 28.3715 |  |  | 78.08
1995-09-01 | 1 | 9 | 0.79167 | 24.4 | 75.92 | 28.2276 |  |  | 75.92
1995-09-01 | 1 | 9 | 0.83333 | 22.8 | 73.04 | 26.2114 |  |  | 73.04
1995-09-01 | 1 | 9 | 0.875 | 21.1 | 69.98 | 24.7736 |  |  | 69.98
1995-09-01 | 1 | 9 | 0.91667 | 20 | 68 | 24.7253 |  |  |  | 68
1995-09-01 | 1 | 9 | 0.95833 | 18.9 | 66.02 | 24.1304 |  |  |  | 66.02
1995-09-01 | 1 | 9 | 1 | 18.3 | 64.94 | 23.5586 |  |  |  | 64.94
1995-09-02 | 2 | 9 | 0.041667 | 17.2 | 62.96 | 23.0742 |  |  |  | 62.96
1995-09-02 | 2 | 9 | 0.083333 | 16.7 | 62.06 | 22.8639 |  |  |  | 62.06
1995-09-02 | 2 | 9 | 0.125 | 16.1 | 60.98 | 22.5492 |  |  |  | 60.98
1995-09-02 | 2 | 9 | 0.16667 | 16.1 | 60.98 | 22.5492 |  |  |  | 60.98
1995-09-02 | 2 | 9 | 0.20833 | 15.6 | 60.08 | 22.4417 |  |  |  | 60.08
1995-09-02 | 2 | 9 | 0.25 | 15.6 | 60.08 | 22.4417 |  |  | 60.08
1995-09-02 | 2 | 9 | 0.29167 | 16.1 | 60.98 | 22.2991 |  |  | 60.98
1995-09-02 | 2 | 9 | 0.33333 | 17.8 | 64.04 | 23.0902 |  |  | 64.04
1995-09-02 | 2 | 9 | 0.375 | 18.3 | 64.94 | 23.5586 |  |  | 64.94
1995-09-02 | 2 | 9 | 0.41667 | 19.4 | 66.92 | 23.8427 |  |  | 66.92
1995-09-02 | 2 | 9 | 0.45833 | 20 | 68 | 24.0837 |  |  | 68
1995-09-02 | 2 | 9 | 0.5 | 21.1 | 69.98 | 23.916 |  |  | 69.98
1995-09-02 | 2 | 9 | 0.54167 | 21.1 | 69.98 | 23.7447 |  |  | 69.98
1995-09-02 | 2 | 9 | 0.58333 | 22.2 | 71.96 | 24.1646 |  |  | 71.96
1995-09-02 | 2 | 9 | 0.625 | 22.8 | 73.04 | 24.4954 |  |  | 73.04
1995-09-02 | 2 | 9 | 0.66667 | 22.2 | 71.96 | 26.0021 |  |  | 71.96
1995-09-02 | 2 | 9 | 0.70833 | 21.7 | 71.06 | 26.0533 |  |  | 71.06
1995-09-02 | 2 | 9 | 0.75 | 21.1 | 69.98 | 25.8057 |  |  | 69.98
1995-09-02 | 2 | 9 | 0.79167 | 20.6 | 69.08 | 25.3099 |  |  | 69.08
1995-09-02 | 2 | 9 | 0.83333 | 20 | 68 | 25.0466 |  |  | 68
1995-09-02 | 2 | 9 | 0.875 | 19.4 | 66.92 | 25.0796 |  |  | 66.92
1995-09-02 | 2 | 9 | 0.91667 | 19.4 | 66.92 | 25.3896 |  |  |  | 66.92
1995-09-02 | 2 | 9 | 0.95833 | 19.4 | 66.92 | 25.6998 |  |  |  | 66.92
1995-09-02 | 2 | 9 | 1 | 18.9 | 66.02 | 25.481 |  |  |  | 66.02
1995-09-03 | 3 | 9 | 0.041667 | 19.4 | 66.92 | 26.1656 |  |  |  | 66.92
1995-09-03 | 3 | 9 | 0.083333 | 18.9 | 66.02 | 25.9323 |  |  |  | 66.02
1995-09-03 | 3 | 9 | 0.125 | 18.9 | 66.02 | 26.2336 |  |  |  | 66.02
1995-09-03 | 3 | 9 | 0.16667 | 18.9 | 66.02 | 26.6859 |  |  |  | 66.02
1995-09-03 | 3 | 9 | 0.20833 | 18.3 | 64.94 | 26.0162 |  |  |  | 64.94
1995-09-03 | 3 | 9 | 0.25 | 18.3 | 64.94 | 26.4517 |  |  | 64.94
1995-09-03 | 3 | 9 | 0.29167 | 18.9 | 66.02 | 26.9878 |  |  | 66.02
1995-09-03 | 3 | 9 | 0.33333 | 20 | 68 | 27.9515 |  |  | 68
1995-09-03 | 3 | 9 | 0.375 | 21.7 | 71.06 | 27.8458 |  |  | 71.06
1995-09-03 | 3 | 9 | 0.41667 | 23.3 | 73.94 | 26.7008 |  |  | 73.94
1995-09-03 | 3 | 9 | 0.45833 | 24.4 | 75.92 | 27.5936 |  |  | 75.92
1995-09-03 | 3 | 9 | 0.5 | 23.9 | 75.02 | 27.7081 |  |  | 75.02
1995-09-03 | 3 | 9 | 0.54167 | 25 | 77 | 28.6426 |  |  | 77
1995-09-03 | 3 | 9 | 0.58333 | 25 | 77 | 27.7659 |  |  | 77
1995-09-03 | 3 | 9 | 0.625 | 25 | 77 | 28.204 |  |  | 77
1995-09-03 | 3 | 9 | 0.66667 | 24.4 | 75.92 | 28.2276 |  |  | 75.92
1995-09-03 | 3 | 9 | 0.70833 | 23.3 | 73.94 | 27.8863 |  |  | 73.94
1995-09-03 | 3 | 9 | 0.75 | 22.2 | 71.96 | 26.9246 |  |  | 71.96
1995-09-03 | 3 | 9 | 0.79167 | 21.7 | 71.06 | 27.4866 |  |  | 71.06
1995-09-03 | 3 | 9 | 0.83333 | 21.7 | 71.06 | 28.2055 |  |  | 71.06
1995-09-03 | 3 | 9 | 0.875 | 21.1 | 69.98 | 29.2683 |  |  | 69.98
1995-09-03 | 3 | 9 | 0.91667 | 21.1 | 69.98 | 29.2683 |  |  |  | 69.98
1995-09-03 | 3 | 9 | 0.95833 | 21.1 | 69.98 | 28.9205 |  |  |  | 69.98
1995-09-03 | 3 | 9 | 1 | 21.1 | 69.98 | 28.9205 |  |  |  | 69.98
1995-09-04 | 4 | 9 | 0.041667 | 20.6 | 69.08 | 29.0003 |  |  |  | 69.08
1995-09-04 | 4 | 9 | 0.083333 | 20.6 | 69.08 | 29.5066 |  |  |  | 69.08
1995-09-04 | 4 | 9 | 0.125 | 20.6 | 69.08 | 30.0137 |  |  |  | 69.08
1995-09-04 | 4 | 9 | 0.16667 | 20.6 | 69.08 | 30.0137 |  |  |  | 69.08
1995-09-04 | 4 | 9 | 0.20833 | 20.6 | 69.08 | 30.0137 |  |  |  | 69.08
1995-09-04 | 4 | 9 | 0.25 | 21.1 | 69.98 | 30.6631 |  |  | 69.98
1995-09-04 | 4 | 9 | 0.29167 | 21.7 | 71.06 | 31.096 |  |  | 71.06
1995-09-04 | 4 | 9 | 0.33333 | 23.3 | 73.94 | 32.2682 |  |  | 73.94
1995-09-04 | 4 | 9 | 0.375 | 25 | 77 | 32.8375 |  |  | 77
1995-09-04 | 4 | 9 | 0.41667 | 25.6 | 78.08 | 33.1753 |  |  | 78.08
1995-09-04 | 4 | 9 | 0.45833 | 25.6 | 78.08 | 33.867 |  |  | 78.08
1995-09-04 | 4 | 9 | 0.5 | 23 | 73.4 | 33.6432 |  |  | 73.4
1995-09-04 | 4 | 9 | 0.54167 | 24.4 | 75.92 | 35.4956 |  |  | 75.92
1995-09-04 | 4 | 9 | 0.58333 | 25.6 | 78.08 | 34.7915 |  |  | 78.08
1995-09-04 | 4 | 9 | 0.625 | 26.1 | 78.98 | 34.5538 |  |  | 78.98
1995-09-04 | 4 | 9 | 0.66667 | 25.6 | 78.08 | 34.7915 |  |  | 78.08
1995-09-04 | 4 | 9 | 0.70833 | 26.1 | 78.98 | 36.2248 |  |  | 78.98
1995-09-04 | 4 | 9 | 0.75 | 25.6 | 78.08 | 35.4864 |  |  | 78.08
1995-09-04 | 4 | 9 | 0.79167 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1995-09-04 | 4 | 9 | 0.83333 | 23.9 | 75.02 | 31.0043 |  |  | 75.02
1995-09-04 | 4 | 9 | 0.875 | 24.4 | 75.92 | 32.2704 |  |  | 75.92
1995-09-04 | 4 | 9 | 0.91667 | 23.3 | 73.94 | 31.6674 |  |  |  | 73.94
1995-09-04 | 4 | 9 | 0.95833 | 23.3 | 73.94 | 31.2674 |  |  |  | 73.94
1995-09-04 | 4 | 9 | 1 | 22.8 | 73.04 | 30.0556 |  |  |  | 73.04
1995-09-05 | 5 | 9 | 0.041667 | 21.7 | 71.06 | 28.7456 |  |  |  | 71.06
1995-09-05 | 5 | 9 | 0.083333 | 21.1 | 69.98 | 28.0524 |  |  |  | 69.98
1995-09-05 | 5 | 9 | 0.125 | 20.6 | 69.08 | 27.8218 |  |  |  | 69.08
1995-09-05 | 5 | 9 | 0.16667 | 20 | 68 | 27.4656 |  |  |  | 68
1995-09-05 | 5 | 9 | 0.20833 | 19.4 | 66.92 | 27.7229 |  |  |  | 66.92
1995-09-05 | 5 | 9 | 0.25 | 18.9 | 66.02 | 26.9878 |  |  | 66.02
1995-09-05 | 5 | 9 | 0.29167 | 19.4 | 66.92 | 27.255 |  |  | 66.92
1995-09-05 | 5 | 9 | 0.33333 | 21.1 | 69.98 | 28.0524 |  |  | 69.98
1995-09-05 | 5 | 9 | 0.375 | 20.6 | 69.08 | 27.318 |  |  | 69.08
1995-09-05 | 5 | 9 | 0.41667 | 20.6 | 69.08 | 26.6473 |  |  | 69.08
1995-09-05 | 5 | 9 | 0.45833 | 21.7 | 71.06 | 26.7692 |  |  | 71.06
1995-09-05 | 5 | 9 | 0.5 | 22.2 | 71.96 | 27.2943 |  |  | 71.96
1995-09-05 | 5 | 9 | 0.54167 | 22.8 | 73.04 | 27.552 |  |  | 73.04
1995-09-05 | 5 | 9 | 0.58333 | 23.9 | 75.02 | 27.2983 |  |  | 75.02
1995-09-05 | 5 | 9 | 0.625 | 25 | 77 | 27.1099 |  |  | 77
1995-09-05 | 5 | 9 | 0.66667 | 25 | 77 | 26.4551 |  |  | 77
1995-09-05 | 5 | 9 | 0.70833 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1995-09-05 | 5 | 9 | 0.75 | 23.9 | 75.02 | 26.2758 |  |  | 75.02
1995-09-05 | 5 | 9 | 0.79167 | 23.3 | 73.94 | 26.1096 |  |  | 73.94
1995-09-05 | 5 | 9 | 0.83333 | 22.2 | 71.96 | 26.0021 |  |  | 71.96
1995-09-05 | 5 | 9 | 0.875 | 22.2 | 71.96 | 25.0821 |  |  | 71.96
1995-09-05 | 5 | 9 | 0.91667 | 21.1 | 69.98 | 24.7736 |  |  |  | 69.98
1995-09-05 | 5 | 9 | 0.95833 | 20.6 | 69.08 | 24.9764 |  |  |  | 69.08
1995-09-05 | 5 | 9 | 1 | 20 | 68 | 23.4433 |  |  |  | 68
1995-09-06 | 6 | 9 | 0.041667 | 20 | 68 | 23.7633 |  |  |  | 68
1995-09-06 | 6 | 9 | 0.083333 | 19.4 | 66.92 | 23.9971 |  |  |  | 66.92
1995-09-06 | 6 | 9 | 0.125 | 18.3 | 64.94 | 24.2796 |  |  |  | 64.94
1995-09-06 | 6 | 9 | 0.16667 | 18.3 | 64.94 | 23.8468 |  |  |  | 64.94
1995-09-06 | 6 | 9 | 0.20833 | 16.7 | 62.06 | 23.5148 |  |  |  | 62.06
1995-09-06 | 6 | 9 | 0.25 | 16.7 | 62.06 | 23.2543 |  |  | 62.06
1995-09-06 | 6 | 9 | 0.29167 | 17.2 | 62.96 | 23.7463 |  |  | 62.96
1995-09-06 | 6 | 9 | 0.33333 | 18.3 | 64.94 | 24.8575 |  |  | 64.94
1995-09-06 | 6 | 9 | 0.375 | 20 | 68 | 26.0121 |  |  | 68
1995-09-06 | 6 | 9 | 0.41667 | 20.6 | 69.08 | 25.3099 |  |  | 69.08
1995-09-06 | 6 | 9 | 0.45833 | 22.2 | 71.96 | 25.6338 |  |  | 71.96
1995-09-06 | 6 | 9 | 0.5 | 22.8 | 73.04 | 25.8293 |  |  | 73.04
1995-09-06 | 6 | 9 | 0.54167 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1995-09-06 | 6 | 9 | 0.58333 | 25.6 | 78.08 | 26.7849 |  |  | 78.08
1995-09-06 | 6 | 9 | 0.625 | 26.1 | 78.98 | 27.949 |  |  | 78.98
1995-09-06 | 6 | 9 | 0.66667 | 25.6 | 78.08 | 29.2814 |  |  | 78.08
1995-09-06 | 6 | 9 | 0.70833 | 24.4 | 75.92 | 28.2276 |  |  | 75.92
1995-09-06 | 6 | 9 | 0.75 | 23.3 | 73.94 | 28.4806 |  |  | 73.94
1995-09-06 | 6 | 9 | 0.79167 | 22.2 | 71.96 | 28.9628 |  |  | 71.96
1995-09-06 | 6 | 9 | 0.83333 | 21.7 | 71.06 | 29.1062 |  |  | 71.06
1995-09-06 | 6 | 9 | 0.875 | 21.7 | 71.06 | 29.1062 |  |  | 71.06
1995-09-06 | 6 | 9 | 0.91667 | 21.7 | 71.06 | 29.4671 |  |  |  | 71.06
1995-09-06 | 6 | 9 | 0.95833 | 21.7 | 71.06 | 29.4671 |  |  |  | 71.06
1995-09-06 | 6 | 9 | 1 | 21.1 | 69.98 | 29.2683 |  |  |  | 69.98
1995-09-07 | 7 | 9 | 0.041667 | 21.1 | 69.98 | 29.2683 |  |  |  | 69.98
1995-09-07 | 7 | 9 | 0.083333 | 20.6 | 69.08 | 29.0003 |  |  |  | 69.08
1995-09-07 | 7 | 9 | 0.125 | 20 | 68 | 28.7628 |  |  |  | 68
1995-09-07 | 7 | 9 | 0.16667 | 20 | 68 | 27.9515 |  |  |  | 68
1995-09-07 | 7 | 9 | 0.20833 | 20 | 68 | 27.1421 |  |  |  | 68
1995-09-07 | 7 | 9 | 0.25 | 20 | 68 | 27.1421 |  |  | 68
1995-09-07 | 7 | 9 | 0.29167 | 21.1 | 69.98 | 27.5326 |  |  | 69.98
1995-09-07 | 7 | 9 | 0.33333 | 22.8 | 73.04 | 27.552 |  |  | 73.04
1995-09-07 | 7 | 9 | 0.375 | 24.4 | 75.92 | 27.8048 |  |  | 75.92
1995-09-07 | 7 | 9 | 0.41667 | 26.1 | 78.98 | 28.4166 |  |  | 78.98
1995-09-07 | 7 | 9 | 0.45833 | 26.7 | 80.06 | 28.2984 |  |  | 80.06
1995-09-07 | 7 | 9 | 0.5 | 28.3 | 82.94 | 28.5731 |  |  | 82.94
1995-09-07 | 7 | 9 | 0.54167 | 27.8 | 82.04 | 29.3949 |  |  | 82.04
1995-09-07 | 7 | 9 | 0.58333 | 29.4 | 84.92 | 30.2022 |  |  | 84.92
1995-09-07 | 7 | 9 | 0.625 | 27.8 | 82.04 | 32.256 |  |  | 82.04
1995-09-07 | 7 | 9 | 0.66667 | 27.2 | 80.96 | 33.3171 |  |  | 80.96
1995-09-07 | 7 | 9 | 0.70833 | 26.1 | 78.98 | 32.8908 |  |  | 78.98
1995-09-07 | 7 | 9 | 0.75 | 25 | 77 | 32.8375 |  |  | 77
1995-09-07 | 7 | 9 | 0.79167 | 24.4 | 75.92 | 33.1275 |  |  | 75.92
1995-09-07 | 7 | 9 | 0.83333 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1995-09-07 | 7 | 9 | 0.875 | 23.9 | 75.02 | 32.0408 |  |  | 75.02
1995-09-07 | 7 | 9 | 0.91667 | 22.8 | 73.04 | 31.0233 |  |  |  | 73.04
1995-09-07 | 7 | 9 | 0.95833 | 22.2 | 71.96 | 31.2 |  |  |  | 71.96
1995-09-07 | 7 | 9 | 1 | 21.7 | 71.06 | 30.0092 |  |  |  | 71.06
1995-09-08 | 8 | 9 | 0.041667 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-08 | 8 | 9 | 0.083333 | 21.1 | 69.98 | 30.6631 |  |  |  | 69.98
1995-09-08 | 8 | 9 | 0.125 | 20.6 | 69.08 | 30.5215 |  |  |  | 69.08
1995-09-08 | 8 | 9 | 0.16667 | 20.6 | 69.08 | 30.5215 |  |  |  | 69.08
1995-09-08 | 8 | 9 | 0.20833 | 20 | 68 | 30.2279 |  |  |  | 68
1995-09-08 | 8 | 9 | 0.25 | 20 | 68 | 30.7176 |  |  | 68
1995-09-08 | 8 | 9 | 0.29167 | 20.6 | 69.08 | 31.03 |  |  | 69.08
1995-09-08 | 8 | 9 | 0.33333 | 21.7 | 71.06 | 32.0043 |  |  | 71.06
1995-09-08 | 8 | 9 | 0.375 | 23.3 | 73.94 | 32.6693 |  |  | 73.94
1995-09-08 | 8 | 9 | 0.41667 | 23.9 | 75.02 | 33.0805 |  |  | 75.02
1995-09-08 | 8 | 9 | 0.45833 | 24.4 | 75.92 | 32.6987 |  |  | 75.92
1995-09-08 | 8 | 9 | 0.5 | 26.1 | 78.98 | 33.3652 |  |  | 78.98
1995-09-08 | 8 | 9 | 0.54167 | 27.2 | 80.96 | 33.8235 |  |  | 80.96
1995-09-08 | 8 | 9 | 0.58333 | 27.2 | 80.96 | 34.8385 |  |  | 80.96
1995-09-08 | 8 | 9 | 0.625 | 27.8 | 82.04 | 34.6146 |  |  | 82.04
1995-09-08 | 8 | 9 | 0.66667 | 27.2 | 80.96 | 34.5845 |  |  | 80.96
1995-09-08 | 8 | 9 | 0.70833 | 26.1 | 78.98 | 34.5538 |  |  | 78.98
1995-09-08 | 8 | 9 | 0.75 | 25 | 77 | 33.9499 |  |  | 77
1995-09-08 | 8 | 9 | 0.79167 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1995-09-08 | 8 | 9 | 0.83333 | 23.9 | 75.02 | 34.1232 |  |  | 75.02
1995-09-08 | 8 | 9 | 0.875 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-08 | 8 | 9 | 0.91667 | 23.9 | 75.02 | 33.0805 |  |  |  | 75.02
1995-09-08 | 8 | 9 | 0.95833 | 23.3 | 73.94 | 32.6693 |  |  |  | 73.94
1995-09-08 | 8 | 9 | 1 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
1995-09-09 | 9 | 9 | 0.041667 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
1995-09-09 | 9 | 9 | 0.083333 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
1995-09-09 | 9 | 9 | 0.125 | 22.8 | 73.04 | 32.5774 |  |  |  | 73.04
1995-09-09 | 9 | 9 | 0.16667 | 22.8 | 73.04 | 32.967 |  |  |  | 73.04
1995-09-09 | 9 | 9 | 0.20833 | 22.2 | 71.96 | 32.3241 |  |  |  | 71.96
1995-09-09 | 9 | 9 | 0.25 | 22.2 | 71.96 | 32.3241 |  |  | 71.96
1995-09-09 | 9 | 9 | 0.29167 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1995-09-09 | 9 | 9 | 0.33333 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-09 | 9 | 9 | 0.375 | 25 | 77 | 33.5046 |  |  | 77
1995-09-09 | 9 | 9 | 0.41667 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
1995-09-09 | 9 | 9 | 0.45833 | 27.2 | 80.96 | 32.5588 |  |  | 80.96
1995-09-09 | 9 | 9 | 0.5 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
1995-09-09 | 9 | 9 | 0.54167 | 27.8 | 82.04 | 34.0891 |  |  | 82.04
1995-09-09 | 9 | 9 | 0.58333 | 27.2 | 80.96 | 33.3171 |  |  | 80.96
1995-09-09 | 9 | 9 | 0.625 | 27.2 | 80.96 | 32.8114 |  |  | 80.96
1995-09-09 | 9 | 9 | 0.66667 | 26.7 | 80.06 | 33.1773 |  |  | 80.06
1995-09-09 | 9 | 9 | 0.70833 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
1995-09-09 | 9 | 9 | 0.75 | 25 | 77 | 32.8375 |  |  | 77
1995-09-09 | 9 | 9 | 0.79167 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1995-09-09 | 9 | 9 | 0.83333 | 24.4 | 75.92 | 34.8482 |  |  | 75.92
1995-09-09 | 9 | 9 | 0.875 | 23.9 | 75.02 | 34.7504 |  |  | 75.02
1995-09-09 | 9 | 9 | 0.91667 | 24.4 | 75.92 | 34.2019 |  |  |  | 75.92
1995-09-09 | 9 | 9 | 0.95833 | 23.9 | 75.02 | 34.7504 |  |  |  | 75.02
1995-09-09 | 9 | 9 | 1 | 23.3 | 73.94 | 34.8837 |  |  |  | 73.94
1995-09-10 | 10 | 9 | 0.041667 | 22.8 | 73.04 | 34.7256 |  |  |  | 73.04
1995-09-10 | 10 | 9 | 0.083333 | 22.8 | 73.04 | 34.7256 |  |  |  | 73.04
1995-09-10 | 10 | 9 | 0.125 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1995-09-10 | 10 | 9 | 0.16667 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1995-09-10 | 10 | 9 | 0.20833 | 23.3 | 73.94 | 35.6924 |  |  |  | 73.94
1995-09-10 | 10 | 9 | 0.25 | 23.3 | 73.94 | 35.6924 |  |  | 73.94
1995-09-10 | 10 | 9 | 0.29167 | 23.9 | 75.02 | 36.4283 |  |  | 75.02
1995-09-10 | 10 | 9 | 0.33333 | 25.6 | 78.08 | 37.3463 |  |  | 78.08
1995-09-10 | 10 | 9 | 0.375 | 26.1 | 78.98 | 36.9434 |  |  | 78.98
1995-09-10 | 10 | 9 | 0.41667 | 26.1 | 78.98 | 36.9434 |  |  | 78.98
1995-09-10 | 10 | 9 | 0.45833 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
1995-09-10 | 10 | 9 | 0.5 | 28.3 | 82.94 | 37.7364 |  |  | 82.94
1995-09-10 | 10 | 9 | 0.54167 | 27.8 | 82.04 | 37.5191 |  |  | 82.04
1995-09-10 | 10 | 9 | 0.58333 | 27.8 | 82.04 | 36.9892 |  |  | 82.04
1995-09-10 | 10 | 9 | 0.625 | 26.1 | 78.98 | 38.8669 |  |  | 78.98
1995-09-10 | 10 | 9 | 0.66667 | 25.6 | 78.08 | 37.3463 |  |  | 78.08
1995-09-10 | 10 | 9 | 0.70833 | 24.4 | 75.92 | 37.4451 |  |  | 75.92
1995-09-10 | 10 | 9 | 0.75 | 24.4 | 75.92 | 37.4451 |  |  | 75.92
1995-09-10 | 10 | 9 | 0.79167 | 23.3 | 73.94 | 36.3002 |  |  | 73.94
1995-09-10 | 10 | 9 | 0.83333 | 23 | 73.4 | 32.6564 |  |  | 73.4
1995-09-10 | 10 | 9 | 0.875 | 22.8 | 73.04 | 32.967 |  |  | 73.04
1995-09-10 | 10 | 9 | 0.91667 | 22.2 | 71.96 | 31.2 |  |  |  | 71.96
1995-09-10 | 10 | 9 | 0.95833 | 21.7 | 71.06 | 30.0092 |  |  |  | 71.06
1995-09-10 | 10 | 9 | 1 | 21.7 | 71.06 | 30.0092 |  |  |  | 71.06
1995-09-11 | 11 | 9 | 0.041667 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-11 | 11 | 9 | 0.083333 | 20.6 | 69.08 | 29.0003 |  |  |  | 69.08
1995-09-11 | 11 | 9 | 0.125 | 20 | 68 | 28.438 |  |  |  | 68
1995-09-11 | 11 | 9 | 0.16667 | 20.6 | 69.08 | 28.1581 |  |  |  | 69.08
1995-09-11 | 11 | 9 | 0.20833 | 19.4 | 66.92 | 27.255 |  |  |  | 66.92
1995-09-11 | 11 | 9 | 0.25 | 19.4 | 66.92 | 27.255 |  |  | 66.92
1995-09-11 | 11 | 9 | 0.29167 | 19.4 | 66.92 | 26.7877 |  |  | 66.92
1995-09-11 | 11 | 9 | 0.33333 | 20 | 68 | 27.1421 |  |  | 68
1995-09-11 | 11 | 9 | 0.375 | 22.2 | 71.96 | 27.6644 |  |  | 71.96
1995-09-11 | 11 | 9 | 0.41667 | 23.3 | 73.94 | 27.8863 |  |  | 73.94
1995-09-11 | 11 | 9 | 0.45833 | 24.4 | 75.92 | 28.2276 |  |  | 75.92
1995-09-11 | 11 | 9 | 0.5 | 25 | 77 | 28.6426 |  |  | 77
1995-09-11 | 11 | 9 | 0.54167 | 26.1 | 78.98 | 29.1192 |  |  | 78.98
1995-09-11 | 11 | 9 | 0.58333 | 26.1 | 78.98 | 29.1192 |  |  | 78.98
1995-09-11 | 11 | 9 | 0.625 | 26.7 | 80.06 | 29.0259 |  |  | 80.06
1995-09-11 | 11 | 9 | 0.66667 | 27.2 | 80.96 | 28.7923 |  |  | 80.96
1995-09-11 | 11 | 9 | 0.70833 | 26.7 | 80.06 | 29.2687 |  |  | 80.06
1995-09-11 | 11 | 9 | 0.75 | 26.1 | 78.98 | 28.6507 |  |  | 78.98
1995-09-11 | 11 | 9 | 0.79167 | 25.6 | 78.08 | 28.1444 |  |  | 78.08
1995-09-11 | 11 | 9 | 0.83333 | 24.4 | 75.92 | 27.1715 |  |  | 75.92
1995-09-11 | 11 | 9 | 0.875 | 23.3 | 73.94 | 26.7008 |  |  | 73.94
1995-09-11 | 11 | 9 | 0.91667 | 22.8 | 73.04 | 26.5939 |  |  |  | 73.04
1995-09-11 | 11 | 9 | 0.95833 | 21.7 | 71.06 | 26.0533 |  |  |  | 71.06
1995-09-11 | 11 | 9 | 1 | 21.1 | 69.98 | 25.4613 |  |  |  | 69.98
1995-09-12 | 12 | 9 | 0.041667 | 20 | 68 | 25.0466 |  |  |  | 68
1995-09-12 | 12 | 9 | 0.083333 | 19.4 | 66.92 | 24.77 |  |  |  | 66.92
1995-09-12 | 12 | 9 | 0.125 | 18.9 | 66.02 | 24.1304 |  |  |  | 66.02
1995-09-12 | 12 | 9 | 0.16667 | 18.3 | 64.94 | 24.2796 |  |  |  | 64.94
1995-09-12 | 12 | 9 | 0.20833 | 17.8 | 64.04 | 24.0676 |  |  |  | 64.04
1995-09-12 | 12 | 9 | 0.25 | 17.8 | 64.04 | 24.0676 |  |  | 64.04
1995-09-12 | 12 | 9 | 0.29167 | 18.3 | 64.94 | 24.8575 |  |  | 64.94
1995-09-12 | 12 | 9 | 0.33333 | 20 | 68 | 26.0121 |  |  | 68
1995-09-12 | 12 | 9 | 0.375 | 21.1 | 69.98 | 26.8408 |  |  | 69.98
1995-09-12 | 12 | 9 | 0.41667 | 21.7 | 71.06 | 26.7692 |  |  | 71.06
1995-09-12 | 12 | 9 | 0.45833 | 22.8 | 73.04 | 25.8293 |  |  | 73.04
1995-09-12 | 12 | 9 | 0.5 | 23.3 | 73.94 | 26.1096 |  |  | 73.94
1995-09-12 | 12 | 9 | 0.54167 | 24.4 | 75.92 | 26.329 |  |  | 75.92
1995-09-12 | 12 | 9 | 0.58333 | 25 | 77 | 26.4551 |  |  | 77
1995-09-12 | 12 | 9 | 0.625 | 25 | 77 | 26.4551 |  |  | 77
1995-09-12 | 12 | 9 | 0.66667 | 24.4 | 75.92 | 26.9607 |  |  | 75.92
1995-09-12 | 12 | 9 | 0.70833 | 23.3 | 73.94 | 26.1096 |  |  | 73.94
1995-09-12 | 12 | 9 | 0.75 | 22.8 | 73.04 | 25.8293 |  |  | 73.04
1995-09-12 | 12 | 9 | 0.79167 | 21.7 | 71.06 | 26.7692 |  |  | 71.06
1995-09-12 | 12 | 9 | 0.83333 | 21.7 | 71.06 | 26.7692 |  |  | 71.06
1995-09-12 | 12 | 9 | 0.875 | 21.7 | 71.06 | 26.0533 |  |  | 71.06
1995-09-12 | 12 | 9 | 0.91667 | 21.1 | 69.98 | 25.8057 |  |  |  | 69.98
1995-09-12 | 12 | 9 | 0.95833 | 20.6 | 69.08 | 25.4768 |  |  |  | 69.08
1995-09-12 | 12 | 9 | 1 | 20.6 | 69.08 | 26.3125 |  |  |  | 69.08
1995-09-13 | 13 | 9 | 0.041667 | 20 | 68 | 26.0121 |  |  |  | 68
1995-09-13 | 13 | 9 | 0.083333 | 20 | 68 | 26.3346 |  |  |  | 68
1995-09-13 | 13 | 9 | 0.125 | 19.4 | 66.92 | 26.4765 |  |  |  | 66.92
1995-09-13 | 13 | 9 | 0.16667 | 19.4 | 66.92 | 27.255 |  |  |  | 66.92
1995-09-13 | 13 | 9 | 0.20833 | 19.4 | 66.92 | 27.255 |  |  |  | 66.92
1995-09-13 | 13 | 9 | 0.25 | 18.9 | 66.02 | 26.9878 |  |  | 66.02
1995-09-13 | 13 | 9 | 0.29167 | 20 | 68 | 27.4656 |  |  | 68
1995-09-13 | 13 | 9 | 0.33333 | 21.7 | 71.06 | 27.4866 |  |  | 71.06
1995-09-13 | 13 | 9 | 0.375 | 23.3 | 73.94 | 28.0843 |  |  | 73.94
1995-09-13 | 13 | 9 | 0.41667 | 25 | 77 | 28.6426 |  |  | 77
1995-09-13 | 13 | 9 | 0.45833 | 26.7 | 80.06 | 29.7549 |  |  | 80.06
1995-09-13 | 13 | 9 | 0.5 | 27.2 | 80.96 | 29.7927 |  |  | 80.96
1995-09-13 | 13 | 9 | 0.54167 | 28.9 | 84.02 | 30.2521 |  |  | 84.02
1995-09-13 | 13 | 9 | 0.58333 | 29.4 | 84.92 | 31.3427 |  |  | 84.92
1995-09-13 | 13 | 9 | 0.625 | 29.4 | 84.92 | 31.3427 |  |  | 84.92
1995-09-13 | 13 | 9 | 0.66667 | 27.8 | 82.04 | 33.8266 |  |  | 82.04
1995-09-13 | 13 | 9 | 0.70833 | 26.7 | 80.06 | 33.669 |  |  | 80.06
1995-09-13 | 13 | 9 | 0.75 | 25.6 | 78.08 | 32.7149 |  |  | 78.08
1995-09-13 | 13 | 9 | 0.79167 | 25 | 77 | 32.8375 |  |  | 77
1995-09-13 | 13 | 9 | 0.83333 | 25 | 77 | 32.8375 |  |  | 77
1995-09-13 | 13 | 9 | 0.875 | 25.6 | 78.08 | 31.3374 |  |  | 78.08
1995-09-13 | 13 | 9 | 0.91667 | 23.9 | 75.02 | 32.0408 |  |  |  | 75.02
1995-09-13 | 13 | 9 | 0.95833 | 22.2 | 71.96 | 29.7069 |  |  |  | 71.96
1995-09-13 | 13 | 9 | 1 | 21.7 | 71.06 | 27.8458 |  |  |  | 71.06
1995-09-14 | 14 | 9 | 0.041667 | 17.2 | 62.96 | 26.7193 |  |  |  | 62.96
1995-09-14 | 14 | 9 | 0.083333 | 16.7 | 62.06 | 26.5249 |  |  |  | 62.06
1995-09-14 | 14 | 9 | 0.125 | 15 | 59 | 25.2653 |  |  |  | 59
1995-09-14 | 14 | 9 | 0.16667 | 15 | 59 | 24.9127 |  |  |  | 59
1995-09-14 | 14 | 9 | 0.20833 | 15.6 | 60.08 | 24.7515 |  |  |  | 60.08
1995-09-14 | 14 | 9 | 0.25 | 15 | 59 | 24.9127 |  |  | 59
1995-09-14 | 14 | 9 | 0.29167 | 13.9 | 57.02 | 23.68 |  |  | 57.02
1995-09-14 | 14 | 9 | 0.33333 | 13.3 | 55.94 | 23.0282 |  |  | 55.94
1995-09-14 | 14 | 9 | 0.375 | 12.8 | 55.04 | 22.4956 |  |  | 55.04
1995-09-14 | 14 | 9 | 0.41667 | 12.8 | 55.04 | 22.4956 |  |  | 55.04
1995-09-14 | 14 | 9 | 0.45833 | 13.3 | 55.94 | 22.4004 |  |  | 55.94
1995-09-14 | 14 | 9 | 0.5 | 13.3 | 55.94 | 22.4004 |  |  | 55.94
1995-09-14 | 14 | 9 | 0.54167 | 13.3 | 55.94 | 22.4004 |  |  | 55.94
1995-09-14 | 14 | 9 | 0.58333 | 13.9 | 57.02 | 22.5911 |  |  | 57.02
1995-09-14 | 14 | 9 | 0.625 | 13.9 | 57.02 | 22.2651 |  |  | 57.02
1995-09-14 | 14 | 9 | 0.66667 | 14.4 | 57.92 | 22.5462 |  |  | 57.92
1995-09-14 | 14 | 9 | 0.70833 | 15.6 | 60.08 | 22.6841 |  |  | 60.08
1995-09-14 | 14 | 9 | 0.75 | 15.6 | 60.08 | 23.0481 |  |  | 60.08
1995-09-14 | 14 | 9 | 0.79167 | 15 | 59 | 23.0385 |  |  | 59
1995-09-14 | 14 | 9 | 0.83333 | 14.4 | 57.92 | 22.8831 |  |  | 57.92
1995-09-14 | 14 | 9 | 0.875 | 14.4 | 57.92 | 22.8831 |  |  | 57.92
1995-09-14 | 14 | 9 | 0.91667 | 15 | 59 | 23.0385 |  |  |  | 59
1995-09-14 | 14 | 9 | 0.95833 | 15.6 | 60.08 | 22.6841 |  |  |  | 60.08
1995-09-14 | 14 | 9 | 1 | 15.6 | 60.08 | 21.8365 |  |  |  | 60.08
1995-09-15 | 15 | 9 | 0.041667 | 14.4 | 57.92 | 20.5315 |  |  |  | 57.92
1995-09-15 | 15 | 9 | 0.083333 | 13.9 | 57.02 | 19.9917 |  |  |  | 57.02
1995-09-15 | 15 | 9 | 0.125 | 13.9 | 57.02 | 20.856 |  |  |  | 57.02
1995-09-15 | 15 | 9 | 0.16667 | 13.3 | 55.94 | 20.0046 |  |  |  | 55.94
1995-09-15 | 15 | 9 | 0.20833 | 13.3 | 55.94 | 19.7971 |  |  |  | 55.94
1995-09-15 | 15 | 9 | 0.25 | 12.8 | 55.04 | 19.7734 |  |  | 55.04
1995-09-15 | 15 | 9 | 0.29167 | 13.3 | 55.94 | 20.0046 |  |  | 55.94
1995-09-15 | 15 | 9 | 0.33333 | 14.4 | 57.92 | 20.5315 |  |  | 57.92
1995-09-15 | 15 | 9 | 0.375 | 15.6 | 60.08 | 20.9909 |  |  | 60.08
1995-09-15 | 15 | 9 | 0.41667 | 16.7 | 62.06 | 21.3068 |  |  | 62.06
1995-09-15 | 15 | 9 | 0.45833 | 17.8 | 64.04 | 21.2822 |  |  | 64.04
1995-09-15 | 15 | 9 | 0.5 | 18.3 | 64.94 | 21.9777 |  |  | 64.94
1995-09-15 | 15 | 9 | 0.54167 | 18.3 | 64.94 | 22.4081 |  |  | 64.94
1995-09-15 | 15 | 9 | 0.58333 | 19.4 | 66.92 | 22.764 |  |  | 66.92
1995-09-15 | 15 | 9 | 0.625 | 19.4 | 66.92 | 22.764 |  |  | 66.92
1995-09-15 | 15 | 9 | 0.66667 | 20 | 68 | 22.6444 |  |  | 68
1995-09-15 | 15 | 9 | 0.70833 | 19.4 | 66.92 | 22.4565 |  |  | 66.92
1995-09-15 | 15 | 9 | 0.75 | 18.9 | 66.02 | 22.0401 |  |  | 66.02
1995-09-15 | 15 | 9 | 0.79167 | 18.3 | 64.94 | 22.2646 |  |  | 64.94
1995-09-15 | 15 | 9 | 0.83333 | 18.3 | 64.94 | 21.6911 |  |  | 64.94
1995-09-15 | 15 | 9 | 0.875 | 17.2 | 62.96 | 22.5374 |  |  | 62.96
1995-09-15 | 15 | 9 | 0.91667 | 16.7 | 62.06 | 22.6039 |  |  |  | 62.06
1995-09-15 | 15 | 9 | 0.95833 | 17.2 | 62.96 | 22.5374 |  |  |  | 62.96
1995-09-15 | 15 | 9 | 1 | 16.7 | 62.06 | 23.2543 |  |  |  | 62.06
1995-09-16 | 16 | 9 | 0.041667 | 16.1 | 60.98 | 22.5492 |  |  |  | 60.98
1995-09-16 | 16 | 9 | 0.083333 | 16.1 | 60.98 | 22.0492 |  |  |  | 60.98
1995-09-16 | 16 | 9 | 0.125 | 15.6 | 60.08 | 21.5947 |  |  |  | 60.08
1995-09-16 | 16 | 9 | 0.16667 | 15 | 59 | 23.0385 |  |  |  | 59
1995-09-16 | 16 | 9 | 0.20833 | 15 | 59 | 23.0385 |  |  |  | 59
1995-09-16 | 16 | 9 | 0.25 | 14.4 | 57.92 | 21.6493 |  |  | 57.92
1995-09-16 | 16 | 9 | 0.29167 | 15 | 59 | 21.5232 |  |  | 59
1995-09-16 | 16 | 9 | 0.33333 | 15.6 | 60.08 | 20.9909 |  |  | 60.08
1995-09-16 | 16 | 9 | 0.375 | 17.2 | 62.96 | 22.0015 |  |  | 62.96
1995-09-16 | 16 | 9 | 0.41667 | 18.3 | 64.94 | 22.4081 |  |  | 64.94
1995-09-16 | 16 | 9 | 0.45833 | 20 | 68 | 23.1235 |  |  | 68
1995-09-16 | 16 | 9 | 0.5 | 20.6 | 69.08 | 23.9777 |  |  | 69.08
1995-09-16 | 16 | 9 | 0.54167 | 20.6 | 69.08 | 23.8116 |  |  | 69.08
1995-09-16 | 16 | 9 | 0.58333 | 21.7 | 71.06 | 24.448 |  |  | 71.06
1995-09-16 | 16 | 9 | 0.625 | 21.7 | 71.06 | 24.2701 |  |  | 71.06
1995-09-16 | 16 | 9 | 0.66667 | 22.2 | 71.96 | 23.9814 |  |  | 71.96
1995-09-16 | 16 | 9 | 0.70833 | 22.2 | 71.96 | 23.6152 |  |  | 71.96
1995-09-16 | 16 | 9 | 0.75 | 20.6 | 69.08 | 24.9764 |  |  | 69.08
1995-09-16 | 16 | 9 | 0.79167 | 19.4 | 66.92 | 24.77 |  |  | 66.92
1995-09-16 | 16 | 9 | 0.83333 | 19.4 | 66.92 | 24.77 |  |  | 66.92
1995-09-16 | 16 | 9 | 0.875 | 18.9 | 66.02 | 24.8801 |  |  | 66.02
1995-09-16 | 16 | 9 | 0.91667 | 18.9 | 66.02 | 25.1804 |  |  |  | 66.02
1995-09-16 | 16 | 9 | 0.95833 | 18.3 | 64.94 | 24.8575 |  |  |  | 64.94
1995-09-16 | 16 | 9 | 1 | 17.8 | 64.04 | 25.4688 |  |  |  | 64.04
1995-09-17 | 17 | 9 | 0.041667 | 17.8 | 64.04 | 25.7498 |  |  |  | 64.04
1995-09-17 | 17 | 9 | 0.083333 | 17.2 | 62.96 | 25.5 |  |  |  | 62.96
1995-09-17 | 17 | 9 | 0.125 | 17.2 | 62.96 | 25.0945 |  |  |  | 62.96
1995-09-17 | 17 | 9 | 0.16667 | 16.7 | 62.06 | 23.9059 |  |  |  | 62.06
1995-09-17 | 17 | 9 | 0.20833 | 16.7 | 62.06 | 23.2543 |  |  |  | 62.06
1995-09-17 | 17 | 9 | 0.25 | 16.1 | 60.98 | 23.3007 |  |  | 60.98
1995-09-17 | 17 | 9 | 0.29167 | 16.1 | 60.98 | 22.9247 |  |  | 60.98
1995-09-17 | 17 | 9 | 0.33333 | 17.2 | 62.96 | 24.0155 |  |  | 62.96
1995-09-17 | 17 | 9 | 0.375 | 19.4 | 66.92 | 24.77 |  |  | 66.92
1995-09-17 | 17 | 9 | 0.41667 | 20.6 | 69.08 | 24.9764 |  |  | 69.08
1995-09-17 | 17 | 9 | 0.45833 | 21.7 | 71.06 | 25.6959 |  |  | 71.06
1995-09-17 | 17 | 9 | 0.5 | 22.8 | 73.04 | 25.4476 |  |  | 73.04
1995-09-17 | 17 | 9 | 0.54167 | 23.3 | 73.94 | 25.5194 |  |  | 73.94
1995-09-17 | 17 | 9 | 0.58333 | 23.9 | 75.02 | 26.0717 |  |  | 75.02
1995-09-17 | 17 | 9 | 0.625 | 23.9 | 75.02 | 26.2758 |  |  | 75.02
1995-09-17 | 17 | 9 | 0.66667 | 23.9 | 75.02 | 26.0717 |  |  | 75.02
1995-09-17 | 17 | 9 | 0.70833 | 22.8 | 73.04 | 25.4476 |  |  | 73.04
1995-09-17 | 17 | 9 | 0.75 | 21.7 | 71.06 | 26.0533 |  |  | 71.06
1995-09-17 | 17 | 9 | 0.79167 | 20.6 | 69.08 | 26.3125 |  |  | 69.08
1995-09-17 | 17 | 9 | 0.83333 | 20.6 | 69.08 | 26.3125 |  |  | 69.08
1995-09-17 | 17 | 9 | 0.875 | 20 | 68 | 26.3346 |  |  | 68
1995-09-17 | 17 | 9 | 0.91667 | 20 | 68 | 26.0121 |  |  |  | 68
1995-09-17 | 17 | 9 | 0.95833 | 19.4 | 66.92 | 26.1656 |  |  |  | 66.92
1995-09-17 | 17 | 9 | 1 | 19.4 | 66.92 | 26.1656 |  |  |  | 66.92
1995-09-18 | 18 | 9 | 0.041667 | 18.9 | 66.02 | 25.9323 |  |  |  | 66.02
1995-09-18 | 18 | 9 | 0.083333 | 18.9 | 66.02 | 25.9323 |  |  |  | 66.02
1995-09-18 | 18 | 9 | 0.125 | 17.8 | 64.04 | 25.7498 |  |  |  | 64.04
1995-09-18 | 18 | 9 | 0.16667 | 17.8 | 64.04 | 25.7498 |  |  |  | 64.04
1995-09-18 | 18 | 9 | 0.20833 | 18.3 | 64.94 | 25.5812 |  |  |  | 64.94
1995-09-18 | 18 | 9 | 0.25 | 17.8 | 64.04 | 25.0479 |  |  | 64.04
1995-09-18 | 18 | 9 | 0.29167 | 18.3 | 64.94 | 24.8575 |  |  | 64.94
1995-09-18 | 18 | 9 | 0.33333 | 19.4 | 66.92 | 25.3896 |  |  | 66.92
1995-09-18 | 18 | 9 | 0.375 | 20.6 | 69.08 | 26.6473 |  |  | 69.08
1995-09-18 | 18 | 9 | 0.41667 | 22.2 | 71.96 | 27.2943 |  |  | 71.96
1995-09-18 | 18 | 9 | 0.45833 | 23.3 | 73.94 | 28.0843 |  |  | 73.94
1995-09-18 | 18 | 9 | 0.5 | 23.9 | 75.02 | 28.1184 |  |  | 75.02
1995-09-18 | 18 | 9 | 0.54167 | 24.4 | 75.92 | 27.5936 |  |  | 75.92
1995-09-18 | 18 | 9 | 0.58333 | 24.4 | 75.92 | 26.9607 |  |  | 75.92
1995-09-18 | 18 | 9 | 0.625 | 24.4 | 75.92 | 26.329 |  |  | 75.92
1995-09-18 | 18 | 9 | 0.66667 | 24.4 | 75.92 | 26.9607 |  |  | 75.92
1995-09-18 | 18 | 9 | 0.70833 | 24.4 | 75.92 | 26.5394 |  |  | 75.92
1995-09-18 | 18 | 9 | 0.75 | 23.9 | 75.02 | 27.0935 |  |  | 75.02
1995-09-18 | 18 | 9 | 0.79167 | 23.9 | 75.02 | 26.2758 |  |  | 75.02
1995-09-18 | 18 | 9 | 0.83333 | 22.8 | 73.04 | 27.936 |  |  | 73.04
1995-09-18 | 18 | 9 | 0.875 | 22.2 | 71.96 | 27.6644 |  |  | 71.96
1995-09-18 | 18 | 9 | 0.91667 | 21.7 | 71.06 | 27.8458 |  |  |  | 71.06
1995-09-18 | 18 | 9 | 0.95833 | 21.7 | 71.06 | 27.8458 |  |  |  | 71.06
1995-09-18 | 18 | 9 | 1 | 20.6 | 69.08 | 29.5066 |  |  |  | 69.08
1995-09-19 | 19 | 9 | 0.041667 | 20 | 68 | 28.438 |  |  |  | 68
1995-09-19 | 19 | 9 | 0.083333 | 20 | 68 | 26.6574 |  |  |  | 68
1995-09-19 | 19 | 9 | 0.125 | 18.9 | 66.02 | 26.2336 |  |  |  | 66.02
1995-09-19 | 19 | 9 | 0.16667 | 18.3 | 64.94 | 25.5812 |  |  |  | 64.94
1995-09-19 | 19 | 9 | 0.20833 | 17.8 | 64.04 | 25.7498 |  |  |  | 64.04
1995-09-19 | 19 | 9 | 0.25 | 17.8 | 64.04 | 25.7498 |  |  | 64.04
1995-09-19 | 19 | 9 | 0.29167 | 17.8 | 64.04 | 26.1716 |  |  | 64.04
1995-09-19 | 19 | 9 | 0.33333 | 18.9 | 66.02 | 27.8951 |  |  | 66.02
1995-09-19 | 19 | 9 | 0.375 | 20 | 68 | 28.7628 |  |  | 68
1995-09-19 | 19 | 9 | 0.41667 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1995-09-19 | 19 | 9 | 0.45833 | 22.2 | 71.96 | 30.6394 |  |  | 71.96
1995-09-19 | 19 | 9 | 0.5 | 23.9 | 75.02 | 31.0043 |  |  | 75.02
1995-09-19 | 19 | 9 | 0.54167 | 25.6 | 78.08 | 28.8262 |  |  | 78.08
1995-09-19 | 19 | 9 | 0.58333 | 25.6 | 78.08 | 28.3715 |  |  | 78.08
1995-09-19 | 19 | 9 | 0.625 | 24.4 | 75.92 | 27.8048 |  |  | 75.92
1995-09-19 | 19 | 9 | 0.66667 | 23.9 | 75.02 | 28.9405 |  |  | 75.02
1995-09-19 | 19 | 9 | 0.70833 | 22.8 | 73.04 | 27.552 |  |  | 73.04
1995-09-19 | 19 | 9 | 0.75 | 22.2 | 71.96 | 29.3347 |  |  | 71.96
1995-09-19 | 19 | 9 | 0.79167 | 21.7 | 71.06 | 29.4671 |  |  | 71.06
1995-09-19 | 19 | 9 | 0.83333 | 21.1 | 69.98 | 29.7907 |  |  | 69.98
1995-09-19 | 19 | 9 | 0.875 | 21.1 | 69.98 | 30.1394 |  |  | 69.98
1995-09-19 | 19 | 9 | 0.91667 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-19 | 19 | 9 | 0.95833 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-19 | 19 | 9 | 1 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-20 | 20 | 9 | 0.041667 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-20 | 20 | 9 | 0.083333 | 21.1 | 69.98 | 30.1394 |  |  |  | 69.98
1995-09-20 | 20 | 9 | 0.125 | 21.1 | 69.98 | 30.6631 |  |  |  | 69.98
1995-09-20 | 20 | 9 | 0.16667 | 21.1 | 69.98 | 31.1876 |  |  |  | 69.98
1995-09-20 | 20 | 9 | 0.20833 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
1995-09-20 | 20 | 9 | 0.25 | 22.2 | 71.96 | 31.7616 |  |  | 71.96
1995-09-20 | 20 | 9 | 0.29167 | 22.2 | 71.96 | 31.7616 |  |  | 71.96
1995-09-20 | 20 | 9 | 0.33333 | 22.8 | 73.04 | 31.9938 |  |  | 73.04
1995-09-20 | 20 | 9 | 0.375 | 22.8 | 73.04 | 32.5774 |  |  | 73.04
1995-09-20 | 20 | 9 | 0.41667 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1995-09-20 | 20 | 9 | 0.45833 | 21.1 | 69.98 | 32.239 |  |  | 69.98
1995-09-20 | 20 | 9 | 0.5 | 20.6 | 69.08 | 32.0493 |  |  | 69.08
1995-09-20 | 20 | 9 | 0.54167 | 19.4 | 66.92 | 30.3867 |  |  | 66.92
1995-09-20 | 20 | 9 | 0.58333 | 18.9 | 66.02 | 29.7169 |  |  | 66.02
1995-09-20 | 20 | 9 | 0.625 | 19.4 | 66.92 | 30.3867 |  |  | 66.92
1995-09-20 | 20 | 9 | 0.66667 | 19.4 | 66.92 | 30.3867 |  |  | 66.92
1995-09-20 | 20 | 9 | 0.70833 | 20.6 | 69.08 | 31.5393 |  |  | 69.08
1995-09-20 | 20 | 9 | 0.75 | 21.1 | 69.98 | 32.7659 |  |  | 69.98
1995-09-20 | 20 | 9 | 0.79167 | 21.7 | 71.06 | 33.6452 |  |  | 71.06
1995-09-20 | 20 | 9 | 0.83333 | 21.7 | 71.06 | 33.0973 |  |  | 71.06
1995-09-20 | 20 | 9 | 0.875 | 21.1 | 69.98 | 32.7659 |  |  | 69.98
1995-09-20 | 20 | 9 | 0.91667 | 19.4 | 66.92 | 29.4442 |  |  |  | 66.92
1995-09-20 | 20 | 9 | 0.95833 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
1995-09-20 | 20 | 9 | 1 | 21.1 | 69.98 | 32.7659 |  |  |  | 69.98
1995-09-21 | 21 | 9 | 0.041667 | 21.1 | 69.98 | 32.239 |  |  |  | 69.98
1995-09-21 | 21 | 9 | 0.083333 | 20.6 | 69.08 | 32.0493 |  |  |  | 69.08
1995-09-21 | 21 | 9 | 0.125 | 21.1 | 69.98 | 32.7659 |  |  |  | 69.98
1995-09-21 | 21 | 9 | 0.16667 | 21.1 | 69.98 | 33.4697 |  |  |  | 69.98
1995-09-21 | 21 | 9 | 0.20833 | 19 | 66.2 | 30.003 |  |  |  | 66.2
1995-09-21 | 21 | 9 | 0.25 | 19.4 | 66.92 | 30.3867 |  |  | 66.92
1995-09-21 | 21 | 9 | 0.29167 | 20 | 68 | 31.2081 |  |  | 68
1995-09-21 | 21 | 9 | 0.33333 | 20.6 | 69.08 | 31.5393 |  |  | 69.08
1995-09-21 | 21 | 9 | 0.375 | 21.7 | 71.06 | 32.0043 |  |  | 71.06
1995-09-21 | 21 | 9 | 0.41667 | 21.1 | 69.98 | 32.7659 |  |  | 69.98
1995-09-21 | 21 | 9 | 0.45833 | 22.8 | 73.04 | 33.5522 |  |  | 73.04
1995-09-21 | 21 | 9 | 0.5 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-21 | 21 | 9 | 0.54167 | 25 | 77 | 33.9499 |  |  | 77
1995-09-21 | 21 | 9 | 0.58333 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
1995-09-21 | 21 | 9 | 0.625 | 25 | 77 | 33.9499 |  |  | 77
1995-09-21 | 21 | 9 | 0.66667 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-21 | 21 | 9 | 0.70833 | 23.3 | 73.94 | 32.6693 |  |  | 73.94
1995-09-21 | 21 | 9 | 0.75 | 22.8 | 73.04 | 32.967 |  |  | 73.04
1995-09-21 | 21 | 9 | 0.79167 | 22.2 | 71.96 | 32.6996 |  |  | 71.96
1995-09-21 | 21 | 9 | 0.83333 | 21.7 | 71.06 | 32.5504 |  |  | 71.06
1995-09-21 | 21 | 9 | 0.875 | 21.7 | 71.06 | 32.5504 |  |  | 71.06
1995-09-21 | 21 | 9 | 0.91667 | 21.7 | 71.06 | 32.5504 |  |  |  | 71.06
1995-09-21 | 21 | 9 | 0.95833 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
1995-09-21 | 21 | 9 | 1 | 21.7 | 71.06 | 32.0043 |  |  |  | 71.06
1995-09-22 | 22 | 9 | 0.041667 | 21.1 | 69.98 | 31.7129 |  |  |  | 69.98
1995-09-22 | 22 | 9 | 0.083333 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
1995-09-22 | 22 | 9 | 0.125 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
1995-09-22 | 22 | 9 | 0.16667 | 20 | 68 | 30.7176 |  |  |  | 68
1995-09-22 | 22 | 9 | 0.20833 | 20 | 68 | 30.7176 |  |  |  | 68
1995-09-22 | 22 | 9 | 0.25 | 19.4 | 66.92 | 30.3867 |  |  | 66.92
1995-09-22 | 22 | 9 | 0.29167 | 20 | 68 | 31.2081 |  |  | 68
1995-09-22 | 22 | 9 | 0.33333 | 21 | 69.8 | 31.7494 |  |  | 69.8
1995-09-22 | 22 | 9 | 0.375 | 21.7 | 71.06 | 31.459 |  |  | 71.06
1995-09-22 | 22 | 9 | 0.41667 | 21.7 | 71.06 | 31.459 |  |  | 71.06
1995-09-22 | 22 | 9 | 0.45833 | 22.8 | 73.04 | 31.9938 |  |  | 73.04
1995-09-22 | 22 | 9 | 0.5 | 23.9 | 75.02 | 32.4563 |  |  | 75.02
1995-09-22 | 22 | 9 | 0.54167 | 25 | 77 | 32.8375 |  |  | 77
1995-09-22 | 22 | 9 | 0.58333 | 26.1 | 78.98 | 34.0779 |  |  | 78.98
1995-09-22 | 22 | 9 | 0.625 | 25.6 | 78.08 | 34.3289 |  |  | 78.08
1995-09-22 | 22 | 9 | 0.66667 | 24.4 | 75.92 | 33.7718 |  |  | 75.92
1995-09-22 | 22 | 9 | 0.70833 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-22 | 22 | 9 | 0.75 | 22.8 | 73.04 | 33.5522 |  |  | 73.04
1995-09-22 | 22 | 9 | 0.79167 | 22.2 | 71.96 | 33.2636 |  |  | 71.96
1995-09-22 | 22 | 9 | 0.83333 | 22.2 | 71.96 | 33.2636 |  |  | 71.96
1995-09-22 | 22 | 9 | 0.875 | 22.2 | 71.96 | 34.017 |  |  | 71.96
1995-09-22 | 22 | 9 | 0.91667 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
1995-09-22 | 22 | 9 | 0.95833 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
1995-09-22 | 22 | 9 | 1 | 21.7 | 71.06 | 33.0973 |  |  |  | 71.06
1995-09-23 | 23 | 9 | 0.041667 | 21.7 | 71.06 | 29.4671 |  |  |  | 71.06
1995-09-23 | 23 | 9 | 0.083333 | 21.1 | 69.98 | 28.3994 |  |  |  | 69.98
1995-09-23 | 23 | 9 | 0.125 | 21.1 | 69.98 | 28.3994 |  |  |  | 69.98
1995-09-23 | 23 | 9 | 0.16667 | 20.6 | 69.08 | 28.1581 |  |  |  | 69.08
1995-09-23 | 23 | 9 | 0.20833 | 18.9 | 66.02 | 26.9878 |  |  |  | 66.02
1995-09-23 | 23 | 9 | 0.25 | 18.3 | 64.94 | 26.4517 |  |  | 64.94
1995-09-23 | 23 | 9 | 0.29167 | 18.3 | 64.94 | 26.4517 |  |  | 64.94
1995-09-23 | 23 | 9 | 0.33333 | 19.4 | 66.92 | 26.7877 |  |  | 66.92
1995-09-23 | 23 | 9 | 0.375 | 21.1 | 69.98 | 28.0524 |  |  | 69.98
1995-09-23 | 23 | 9 | 0.41667 | 22.2 | 71.96 | 28.0348 |  |  | 71.96
1995-09-23 | 23 | 9 | 0.45833 | 22.8 | 73.04 | 27.936 |  |  | 73.04
1995-09-23 | 23 | 9 | 0.5 | 23.3 | 73.94 | 28.8773 |  |  | 73.94
1995-09-23 | 23 | 9 | 0.54167 | 24.4 | 75.92 | 30.3495 |  |  | 75.92
1995-09-23 | 23 | 9 | 0.58333 | 25 | 77 | 29.3016 |  |  | 77
1995-09-23 | 23 | 9 | 0.625 | 25 | 77 | 28.8622 |  |  | 77
1995-09-23 | 23 | 9 | 0.66667 | 24.4 | 75.92 | 30.7754 |  |  | 75.92
1995-09-23 | 23 | 9 | 0.70833 | 23.9 | 75.02 | 31.0043 |  |  | 75.02
1995-09-23 | 23 | 9 | 0.75 | 22.8 | 73.04 | 31.0233 |  |  | 73.04
1995-09-23 | 23 | 9 | 0.79167 | 22.2 | 71.96 | 30.6394 |  |  | 71.96
1995-09-23 | 23 | 9 | 0.83333 | 22.2 | 71.96 | 30.2661 |  |  | 71.96
1995-09-23 | 23 | 9 | 0.875 | 21.7 | 71.06 | 31.459 |  |  | 71.06
1995-09-23 | 23 | 9 | 0.91667 | 21.7 | 71.06 | 32.5504 |  |  |  | 71.06
1995-09-23 | 23 | 9 | 0.95833 | 21.7 | 71.06 | 32.5504 |  |  |  | 71.06
1995-09-23 | 23 | 9 | 1 | 21.1 | 69.98 | 32.239 |  |  |  | 69.98
1995-09-24 | 24 | 9 | 0.041667 | 20.6 | 69.08 | 31.5393 |  |  |  | 69.08
1995-09-24 | 24 | 9 | 0.083333 | 20.6 | 69.08 | 31.03 |  |  |  | 69.08
1995-09-24 | 24 | 9 | 0.125 | 21.1 | 69.98 | 31.7129 |  |  |  | 69.98
1995-09-24 | 24 | 9 | 0.16667 | 21.1 | 69.98 | 32.239 |  |  |  | 69.98
1995-09-24 | 24 | 9 | 0.20833 | 21.1 | 69.98 | 32.239 |  |  |  | 69.98
1995-09-24 | 24 | 9 | 0.25 | 21.7 | 71.06 | 33.0973 |  |  | 71.06
1995-09-24 | 24 | 9 | 0.29167 | 22.2 | 71.96 | 33.2636 |  |  | 71.96
1995-09-24 | 24 | 9 | 0.33333 | 23 | 73.4 | 33.6432 |  |  | 73.4
1995-09-24 | 24 | 9 | 0.375 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1995-09-24 | 24 | 9 | 0.41667 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1995-09-24 | 24 | 9 | 0.45833 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-24 | 24 | 9 | 0.5 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1995-09-24 | 24 | 9 | 0.54167 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1995-09-24 | 24 | 9 | 0.58333 | 24.4 | 75.92 | 34.2019 |  |  | 75.92
1995-09-24 | 24 | 9 | 0.625 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-24 | 24 | 9 | 0.66667 | 23.9 | 75.02 | 33.4972 |  |  | 75.02
1995-09-24 | 24 | 9 | 0.70833 | 23.3 | 73.94 | 33.2718 |  |  | 73.94
1995-09-24 | 24 | 9 | 0.75 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1995-09-24 | 24 | 9 | 0.79167 | 23.3 | 73.94 | 31.6674 |  |  | 73.94
1995-09-24 | 24 | 9 | 0.83333 | 22.8 | 73.04 | 32.967 |  |  | 73.04
1995-09-24 | 24 | 9 | 0.875 | 22.8 | 73.04 | 32.967 |  |  | 73.04
1995-09-24 | 24 | 9 | 0.91667 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
1995-09-24 | 24 | 9 | 0.95833 | 22.8 | 73.04 | 34.1384 |  |  |  | 73.04
1995-09-24 | 24 | 9 | 1 | 22.8 | 73.04 | 34.7256 |  |  |  | 73.04
1995-09-25 | 25 | 9 | 0.041667 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1995-09-25 | 25 | 9 | 0.083333 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1995-09-25 | 25 | 9 | 0.125 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1995-09-25 | 25 | 9 | 0.16667 | 22.8 | 73.04 | 35.5101 |  |  |  | 73.04
1995-09-25 | 25 | 9 | 0.20833 | 22.2 | 71.96 | 34.017 |  |  |  | 71.96
1995-09-25 | 25 | 9 | 0.25 | 22.8 | 73.04 | 34.1384 |  |  | 73.04
1995-09-25 | 25 | 9 | 0.29167 | 22.2 | 71.96 | 32.6996 |  |  | 71.96
1995-09-25 | 25 | 9 | 0.33333 | 21.7 | 71.06 | 32.0043 |  |  | 71.06
1995-09-25 | 25 | 9 | 0.375 | 21.1 | 69.98 | 30.6631 |  |  | 69.98
1995-09-25 | 25 | 9 | 0.41667 | 20.6 | 69.08 | 30.5215 |  |  | 69.08
1995-09-25 | 25 | 9 | 0.45833 | 20.6 | 69.08 | 31.03 |  |  | 69.08
1995-09-25 | 25 | 9 | 0.5 | 20.6 | 69.08 | 30.5215 |  |  | 69.08
1995-09-25 | 25 | 9 | 0.54167 | 21.1 | 69.98 | 30.1394 |  |  | 69.98
1995-09-25 | 25 | 9 | 0.58333 | 21.1 | 69.98 | 30.1394 |  |  | 69.98
1995-09-25 | 25 | 9 | 0.625 | 21.7 | 71.06 | 30.0092 |  |  | 71.06
1995-09-25 | 25 | 9 | 0.66667 | 21.7 | 71.06 | 29.4671 |  |  | 71.06
1995-09-25 | 25 | 9 | 0.70833 | 21.7 | 71.06 | 29.2866 |  |  | 71.06
1995-09-25 | 25 | 9 | 0.75 | 21.7 | 71.06 | 28.5655 |  |  | 71.06
1995-09-25 | 25 | 9 | 0.79167 | 20.6 | 69.08 | 26.6473 |  |  | 69.08
1995-09-25 | 25 | 9 | 0.83333 | 17.8 | 64.04 | 24.4874 |  |  | 64.04
1995-09-25 | 25 | 9 | 0.875 | 16.7 | 62.06 | 24.1669 |  |  | 62.06
1995-09-25 | 25 | 9 | 0.91667 | 15.5 | 59.9 | 23.9143 |  |  |  | 59.9
1995-09-25 | 25 | 9 | 0.95833 | 15 | 59 | 23.6231 |  |  |  | 59
1995-09-25 | 25 | 9 | 1 | 15 | 59 | 23.6231 |  |  |  | 59
1995-09-26 | 26 | 9 | 0.041667 | 14 | 57.2 | 22.2562 |  |  |  | 57.2
1995-09-26 | 26 | 9 | 0.083333 | 13.4 | 56.12 | 21.7679 |  |  |  | 56.12
1995-09-26 | 26 | 9 | 0.125 | 12 | 53.6 | 20.6102 |  |  |  | 53.6
1995-09-26 | 26 | 9 | 0.16667 | 12 | 53.6 | 20.6102 |  |  |  | 53.6
1995-09-26 | 26 | 9 | 0.20833 | 11 | 51.8 | 19.6713 |  |  |  | 51.8
1995-09-26 | 26 | 9 | 0.25 | 11 | 51.8 | 18.7801 |  |  | 51.8
1995-09-26 | 26 | 9 | 0.29167 | 11.7 | 53.06 | 19.2038 |  |  | 53.06
1995-09-26 | 26 | 9 | 0.33333 | 12.2 | 53.96 | 18.4849 |  |  | 53.96
1995-09-26 | 26 | 9 | 0.375 | 13 | 55.4 | 19.643 |  |  | 55.4
1995-09-26 | 26 | 9 | 0.41667 | 13.6 | 56.48 | 19.2095 |  |  | 56.48
1995-09-26 | 26 | 9 | 0.45833 | 14.4 | 57.92 | 19.5286 |  |  | 57.92
1995-09-26 | 26 | 9 | 0.5 | 15.6 | 60.08 | 20.2678 |  |  | 60.08
1995-09-26 | 26 | 9 | 0.54167 | 16.7 | 62.06 | 20.7894 |  |  | 62.06
1995-09-26 | 26 | 9 | 0.58333 | 17.2 | 62.96 | 21.1993 |  |  | 62.96
1995-09-26 | 26 | 9 | 0.625 | 17.2 | 62.96 | 21.1993 |  |  | 62.96
1995-09-26 | 26 | 9 | 0.66667 | 17.8 | 64.04 | 21.2822 |  |  | 64.04
1995-09-26 | 26 | 9 | 0.70833 | 17.2 | 62.96 | 20.7988 |  |  | 62.96
1995-09-26 | 26 | 9 | 0.75 | 16.7 | 62.06 | 20.2727 |  |  | 62.06
1995-09-26 | 26 | 9 | 0.79167 | 16.7 | 62.06 | 20.5309 |  |  | 62.06
1995-09-26 | 26 | 9 | 0.83333 | 16.1 | 60.98 | 20.3048 |  |  | 60.98
1995-09-26 | 26 | 9 | 0.875 | 16.1 | 60.98 | 20.3048 |  |  | 60.98
1995-09-26 | 26 | 9 | 0.91667 | 16.1 | 60.98 | 20.5534 |  |  |  | 60.98
1995-09-26 | 26 | 9 | 0.95833 | 15 | 59 | 20.2463 |  |  |  | 59
1995-09-26 | 26 | 9 | 1 | 15.6 | 60.08 | 20.5087 |  |  |  | 60.08
1995-09-27 | 27 | 9 | 0.041667 | 15 | 59 | 20.8261 |  |  |  | 59
1995-09-27 | 27 | 9 | 0.083333 | 14.4 | 57.92 | 20.5315 |  |  |  | 57.92
1995-09-27 | 27 | 9 | 0.125 | 13.3 | 55.94 | 20.3162 |  |  |  | 55.94
1995-09-27 | 27 | 9 | 0.16667 | 12.8 | 55.04 | 20.3765 |  |  |  | 55.04
1995-09-27 | 27 | 9 | 0.20833 | 12.8 | 55.04 | 20.3765 |  |  |  | 55.04
1995-09-27 | 27 | 9 | 0.25 | 12.8 | 55.04 | 20.3765 |  |  | 55.04
1995-09-27 | 27 | 9 | 0.29167 | 13.9 | 57.02 | 21.0724 |  |  | 57.02
1995-09-27 | 27 | 9 | 0.33333 | 15.6 | 60.08 | 20.9909 |  |  | 60.08
1995-09-27 | 27 | 9 | 0.375 | 16.1 | 60.98 | 20.5534 |  |  | 60.98
1995-09-27 | 27 | 9 | 0.41667 | 17.8 | 64.04 | 21.2822 |  |  | 64.04
1995-09-27 | 27 | 9 | 0.45833 | 17.8 | 64.04 | 21.2822 |  |  | 64.04
1995-09-27 | 27 | 9 | 0.5 | 17.8 | 64.04 | 21.5598 |  |  | 64.04
1995-09-27 | 27 | 9 | 0.54167 | 17.8 | 64.04 | 21.6986 |  |  | 64.04
1995-09-27 | 27 | 9 | 0.58333 | 18.3 | 64.94 | 21.9777 |  |  | 64.94
1995-09-27 | 27 | 9 | 0.625 | 18.3 | 64.94 | 21.9777 |  |  | 64.94
1995-09-27 | 27 | 9 | 0.66667 | 17.8 | 64.04 | 21.6986 |  |  | 64.04
1995-09-27 | 27 | 9 | 0.70833 | 17.2 | 62.96 | 20.9323 |  |  | 62.96
1995-09-27 | 27 | 9 | 0.75 | 17.2 | 62.96 | 21.4665 |  |  | 62.96
1995-09-27 | 27 | 9 | 0.79167 | 16.7 | 62.06 | 21.5659 |  |  | 62.06
1995-09-27 | 27 | 9 | 0.83333 | 16.1 | 60.98 | 21.3005 |  |  | 60.98
1995-09-27 | 27 | 9 | 0.875 | 16.1 | 60.98 | 21.3005 |  |  | 60.98
1995-09-27 | 27 | 9 | 0.91667 | 15.6 | 60.08 | 21.5947 |  |  |  | 60.08
1995-09-27 | 27 | 9 | 0.95833 | 15 | 59 | 21.2907 |  |  |  | 59
1995-09-27 | 27 | 9 | 1 | 15 | 59 | 21.0583 |  |  |  | 59
1995-09-28 | 28 | 9 | 0.041667 | 14.4 | 57.92 | 20.7548 |  |  |  | 57.92
1995-09-28 | 28 | 9 | 0.083333 | 14.4 | 57.92 | 21.09 |  |  |  | 57.92
1995-09-28 | 28 | 9 | 0.125 | 13.9 | 57.02 | 21.0724 |  |  |  | 57.02
1995-09-28 | 28 | 9 | 0.16667 | 12.8 | 55.04 | 20.5777 |  |  |  | 55.04
1995-09-28 | 28 | 9 | 0.20833 | 12.2 | 53.96 | 20.0277 |  |  |  | 53.96
1995-09-28 | 28 | 9 | 0.25 | 12.2 | 53.96 | 20.0277 |  |  | 53.96
1995-09-28 | 28 | 9 | 0.29167 | 12.2 | 53.96 | 20.0277 |  |  | 53.96
1995-09-28 | 28 | 9 | 0.33333 | 12.8 | 55.04 | 20.0748 |  |  | 55.04
1995-09-28 | 28 | 9 | 0.375 | 13.9 | 57.02 | 21.0724 |  |  | 57.02
1995-09-28 | 28 | 9 | 0.41667 | 15.6 | 60.08 | 21.5947 |  |  | 60.08
1995-09-28 | 28 | 9 | 0.45833 | 16.1 | 60.98 | 22.0492 |  |  | 60.98
1995-09-28 | 28 | 9 | 0.5 | 17.2 | 62.96 | 22.5374 |  |  | 62.96
1995-09-28 | 28 | 9 | 0.54167 | 16.7 | 62.06 | 22.3441 |  |  | 62.06
1995-09-28 | 28 | 9 | 0.58333 | 16.7 | 62.06 | 22.3441 |  |  | 62.06
1995-09-28 | 28 | 9 | 0.625 | 17.2 | 62.96 | 22.8057 |  |  | 62.96
1995-09-28 | 28 | 9 | 0.66667 | 17.2 | 62.96 | 22.2694 |  |  | 62.96
1995-09-28 | 28 | 9 | 0.70833 | 16.7 | 62.06 | 22.3441 |  |  | 62.06
1995-09-28 | 28 | 9 | 0.75 | 16.1 | 60.98 | 22.2991 |  |  | 60.98
1995-09-28 | 28 | 9 | 0.79167 | 15.6 | 60.08 | 21.5947 |  |  | 60.08
1995-09-28 | 28 | 9 | 0.83333 | 15 | 59 | 21.2907 |  |  | 59
1995-09-28 | 28 | 9 | 0.875 | 14.4 | 57.92 | 21.6493 |  |  | 57.92
1995-09-28 | 28 | 9 | 0.91667 | 13.9 | 57.02 | 21.614 |  |  |  | 57.02
1995-09-28 | 28 | 9 | 0.95833 | 13.3 | 55.94 | 21.3567 |  |  |  | 55.94
1995-09-28 | 28 | 9 | 1 | 13.3 | 55.94 | 21.6695 |  |  |  | 55.94
1995-09-29 | 29 | 9 | 0.041667 | 12.8 | 55.04 | 21.4848 |  |  |  | 55.04
1995-09-29 | 29 | 9 | 0.083333 | 12.8 | 55.04 | 21.4848 |  |  |  | 55.04
1995-09-29 | 29 | 9 | 0.125 | 12.8 | 55.04 | 21.4848 |  |  |  | 55.04
1995-09-29 | 29 | 9 | 0.16667 | 12.8 | 55.04 | 21.4848 |  |  |  | 55.04
1995-09-29 | 29 | 9 | 0.20833 | 12.8 | 55.04 | 21.4848 |  |  |  | 55.04
1995-09-29 | 29 | 9 | 0.25 | 12.8 | 55.04 | 21.4848 |  |  | 55.04
1995-09-29 | 29 | 9 | 0.29167 | 12.8 | 55.04 | 21.4848 |  |  | 55.04
1995-09-29 | 29 | 9 | 0.33333 | 13.3 | 55.94 | 21.6695 |  |  | 55.94
1995-09-29 | 29 | 9 | 0.375 | 14.4 | 57.92 | 22.2096 |  |  | 57.92
1995-09-29 | 29 | 9 | 0.41667 | 15.6 | 60.08 | 22.4417 |  |  | 60.08
1995-09-29 | 29 | 9 | 0.45833 | 16.1 | 60.98 | 22.2991 |  |  | 60.98
1995-09-29 | 29 | 9 | 0.5 | 16.7 | 62.06 | 22.6039 |  |  | 62.06
1995-09-29 | 29 | 9 | 0.54167 | 16.7 | 62.06 | 22.3441 |  |  | 62.06
1995-09-29 | 29 | 9 | 0.58333 | 17.2 | 62.96 | 22.2694 |  |  | 62.96
1995-09-29 | 29 | 9 | 0.625 | 17.8 | 64.04 | 22.2545 |  |  | 64.04
1995-09-29 | 29 | 9 | 0.66667 | 17.2 | 62.96 | 21.7339 |  |  | 62.96
1995-09-29 | 29 | 9 | 0.70833 | 16.7 | 62.06 | 21.3068 |  |  | 62.06
1995-09-29 | 29 | 9 | 0.75 | 16.1 | 60.98 | 20.9267 |  |  | 60.98
1995-09-29 | 29 | 9 | 0.79167 | 15.6 | 60.08 | 20.5087 |  |  | 60.08
1995-09-29 | 29 | 9 | 0.83333 | 15 | 59 | 20.8261 |  |  | 59
1995-09-29 | 29 | 9 | 0.875 | 15 | 59 | 21.0583 |  |  | 59
1995-09-29 | 29 | 9 | 0.91667 | 13.9 | 57.02 | 19.5604 |  |  |  | 57.02
1995-09-29 | 29 | 9 | 0.95833 | 12.8 | 55.04 | 18.2705 |  |  |  | 55.04
1995-09-29 | 29 | 9 | 1 | 12.2 | 53.96 | 18.3887 |  |  |  | 53.96
1995-09-30 | 30 | 9 | 0.041667 | 12.2 | 53.96 | 18.7737 |  |  |  | 53.96
1995-09-30 | 30 | 9 | 0.083333 | 11.7 | 53.06 | 18.8308 |  |  |  | 53.06
1995-09-30 | 30 | 9 | 0.125 | 11.7 | 53.06 | 18.8308 |  |  |  | 53.06
1995-09-30 | 30 | 9 | 0.16667 | 11.1 | 51.98 | 18.5978 |  |  |  | 51.98
1995-09-30 | 30 | 9 | 0.20833 | 11.1 | 51.98 | 18.7769 |  |  |  | 51.98
1995-09-30 | 30 | 9 | 0.25 | 11.1 | 51.98 | 18.7769 |  |  | 51.98
1995-09-30 | 30 | 9 | 0.29167 | 11.1 | 51.98 | 18.7769 |  |  | 51.98
1995-09-30 | 30 | 9 | 0.33333 | 11.1 | 51.98 | 18.5978 |  |  | 51.98
1995-09-30 | 30 | 9 | 0.375 | 11.7 | 53.06 | 18.8308 |  |  | 53.06
1995-09-30 | 30 | 9 | 0.41667 | 12.2 | 53.96 | 18.7737 |  |  | 53.96
1995-09-30 | 30 | 9 | 0.45833 | 12.8 | 55.04 | 19.0712 |  |  | 55.04
1995-09-30 | 30 | 9 | 0.5 | 12.8 | 55.04 | 19.0712 |  |  | 55.04
1995-09-30 | 30 | 9 | 0.54167 | 12.2 | 53.96 | 19.2554 |  |  | 53.96
1995-09-30 | 30 | 9 | 0.58333 | 12.8 | 55.04 | 19.5727 |  |  | 55.04
1995-09-30 | 30 | 9 | 0.625 | 13.3 | 55.94 | 19.7971 |  |  | 55.94
1995-09-30 | 30 | 9 | 0.66667 | 12.8 | 55.04 | 19.5727 |  |  | 55.04
1995-09-30 | 30 | 9 | 0.70833 | 12.8 | 55.04 | 19.7734 |  |  | 55.04
1995-09-30 | 30 | 9 | 0.75 | 11.7 | 53.06 | 19.5772 |  |  | 53.06
1995-09-30 | 30 | 9 | 0.79167 | 11.7 | 53.06 | 19.5772 |  |  | 53.06
1995-09-30 | 30 | 9 | 0.83333 | 11.7 | 53.06 | 19.8575 |  |  | 53.06
1995-09-30 | 30 | 9 | 0.875 | 11.1 | 51.98 | 19.3149 |  |  | 51.98
1995-09-30 | 30 | 9 | 0.91667 | 10.9 | 51.62 | 18.8708 |  |  |  | 51.62
1995-09-30 | 30 | 9 | 0.95833 | 10.8 | 51.44 | 18.7838 |  |  |  | 51.44
1995-09-30 | 30 | 9 | 1 | 10.6 | 51.08 | 19.1306 |  |  |  | 51.08
1999-10-01 | 1 | 10 | 0.041667 | 10.5 | 50.9 | 19.2994 |  | 50.9
1999-10-01 | 1 | 10 | 0.083333 | 10.3 | 50.54 | 19.117 |  | 50.54
1999-10-01 | 1 | 10 | 0.125 | 10.2 | 50.36 | 18.7729 |  | 50.36
1999-10-01 | 1 | 10 | 0.16667 | 10 | 50 | 18.3461 |  | 50
1999-10-01 | 1 | 10 | 0.20833 | 10.6 | 51.08 | 18.6104 |  | 51.08
1999-10-01 | 1 | 10 | 0.25 | 11.1 | 51.98 | 18.7769 | 51.98
1999-10-01 | 1 | 10 | 0.29167 | 11.7 | 53.06 | 18.3651 | 53.06
1999-10-01 | 1 | 10 | 0.33333 | 13.1 | 55.58 | 18.9106 | 55.58
1999-10-01 | 1 | 10 | 0.375 | 12.8 | 55.04 | 18.6706 | 55.04
1999-10-01 | 1 | 10 | 0.41667 | 13.6 | 56.48 | 19.1039 | 56.48
1999-10-01 | 1 | 10 | 0.45833 | 13.5 | 56.3 | 18.8143 | 56.3
1999-10-01 | 1 | 10 | 0.5 | 13.7 | 56.66 | 19.2903 | 56.66
1999-10-01 | 1 | 10 | 0.54167 | 13.7 | 56.66 | 19.2903 | 56.66
1999-10-01 | 1 | 10 | 0.58333 | 13.9 | 57.02 | 19.776 | 57.02
1999-10-01 | 1 | 10 | 0.625 | 13.9 | 57.02 | 20.5316 | 57.02
1999-10-01 | 1 | 10 | 0.66667 | 14.4 | 57.92 | 21.09 | 57.92
1999-10-01 | 1 | 10 | 0.70833 | 13.1 | 55.58 | 18.9106 | 55.58
1999-10-01 | 1 | 10 | 0.75 | 14.4 | 57.92 | 21.09 | 57.92
1999-10-01 | 1 | 10 | 0.79167 | 15 | 59 | 21.5232 | 59
1999-10-01 | 1 | 10 | 0.83333 | 15 | 59 | 21.5232 | 59
1999-10-01 | 1 | 10 | 0.875 | 13.9 | 57.02 | 21.9394 | 57.02
1999-10-01 | 1 | 10 | 0.91667 | 13.9 | 57.02 | 21.9394 |  | 57.02
1999-10-01 | 1 | 10 | 0.95833 | 13.3 | 55.94 | 21.6695 |  | 55.94
1999-10-01 | 1 | 10 | 1 | 12.8 | 55.04 | 21.4848 |  | 55.04
1999-10-02 | 2 | 10 | 0.041667 | 12.2 | 53.96 | 21.1894 |  | 53.96
1999-10-02 | 2 | 10 | 0.083333 | 11.7 | 53.06 | 20.7 |  | 53.06
1999-10-02 | 2 | 10 | 0.125 | 13.3 | 55.94 | 21.6695 |  | 55.94
1999-10-02 | 2 | 10 | 0.16667 | 12.8 | 55.04 | 21.4848 |  | 55.04
1999-10-02 | 2 | 10 | 0.20833 | 13.3 | 55.94 | 21.3567 |  | 55.94
1999-10-02 | 2 | 10 | 0.25 | 13.9 | 57.02 | 21.9394 | 57.02
1999-10-02 | 2 | 10 | 0.29167 | 13.9 | 57.02 | 21.614 | 57.02
1999-10-02 | 2 | 10 | 0.33333 | 15.6 | 60.08 | 22.4417 | 60.08
1999-10-02 | 2 | 10 | 0.375 | 17.2 | 62.96 | 23.0742 | 62.96
1999-10-02 | 2 | 10 | 0.41667 | 17.8 | 64.04 | 24.3474 | 64.04
1999-10-02 | 2 | 10 | 0.45833 | 20.6 | 69.08 | 25.3099 | 69.08
1999-10-02 | 2 | 10 | 0.5 | 22.2 | 71.96 | 26.0021 | 71.96
1999-10-02 | 2 | 10 | 0.54167 | 22.2 | 71.96 | 26.5553 | 71.96
1999-10-02 | 2 | 10 | 0.58333 | 23.3 | 73.94 | 26.7008 | 73.94
1999-10-02 | 2 | 10 | 0.625 | 23.9 | 75.02 | 26.0717 | 75.02
1999-10-02 | 2 | 10 | 0.66667 | 23.9 | 75.02 | 26.0717 | 75.02
1999-10-02 | 2 | 10 | 0.70833 | 23.9 | 75.02 | 26.2758 | 75.02
1999-10-02 | 2 | 10 | 0.75 | 22.8 | 73.04 | 25.8293 | 73.04
1999-10-02 | 2 | 10 | 0.79167 | 21.7 | 71.06 | 26.0533 | 71.06
1999-10-02 | 2 | 10 | 0.83333 | 21.1 | 69.98 | 25.4613 | 69.98
1999-10-02 | 2 | 10 | 0.875 | 20.6 | 69.08 | 25.978 | 69.08
1999-10-02 | 2 | 10 | 0.91667 | 20 | 68 | 26.0121 |  | 68
1999-10-02 | 2 | 10 | 0.95833 | 20 | 68 | 26.6574 |  | 68
1999-10-02 | 2 | 10 | 1 | 19.4 | 66.92 | 27.255 |  | 66.92
1999-10-03 | 3 | 10 | 0.041667 | 17.8 | 64.04 | 25.7498 |  | 64.04
1999-10-03 | 3 | 10 | 0.083333 | 17.2 | 62.96 | 25.0945 |  | 62.96
1999-10-03 | 3 | 10 | 0.125 | 16.7 | 62.06 | 24.9511 |  | 62.06
1999-10-03 | 3 | 10 | 0.16667 | 16.7 | 62.06 | 25.2129 |  | 62.06
1999-10-03 | 3 | 10 | 0.20833 | 16.7 | 62.06 | 25.2129 |  | 62.06
1999-10-03 | 3 | 10 | 0.25 | 16.7 | 62.06 | 25.2129 | 62.06
1999-10-03 | 3 | 10 | 0.29167 | 17.2 | 62.96 | 25.9059 | 62.96
1999-10-03 | 3 | 10 | 0.33333 | 18.9 | 66.02 | 26.6859 | 66.02
1999-10-03 | 3 | 10 | 0.375 | 20.6 | 69.08 | 27.8218 | 69.08
1999-10-03 | 3 | 10 | 0.41667 | 22.8 | 73.04 | 28.3204 | 73.04
1999-10-03 | 3 | 10 | 0.45833 | 24.4 | 75.92 | 29.0748 | 75.92
1999-10-03 | 3 | 10 | 0.5 | 26.1 | 78.98 | 29.1192 | 78.98
1999-10-03 | 3 | 10 | 0.54167 | 26.7 | 80.06 | 28.5407 | 80.06
1999-10-03 | 3 | 10 | 0.58333 | 27.2 | 80.96 | 29.7927 | 80.96
1999-10-03 | 3 | 10 | 0.625 | 27.8 | 82.04 | 30.1728 | 82.04
1999-10-03 | 3 | 10 | 0.66667 | 27.2 | 80.96 | 30.294 | 80.96
1999-10-03 | 3 | 10 | 0.70833 | 26.7 | 80.06 | 29.9982 | 80.06
1999-10-03 | 3 | 10 | 0.75 | 25 | 77 | 30.6234 | 77
1999-10-03 | 3 | 10 | 0.79167 | 24.4 | 75.92 | 29.4992 | 75.92
1999-10-03 | 3 | 10 | 0.83333 | 23.9 | 75.02 | 28.3237 | 75.02
1999-10-03 | 3 | 10 | 0.875 | 23.3 | 73.94 | 28.0843 | 73.94
1999-10-03 | 3 | 10 | 0.91667 | 22.8 | 73.04 | 28.3204 |  | 73.04
1999-10-03 | 3 | 10 | 0.95833 | 22.2 | 71.96 | 28.0348 |  | 71.96
1999-10-03 | 3 | 10 | 1 | 21.1 | 69.98 | 27.5326 |  | 69.98
1999-10-04 | 4 | 10 | 0.041667 | 20.6 | 69.08 | 27.8218 |  | 69.08
1999-10-04 | 4 | 10 | 0.083333 | 20.6 | 69.08 | 27.318 |  | 69.08
1999-10-04 | 4 | 10 | 0.125 | 20 | 68 | 27.1421 |  | 68
1999-10-04 | 4 | 10 | 0.16667 | 19.4 | 66.92 | 27.255 |  | 66.92
1999-10-04 | 4 | 10 | 0.20833 | 18.9 | 66.02 | 26.9878 |  | 66.02
1999-10-04 | 4 | 10 | 0.25 | 18.3 | 64.94 | 26.7424 | 64.94
1999-10-04 | 4 | 10 | 0.29167 | 18.9 | 66.02 | 26.9878 | 66.02
1999-10-04 | 4 | 10 | 0.33333 | 20.6 | 69.08 | 27.8218 | 69.08
1999-10-04 | 4 | 10 | 0.375 | 22.2 | 71.96 | 28.4057 | 71.96
1999-10-04 | 4 | 10 | 0.41667 | 23.9 | 75.02 | 28.3237 | 75.02
1999-10-04 | 4 | 10 | 0.45833 | 25 | 77 | 27.7659 | 77
1999-10-04 | 4 | 10 | 0.5 | 26.1 | 78.98 | 28.6507 | 78.98
1999-10-04 | 4 | 10 | 0.54167 | 26.7 | 80.06 | 28.2984 | 80.06
1999-10-04 | 4 | 10 | 0.58333 | 27.2 | 80.96 | 28.5426 | 80.96
1999-10-04 | 4 | 10 | 0.625 | 27.8 | 82.04 | 27.8441 | 82.04
1999-10-04 | 4 | 10 | 0.66667 | 27.2 | 80.96 | 27.5458 | 80.96
1999-10-04 | 4 | 10 | 0.70833 | 26.7 | 80.06 | 27.3308 | 80.06
1999-10-04 | 4 | 10 | 0.75 | 25.6 | 78.08 | 26.7849 | 78.08
1999-10-04 | 4 | 10 | 0.79167 | 25 | 77 | 26.4551 | 77
1999-10-04 | 4 | 10 | 0.83333 | 24.4 | 75.92 | 26.5394 | 75.92
1999-10-04 | 4 | 10 | 0.875 | 23.3 | 73.94 | 27.0955 | 73.94
1999-10-04 | 4 | 10 | 0.91667 | 23.3 | 73.94 | 26.7008 |  | 73.94
1999-10-04 | 4 | 10 | 0.95833 | 21.7 | 71.06 | 26.7692 |  | 71.06
1999-10-04 | 4 | 10 | 1 | 21.1 | 69.98 | 26.4954 |  | 69.98
1999-10-05 | 5 | 10 | 0.041667 | 21.7 | 71.06 | 27.1277 |  | 71.06
1999-10-05 | 5 | 10 | 0.083333 | 20.6 | 69.08 | 26.3125 |  | 69.08
1999-10-05 | 5 | 10 | 0.125 | 19.4 | 66.92 | 26.1656 |  | 66.92
1999-10-05 | 5 | 10 | 0.16667 | 19.4 | 66.92 | 26.1656 |  | 66.92
1999-10-05 | 5 | 10 | 0.20833 | 18.3 | 64.94 | 25.5812 |  | 64.94
1999-10-05 | 5 | 10 | 0.25 | 18.3 | 64.94 | 26.0162 | 64.94
1999-10-05 | 5 | 10 | 0.29167 | 18.3 | 64.94 | 26.0162 | 64.94
1999-10-05 | 5 | 10 | 0.33333 | 20 | 68 | 26.6574 | 68
1999-10-05 | 5 | 10 | 0.375 | 21.1 | 69.98 | 27.5326 | 69.98
1999-10-05 | 5 | 10 | 0.41667 | 22.8 | 73.04 | 27.552 | 73.04
1999-10-05 | 5 | 10 | 0.45833 | 24.4 | 75.92 | 27.8048 | 75.92
1999-10-05 | 5 | 10 | 0.5 | 25.6 | 78.08 | 28.1444 | 78.08
1999-10-05 | 5 | 10 | 0.54167 | 26.1 | 78.98 | 28.4166 | 78.98
1999-10-05 | 5 | 10 | 0.58333 | 26.7 | 80.06 | 28.5407 | 80.06
1999-10-05 | 5 | 10 | 0.625 | 26.1 | 78.98 | 29.1192 | 78.98
1999-10-05 | 5 | 10 | 0.66667 | 25 | 77 | 30.6234 | 77
1999-10-05 | 5 | 10 | 0.70833 | 23.9 | 75.02 | 30.1773 | 75.02
1999-10-05 | 5 | 10 | 0.75 | 22.8 | 73.04 | 29.6692 | 73.04
1999-10-05 | 5 | 10 | 0.79167 | 22.2 | 71.96 | 29.3347 | 71.96
1999-10-05 | 5 | 10 | 0.83333 | 21.7 | 71.06 | 29.4671 | 71.06
1999-10-05 | 5 | 10 | 0.875 | 22.2 | 71.96 | 28.4057 | 71.96
1999-10-05 | 5 | 10 | 0.91667 | 22.2 | 71.96 | 28.0348 |  | 71.96
1999-10-05 | 5 | 10 | 0.95833 | 21.1 | 69.98 | 28.3994 |  | 69.98
1999-10-05 | 5 | 10 | 1 | 21.1 | 69.98 | 29.2683 |  | 69.98
1999-10-06 | 6 | 10 | 0.041667 | 21.7 | 71.06 | 29.4671 |  | 71.06
1999-10-06 | 6 | 10 | 0.083333 | 20.6 | 69.08 | 28.6632 |  | 69.08
1999-10-06 | 6 | 10 | 0.125 | 21.1 | 69.98 | 28.9205 |  | 69.98
1999-10-06 | 6 | 10 | 0.16667 | 21.1 | 69.98 | 28.9205 |  | 69.98
1999-10-06 | 6 | 10 | 0.20833 | 21.1 | 69.98 | 29.2683 |  | 69.98
1999-10-06 | 6 | 10 | 0.25 | 21.7 | 71.06 | 29.4671 | 71.06
1999-10-06 | 6 | 10 | 0.29167 | 21.7 | 71.06 | 29.4671 | 71.06
1999-10-06 | 6 | 10 | 0.33333 | 20.6 | 69.08 | 30.0137 | 69.08
1999-10-06 | 6 | 10 | 0.375 | 20 | 68 | 29.7388 | 68
1999-10-06 | 6 | 10 | 0.41667 | 17.2 | 62.96 | 25.5 | 62.96
1999-10-06 | 6 | 10 | 0.45833 | 14.4 | 57.92 | 22.2096 | 57.92
1999-10-06 | 6 | 10 | 0.5 | 13.9 | 57.02 | 21.0724 | 57.02
1999-10-06 | 6 | 10 | 0.54167 | 16.1 | 60.98 | 21.5499 | 60.98
1999-10-06 | 6 | 10 | 0.58333 | 16.7 | 62.06 | 21.048 | 62.06
1999-10-06 | 6 | 10 | 0.625 | 17.2 | 62.96 | 21.1993 | 62.96
1999-10-06 | 6 | 10 | 0.66667 | 16.7 | 62.06 | 20.7894 | 62.06
1999-10-06 | 6 | 10 | 0.70833 | 16.1 | 60.98 | 20.0563 | 60.98
1999-10-06 | 6 | 10 | 0.75 | 15.6 | 60.08 | 19.6664 | 60.08
1999-10-06 | 6 | 10 | 0.79167 | 15.6 | 60.08 | 19.6664 | 60.08
1999-10-06 | 6 | 10 | 0.83333 | 15 | 59 | 19.205 | 59
1999-10-06 | 6 | 10 | 0.875 | 14.4 | 57.92 | 18.7506 | 57.92
1999-10-06 | 6 | 10 | 0.91667 | 14.4 | 57.92 | 18.9727 |  | 57.92
1999-10-06 | 6 | 10 | 0.95833 | 13.3 | 55.94 | 18.8648 |  | 55.94
1999-10-06 | 6 | 10 | 1 | 12.2 | 53.96 | 18.1003 |  | 53.96
1999-10-07 | 7 | 10 | 0.041667 | 11.7 | 53.06 | 18.3651 |  | 53.06
1999-10-07 | 7 | 10 | 0.083333 | 11.1 | 51.98 | 17.525 |  | 51.98
1999-10-07 | 7 | 10 | 0.125 | 10 | 50 | 17.0176 |  | 50
1999-10-07 | 7 | 10 | 0.16667 | 10 | 50 | 17.1834 |  | 50
1999-10-07 | 7 | 10 | 0.20833 | 9.4 | 48.92 | 16.0005 |  | 48.92
1999-10-07 | 7 | 10 | 0.25 | 8.9 | 48.02 | 15.6409 | 48.02
1999-10-07 | 7 | 10 | 0.29167 | 8.9 | 48.02 | 15.7943 | 48.02
1999-10-07 | 7 | 10 | 0.33333 | 9.4 | 48.92 | 16.0005 | 48.92
1999-10-07 | 7 | 10 | 0.375 | 10 | 50 | 16.2726 | 50
1999-10-07 | 7 | 10 | 0.41667 | 11.1 | 51.98 | 16.5446 | 51.98
1999-10-07 | 7 | 10 | 0.45833 | 12.2 | 53.96 | 16.8533 | 53.96
1999-10-07 | 7 | 10 | 0.5 | 13.3 | 55.94 | 17.3165 | 55.94
1999-10-07 | 7 | 10 | 0.54167 | 13.3 | 55.94 | 17.3165 | 55.94
1999-10-07 | 7 | 10 | 0.58333 | 13.3 | 55.94 | 17.0077 | 55.94
1999-10-07 | 7 | 10 | 0.625 | 12.8 | 55.04 | 16.2768 | 55.04
1999-10-07 | 7 | 10 | 0.66667 | 12.8 | 55.04 | 16.4756 | 55.04
1999-10-07 | 7 | 10 | 0.70833 | 12.2 | 53.96 | 16.6619 | 53.96
1999-10-07 | 7 | 10 | 0.75 | 11.7 | 53.06 | 16.1385 | 53.06
1999-10-07 | 7 | 10 | 0.79167 | 10.6 | 51.08 | 16.0212 | 51.08
1999-10-07 | 7 | 10 | 0.83333 | 10 | 50 | 15.117 | 50
1999-10-07 | 7 | 10 | 0.875 | 10 | 50 | 14.7052 | 50
1999-10-07 | 7 | 10 | 0.91667 | 8.9 | 48.02 | 14.3397 |  | 48.02
1999-10-07 | 7 | 10 | 0.95833 | 8.3 | 46.94 | 14.1133 |  | 46.94
1999-10-07 | 7 | 10 | 1 | 8.3 | 46.94 | 14.1133 |  | 46.94
1999-10-08 | 8 | 10 | 0.041667 | 7.2 | 44.96 | 14.0412 |  | 44.96
1999-10-08 | 8 | 10 | 0.083333 | 6.7 | 44.06 | 14.3057 |  | 44.06
1999-10-08 | 8 | 10 | 0.125 | 6.1 | 42.98 | 14.0191 |  | 42.98
1999-10-08 | 8 | 10 | 0.16667 | 6.1 | 42.98 | 14.2086 |  | 42.98
1999-10-08 | 8 | 10 | 0.20833 | 6.1 | 42.98 | 14.3981 |  | 42.98
1999-10-08 | 8 | 10 | 0.25 | 5.6 | 42.08 | 13.7969 | 42.08
1999-10-08 | 8 | 10 | 0.29167 | 5.6 | 42.08 | 13.7969 | 42.08
1999-10-08 | 8 | 10 | 0.33333 | 6.1 | 42.98 | 13.8298 | 42.98
1999-10-08 | 8 | 10 | 0.375 | 7.2 | 44.96 | 14.3135 | 44.96
1999-10-08 | 8 | 10 | 0.41667 | 7.8 | 46.04 | 14.4387 | 46.04
1999-10-08 | 8 | 10 | 0.45833 | 8.9 | 48.02 | 15.1045 | 48.02
1999-10-08 | 8 | 10 | 0.5 | 10 | 50 | 15.3643 | 50
1999-10-08 | 8 | 10 | 0.54167 | 11.1 | 51.98 | 15.9222 | 51.98
1999-10-08 | 8 | 10 | 0.58333 | 11.7 | 53.06 | 16.5086 | 53.06
1999-10-08 | 8 | 10 | 0.625 | 12.2 | 53.96 | 16.6619 | 53.96
1999-10-08 | 8 | 10 | 0.66667 | 11.7 | 53.06 | 16.3235 | 53.06
1999-10-08 | 8 | 10 | 0.70833 | 12.2 | 53.96 | 16.6619 | 53.96
1999-10-08 | 8 | 10 | 0.75 | 11.1 | 51.98 | 16.1888 | 51.98
1999-10-08 | 8 | 10 | 0.79167 | 11.1 | 51.98 | 16.011 | 51.98
1999-10-08 | 8 | 10 | 0.83333 | 10.6 | 51.08 | 15.6775 | 51.08
1999-10-08 | 8 | 10 | 0.875 | 10 | 50 | 15.8594 | 50
1999-10-08 | 8 | 10 | 0.91667 | 9.4 | 48.92 | 15.4453 |  | 48.92
1999-10-08 | 8 | 10 | 0.95833 | 9.4 | 48.92 | 15.6038 |  | 48.92
1999-10-08 | 8 | 10 | 1 | 8.9 | 48.02 | 15.4109 |  | 48.02
1999-10-09 | 9 | 10 | 0.041667 | 8.9 | 48.02 | 15.4109 |  | 48.02
1999-10-09 | 9 | 10 | 0.083333 | 8.3 | 46.94 | 15.1414 |  | 46.94
1999-10-09 | 9 | 10 | 0.125 | 6.7 | 44.06 | 14.635 |  | 44.06
1999-10-09 | 9 | 10 | 0.16667 | 7.8 | 46.04 | 15.149 |  | 46.04
1999-10-09 | 9 | 10 | 0.20833 | 7.8 | 46.04 | 14.9358 |  | 46.04
1999-10-09 | 9 | 10 | 0.25 | 7.2 | 44.96 | 15.0635 | 44.96
1999-10-09 | 9 | 10 | 0.29167 | 7.8 | 46.04 | 15.149 | 46.04
1999-10-09 | 9 | 10 | 0.33333 | 9.4 | 48.92 | 15.8418 | 48.92
1999-10-09 | 9 | 10 | 0.375 | 11.1 | 51.98 | 16.3667 | 51.98
1999-10-09 | 9 | 10 | 0.41667 | 11.7 | 53.06 | 17.5284 | 53.06
1999-10-09 | 9 | 10 | 0.45833 | 12.8 | 55.04 | 16.5751 | 55.04
1999-10-09 | 9 | 10 | 0.5 | 13.9 | 57.02 | 16.5565 | 57.02
1999-10-09 | 9 | 10 | 0.54167 | 15 | 59 | 17.1321 | 59
1999-10-09 | 9 | 10 | 0.58333 | 15.6 | 60.08 | 17.51 | 60.08
1999-10-09 | 9 | 10 | 0.625 | 15.6 | 60.08 | 17.51 | 60.08
1999-10-09 | 9 | 10 | 0.66667 | 15 | 59 | 18.0518 | 59
1999-10-09 | 9 | 10 | 0.70833 | 14.4 | 57.92 | 18.3069 | 57.92
1999-10-09 | 9 | 10 | 0.75 | 14.4 | 57.92 | 17.3105 | 57.92
1999-10-09 | 9 | 10 | 0.79167 | 14.4 | 57.92 | 17.3105 | 57.92
1999-10-09 | 9 | 10 | 0.83333 | 14.4 | 57.92 | 17.753 | 57.92
1999-10-09 | 9 | 10 | 0.875 | 13.3 | 55.94 | 18.4512 | 55.94
1999-10-09 | 9 | 10 | 0.91667 | 13.3 | 55.94 | 17.2135 |  | 55.94
1999-10-09 | 9 | 10 | 0.95833 | 12.2 | 53.96 | 18.3887 |  | 53.96
1999-10-09 | 9 | 10 | 1 | 12.2 | 53.96 | 18.3887 |  | 53.96
1999-10-10 | 10 | 10 | 0.041667 | 11.7 | 53.06 | 19.0172 |  | 53.06
1999-10-10 | 10 | 10 | 0.083333 | 12.2 | 53.96 | 18.3887 |  | 53.96
1999-10-10 | 10 | 10 | 0.125 | 11.7 | 53.06 | 17.9 |  | 53.06
1999-10-10 | 10 | 10 | 0.16667 | 11.1 | 51.98 | 17.7036 |  | 51.98
1999-10-10 | 10 | 10 | 0.20833 | 10.6 | 51.08 | 17.8316 |  | 51.08
1999-10-10 | 10 | 10 | 0.25 | 10.6 | 51.08 | 17.8316 | 51.08
1999-10-10 | 10 | 10 | 0.29167 | 11.1 | 51.98 | 18.3293 | 51.98
1999-10-10 | 10 | 10 | 0.33333 | 12.8 | 55.04 | 19.5727 | 55.04
1999-10-10 | 10 | 10 | 0.375 | 13.9 | 57.02 | 20.3156 | 57.02
1999-10-10 | 10 | 10 | 0.41667 | 15 | 59 | 21.0583 | 59
1999-10-10 | 10 | 10 | 0.45833 | 16.7 | 62.06 | 21.3068 | 62.06
1999-10-10 | 10 | 10 | 0.5 | 17.8 | 64.04 | 21.0049 | 64.04
1999-10-10 | 10 | 10 | 0.54167 | 18.9 | 66.02 | 22.0401 | 66.02
1999-10-10 | 10 | 10 | 0.58333 | 20 | 68 | 22.9637 | 68
1999-10-10 | 10 | 10 | 0.625 | 20 | 68 | 22.9637 | 68
1999-10-10 | 10 | 10 | 0.66667 | 20.6 | 69.08 | 23.1477 | 69.08
1999-10-10 | 10 | 10 | 0.70833 | 20 | 68 | 23.4433 | 68
1999-10-10 | 10 | 10 | 0.75 | 18.3 | 64.94 | 23.2706 | 64.94
1999-10-10 | 10 | 10 | 0.79167 | 18.3 | 64.94 | 22.6954 | 64.94
1999-10-10 | 10 | 10 | 0.83333 | 17.8 | 64.04 | 22.8114 | 64.04
1999-10-10 | 10 | 10 | 0.875 | 16.7 | 62.06 | 23.5148 | 62.06
1999-10-10 | 10 | 10 | 0.91667 | 16.1 | 60.98 | 23.9281 |  | 60.98
1999-10-10 | 10 | 10 | 0.95833 | 15.6 | 60.08 | 24.0204 |  | 60.08
1999-10-10 | 10 | 10 | 1 | 15 | 59 | 24.2087 |  | 59
1999-10-11 | 11 | 10 | 0.041667 | 15 | 59 | 23.7401 |  | 59
1999-10-11 | 11 | 10 | 0.083333 | 15 | 59 | 23.7401 |  | 59
1999-10-11 | 11 | 10 | 0.125 | 15 | 59 | 24.2087 |  | 59
1999-10-11 | 11 | 10 | 0.16667 | 14.4 | 57.92 | 23.8959 |  | 57.92
1999-10-11 | 11 | 10 | 0.20833 | 13.9 | 57.02 | 23.68 |  | 57.02
1999-10-11 | 11 | 10 | 0.25 | 13.9 | 57.02 | 23.68 | 57.02
1999-10-11 | 11 | 10 | 0.29167 | 14.4 | 57.92 | 23.8959 | 57.92
1999-10-11 | 11 | 10 | 0.33333 | 15.6 | 60.08 | 24.3858 | 60.08
1999-10-11 | 11 | 10 | 0.375 | 16.7 | 62.06 | 24.9511 | 62.06
1999-10-11 | 11 | 10 | 0.41667 | 18.3 | 64.94 | 25.5812 | 64.94
1999-10-11 | 11 | 10 | 0.45833 | 20 | 68 | 26.3346 | 68
1999-10-11 | 11 | 10 | 0.5 | 21.1 | 69.98 | 26.8408 | 69.98
1999-10-11 | 11 | 10 | 0.54167 | 22.2 | 71.96 | 27.6644 | 71.96
1999-10-11 | 11 | 10 | 0.58333 | 23.3 | 73.94 | 28.0843 | 73.94
1999-10-11 | 11 | 10 | 0.625 | 21.7 | 71.06 | 28.2055 | 71.06
1999-10-11 | 11 | 10 | 0.66667 | 21.7 | 71.06 | 28.2055 | 71.06
1999-10-11 | 11 | 10 | 0.70833 | 20 | 68 | 27.9515 | 68
1999-10-11 | 11 | 10 | 0.75 | 19.4 | 66.92 | 27.7229 | 66.92
1999-10-11 | 11 | 10 | 0.79167 | 18.9 | 66.02 | 27.8951 | 66.02
1999-10-11 | 11 | 10 | 0.83333 | 19.4 | 66.92 | 27.255 | 66.92
1999-10-11 | 11 | 10 | 0.875 | 18.9 | 66.02 | 26.2336 | 66.02
1999-10-11 | 11 | 10 | 0.91667 | 18.9 | 66.02 | 25.9323 |  | 66.02
1999-10-11 | 11 | 10 | 0.95833 | 18.3 | 64.94 | 26.0162 |  | 64.94
1999-10-11 | 11 | 10 | 1 | 17.2 | 62.96 | 25.5 |  | 62.96
1999-10-12 | 12 | 10 | 0.041667 | 16.7 | 62.06 | 25.2129 |  | 62.06
1999-10-12 | 12 | 10 | 0.083333 | 16.7 | 62.06 | 24.9511 |  | 62.06
1999-10-12 | 12 | 10 | 0.125 | 16.7 | 62.06 | 24.9511 |  | 62.06
1999-10-12 | 12 | 10 | 0.16667 | 15.6 | 60.08 | 24.3858 |  | 60.08
1999-10-12 | 12 | 10 | 0.20833 | 15.6 | 60.08 | 24.0204 |  | 60.08
1999-10-12 | 12 | 10 | 0.25 | 15.6 | 60.08 | 24.0204 | 60.08
1999-10-12 | 12 | 10 | 0.29167 | 15.6 | 60.08 | 24.0204 | 60.08
1999-10-12 | 12 | 10 | 0.33333 | 17.2 | 62.96 | 25.0945 | 62.96
1999-10-12 | 12 | 10 | 0.375 | 18.9 | 66.02 | 25.9323 | 66.02
1999-10-12 | 12 | 10 | 0.41667 | 20 | 68 | 26.3346 | 68
1999-10-12 | 12 | 10 | 0.45833 | 21.7 | 71.06 | 27.4866 | 71.06
1999-10-12 | 12 | 10 | 0.5 | 23.3 | 73.94 | 28.0843 | 73.94
1999-10-12 | 12 | 10 | 0.54167 | 23.9 | 75.02 | 27.7081 | 75.02
1999-10-12 | 12 | 10 | 0.58333 | 23.9 | 75.02 | 27.2983 | 75.02
1999-10-12 | 12 | 10 | 0.625 | 24.4 | 75.92 | 27.5936 | 75.92
1999-10-12 | 12 | 10 | 0.66667 | 21.7 | 71.06 | 27.8458 | 71.06
1999-10-12 | 12 | 10 | 0.70833 | 20.6 | 69.08 | 27.318 | 69.08
1999-10-12 | 12 | 10 | 0.75 | 19.4 | 66.92 | 27.255 | 66.92
1999-10-12 | 12 | 10 | 0.79167 | 19.4 | 66.92 | 26.4765 | 66.92
1999-10-12 | 12 | 10 | 0.83333 | 19.4 | 66.92 | 26.1656 | 66.92
1999-10-12 | 12 | 10 | 0.875 | 18.9 | 66.02 | 26.2336 | 66.02
1999-10-12 | 12 | 10 | 0.91667 | 18.3 | 64.94 | 26.4517 |  | 64.94
1999-10-12 | 12 | 10 | 0.95833 | 18.3 | 64.94 | 26.0162 |  | 64.94
1999-10-12 | 12 | 10 | 1 | 18.9 | 66.02 | 25.9323 |  | 66.02
1999-10-13 | 13 | 10 | 0.041667 | 18.9 | 66.02 | 25.9323 |  | 66.02
1999-10-13 | 13 | 10 | 0.083333 | 18.3 | 64.94 | 25.5812 |  | 64.94
1999-10-13 | 13 | 10 | 0.125 | 17.8 | 64.04 | 25.7498 |  | 64.04
1999-10-13 | 13 | 10 | 0.16667 | 17.2 | 62.96 | 26.3124 |  | 62.96
1999-10-13 | 13 | 10 | 0.20833 | 17.8 | 64.04 | 26.4531 |  | 64.04
1999-10-13 | 13 | 10 | 0.25 | 17.2 | 62.96 | 26.7193 | 62.96
1999-10-13 | 13 | 10 | 0.29167 | 17.2 | 62.96 | 26.3124 | 62.96
1999-10-13 | 13 | 10 | 0.33333 | 18.3 | 64.94 | 26.7424 | 64.94
1999-10-13 | 13 | 10 | 0.375 | 18.3 | 64.94 | 27.1788 | 64.94
1999-10-13 | 13 | 10 | 0.41667 | 19.4 | 66.92 | 27.255 | 66.92
1999-10-13 | 13 | 10 | 0.45833 | 20.6 | 69.08 | 29.0003 | 69.08
1999-10-13 | 13 | 10 | 0.5 | 21.1 | 69.98 | 29.2683 | 69.98
1999-10-13 | 13 | 10 | 0.54167 | 22.2 | 71.96 | 29.7069 | 71.96
1999-10-13 | 13 | 10 | 0.58333 | 22.8 | 73.04 | 28.7052 | 73.04
1999-10-13 | 13 | 10 | 0.625 | 23.3 | 73.94 | 27.8863 | 73.94
1999-10-13 | 13 | 10 | 0.66667 | 22.2 | 71.96 | 27.2943 | 71.96
1999-10-13 | 13 | 10 | 0.70833 | 20.6 | 69.08 | 27.318 | 69.08
1999-10-13 | 13 | 10 | 0.75 | 18.9 | 66.02 | 27.4412 | 66.02
1999-10-13 | 13 | 10 | 0.79167 | 17.2 | 62.96 | 26.3124 | 62.96
1999-10-13 | 13 | 10 | 0.83333 | 17 | 62.6 | 25.8136 | 62.6
1999-10-13 | 13 | 10 | 0.875 | 16.7 | 62.06 | 25.7371 | 62.06
1999-10-13 | 13 | 10 | 0.91667 | 16.1 | 60.98 | 25.4387 |  | 60.98
1999-10-13 | 13 | 10 | 0.95833 | 16.1 | 60.98 | 26.323 |  | 60.98
1999-10-13 | 13 | 10 | 1 | 16.1 | 60.98 | 25.4387 |  | 60.98
1999-10-14 | 14 | 10 | 0.041667 | 16.1 | 60.98 | 24.9345 |  | 60.98
1999-10-14 | 14 | 10 | 0.083333 | 15.6 | 60.08 | 24.0204 |  | 60.08
1999-10-14 | 14 | 10 | 0.125 | 15.6 | 60.08 | 23.4124 |  | 60.08
1999-10-14 | 14 | 10 | 0.16667 | 15 | 59 | 23.0385 |  | 59
1999-10-14 | 14 | 10 | 0.20833 | 14.4 | 57.92 | 22.8831 |  | 57.92
1999-10-14 | 14 | 10 | 0.25 | 14.4 | 57.92 | 23.2204 | 57.92
1999-10-14 | 14 | 10 | 0.29167 | 14.4 | 57.92 | 23.2204 | 57.92
1999-10-14 | 14 | 10 | 0.33333 | 14.4 | 57.92 | 23.2204 | 57.92
1999-10-14 | 14 | 10 | 0.375 | 15 | 59 | 24.2087 | 59
1999-10-14 | 14 | 10 | 0.41667 | 16.1 | 60.98 | 24.6826 | 60.98
1999-10-14 | 14 | 10 | 0.45833 | 17.2 | 62.96 | 25.5 | 62.96
1999-10-14 | 14 | 10 | 0.5 | 17.8 | 64.04 | 25.7498 | 64.04
1999-10-14 | 14 | 10 | 0.54167 | 18.3 | 64.94 | 25.5812 | 64.94
1999-10-14 | 14 | 10 | 0.58333 | 18.9 | 66.02 | 26.2336 | 66.02
1999-10-14 | 14 | 10 | 0.625 | 19.4 | 66.92 | 26.4765 | 66.92
1999-10-14 | 14 | 10 | 0.66667 | 18 | 64.4 | 25.6866 | 64.4
1999-10-14 | 14 | 10 | 0.70833 | 17.8 | 64.04 | 25.7498 | 64.04
1999-10-14 | 14 | 10 | 0.75 | 17.2 | 62.96 | 26.3124 | 62.96
1999-10-14 | 14 | 10 | 0.79167 | 17.2 | 62.96 | 26.3124 | 62.96
1999-10-14 | 14 | 10 | 0.83333 | 17 | 62.6 | 26.6166 | 62.6
1999-10-14 | 14 | 10 | 0.875 | 17.2 | 62.96 | 26.7193 | 62.96
1999-10-14 | 14 | 10 | 0.91667 | 17.8 | 64.04 | 27.4402 |  | 64.04
1999-10-14 | 14 | 10 | 0.95833 | 17.8 | 64.04 | 27.8641 |  | 64.04
1999-10-14 | 14 | 10 | 1 | 17.8 | 64.04 | 28.2885 |  | 64.04
1999-10-15 | 15 | 10 | 0.041667 | 18.3 | 64.94 | 29.5159 |  | 64.94
1999-10-15 | 15 | 10 | 0.083333 | 18.9 | 66.02 | 29.2605 |  | 66.02
1999-10-15 | 15 | 10 | 0.125 | 18.9 | 66.02 | 29.7169 |  | 66.02
1999-10-15 | 15 | 10 | 0.16667 | 16.7 | 62.06 | 24.9511 |  | 62.06
1999-10-15 | 15 | 10 | 0.20833 | 16.7 | 62.06 | 24.5588 |  | 62.06
1999-10-15 | 15 | 10 | 0.25 | 16.1 | 60.98 | 24.3052 | 60.98
1999-10-15 | 15 | 10 | 0.29167 | 15.6 | 60.08 | 24.0204 | 60.08
1999-10-15 | 15 | 10 | 0.33333 | 15.6 | 60.08 | 22.6841 | 60.08
1999-10-15 | 15 | 10 | 0.375 | 16.7 | 62.06 | 22.3441 | 62.06
1999-10-15 | 15 | 10 | 0.41667 | 17.8 | 64.04 | 22.2545 | 64.04
1999-10-15 | 15 | 10 | 0.45833 | 18.9 | 66.02 | 22.7852 | 66.02
1999-10-15 | 15 | 10 | 0.5 | 20 | 68 | 22.166 | 68
1999-10-15 | 15 | 10 | 0.54167 | 20 | 68 | 22.6444 | 68
1999-10-15 | 15 | 10 | 0.58333 | 20.6 | 69.08 | 22.6507 | 69.08
1999-10-15 | 15 | 10 | 0.625 | 20.6 | 69.08 | 21.8239 | 69.08
1999-10-15 | 15 | 10 | 0.66667 | 20 | 68 | 21.8474 | 68
1999-10-15 | 15 | 10 | 0.70833 | 19.4 | 66.92 | 21.5354 | 66.92
1999-10-15 | 15 | 10 | 0.75 | 18.9 | 66.02 | 21.7425 | 66.02
1999-10-15 | 15 | 10 | 0.79167 | 18.3 | 64.94 | 21.2615 | 64.94
1999-10-15 | 15 | 10 | 0.83333 | 17.8 | 64.04 | 21.0049 | 64.04
1999-10-15 | 15 | 10 | 0.875 | 17.2 | 62.96 | 21.1993 | 62.96
1999-10-15 | 15 | 10 | 0.91667 | 16.7 | 62.06 | 21.048 |  | 62.06
1999-10-15 | 15 | 10 | 0.95833 | 16.1 | 60.98 | 20.8023 |  | 60.98
1999-10-15 | 15 | 10 | 1 | 15.6 | 60.08 | 20.5087 |  | 60.08
1999-10-16 | 16 | 10 | 0.041667 | 15 | 59 | 20.4781 |  | 59
1999-10-16 | 16 | 10 | 0.083333 | 13.9 | 57.02 | 19.9917 |  | 57.02
1999-10-16 | 16 | 10 | 0.125 | 13.3 | 55.94 | 20.524 |  | 55.94
1999-10-16 | 16 | 10 | 0.16667 | 13.3 | 55.94 | 21.3567 |  | 55.94
1999-10-16 | 16 | 10 | 0.20833 | 12.8 | 55.04 | 20.8798 |  | 55.04
1999-10-16 | 16 | 10 | 0.25 | 13.3 | 55.94 | 20.524 | 55.94
1999-10-16 | 16 | 10 | 0.29167 | 13.3 | 55.94 | 20.3162 | 55.94
1999-10-16 | 16 | 10 | 0.33333 | 15 | 59 | 20.8261 | 59
1999-10-16 | 16 | 10 | 0.375 | 17.2 | 62.96 | 22.5374 | 62.96
1999-10-16 | 16 | 10 | 0.41667 | 18.3 | 64.94 | 23.5586 | 64.94
1999-10-16 | 16 | 10 | 0.45833 | 18.3 | 64.94 | 24.2796 | 64.94
1999-10-16 | 16 | 10 | 0.5 | 19.4 | 66.92 | 24.306 | 66.92
1999-10-16 | 16 | 10 | 0.54167 | 20 | 68 | 24.7253 | 68
1999-10-16 | 16 | 10 | 0.58333 | 20 | 68 | 25.3681 | 68
1999-10-16 | 16 | 10 | 0.625 | 20 | 68 | 25.3681 | 68
1999-10-16 | 16 | 10 | 0.66667 | 20 | 68 | 25.69 | 68
1999-10-16 | 16 | 10 | 0.70833 | 18.9 | 66.02 | 25.9323 | 66.02
1999-10-16 | 16 | 10 | 0.75 | 17.8 | 64.04 | 26.1716 | 64.04
1999-10-16 | 16 | 10 | 0.79167 | 17.8 | 64.04 | 26.4531 | 64.04
1999-10-16 | 16 | 10 | 0.83333 | 17.2 | 62.96 | 26.7193 | 62.96
1999-10-16 | 16 | 10 | 0.875 | 17.2 | 62.96 | 26.7193 | 62.96
1999-10-16 | 16 | 10 | 0.91667 | 13.9 | 57.02 | 21.9394 |  | 57.02
1999-10-16 | 16 | 10 | 0.95833 | 11.7 | 53.06 | 19.2971 |  | 53.06
1999-10-16 | 16 | 10 | 1 | 11.1 | 51.98 | 18.7769 |  | 51.98
1999-10-17 | 17 | 10 | 0.041667 | 11.1 | 51.98 | 19.0458 |  | 51.98
1999-10-17 | 17 | 10 | 0.083333 | 11.1 | 51.98 | 18.3293 |  | 51.98
1999-10-17 | 17 | 10 | 0.125 | 11.1 | 51.98 | 18.3293 |  | 51.98
1999-10-17 | 17 | 10 | 0.16667 | 10 | 50 | 17.8473 |  | 50
1999-10-17 | 17 | 10 | 0.20833 | 10 | 50 | 17.8473 |  | 50
1999-10-17 | 17 | 10 | 0.25 | 10.6 | 51.08 | 17.6587 | 51.08
1999-10-17 | 17 | 10 | 0.29167 | 10.6 | 51.08 | 17.6587 | 51.08
1999-10-17 | 17 | 10 | 0.33333 | 11.1 | 51.98 | 17.8823 | 51.98
1999-10-17 | 17 | 10 | 0.375 | 11.7 | 53.06 | 18.179 | 53.06
1999-10-17 | 17 | 10 | 0.41667 | 13.3 | 55.94 | 18.6579 | 55.94
1999-10-17 | 17 | 10 | 0.45833 | 13.9 | 57.02 | 18.3771 | 57.02
1999-10-17 | 17 | 10 | 0.5 | 13.9 | 57.02 | 18.1624 | 57.02
1999-10-17 | 17 | 10 | 0.54167 | 14.4 | 57.92 | 17.9744 | 57.92
1999-10-17 | 17 | 10 | 0.58333 | 14.4 | 57.92 | 17.6423 | 57.92
1999-10-17 | 17 | 10 | 0.625 | 13.9 | 57.02 | 17.198 | 57.02
1999-10-17 | 17 | 10 | 0.66667 | 13.3 | 55.94 | 17.0077 | 55.94
1999-10-17 | 17 | 10 | 0.70833 | 12.8 | 55.04 | 16.4756 | 55.04
1999-10-17 | 17 | 10 | 0.75 | 12.2 | 53.96 | 16.0883 | 53.96
1999-10-17 | 17 | 10 | 0.79167 | 11.1 | 51.98 | 15.7446 | 51.98
1999-10-17 | 17 | 10 | 0.83333 | 11.1 | 51.98 | 15.7446 | 51.98
1999-10-17 | 17 | 10 | 0.875 | 10.6 | 51.08 | 15.5057 | 51.08
1999-10-17 | 17 | 10 | 0.91667 | 10 | 50 | 15.117 |  | 50
1999-10-17 | 17 | 10 | 0.95833 | 10 | 50 | 15.1994 |  | 50
1999-10-17 | 17 | 10 | 1 | 8.9 | 48.02 | 14.3397 |  | 48.02
1999-10-18 | 18 | 10 | 0.041667 | 8.3 | 46.94 | 14.4801 |  | 46.94
1999-10-18 | 18 | 10 | 0.083333 | 8.3 | 46.94 | 14.1866 |  | 46.94
1999-10-18 | 18 | 10 | 0.125 | 7.8 | 46.04 | 14.0132 |  | 46.04
1999-10-18 | 18 | 10 | 0.16667 | 7.2 | 44.96 | 13.9051 |  | 44.96
1999-10-18 | 18 | 10 | 0.20833 | 7.2 | 44.96 | 14.0412 |  | 44.96
1999-10-18 | 18 | 10 | 0.25 | 6.7 | 44.06 | 13.7795 | 44.06
1999-10-18 | 18 | 10 | 0.29167 | 6.7 | 44.06 | 13.9768 | 44.06
1999-10-18 | 18 | 10 | 0.33333 | 7.2 | 44.96 | 14.0412 | 44.96
1999-10-18 | 18 | 10 | 0.375 | 8.3 | 46.94 | 14.4801 | 46.94
1999-10-18 | 18 | 10 | 0.41667 | 10 | 50 | 15.3643 | 50
1999-10-18 | 18 | 10 | 0.45833 | 10.6 | 51.08 | 15.8493 | 51.08
1999-10-18 | 18 | 10 | 0.5 | 11.1 | 51.98 | 15.9222 | 51.98
1999-10-18 | 18 | 10 | 0.54167 | 12.8 | 55.04 | 16.5751 | 55.04
1999-10-18 | 18 | 10 | 0.58333 | 13.3 | 55.94 | 16.2882 | 55.94
1999-10-18 | 18 | 10 | 0.625 | 13.9 | 57.02 | 16.7702 | 57.02
1999-10-18 | 18 | 10 | 0.66667 | 13.9 | 57.02 | 16.6633 | 57.02
1999-10-18 | 18 | 10 | 0.70833 | 13.9 | 57.02 | 16.8771 | 57.02
1999-10-18 | 18 | 10 | 0.75 | 13.3 | 55.94 | 16.3909 | 55.94
1999-10-18 | 18 | 10 | 0.79167 | 12.8 | 55.04 | 16.4756 | 55.04
1999-10-18 | 18 | 10 | 0.83333 | 12.2 | 53.96 | 16.1838 | 53.96
1999-10-18 | 18 | 10 | 0.875 | 11.7 | 53.06 | 16.3235 | 53.06
1999-10-18 | 18 | 10 | 0.91667 | 11.7 | 53.06 | 16.6012 |  | 53.06
1999-10-18 | 18 | 10 | 0.95833 | 10.6 | 51.08 | 16.1932 |  | 51.08
1999-10-18 | 18 | 10 | 1 | 10 | 50 | 15.8594 |  | 50
1999-10-19 | 19 | 10 | 0.041667 | 10 | 50 | 16.2726 |  | 50
1999-10-19 | 19 | 10 | 0.083333 | 8.3 | 46.94 | 15.6567 |  | 46.94
1999-10-19 | 19 | 10 | 0.125 | 8.9 | 48.02 | 16.1781 |  | 48.02
1999-10-19 | 19 | 10 | 0.16667 | 8.3 | 46.94 | 15.8777 |  | 46.94
1999-10-19 | 19 | 10 | 0.20833 | 8.9 | 48.02 | 16.3318 |  | 48.02
1999-10-19 | 19 | 10 | 0.25 | 8.9 | 48.02 | 16.1781 | 48.02
1999-10-19 | 19 | 10 | 0.29167 | 9.4 | 48.92 | 16.5567 | 48.92
1999-10-19 | 19 | 10 | 0.33333 | 10.6 | 51.08 | 17.0545 | 51.08
1999-10-19 | 19 | 10 | 0.375 | 12.8 | 55.04 | 17.8708 | 55.04
1999-10-19 | 19 | 10 | 0.41667 | 13.3 | 55.94 | 18.2446 | 55.94
1999-10-19 | 19 | 10 | 0.45833 | 14.4 | 57.92 | 18.3069 | 57.92
1999-10-19 | 19 | 10 | 0.5 | 15.6 | 60.08 | 19.186 | 60.08
1999-10-19 | 19 | 10 | 0.54167 | 16.7 | 62.06 | 19.4991 | 62.06
1999-10-19 | 19 | 10 | 0.58333 | 16.7 | 62.06 | 19.8857 | 62.06
1999-10-19 | 19 | 10 | 0.625 | 16.1 | 60.98 | 20.0563 | 60.98
1999-10-19 | 19 | 10 | 0.66667 | 15.6 | 60.08 | 20.2678 | 60.08
1999-10-19 | 19 | 10 | 0.70833 | 15 | 59 | 20.8261 | 59
1999-10-19 | 19 | 10 | 0.75 | 15 | 59 | 21.2907 | 59
1999-10-19 | 19 | 10 | 0.79167 | 14.4 | 57.92 | 19.974 | 57.92
1999-10-19 | 19 | 10 | 0.83333 | 13.9 | 57.02 | 19.9917 | 57.02
1999-10-19 | 19 | 10 | 0.875 | 13.9 | 57.02 | 20.3156 | 57.02
1999-10-19 | 19 | 10 | 0.91667 | 13.9 | 57.02 | 20.856 |  | 57.02
1999-10-19 | 19 | 10 | 0.95833 | 13.3 | 55.94 | 20.836 |  | 55.94
1999-10-19 | 19 | 10 | 1 | 13.3 | 55.94 | 20.524 |  | 55.94
1999-10-20 | 20 | 10 | 0.041667 | 12.8 | 55.04 | 19.0712 |  | 55.04
1999-10-20 | 20 | 10 | 0.083333 | 12.8 | 55.04 | 20.5777 |  | 55.04
1999-10-20 | 20 | 10 | 0.125 | 12.8 | 55.04 | 21.1822 |  | 55.04
1999-10-20 | 20 | 10 | 0.16667 | 12.2 | 53.96 | 20.8986 |  | 53.96
1999-10-20 | 20 | 10 | 0.20833 | 11.7 | 53.06 | 20.7 |  | 53.06
1999-10-20 | 20 | 10 | 0.25 | 11.7 | 53.06 | 20.9812 | 53.06
1999-10-20 | 20 | 10 | 0.29167 | 11.7 | 53.06 | 20.9812 | 53.06
1999-10-20 | 20 | 10 | 0.33333 | 13.3 | 55.94 | 21.6695 | 55.94
1999-10-20 | 20 | 10 | 0.375 | 13.9 | 57.02 | 21.614 | 57.02
1999-10-20 | 20 | 10 | 0.41667 | 15 | 59 | 21.2907 | 59
1999-10-20 | 20 | 10 | 0.45833 | 16.7 | 62.06 | 22.3441 | 62.06
1999-10-20 | 20 | 10 | 0.5 | 18.9 | 66.02 | 22.487 | 66.02
1999-10-20 | 20 | 10 | 0.54167 | 20 | 68 | 23.1235 | 68
1999-10-20 | 20 | 10 | 0.58333 | 21.1 | 69.98 | 22.8896 | 69.98
1999-10-20 | 20 | 10 | 0.625 | 21.7 | 71.06 | 23.2046 | 71.06
1999-10-20 | 20 | 10 | 0.66667 | 21.1 | 69.98 | 22.7188 | 69.98
1999-10-20 | 20 | 10 | 0.70833 | 20.6 | 69.08 | 22.4852 | 69.08
1999-10-20 | 20 | 10 | 0.75 | 20.6 | 69.08 | 22.6507 | 69.08
1999-10-20 | 20 | 10 | 0.79167 | 20 | 68 | 22.0067 | 68
1999-10-20 | 20 | 10 | 0.83333 | 18.9 | 66.02 | 21.4452 | 66.02
1999-10-20 | 20 | 10 | 0.875 | 17.8 | 64.04 | 20.5894 | 64.04
1999-10-20 | 20 | 10 | 0.91667 | 16.7 | 62.06 | 21.3068 |  | 62.06
1999-10-20 | 20 | 10 | 0.95833 | 15.6 | 60.08 | 21.2323 |  | 60.08
1999-10-20 | 20 | 10 | 1 | 15.6 | 60.08 | 21.2323 |  | 60.08
1999-10-21 | 21 | 10 | 0.041667 | 15.6 | 60.08 | 20.5087 |  | 60.08
1999-10-21 | 21 | 10 | 0.083333 | 15.6 | 60.08 | 21.2323 |  | 60.08
1999-10-21 | 21 | 10 | 0.125 | 15 | 59 | 21.5232 |  | 59
1999-10-21 | 21 | 10 | 0.16667 | 14.4 | 57.92 | 21.09 |  | 57.92
1999-10-21 | 21 | 10 | 0.20833 | 13.9 | 57.02 | 20.856 |  | 57.02
1999-10-21 | 21 | 10 | 0.25 | 13.3 | 55.94 | 20.524 | 55.94
1999-10-21 | 21 | 10 | 0.29167 | 13.9 | 57.02 | 21.0724 | 57.02
1999-10-21 | 21 | 10 | 0.33333 | 15 | 59 | 21.8723 | 59
1999-10-21 | 21 | 10 | 0.375 | 17.2 | 62.96 | 22.8057 | 62.96
1999-10-21 | 21 | 10 | 0.41667 | 19.4 | 66.92 | 23.2259 | 66.92
1999-10-21 | 21 | 10 | 0.45833 | 21.1 | 69.98 | 24.6019 | 69.98
1999-10-21 | 21 | 10 | 0.5 | 21.7 | 71.06 | 25.6959 | 71.06
1999-10-21 | 21 | 10 | 0.54167 | 21.1 | 69.98 | 25.8057 | 69.98
1999-10-21 | 21 | 10 | 0.58333 | 21.7 | 71.06 | 26.7692 | 71.06
1999-10-21 | 21 | 10 | 0.625 | 21.1 | 69.98 | 28.0524 | 69.98
1999-10-21 | 21 | 10 | 0.66667 | 21.1 | 69.98 | 27.1866 | 69.98
1999-10-21 | 21 | 10 | 0.70833 | 20.6 | 69.08 | 26.3125 | 69.08
1999-10-21 | 21 | 10 | 0.75 | 19.4 | 66.92 | 24.77 | 66.92
1999-10-21 | 21 | 10 | 0.79167 | 20 | 68 | 24.0837 | 68
1999-10-21 | 21 | 10 | 0.83333 | 19.4 | 66.92 | 23.5342 | 66.92
1999-10-21 | 21 | 10 | 0.875 | 18.9 | 66.02 | 24.1304 | 66.02
1999-10-21 | 21 | 10 | 0.91667 | 17.8 | 64.04 | 24.6274 |  | 64.04
1999-10-21 | 21 | 10 | 0.95833 | 17.8 | 64.04 | 25.7498 |  | 64.04
1999-10-21 | 21 | 10 | 1 | 17.8 | 64.04 | 25.7498 |  | 64.04
1999-10-22 | 22 | 10 | 0.041667 | 17.2 | 62.96 | 23.7463 |  | 62.96
1999-10-22 | 22 | 10 | 0.083333 | 17.2 | 62.96 | 25.9059 |  | 62.96
1999-10-22 | 22 | 10 | 0.125 | 16.7 | 62.06 | 25.7371 |  | 62.06
1999-10-22 | 22 | 10 | 0.16667 | 16.7 | 62.06 | 25.7371 |  | 62.06
1999-10-22 | 22 | 10 | 0.20833 | 16.1 | 60.98 | 25.4387 |  | 60.98
1999-10-22 | 22 | 10 | 0.25 | 15.6 | 60.08 | 25.2398 | 60.08
1999-10-22 | 22 | 10 | 0.29167 | 16.7 | 62.06 | 25.9995 | 62.06
1999-10-22 | 22 | 10 | 0.33333 | 16.7 | 62.06 | 25.7371 | 62.06
1999-10-22 | 22 | 10 | 0.375 | 17.8 | 64.04 | 26.1716 | 64.04
1999-10-22 | 22 | 10 | 0.41667 | 18.3 | 64.94 | 24.5684 | 64.94
1999-10-22 | 22 | 10 | 0.45833 | 18.9 | 66.02 | 25.1804 | 66.02
1999-10-22 | 22 | 10 | 0.5 | 20 | 68 | 25.3681 | 68
1999-10-22 | 22 | 10 | 0.54167 | 20.6 | 69.08 | 25.978 | 69.08
1999-10-22 | 22 | 10 | 0.58333 | 21.1 | 69.98 | 25.8057 | 69.98
1999-10-22 | 22 | 10 | 0.625 | 21.1 | 69.98 | 26.1504 | 69.98
1999-10-22 | 22 | 10 | 0.66667 | 20.6 | 69.08 | 25.4768 | 69.08
1999-10-22 | 22 | 10 | 0.70833 | 20.6 | 69.08 | 25.3099 | 69.08
1999-10-22 | 22 | 10 | 0.75 | 19.4 | 66.92 | 25.3896 | 66.92
1999-10-22 | 22 | 10 | 0.79167 | 17.8 | 64.04 | 23.3691 | 64.04
1999-10-22 | 22 | 10 | 0.83333 | 17.2 | 62.96 | 23.0742 | 62.96
1999-10-22 | 22 | 10 | 0.875 | 16.7 | 62.06 | 23.2543 | 62.06
1999-10-22 | 22 | 10 | 0.91667 | 16.1 | 60.98 | 22.5492 |  | 60.98
1999-10-22 | 22 | 10 | 0.95833 | 16.1 | 60.98 | 21.7994 |  | 60.98
1999-10-22 | 22 | 10 | 1 | 15.6 | 60.08 | 21.2323 |  | 60.08
1999-10-23 | 23 | 10 | 0.041667 | 15 | 59 | 20.4781 |  | 59
1999-10-23 | 23 | 10 | 0.083333 | 15 | 59 | 21.2907 |  | 59
1999-10-23 | 23 | 10 | 0.125 | 14.4 | 57.92 | 21.09 |  | 57.92
1999-10-23 | 23 | 10 | 0.16667 | 14.4 | 57.92 | 20.7548 |  | 57.92
1999-10-23 | 23 | 10 | 0.20833 | 15 | 59 | 20.8261 |  | 59
1999-10-23 | 23 | 10 | 0.25 | 14.4 | 57.92 | 21.3136 | 57.92
1999-10-23 | 23 | 10 | 0.29167 | 15 | 59 | 22.8049 | 59
1999-10-23 | 23 | 10 | 0.33333 | 16.1 | 60.98 | 24.6826 | 60.98
1999-10-23 | 23 | 10 | 0.375 | 16.7 | 62.06 | 24.9511 | 62.06
1999-10-23 | 23 | 10 | 0.41667 | 17.2 | 62.96 | 25.5 | 62.96
1999-10-23 | 23 | 10 | 0.45833 | 18 | 64.4 | 26.2562 | 64.4
1999-10-23 | 23 | 10 | 0.5 | 18.3 | 64.94 | 27.1788 | 64.94
1999-10-23 | 23 | 10 | 0.54167 | 18.9 | 66.02 | 27.8951 | 66.02
1999-10-23 | 23 | 10 | 0.58333 | 19.4 | 66.92 | 28.1915 | 66.92
1999-10-23 | 23 | 10 | 0.625 | 19.4 | 66.92 | 28.5043 | 66.92
1999-10-23 | 23 | 10 | 0.66667 | 18.9 | 66.02 | 28.8048 | 66.02
1999-10-23 | 23 | 10 | 0.70833 | 18.3 | 64.94 | 28.4915 | 64.94
1999-10-23 | 23 | 10 | 0.75 | 18 | 64.4 | 28.6872 | 64.4
1999-10-23 | 23 | 10 | 0.79167 | 17.8 | 64.04 | 29.2808 | 64.04
1999-10-23 | 23 | 10 | 0.83333 | 18 | 64.4 | 29.5493 | 64.4
1999-10-23 | 23 | 10 | 0.875 | 18.3 | 64.94 | 29.9559 | 64.94
1999-10-23 | 23 | 10 | 0.91667 | 18.9 | 66.02 | 29.7169 |  | 66.02
1999-10-23 | 23 | 10 | 0.95833 | 18.9 | 66.02 | 29.7169 |  | 66.02
1999-10-23 | 23 | 10 | 1 | 18.3 | 64.94 | 29.5159 |  | 64.94
1999-10-24 | 24 | 10 | 0.041667 | 17.8 | 64.04 | 27.4402 |  | 64.04
1999-10-24 | 24 | 10 | 0.083333 | 17.8 | 64.04 | 28.7134 |  | 64.04
1999-10-24 | 24 | 10 | 0.125 | 18.3 | 64.94 | 28.9302 |  | 64.94
1999-10-24 | 24 | 10 | 0.16667 | 18.9 | 66.02 | 29.2605 |  | 66.02
1999-10-24 | 24 | 10 | 0.20833 | 18.3 | 64.94 | 28.4915 |  | 64.94
1999-10-24 | 24 | 10 | 0.25 | 17.8 | 64.04 | 28.2885 | 64.04
1999-10-24 | 24 | 10 | 0.29167 | 17.8 | 64.04 | 28.2885 | 64.04
1999-10-24 | 24 | 10 | 0.33333 | 18.9 | 66.02 | 29.2605 | 66.02
1999-10-24 | 24 | 10 | 0.375 | 20.6 | 69.08 | 30.0137 | 69.08
1999-10-24 | 24 | 10 | 0.41667 | 21.7 | 71.06 | 30.0092 | 71.06
1999-10-24 | 24 | 10 | 0.45833 | 23.3 | 73.94 | 30.6683 | 73.94
1999-10-24 | 24 | 10 | 0.5 | 24.4 | 75.92 | 30.7754 | 75.92
1999-10-24 | 24 | 10 | 0.54167 | 25.6 | 78.08 | 31.3374 | 78.08
1999-10-24 | 24 | 10 | 0.58333 | 26.1 | 78.98 | 31.4717 | 78.98
1999-10-24 | 24 | 10 | 0.625 | 25 | 77 | 31.5074 | 77
1999-10-24 | 24 | 10 | 0.66667 | 23.9 | 75.02 | 31.4185 | 75.02
1999-10-24 | 24 | 10 | 0.70833 | 22.2 | 71.96 | 30.6394 | 71.96
1999-10-24 | 24 | 10 | 0.75 | 20.6 | 69.08 | 30.0137 | 69.08
1999-10-24 | 24 | 10 | 0.79167 | 20 | 68 | 29.7388 | 68
1999-10-24 | 24 | 10 | 0.83333 | 20.6 | 69.08 | 30.0137 | 69.08
1999-10-24 | 24 | 10 | 0.875 | 20 | 68 | 29.2504 | 68
1999-10-24 | 24 | 10 | 0.91667 | 20 | 68 | 29.2504 |  | 68
1999-10-24 | 24 | 10 | 0.95833 | 19.4 | 66.92 | 28.5043 |  | 66.92
1999-10-24 | 24 | 10 | 1 | 18.9 | 66.02 | 28.3496 |  | 66.02
1999-10-25 | 25 | 10 | 0.041667 | 18.9 | 66.02 | 27.4412 |  | 66.02
1999-10-25 | 25 | 10 | 0.083333 | 18 | 64.4 | 28.6872 |  | 64.4
1999-10-25 | 25 | 10 | 0.125 | 17.8 | 64.04 | 28.7134 |  | 64.04
1999-10-25 | 25 | 10 | 0.16667 | 17.2 | 62.96 | 28.0792 |  | 62.96
1999-10-25 | 25 | 10 | 0.20833 | 17.8 | 64.04 | 28.7134 |  | 64.04
1999-10-25 | 25 | 10 | 0.25 | 18 | 64.4 | 28.6872 | 64.4
1999-10-25 | 25 | 10 | 0.29167 | 18.3 | 64.94 | 28.9302 | 64.94
1999-10-25 | 25 | 10 | 0.33333 | 20 | 68 | 29.7388 | 68
1999-10-25 | 25 | 10 | 0.375 | 22.8 | 73.04 | 31.4112 | 73.04
1999-10-25 | 25 | 10 | 0.41667 | 24.4 | 75.92 | 30.7754 | 75.92
1999-10-25 | 25 | 10 | 0.45833 | 25.6 | 78.08 | 29.9654 | 78.08
1999-10-25 | 25 | 10 | 0.5 | 23.9 | 75.02 | 28.1184 | 75.02
1999-10-25 | 25 | 10 | 0.54167 | 23.3 | 73.94 | 26.1096 | 73.94
1999-10-25 | 25 | 10 | 0.58333 | 23.9 | 75.02 | 22.4181 | 75.02
1999-10-25 | 25 | 10 | 0.625 | 23.3 | 73.94 | 20.0592 | 73.94
1999-10-25 | 25 | 10 | 0.66667 | 22.2 | 71.96 | 19.9752 | 71.96
1999-10-25 | 25 | 10 | 0.70833 | 20.6 | 69.08 | 19.8477 | 69.08
1999-10-25 | 25 | 10 | 0.75 | 20 | 68 | 19.6257 | 68
1999-10-25 | 25 | 10 | 0.79167 | 19.4 | 66.92 | 19.0914 | 66.92
1999-10-25 | 25 | 10 | 0.83333 | 18.9 | 66.02 | 18.9284 | 66.02
1999-10-25 | 25 | 10 | 0.875 | 17.8 | 64.04 | 18.3818 | 64.04
1999-10-25 | 25 | 10 | 0.91667 | 17.2 | 62.96 | 18.0089 |  | 62.96
1999-10-25 | 25 | 10 | 0.95833 | 16.1 | 60.98 | 17.3349 |  | 60.98
1999-10-25 | 25 | 10 | 1 | 15.6 | 60.08 | 17.0326 |  | 60.08
1999-10-26 | 26 | 10 | 0.041667 | 15.6 | 60.08 | 16.9134 |  | 60.08
1999-10-26 | 26 | 10 | 0.083333 | 14.4 | 57.92 | 16.4273 |  | 57.92
1999-10-26 | 26 | 10 | 0.125 | 14.4 | 57.92 | 16.7582 |  | 57.92
1999-10-26 | 26 | 10 | 0.16667 | 13.3 | 55.94 | 16.3909 |  | 55.94
1999-10-26 | 26 | 10 | 0.20833 | 12.8 | 55.04 | 16.0781 |  | 55.04
1999-10-26 | 26 | 10 | 0.25 | 12.2 | 53.96 | 15.8018 | 53.96
1999-10-26 | 26 | 10 | 0.29167 | 12.2 | 53.96 | 15.8973 | 53.96
1999-10-26 | 26 | 10 | 0.33333 | 12.2 | 53.96 | 15.8018 | 53.96
1999-10-26 | 26 | 10 | 0.375 | 12.8 | 55.04 | 16.1774 | 55.04
1999-10-26 | 26 | 10 | 0.41667 | 13.3 | 55.94 | 16.3909 | 55.94
1999-10-26 | 26 | 10 | 0.45833 | 13.9 | 57.02 | 16.5565 | 57.02
1999-10-26 | 26 | 10 | 0.5 | 13.3 | 55.94 | 16.083 | 55.94
1999-10-26 | 26 | 10 | 0.54167 | 12.8 | 55.04 | 15.8795 | 55.04
1999-10-26 | 26 | 10 | 0.58333 | 13.3 | 55.94 | 15.9804 | 55.94
1999-10-26 | 26 | 10 | 0.625 | 12.8 | 55.04 | 16.0781 | 55.04
1999-10-26 | 26 | 10 | 0.66667 | 12.2 | 53.96 | 15.8973 | 53.96
1999-10-26 | 26 | 10 | 0.70833 | 11.1 | 51.98 | 15.3896 | 51.98
1999-10-26 | 26 | 10 | 0.75 | 10.6 | 51.08 | 15.0768 | 51.08
1999-10-26 | 26 | 10 | 0.79167 | 10 | 50 | 14.9522 | 50
1999-10-26 | 26 | 10 | 0.83333 | 9.4 | 48.92 | 14.6537 | 48.92
1999-10-26 | 26 | 10 | 0.875 | 8.3 | 46.94 | 14.3333 | 46.94
1999-10-26 | 26 | 10 | 0.91667 | 7.8 | 46.04 | 14.1549 |  | 46.04
1999-10-26 | 26 | 10 | 0.95833 | 7.2 | 44.96 | 13.9051 |  | 44.96
1999-10-26 | 26 | 10 | 1 | 7.2 | 44.96 | 14.0412 |  | 44.96
1999-10-27 | 27 | 10 | 0.041667 | 6.7 | 44.06 | 13.3854 |  | 44.06
1999-10-27 | 27 | 10 | 0.083333 | 6.7 | 44.06 | 13.9768 |  | 44.06
1999-10-27 | 27 | 10 | 0.125 | 6.7 | 44.06 | 14.1083 |  | 44.06
1999-10-27 | 27 | 10 | 0.16667 | 6.7 | 44.06 | 14.1083 |  | 44.06
1999-10-27 | 27 | 10 | 0.20833 | 6.7 | 44.06 | 14.1083 |  | 44.06
1999-10-27 | 27 | 10 | 0.25 | 6.7 | 44.06 | 14.3057 | 44.06
1999-10-27 | 27 | 10 | 0.29167 | 6.7 | 44.06 | 14.4374 | 44.06
1999-10-27 | 27 | 10 | 0.33333 | 7.2 | 44.96 | 14.6542 | 44.96
1999-10-27 | 27 | 10 | 0.375 | 8.3 | 46.94 | 15.1414 | 46.94
1999-10-27 | 27 | 10 | 0.41667 | 9.4 | 48.92 | 15.6038 | 48.92
1999-10-27 | 27 | 10 | 0.45833 | 10 | 50 | 15.6943 | 50
1999-10-27 | 27 | 10 | 0.5 | 10.6 | 51.08 | 16.0212 | 51.08
1999-10-27 | 27 | 10 | 0.54167 | 10.6 | 51.08 | 15.8493 | 51.08
1999-10-27 | 27 | 10 | 0.58333 | 11.1 | 51.98 | 16.1888 | 51.98
1999-10-27 | 27 | 10 | 0.625 | 10.6 | 51.08 | 15.8493 | 51.08
1999-10-27 | 27 | 10 | 0.66667 | 10.6 | 51.08 | 16.0212 | 51.08
1999-10-27 | 27 | 10 | 0.70833 | 9.4 | 48.92 | 15.6038 | 48.92
1999-10-27 | 27 | 10 | 0.75 | 8.9 | 48.02 | 15.4109 | 48.02
1999-10-27 | 27 | 10 | 0.79167 | 8.3 | 46.94 | 15.1414 | 46.94
1999-10-27 | 27 | 10 | 0.83333 | 7.8 | 46.04 | 14.9358 | 46.04
1999-10-27 | 27 | 10 | 0.875 | 7.9 | 46.22 | 14.9344 | 46.22
1999-10-27 | 27 | 10 | 0.91667 | 7.8 | 46.04 | 14.7937 |  | 46.04
1999-10-27 | 27 | 10 | 0.95833 | 7.2 | 44.96 | 14.6542 |  | 44.96
1999-10-27 | 27 | 10 | 1 | 7.2 | 44.96 | 14.5179 |  | 44.96
1999-10-28 | 28 | 10 | 0.041667 | 6.7 | 44.06 | 13.9768 |  | 44.06
1999-10-28 | 28 | 10 | 0.083333 | 6.1 | 42.98 | 14.0191 |  | 42.98
1999-10-28 | 28 | 10 | 0.125 | 5.6 | 42.08 | 13.6141 |  | 42.08
1999-10-28 | 28 | 10 | 0.16667 | 5.6 | 42.08 | 13.6141 |  | 42.08
1999-10-28 | 28 | 10 | 0.20833 | 5 | 41 | 13.209 |  | 41
1999-10-28 | 28 | 10 | 0.25 | 5 | 41 | 13.0339 | 41
1999-10-28 | 28 | 10 | 0.29167 | 5 | 41 | 13.0339 | 41
1999-10-28 | 28 | 10 | 0.33333 | 5.6 | 42.08 | 13.0663 | 42.08
1999-10-28 | 28 | 10 | 0.375 | 6.7 | 44.06 | 13.6481 | 44.06
1999-10-28 | 28 | 10 | 0.41667 | 7.2 | 44.96 | 13.6331 | 44.96
1999-10-28 | 28 | 10 | 0.45833 | 7.8 | 46.04 | 14.0132 | 46.04
1999-10-28 | 28 | 10 | 0.5 | 8.9 | 48.02 | 14.1869 | 48.02
1999-10-28 | 28 | 10 | 0.54167 | 10 | 50 | 14.7875 | 50
1999-10-28 | 28 | 10 | 0.58333 | 10.6 | 51.08 | 14.9053 | 51.08
1999-10-28 | 28 | 10 | 0.625 | 10.6 | 51.08 | 14.9053 | 51.08
1999-10-28 | 28 | 10 | 0.66667 | 10.6 | 51.08 | 15.0768 | 51.08
1999-10-28 | 28 | 10 | 0.70833 | 10 | 50 | 14.7052 | 50
1999-10-28 | 28 | 10 | 0.75 | 10 | 50 | 14.7875 | 50
1999-10-28 | 28 | 10 | 0.79167 | 9.4 | 48.92 | 14.6537 | 48.92
1999-10-28 | 28 | 10 | 0.83333 | 8.9 | 48.02 | 14.7218 | 48.02
1999-10-28 | 28 | 10 | 0.875 | 8.3 | 46.94 | 14.4801 | 46.94
1999-10-28 | 28 | 10 | 0.91667 | 8.3 | 46.94 | 14.3333 |  | 46.94
1999-10-28 | 28 | 10 | 0.95833 | 7.2 | 44.96 | 14.1773 |  | 44.96
1999-10-28 | 28 | 10 | 1 | 7.2 | 44.96 | 14.3135 |  | 44.96
1999-10-29 | 29 | 10 | 0.041667 | 6.7 | 44.06 | 13.3854 |  | 44.06
1999-10-29 | 29 | 10 | 0.083333 | 6.1 | 42.98 | 13.8298 |  | 42.98
1999-10-29 | 29 | 10 | 0.125 | 5.6 | 42.08 | 13.7969 |  | 42.08
1999-10-29 | 29 | 10 | 0.16667 | 5.6 | 42.08 | 13.9798 |  | 42.08
1999-10-29 | 29 | 10 | 0.20833 | 5.6 | 42.08 | 14.1629 |  | 42.08
1999-10-29 | 29 | 10 | 0.25 | 5.6 | 42.08 | 14.1629 | 42.08
1999-10-29 | 29 | 10 | 0.29167 | 5.6 | 42.08 | 14.1629 | 42.08
1999-10-29 | 29 | 10 | 0.33333 | 6.1 | 42.98 | 14.0191 | 42.98
1999-10-29 | 29 | 10 | 0.375 | 7.8 | 46.04 | 14.4387 | 46.04
1999-10-29 | 29 | 10 | 0.41667 | 8.9 | 48.02 | 14.7218 | 48.02
1999-10-29 | 29 | 10 | 0.45833 | 10 | 50 | 15.1994 | 50
1999-10-29 | 29 | 10 | 0.5 | 11.1 | 51.98 | 15.7446 | 51.98
1999-10-29 | 29 | 10 | 0.54167 | 12.2 | 53.96 | 16.375 | 53.96
1999-10-29 | 29 | 10 | 0.58333 | 13.3 | 55.94 | 16.6992 | 55.94
1999-10-29 | 29 | 10 | 0.625 | 14.4 | 57.92 | 17.2 | 57.92
1999-10-29 | 29 | 10 | 0.66667 | 15 | 59 | 17.3618 | 59
1999-10-29 | 29 | 10 | 0.70833 | 14.4 | 57.92 | 17.3105 | 57.92
1999-10-29 | 29 | 10 | 0.75 | 14.4 | 57.92 | 17.2 | 57.92
1999-10-29 | 29 | 10 | 0.79167 | 13.9 | 57.02 | 17.091 | 57.02
1999-10-29 | 29 | 10 | 0.83333 | 13.9 | 57.02 | 17.198 | 57.02
1999-10-29 | 29 | 10 | 0.875 | 13.9 | 57.02 | 17.4121 | 57.02
1999-10-29 | 29 | 10 | 0.91667 | 13.3 | 55.94 | 17.2135 |  | 55.94
1999-10-29 | 29 | 10 | 0.95833 | 13.3 | 55.94 | 17.3165 |  | 55.94
1999-10-29 | 29 | 10 | 1 | 13.3 | 55.94 | 17.3165 |  | 55.94
1999-10-30 | 30 | 10 | 0.041667 | 13.3 | 55.94 | 17.3165 |  | 55.94
1999-10-30 | 30 | 10 | 0.083333 | 12.8 | 55.04 | 17.2722 |  | 55.04
1999-10-30 | 30 | 10 | 0.125 | 12.8 | 55.04 | 17.6711 |  | 55.04
1999-10-30 | 30 | 10 | 0.16667 | 12.2 | 53.96 | 17.4283 |  | 53.96
1999-10-30 | 30 | 10 | 0.20833 | 12.2 | 53.96 | 17.6202 |  | 53.96
1999-10-30 | 30 | 10 | 0.25 | 11.7 | 53.06 | 17.3428 | 53.06
1999-10-30 | 30 | 10 | 0.29167 | 11.7 | 53.06 | 17.3428 | 53.06
1999-10-30 | 30 | 10 | 0.33333 | 11.7 | 53.06 | 17.7141 | 53.06
1999-10-30 | 30 | 10 | 0.375 | 12.2 | 53.96 | 18.1003 | 53.96
1999-10-30 | 30 | 10 | 0.41667 | 13.3 | 55.94 | 18.8648 | 55.94
1999-10-30 | 30 | 10 | 0.45833 | 13.9 | 57.02 | 18.9145 | 57.02
1999-10-30 | 30 | 10 | 0.5 | 14.4 | 57.92 | 19.0839 | 57.92
1999-10-30 | 30 | 10 | 0.54167 | 15 | 59 | 18.9741 | 59
1999-10-30 | 30 | 10 | 0.58333 | 16.1 | 60.98 | 19.3119 | 60.98
1999-10-30 | 30 | 10 | 0.625 | 15.6 | 60.08 | 17.3906 | 60.08
1999-10-30 | 30 | 10 | 0.66667 | 15.6 | 60.08 | 17.988 | 60.08
1999-10-30 | 30 | 10 | 0.70833 | 14.4 | 57.92 | 16.979 | 57.92
1999-10-30 | 30 | 10 | 0.75 | 13.3 | 55.94 | 16.4936 | 55.94
1999-10-30 | 30 | 10 | 0.79167 | 12.2 | 53.96 | 15.6109 | 53.96
1999-10-30 | 30 | 10 | 0.83333 | 11.7 | 53.06 | 15.3073 | 53.06
1999-10-30 | 30 | 10 | 0.875 | 11.1 | 51.98 | 15.035 | 51.98
1999-10-30 | 30 | 10 | 0.91667 | 10 | 50 | 14.1295 |  | 50
1999-10-30 | 30 | 10 | 0.95833 | 9.4 | 48.92 | 13.7851 |  | 48.92
1999-10-30 | 30 | 10 | 1 | 8.9 | 48.02 | 13.729 |  | 48.02
1999-10-31 | 31 | 10 | 0.041667 | 8.3 | 46.94 | 13.6736 |  | 46.94
1999-10-31 | 31 | 10 | 0.083333 | 7.8 | 46.04 | 13.5882 |  | 46.04
1999-10-31 | 31 | 10 | 0.125 | 7.2 | 44.96 | 13.4972 |  | 44.96
1999-10-31 | 31 | 10 | 0.16667 | 6.7 | 44.06 | 13.2542 |  | 44.06
1999-10-31 | 31 | 10 | 0.20833 | 6.7 | 44.06 | 13.5168 |  | 44.06
1999-10-31 | 31 | 10 | 0.25 | 7.2 | 44.96 | 13.6331 | 44.96
1999-10-31 | 31 | 10 | 0.29167 | 7.8 | 46.04 | 13.8715 | 46.04
1999-10-31 | 31 | 10 | 0.33333 | 7.2 | 44.96 | 13.9051 | 44.96
1999-10-31 | 31 | 10 | 0.375 | 7.8 | 46.04 | 14.2968 | 46.04
1999-10-31 | 31 | 10 | 0.41667 | 8.9 | 48.02 | 15.2576 | 48.02
1999-10-31 | 31 | 10 | 0.45833 | 9.4 | 48.92 | 15.8418 | 48.92
1999-10-31 | 31 | 10 | 0.5 | 10 | 50 | 16.1073 | 50
1999-10-31 | 31 | 10 | 0.54167 | 10.6 | 51.08 | 16.1932 | 51.08
1999-10-31 | 31 | 10 | 0.58333 | 11.1 | 51.98 | 16.3667 | 51.98
1999-10-31 | 31 | 10 | 0.625 | 12.8 | 55.04 | 17.0729 | 55.04
1999-10-31 | 31 | 10 | 0.66667 | 13.3 | 55.94 | 17.3165 | 55.94
1999-10-31 | 31 | 10 | 0.70833 | 13.3 | 55.94 | 17.3165 | 55.94
1999-10-31 | 31 | 10 | 0.75 | 13.9 | 57.02 | 17.6263 | 57.02
1999-10-31 | 31 | 10 | 0.79167 | 13.9 | 57.02 | 17.6263 | 57.02
1999-10-31 | 31 | 10 | 0.83333 | 14.4 | 57.92 | 17.753 | 57.92
1999-10-31 | 31 | 10 | 0.875 | 14.4 | 57.92 | 17.6423 | 57.92
1999-10-31 | 31 | 10 | 0.91667 | 14.8 | 58.64 | 18.0284 |  | 58.64
1999-10-31 | 31 | 10 | 0.95833 | 15.2 | 59.36 | 18.0729 |  | 59.36
1999-10-31 | 31 | 10 | 1 | 15.6 | 60.08 | 18.347 |  | 60.08
1977-11-01 | 1 | 11 | 0.041667 | 16 | 60.8 | 26.9579 |  | 60.8
1977-11-01 | 1 | 11 | 0.083333 | 16.4 | 61.52 | 26.9432 |  | 61.52
1977-11-01 | 1 | 11 | 0.125 | 16.8 | 62.24 | 27.4392 |  | 62.24
1977-11-01 | 1 | 11 | 0.16667 | 17.2 | 62.96 | 28.4882 |  | 62.96
1977-11-01 | 1 | 11 | 0.20833 | 17.8 | 64.04 | 28.7134 |  | 64.04
1977-11-01 | 1 | 11 | 0.25 | 17.2 | 62.96 | 28.4882 | 62.96
1977-11-01 | 1 | 11 | 0.29167 | 17.2 | 62.96 | 28.0792 | 62.96
1977-11-01 | 1 | 11 | 0.33333 | 17.2 | 62.96 | 28.0792 | 62.96
1977-11-01 | 1 | 11 | 0.375 | 18.3 | 64.94 | 29.5159 | 64.94
1977-11-01 | 1 | 11 | 0.41667 | 18.3 | 64.94 | 28.9302 | 64.94
1977-11-01 | 1 | 11 | 0.45833 | 17.8 | 64.04 | 28.2885 | 64.04
1977-11-01 | 1 | 11 | 0.5 | 17.8 | 64.04 | 28.2885 | 64.04
1977-11-01 | 1 | 11 | 0.54167 | 17.2 | 62.96 | 28.0792 | 62.96
1977-11-01 | 1 | 11 | 0.58333 | 18.3 | 64.94 | 28.9302 | 64.94
1977-11-01 | 1 | 11 | 0.625 | 18.3 | 64.94 | 28.9302 | 64.94
1977-11-01 | 1 | 11 | 0.66667 | 18.3 | 64.94 | 28.9302 | 64.94
1977-11-01 | 1 | 11 | 0.70833 | 18.9 | 66.02 | 29.2605 | 66.02
1977-11-01 | 1 | 11 | 0.75 | 18.3 | 64.94 | 28.4915 | 64.94
1977-11-01 | 1 | 11 | 0.79167 | 18.3 | 64.94 | 27.6159 | 64.94
1977-11-01 | 1 | 11 | 0.83333 | 13.3 | 55.94 | 21.6695 | 55.94
1977-11-01 | 1 | 11 | 0.875 | 13.9 | 57.02 | 21.3973 | 57.02
1977-11-01 | 1 | 11 | 0.91667 | 12.8 | 55.04 | 20.5777 |  | 55.04
1977-11-01 | 1 | 11 | 0.95833 | 12.2 | 53.96 | 20.0277 |  | 53.96
1977-11-01 | 1 | 11 | 1 | 11.7 | 53.06 | 19.8575 |  | 53.06
1977-11-02 | 2 | 11 | 0.041667 | 10.6 | 51.08 | 17.8316 |  | 51.08
1977-11-02 | 2 | 11 | 0.083333 | 9.4 | 48.92 | 17.1137 |  | 48.92
1977-11-02 | 2 | 11 | 0.125 | 8.9 | 48.02 | 17.4093 |  | 48.02
1977-11-02 | 2 | 11 | 0.16667 | 9.4 | 48.92 | 17.3527 |  | 48.92
1977-11-02 | 2 | 11 | 0.20833 | 8.9 | 48.02 | 17.4093 |  | 48.02
1977-11-02 | 2 | 11 | 0.25 | 8.3 | 46.94 | 17.1331 | 46.94
1977-11-02 | 2 | 11 | 0.29167 | 8.3 | 46.94 | 17.3552 | 46.94
1977-11-02 | 2 | 11 | 0.33333 | 9.4 | 48.92 | 17.8313 | 48.92
1977-11-02 | 2 | 11 | 0.375 | 10.6 | 51.08 | 17.6587 | 51.08
1977-11-02 | 2 | 11 | 0.41667 | 10.6 | 51.08 | 17.227 | 51.08
1977-11-02 | 2 | 11 | 0.45833 | 10 | 50 | 17.0176 | 50
1977-11-02 | 2 | 11 | 0.5 | 10.6 | 51.08 | 17.227 | 51.08
1977-11-02 | 2 | 11 | 0.54167 | 12.2 | 53.96 | 18.0042 | 53.96
1977-11-02 | 2 | 11 | 0.58333 | 12.8 | 55.04 | 17.9707 | 55.04
1977-11-02 | 2 | 11 | 0.625 | 13.9 | 57.02 | 18.4845 | 57.02
1977-11-02 | 2 | 11 | 0.66667 | 14.4 | 57.92 | 18.3069 | 57.92
1977-11-02 | 2 | 11 | 0.70833 | 13.9 | 57.02 | 17.7334 | 57.02
1977-11-02 | 2 | 11 | 0.75 | 13.9 | 57.02 | 17.198 | 57.02
1977-11-02 | 2 | 11 | 0.79167 | 13.3 | 55.94 | 17.0077 | 55.94
1977-11-02 | 2 | 11 | 0.83333 | 12.8 | 55.04 | 17.0729 | 55.04
1977-11-02 | 2 | 11 | 0.875 | 12.2 | 53.96 | 16.4706 | 53.96
1977-11-02 | 2 | 11 | 0.91667 | 12.2 | 53.96 | 17.0449 |  | 53.96
1977-11-02 | 2 | 11 | 0.95833 | 11.1 | 51.98 | 16.7227 |  | 51.98
1977-11-02 | 2 | 11 | 1 | 11.1 | 51.98 | 16.9008 |  | 51.98
1977-11-03 | 3 | 11 | 0.041667 | 10.6 | 51.08 | 16.7097 |  | 51.08
1977-11-03 | 3 | 11 | 0.083333 | 10 | 50 | 16.2726 |  | 50
1977-11-03 | 3 | 11 | 0.125 | 9.4 | 48.92 | 16.1593 |  | 48.92
1977-11-03 | 3 | 11 | 0.16667 | 9.4 | 48.92 | 16.3977 |  | 48.92
1977-11-03 | 3 | 11 | 0.20833 | 8.3 | 46.94 | 16.0252 |  | 46.94
1977-11-03 | 3 | 11 | 0.25 | 8.3 | 46.94 | 16.0252 | 46.94
1977-11-03 | 3 | 11 | 0.29167 | 8.3 | 46.94 | 16.0252 | 46.94
1977-11-03 | 3 | 11 | 0.33333 | 9.4 | 48.92 | 16.7157 | 48.92
1977-11-03 | 3 | 11 | 0.375 | 10.6 | 51.08 | 17.227 | 51.08
1977-11-03 | 3 | 11 | 0.41667 | 12.2 | 53.96 | 17.7161 | 53.96
1977-11-03 | 3 | 11 | 0.45833 | 15 | 59 | 18.9741 | 59
1977-11-03 | 3 | 11 | 0.5 | 16.7 | 62.06 | 19.3704 | 62.06
1977-11-03 | 3 | 11 | 0.54167 | 17.8 | 64.04 | 19.4838 | 64.04
1977-11-03 | 3 | 11 | 0.58333 | 20 | 68 | 20.4175 | 68
1977-11-03 | 3 | 11 | 0.625 | 20.6 | 69.08 | 20.5051 | 69.08
1977-11-03 | 3 | 11 | 0.66667 | 20 | 68 | 20.259 | 68
1977-11-03 | 3 | 11 | 0.70833 | 15.6 | 60.08 | 20.0271 | 60.08
1977-11-03 | 3 | 11 | 0.75 | 14.4 | 57.92 | 21.6493 | 57.92
1977-11-03 | 3 | 11 | 0.79167 | 15 | 59 | 22.1052 | 59
1977-11-03 | 3 | 11 | 0.83333 | 17.2 | 62.96 | 19.7333 | 62.96
1977-11-03 | 3 | 11 | 0.875 | 17.2 | 62.96 | 19.4674 | 62.96
1977-11-03 | 3 | 11 | 0.91667 | 17.2 | 62.96 | 19.069 |  | 62.96
1977-11-03 | 3 | 11 | 0.95833 | 16.7 | 62.06 | 19.2417 |  | 62.06
1977-11-03 | 3 | 11 | 1 | 16.7 | 62.06 | 19.3704 |  | 62.06
1977-11-04 | 4 | 11 | 0.041667 | 16.1 | 60.98 | 19.4359 |  | 60.98
1977-11-04 | 4 | 11 | 0.083333 | 16.1 | 60.98 | 19.6839 |  | 60.98
1977-11-04 | 4 | 11 | 0.125 | 15.6 | 60.08 | 19.9068 |  | 60.08
1977-11-04 | 4 | 11 | 0.16667 | 15 | 59 | 20.2463 |  | 59
1977-11-04 | 4 | 11 | 0.20833 | 14.4 | 57.92 | 19.7512 |  | 57.92
1977-11-04 | 4 | 11 | 0.25 | 14.4 | 57.92 | 19.974 | 57.92
1977-11-04 | 4 | 11 | 0.29167 | 15.6 | 60.08 | 20.5087 | 60.08
1977-11-04 | 4 | 11 | 0.33333 | 16.1 | 60.98 | 20.9267 | 60.98
1977-11-04 | 4 | 11 | 0.375 | 17.8 | 64.04 | 21.9765 | 64.04
1977-11-04 | 4 | 11 | 0.41667 | 19.4 | 66.92 | 22.9179 | 66.92
1977-11-04 | 4 | 11 | 0.45833 | 21.1 | 69.98 | 23.7447 | 69.98
1977-11-04 | 4 | 11 | 0.5 | 21.1 | 69.98 | 24.2588 | 69.98
1977-11-04 | 4 | 11 | 0.54167 | 21.1 | 69.98 | 24.2588 | 69.98
1977-11-04 | 4 | 11 | 0.58333 | 21.1 | 69.98 | 24.7736 | 69.98
1977-11-04 | 4 | 11 | 0.625 | 21.1 | 69.98 | 24.6019 | 69.98
1977-11-04 | 4 | 11 | 0.66667 | 20.6 | 69.08 | 25.3099 | 69.08
1977-11-04 | 4 | 11 | 0.70833 | 18.9 | 66.02 | 25.481 | 66.02
1977-11-04 | 4 | 11 | 0.75 | 17.8 | 64.04 | 25.0479 | 64.04
1977-11-04 | 4 | 11 | 0.79167 | 18.9 | 66.02 | 25.481 | 66.02
1977-11-04 | 4 | 11 | 0.83333 | 17.8 | 64.04 | 25.0479 | 64.04
1977-11-04 | 4 | 11 | 0.875 | 18.3 | 64.94 | 23.8468 | 64.94
1977-11-04 | 4 | 11 | 0.91667 | 17.8 | 64.04 | 23.3691 |  | 64.04
1977-11-04 | 4 | 11 | 0.95833 | 17.8 | 64.04 | 21.9765 |  | 64.04
1977-11-04 | 4 | 11 | 1 | 17.8 | 64.04 | 21.9765 |  | 64.04
1977-11-05 | 5 | 11 | 0.041667 | 17.2 | 62.96 | 21.7339 |  | 62.96
1977-11-05 | 5 | 11 | 0.083333 | 16.1 | 60.98 | 21.3005 |  | 60.98
1977-11-05 | 5 | 11 | 0.125 | 15.6 | 60.08 | 21.2323 |  | 60.08
1977-11-05 | 5 | 11 | 0.16667 | 15 | 59 | 21.2907 |  | 59
1977-11-05 | 5 | 11 | 0.20833 | 14.4 | 57.92 | 20.7548 |  | 57.92
1977-11-05 | 5 | 11 | 0.25 | 14.4 | 57.92 | 20.7548 | 57.92
1977-11-05 | 5 | 11 | 0.29167 | 15 | 59 | 21.2907 | 59
1977-11-05 | 5 | 11 | 0.33333 | 16.1 | 60.98 | 22.0492 | 60.98
1977-11-05 | 5 | 11 | 0.375 | 16.1 | 60.98 | 22.0492 | 60.98
1977-11-05 | 5 | 11 | 0.41667 | 17.8 | 64.04 | 22.5329 | 64.04
1977-11-05 | 5 | 11 | 0.45833 | 18.3 | 64.94 | 22.9829 | 64.94
1977-11-05 | 5 | 11 | 0.5 | 19.4 | 66.92 | 23.2259 | 66.92
1977-11-05 | 5 | 11 | 0.54167 | 20 | 68 | 23.7633 | 68
1977-11-05 | 5 | 11 | 0.58333 | 21.1 | 69.98 | 24.2588 | 69.98
1977-11-05 | 5 | 11 | 0.625 | 22.2 | 71.96 | 24.7148 | 71.96
1977-11-05 | 5 | 11 | 0.66667 | 22.8 | 73.04 | 24.8759 | 73.04
1977-11-05 | 5 | 11 | 0.70833 | 21.1 | 69.98 | 24.2588 | 69.98
1977-11-05 | 5 | 11 | 0.75 | 18.3 | 64.94 | 24.2796 | 64.94
1977-11-05 | 5 | 11 | 0.79167 | 18.9 | 66.02 | 24.1304 | 66.02
1977-11-05 | 5 | 11 | 0.83333 | 18.9 | 66.02 | 23.831 | 66.02
1977-11-05 | 5 | 11 | 0.875 | 18.9 | 66.02 | 23.831 | 66.02
1977-11-05 | 5 | 11 | 0.91667 | 18.9 | 66.02 | 24.1304 |  | 66.02
1977-11-05 | 5 | 11 | 0.95833 | 18.3 | 64.94 | 23.8468 |  | 64.94
1977-11-05 | 5 | 11 | 1 | 17.8 | 64.04 | 23.6484 |  | 64.04
1977-11-06 | 6 | 11 | 0.041667 | 17.8 | 64.04 | 24.0676 |  | 64.04
1977-11-06 | 6 | 11 | 0.083333 | 16.7 | 62.06 | 23.5148 |  | 62.06
1977-11-06 | 6 | 11 | 0.125 | 16.1 | 60.98 | 23.5515 |  | 60.98
1977-11-06 | 6 | 11 | 0.16667 | 15.6 | 60.08 | 23.7771 |  | 60.08
1977-11-06 | 6 | 11 | 0.20833 | 15 | 59 | 24.5605 |  | 59
1977-11-06 | 6 | 11 | 0.25 | 14.4 | 57.92 | 24.2342 | 57.92
1977-11-06 | 6 | 11 | 0.29167 | 15.6 | 60.08 | 25.2398 | 60.08
1977-11-06 | 6 | 11 | 0.33333 | 16.7 | 62.06 | 25.9995 | 62.06
1977-11-06 | 6 | 11 | 0.375 | 18.9 | 66.02 | 27.4412 | 66.02
1977-11-06 | 6 | 11 | 0.41667 | 18.9 | 66.02 | 27.4412 | 66.02
1977-11-06 | 6 | 11 | 0.45833 | 19.4 | 66.92 | 27.255 | 66.92
1977-11-06 | 6 | 11 | 0.5 | 20 | 68 | 28.438 | 68
1977-11-06 | 6 | 11 | 0.54167 | 19.4 | 66.92 | 28.1915 | 66.92
1977-11-06 | 6 | 11 | 0.58333 | 20.6 | 69.08 | 29.0003 | 69.08
1977-11-06 | 6 | 11 | 0.625 | 20 | 68 | 28.438 | 68
1977-11-06 | 6 | 11 | 0.66667 | 20 | 68 | 28.438 | 68
1977-11-06 | 6 | 11 | 0.70833 | 19.4 | 66.92 | 28.1915 | 66.92
1977-11-06 | 6 | 11 | 0.75 | 19.4 | 66.92 | 28.1915 | 66.92
1977-11-06 | 6 | 11 | 0.79167 | 19.4 | 66.92 | 28.1915 | 66.92
1977-11-06 | 6 | 11 | 0.83333 | 20 | 68 | 27.9515 | 68
1977-11-06 | 6 | 11 | 0.875 | 18.9 | 66.02 | 23.233 | 66.02
1977-11-06 | 6 | 11 | 0.91667 | 17.8 | 64.04 | 21.6986 |  | 64.04
1977-11-06 | 6 | 11 | 0.95833 | 17.2 | 62.96 | 21.1993 |  | 62.96
1977-11-06 | 6 | 11 | 1 | 16.1 | 60.98 | 20.8023 |  | 60.98
1977-11-07 | 7 | 11 | 0.041667 | 15 | 59 | 20.8261 |  | 59
1977-11-07 | 7 | 11 | 0.083333 | 13.3 | 55.94 | 19.0717 |  | 55.94
1977-11-07 | 7 | 11 | 0.125 | 12.2 | 53.96 | 18.0042 |  | 53.96
1977-11-07 | 7 | 11 | 0.16667 | 11.7 | 53.06 | 17.3428 |  | 53.06
1977-11-07 | 7 | 11 | 0.20833 | 11.1 | 51.98 | 17.079 |  | 51.98
1977-11-07 | 7 | 11 | 0.25 | 10 | 50 | 16.6035 | 50
1977-11-07 | 7 | 11 | 0.29167 | 8.9 | 48.02 | 15.7943 | 48.02
1977-11-07 | 7 | 11 | 0.33333 | 9.4 | 48.92 | 16.1593 | 48.92
1977-11-07 | 7 | 11 | 0.375 | 10 | 50 | 16.2726 | 50
1977-11-07 | 7 | 11 | 0.41667 | 10.6 | 51.08 | 16.0212 | 51.08
1977-11-07 | 7 | 11 | 0.45833 | 11.7 | 53.06 | 16.3235 | 53.06
1977-11-07 | 7 | 11 | 0.5 | 12.8 | 55.04 | 16.5751 | 55.04
1977-11-07 | 7 | 11 | 0.54167 | 13.9 | 57.02 | 17.198 | 57.02
1977-11-07 | 7 | 11 | 0.58333 | 13.9 | 57.02 | 17.091 | 57.02
1977-11-07 | 7 | 11 | 0.625 | 14.4 | 57.92 | 17.3105 | 57.92
1977-11-07 | 7 | 11 | 0.66667 | 14.4 | 57.92 | 16.979 | 57.92
1977-11-07 | 7 | 11 | 0.70833 | 13.9 | 57.02 | 16.7702 | 57.02
1977-11-07 | 7 | 11 | 0.75 | 13.3 | 55.94 | 16.802 | 55.94
1977-11-07 | 7 | 11 | 0.79167 | 12.8 | 55.04 | 16.7741 | 55.04
1977-11-07 | 7 | 11 | 0.83333 | 12.2 | 53.96 | 16.4706 | 53.96
1977-11-07 | 7 | 11 | 0.875 | 11.7 | 53.06 | 16.1385 | 53.06
1977-11-07 | 7 | 11 | 0.91667 | 11.7 | 53.06 | 15.9537 |  | 53.06
1977-11-07 | 7 | 11 | 0.95833 | 11.1 | 51.98 | 15.7446 |  | 51.98
1977-11-07 | 7 | 11 | 1 | 10.6 | 51.08 | 15.3341 |  | 51.08
1977-11-08 | 8 | 11 | 0.041667 | 10.6 | 51.08 | 15.6775 |  | 51.08
1977-11-08 | 8 | 11 | 0.083333 | 10.6 | 51.08 | 15.2483 |  | 51.08
1977-11-08 | 8 | 11 | 0.125 | 10.6 | 51.08 | 15.6775 |  | 51.08
1977-11-08 | 8 | 11 | 0.16667 | 10.6 | 51.08 | 15.8493 |  | 51.08
1977-11-08 | 8 | 11 | 0.20833 | 9.4 | 48.92 | 15.4453 |  | 48.92
1977-11-08 | 8 | 11 | 0.25 | 9.4 | 48.92 | 15.4453 | 48.92
1977-11-08 | 8 | 11 | 0.29167 | 9.4 | 48.92 | 15.6038 | 48.92
1977-11-08 | 8 | 11 | 0.33333 | 11.1 | 51.98 | 16.3667 | 51.98
1977-11-08 | 8 | 11 | 0.375 | 12.2 | 53.96 | 17.4283 | 53.96
1977-11-08 | 8 | 11 | 0.41667 | 13.9 | 57.02 | 18.1624 | 57.02
1977-11-08 | 8 | 11 | 0.45833 | 15 | 59 | 18.6279 | 59
1977-11-08 | 8 | 11 | 0.5 | 16.7 | 62.06 | 19.4991 | 62.06
1977-11-08 | 8 | 11 | 0.54167 | 18.9 | 66.02 | 20.2585 | 66.02
1977-11-08 | 8 | 11 | 0.58333 | 20 | 68 | 20.259 | 68
1977-11-08 | 8 | 11 | 0.625 | 20.6 | 69.08 | 20.6697 | 69.08
1977-11-08 | 8 | 11 | 0.66667 | 19.4 | 66.92 | 20.3112 | 66.92
1977-11-08 | 8 | 11 | 0.70833 | 20 | 68 | 21.2112 | 68
1977-11-08 | 8 | 11 | 0.75 | 18.9 | 66.02 | 20.8513 | 66.02
1977-11-08 | 8 | 11 | 0.79167 | 18.3 | 64.94 | 20.6897 | 64.94
1977-11-08 | 8 | 11 | 0.83333 | 17.2 | 62.96 | 20.1325 | 62.96
1977-11-08 | 8 | 11 | 0.875 | 16.7 | 62.06 | 19.7568 | 62.06
1977-11-08 | 8 | 11 | 0.91667 | 16.7 | 62.06 | 19.7568 |  | 62.06
1977-11-08 | 8 | 11 | 0.95833 | 16.7 | 62.06 | 19.4991 |  | 62.06
1977-11-08 | 8 | 11 | 1 | 16.7 | 62.06 | 19.4991 |  | 62.06
1977-11-09 | 9 | 11 | 0.041667 | 16.1 | 60.98 | 19.4359 |  | 60.98
1977-11-09 | 9 | 11 | 0.083333 | 16.7 | 62.06 | 19.8857 |  | 62.06
1977-11-09 | 9 | 11 | 0.125 | 16.7 | 62.06 | 20.2727 |  | 62.06
1977-11-09 | 9 | 11 | 0.16667 | 16.1 | 60.98 | 20.3048 |  | 60.98
1977-11-09 | 9 | 11 | 0.20833 | 16.1 | 60.98 | 19.808 |  | 60.98
1977-11-09 | 9 | 11 | 0.25 | 15.6 | 60.08 | 20.2678 | 60.08
1977-11-09 | 9 | 11 | 0.29167 | 16.1 | 60.98 | 20.5534 | 60.98
1977-11-09 | 9 | 11 | 0.33333 | 17.2 | 62.96 | 20.9323 | 62.96
1977-11-09 | 9 | 11 | 0.375 | 18.3 | 64.94 | 21.6911 | 64.94
1977-11-09 | 9 | 11 | 0.41667 | 19.4 | 66.92 | 22.764 | 66.92
1977-11-09 | 9 | 11 | 0.45833 | 20 | 68 | 23.1235 | 68
1977-11-09 | 9 | 11 | 0.5 | 21.1 | 69.98 | 23.916 | 69.98
1977-11-09 | 9 | 11 | 0.54167 | 20.6 | 69.08 | 23.9777 | 69.08
1977-11-09 | 9 | 11 | 0.58333 | 20 | 68 | 24.0837 | 68
1977-11-09 | 9 | 11 | 0.625 | 19.4 | 66.92 | 23.8427 | 66.92
1977-11-09 | 9 | 11 | 0.66667 | 18.3 | 64.94 | 23.5586 | 64.94
1977-11-09 | 9 | 11 | 0.70833 | 17.8 | 64.04 | 23.6484 | 64.04
1977-11-09 | 9 | 11 | 0.75 | 17.2 | 62.96 | 23.4773 | 62.96
1977-11-09 | 9 | 11 | 0.79167 | 16.1 | 60.98 | 22.5492 | 60.98
1977-11-09 | 9 | 11 | 0.83333 | 15.6 | 60.08 | 22.4417 | 60.08
1977-11-09 | 9 | 11 | 0.875 | 15 | 59 | 22.4549 | 59
1977-11-09 | 9 | 11 | 0.91667 | 13.3 | 55.94 | 21.6695 |  | 55.94
1977-11-09 | 9 | 11 | 0.95833 | 11.7 | 53.06 | 21.3566 |  | 53.06
1977-11-09 | 9 | 11 | 1 | 11.7 | 53.06 | 21.3566 |  | 53.06
1977-11-10 | 10 | 11 | 0.041667 | 11.1 | 51.98 | 20.7536 |  | 51.98
1977-11-10 | 10 | 11 | 0.083333 | 10 | 50 | 19.3458 |  | 50
1977-11-10 | 10 | 11 | 0.125 | 8.3 | 46.94 | 17.8738 |  | 46.94
1977-11-10 | 10 | 11 | 0.16667 | 6.1 | 42.98 | 15.9182 |  | 42.98
1977-11-10 | 10 | 11 | 0.20833 | 6.1 | 42.98 | 15.9182 |  | 42.98
1977-11-10 | 10 | 11 | 0.25 | 6.1 | 42.98 | 15.9182 | 42.98
1977-11-10 | 10 | 11 | 0.29167 | 6.1 | 42.98 | 15.9182 | 42.98
1977-11-10 | 10 | 11 | 0.33333 | 6.7 | 44.06 | 16.1539 | 44.06
1977-11-10 | 10 | 11 | 0.375 | 7.2 | 44.96 | 16.2259 | 44.96
1977-11-10 | 10 | 11 | 0.41667 | 7.8 | 46.04 | 16.4315 | 46.04
1977-11-10 | 10 | 11 | 0.45833 | 8.9 | 48.02 | 16.7162 | 48.02
1977-11-10 | 10 | 11 | 0.5 | 10 | 50 | 16.6035 | 50
1977-11-10 | 10 | 11 | 0.54167 | 11.7 | 53.06 | 17.1572 | 53.06
1977-11-10 | 10 | 11 | 0.58333 | 12.2 | 53.96 | 16.8533 | 53.96
1977-11-10 | 10 | 11 | 0.625 | 12.8 | 55.04 | 16.7741 | 55.04
1977-11-10 | 10 | 11 | 0.66667 | 12.2 | 53.96 | 16.1838 | 53.96
1977-11-10 | 10 | 11 | 0.70833 | 11.1 | 51.98 | 15.567 | 51.98
1977-11-10 | 10 | 11 | 0.75 | 10.6 | 51.08 | 15.0768 | 51.08
1977-11-10 | 10 | 11 | 0.79167 | 10 | 50 | 14.9522 | 50
1977-11-10 | 10 | 11 | 0.83333 | 8.9 | 48.02 | 14.6454 | 48.02
1977-11-10 | 10 | 11 | 0.875 | 7.8 | 46.04 | 14.2968 | 46.04
1977-11-10 | 10 | 11 | 0.91667 | 6.7 | 44.06 | 13.5168 |  | 44.06
1977-11-10 | 10 | 11 | 0.95833 | 5.6 | 42.08 | 12.8839 |  | 42.08
1977-11-10 | 10 | 11 | 1 | 6.1 | 42.98 | 13.3885 |  | 42.98
1977-11-11 | 11 | 11 | 0.041667 | 5.6 | 42.08 | 13.3097 |  | 42.08
1977-11-11 | 11 | 11 | 0.083333 | 5.6 | 42.08 | 13.4923 |  | 42.08
1977-11-11 | 11 | 11 | 0.125 | 5.6 | 42.08 | 13.3097 |  | 42.08
1977-11-11 | 11 | 11 | 0.16667 | 5 | 41 | 12.9172 |  | 41
1977-11-11 | 11 | 11 | 0.20833 | 4.4 | 39.92 | 12.418 |  | 39.92
1977-11-11 | 11 | 11 | 0.25 | 3.9 | 39.02 | 12.1566 | 39.02
1977-11-11 | 11 | 11 | 0.29167 | 3.9 | 39.02 | 11.8872 | 39.02
1977-11-11 | 11 | 11 | 0.33333 | 3.9 | 39.02 | 11.6717 | 39.02
1977-11-11 | 11 | 11 | 0.375 | 5 | 41 | 12.0435 | 41
1977-11-11 | 11 | 11 | 0.41667 | 5.6 | 42.08 | 12.3372 | 42.08
1977-11-11 | 11 | 11 | 0.45833 | 6.7 | 44.06 | 12.8607 | 44.06
1977-11-11 | 11 | 11 | 0.5 | 8.3 | 46.94 | 13.6004 | 46.94
1977-11-11 | 11 | 11 | 0.54167 | 8.9 | 48.02 | 13.8053 | 48.02
1977-11-11 | 11 | 11 | 0.58333 | 10 | 50 | 14.5406 | 50
1977-11-11 | 11 | 11 | 0.625 | 10 | 50 | 14.5406 | 50
1977-11-11 | 11 | 11 | 0.66667 | 10 | 50 | 14.7875 | 50
1977-11-11 | 11 | 11 | 0.70833 | 10 | 50 | 14.7875 | 50
1977-11-11 | 11 | 11 | 0.75 | 9.4 | 48.92 | 14.2586 | 48.92
1977-11-11 | 11 | 11 | 0.79167 | 8.9 | 48.02 | 14.1869 | 48.02
1977-11-11 | 11 | 11 | 0.83333 | 8.9 | 48.02 | 14.1869 | 48.02
1977-11-11 | 11 | 11 | 0.875 | 7.8 | 46.04 | 13.8715 | 46.04
1977-11-11 | 11 | 11 | 0.91667 | 7.2 | 44.96 | 14.0412 |  | 44.96
1977-11-11 | 11 | 11 | 0.95833 | 6.7 | 44.06 | 13.7795 |  | 44.06
1977-11-11 | 11 | 11 | 1 | 6.1 | 42.98 | 13.5145 |  | 42.98
1977-11-12 | 12 | 11 | 0.041667 | 5.6 | 42.08 | 13.6141 |  | 42.08
1977-11-12 | 12 | 11 | 0.083333 | 5.6 | 42.08 | 13.6141 |  | 42.08
1977-11-12 | 12 | 11 | 0.125 | 5 | 41 | 13.0339 |  | 41
1977-11-12 | 12 | 11 | 0.16667 | 4.4 | 39.92 | 12.5298 |  | 39.92
1977-11-12 | 12 | 11 | 0.20833 | 3.3 | 37.94 | 12.3486 |  | 37.94
1977-11-12 | 12 | 11 | 0.25 | 3.3 | 37.94 | 12.1934 | 37.94
1977-11-12 | 12 | 11 | 0.29167 | 3.3 | 37.94 | 12.3486 | 37.94
1977-11-12 | 12 | 11 | 0.33333 | 4.4 | 39.92 | 12.5298 | 39.92
1977-11-12 | 12 | 11 | 0.375 | 6.1 | 42.98 | 13.2625 | 42.98
1977-11-12 | 12 | 11 | 0.41667 | 6.7 | 44.06 | 13.7795 | 44.06
1977-11-12 | 12 | 11 | 0.45833 | 8.9 | 48.02 | 14.7218 | 48.02
1977-11-12 | 12 | 11 | 0.5 | 6.7 | 44.06 | 13.6481 | 44.06
1977-11-12 | 12 | 11 | 0.54167 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-12 | 12 | 11 | 0.58333 | 11.1 | 51.98 | 15.7446 | 51.98
1977-11-12 | 12 | 11 | 0.625 | 11.1 | 51.98 | 15.7446 | 51.98
1977-11-12 | 12 | 11 | 0.66667 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-12 | 12 | 11 | 0.70833 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-12 | 12 | 11 | 0.75 | 10 | 50 | 15.1994 | 50
1977-11-12 | 12 | 11 | 0.79167 | 9.4 | 48.92 | 15.2868 | 48.92
1977-11-12 | 12 | 11 | 0.83333 | 9.4 | 48.92 | 15.4453 | 48.92
1977-11-12 | 12 | 11 | 0.875 | 9.4 | 48.92 | 16.0005 | 48.92
1977-11-12 | 12 | 11 | 0.91667 | 9.4 | 48.92 | 16.1593 |  | 48.92
1977-11-12 | 12 | 11 | 0.95833 | 9.4 | 48.92 | 16.0005 |  | 48.92
1977-11-12 | 12 | 11 | 1 | 9.4 | 48.92 | 15.6038 |  | 48.92
1977-11-13 | 13 | 11 | 0.041667 | 9.4 | 48.92 | 15.4453 |  | 48.92
1977-11-13 | 13 | 11 | 0.083333 | 9.4 | 48.92 | 15.4453 |  | 48.92
1977-11-13 | 13 | 11 | 0.125 | 9.4 | 48.92 | 15.6038 |  | 48.92
1977-11-13 | 13 | 11 | 0.16667 | 9.4 | 48.92 | 15.4453 |  | 48.92
1977-11-13 | 13 | 11 | 0.20833 | 10 | 50 | 15.8594 |  | 50
1977-11-13 | 13 | 11 | 0.25 | 10 | 50 | 15.8594 | 50
1977-11-13 | 13 | 11 | 0.29167 | 11.1 | 51.98 | 16.5446 | 51.98
1977-11-13 | 13 | 11 | 0.33333 | 11.1 | 51.98 | 16.9008 | 51.98
1977-11-13 | 13 | 11 | 0.375 | 11.7 | 53.06 | 17.3428 | 53.06
1977-11-13 | 13 | 11 | 0.41667 | 12.2 | 53.96 | 17.7161 | 53.96
1977-11-13 | 13 | 11 | 0.45833 | 12.8 | 55.04 | 18.2705 | 55.04
1977-11-13 | 13 | 11 | 0.5 | 13.3 | 55.94 | 18.8648 | 55.94
1977-11-13 | 13 | 11 | 0.54167 | 13.9 | 57.02 | 19.345 | 57.02
1977-11-13 | 13 | 11 | 0.58333 | 14.4 | 57.92 | 19.7512 | 57.92
1977-11-13 | 13 | 11 | 0.625 | 14.4 | 57.92 | 19.7512 | 57.92
1977-11-13 | 13 | 11 | 0.66667 | 14.4 | 57.92 | 19.974 | 57.92
1977-11-13 | 13 | 11 | 0.70833 | 13.9 | 57.02 | 19.5604 | 57.02
1977-11-13 | 13 | 11 | 0.75 | 12.8 | 55.04 | 19.0712 | 55.04
1977-11-13 | 13 | 11 | 0.79167 | 12.8 | 55.04 | 19.0712 | 55.04
1977-11-13 | 13 | 11 | 0.83333 | 11.7 | 53.06 | 19.5772 | 53.06
1977-11-13 | 13 | 11 | 0.875 | 12.2 | 53.96 | 19.0626 | 53.96
1977-11-13 | 13 | 11 | 0.91667 | 11.1 | 51.98 | 19.0458 |  | 51.98
1977-11-13 | 13 | 11 | 0.95833 | 10.6 | 51.08 | 18.3506 |  | 51.08
1977-11-13 | 13 | 11 | 1 | 10.6 | 51.08 | 18.3506 |  | 51.08
1977-11-14 | 14 | 11 | 0.041667 | 10 | 50 | 18.0966 |  | 50
1977-11-14 | 14 | 11 | 0.083333 | 9.4 | 48.92 | 17.8313 |  | 48.92
1977-11-14 | 14 | 11 | 0.125 | 10 | 50 | 18.0966 |  | 50
1977-11-14 | 14 | 11 | 0.16667 | 10 | 50 | 18.0966 |  | 50
1977-11-14 | 14 | 11 | 0.20833 | 10 | 50 | 18.3461 |  | 50
1977-11-14 | 14 | 11 | 0.25 | 9.4 | 48.92 | 17.8313 | 48.92
1977-11-14 | 14 | 11 | 0.29167 | 10 | 50 | 18.3461 | 50
1977-11-14 | 14 | 11 | 0.33333 | 10.6 | 51.08 | 18.8704 | 51.08
1977-11-14 | 14 | 11 | 0.375 | 11.1 | 51.98 | 19.3149 | 51.98
1977-11-14 | 14 | 11 | 0.41667 | 12.8 | 55.04 | 20.3765 | 55.04
1977-11-14 | 14 | 11 | 0.45833 | 16.1 | 60.98 | 20.5534 | 60.98
1977-11-14 | 14 | 11 | 0.5 | 16.7 | 62.06 | 20.5309 | 62.06
1977-11-14 | 14 | 11 | 0.54167 | 16.1 | 60.98 | 20.5534 | 60.98
1977-11-14 | 14 | 11 | 0.58333 | 16.1 | 60.98 | 20.9267 | 60.98
1977-11-14 | 14 | 11 | 0.625 | 16.1 | 60.98 | 21.7994 | 60.98
1977-11-14 | 14 | 11 | 0.66667 | 15 | 59 | 21.2907 | 59
1977-11-14 | 14 | 11 | 0.70833 | 13.9 | 57.02 | 21.614 | 57.02
1977-11-14 | 14 | 11 | 0.75 | 13.9 | 57.02 | 21.614 | 57.02
1977-11-14 | 14 | 11 | 0.79167 | 13.9 | 57.02 | 21.614 | 57.02
1977-11-14 | 14 | 11 | 0.83333 | 13.9 | 57.02 | 20.856 | 57.02
1977-11-14 | 14 | 11 | 0.875 | 13.9 | 57.02 | 20.856 | 57.02
1977-11-14 | 14 | 11 | 0.91667 | 13.3 | 55.94 | 20.524 |  | 55.94
1977-11-14 | 14 | 11 | 0.95833 | 13.3 | 55.94 | 20.836 |  | 55.94
1977-11-14 | 14 | 11 | 1 | 13.3 | 55.94 | 21.3567 |  | 55.94
1977-11-15 | 15 | 11 | 0.041667 | 12.8 | 55.04 | 21.1822 |  | 55.04
1977-11-15 | 15 | 11 | 0.083333 | 12.8 | 55.04 | 21.4848 |  | 55.04
1977-11-15 | 15 | 11 | 0.125 | 13.3 | 55.94 | 21.6695 |  | 55.94
1977-11-15 | 15 | 11 | 0.16667 | 13.3 | 55.94 | 21.6695 |  | 55.94
1977-11-15 | 15 | 11 | 0.20833 | 13.3 | 55.94 | 21.6695 |  | 55.94
1977-11-15 | 15 | 11 | 0.25 | 13.9 | 57.02 | 21.9394 | 57.02
1977-11-15 | 15 | 11 | 0.29167 | 13.3 | 55.94 | 21.6695 | 55.94
1977-11-15 | 15 | 11 | 0.33333 | 13.3 | 55.94 | 21.6695 | 55.94
1977-11-15 | 15 | 11 | 0.375 | 15 | 59 | 22.4549 | 59
1977-11-15 | 15 | 11 | 0.41667 | 17.2 | 62.96 | 23.4773 | 62.96
1977-11-15 | 15 | 11 | 0.45833 | 17.8 | 64.04 | 24.0676 | 64.04
1977-11-15 | 15 | 11 | 0.5 | 18.3 | 64.94 | 24.2796 | 64.94
1977-11-15 | 15 | 11 | 0.54167 | 20 | 68 | 25.0466 | 68
1977-11-15 | 15 | 11 | 0.58333 | 20 | 68 | 25.0466 | 68
1977-11-15 | 15 | 11 | 0.625 | 20 | 68 | 25.3681 | 68
1977-11-15 | 15 | 11 | 0.66667 | 18.9 | 66.02 | 24.8801 | 66.02
1977-11-15 | 15 | 11 | 0.70833 | 18.9 | 66.02 | 24.58 | 66.02
1977-11-15 | 15 | 11 | 0.75 | 16.1 | 60.98 | 20.9267 | 60.98
1977-11-15 | 15 | 11 | 0.79167 | 15 | 59 | 20.2463 | 59
1977-11-15 | 15 | 11 | 0.83333 | 14.4 | 57.92 | 19.7512 | 57.92
1977-11-15 | 15 | 11 | 0.875 | 13.9 | 57.02 | 19.5604 | 57.02
1977-11-15 | 15 | 11 | 0.91667 | 12.8 | 55.04 | 18.8709 |  | 55.04
1977-11-15 | 15 | 11 | 0.95833 | 12.2 | 53.96 | 18.1003 |  | 53.96
1977-11-15 | 15 | 11 | 1 | 11.7 | 53.06 | 17.5284 |  | 53.06
1977-11-16 | 16 | 11 | 0.041667 | 11.1 | 51.98 | 17.2574 |  | 51.98
1977-11-16 | 16 | 11 | 0.083333 | 10.6 | 51.08 | 17.227 |  | 51.08
1977-11-16 | 16 | 11 | 0.125 | 10 | 50 | 16.7691 |  | 50
1977-11-16 | 16 | 11 | 0.16667 | 9.4 | 48.92 | 16.7157 |  | 48.92
1977-11-16 | 16 | 11 | 0.20833 | 10 | 50 | 17.0176 |  | 50
1977-11-16 | 16 | 11 | 0.25 | 10 | 50 | 16.7691 | 50
1977-11-16 | 16 | 11 | 0.29167 | 10 | 50 | 16.6035 | 50
1977-11-16 | 16 | 11 | 0.33333 | 9.4 | 48.92 | 16.3977 | 48.92
1977-11-16 | 16 | 11 | 0.375 | 10 | 50 | 16.7691 | 50
1977-11-16 | 16 | 11 | 0.41667 | 10 | 50 | 16.438 | 50
1977-11-16 | 16 | 11 | 0.45833 | 10.6 | 51.08 | 16.7097 | 51.08
1977-11-16 | 16 | 11 | 0.5 | 10.6 | 51.08 | 17.0545 | 51.08
1977-11-16 | 16 | 11 | 0.54167 | 10.6 | 51.08 | 17.0545 | 51.08
1977-11-16 | 16 | 11 | 0.58333 | 10 | 50 | 16.7691 | 50
1977-11-16 | 16 | 11 | 0.625 | 10 | 50 | 17.0176 | 50
1977-11-16 | 16 | 11 | 0.66667 | 10 | 50 | 16.6035 | 50
1977-11-16 | 16 | 11 | 0.70833 | 10 | 50 | 16.438 | 50
1977-11-16 | 16 | 11 | 0.75 | 10 | 50 | 16.2726 | 50
1977-11-16 | 16 | 11 | 0.79167 | 10 | 50 | 15.5292 | 50
1977-11-16 | 16 | 11 | 0.83333 | 11.1 | 51.98 | 16.3667 | 51.98
1977-11-16 | 16 | 11 | 0.875 | 10.6 | 51.08 | 16.0212 | 51.08
1977-11-16 | 16 | 11 | 0.91667 | 10 | 50 | 16.2726 |  | 50
1977-11-16 | 16 | 11 | 0.95833 | 9.4 | 48.92 | 16.3977 |  | 48.92
1977-11-16 | 16 | 11 | 1 | 8.9 | 48.02 | 15.2576 |  | 48.02
1977-11-17 | 17 | 11 | 0.041667 | 9.4 | 48.92 | 16.1593 |  | 48.92
1977-11-17 | 17 | 11 | 0.083333 | 9.4 | 48.92 | 16.5567 |  | 48.92
1977-11-17 | 17 | 11 | 0.125 | 9.4 | 48.92 | 16.5567 |  | 48.92
1977-11-17 | 17 | 11 | 0.16667 | 8.9 | 48.02 | 16.1781 |  | 48.02
1977-11-17 | 17 | 11 | 0.20833 | 8.9 | 48.02 | 16.5624 |  | 48.02
1977-11-17 | 17 | 11 | 0.25 | 8.9 | 48.02 | 16.5624 | 48.02
1977-11-17 | 17 | 11 | 0.29167 | 7.8 | 46.04 | 15.149 | 46.04
1977-11-17 | 17 | 11 | 0.33333 | 7.8 | 46.04 | 15.2913 | 46.04
1977-11-17 | 17 | 11 | 0.375 | 8.3 | 46.94 | 16.4679 | 46.94
1977-11-17 | 17 | 11 | 0.41667 | 10 | 50 | 17.8473 | 50
1977-11-17 | 17 | 11 | 0.45833 | 10 | 50 | 17.8473 | 50
1977-11-17 | 17 | 11 | 0.5 | 11.1 | 51.98 | 18.5978 | 51.98
1977-11-17 | 17 | 11 | 0.54167 | 11.7 | 53.06 | 19.2971 | 53.06
1977-11-17 | 17 | 11 | 0.58333 | 12.8 | 55.04 | 20.0748 | 55.04
1977-11-17 | 17 | 11 | 0.625 | 12.2 | 53.96 | 20.0277 | 53.96
1977-11-17 | 17 | 11 | 0.66667 | 12.2 | 53.96 | 19.7379 | 53.96
1977-11-17 | 17 | 11 | 0.70833 | 12.8 | 55.04 | 20.3765 | 55.04
1977-11-17 | 17 | 11 | 0.75 | 12.2 | 53.96 | 20.3177 | 53.96
1977-11-17 | 17 | 11 | 0.79167 | 12.8 | 55.04 | 20.5777 | 55.04
1977-11-17 | 17 | 11 | 0.83333 | 13.3 | 55.94 | 20.836 | 55.94
1977-11-17 | 17 | 11 | 0.875 | 12.8 | 55.04 | 20.8798 | 55.04
1977-11-17 | 17 | 11 | 0.91667 | 12.2 | 53.96 | 20.608 |  | 53.96
1977-11-17 | 17 | 11 | 0.95833 | 11.7 | 53.06 | 20.4189 |  | 53.06
1977-11-17 | 17 | 11 | 1 | 11.7 | 53.06 | 20.4189 |  | 53.06
1977-11-18 | 18 | 11 | 0.041667 | 11.7 | 53.06 | 20.4189 |  | 53.06
1977-11-18 | 18 | 11 | 0.083333 | 11.1 | 51.98 | 20.3933 |  | 51.98
1977-11-18 | 18 | 11 | 0.125 | 11.1 | 51.98 | 20.1234 |  | 51.98
1977-11-18 | 18 | 11 | 0.16667 | 11.1 | 51.98 | 20.3933 |  | 51.98
1977-11-18 | 18 | 11 | 0.20833 | 10.6 | 51.08 | 19.9124 |  | 51.08
1977-11-18 | 18 | 11 | 0.25 | 10.6 | 51.08 | 19.9124 | 51.08
1977-11-18 | 18 | 11 | 0.29167 | 11.7 | 53.06 | 20.7 | 53.06
1977-11-18 | 18 | 11 | 0.33333 | 11.7 | 53.06 | 20.7 | 53.06
1977-11-18 | 18 | 11 | 0.375 | 12.2 | 53.96 | 21.1894 | 53.96
1977-11-18 | 18 | 11 | 0.41667 | 12.2 | 53.96 | 21.5775 | 53.96
1977-11-18 | 18 | 11 | 0.45833 | 12.8 | 55.04 | 21.7877 | 55.04
1977-11-18 | 18 | 11 | 0.5 | 13.3 | 55.94 | 22.7141 | 55.94
1977-11-18 | 18 | 11 | 0.54167 | 12.8 | 55.04 | 22.7994 | 55.04
1977-11-18 | 18 | 11 | 0.58333 | 12.8 | 55.04 | 23.2049 | 55.04
1977-11-18 | 18 | 11 | 0.625 | 13.3 | 55.94 | 23.4473 | 55.94
1977-11-18 | 18 | 11 | 0.66667 | 13.9 | 57.02 | 24.0074 | 57.02
1977-11-18 | 18 | 11 | 0.70833 | 13.9 | 57.02 | 24.0074 | 57.02
1977-11-18 | 18 | 11 | 0.75 | 14.4 | 57.92 | 24.6857 | 57.92
1977-11-18 | 18 | 11 | 0.79167 | 13.9 | 57.02 | 24.4443 | 57.02
1977-11-18 | 18 | 11 | 0.83333 | 15.6 | 60.08 | 25.9735 | 60.08
1977-11-18 | 18 | 11 | 0.875 | 15 | 59 | 25.7359 | 59
1977-11-18 | 18 | 11 | 0.91667 | 15.6 | 60.08 | 25.6064 |  | 60.08
1977-11-18 | 18 | 11 | 0.95833 | 15 | 59 | 24.9127 |  | 59
1977-11-18 | 18 | 11 | 1 | 14.4 | 57.92 | 24.6857 |  | 57.92
1977-11-19 | 19 | 11 | 0.041667 | 14.4 | 57.92 | 24.6857 |  | 57.92
1977-11-19 | 19 | 11 | 0.083333 | 15 | 59 | 24.9127 |  | 59
1977-11-19 | 19 | 11 | 0.125 | 15 | 59 | 23.7401 |  | 59
1977-11-19 | 19 | 11 | 0.16667 | 15 | 59 | 22.1052 |  | 59
1977-11-19 | 19 | 11 | 0.20833 | 14.4 | 57.92 | 21.3136 |  | 57.92
1977-11-19 | 19 | 11 | 0.25 | 13.9 | 57.02 | 20.3156 | 57.02
1977-11-19 | 19 | 11 | 0.29167 | 13.3 | 55.94 | 19.7971 | 55.94
1977-11-19 | 19 | 11 | 0.33333 | 13.3 | 55.94 | 19.2788 | 55.94
1977-11-19 | 19 | 11 | 0.375 | 13.3 | 55.94 | 18.8648 | 55.94
1977-11-19 | 19 | 11 | 0.41667 | 13.9 | 57.02 | 18.6995 | 57.02
1977-11-19 | 19 | 11 | 0.45833 | 13.9 | 57.02 | 18.3771 | 57.02
1977-11-19 | 19 | 11 | 0.5 | 14.4 | 57.92 | 18.5287 | 57.92
1977-11-19 | 19 | 11 | 0.54167 | 15.6 | 60.08 | 18.8262 | 60.08
1977-11-19 | 19 | 11 | 0.58333 | 15.6 | 60.08 | 18.7063 | 60.08
1977-11-19 | 19 | 11 | 0.625 | 15.6 | 60.08 | 18.7063 | 60.08
1977-11-19 | 19 | 11 | 0.66667 | 15.6 | 60.08 | 18.347 | 60.08
1977-11-19 | 19 | 11 | 0.70833 | 15 | 59 | 18.0518 | 59
1977-11-19 | 19 | 11 | 0.75 | 13.9 | 57.02 | 17.7334 | 57.02
1977-11-19 | 19 | 11 | 0.79167 | 13.3 | 55.94 | 17.3165 | 55.94
1977-11-19 | 19 | 11 | 0.83333 | 12.2 | 53.96 | 17.0449 | 53.96
1977-11-19 | 19 | 11 | 0.875 | 11.7 | 53.06 | 16.6012 | 53.06
1977-11-19 | 19 | 11 | 0.91667 | 11.1 | 51.98 | 16.5446 |  | 51.98
1977-11-19 | 19 | 11 | 0.95833 | 10.6 | 51.08 | 16.5375 |  | 51.08
1977-11-19 | 19 | 11 | 1 | 10 | 50 | 16.2726 |  | 50
1977-11-20 | 20 | 11 | 0.041667 | 9.4 | 48.92 | 16.0005 |  | 48.92
1977-11-20 | 20 | 11 | 0.083333 | 8.9 | 48.02 | 15.7943 |  | 48.02
1977-11-20 | 20 | 11 | 0.125 | 8.3 | 46.94 | 15.5094 |  | 46.94
1977-11-20 | 20 | 11 | 0.16667 | 8.3 | 46.94 | 15.3622 |  | 46.94
1977-11-20 | 20 | 11 | 0.20833 | 8.3 | 46.94 | 15.5094 |  | 46.94
1977-11-20 | 20 | 11 | 0.25 | 8.3 | 46.94 | 15.5094 | 46.94
1977-11-20 | 20 | 11 | 0.29167 | 7.8 | 46.04 | 15.2913 | 46.04
1977-11-20 | 20 | 11 | 0.33333 | 7.8 | 46.04 | 15.5048 | 46.04
1977-11-20 | 20 | 11 | 0.375 | 8.3 | 46.94 | 15.5094 | 46.94
1977-11-20 | 20 | 11 | 0.41667 | 8.9 | 48.02 | 15.7943 | 48.02
1977-11-20 | 20 | 11 | 0.45833 | 8.9 | 48.02 | 15.7943 | 48.02
1977-11-20 | 20 | 11 | 0.5 | 9.4 | 48.92 | 16.0005 | 48.92
1977-11-20 | 20 | 11 | 0.54167 | 10 | 50 | 16.2726 | 50
1977-11-20 | 20 | 11 | 0.58333 | 10.6 | 51.08 | 16.5375 | 51.08
1977-11-20 | 20 | 11 | 0.625 | 10.6 | 51.08 | 16.1932 | 51.08
1977-11-20 | 20 | 11 | 0.66667 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-20 | 20 | 11 | 0.70833 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-20 | 20 | 11 | 0.75 | 10.6 | 51.08 | 16.0212 | 51.08
1977-11-20 | 20 | 11 | 0.79167 | 10.6 | 51.08 | 16.0212 | 51.08
1977-11-20 | 20 | 11 | 0.83333 | 10.6 | 51.08 | 16.1932 | 51.08
1977-11-20 | 20 | 11 | 0.875 | 10 | 50 | 16.1073 | 50
1977-11-20 | 20 | 11 | 0.91667 | 8.9 | 48.02 | 15.9478 |  | 48.02
1977-11-20 | 20 | 11 | 0.95833 | 9.4 | 48.92 | 16.3977 |  | 48.92
1977-11-20 | 20 | 11 | 1 | 8.9 | 48.02 | 15.9478 |  | 48.02
1977-11-21 | 21 | 11 | 0.041667 | 8.3 | 46.94 | 15.5094 |  | 46.94
1977-11-21 | 21 | 11 | 0.083333 | 8.3 | 46.94 | 15.6567 |  | 46.94
1977-11-21 | 21 | 11 | 0.125 | 7.8 | 46.04 | 15.8609 |  | 46.04
1977-11-21 | 21 | 11 | 0.16667 | 7.8 | 46.04 | 16.2174 |  | 46.04
1977-11-21 | 21 | 11 | 0.20833 | 8.3 | 46.94 | 16.8373 |  | 46.94
1977-11-21 | 21 | 11 | 0.25 | 8.9 | 48.02 | 17.6407 | 48.02
1977-11-21 | 21 | 11 | 0.29167 | 8.9 | 48.02 | 17.8722 | 48.02
1977-11-21 | 21 | 11 | 0.33333 | 11.7 | 53.06 | 19.5772 | 53.06
1977-11-21 | 21 | 11 | 0.375 | 12.2 | 53.96 | 20.3177 | 53.96
1977-11-21 | 21 | 11 | 0.41667 | 13.3 | 55.94 | 21.1483 | 55.94
1977-11-21 | 21 | 11 | 0.45833 | 13.9 | 57.02 | 21.3973 | 57.02
1977-11-21 | 21 | 11 | 0.5 | 14.4 | 57.92 | 22.2096 | 57.92
1977-11-21 | 21 | 11 | 0.54167 | 14.4 | 57.92 | 22.5462 | 57.92
1977-11-21 | 21 | 11 | 0.58333 | 14.4 | 57.92 | 23.2204 | 57.92
1977-11-21 | 21 | 11 | 0.625 | 14.4 | 57.92 | 23.558 | 57.92
1977-11-21 | 21 | 11 | 0.66667 | 15 | 59 | 24.9127 | 59
1977-11-21 | 21 | 11 | 0.70833 | 15.6 | 60.08 | 25.6064 | 60.08
1977-11-21 | 21 | 11 | 0.75 | 16.1 | 60.98 | 26.1965 | 60.98
1977-11-21 | 21 | 11 | 0.79167 | 15.6 | 60.08 | 25.9735 | 60.08
1977-11-21 | 21 | 11 | 0.83333 | 16.1 | 60.98 | 26.1965 | 60.98
1977-11-21 | 21 | 11 | 0.875 | 16.1 | 60.98 | 26.1965 | 60.98
1977-11-21 | 21 | 11 | 0.91667 | 16.1 | 60.98 | 26.7027 |  | 60.98
1977-11-21 | 21 | 11 | 0.95833 | 16.1 | 60.98 | 26.7027 |  | 60.98
1977-11-21 | 21 | 11 | 1 | 16.7 | 62.06 | 26.5249 |  | 62.06
1977-11-22 | 22 | 11 | 0.041667 | 16.7 | 62.06 | 26.5249 |  | 62.06
1977-11-22 | 22 | 11 | 0.083333 | 16.7 | 62.06 | 25.9995 |  | 62.06
1977-11-22 | 22 | 11 | 0.125 | 15.6 | 60.08 | 25.2398 |  | 60.08
1977-11-22 | 22 | 11 | 0.16667 | 14.4 | 57.92 | 23.2204 |  | 57.92
1977-11-22 | 22 | 11 | 0.20833 | 13.3 | 55.94 | 22.087 |  | 55.94
1977-11-22 | 22 | 11 | 0.25 | 12.8 | 55.04 | 20.0748 | 55.04
1977-11-22 | 22 | 11 | 0.29167 | 12.2 | 53.96 | 17.7161 | 53.96
1977-11-22 | 22 | 11 | 0.33333 | 11.7 | 53.06 | 17.3428 | 53.06
1977-11-22 | 22 | 11 | 0.375 | 12.2 | 53.96 | 17.2365 | 53.96
1977-11-22 | 22 | 11 | 0.41667 | 12.8 | 55.04 | 17.4716 | 55.04
1977-11-22 | 22 | 11 | 0.45833 | 12.8 | 55.04 | 17.0729 | 55.04
1977-11-22 | 22 | 11 | 0.5 | 12.8 | 55.04 | 17.2722 | 55.04
1977-11-22 | 22 | 11 | 0.54167 | 13.3 | 55.94 | 17.0077 | 55.94
1977-11-22 | 22 | 11 | 0.58333 | 13.3 | 55.94 | 17.0077 | 55.94
1977-11-22 | 22 | 11 | 0.625 | 12.8 | 55.04 | 16.9733 | 55.04
1977-11-22 | 22 | 11 | 0.66667 | 12.2 | 53.96 | 16.6619 | 53.96
1977-11-22 | 22 | 11 | 0.70833 | 10.6 | 51.08 | 15.6775 | 51.08
1977-11-22 | 22 | 11 | 0.75 | 10 | 50 | 15.1994 | 50
1977-11-22 | 22 | 11 | 0.79167 | 8.9 | 48.02 | 14.6454 | 48.02
1977-11-22 | 22 | 11 | 0.83333 | 7.8 | 46.04 | 13.5882 | 46.04
1977-11-22 | 22 | 11 | 0.875 | 6.1 | 42.98 | 12.6332 | 42.98
1977-11-22 | 22 | 11 | 0.91667 | 5.6 | 42.08 | 12.5194 |  | 42.08
1977-11-22 | 22 | 11 | 0.95833 | 5 | 41 | 12.0435 |  | 41
1977-11-22 | 22 | 11 | 1 | 4.4 | 39.92 | 11.6925 |  | 39.92
1977-11-23 | 23 | 11 | 0.041667 | 3.9 | 39.02 | 11.3489 |  | 39.02
1977-11-23 | 23 | 11 | 0.083333 | 3.3 | 37.94 | 10.9034 |  | 37.94
1977-11-23 | 23 | 11 | 0.125 | 2.8 | 37.04 | 10.7731 |  | 37.04
1977-11-23 | 23 | 11 | 0.16667 | 2.8 | 37.04 | 10.7731 |  | 37.04
1977-11-23 | 23 | 11 | 0.20833 | 2.2 | 35.96 | 10.5293 |  | 35.96
1977-11-23 | 23 | 11 | 0.25 | 2.2 | 35.96 | 10.5293 | 35.96
1977-11-23 | 23 | 11 | 0.29167 | 2.8 | 37.04 | 10.8725 | 37.04
1977-11-23 | 23 | 11 | 0.33333 | 2.8 | 37.04 | 10.8725 | 37.04
1977-11-23 | 23 | 11 | 0.375 | 3.3 | 37.94 | 11.2125 | 37.94
1977-11-23 | 23 | 11 | 0.41667 | 5 | 41 | 11.9271 | 41
1977-11-23 | 23 | 11 | 0.45833 | 6.1 | 42.98 | 12.3191 | 42.98
1977-11-23 | 23 | 11 | 0.5 | 7.2 | 44.96 | 12.6829 | 44.96
1977-11-23 | 23 | 11 | 0.54167 | 7.8 | 46.04 | 12.8811 | 46.04
1977-11-23 | 23 | 11 | 0.58333 | 7.8 | 46.04 | 13.0931 | 46.04
1977-11-23 | 23 | 11 | 0.625 | 7.8 | 46.04 | 13.1638 | 46.04
1977-11-23 | 23 | 11 | 0.66667 | 6.7 | 44.06 | 12.6641 | 44.06
1977-11-23 | 23 | 11 | 0.70833 | 3.3 | 37.94 | 12.3486 | 37.94
1977-11-23 | 23 | 11 | 0.75 | 3.3 | 37.94 | 12.0383 | 37.94
1977-11-23 | 23 | 11 | 0.79167 | 2.2 | 35.96 | 10.5293 | 35.96
1977-11-23 | 23 | 11 | 0.83333 | 1.1 | 33.98 | 9.7326 | 33.98
1977-11-23 | 23 | 11 | 0.875 | 0 | 32 | 9.0137 | 32
1977-11-23 | 23 | 11 | 0.91667 | -1.1 | 30.02 | 8.3475 |  | 30.02
1977-11-23 | 23 | 11 | 0.95833 | -1.7 | 28.94 | 8.0321 |  | 28.94
1977-11-23 | 23 | 11 | 1 | -2.2 | 28.04 | 7.9395 |  | 28.04
1977-11-24 | 24 | 11 | 0.041667 | -2.8 | 26.96 | 7.6203 |  | 26.96
1977-11-24 | 24 | 11 | 0.083333 | -3.3 | 26.06 | 7.6017 |  | 26.06
1977-11-24 | 24 | 11 | 0.125 | -3.3 | 26.06 | 7.6631 |  | 26.06
1977-11-24 | 24 | 11 | 0.16667 | -2.8 | 26.96 | 8.0365 |  | 26.96
1977-11-24 | 24 | 11 | 0.20833 | -3.3 | 26.06 | 7.7245 |  | 26.06
1977-11-24 | 24 | 11 | 0.25 | -3.3 | 26.06 | 7.878 | 26.06
1977-11-24 | 24 | 11 | 0.29167 | -2.8 | 26.96 | 8.1005 | 26.96
1977-11-24 | 24 | 11 | 0.33333 | -2.2 | 28.04 | 8.2763 | 28.04
1977-11-24 | 24 | 11 | 0.375 | -1.7 | 28.94 | 8.559 | 28.94
1977-11-24 | 24 | 11 | 0.41667 | -1.1 | 30.02 | 8.7539 | 30.02
1977-11-24 | 24 | 11 | 0.45833 | 0 | 32 | 9.2973 | 32
1977-11-24 | 24 | 11 | 0.5 | 1.7 | 35.06 | 10.154 | 35.06
1977-11-24 | 24 | 11 | 0.54167 | 2.2 | 35.96 | 10.1962 | 35.96
1977-11-24 | 24 | 11 | 0.58333 | 2.8 | 37.04 | 10.475 | 37.04
1977-11-24 | 24 | 11 | 0.625 | 3.3 | 37.94 | 10.7489 | 37.94
1977-11-24 | 24 | 11 | 0.66667 | 3.9 | 39.02 | 10.9189 | 39.02
1977-11-24 | 24 | 11 | 0.70833 | 3.3 | 37.94 | 10.7489 | 37.94
1977-11-24 | 24 | 11 | 0.75 | 2.8 | 37.04 | 10.7731 | 37.04
1977-11-24 | 24 | 11 | 0.79167 | 2.8 | 37.04 | 10.8725 | 37.04
1977-11-24 | 24 | 11 | 0.83333 | 2.8 | 37.04 | 10.8725 | 37.04
1977-11-24 | 24 | 11 | 0.875 | 3.3 | 37.94 | 11.1094 | 37.94
1977-11-24 | 24 | 11 | 0.91667 | 3.3 | 37.94 | 11.1094 |  | 37.94
1977-11-24 | 24 | 11 | 0.95833 | 3.3 | 37.94 | 11.1094 |  | 37.94
1977-11-24 | 24 | 11 | 1 | 3.3 | 37.94 | 11.1094 |  | 37.94
1977-11-25 | 25 | 11 | 0.041667 | 3.3 | 37.94 | 11.4188 |  | 37.94
1977-11-25 | 25 | 11 | 0.083333 | 3.9 | 39.02 | 11.8872 |  | 39.02
1977-11-25 | 25 | 11 | 0.125 | 3.9 | 39.02 | 12.0488 |  | 39.02
1977-11-25 | 25 | 11 | 0.16667 | 3.9 | 39.02 | 12.1566 |  | 39.02
1977-11-25 | 25 | 11 | 0.20833 | 4.4 | 39.92 | 12.418 |  | 39.92
1977-11-25 | 25 | 11 | 0.25 | 4.4 | 39.92 | 12.418 | 39.92
1977-11-25 | 25 | 11 | 0.29167 | 5 | 41 | 12.6257 | 41
1977-11-25 | 25 | 11 | 0.33333 | 5.6 | 42.08 | 12.7623 | 42.08
1977-11-25 | 25 | 11 | 0.375 | 5.6 | 42.08 | 12.7623 | 42.08
1977-11-25 | 25 | 11 | 0.41667 | 6.7 | 44.06 | 13.2542 | 44.06
1977-11-25 | 25 | 11 | 0.45833 | 7.8 | 46.04 | 13.8715 | 46.04
1977-11-25 | 25 | 11 | 0.5 | 9.4 | 48.92 | 14.6537 | 48.92
1977-11-25 | 25 | 11 | 0.54167 | 10 | 50 | 15.117 | 50
1977-11-25 | 25 | 11 | 0.58333 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-25 | 25 | 11 | 0.625 | 10.6 | 51.08 | 15.5057 | 51.08
1977-11-25 | 25 | 11 | 0.66667 | 11.1 | 51.98 | 15.7446 | 51.98
1977-11-25 | 25 | 11 | 0.70833 | 10.6 | 51.08 | 15.6775 | 51.08
1977-11-25 | 25 | 11 | 0.75 | 10 | 50 | 15.5292 | 50
1977-11-25 | 25 | 11 | 0.79167 | 9.4 | 48.92 | 15.4453 | 48.92
1977-11-25 | 25 | 11 | 0.83333 | 9.4 | 48.92 | 15.2868 | 48.92
1977-11-25 | 25 | 11 | 0.875 | 8.9 | 48.02 | 14.9514 | 48.02
1977-11-25 | 25 | 11 | 0.91667 | 8.3 | 46.94 | 14.627 |  | 46.94
1977-11-25 | 25 | 11 | 0.95833 | 7.8 | 46.04 | 14.7937 |  | 46.04
1977-11-25 | 25 | 11 | 1 | 7.8 | 46.04 | 14.4387 |  | 46.04
1977-11-26 | 26 | 11 | 0.041667 | 8.3 | 46.94 | 14.627 |  | 46.94
1977-11-26 | 26 | 11 | 0.083333 | 7.8 | 46.04 | 14.2968 |  | 46.04
1977-11-26 | 26 | 11 | 0.125 | 7.2 | 44.96 | 13.9051 |  | 44.96
1977-11-26 | 26 | 11 | 0.16667 | 6.1 | 42.98 | 13.2625 |  | 42.98
1977-11-26 | 26 | 11 | 0.20833 | 6.1 | 42.98 | 13.0106 |  | 42.98
1977-11-26 | 26 | 11 | 0.25 | 6.1 | 42.98 | 13.2625 | 42.98
1977-11-26 | 26 | 11 | 0.29167 | 5.6 | 42.08 | 12.5194 | 42.08
1977-11-26 | 26 | 11 | 0.33333 | 5.6 | 42.08 | 12.6408 | 42.08
1977-11-26 | 26 | 11 | 0.375 | 6.1 | 42.98 | 12.6332 | 42.98
1977-11-26 | 26 | 11 | 0.41667 | 6.7 | 44.06 | 12.8607 | 44.06
1977-11-26 | 26 | 11 | 0.45833 | 7.2 | 44.96 | 13.0219 | 44.96
1977-11-26 | 26 | 11 | 0.5 | 7.2 | 44.96 | 12.8863 | 44.96
1977-11-26 | 26 | 11 | 0.54167 | 6.7 | 44.06 | 12.7951 | 44.06
1977-11-26 | 26 | 11 | 0.58333 | 7.2 | 44.96 | 13.0219 | 44.96
1977-11-26 | 26 | 11 | 0.625 | 6.7 | 44.06 | 12.6641 | 44.06
1977-11-26 | 26 | 11 | 0.66667 | 6.7 | 44.06 | 12.6641 | 44.06
1977-11-26 | 26 | 11 | 0.70833 | 5.6 | 42.08 | 12.2159 | 42.08
1977-11-26 | 26 | 11 | 0.75 | 5 | 41 | 11.9271 | 41
1977-11-26 | 26 | 11 | 0.79167 | 3.9 | 39.02 | 11.3489 | 39.02
1977-11-26 | 26 | 11 | 0.83333 | 3.3 | 37.94 | 11.1094 | 37.94
1977-11-26 | 26 | 11 | 0.875 | 2.2 | 35.96 | 10.6246 | 35.96
1977-11-26 | 26 | 11 | 0.91667 | 1.7 | 35.06 | 10.4295 |  | 35.06
1977-11-26 | 26 | 11 | 0.95833 | 1.1 | 33.98 | 10.1721 |  | 33.98
1977-11-26 | 26 | 11 | 1 | 0.6 | 33.08 | 9.9261 |  | 33.08
1977-11-27 | 27 | 11 | 0.041667 | 0 | 32 | 9.5811 |  | 32
1977-11-27 | 27 | 11 | 0.083333 | -0.6 | 30.92 | 9.3062 |  | 30.92
1977-11-27 | 27 | 11 | 0.125 | -1.1 | 30.02 | 9.0128 |  | 30.02
1977-11-27 | 27 | 11 | 0.16667 | -2.2 | 28.04 | 8.546 |  | 28.04
1977-11-27 | 27 | 11 | 0.20833 | -2.2 | 28.04 | 8.6135 |  | 28.04
1977-11-27 | 27 | 11 | 0.25 | -2.8 | 26.96 | 8.357 | 26.96
1977-11-27 | 27 | 11 | 0.29167 | -2.8 | 26.96 | 8.4532 | 26.96
1977-11-27 | 27 | 11 | 0.33333 | -2.8 | 26.96 | 8.4532 | 26.96
1977-11-27 | 27 | 11 | 0.375 | -2.2 | 28.04 | 8.816 | 28.04
1977-11-27 | 27 | 11 | 0.41667 | -1.1 | 30.02 | 9.42 | 30.02
1977-11-27 | 27 | 11 | 0.45833 | -0.6 | 30.92 | 9.7309 | 30.92
1977-11-27 | 27 | 11 | 0.5 | 0.6 | 33.08 | 10.3504 | 33.08
1977-11-27 | 27 | 11 | 0.54167 | 1.1 | 33.98 | 10.4361 | 33.98
1977-11-27 | 27 | 11 | 0.58333 | 1.7 | 35.06 | 10.9351 | 35.06
1977-11-27 | 27 | 11 | 0.625 | 2.2 | 35.96 | 11.4351 | 35.96
1977-11-27 | 27 | 11 | 0.66667 | 2.8 | 37.04 | 11.9681 | 37.04
1977-11-27 | 27 | 11 | 0.70833 | 3.3 | 37.94 | 12.5038 | 37.94
1977-11-27 | 27 | 11 | 0.75 | 3.9 | 39.02 | 12.9122 | 39.02
1977-11-27 | 27 | 11 | 0.79167 | 5 | 41 | 13.5595 | 41
1977-11-27 | 27 | 11 | 0.83333 | 5 | 41 | 14.0858 | 41
1977-11-27 | 27 | 11 | 0.875 | 5 | 41 | 14.0858 | 41
1977-11-27 | 27 | 11 | 0.91667 | 6.7 | 44.06 | 14.8327 |  | 44.06
1977-11-27 | 27 | 11 | 0.95833 | 6.7 | 44.06 | 14.8327 |  | 44.06
1977-11-27 | 27 | 11 | 1 | 6.7 | 44.06 | 16.1539 |  | 44.06
1977-11-28 | 28 | 11 | 0.041667 | 6.7 | 44.06 | 16.6838 |  | 44.06
1977-11-28 | 28 | 11 | 0.083333 | 6.1 | 42.98 | 16.4264 |  | 42.98
1977-11-28 | 28 | 11 | 0.125 | 7.2 | 44.96 | 17.1175 |  | 44.96
1977-11-28 | 28 | 11 | 0.16667 | 7.8 | 46.04 | 17.6471 |  | 46.04
1977-11-28 | 28 | 11 | 0.20833 | 8.3 | 46.94 | 18.0963 |  | 46.94
1977-11-28 | 28 | 11 | 0.25 | 8.9 | 48.02 | 18.8772 | 48.02
1977-11-28 | 28 | 11 | 0.29167 | 9.4 | 48.92 | 19.4313 | 48.92
1977-11-28 | 28 | 11 | 0.33333 | 9.4 | 48.92 | 19.4313 | 48.92
1977-11-28 | 28 | 11 | 0.375 | 10 | 50 | 19.9304 | 50
1977-11-28 | 28 | 11 | 0.41667 | 11.7 | 53.06 | 22.0145 | 53.06
1977-11-28 | 28 | 11 | 0.45833 | 14.4 | 57.92 | 25.0248 | 57.92
1977-11-28 | 28 | 11 | 0.5 | 14.4 | 57.92 | 25.0248 | 57.92
1977-11-28 | 28 | 11 | 0.54167 | 15 | 59 | 25.7359 | 59
1977-11-28 | 28 | 11 | 0.58333 | 16.7 | 62.06 | 27.3145 | 62.06
1977-11-28 | 28 | 11 | 0.625 | 16.1 | 60.98 | 26.1965 | 60.98
1977-11-28 | 28 | 11 | 0.66667 | 16.7 | 62.06 | 26.9195 | 62.06
1977-11-28 | 28 | 11 | 0.70833 | 17.2 | 62.96 | 27.5346 | 62.96
1977-11-28 | 28 | 11 | 0.75 | 18.3 | 64.94 | 26.7424 | 64.94
1977-11-28 | 28 | 11 | 0.79167 | 15 | 59 | 23.5061 | 59
1977-11-28 | 28 | 11 | 0.83333 | 14.4 | 57.92 | 22.2096 | 57.92
1977-11-28 | 28 | 11 | 0.875 | 13.9 | 57.02 | 21.3973 | 57.02
1977-11-28 | 28 | 11 | 0.91667 | 13.3 | 55.94 | 20.524 |  | 55.94
1977-11-28 | 28 | 11 | 0.95833 | 12.8 | 55.04 | 19.0712 |  | 55.04
1977-11-28 | 28 | 11 | 1 | 12.8 | 55.04 | 18.2705 |  | 55.04
1977-11-29 | 29 | 11 | 0.041667 | 12.8 | 55.04 | 16.9733 |  | 55.04
1977-11-29 | 29 | 11 | 0.083333 | 11.7 | 53.06 | 15.6765 |  | 53.06
1977-11-29 | 29 | 11 | 0.125 | 11.1 | 51.98 | 15.035 |  | 51.98
1977-11-29 | 29 | 11 | 0.16667 | 10.6 | 51.08 | 15.0768 |  | 51.08
1977-11-29 | 29 | 11 | 0.20833 | 10 | 50 | 14.7052 |  | 50
1977-11-29 | 29 | 11 | 0.25 | 10 | 50 | 14.7875 | 50
1977-11-29 | 29 | 11 | 0.29167 | 8.9 | 48.02 | 14.3397 | 48.02
1977-11-29 | 29 | 11 | 0.33333 | 9.4 | 48.92 | 14.4166 | 48.92
1977-11-29 | 29 | 11 | 0.375 | 10 | 50 | 14.7875 | 50
1977-11-29 | 29 | 11 | 0.41667 | 11.7 | 53.06 | 15.3996 | 53.06
1977-11-29 | 29 | 11 | 0.45833 | 12.2 | 53.96 | 15.6109 | 53.96
1977-11-29 | 29 | 11 | 0.5 | 12.8 | 55.04 | 15.4826 | 55.04
1977-11-29 | 29 | 11 | 0.54167 | 12.8 | 55.04 | 15.3835 | 55.04
1977-11-29 | 29 | 11 | 0.58333 | 13.3 | 55.94 | 15.5703 | 55.94
1977-11-29 | 29 | 11 | 0.625 | 12.8 | 55.04 | 15.4826 | 55.04
1977-11-29 | 29 | 11 | 0.66667 | 12.8 | 55.04 | 15.4826 | 55.04
1977-11-29 | 29 | 11 | 0.70833 | 12.2 | 53.96 | 15.5156 | 53.96
1977-11-29 | 29 | 11 | 0.75 | 11.7 | 53.06 | 15.3073 | 53.06
1977-11-29 | 29 | 11 | 0.79167 | 11.7 | 53.06 | 15.3073 | 53.06
1977-11-29 | 29 | 11 | 0.83333 | 11.7 | 53.06 | 15.3073 | 53.06
1977-11-29 | 29 | 11 | 0.875 | 11.1 | 51.98 | 15.3896 | 51.98
1977-11-29 | 29 | 11 | 0.91667 | 11.1 | 51.98 | 15.7446 |  | 51.98
1977-11-29 | 29 | 11 | 0.95833 | 11.1 | 51.98 | 15.7446 |  | 51.98
1977-11-29 | 29 | 11 | 1 | 10.6 | 51.08 | 15.5057 |  | 51.08
1977-11-30 | 30 | 11 | 0.041667 | 10 | 50 | 15.1994 |  | 50
1977-11-30 | 30 | 11 | 0.083333 | 9.4 | 48.92 | 15.1284 |  | 48.92
1977-11-30 | 30 | 11 | 0.125 | 8.9 | 48.02 | 15.1045 |  | 48.02
1977-11-30 | 30 | 11 | 0.16667 | 8.3 | 46.94 | 15.1414 |  | 46.94
1977-11-30 | 30 | 11 | 0.20833 | 8.3 | 46.94 | 15.1414 |  | 46.94
1977-11-30 | 30 | 11 | 0.25 | 8.9 | 48.02 | 15.2576 | 48.02
1977-11-30 | 30 | 11 | 0.29167 | 8.9 | 48.02 | 14.7218 | 48.02
1977-11-30 | 30 | 11 | 0.33333 | 8.9 | 48.02 | 14.1869 | 48.02
1977-11-30 | 30 | 11 | 0.375 | 8.9 | 48.02 | 14.3397 | 48.02
1977-11-30 | 30 | 11 | 0.41667 | 9.4 | 48.92 | 14.5746 | 48.92
1977-11-30 | 30 | 11 | 0.45833 | 10 | 50 | 14.4584 | 50
1977-11-30 | 30 | 11 | 0.5 | 10.6 | 51.08 | 14.4771 | 51.08
1977-11-30 | 30 | 11 | 0.54167 | 10.6 | 51.08 | 14.4771 | 51.08
1977-11-30 | 30 | 11 | 0.58333 | 10.6 | 51.08 | 14.3916 | 51.08
1977-11-30 | 30 | 11 | 0.625 | 10.6 | 51.08 | 14.4771 | 51.08
1977-11-30 | 30 | 11 | 0.66667 | 10 | 50 | 14.1295 | 50
1977-11-30 | 30 | 11 | 0.70833 | 8.9 | 48.02 | 13.9579 | 48.02
1977-11-30 | 30 | 11 | 0.75 | 8.9 | 48.02 | 14.3397 | 48.02
1977-11-30 | 30 | 11 | 0.79167 | 7.8 | 46.04 | 13.5882 | 46.04
1977-11-30 | 30 | 11 | 0.83333 | 6.7 | 44.06 | 13.3854 | 44.06
1977-11-30 | 30 | 11 | 0.875 | 5.6 | 42.08 | 13.0663 | 42.08
1977-11-30 | 30 | 11 | 0.91667 | 5.9 | 42.62 | 13.5078 |  | 42.62
1977-11-30 | 30 | 11 | 0.95833 | 6.2 | 43.16 | 13.8342 |  | 43.16
1977-11-30 | 30 | 11 | 1 | 6.5 | 43.7 | 13.908 |  | 43.7
1981-12-01 | 1 | 12 | 0.041667 | 6.9 | 44.42 | 13.7111 |  | 44.42
1981-12-01 | 1 | 12 | 0.083333 | 7.2 | 44.96 | 14.0412 |  | 44.96
1981-12-01 | 1 | 12 | 0.125 | 7.5 | 45.5 | 14.4478 |  | 45.5
1981-12-01 | 1 | 12 | 0.16667 | 7.8 | 46.04 | 14.9358 |  | 46.04
1981-12-01 | 1 | 12 | 0.20833 | 8.3 | 46.94 | 14.9944 |  | 46.94
1981-12-01 | 1 | 12 | 0.25 | 8.9 | 48.02 | 15.1045 | 48.02
1981-12-01 | 1 | 12 | 0.29167 | 8.9 | 48.02 | 15.1045 | 48.02
1981-12-01 | 1 | 12 | 0.33333 | 10 | 50 | 15.6943 | 50
1981-12-01 | 1 | 12 | 0.375 | 10 | 50 | 15.6943 | 50
1981-12-01 | 1 | 12 | 0.41667 | 10.6 | 51.08 | 16.0212 | 51.08
1981-12-01 | 1 | 12 | 0.45833 | 8.3 | 46.94 | 15.6567 | 46.94
1981-12-01 | 1 | 12 | 0.5 | 8.3 | 46.94 | 15.1414 | 46.94
1981-12-01 | 1 | 12 | 0.54167 | 10 | 50 | 14.7875 | 50
1981-12-01 | 1 | 12 | 0.58333 | 9.4 | 48.92 | 14.5746 | 48.92
1981-12-01 | 1 | 12 | 0.625 | 6.1 | 42.98 | 14.0191 | 42.98
1981-12-01 | 1 | 12 | 0.66667 | 6.1 | 42.98 | 13.0106 | 42.98
1981-12-01 | 1 | 12 | 0.70833 | 5.6 | 42.08 | 12.8839 | 42.08
1981-12-01 | 1 | 12 | 0.75 | 4.4 | 39.92 | 12.6416 | 39.92
1981-12-01 | 1 | 12 | 0.79167 | 4.4 | 39.92 | 12.0272 | 39.92
1981-12-01 | 1 | 12 | 0.83333 | 4.4 | 39.92 | 12.1388 | 39.92
1981-12-01 | 1 | 12 | 0.875 | 3.3 | 37.94 | 11.522 | 37.94
1981-12-01 | 1 | 12 | 0.91667 | 3.3 | 37.94 | 11.3157 |  | 37.94
1981-12-01 | 1 | 12 | 0.95833 | 2.8 | 37.04 | 11.1709 |  | 37.04
1981-12-01 | 1 | 12 | 1 | 2.8 | 37.04 | 10.972 |  | 37.04
1981-12-02 | 2 | 12 | 0.041667 | 2.8 | 37.04 | 11.0714 |  | 37.04
1981-12-02 | 2 | 12 | 0.083333 | 2.8 | 37.04 | 11.0714 |  | 37.04
1981-12-02 | 2 | 12 | 0.125 | 2.2 | 35.96 | 10.7198 |  | 35.96
1981-12-02 | 2 | 12 | 0.16667 | 2.2 | 35.96 | 10.8151 |  | 35.96
1981-12-02 | 2 | 12 | 0.20833 | 1.7 | 35.06 | 10.7052 |  | 35.06
1981-12-02 | 2 | 12 | 0.25 | 1.7 | 35.06 | 11.0732 | 35.06
1981-12-02 | 2 | 12 | 0.29167 | 1.7 | 35.06 | 10.6133 | 35.06
1981-12-02 | 2 | 12 | 0.33333 | -0.6 | 30.92 | 10.3496 | 30.92
1981-12-02 | 2 | 12 | 0.375 | 1.1 | 33.98 | 10.2601 | 33.98
1981-12-02 | 2 | 12 | 0.41667 | 1.7 | 35.06 | 10.2458 | 35.06
1981-12-02 | 2 | 12 | 0.45833 | 2.2 | 35.96 | 10.6246 | 35.96
1981-12-02 | 2 | 12 | 0.5 | 1.1 | 33.98 | 10.4361 | 33.98
1981-12-02 | 2 | 12 | 0.54167 | 2.2 | 35.96 | 10.5293 | 35.96
1981-12-02 | 2 | 12 | 0.58333 | 0.6 | 33.08 | 9.8413 | 33.08
1981-12-02 | 2 | 12 | 0.625 | 1.1 | 33.98 | 9.5131 | 33.98
1981-12-02 | 2 | 12 | 0.66667 | 0 | 32 | 8.8922 | 32
1981-12-02 | 2 | 12 | 0.70833 | -0.6 | 30.92 | 8.6894 | 30.92
1981-12-02 | 2 | 12 | 0.75 | -1.1 | 30.02 | 8.68 | 30.02
1981-12-02 | 2 | 12 | 0.79167 | -1.7 | 28.94 | 8.4184 | 28.94
1981-12-02 | 2 | 12 | 0.83333 | -2.2 | 28.04 | 8.3437 | 28.04
1981-12-02 | 2 | 12 | 0.875 | -3.3 | 26.06 | 7.7245 | 26.06
1981-12-02 | 2 | 12 | 0.91667 | -3.3 | 26.06 | 7.8166 |  | 26.06
1981-12-02 | 2 | 12 | 0.95833 | -3.9 | 24.98 | 7.3334 |  | 24.98
1981-12-02 | 2 | 12 | 1 | -4.4 | 24.08 | 6.9775 |  | 24.08
1981-12-03 | 3 | 12 | 0.041667 | -4.4 | 24.08 | 7.1171 |  | 24.08
1981-12-03 | 3 | 12 | 0.083333 | -4.4 | 24.08 | 7.2567 |  | 24.08
1981-12-03 | 3 | 12 | 0.125 | -5 | 23 | 7.0026 |  | 23
1981-12-03 | 3 | 12 | 0.16667 | -5 | 23 | 7.0823 |  | 23
1981-12-03 | 3 | 12 | 0.20833 | -5 | 23 | 7.0823 |  | 23
1981-12-03 | 3 | 12 | 0.25 | -5 | 23 | 7.2415 | 23
1981-12-03 | 3 | 12 | 0.29167 | -5 | 23 | 7.0823 | 23
1981-12-03 | 3 | 12 | 0.33333 | -5 | 23 | 7.0823 | 23
1981-12-03 | 3 | 12 | 0.375 | -4.4 | 24.08 | 7.3406 | 24.08
1981-12-03 | 3 | 12 | 0.41667 | -3.9 | 24.98 | 7.4792 | 24.98
1981-12-03 | 3 | 12 | 0.45833 | -3.3 | 26.06 | 7.8166 | 26.06
1981-12-03 | 3 | 12 | 0.5 | -2.2 | 28.04 | 8.1415 | 28.04
1981-12-03 | 3 | 12 | 0.54167 | -1.1 | 30.02 | 8.68 | 30.02
1981-12-03 | 3 | 12 | 0.58333 | -0.6 | 30.92 | 8.8435 | 30.92
1981-12-03 | 3 | 12 | 0.625 | 0 | 32 | 9.0137 | 32
1981-12-03 | 3 | 12 | 0.66667 | 0 | 32 | 9.1757 | 32
1981-12-03 | 3 | 12 | 0.70833 | 0 | 32 | 9.1757 | 32
1981-12-03 | 3 | 12 | 0.75 | -0.6 | 30.92 | 8.8435 | 30.92
1981-12-03 | 3 | 12 | 0.79167 | -0.6 | 30.92 | 8.882 | 30.92
1981-12-03 | 3 | 12 | 0.83333 | -0.6 | 30.92 | 8.9976 | 30.92
1981-12-03 | 3 | 12 | 0.875 | -1.1 | 30.02 | 8.7539 | 30.02
1981-12-03 | 3 | 12 | 0.91667 | -1.7 | 28.94 | 8.4887 |  | 28.94
1981-12-03 | 3 | 12 | 0.95833 | -1.7 | 28.94 | 8.4887 |  | 28.94
1981-12-03 | 3 | 12 | 1 | -1.7 | 28.94 | 8.559 |  | 28.94
1981-12-04 | 4 | 12 | 0.041667 | -1.7 | 28.94 | 8.559 |  | 28.94
1981-12-04 | 4 | 12 | 0.083333 | -1.7 | 28.94 | 8.559 |  | 28.94
1981-12-04 | 4 | 12 | 0.125 | -1.7 | 28.94 | 8.559 |  | 28.94
1981-12-04 | 4 | 12 | 0.16667 | -1.1 | 30.02 | 8.8278 |  | 30.02
1981-12-04 | 4 | 12 | 0.20833 | -1.1 | 30.02 | 8.7539 |  | 30.02
1981-12-04 | 4 | 12 | 0.25 | -1.1 | 30.02 | 8.9388 | 30.02
1981-12-04 | 4 | 12 | 0.29167 | -1.1 | 30.02 | 9.0128 | 30.02
1981-12-04 | 4 | 12 | 0.33333 | 0 | 32 | 9.5811 | 32
1981-12-04 | 4 | 12 | 0.375 | 1.1 | 33.98 | 10.2601 | 33.98
1981-12-04 | 4 | 12 | 0.41667 | 1.7 | 35.06 | 10.4295 | 35.06
1981-12-04 | 4 | 12 | 0.45833 | 2.2 | 35.96 | 10.7198 | 35.96
1981-12-04 | 4 | 12 | 0.5 | 3.3 | 37.94 | 11.1094 | 37.94
1981-12-04 | 4 | 12 | 0.54167 | 4.4 | 39.92 | 11.4696 | 39.92
1981-12-04 | 4 | 12 | 0.58333 | 5 | 41 | 11.869 | 41
1981-12-04 | 4 | 12 | 0.625 | 5.6 | 42.08 | 11.8521 | 42.08
1981-12-04 | 4 | 12 | 0.66667 | 5 | 41 | 11.4622 | 41
1981-12-04 | 4 | 12 | 0.70833 | 5 | 41 | 11.5784 | 41
1981-12-04 | 4 | 12 | 0.75 | 4.4 | 39.92 | 11.1912 | 39.92
1981-12-04 | 4 | 12 | 0.79167 | 3.9 | 39.02 | 11.1876 | 39.02
1981-12-04 | 4 | 12 | 0.83333 | 2.8 | 37.04 | 10.972 | 37.04
1981-12-04 | 4 | 12 | 0.875 | 3.3 | 37.94 | 11.1094 | 37.94
1981-12-04 | 4 | 12 | 0.91667 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-04 | 4 | 12 | 0.95833 | 2.8 | 37.04 | 10.972 |  | 37.04
1981-12-04 | 4 | 12 | 1 | 2.2 | 35.96 | 10.7198 |  | 35.96
1981-12-05 | 5 | 12 | 0.041667 | 2.8 | 37.04 | 11.1709 |  | 37.04
1981-12-05 | 5 | 12 | 0.083333 | 1.7 | 35.06 | 11.0732 |  | 35.06
1981-12-05 | 5 | 12 | 0.125 | 1.7 | 35.06 | 11.3494 |  | 35.06
1981-12-05 | 5 | 12 | 0.16667 | 1.1 | 33.98 | 11.5382 |  | 33.98
1981-12-05 | 5 | 12 | 0.20833 | 1.1 | 33.98 | 11.8475 |  | 33.98
1981-12-05 | 5 | 12 | 0.25 | 1.1 | 33.98 | 12.0243 | 33.98
1981-12-05 | 5 | 12 | 0.29167 | 1.7 | 35.06 | 12.2719 | 35.06
1981-12-05 | 5 | 12 | 0.33333 | 1.1 | 33.98 | 11.8475 | 33.98
1981-12-05 | 5 | 12 | 0.375 | 1.1 | 33.98 | 11.5382 | 33.98
1981-12-05 | 5 | 12 | 0.41667 | 1.1 | 33.98 | 11.3616 | 33.98
1981-12-05 | 5 | 12 | 0.45833 | 0.6 | 33.08 | 11.3283 | 33.08
1981-12-05 | 5 | 12 | 0.5 | 0 | 32 | 11.0446 | 32
1981-12-05 | 5 | 12 | 0.54167 | -1.1 | 30.02 | 10.905 | 30.02
1981-12-05 | 5 | 12 | 0.58333 | -1.7 | 28.94 | 10.4631 | 28.94
1981-12-05 | 5 | 12 | 0.625 | -1.7 | 28.94 | 10.4631 | 28.94
1981-12-05 | 5 | 12 | 0.66667 | -1.7 | 28.94 | 10.4631 | 28.94
1981-12-05 | 5 | 12 | 0.70833 | -2.2 | 28.04 | 9.9318 | 28.04
1981-12-05 | 5 | 12 | 0.75 | -1.7 | 28.94 | 10.4631 | 28.94
1981-12-05 | 5 | 12 | 0.79167 | -2.8 | 26.96 | 9.6742 | 26.96
1981-12-05 | 5 | 12 | 0.83333 | -2.2 | 28.04 | 10.1012 | 28.04
1981-12-05 | 5 | 12 | 0.875 | -1.1 | 30.02 | 10.719 | 30.02
1981-12-05 | 5 | 12 | 0.91667 | 0 | 32 | 11.5339 |  | 32
1981-12-05 | 5 | 12 | 0.95833 | -0.6 | 30.92 | 10.9307 |  | 30.92
1981-12-05 | 5 | 12 | 1 | -1.1 | 30.02 | 10.719 |  | 30.02
1981-12-06 | 6 | 12 | 0.041667 | -1.1 | 30.02 | 10.719 |  | 30.02
1981-12-06 | 6 | 12 | 0.083333 | -1.7 | 28.94 | 10.3217 |  | 28.94
1981-12-06 | 6 | 12 | 0.125 | -1.7 | 28.94 | 10.145 |  | 28.94
1981-12-06 | 6 | 12 | 0.16667 | -1.7 | 28.94 | 10.0037 |  | 28.94
1981-12-06 | 6 | 12 | 0.20833 | -1.7 | 28.94 | 9.8625 |  | 28.94
1981-12-06 | 6 | 12 | 0.25 | -2.2 | 28.04 | 9.6609 | 28.04
1981-12-06 | 6 | 12 | 0.29167 | -2.2 | 28.04 | 9.7963 | 28.04
1981-12-06 | 6 | 12 | 0.33333 | -2.2 | 28.04 | 9.7963 | 28.04
1981-12-06 | 6 | 12 | 0.375 | -3.3 | 26.06 | 9.0469 | 26.06
1981-12-06 | 6 | 12 | 0.41667 | -3.9 | 24.98 | 8.6478 | 24.98
1981-12-06 | 6 | 12 | 0.45833 | -3.9 | 24.98 | 8.6478 | 24.98
1981-12-06 | 6 | 12 | 0.5 | -3.3 | 26.06 | 9.0469 | 26.06
1981-12-06 | 6 | 12 | 0.54167 | -3.9 | 24.98 | 8.6478 | 24.98
1981-12-06 | 6 | 12 | 0.58333 | -3.3 | 26.06 | 8.9237 | 26.06
1981-12-06 | 6 | 12 | 0.625 | -3.3 | 26.06 | 9.0469 | 26.06
1981-12-06 | 6 | 12 | 0.66667 | -3.3 | 26.06 | 9.0469 | 26.06
1981-12-06 | 6 | 12 | 0.70833 | -2.8 | 26.96 | 9.256 | 26.96
1981-12-06 | 6 | 12 | 0.75 | -2.8 | 26.96 | 9.256 | 26.96
1981-12-06 | 6 | 12 | 0.79167 | -2.2 | 28.04 | 9.3903 | 28.04
1981-12-06 | 6 | 12 | 0.83333 | -2.8 | 26.96 | 8.9989 | 26.96
1981-12-06 | 6 | 12 | 0.875 | -2.8 | 26.96 | 8.9989 | 26.96
1981-12-06 | 6 | 12 | 0.91667 | -2.8 | 26.96 | 9.1274 |  | 26.96
1981-12-06 | 6 | 12 | 0.95833 | -2.2 | 28.04 | 9.3903 |  | 28.04
1981-12-06 | 6 | 12 | 1 | -2.2 | 28.04 | 9.2551 |  | 28.04
1981-12-07 | 7 | 12 | 0.041667 | -2.2 | 28.04 | 9.1537 |  | 28.04
1981-12-07 | 7 | 12 | 0.083333 | -2.2 | 28.04 | 9.1537 |  | 28.04
1981-12-07 | 7 | 12 | 0.125 | -2.8 | 26.96 | 8.9989 |  | 26.96
1981-12-07 | 7 | 12 | 0.16667 | -3.3 | 26.06 | 8.9237 |  | 26.06
1981-12-07 | 7 | 12 | 0.20833 | -2.8 | 26.96 | 8.9989 |  | 26.96
1981-12-07 | 7 | 12 | 0.25 | -3.3 | 26.06 | 8.9237 | 26.06
1981-12-07 | 7 | 12 | 0.29167 | -3.3 | 26.06 | 8.4619 | 26.06
1981-12-07 | 7 | 12 | 0.33333 | -3.3 | 26.06 | 8.3389 | 26.06
1981-12-07 | 7 | 12 | 0.375 | -4.4 | 24.08 | 7.6761 | 24.08
1981-12-07 | 7 | 12 | 0.41667 | -3.3 | 26.06 | 8.2467 | 26.06
1981-12-07 | 7 | 12 | 0.45833 | -2.8 | 26.96 | 8.4532 | 26.96
1981-12-07 | 7 | 12 | 0.5 | -1.7 | 28.94 | 8.946 | 28.94
1981-12-07 | 7 | 12 | 0.54167 | -1.1 | 30.02 | 9.3089 | 30.02
1981-12-07 | 7 | 12 | 0.58333 | -0.6 | 30.92 | 9.4992 | 30.92
1981-12-07 | 7 | 12 | 0.625 | -0.6 | 30.92 | 9.422 | 30.92
1981-12-07 | 7 | 12 | 0.66667 | -0.6 | 30.92 | 9.4992 | 30.92
1981-12-07 | 7 | 12 | 0.70833 | -1.1 | 30.02 | 9.3089 | 30.02
1981-12-07 | 7 | 12 | 0.75 | -1.1 | 30.02 | 9.3089 | 30.02
1981-12-07 | 7 | 12 | 0.79167 | -1.1 | 30.02 | 9.3089 | 30.02
1981-12-07 | 7 | 12 | 0.83333 | -2.2 | 28.04 | 8.7147 | 28.04
1981-12-07 | 7 | 12 | 0.875 | -2.2 | 28.04 | 8.7147 | 28.04
1981-12-07 | 7 | 12 | 0.91667 | -2.8 | 26.96 | 8.4532 |  | 26.96
1981-12-07 | 7 | 12 | 0.95833 | -2.8 | 26.96 | 8.4532 |  | 26.96
1981-12-07 | 7 | 12 | 1 | -2.8 | 26.96 | 8.357 |  | 26.96
1981-12-08 | 8 | 12 | 0.041667 | -3.3 | 26.06 | 8.2467 |  | 26.06
1981-12-08 | 8 | 12 | 0.083333 | -3.3 | 26.06 | 8.1545 |  | 26.06
1981-12-08 | 8 | 12 | 0.125 | -3.9 | 24.98 | 7.8002 |  | 24.98
1981-12-08 | 8 | 12 | 0.16667 | -3.9 | 24.98 | 7.8002 |  | 24.98
1981-12-08 | 8 | 12 | 0.20833 | -3.9 | 24.98 | 7.8002 |  | 24.98
1981-12-08 | 8 | 12 | 0.25 | -3.3 | 26.06 | 8.0623 | 26.06
1981-12-08 | 8 | 12 | 0.29167 | -3.3 | 26.06 | 8.1545 | 26.06
1981-12-08 | 8 | 12 | 0.33333 | -3.3 | 26.06 | 8.1545 | 26.06
1981-12-08 | 8 | 12 | 0.375 | -2.2 | 28.04 | 8.6135 | 28.04
1981-12-08 | 8 | 12 | 0.41667 | -1.7 | 28.94 | 8.8404 | 28.94
1981-12-08 | 8 | 12 | 0.45833 | 0 | 32 | 9.6623 | 32
1981-12-08 | 8 | 12 | 0.5 | 1.1 | 33.98 | 10.2601 | 33.98
1981-12-08 | 8 | 12 | 0.54167 | 1.7 | 35.06 | 10.7052 | 35.06
1981-12-08 | 8 | 12 | 0.58333 | 2.8 | 37.04 | 11.0714 | 37.04
1981-12-08 | 8 | 12 | 0.625 | 2.8 | 37.04 | 11.0714 | 37.04
1981-12-08 | 8 | 12 | 0.66667 | 2.8 | 37.04 | 11.0714 | 37.04
1981-12-08 | 8 | 12 | 0.70833 | 2.8 | 37.04 | 11.3203 | 37.04
1981-12-08 | 8 | 12 | 0.75 | 2.2 | 35.96 | 11.1488 | 35.96
1981-12-08 | 8 | 12 | 0.79167 | 2.2 | 35.96 | 11.0534 | 35.96
1981-12-08 | 8 | 12 | 0.83333 | 1.7 | 35.06 | 11.0732 | 35.06
1981-12-08 | 8 | 12 | 0.875 | 2.8 | 37.04 | 11.4199 | 37.04
1981-12-08 | 8 | 12 | 0.91667 | 2.2 | 35.96 | 11.1488 |  | 35.96
1981-12-08 | 8 | 12 | 0.95833 | 1.7 | 35.06 | 10.8431 |  | 35.06
1981-12-08 | 8 | 12 | 1 | 1.1 | 33.98 | 10.5682 |  | 33.98
1981-12-09 | 9 | 12 | 0.041667 | 0.6 | 33.08 | 10.3504 |  | 33.08
1981-12-09 | 9 | 12 | 0.083333 | 0.6 | 33.08 | 10.3504 |  | 33.08
1981-12-09 | 9 | 12 | 0.125 | 0.6 | 33.08 | 10.3504 |  | 33.08
1981-12-09 | 9 | 12 | 0.16667 | 0.6 | 33.08 | 10.3504 |  | 33.08
1981-12-09 | 9 | 12 | 0.20833 | 0 | 32 | 9.987 |  | 32
1981-12-09 | 9 | 12 | 0.25 | 0 | 32 | 9.987 | 32
1981-12-09 | 9 | 12 | 0.29167 | 0 | 32 | 10.1089 | 32
1981-12-09 | 9 | 12 | 0.33333 | 0 | 32 | 9.987 | 32
1981-12-09 | 9 | 12 | 0.375 | 0.6 | 33.08 | 10.3504 | 33.08
1981-12-09 | 9 | 12 | 0.41667 | 0.6 | 33.08 | 10.4778 | 33.08
1981-12-09 | 9 | 12 | 0.45833 | 1.1 | 33.98 | 10.8324 | 33.98
1981-12-09 | 9 | 12 | 0.5 | 1.1 | 33.98 | 10.9647 | 33.98
1981-12-09 | 9 | 12 | 0.54167 | 1.7 | 35.06 | 11.0732 | 35.06
1981-12-09 | 9 | 12 | 0.58333 | 2.2 | 35.96 | 11.2919 | 35.96
1981-12-09 | 9 | 12 | 0.625 | 2.2 | 35.96 | 11.4351 | 35.96
1981-12-09 | 9 | 12 | 0.66667 | 2.2 | 35.96 | 11.4351 | 35.96
1981-12-09 | 9 | 12 | 0.70833 | 2.8 | 37.04 | 12.1178 | 37.04
1981-12-09 | 9 | 12 | 0.75 | 3.3 | 37.94 | 12.3486 | 37.94
1981-12-09 | 9 | 12 | 0.79167 | 2.8 | 37.04 | 12.1178 | 37.04
1981-12-09 | 9 | 12 | 0.83333 | 2.8 | 37.04 | 11.9681 | 37.04
1981-12-09 | 9 | 12 | 0.875 | 2.8 | 37.04 | 12.1178 | 37.04
1981-12-09 | 9 | 12 | 0.91667 | 2.8 | 37.04 | 12.1178 |  | 37.04
1981-12-09 | 9 | 12 | 0.95833 | 2.8 | 37.04 | 12.2675 |  | 37.04
1981-12-09 | 9 | 12 | 1 | 2.2 | 35.96 | 12.1519 |  | 35.96
1981-12-10 | 10 | 12 | 0.041667 | 2.8 | 37.04 | 12.6172 |  | 37.04
1981-12-10 | 10 | 12 | 0.083333 | 2.8 | 37.04 | 12.6172 |  | 37.04
1981-12-10 | 10 | 12 | 0.125 | 2.8 | 37.04 | 12.7672 |  | 37.04
1981-12-10 | 10 | 12 | 0.16667 | 2.8 | 37.04 | 12.7672 |  | 37.04
1981-12-10 | 10 | 12 | 0.20833 | 2.2 | 35.96 | 12.3433 |  | 35.96
1981-12-10 | 10 | 12 | 0.25 | 2.8 | 37.04 | 12.6172 | 37.04
1981-12-10 | 10 | 12 | 0.29167 | 3.3 | 37.94 | 12.8144 | 37.94
1981-12-10 | 10 | 12 | 0.33333 | 3.3 | 37.94 | 12.9698 | 37.94
1981-12-10 | 10 | 12 | 0.375 | 4.4 | 39.92 | 13.6493 | 39.92
1981-12-10 | 10 | 12 | 0.41667 | 5 | 41 | 13.7348 | 41
1981-12-10 | 10 | 12 | 0.45833 | 6.1 | 42.98 | 14.2086 | 42.98
1981-12-10 | 10 | 12 | 0.5 | 6.1 | 42.98 | 14.2086 | 42.98
1981-12-10 | 10 | 12 | 0.54167 | 6.7 | 44.06 | 14.635 | 44.06
1981-12-10 | 10 | 12 | 0.58333 | 8.3 | 46.94 | 16.9852 | 46.94
1981-12-10 | 10 | 12 | 0.625 | 9.4 | 48.92 | 17.5919 | 48.92
1981-12-10 | 10 | 12 | 0.66667 | 10 | 50 | 18.5957 | 50
1981-12-10 | 10 | 12 | 0.70833 | 10 | 50 | 18.5957 | 50
1981-12-10 | 10 | 12 | 0.75 | 8.9 | 48.02 | 17.8722 | 48.02
1981-12-10 | 10 | 12 | 0.79167 | 9.4 | 48.92 | 18.3105 | 48.92
1981-12-10 | 10 | 12 | 0.83333 | 10 | 50 | 18.8456 | 50
1981-12-10 | 10 | 12 | 0.875 | 10 | 50 | 19.3458 | 50
1981-12-10 | 10 | 12 | 0.91667 | 10.6 | 51.08 | 19.9124 |  | 51.08
1981-12-10 | 10 | 12 | 0.95833 | 11.1 | 51.98 | 20.3933 |  | 51.98
1981-12-10 | 10 | 12 | 1 | 11.1 | 51.98 | 20.3933 |  | 51.98
1981-12-11 | 11 | 12 | 0.041667 | 11.1 | 51.98 | 20.3933 |  | 51.98
1981-12-11 | 11 | 12 | 0.083333 | 11.7 | 53.06 | 20.9812 |  | 53.06
1981-12-11 | 11 | 12 | 0.125 | 11.7 | 53.06 | 20.9812 |  | 53.06
1981-12-11 | 11 | 12 | 0.16667 | 11.7 | 53.06 | 21.3566 |  | 53.06
1981-12-11 | 11 | 12 | 0.20833 | 12.2 | 53.96 | 21.8688 |  | 53.96
1981-12-11 | 11 | 12 | 0.25 | 12.8 | 55.04 | 22.4956 | 55.04
1981-12-11 | 11 | 12 | 0.29167 | 13.3 | 55.94 | 22.7141 | 55.94
1981-12-11 | 11 | 12 | 0.33333 | 13.9 | 57.02 | 23.0263 | 57.02
1981-12-11 | 11 | 12 | 0.375 | 14.4 | 57.92 | 23.558 | 57.92
1981-12-11 | 11 | 12 | 0.41667 | 15 | 59 | 24.2087 | 59
1981-12-11 | 11 | 12 | 0.45833 | 14.4 | 57.92 | 23.8959 | 57.92
1981-12-11 | 11 | 12 | 0.5 | 13.9 | 57.02 | 23.68 | 57.02
1981-12-11 | 11 | 12 | 0.54167 | 11.7 | 53.06 | 22.0145 | 53.06
1981-12-11 | 11 | 12 | 0.58333 | 11.7 | 53.06 | 22.0145 | 53.06
1981-12-11 | 11 | 12 | 0.625 | 13.3 | 55.94 | 22.4004 | 55.94
1981-12-11 | 11 | 12 | 0.66667 | 12.2 | 53.96 | 19.7379 | 53.96
1981-12-11 | 11 | 12 | 0.70833 | 11.7 | 53.06 | 19.0172 | 53.06
1981-12-11 | 11 | 12 | 0.75 | 11.1 | 51.98 | 18.3293 | 51.98
1981-12-11 | 11 | 12 | 0.79167 | 9.4 | 48.92 | 16.9545 | 48.92
1981-12-11 | 11 | 12 | 0.83333 | 8.3 | 46.94 | 15.8777 | 46.94
1981-12-11 | 11 | 12 | 0.875 | 6.7 | 44.06 | 14.4374 | 44.06
1981-12-11 | 11 | 12 | 0.91667 | 6.1 | 42.98 | 13.8298 |  | 42.98
1981-12-11 | 11 | 12 | 0.95833 | 5.6 | 42.08 | 13.188 |  | 42.08
1981-12-11 | 11 | 12 | 1 | 5 | 41 | 12.8006 |  | 41
1981-12-12 | 12 | 12 | 0.041667 | 5 | 41 | 12.6257 |  | 41
1981-12-12 | 12 | 12 | 0.083333 | 5 | 41 | 12.6257 |  | 41
1981-12-12 | 12 | 12 | 0.125 | 4.4 | 39.92 | 12.1388 |  | 39.92
1981-12-12 | 12 | 12 | 0.16667 | 3.9 | 39.02 | 11.7794 |  | 39.02
1981-12-12 | 12 | 12 | 0.20833 | 3.9 | 39.02 | 11.5641 |  | 39.02
1981-12-12 | 12 | 12 | 0.25 | 3.9 | 39.02 | 11.7794 | 39.02
1981-12-12 | 12 | 12 | 0.29167 | 3.3 | 37.94 | 11.6252 | 37.94
1981-12-12 | 12 | 12 | 0.33333 | 3.3 | 37.94 | 11.6252 | 37.94
1981-12-12 | 12 | 12 | 0.375 | 3.3 | 37.94 | 11.6252 | 37.94
1981-12-12 | 12 | 12 | 0.41667 | 3.9 | 39.02 | 11.8872 | 39.02
1981-12-12 | 12 | 12 | 0.45833 | 4.4 | 39.92 | 11.8598 | 39.92
1981-12-12 | 12 | 12 | 0.5 | 5 | 41 | 12.1598 | 41
1981-12-12 | 12 | 12 | 0.54167 | 5 | 41 | 12.2762 | 41
1981-12-12 | 12 | 12 | 0.58333 | 5 | 41 | 12.5092 | 41
1981-12-12 | 12 | 12 | 0.625 | 5 | 41 | 12.5092 | 41
1981-12-12 | 12 | 12 | 0.66667 | 5 | 41 | 12.5092 | 41
1981-12-12 | 12 | 12 | 0.70833 | 3.9 | 39.02 | 11.8872 | 39.02
1981-12-12 | 12 | 12 | 0.75 | 3.9 | 39.02 | 11.6717 | 39.02
1981-12-12 | 12 | 12 | 0.79167 | 3.3 | 37.94 | 11.4188 | 37.94
1981-12-12 | 12 | 12 | 0.83333 | 3.3 | 37.94 | 11.4188 | 37.94
1981-12-12 | 12 | 12 | 0.875 | 3.3 | 37.94 | 11.3157 | 37.94
1981-12-12 | 12 | 12 | 0.91667 | 2.8 | 37.04 | 10.7731 |  | 37.04
1981-12-12 | 12 | 12 | 0.95833 | 2.2 | 35.96 | 10.5293 |  | 35.96
1981-12-12 | 12 | 12 | 1 | 2.2 | 35.96 | 10.4341 |  | 35.96
1981-12-13 | 13 | 12 | 0.041667 | 1.1 | 33.98 | 9.8644 |  | 33.98
1981-12-13 | 13 | 12 | 0.083333 | 1.1 | 33.98 | 9.9523 |  | 33.98
1981-12-13 | 13 | 12 | 0.125 | 0.6 | 33.08 | 9.8413 |  | 33.08
1981-12-13 | 13 | 12 | 0.16667 | 0 | 32 | 9.5 |  | 32
1981-12-13 | 13 | 12 | 0.20833 | 0 | 32 | 9.784 |  | 32
1981-12-13 | 13 | 12 | 0.25 | -0.6 | 30.92 | 9.422 | 30.92
1981-12-13 | 13 | 12 | 0.29167 | -0.6 | 30.92 | 9.4992 | 30.92
1981-12-13 | 13 | 12 | 0.33333 | -0.6 | 30.92 | 9.615 | 30.92
1981-12-13 | 13 | 12 | 0.375 | -0.6 | 30.92 | 9.422 | 30.92
1981-12-13 | 13 | 12 | 0.41667 | 0 | 32 | 9.5 | 32
1981-12-13 | 13 | 12 | 0.45833 | 0 | 32 | 9.5 | 32
1981-12-13 | 13 | 12 | 0.5 | 0.6 | 33.08 | 9.4177 | 33.08
1981-12-13 | 13 | 12 | 0.54167 | 0.6 | 33.08 | 9.5024 | 33.08
1981-12-13 | 13 | 12 | 0.58333 | 0.6 | 33.08 | 9.5024 | 33.08
1981-12-13 | 13 | 12 | 0.625 | 0.6 | 33.08 | 9.5024 | 33.08
1981-12-13 | 13 | 12 | 0.66667 | 0.6 | 33.08 | 9.5024 | 33.08
1981-12-13 | 13 | 12 | 0.70833 | 0.6 | 33.08 | 9.5024 | 33.08
1981-12-13 | 13 | 12 | 0.75 | 0 | 32 | 9.2568 | 32
1981-12-13 | 13 | 12 | 0.79167 | 0 | 32 | 9.2973 | 32
1981-12-13 | 13 | 12 | 0.83333 | -0.6 | 30.92 | 8.9976 | 30.92
1981-12-13 | 13 | 12 | 0.875 | -0.6 | 30.92 | 8.882 | 30.92
1981-12-13 | 13 | 12 | 0.91667 | -0.6 | 30.92 | 8.9976 |  | 30.92
1981-12-13 | 13 | 12 | 0.95833 | -0.6 | 30.92 | 8.882 |  | 30.92
1981-12-13 | 13 | 12 | 1 | -1.1 | 30.02 | 8.68 |  | 30.02
1981-12-14 | 14 | 12 | 0.041667 | -1.1 | 30.02 | 8.8278 |  | 30.02
1981-12-14 | 14 | 12 | 0.083333 | -1.7 | 28.94 | 8.6645 |  | 28.94
1981-12-14 | 14 | 12 | 0.125 | -1.7 | 28.94 | 8.559 |  | 28.94
1981-12-14 | 14 | 12 | 0.16667 | -2.2 | 28.04 | 8.2763 |  | 28.04
1981-12-14 | 14 | 12 | 0.20833 | -1.7 | 28.94 | 8.6645 |  | 28.94
1981-12-14 | 14 | 12 | 0.25 | -1.7 | 28.94 | 8.6645 | 28.94
1981-12-14 | 14 | 12 | 0.29167 | -1.1 | 30.02 | 9.0128 | 30.02
1981-12-14 | 14 | 12 | 0.33333 | -0.6 | 30.92 | 9.615 | 30.92
1981-12-14 | 14 | 12 | 0.375 | -1.7 | 28.94 | 10.145 | 28.94
1981-12-14 | 14 | 12 | 0.41667 | -1.7 | 28.94 | 10.3217 | 28.94
1981-12-14 | 14 | 12 | 0.45833 | -1.7 | 28.94 | 10.4631 | 28.94
1981-12-14 | 14 | 12 | 0.5 | -1.7 | 28.94 | 10.3217 | 28.94
1981-12-14 | 14 | 12 | 0.54167 | -1.1 | 30.02 | 10.905 | 30.02
1981-12-14 | 14 | 12 | 0.58333 | 0 | 32 | 11.5339 | 32
1981-12-14 | 14 | 12 | 0.625 | 1.1 | 33.98 | 12.2012 | 33.98
1981-12-14 | 14 | 12 | 0.66667 | 1.7 | 35.06 | 12.6416 | 35.06
1981-12-14 | 14 | 12 | 0.70833 | 1.7 | 35.06 | 12.8266 | 35.06
1981-12-14 | 14 | 12 | 0.75 | 2.8 | 37.04 | 13.6684 | 37.04
1981-12-14 | 14 | 12 | 0.79167 | 3.9 | 39.02 | 14.3743 | 39.02
1981-12-14 | 14 | 12 | 0.83333 | 5.6 | 42.08 | 15.5079 | 42.08
1981-12-14 | 14 | 12 | 0.875 | 5 | 41 | 15.4347 | 41
1981-12-14 | 14 | 12 | 0.91667 | 5 | 41 | 15.4347 |  | 41
1981-12-14 | 14 | 12 | 0.95833 | 4.4 | 39.92 | 15.1667 |  | 39.92
1981-12-14 | 14 | 12 | 1 | 4.4 | 39.92 | 15.1667 |  | 39.92
1981-12-15 | 15 | 12 | 0.041667 | 5 | 41 | 15.4347 |  | 41
1981-12-15 | 15 | 12 | 0.083333 | 2.8 | 37.04 | 13.4679 |  | 37.04
1981-12-15 | 15 | 12 | 0.125 | 0.6 | 33.08 | 11.797 |  | 33.08
1981-12-15 | 15 | 12 | 0.16667 | 0 | 32 | 11.2076 |  | 32
1981-12-15 | 15 | 12 | 0.20833 | 0 | 32 | 11.3707 |  | 32
1981-12-15 | 15 | 12 | 0.25 | 0 | 32 | 11.3707 | 32
1981-12-15 | 15 | 12 | 0.29167 | 0 | 32 | 10.8817 | 32
1981-12-15 | 15 | 12 | 0.33333 | 0 | 32 | 10.5968 | 32
1981-12-15 | 15 | 12 | 0.375 | 0 | 32 | 10.4747 | 32
1981-12-15 | 15 | 12 | 0.41667 | 1.1 | 33.98 | 11.0969 | 33.98
1981-12-15 | 15 | 12 | 0.45833 | 2.2 | 35.96 | 11.5783 | 35.96
1981-12-15 | 15 | 12 | 0.5 | 2.8 | 37.04 | 11.9681 | 37.04
1981-12-15 | 15 | 12 | 0.54167 | 3.3 | 37.94 | 12.1934 | 37.94
1981-12-15 | 15 | 12 | 0.58333 | 3.3 | 37.94 | 12.0383 | 37.94
1981-12-15 | 15 | 12 | 0.625 | 3.9 | 39.02 | 12.3184 | 39.02
1981-12-15 | 15 | 12 | 0.66667 | 3.3 | 37.94 | 12.0383 | 37.94
1981-12-15 | 15 | 12 | 0.70833 | 3.3 | 37.94 | 11.935 | 37.94
1981-12-15 | 15 | 12 | 0.75 | 2.8 | 37.04 | 11.7188 | 37.04
1981-12-15 | 15 | 12 | 0.79167 | 2.8 | 37.04 | 11.7188 | 37.04
1981-12-15 | 15 | 12 | 0.83333 | 2.2 | 35.96 | 11.2919 | 35.96
1981-12-15 | 15 | 12 | 0.875 | 2.2 | 35.96 | 11.4351 | 35.96
1981-12-15 | 15 | 12 | 0.91667 | 2.2 | 35.96 | 11.2919 |  | 35.96
1981-12-15 | 15 | 12 | 0.95833 | 1.7 | 35.06 | 11.2113 |  | 35.06
1981-12-15 | 15 | 12 | 1 | 1.7 | 35.06 | 11.0732 |  | 35.06
1981-12-16 | 16 | 12 | 0.041667 | 1.7 | 35.06 | 10.9351 |  | 35.06
1981-12-16 | 16 | 12 | 0.083333 | 1.1 | 33.98 | 10.8324 |  | 33.98
1981-12-16 | 16 | 12 | 0.125 | 1.1 | 33.98 | 10.9647 |  | 33.98
1981-12-16 | 16 | 12 | 0.16667 | 1.1 | 33.98 | 10.9647 |  | 33.98
1981-12-16 | 16 | 12 | 0.20833 | 1.1 | 33.98 | 11.0969 |  | 33.98
1981-12-16 | 16 | 12 | 0.25 | 1.7 | 35.06 | 11.2113 | 35.06
1981-12-16 | 16 | 12 | 0.29167 | 1.1 | 33.98 | 11.0969 | 33.98
1981-12-16 | 16 | 12 | 0.33333 | 1.1 | 33.98 | 11.0969 | 33.98
1981-12-16 | 16 | 12 | 0.375 | 2.2 | 35.96 | 11.5783 | 35.96
1981-12-16 | 16 | 12 | 0.41667 | 3.3 | 37.94 | 12.1934 | 37.94
1981-12-16 | 16 | 12 | 0.45833 | 5 | 41 | 13.0339 | 41
1981-12-16 | 16 | 12 | 0.5 | 6.1 | 42.98 | 13.7037 | 42.98
1981-12-16 | 16 | 12 | 0.54167 | 7.8 | 46.04 | 14.0132 | 46.04
1981-12-16 | 16 | 12 | 0.58333 | 8.3 | 46.94 | 14.3333 | 46.94
1981-12-16 | 16 | 12 | 0.625 | 7.8 | 46.04 | 14.4387 | 46.04
1981-12-16 | 16 | 12 | 0.66667 | 5.6 | 42.08 | 13.9798 | 42.08
1981-12-16 | 16 | 12 | 0.70833 | 5.6 | 42.08 | 14.7125 | 42.08
1981-12-16 | 16 | 12 | 0.75 | 6.1 | 42.98 | 15.284 | 42.98
1981-12-16 | 16 | 12 | 0.79167 | 6.1 | 42.98 | 15.7278 | 42.98
1981-12-16 | 16 | 12 | 0.83333 | 6.7 | 44.06 | 16.1539 | 44.06
1981-12-16 | 16 | 12 | 0.875 | 6.7 | 44.06 | 16.1539 | 44.06
1981-12-16 | 16 | 12 | 0.91667 | 6.7 | 44.06 | 15.9554 |  | 44.06
1981-12-16 | 16 | 12 | 0.95833 | 7.2 | 44.96 | 16.6371 |  | 44.96
1981-12-16 | 16 | 12 | 1 | 7.2 | 44.96 | 16.6371 |  | 44.96
1981-12-17 | 17 | 12 | 0.041667 | 6.7 | 44.06 | 16.1539 |  | 44.06
1981-12-17 | 17 | 12 | 0.083333 | 6.7 | 44.06 | 15.9554 |  | 44.06
1981-12-17 | 17 | 12 | 0.125 | 6.7 | 44.06 | 16.1539 |  | 44.06
1981-12-17 | 17 | 12 | 0.16667 | 7.2 | 44.96 | 16.9115 |  | 44.96
1981-12-17 | 17 | 12 | 0.20833 | 7.2 | 44.96 | 17.1175 |  | 44.96
1981-12-17 | 17 | 12 | 0.25 | 9.4 | 48.92 | 19.1107 | 48.92
1981-12-17 | 17 | 12 | 0.29167 | 8.9 | 48.02 | 18.645 | 48.02
1981-12-17 | 17 | 12 | 0.33333 | 10 | 50 | 19.6798 | 50
1981-12-17 | 17 | 12 | 0.375 | 10.6 | 51.08 | 20.1734 | 51.08
1981-12-17 | 17 | 12 | 0.41667 | 12.2 | 53.96 | 21.5775 | 53.96
1981-12-17 | 17 | 12 | 0.45833 | 12.8 | 55.04 | 22.0909 | 55.04
1981-12-17 | 17 | 12 | 0.5 | 12.2 | 53.96 | 21.8688 | 53.96
1981-12-17 | 17 | 12 | 0.54167 | 11.7 | 53.06 | 21.6384 | 53.06
1981-12-17 | 17 | 12 | 0.58333 | 12.2 | 53.96 | 22.2577 | 53.96
1981-12-17 | 17 | 12 | 0.625 | 10.6 | 51.08 | 20.5217 | 51.08
1981-12-17 | 17 | 12 | 0.66667 | 7.8 | 46.04 | 17.3607 | 46.04
1981-12-17 | 17 | 12 | 0.70833 | 6.1 | 42.98 | 15.9182 | 42.98
1981-12-17 | 17 | 12 | 0.75 | 5.6 | 42.08 | 15.5079 | 42.08
1981-12-17 | 17 | 12 | 0.79167 | 5.6 | 42.08 | 15.263 | 42.08
1981-12-17 | 17 | 12 | 0.83333 | 3.3 | 37.94 | 13.6961 | 37.94
1981-12-17 | 17 | 12 | 0.875 | 2.8 | 37.04 | 13.3176 | 37.04
1981-12-17 | 17 | 12 | 0.91667 | 3.3 | 37.94 | 12.9698 |  | 37.94
1981-12-17 | 17 | 12 | 0.95833 | 3.3 | 37.94 | 12.659 |  | 37.94
1981-12-17 | 17 | 12 | 1 | 2.2 | 35.96 | 11.2919 |  | 35.96
1981-12-18 | 18 | 12 | 0.041667 | 1.7 | 35.06 | 11.0732 |  | 35.06
1981-12-18 | 18 | 12 | 0.083333 | 1.1 | 33.98 | 10.8324 |  | 33.98
1981-12-18 | 18 | 12 | 0.125 | 1.1 | 33.98 | 10.5682 |  | 33.98
1981-12-18 | 18 | 12 | 0.16667 | 1.1 | 33.98 | 10.4361 |  | 33.98
1981-12-18 | 18 | 12 | 0.20833 | 1.1 | 33.98 | 10.4361 |  | 33.98
1981-12-18 | 18 | 12 | 0.25 | 0.6 | 33.08 | 10.2231 | 33.08
1981-12-18 | 18 | 12 | 0.29167 | 0.6 | 33.08 | 10.2231 | 33.08
1981-12-18 | 18 | 12 | 0.33333 | 0.6 | 33.08 | 10.1382 | 33.08
1981-12-18 | 18 | 12 | 0.375 | 1.1 | 33.98 | 10.3481 | 33.98
1981-12-18 | 18 | 12 | 0.41667 | 1.7 | 35.06 | 10.6133 | 35.06
1981-12-18 | 18 | 12 | 0.45833 | 2.2 | 35.96 | 10.8151 | 35.96
1981-12-18 | 18 | 12 | 0.5 | 2.2 | 35.96 | 10.8151 | 35.96
1981-12-18 | 18 | 12 | 0.54167 | 2.2 | 35.96 | 10.8151 | 35.96
1981-12-18 | 18 | 12 | 0.58333 | 2.2 | 35.96 | 10.8151 | 35.96
1981-12-18 | 18 | 12 | 0.625 | 2.2 | 35.96 | 10.9104 | 35.96
1981-12-18 | 18 | 12 | 0.66667 | 2.2 | 35.96 | 10.9104 | 35.96
1981-12-18 | 18 | 12 | 0.70833 | 1.7 | 35.06 | 10.7052 | 35.06
1981-12-18 | 18 | 12 | 0.75 | 2.2 | 35.96 | 10.8151 | 35.96
1981-12-18 | 18 | 12 | 0.79167 | 1.7 | 35.06 | 10.6133 | 35.06
1981-12-18 | 18 | 12 | 0.83333 | 1.7 | 35.06 | 10.7052 | 35.06
1981-12-18 | 18 | 12 | 0.875 | 1.7 | 35.06 | 10.7052 | 35.06
1981-12-18 | 18 | 12 | 0.91667 | 1.7 | 35.06 | 10.8431 |  | 35.06
1981-12-18 | 18 | 12 | 0.95833 | 1.7 | 35.06 | 10.8431 |  | 35.06
1981-12-18 | 18 | 12 | 1 | 1.7 | 35.06 | 10.9351 |  | 35.06
1981-12-19 | 19 | 12 | 0.041667 | 1.1 | 33.98 | 10.5682 |  | 33.98
1981-12-19 | 19 | 12 | 0.083333 | 1.1 | 33.98 | 10.5682 |  | 33.98
1981-12-19 | 19 | 12 | 0.125 | 0.6 | 33.08 | 10.3504 |  | 33.08
1981-12-19 | 19 | 12 | 0.16667 | 0.6 | 33.08 | 10.3504 |  | 33.08
1981-12-19 | 19 | 12 | 0.20833 | 0 | 32 | 10.1089 |  | 32
1981-12-19 | 19 | 12 | 0.25 | 0 | 32 | 9.987 | 32
1981-12-19 | 19 | 12 | 0.29167 | 0 | 32 | 9.8652 | 32
1981-12-19 | 19 | 12 | 0.33333 | -0.6 | 30.92 | 9.7309 | 30.92
1981-12-19 | 19 | 12 | 0.375 | 0 | 32 | 9.8652 | 32
1981-12-19 | 19 | 12 | 0.41667 | 0 | 32 | 9.784 | 32
1981-12-19 | 19 | 12 | 0.45833 | 0.6 | 33.08 | 10.0109 | 33.08
1981-12-19 | 19 | 12 | 0.5 | 1.1 | 33.98 | 10.2601 | 33.98
1981-12-19 | 19 | 12 | 0.54167 | 1.1 | 33.98 | 10.1721 | 33.98
1981-12-19 | 19 | 12 | 0.58333 | 1.1 | 33.98 | 10.1721 | 33.98
1981-12-19 | 19 | 12 | 0.625 | 1.7 | 35.06 | 10.5213 | 35.06
1981-12-19 | 19 | 12 | 0.66667 | 2.2 | 35.96 | 10.6246 | 35.96
1981-12-19 | 19 | 12 | 0.70833 | 2.2 | 35.96 | 10.6246 | 35.96
1981-12-19 | 19 | 12 | 0.75 | 2.2 | 35.96 | 10.7198 | 35.96
1981-12-19 | 19 | 12 | 0.79167 | 2.2 | 35.96 | 10.7198 | 35.96
1981-12-19 | 19 | 12 | 0.83333 | 2.2 | 35.96 | 10.8151 | 35.96
1981-12-19 | 19 | 12 | 0.875 | 1.7 | 35.06 | 10.8431 | 35.06
1981-12-19 | 19 | 12 | 0.91667 | 1.7 | 35.06 | 10.8431 |  | 35.06
1981-12-19 | 19 | 12 | 0.95833 | 1.7 | 35.06 | 10.8431 |  | 35.06
1981-12-19 | 19 | 12 | 1 | 1.7 | 35.06 | 10.9351 |  | 35.06
1981-12-20 | 20 | 12 | 0.041667 | 1.7 | 35.06 | 11.0732 |  | 35.06
1981-12-20 | 20 | 12 | 0.083333 | 1.1 | 33.98 | 10.7003 |  | 33.98
1981-12-20 | 20 | 12 | 0.125 | 1.1 | 33.98 | 10.7003 |  | 33.98
1981-12-20 | 20 | 12 | 0.16667 | 0.6 | 33.08 | 10.6052 |  | 33.08
1981-12-20 | 20 | 12 | 0.20833 | 0.6 | 33.08 | 10.6052 |  | 33.08
1981-12-20 | 20 | 12 | 0.25 | 0.6 | 33.08 | 10.7327 | 33.08
1981-12-20 | 20 | 12 | 0.29167 | 0 | 32 | 10.4747 | 32
1981-12-20 | 20 | 12 | 0.33333 | 0 | 32 | 10.4747 | 32
1981-12-20 | 20 | 12 | 0.375 | 0.6 | 33.08 | 10.7327 | 33.08
1981-12-20 | 20 | 12 | 0.41667 | 1.1 | 33.98 | 10.9647 | 33.98
1981-12-20 | 20 | 12 | 0.45833 | 2.2 | 35.96 | 11.2919 | 35.96
1981-12-20 | 20 | 12 | 0.5 | 2.8 | 37.04 | 11.7188 | 37.04
1981-12-20 | 20 | 12 | 0.54167 | 3.3 | 37.94 | 11.935 | 37.94
1981-12-20 | 20 | 12 | 0.58333 | 3.3 | 37.94 | 11.7801 | 37.94
1981-12-20 | 20 | 12 | 0.625 | 2.8 | 37.04 | 11.3203 | 37.04
1981-12-20 | 20 | 12 | 0.66667 | 2.8 | 37.04 | 11.1709 | 37.04
1981-12-20 | 20 | 12 | 0.70833 | 2.2 | 35.96 | 10.7198 | 35.96
1981-12-20 | 20 | 12 | 0.75 | 1.7 | 35.06 | 10.5213 | 35.06
1981-12-20 | 20 | 12 | 0.79167 | 1.1 | 33.98 | 10.2601 | 33.98
1981-12-20 | 20 | 12 | 0.83333 | 0 | 32 | 9.5811 | 32
1981-12-20 | 20 | 12 | 0.875 | -0.6 | 30.92 | 9.229 | 30.92
1981-12-20 | 20 | 12 | 0.91667 | -1.1 | 30.02 | 9.0868 |  | 30.02
1981-12-20 | 20 | 12 | 0.95833 | -1.1 | 30.02 | 9.0868 |  | 30.02
1981-12-20 | 20 | 12 | 1 | -2.2 | 28.04 | 8.546 |  | 28.04
1981-12-21 | 21 | 12 | 0.041667 | -2.8 | 26.96 | 8.1967 |  | 26.96
1981-12-21 | 21 | 12 | 0.083333 | -2.8 | 26.96 | 8.1967 |  | 26.96
1981-12-21 | 21 | 12 | 0.125 | -3.3 | 26.06 | 7.9701 |  | 26.06
1981-12-21 | 21 | 12 | 0.16667 | -3.3 | 26.06 | 7.878 |  | 26.06
1981-12-21 | 21 | 12 | 0.20833 | -3.3 | 26.06 | 7.9701 |  | 26.06
1981-12-21 | 21 | 12 | 0.25 | -2.8 | 26.96 | 8.1005 | 26.96
1981-12-21 | 21 | 12 | 0.29167 | -2.2 | 28.04 | 8.4449 | 28.04
1981-12-21 | 21 | 12 | 0.33333 | -1.7 | 28.94 | 8.8404 | 28.94
1981-12-21 | 21 | 12 | 0.375 | -0.6 | 30.92 | 9.4992 | 30.92
1981-12-21 | 21 | 12 | 0.41667 | -0.6 | 30.92 | 9.4992 | 30.92
1981-12-21 | 21 | 12 | 0.45833 | 1.1 | 33.98 | 10.2601 | 33.98
1981-12-21 | 21 | 12 | 0.5 | 1.7 | 35.06 | 10.4295 | 35.06
1981-12-21 | 21 | 12 | 0.54167 | 2.2 | 35.96 | 10.4341 | 35.96
1981-12-21 | 21 | 12 | 0.58333 | 3.3 | 37.94 | 10.8519 | 37.94
1981-12-21 | 21 | 12 | 0.625 | 3.9 | 39.02 | 11.0801 | 39.02
1981-12-21 | 21 | 12 | 0.66667 | 3.9 | 39.02 | 11.0801 | 39.02
1981-12-21 | 21 | 12 | 0.70833 | 3.3 | 37.94 | 10.9034 | 37.94
1981-12-21 | 21 | 12 | 0.75 | 3.3 | 37.94 | 10.9034 | 37.94
1981-12-21 | 21 | 12 | 0.79167 | 3.3 | 37.94 | 11.1094 | 37.94
1981-12-21 | 21 | 12 | 0.83333 | 3.3 | 37.94 | 11.2125 | 37.94
1981-12-21 | 21 | 12 | 0.875 | 3.3 | 37.94 | 11.2125 | 37.94
1981-12-21 | 21 | 12 | 0.91667 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-21 | 21 | 12 | 0.95833 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-21 | 21 | 12 | 1 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-22 | 22 | 12 | 0.041667 | 3.9 | 39.02 | 11.4565 |  | 39.02
1981-12-22 | 22 | 12 | 0.083333 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-22 | 22 | 12 | 0.125 | 3.9 | 39.02 | 11.4565 |  | 39.02
1981-12-22 | 22 | 12 | 0.16667 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-22 | 22 | 12 | 0.20833 | 3.3 | 37.94 | 11.2125 |  | 37.94
1981-12-22 | 22 | 12 | 0.25 | 2.8 | 37.04 | 11.0714 | 37.04
1981-12-22 | 22 | 12 | 0.29167 | 2.8 | 37.04 | 11.0714 | 37.04
1981-12-22 | 22 | 12 | 0.33333 | 2.8 | 37.04 | 11.1709 | 37.04
1981-12-22 | 22 | 12 | 0.375 | 4.4 | 39.92 | 11.804 | 39.92
1981-12-22 | 22 | 12 | 0.41667 | 5 | 41 | 12.0435 | 41
1981-12-22 | 22 | 12 | 0.45833 | 7.2 | 44.96 | 12.8863 | 44.96
1981-12-22 | 22 | 12 | 0.5 | 7.2 | 44.96 | 12.8863 | 44.96
1981-12-22 | 22 | 12 | 0.54167 | 8.3 | 46.94 | 13.454 | 46.94
1981-12-22 | 22 | 12 | 0.58333 | 9.4 | 48.92 | 14.0218 | 48.92
1981-12-22 | 22 | 12 | 0.625 | 10 | 50 | 14.5406 | 50
1981-12-22 | 22 | 12 | 0.66667 | 10 | 50 | 14.7052 | 50
1981-12-22 | 22 | 12 | 0.70833 | 10 | 50 | 14.7875 | 50
1981-12-22 | 22 | 12 | 0.75 | 10 | 50 | 15.117 | 50
1981-12-22 | 22 | 12 | 0.79167 | 9.4 | 48.92 | 14.6537 | 48.92
1981-12-22 | 22 | 12 | 0.83333 | 9.4 | 48.92 | 14.5746 | 48.92
1981-12-22 | 22 | 12 | 0.875 | 9.4 | 48.92 | 14.6537 | 48.92
1981-12-22 | 22 | 12 | 0.91667 | 8.9 | 48.02 | 14.6454 |  | 48.02
1981-12-22 | 22 | 12 | 0.95833 | 8.9 | 48.02 | 14.6454 |  | 48.02
1981-12-22 | 22 | 12 | 1 | 8.9 | 48.02 | 14.7218 |  | 48.02
1981-12-23 | 23 | 12 | 0.041667 | 8.3 | 46.94 | 14.4801 |  | 46.94
1981-12-23 | 23 | 12 | 0.083333 | 8.3 | 46.94 | 14.627 |  | 46.94
1981-12-23 | 23 | 12 | 0.125 | 8.3 | 46.94 | 14.627 |  | 46.94
1981-12-23 | 23 | 12 | 0.16667 | 8.3 | 46.94 | 14.627 |  | 46.94
1981-12-23 | 23 | 12 | 0.20833 | 8.3 | 46.94 | 14.7739 |  | 46.94
1981-12-23 | 23 | 12 | 0.25 | 8.9 | 48.02 | 15.2576 | 48.02
1981-12-23 | 23 | 12 | 0.29167 | 7.8 | 46.04 | 15.2913 | 46.04
1981-12-23 | 23 | 12 | 0.33333 | 7.8 | 46.04 | 15.2913 | 46.04
1981-12-23 | 23 | 12 | 0.375 | 8.3 | 46.94 | 15.3622 | 46.94
1981-12-23 | 23 | 12 | 0.41667 | 9.4 | 48.92 | 15.8418 | 48.92
1981-12-23 | 23 | 12 | 0.45833 | 10.6 | 51.08 | 16.0212 | 51.08
1981-12-23 | 23 | 12 | 0.5 | 10.6 | 51.08 | 16.1932 | 51.08
1981-12-23 | 23 | 12 | 0.54167 | 11.7 | 53.06 | 16.5086 | 53.06
1981-12-23 | 23 | 12 | 0.58333 | 11.7 | 53.06 | 16.9718 | 53.06
1981-12-23 | 23 | 12 | 0.625 | 11.1 | 51.98 | 17.525 | 51.98
1981-12-23 | 23 | 12 | 0.66667 | 10.6 | 51.08 | 17.6587 | 51.08
1981-12-23 | 23 | 12 | 0.70833 | 9.4 | 48.92 | 17.1137 | 48.92
1981-12-23 | 23 | 12 | 0.75 | 9.4 | 48.92 | 16.7157 | 48.92
1981-12-23 | 23 | 12 | 0.79167 | 8.9 | 48.02 | 16.9471 | 48.02
1981-12-23 | 23 | 12 | 0.83333 | 8.9 | 48.02 | 17.4093 | 48.02
1981-12-23 | 23 | 12 | 0.875 | 8.9 | 48.02 | 17.6407 | 48.02
1981-12-23 | 23 | 12 | 0.91667 | 8.9 | 48.02 | 18.3357 |  | 48.02
1981-12-23 | 23 | 12 | 0.95833 | 9.4 | 48.92 | 19.1107 |  | 48.92
1981-12-23 | 23 | 12 | 1 | 10 | 50 | 19.3458 |  | 50
1981-12-24 | 24 | 12 | 0.041667 | 10 | 50 | 19.3458 |  | 50
1981-12-24 | 24 | 12 | 0.083333 | 10 | 50 | 19.0956 |  | 50
1981-12-24 | 24 | 12 | 0.125 | 10 | 50 | 19.3458 |  | 50
1981-12-24 | 24 | 12 | 0.16667 | 11.1 | 51.98 | 20.1234 |  | 51.98
1981-12-24 | 24 | 12 | 0.20833 | 11.1 | 51.98 | 20.3933 |  | 51.98
1981-12-24 | 24 | 12 | 0.25 | 11.7 | 53.06 | 21.3566 | 53.06
1981-12-24 | 24 | 12 | 0.29167 | 12.2 | 53.96 | 22.2577 | 53.96
1981-12-24 | 24 | 12 | 0.33333 | 13.3 | 55.94 | 22.7141 | 55.94
1981-12-24 | 24 | 12 | 0.375 | 12.2 | 53.96 | 21.5775 | 53.96
1981-12-24 | 24 | 12 | 0.41667 | 12.2 | 53.96 | 21.8688 | 53.96
1981-12-24 | 24 | 12 | 0.45833 | 11.7 | 53.06 | 21.6384 | 53.06
1981-12-24 | 24 | 12 | 0.5 | 13.3 | 55.94 | 23.0282 | 55.94
1981-12-24 | 24 | 12 | 0.54167 | 13.9 | 57.02 | 23.68 | 57.02
1981-12-24 | 24 | 12 | 0.58333 | 12.2 | 53.96 | 22.2577 | 53.96
1981-12-24 | 24 | 12 | 0.625 | 11.7 | 53.06 | 22.0145 | 53.06
1981-12-24 | 24 | 12 | 0.66667 | 11.7 | 53.06 | 21.6384 | 53.06
1981-12-24 | 24 | 12 | 0.70833 | 11.7 | 53.06 | 21.6384 | 53.06
1981-12-24 | 24 | 12 | 0.75 | 11.1 | 51.98 | 21.3849 | 51.98
1981-12-24 | 24 | 12 | 0.79167 | 11.1 | 51.98 | 21.1142 | 51.98
1981-12-24 | 24 | 12 | 0.83333 | 12.2 | 53.96 | 21.8688 | 53.96
1981-12-24 | 24 | 12 | 0.875 | 11.1 | 51.98 | 20.3933 | 51.98
1981-12-24 | 24 | 12 | 0.91667 | 10 | 50 | 19.0956 |  | 50
1981-12-24 | 24 | 12 | 0.95833 | 9.4 | 48.92 | 18.0708 |  | 48.92
1981-12-24 | 24 | 12 | 1 | 8.3 | 46.94 | 17.5773 |  | 46.94
1981-12-25 | 25 | 12 | 0.041667 | 7.8 | 46.04 | 17.146 |  | 46.04
1981-12-25 | 25 | 12 | 0.083333 | 7.2 | 44.96 | 15.8152 |  | 44.96
1981-12-25 | 25 | 12 | 0.125 | 6.7 | 44.06 | 15.3606 |  | 44.06
1981-12-25 | 25 | 12 | 0.16667 | 6.1 | 42.98 | 15.094 |  | 42.98
1981-12-25 | 25 | 12 | 0.20833 | 5.6 | 42.08 | 14.7125 |  | 42.08
1981-12-25 | 25 | 12 | 0.25 | 5.6 | 42.08 | 14.5292 | 42.08
1981-12-25 | 25 | 12 | 0.29167 | 5.6 | 42.08 | 14.5292 | 42.08
1981-12-25 | 25 | 12 | 0.33333 | 5.6 | 42.08 | 14.346 | 42.08
1981-12-25 | 25 | 12 | 0.375 | 5.6 | 42.08 | 14.5292 | 42.08
1981-12-25 | 25 | 12 | 0.41667 | 5 | 41 | 14.2614 | 41
1981-12-25 | 25 | 12 | 0.45833 | 5.6 | 42.08 | 14.346 | 42.08
1981-12-25 | 25 | 12 | 0.5 | 5.6 | 42.08 | 13.9798 | 42.08
1981-12-25 | 25 | 12 | 0.54167 | 5.6 | 42.08 | 13.7969 | 42.08
1981-12-25 | 25 | 12 | 0.58333 | 5.6 | 42.08 | 13.7969 | 42.08
1981-12-25 | 25 | 12 | 0.625 | 5.6 | 42.08 | 13.3097 | 42.08
1981-12-25 | 25 | 12 | 0.66667 | 5 | 41 | 13.0339 | 41
1981-12-25 | 25 | 12 | 0.70833 | 3.9 | 39.02 | 12.7502 | 39.02
1981-12-25 | 25 | 12 | 0.75 | 3.9 | 39.02 | 12.5882 | 39.02
1981-12-25 | 25 | 12 | 0.79167 | 3.9 | 39.02 | 11.7794 | 39.02
1981-12-25 | 25 | 12 | 0.83333 | 2.8 | 37.04 | 11.3203 | 37.04
1981-12-25 | 25 | 12 | 0.875 | 2.8 | 37.04 | 11.1709 | 37.04
1981-12-25 | 25 | 12 | 0.91667 | 2.2 | 35.96 | 11.0534 |  | 35.96
1981-12-25 | 25 | 12 | 0.95833 | 1.7 | 35.06 | 10.9351 |  | 35.06
1981-12-25 | 25 | 12 | 1 | 1.7 | 35.06 | 10.9351 |  | 35.06
1981-12-26 | 26 | 12 | 0.041667 | 1.1 | 33.98 | 10.5682 |  | 33.98
1981-12-26 | 26 | 12 | 0.083333 | 1.1 | 33.98 | 10.4361 |  | 33.98
1981-12-26 | 26 | 12 | 0.125 | 1.1 | 33.98 | 10.3481 |  | 33.98
1981-12-26 | 26 | 12 | 0.16667 | 1.1 | 33.98 | 10.3481 |  | 33.98
1981-12-26 | 26 | 12 | 0.20833 | 0.6 | 33.08 | 10.2231 |  | 33.08
1981-12-26 | 26 | 12 | 0.25 | 0 | 32 | 9.8652 | 32
1981-12-26 | 26 | 12 | 0.29167 | 0.6 | 33.08 | 10.2231 | 33.08
1981-12-26 | 26 | 12 | 0.33333 | 0.6 | 33.08 | 10.3504 | 33.08
1981-12-26 | 26 | 12 | 0.375 | 1.1 | 33.98 | 10.5682 | 33.98
1981-12-26 | 26 | 12 | 0.41667 | 2.2 | 35.96 | 11.0534 | 35.96
1981-12-26 | 26 | 12 | 0.45833 | 2.8 | 37.04 | 11.4199 | 37.04
1981-12-26 | 26 | 12 | 0.5 | 3.3 | 37.94 | 11.935 | 37.94
1981-12-26 | 26 | 12 | 0.54167 | 3.9 | 39.02 | 12.3184 | 39.02
1981-12-26 | 26 | 12 | 0.58333 | 4.4 | 39.92 | 12.8093 | 39.92
1981-12-26 | 26 | 12 | 0.625 | 5.6 | 42.08 | 13.3097 | 42.08
1981-12-26 | 26 | 12 | 0.66667 | 5.6 | 42.08 | 13.4923 | 42.08
1981-12-26 | 26 | 12 | 0.70833 | 5.6 | 42.08 | 13.3097 | 42.08
1981-12-26 | 26 | 12 | 0.75 | 5.6 | 42.08 | 13.3097 | 42.08
1981-12-26 | 26 | 12 | 0.79167 | 5.6 | 42.08 | 12.8839 | 42.08
1981-12-26 | 26 | 12 | 0.83333 | 5.6 | 42.08 | 12.7623 | 42.08
1981-12-26 | 26 | 12 | 0.875 | 5.6 | 42.08 | 12.7623 | 42.08
1981-12-26 | 26 | 12 | 0.91667 | 5.6 | 42.08 | 12.8839 |  | 42.08
1981-12-26 | 26 | 12 | 0.95833 | 5 | 41 | 12.6257 |  | 41
1981-12-26 | 26 | 12 | 1 | 5 | 41 | 12.8006 |  | 41
1981-12-27 | 27 | 12 | 0.041667 | 4.4 | 39.92 | 12.8093 |  | 39.92
1981-12-27 | 27 | 12 | 0.083333 | 3.9 | 39.02 | 12.5882 |  | 39.02
1981-12-27 | 27 | 12 | 0.125 | 4.4 | 39.92 | 12.9771 |  | 39.92
1981-12-27 | 27 | 12 | 0.16667 | 4.4 | 39.92 | 12.9771 |  | 39.92
1981-12-27 | 27 | 12 | 0.20833 | 4.4 | 39.92 | 12.8093 |  | 39.92
1981-12-27 | 27 | 12 | 0.25 | 4.4 | 39.92 | 12.8093 | 39.92
1981-12-27 | 27 | 12 | 0.29167 | 4.4 | 39.92 | 12.8093 | 39.92
1981-12-27 | 27 | 12 | 0.33333 | 4.4 | 39.92 | 12.8093 | 39.92
1981-12-27 | 27 | 12 | 0.375 | 5 | 41 | 12.9172 | 41
1981-12-27 | 27 | 12 | 0.41667 | 6.1 | 42.98 | 13.2625 | 42.98
1981-12-27 | 27 | 12 | 0.45833 | 7.8 | 46.04 | 14.0132 | 46.04
1981-12-27 | 27 | 12 | 0.5 | 8.9 | 48.02 | 14.4925 | 48.02
1981-12-27 | 27 | 12 | 0.54167 | 10 | 50 | 14.9522 | 50
1981-12-27 | 27 | 12 | 0.58333 | 10.6 | 51.08 | 15.2483 | 51.08
1981-12-27 | 27 | 12 | 0.625 | 11.1 | 51.98 | 15.3009 | 51.98
1981-12-27 | 27 | 12 | 0.66667 | 10.6 | 51.08 | 15.5057 | 51.08
1981-12-27 | 27 | 12 | 0.70833 | 10 | 50 | 15.117 | 50
1981-12-27 | 27 | 12 | 0.75 | 8.9 | 48.02 | 14.6454 | 48.02
1981-12-27 | 27 | 12 | 0.79167 | 7.8 | 46.04 | 14.1549 | 46.04
1981-12-27 | 27 | 12 | 0.83333 | 7.2 | 44.96 | 13.7011 | 44.96
1981-12-27 | 27 | 12 | 0.875 | 6.1 | 42.98 | 13.2625 | 42.98
1981-12-27 | 27 | 12 | 0.91667 | 5 | 41 | 12.6257 |  | 41
1981-12-27 | 27 | 12 | 0.95833 | 5 | 41 | 12.6257 |  | 41
1981-12-27 | 27 | 12 | 1 | 4.4 | 39.92 | 12.418 |  | 39.92
1981-12-28 | 28 | 12 | 0.041667 | 3.9 | 39.02 | 12.3184 |  | 39.02
1981-12-28 | 28 | 12 | 0.083333 | 3.3 | 37.94 | 12.0383 |  | 37.94
1981-12-28 | 28 | 12 | 0.125 | 3.9 | 39.02 | 12.1566 |  | 39.02
1981-12-28 | 28 | 12 | 0.16667 | 3.3 | 37.94 | 11.935 |  | 37.94
1981-12-28 | 28 | 12 | 0.20833 | 2.8 | 37.04 | 11.7188 |  | 37.04
1981-12-28 | 28 | 12 | 0.25 | 2.2 | 35.96 | 11.5783 | 35.96
1981-12-28 | 28 | 12 | 0.29167 | 2.8 | 37.04 | 11.9681 | 37.04
1981-12-28 | 28 | 12 | 0.33333 | 2.8 | 37.04 | 11.9681 | 37.04
1981-12-28 | 28 | 12 | 0.375 | 3.3 | 37.94 | 12.0383 | 37.94
1981-12-28 | 28 | 12 | 0.41667 | 4.4 | 39.92 | 12.2504 | 39.92
1981-12-28 | 28 | 12 | 0.45833 | 6.7 | 44.06 | 13.1229 | 44.06
1981-12-28 | 28 | 12 | 0.5 | 7.8 | 46.04 | 13.3759 | 46.04
1981-12-28 | 28 | 12 | 0.54167 | 9.4 | 48.92 | 14.5746 | 48.92
1981-12-28 | 28 | 12 | 0.58333 | 10.6 | 51.08 | 14.3916 | 51.08
1981-12-28 | 28 | 12 | 0.625 | 10.6 | 51.08 | 14.306 | 51.08
1981-12-28 | 28 | 12 | 0.66667 | 10.6 | 51.08 | 14.306 | 51.08
1981-12-28 | 28 | 12 | 0.70833 | 8.3 | 46.94 | 14.4801 | 46.94
1981-12-28 | 28 | 12 | 0.75 | 7.2 | 44.96 | 14.3135 | 44.96
1981-12-28 | 28 | 12 | 0.79167 | 6.7 | 44.06 | 14.4374 | 44.06
1981-12-28 | 28 | 12 | 0.83333 | 5.6 | 42.08 | 13.9798 | 42.08
1981-12-28 | 28 | 12 | 0.875 | 6.1 | 42.98 | 14.2086 | 42.98
1981-12-28 | 28 | 12 | 0.91667 | 5.6 | 42.08 | 13.9798 |  | 42.08
1981-12-28 | 28 | 12 | 0.95833 | 5.6 | 42.08 | 13.9798 |  | 42.08
1981-12-28 | 28 | 12 | 1 | 5.6 | 42.08 | 13.9798 |  | 42.08
1981-12-29 | 29 | 12 | 0.041667 | 5 | 41 | 13.7348 |  | 41
1981-12-29 | 29 | 12 | 0.083333 | 5 | 41 | 13.0339 |  | 41
1981-12-29 | 29 | 12 | 0.125 | 3.9 | 39.02 | 13.2366 |  | 39.02
1981-12-29 | 29 | 12 | 0.16667 | 3.9 | 39.02 | 13.2366 |  | 39.02
1981-12-29 | 29 | 12 | 0.20833 | 3.3 | 37.94 | 12.9698 |  | 37.94
1981-12-29 | 29 | 12 | 0.25 | 3.9 | 39.02 | 13.453 | 39.02
1981-12-29 | 29 | 12 | 0.29167 | 3.9 | 39.02 | 13.453 | 39.02
1981-12-29 | 29 | 12 | 0.33333 | 3.9 | 39.02 | 13.453 | 39.02
1981-12-29 | 29 | 12 | 0.375 | 5 | 41 | 13.9103 | 41
1981-12-29 | 29 | 12 | 0.41667 | 6.7 | 44.06 | 14.635 | 44.06
1981-12-29 | 29 | 12 | 0.45833 | 7.8 | 46.04 | 14.9358 | 46.04
1981-12-29 | 29 | 12 | 0.5 | 10 | 50 | 15.6943 | 50
1981-12-29 | 29 | 12 | 0.54167 | 11.1 | 51.98 | 16.3667 | 51.98
1981-12-29 | 29 | 12 | 0.58333 | 12.2 | 53.96 | 16.8533 | 53.96
1981-12-29 | 29 | 12 | 0.625 | 12.8 | 55.04 | 17.0729 | 55.04
1981-12-29 | 29 | 12 | 0.66667 | 10.6 | 51.08 | 16.3653 | 51.08
1981-12-29 | 29 | 12 | 0.70833 | 8.9 | 48.02 | 15.6409 | 48.02
1981-12-29 | 29 | 12 | 0.75 | 7.8 | 46.04 | 15.149 | 46.04
1981-12-29 | 29 | 12 | 0.79167 | 7.8 | 46.04 | 15.149 | 46.04
1981-12-29 | 29 | 12 | 0.83333 | 7.8 | 46.04 | 15.149 | 46.04
1981-12-29 | 29 | 12 | 0.875 | 8.3 | 46.94 | 15.3622 | 46.94
1981-12-29 | 29 | 12 | 0.91667 | 8.3 | 46.94 | 15.3622 |  | 46.94
1981-12-29 | 29 | 12 | 0.95833 | 8.3 | 46.94 | 15.3622 |  | 46.94
1981-12-29 | 29 | 12 | 1 | 7.2 | 44.96 | 14.8588 |  | 44.96
1981-12-30 | 30 | 12 | 0.041667 | 6.7 | 44.06 | 14.635 |  | 44.06
1981-12-30 | 30 | 12 | 0.083333 | 6.7 | 44.06 | 16.1539 |  | 44.06
1981-12-30 | 30 | 12 | 0.125 | 6.7 | 44.06 | 16.4187 |  | 44.06
1981-12-30 | 30 | 12 | 0.16667 | 7.2 | 44.96 | 16.6371 |  | 44.96
1981-12-30 | 30 | 12 | 0.20833 | 7.8 | 46.04 | 17.146 |  | 46.04
1981-12-30 | 30 | 12 | 0.25 | 7.8 | 46.04 | 17.3607 | 46.04
1981-12-30 | 30 | 12 | 0.29167 | 8.3 | 46.94 | 17.8738 | 46.94
1981-12-30 | 30 | 12 | 0.33333 | 9.4 | 48.92 | 18.5503 | 48.92
1981-12-30 | 30 | 12 | 0.375 | 10 | 50 | 19.0956 | 50
1981-12-30 | 30 | 12 | 0.41667 | 10.6 | 51.08 | 19.391 | 51.08
1981-12-30 | 30 | 12 | 0.45833 | 11.1 | 51.98 | 18.5978 | 51.98
1981-12-30 | 30 | 12 | 0.5 | 11.1 | 51.98 | 17.525 | 51.98
1981-12-30 | 30 | 12 | 0.54167 | 10.6 | 51.08 | 15.8493 | 51.08
1981-12-30 | 30 | 12 | 0.58333 | 10 | 50 | 15.3643 | 50
1981-12-30 | 30 | 12 | 0.625 | 9.4 | 48.92 | 14.5746 | 48.92
1981-12-30 | 30 | 12 | 0.66667 | 8.3 | 46.94 | 14.1866 | 46.94
1981-12-30 | 30 | 12 | 0.70833 | 7.8 | 46.04 | 14.1549 | 46.04
1981-12-30 | 30 | 12 | 0.75 | 7.2 | 44.96 | 13.6331 | 44.96
1981-12-30 | 30 | 12 | 0.79167 | 6.7 | 44.06 | 13.5168 | 44.06
1981-12-30 | 30 | 12 | 0.83333 | 6.1 | 42.98 | 13.1365 | 42.98
1981-12-30 | 30 | 12 | 0.875 | 5.6 | 42.08 | 13.0663 | 42.08
1981-12-30 | 30 | 12 | 0.91667 | 5.6 | 42.08 | 12.8839 |  | 42.08
1981-12-30 | 30 | 12 | 0.95833 | 5 | 41 | 12.5092 |  | 41
1981-12-30 | 30 | 12 | 1 | 5 | 41 | 12.5092 |  | 41
1981-12-31 | 31 | 12 | 0.041667 | 5 | 41 | 12.5092 |  | 41
1981-12-31 | 31 | 12 | 0.083333 | 5 | 41 | 12.5092 |  | 41
1981-12-31 | 31 | 12 | 0.125 | 4.4 | 39.92 | 12.418 |  | 39.92
1981-12-31 | 31 | 12 | 0.16667 | 4.4 | 39.92 | 12.2504 |  | 39.92
1981-12-31 | 31 | 12 | 0.20833 | 4.4 | 39.92 | 12.418 |  | 39.92
1981-12-31 | 31 | 12 | 0.25 | 3.9 | 39.02 | 12.3184 | 39.02
1981-12-31 | 31 | 12 | 0.29167 | 3.9 | 39.02 | 12.0488 | 39.02
1981-12-31 | 31 | 12 | 0.33333 | 3.9 | 39.02 | 12.3184 | 39.02
1981-12-31 | 31 | 12 | 0.375 | 3.9 | 39.02 | 12.3184 | 39.02
1981-12-31 | 31 | 12 | 0.41667 | 3.9 | 39.02 | 12.4263 | 39.02
1981-12-31 | 31 | 12 | 0.45833 | 5 | 41 | 12.9172 | 41
1981-12-31 | 31 | 12 | 0.5 | 5.6 | 42.08 | 13.0663 | 42.08
1981-12-31 | 31 | 12 | 0.54167 | 6.1 | 42.98 | 13.3885 | 42.98
1981-12-31 | 31 | 12 | 0.58333 | 7.2 | 44.96 | 13.7011 | 44.96
1981-12-31 | 31 | 12 | 0.625 | 7.8 | 46.04 | 13.8715 | 46.04
1981-12-31 | 31 | 12 | 0.66667 | 7.8 | 46.04 | 13.8715 | 46.04
1981-12-31 | 31 | 12 | 0.70833 | 7.2 | 44.96 | 13.6331 | 44.96
1981-12-31 | 31 | 12 | 0.75 | 7.2 | 44.96 | 13.4972 | 44.96
1981-12-31 | 31 | 12 | 0.79167 | 7.2 | 44.96 | 13.6331 | 44.96
1981-12-31 | 31 | 12 | 0.83333 | 6.7 | 44.06 | 13.5168 | 44.06
1981-12-31 | 31 | 12 | 0.875 | 6.1 | 42.98 | 13.2625 | 42.98
1981-12-31 | 31 | 12 | 0.91667 | 6.1 | 42.98 | 13.3885 |  | 42.98
1981-12-31 | 31 | 12 | 0.95833 | 6.1 | 42.98 | 13.2625 |  | 42.98
29951 | 31 | 12 | 1 | 6.1 | 42.98 | 13.2625 |  | 42.98

## Steam Trap - ConEd Method - Old (hidden)
Orifice Plate and Common Area Stream trap Savings
Development |  | 3611 HHP |  | Steam Loss (lb/hr) | 3515.6053
Boiler Data | Make/Model | Federal / FST 200 |  | Annual Savings (therms) | 23936.1532
| Quantity | 1 |  | Repair Cost
| Input Capacity (kBtuhin) | 6695 |  | TRC
| Efficiency (Et) | 0.75 |  | Max Incentive | 47872.3063
| Operating Pressure (psig) | 2
| EFLH | 526
Steam Trap Data | Make/Model | ½” Mepco Model # 1E | Comments
| Orifice Size (in2)* | 0.051875 | * ½” Mepco Model # 1E. The orifice size is .25”
| Total Quantity | 354 | Average common area trap orifice is .374"
| Quantity Sampled | 79 | Weighted Avg is 0.257" (Used in Formula) ==> |  |  | 0.257
| Failure Rate | 0.6 | Conservative Estimate
| Failure Position (% open) | 0.5 | Conservative Estimate

## Inputs (hidden)
Inputs
Financing
| Interest Rate | 3%
[6 empty] | Steam trap | Value | Unit | Suggested value
| Building Info | Value | Unit | Suggested value |  | Total number of steam traps | 373 | traps
| Floor Area | 134000 | SF |  |  | Percentage Failed steam traps | 65% |  | 10%-50%, useful life of a trap is 4-6 years
| Percentage Heated Area | 100% | % | 75%-100% |  | Orifice steam trap diameter | 0.257 | in | 1/4" or 1/2"
| Number of Units | 123 | Units |  |  | Average opening of the failed trap | 50% | % | 75%, failed-close traps are usually changed right away (no heat)
[6 empty] | Number of New Steam Trap | 0 | traps
| Boiler Info | Value | Unit | Suggested value |  | Cost | 140 | per steam trap including labor
| Boiler efficiency | 75% | η (%) | 80% |  | Operation pressure | 2 | PSI | 1-6 PSI
| Current Pressure | 5 | psi
| Boiler Capacity | 254.443 | MBTUH |  |  | Roof Insulation | Value | Unit | Suggested value
| Equivalent Full Load Hours for steam season | 526 | EFLH (hrs) | 40% during 6 months |  | Roof Area | 31000 | SF | Footprint of the building
| Boiler Length (without smoke box) | 94 | in | 80in to 100in |  | Existing R-Value Roof | 3 | h.°F.ft²/BTU
| Boiler Diameter | 54 | in | 40in to 65in |  | Cost of insulating from R-existing to R-38 | 3 | $/sqft | $2 to $4
| DHW Heating Efficiency | 0.7 | η (%) | 0.65 - 0.75
[6 empty] | Low Flow Devices | Quantity | Averaged Existing GPM | Proposed GPM | Cost
| Energy Cost | Value | Unit | Suggested value |  | Kitchen Faucets | 139 | 2 | 1.5 | 15
| Gas | 1.1 | $/therm | 0.9-1.2 $/Therm |  | Restroom Faucets | 139 | 2.5 | 0.75 | 15
| Electricity | 0.2 | $/kWh | 0.19-0.3 $/kWh |  | Showerheads | 139 | 2 | 1.75 | 75
| Air Sealing | Value | Suggested Value
| Cost per Unit | 250 | $200-$300 |  |  | TRVs | Quantity | Unit
| ACH Reduction | 0.25 | 0.05 to 0.3 |  |  | Number of radiators | 373 | radiators | 2-3 per unit
[6 empty] | Cost per TRV | 175 | per TRV | $90 to $150
| MasterVenting/Balancing | Value | Unit | Suggested Value
| Cost per building | 32000 | $ |  |  | EMS | Value | Unit | Suggested Value
[6 empty] | Cost | 15000 | $
| Pipe Insulation | Type | Diameter | Length | Proposed Insulation Type | Proposed Insulation Thickness
| Riser Supply | Steam Heat | 2 | 1 | Rigid Foam | 1
| Riser Return | Steam Heat | 0.75 | 1 | Rigid Foam | 1
| Radiator Supply | Steam Heat | 0.75 | 1 | Rigid Foam | 1
| Radiator Return | Steam Heat | 0.5 | 1 | Rigid Foam | 1
Type 5
Type 6
Type 7
Type 8
Type 9
| Pipe Insulation | Value | Unit | Suggested Value
| Cost | 20 | $/LF | $20 to $30
Note on C15: Julien Marrec: Hope you're not using 4400hrs as EFLH, otherwise it should be more like 1800 if only heating, or 2200 if heating + summer dhw
Note on F32: Fabien Bar: ConEdison do not incentives insulation other than Fiberglass type.

## Boiler Insulation (custom) (hidden)
Boiler Insulation
| Constant | Value | Units |  |  | Inputs | Value | Units |  |  | Heat Transfer through the Boiler Jacket is modeled as three parallele branches, one branch for each surface area of the boiler :
| Hc Air | 2.5 | BTU/SF-hr-F |  |  | Length | 94 | in |  |  | Front, Back and Curved Side. For each surface, the equivalent resistance is the sum of the conductive resistance through the steel, the conductive resistance through the insulation and the convective resistance due to the surrounding air.
| Thermal conductivity Steel | 298.42 | Btu-in/hr-ft2-F |  |  | Diameter | 54 | in
|  | 2.0724 | Btu/hr-in-F |  |  | EFHL Summer | 4380 | hours
| K-value Insulation | 0.25 | Btu-in/hr-ft2-F |  |  | EFHL Winter | 4380 | hours
|  | 0.0017361 | Btu/hr-in-F |  |  | Delta Summer | 105 | F
| K-value Insulation derated | 0.5 | Btu-in/hr-ft2-F |  |  | Delta Winter | 157 | F
|  | 0.0034722 | Btu/hr-in-F |  |  | Thickness Insulation | 2 | in
[6 empty] | Thickness Steel | 0.375 | in
| Desc | Value | Unit |  |  | Average Temp Inside Boiler Winter | 212 | F
| Area middle | 110.7411 | SF |  |  | Average Temp Inside Boiler Summer | 180 | F
| Area front | 15.9043 | SF |  |  | Inner Diameter | 53.25 | in
| Area back | 15.9043 | SF |  |  | Outer Diameter | 54 | in
[6 empty] | Outer Diameter Insulation | 58 | in |  |  |  |  | R_conduction through steel |  | R_conduction through insulation | R_convection
FRONT
| Baseline |  |  |  |  | Proposed | [5 empty] | BACK
|  | Front | Back | Side | Units |  | Front | Back | Side | Units
| R_convection | 0.02515 | 0.02515 | 0.003612 | hr-F/BTU | R_convection | 0.02515 | 0.02515 | 0.003612 | hr-F/BTU
| R_conduction_steel | 7.9011e-05 | 7.9011e-05 | 1.1427e-05 | hr-F/BTU | R_conduction_steel | 7.9011e-05 | 7.9011e-05 | 1.1427e-05 | hr-F/BTU |  | SIDE
| Insulation Thickness | 0 | 0 | 2 | in | Insulation Thickness | 2 | 2 | 2 | in
| R_conduction_ins | 0 | 0 | 0.034845 | hr-F/BTU | R_conduction_ins | 0.2515 | 0.2515 | 0.034845 | hr-F/BTU
| R_total | 0.025229 | 0.025229 | 0.038469 | hr-F/BTU | R_total | 0.27673 | 0.27673 | 0.038469 | hr-F/BTU
| R_total | 0.0094996 |  |  | hr-F/BTU | R_total | 0.0301 |  |  | hr-F/BTU
R_tot equivalent for the Boiler
| Losses Summer | 11053.1187 | Btu/hr |  |  | Losses Summer | 3488.3562 | Btu/hr
| Annual Losses Summer | 48.4127 | MMBtu |  |  | Annual Losses Summer | 15.279 | MMBtu
| Losses Winter | 16000.7051 | Btu/hr |  |  | Losses Winter | 5049.8109 | Btu/hr
| Annual Losses Winter | 70.0831 | MMBtu |  |  | Annual Losses Winter | 22.1182 | MMBtu
| Savings | 81.0986 | MMBTU