## Instructions
Low Carbon Pathways Workscope Tool Instructions
Tool Version 4.2, Released April 2025
1. Complete one tool for each building within a project. If there are multiple buildings with the SAME height, heating fuel, type of heating equipment, and DHW equipment, the information for those buildings may be combined into one tool. In that instance, information should be aggregated accordingly (e.g. number of 1-bedroom units should represent the number across all buildings represented).
2. During the Pre-Construction stage, complete the 'General Project Info' tab and applicable 'Pre-const' tab(s).
3. During the Partial and Construction complete stages, complete the applicable sections in the 'Const' tab(s).
4. Complete all applicable tabs and blue cells within those tabs.
5. Throughout the tool there are comments embedded in some cells to assist in data entry. Hover over the cell to read the comments.
6. Program staff will provide comments in the applicable 'QC Feedback' tabs and sections. Please review and respond within those tabs and update the tool as requested.

## General Project Info
General Project Information
Instructions
Complete the blue cells as applicable.
If submitting multiple Workscope Tools, please complete the General Project Info tab only once.
Project Name (as listed in application)
Total number of buildings in entire project
Total number of units in entire project
Building Information
Building Name, if applicable
Building Street Address
Building city
Building State
Building Zip Code
Building County
Borough-Block-Lot (BBL) Number (NYC Only) |  | Additional Notes
Year building was constructed (approximate is acceptable)
Number of stories (if multiple buildings, please enter the stories of the building(s) with the greatest number of units)
Number of buildings described in this tool
Are there non-residential uses at this property?
Total gross floor area within the thermal envelope (include commercial/retail spaces and conditioned garages)
Gross floor area for commercial/retail spaces, if any
Gross floor area of conditioned garage, if any
Dwelling Units and Occupancy
Number of studio units
Number of 1-bedroom units
Number of 2-bedroom units
Number of 3-bedroom units
Number of 4-bedroom units
Number of 5-bedroom units
Total number of units | 0
Total number of bedrooms | 0
Primary residential demographic
Full-year average vacancy rate for most recent 12 months
Full-year average vacancy rate for the year before last (24-12 months ago)
Utility Information
Electric Utility Company
Gas Utility Company
Other Utility (if not mentioned in list)
Electric Metering Configuration
Are 100% of the apartments metered for electricity as described above? If not, how many are not?
Gas Metering Configuration
Are 100% of the apartments metered for gas as described above? If not, how many are not?
If the property has natural gas, what options best describe how it is used in the building? Mark with an "X" all that apply.
Space Heating
DHW Heating
Cooking
Other, please describe
On-site Solar (If a project has on-site solar, daily solar production must be submitted. See Appendix B in Attachment A for details.)
Does the property have a behind-the-meter solar PV system?
If yes, what is the rated total DC wattage of the system? (in kW)
Combined Heat and Power (If a project has CHP, daily electricity and useful heat production must be submitted. See Appendix B in Attachment A for details.)
Does the property have a cogeneration (combined heat and power) system?
If yes, please describe what the recovered heat is used for (e.g. space heating; DHW; etc.).
Space Heating Information
Primary Space Heating System
Space Heating Fuel
Equipment Type
Is the heating equipment central or in-unit?
How many heaters (boilers/furnaces/etc.) are there?
Spaces Served
End Use Equipment
Distribution Type
Secondary Space Heating System, if applicable
Space Heating Fuel
Equipment Type
Is the heating equipment central or in-unit?
How many heaters (boilers/furnaces/etc.) are there?
Spaces Served
End Use Equipment
Distribution Type
Space Cooling Information
Primary Cooling System
Space Cooling Fuel
Equipment Type
Equipment Quantity
Spaces Served
Controls
Distribution Type
Equipment Ownership
Secondary Cooling System, if applicable
Space Cooling Fuel
Equipment Type
Equipment Quantity
Spaces Served
Controls
Distribution Type
Equipment Ownership
Domestic Hot Water (DHW) Information
DHW System 1
Is DHW heated by the space heating boiler?
DHW Fuel Type
DHW Equipment Type
Quantity of DHW Heaters
Location of DHW Heaters
Spaces Served
DHW System 2, if applicable
Is DHW heated by the space heating boiler?
DHW Fuel Type
DHW Equipment Type
Quantity of DHW Heaters
Location of DHW Heaters
Spaces Served
Other Project Information
If applicable, please provide any additional info about the heating, cooling, and DHW systems to assist us in understanding the energy usage patterns in the building(s).
Note on B10: Complete one tool for each building within a project. If there are multiple buildings with the SAME height, heating fuel, type of heating equipment, and DHW equipment, the information for those buildings may be combined into one tool. In that instance, information should be aggregated accordingly (e.g. number of 1-bedroom units should represent the number across all buildings represented).

## Env Pre-const (hidden)
Envelope Pre-Construction Information
Instructions
This tab calculates existing and proposed area weighted U-value. Complete the blue cells as applicable.
Envelope Existing Conditions
Describe General Envelope Condition and Construction
Envelope Components | Description of Existing Construction (include depths, dimensions, and material) |  |  | Verification Method | Existing R-Value | Existing U-Value | Area (sqft) | Existing Area Weighted U-Value by Component | Additional Notes
Roof 1
Roof 2
Wall 1
Wall 2
Wall 3
Other 1 | [7 empty] | -
Other 2 | [7 empty] | -
Windows | Describe Existing Construction | Existing Operation Type | Existing Framing Material | # of Panes | Qty. | Existing U-Value | Total Area (sqft) for all the Windows per Type | Existing Area Weighted U-Value by Component | Additional Notes
Window 1
Window 2
Window 3
Sliding Glass Door 1
Sliding Glass Door 2
Sliding Glass Door 3
Opaque Door 1 | [7 empty] | -
Opaque Door 2 | [7 empty] | -
Opaque Door 3 | [7 empty] | -
Window-to-Wall Ratio
[7 empty] | Area (sqft) | Existing Area Weighted U-Value by Component
[5 empty] | Whole Building Envelope Total |  | 0
[5 empty] | Roof Total |  | 0 | 0
[5 empty] | Wall Total | Wall Total | 0 | 0
[5 empty] | Window Total | Window Total | 0 | 0
[5 empty] | Sliding Glass Door Total | Window Total | 0 | 0
Envelope Proposed Upgrade
Envelope Components | Description of Proposed Construction (include depths, dimensions, and material) |  |  | Proposed Added R-Value | Total Proposed R-Value | Proposed Total U-Value | Area (sqft) | Proposed Area Weighted U-Value by Component | Additional Notes
Roof 1
Roof 2
Wall 1
Wall 2
Wall 3
Other 1 | [7 empty] | -
Other 2 | [7 empty] | -
Windows | Describe Proposed Construction | Proposed Operation Type | Proposed Framing Material | # of Panes | Qty. | Proposed U-Value | Total Area (sqft) for all the Windows per Type | Proposed Area Weighted U-Value by Component | Additional Notes
Window 1
Window 2
Window 3
Sliding Glass Door 1
Sliding Glass Door 2
Sliding Glass Door 3
Opaque Door 1 | [7 empty] | -
Opaque Door 2 | [7 empty] | -
Opaque Door 3 | [7 empty] | -
Window-to-Wall Ratio
[7 empty] | Area (sqft) | Proposed Area Weighted U-Value by Component | U-Value Target based on Tier | Current tier
[6 empty] | Whole Building Envelope Total |  |  | N/A
[5 empty] | Roof Total |  |  |  | Tier 1 ≤0.025; Tier 2 ≤0.020
[5 empty] | Wall Total | Wall Total |  |  | Tier 1 ≤0.05 ; Tier 2 ≤0.03
[5 empty] | Window Total | Window Total |  |  | Tier 1 N/A; Tier 2 ≤0.27
[5 empty] | Sliding Glass Door Total | Window Total |  |  | Tier 1 N/A; Tier 2 ≤0.27
Proposed Thermal Bridging Mitigation
Area | Please explain how thermal bridging will be mitigated
Slab Edges
Bulkheads
Rim Joists
Roof-to-Wall Connections
Proposed Installed Cost Information
Component Type | Total Measure Cost | Additional Notes
Note on G8: If R-Value is estimated, be sure to select "estimated" in the Verification Method column.
Note on I8: Area should only include the applicable envelope component. E.g. wall area should exclude doors and windows, etc.
Note on H16: If unknown, use ASHRAE-estimated U-Value
Note on I36: Area should only include the applicable envelope component. E.g. wall area should exclude doors and windows, etc.
Note on B70: Group components as appropriate, e.g. windows, wall insulation, etc.
Note on C70: Include all costs such as labor and material.

## Env Const (hidden)
Envelope Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Roof and Wall Insulation
Building Address | Location | Envelope Component | Type of Insulation Installed | Cavity insulation installed without compression or slumping? | Wall Section Description |  |  | Area Insulated (sqft) | Effective R-Value of Envelope Component | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 30% of the wall insulation installed? |  |  | #DIV/0!
Partial Installation - PROGRAM STAFF COMPLETES
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 30% of the wall insulation installed? |  |  | #DIV/0!
Construction Complete
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 100% of the wall insulation installed? |  |  | #DIV/0!
Construction Complete - PROGRAM STAFF COMPLETES
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 100% of the wall insulation installed? |  |  | #DIV/0!
Door Replacement
Building Address | Location | Door Type (Slider, Patio, Garage, etc.) | Energy Star? | U-Value | Properly Air Sealed? | % Glazing | Low-E? | Additional Notes |  |  | Quantity Inspected
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Window Replacement
Building Address | Location | Window Operation Type | # of Panes | Frame Material | U-Value | SHGC | Gas Fill | Low-E? | Energy Star? | Properly Air Sealed? | Quantity Inspected | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Component Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
|  |  | 0 |  |  |  |  | Measure
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Envelope
Category | Measure | Task |  | Description |  | Reference | Non-Conformance Category | Failure Description | Pass/Fail | Comment
Envelope - Roof | Insulation | Roof U-value target is met, confirmed with as-built workscope tool. Final roof R-values and U-value checked. |  | Verify that actual/installed roof U-value meets the target proposed in the envelope workscope tool. Minor failure if U-value is 100-105% of target. |  | Attachment A - Envelope | Minor | Roof U-value target was not met. Modify if non-conformance is critical.
Envelope - Roof | Insulation | Roof U-value target is met, confirmed with as-built workscope tool. Final roof R-values and U-value checked. |  | Verify that actual/installed roof U-value meets the target proposed in the envelope workscope tool. Major failure if U-value is 105-110% of target. |  | Attachment A - Envelope | Major | Roof U-value target was not met. Modify if non-conformance is critical.
Envelope - Roof | Insulation | Roof U-value target is met, confirmed with as-built workscope tool. Final roof R-values and U-value checked. |  | Verify that actual/installed roof U-value meets the target proposed in the envelope workscope tool. Critical failure if U-value is greater than 110% of target. |  | Attachment A - Envelope | Critical | Roof U-value target was not met. Modify if non-conformance is critical.
Envelope - Roof | General | Roof insulation must comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | System and system components must be installed in accordance with manufacturer requirements and relevant permit/code requirements. |  | Attachment A - Envelope | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Envelope - Roof | Thermal bridging | Thermal bridging at bulkheads must be mitigated. Photo documentation has been submitted. |  | Thermal bridging mitigated at bulkheads. |  | Attachment A - Envelope | Minor | Thermal bridging was not mitigated at the following locations: _________. Mitigate thermal bridging and provide photo documentation.
Envelope - Roof | Continuous Air Barrier | A continuous air barrier must be installed at the thermal envelope. |  | A continuous air barrier must be installed at the roof/attic plane that forms the thermal envelope. |  | Attachment A - Envelope | Minor | A continuous air barrier was not installed; the following locations must be air sealed: ________. Provide photo documentation.
Envelope - Roof | Cavity insulation | If installed, cavity insulation must not compress or slump. Photo documentation has been submitted. |  | Cavity insulation does not compress or slump, refer to grade 1 condition according latest RESNET standards. |  | Attachment A - Envelope | Minor | Cavity insulation compresses or slumps based on photo file named ________________. Correct compression or slumping and provide photo documentation or IR scan.
Envelope - Roof | Cutsheets | Cutsheets must be submitted for installed roof insulation. |  | Verify that submitted cutsheets match what was observed on site. |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Wall | Insulation | Wall U-value target is met, confirmed with as-built workscope tool. Final wall R-values and U-values checked. |  | Verify that actual/installed wall U-value meets the target proposed in the envelope workscope tool. Minor failure if U-value is 100-105% of target. |  | Attachment A - Envelope | Minor | Wall U-value target was not met. Modify if non-conformance is critical.
Envelope - Wall | Insulation | Wall U-value target is met, confirmed with as-built workscope tool. Final wall R-values and U-values checked. |  | Verify that actual/installed wall U-value meets the target proposed in the envelope workscope tool. Major failure if U-value is 105-110% of target. |  | Attachment A - Envelope | Major | Wall U-value target was not met. Modify if non-conformance is critical.
Envelope - Wall | Insulation | Wall U-value target is met, confirmed with as-built workscope tool. Final wall R-values and U-values checked. |  | Verify that actual/installed wall U-value meets the target proposed in the envelope workscope tool. Critical failure if U-value is greater than 110% of target. |  | Attachment A - Envelope | Critical | Wall U-value target was not met. Modify if non-conformance is critical.
Envelope - Wall | General | Wall insulation must comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | System and system components must be installed in accordance with manufacturer requirements and relevant permit/code requirements. |  | Attachment A - Envelope | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Envelope - Wall | Thermal bridging | Thermal bridging at slab edges, bulkhead, rim joists, and roof-to-wall connections must be mitigated. Photo documentation has been submitted. |  | Thermal bridging mitigated at slab edges, bulkhead, rim joists, and roof-to-wall connections. |  | Attachment A - Envelope | Minor | Thermal bridging was not mitigated at the following locations. Mitigate thermal bridging and provide photo documentation.
Envelope - Wall | Continuous insulation | Exterior insulation must be continuous. Photo documentation has been submitted. |  | Exterior insulation is continuous, metal Z-girts are not allowed |  | Attachment A - Envelope | Minor | Exterior insulation is not continuous at the following locations: __________________ Provide continuous insulation at these locations and photo documentation.
Envelope - Wall | Continuous Air Barrier | A continuous air barrier must be installed, including at the roof-to-wall connection. |  | Continuous air barrier installed |  | Attachment A - Envelope | Minor | A continuous air barrier was not installed; the following locations must be air sealed: ________. Provide photo documentation.
Envelope - Wall | Cavity insulation | If installed, cavity insulation must not compress or slump. Photo documentation has been submitted. |  | Cavity insulation does not compress or slump, refer to grade 1 condition according latest RESNET standards. |  | Attachment A - Envelope | Minor | Cavity insulation compresses or slumps based on photo file named ________________. Correct compression or slumping and provide photo documentation or IR scan.
Envelope - Wall | Cutsheets | Cutsheets must be submitted for installed wall insulation. |  | Verify that submitted cutsheets match what was observed on site. |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Windows | Window U-value | Window U-value target is met, confirmed with as-built workscope tool. Final window R-value and U-value checked. |  | Verify that actual/installed window U-value meets the program target. Minor failure if U-value is 100-105% of target. |  | Attachment A - Envelope | Minor | Program U-value target was not met for installed windows. Modify if non-conformance is critical.
Envelope - Windows | Window U-value | Window U-value target is met, confirmed with as-built workscope tool. Final window R-value and U-value checked. |  | Verify that actual/installed window U-value meets the program target. Major failure if U-value is 105-110% of target. |  | Attachment A - Envelope | Major | Program U-value target was not met for installed windows. Modify if non-conformance is critical.
Envelope - Windows | Window U-value | Window U-value target is met, confirmed with as-built workscope tool. Final window R-value and U-value checked. |  | Verify that actual/installed window U-value meets the program target. Critical failure if U-value is greater than 110% of target. |  | Attachment A - Envelope | Critical | Program U-value target was not met for installed windows. Modify if non-conformance is critical.
Envelope - Windows | General | Windows comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | System and system components must be installed in accordance with manufacturer requirements and relevant permit/code requirements. |  | Attachment A - Envelope | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Envelope - Windows | Air sealing | Windows must be air sealed to the opening. Photo documentation has been submitted. |  | Seal windows to the opening with 2x backer rod and caulk sealant joints or applicable tape. Major failure if windows are not sealed or sealing is clearly inadequate. |  | Attachment A - Envelope | Major | New windows are not adequately sealed. Seal per program requirements and provide photo documentation.
Envelope - Windows | Air sealing | Windows must be air sealed to the opening. Photo documentation has been submitted. |  | Seal windows to the opening with 2x backer rod and caulk sealant joints or applicable tape. Minor failure if sealing is minorly deficient. |  | Attachment A - Envelope | Minor | New windows are not adequately sealed. Seal per program requirements and provide photo documentation.
Envelope - Windows | Cutsheets | Cutsheets must be submitted for installed windows. |  | Verify that submitted cutsheets match what was observed on site. |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Note on G7: List each component of the wall section from the exterior surface to the interior surface. Include the thickness of each component in inches.
Note on L83: Per the Program's minimum installation standards, windows must be air sealed with either 2x backer rod and caulk sealant joints or applicable tapes
Note on B112: Total Cost should align with submitted invoices.
Note on B114: Group components as appropriate, e.g. windows, wall insulation, etc.

## Code Vent Pre-const (hidden)
Envelope Package Ventilation Pre-Construction Information
Instructions
Complete the blue cells as applicable. Please see Attachment A for ventilation test-out option requirements. If the project is not pursuing the ventilation test out option, then please complete the ventilation proposed upgrades table. If the project is pursuing the ventilation test out option, then please complete the duct sealing table in the Test Out tab.
Will the add-on incentive ventilation option also be pursued?
Ventilation Existing Conditions
Ventilation | Equipment Type |  | System Type | Qty. | Location of Equipment |  | Total CFM | Method for Total CFM Calculation | If Other method was used, please describe |  | Duct Leakiness | System Operational? | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
[other]
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/ Commercial Kitchen
Garage
Laundry
[other]
Ventilation Test Out Option
Is the project pursuing the ventilation test out compliance option?
If yes, what equipment will be used for testing? Include manufacturer, model number, and date of last calibration.
Ventilation Proposed Upgrades
Ventilation | Equipment Type |  | System Type | Qty. | Manufacturer | Model | Location of Equipment |  | Controls | Total Fan Power (W) | Sensible Heat Recovery Efficiency | CFM/ Register | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
[other]
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/ Commercial Kitchen
Garage
Laundry
[other]
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on C9: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on O9: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B14: For other areas as needed, overwrite the header with an appropriate description.
Note on B23: For other areas as needed, overwrite the header with an appropriate description.
Note on C30: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on L30: At design external static pressure and design CFM
Note on M30: At manufacturer rated design conditions
Note on O30: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B35: For other areas as needed, overwrite the header with an appropriate description.
Note on B44: For other areas as needed, overwrite the header with an appropriate description.
Note on B47: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.
Note on C47: Include all costs such as labor and material.

## Code Vent TestOut & Const (hidden)
Envelope Package Ventilation Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable.
Kitchen
Building Address | Location | Measured CFM | CAR installed? | Duct-to-Sheetrock connection air sealed? | New exhaust fan installed? | New exhaust fan make and model | Controls for new fan | Exterior penetrations air sealed? | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Bathroom
Building Address | Location | Measured CFM | CAR installed? | Duct-to-Sheetrock connection air sealed? | New exhaust fan installed? | New exhaust fan make and model | Controls for new fan | Exterior penetrations air sealed? | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Ventilation Ductwork Sealing
Building Address | Shaft Description |  |  | # of Registers Served | # of Floors Served | Total Allowable Leakage (CFM50) | Total Measured Leakage (CFM50) | Additional Notes
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Ventilation
Category | Measure | Task |  | Description |  | Reference | Non-Conformance Category | Failure Description | Pass/Fail | Comment
Envelope - Ventilation | Central Exhaust | Ductwork must be cleaned. Photos have been submitted to show clean ductwork. (N/A if project is using Operation Test Out option.) |  | Verify that ductwork was cleaned. |  | Attachment A - Envelope | Incidental | Ductwork was not cleaned. Clean ductwork and submit photos before and after to demonstration cleaning.
Envelope - Ventilation | Central Exhaust | Ductwork must be sealed to program requirements. (N/A if project is using Operation Test Out option.) |  | Verify that ductwork was sealed. Major failure if no evidence of sealing or sealing is highly inadequate. |  | Attachment A - Envelope | Major | Ductwork was not sealed or sealing did not meet program requirements. Seal ductwork and submit photos test-out results.
Envelope - Ventilation | Central Exhaust | Ductwork must be sealed to program requirements. (N/A if project is using Operation Test Out option.) |  | Verify that ductwork was sealed. Minor failure if sealing was performed but some minor holes/gaps remain. |  | Attachment A - Envelope | Minor | Ductwork was not sealed or sealing did not meet program requirements. Seal ductwork and submit photos test-out results.
Envelope - Ventilation | Cutsheets | Cutsheets must be submitted for duct sealant. |  | Verify that submitted cutsheets match what was observed on site. |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Ventilation | Central Exhaust | System must exhaust airflow per program requirements for central exhaust systems. Testing and balancing results have been submitted. |  | 25 cubic feet per minute (CFM) continuous for each kitchen, 20 CFM continuous for each bathroom. Major failure if ventilation flow rate is <80% or >150% of target. |  | Attachment A - Envelope | Major | Central exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Central Exhaust | System must exhaust airflow per program requirements for central exhaust systems. Testing and balancing results have been submitted. |  | 25 cubic feet per minute (CFM) continuous for each kitchen, 20 CFM continuous for each bathroom. Minor failure if ventilation flow rate is 80-150% of target. |  | Attachment A - Envelope | Minor | Central exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Unitized Exhaust | System must exhaust airflow per program requirements for unitized exhaust systems. Testing and balancing results have been submitted. |  | 25 CFM continuous or 100 CFM intermittent for each kitchen; 20 CFM continuous or 50 CFM intermittent for each bathroom. Major failure if ventilation flow rate is <80% or >150% of target. |  | Attachment A - Envelope | Major | Unitized exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Unitized Exhaust | System must exhaust airflow per program requirements for unitized exhaust systems. Testing and balancing results have been submitted. |  | 25 CFM continuous or 100 CFM intermittent for each kitchen; 20 CFM continuous or 50 CFM intermittent for each bathroom. Minor failure of ventilation flow rate is 80-150% of target. |  | Attachment A - Envelope | Minor | Unitized exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Unitized Exhaust | If replacing windows in a building without mechanical exhaust, install mechanical exhaust in each bathroom and kitchen. Contractor's log of installed exhaust fans by apartment number has been submitted. |  | Verify that an exhaust system was installed in every apartment. |  | Attachment A - Envelope | Major | An exhaust system was not installed. Install compliant ventilation system.
Envelope - Ventilation | Cutsheets | Cutsheets must be submitted for exhaust fans. |  | Verify that submitted cutsheets match what was observed on site. |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Ventilation | Central or Unitized Exhaust | A third-party testing and balancing (TAB) contractor must balance and verify flow rates. (N/A if project is using Operation Test Out option.) |  | Testing and Balancing (TAB) contractor must be independent, hired by owner, not by energy contractor. |  | Attachment A - Envelope | Incidental | TAB contractor is not independent. Submit contract showing that TAB contractor is hired by owner.
Envelope - Ventilation | Central or Unitized Exhaust | The flow rates must be verified by the TAB contractor. Submit contractor's TAB report. (N/A if project is using Operation Test Out option.) |  | Verify that a TAB report has been submitted. |  | Attachment A - Envelope | Minor | No TAB report submitted. Submit report.
Envelope - Ventilation | Central or Unitized Exhaust | Flow measuring equipment must capable of measuring within a +/1 CFM tolerance at flow rates as low as 20 CFM. |  | Equipment meets program accuracy requirements; testing was not yet performed. |  | Attachment A - Envelope | Minor | Ventilation testing equipment does not meet program requirements. Re-submit ventilation testing equipment that meets program requirements.
Envelope - Ventilation | Central or Unitized Exhaust | Flow measuring equipment must capable of measuring within a +/1 CFM tolerance at flow rates as low as 20 CFM. |  | Testing was performed with equipment that does not meet program requirements |  | Attachment A - Envelope | Major | Ventilation testing equipment does not meet program requirements. Re-do all tests using test equipment that meets program requirements, and re-submit the final report.
Envelope - Ventilation | Central or Unitized Exhaust | If project is using the Operation Test Out option, Residential Energy Services Network (RESNET) sampling protocols must be followed. |  | Follow RESNET sampling protocols; for central systems, include at minimum top and bottom floors served by a riser. |  | Attachment A - Envelope | Minor | Sampling protocol does not match program requirements per RESNET. Re-submit ventilation test results that meets program requirements.
Envelope - Ventilation | Central or Unitized Exhaust | If project is using the Operation Test Out option, notification must be submitted to the Program when the ventilation testing will occur so site staff can attend. |  | Notify program staff at least two weeks prior to testing. |  | Attachment A - Envelope | Incidental | If program staff cannot attend testing, re-schedule testing.
Envelope - Ventilation | Unitized Exhaust | If project installed new unitized exhaust fans, submit duct sizing information in lieu of testing flows. |  | Duct sizes information must be submitted if the actual airflow is not tested in a sample of apartments. |  | Energy Star Multifamily New Construction - https://www.energystar.gov/sites/default/files/asset/document/Kitchen%20Exhaust%20Reference%20Guide%20ENERGY%20STAR%20Single-Family%20New%20Homes_Rev12.pdf | Incidental | Duct sizing information was not submitted. Submit all information required by Energy Star.
Envelope - Ventilation | Unitized Exhaust | Duct sizing meets Energy Star Multifamily New Construction requirements. |  | Duct sizes must comply with the prescriptive path of Energy Star Multifamily New Construction requirements. |  | Energy Star Multifamily New Construction - https://www.energystar.gov/sites/default/files/asset/document/Kitchen%20Exhaust%20Reference%20Guide%20ENERGY%20STAR%20Single-Family%20New%20Homes_Rev12.pdf | Minor | Duct sizing does not comply with Energy Star Multifamily New Construction requirements. Submit test results showing that airflow is adequate or re-install ducts that meet the sizing requirements.
Envelope - Ventilation | Exhaust penetrations | New exhaust penetrations must be air sealed at envelope. Photo documentation has been submitted. |  | New exhaust penetrations must be air sealed. |  | Attachment A - Envelope | Minor | Exhaust penetrations are not air sealed. Seal and provide photo documentation.
Envelope - Ventilation | Exhaust | Ventilation exhaust must vent to outside. Photo documentation has been submitted. |  | Exhaust must vent to outside. |  | Attachment A - Envelope | Major | Exhaust does not vent to the outside. Vent to the outside and provide photo documentation.
Envelope - Ventilation | Owner training and documentation | Owner's representative and onsite staff must trained in the use of the new ventilation system, and an owner's manual must be provided. |  | Training and documentation must be provided to site staff on how to use and maintain the new ventilation equipment. |  | Attachment A - Envelope | Minor | Site staff was not trained in the use of the new ventilation equipment. Provide training. OR An owner's manual detailing the new ventilation equipment was not provided to site staff. Provide owner's manual.

## H&C Pre-const
Heating and Cooling Pre-Construction Information
Instructions
Complete the blue cells as applicable.
Heating and Cooling Existing Conditions
| Heating Systems | Equipment Type | Qty. | Spaces Served | Fuel Source | Rated Efficiency | Rated Efficiency Units | Total System Output (Mbh) | Distribution Type | End Use Equipment | Additional Notes
* * | Primary Heating System
* * | Secondary Heating System
| Cooling Components | Equipment Type | Qty. | Spaces Served | Fuel Source | Rated Efficiency | Rated Efficiency Units | Distribution Type | Additional Notes
* * | Primary Cooling System
* * | Secondary Cooling System
Heating and Cooling Proposed Upgrade
| Heating System | Equipment Type | Spaces Served | Condenser Information | [7 empty] | Indoor Unit Information |  |  |  | Initial Heat Source for Water Loop (WWHP only) | Initial Cooling Source for Water Loop (WWHP only) | Additional Notes
|  |  |  | Qty. | Make | Model | Outdoor Unit Type | Rated Heating Capacity (Btu/hr.) | Required Heating Capacity (Btu/hr.) | Rated Efficiency | Required Efficiency | Indoor Unit Type | Qty. | Rated Efficiency | Required Efficiency
* * | System 1
* * | System 2
* * | System 3
| Electrical Service Upgrade Required? |  |  | Description of electric service upgrade, if applicable
| Is the existing fossil fuel equipment being removed? |  |  | Description of fossil fuel removal workscope, if applicable
Proposed Installed Cost Information
| Equipment Type | Total Measure Cost | Additional Notes
Note on H7: AFUE = Annual Fuel Utilization Efficiency Et = Thermal Efficiency HSPF = Heating Season Performance Factor COP = Coefficient of Performance
Note on L7: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on H11: SEER = Seasonal Energy Efficiency Ratio EER = Energy Efficiency Ratio COP = Coefficient of Performance
Note on J11: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on J17: Enter the efficiency required by in Attachment A.
Note on K17: Include the units of the efficiency you provide.
Note on L17: Enter the efficiency required by in Attachment A. Include the units of the efficiency.
Note on O17: Include the units of the efficiency you provide.
Note on P17: Include the units of the efficiency.
Note on B25: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.
Note on C25: Include all costs such as labor and material.

## H&C Const
Heating and Cooling Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Indoor Units
Building Address | Location | Manufacturer | Model # | Thermostat Setpoints | Space Temperature (F) | Outdoor Temp at Inspection (F) | Electric Resistance Control Set Correctly? | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Outdoor Units
Building Address | Space(s) Served | Manufacturer | Model # | Uniform Energy Factor | Rated Heating Capacity (Btu/hr) | Additional Notes
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Heating and Cooling
Category | Measure | Task |  | Description |  |  | Reference | Non-Conformance Category | Failure Description | Pass/Fail | Comment
Heating and Cooling Package | General | Electrification completed per workscope (heat pumps installed and functional). |  | Verify that the heat pumps are installed and functional. Major failure if installation is <80% complete. |  |  | Attachment A | Major | Space electrification was not complete. Complete the conversion and provide documentation to verify completion.
Heating and Cooling Package | General | Electrification completed per workscope (heat pumps installed and functional). |  | Verify that the heat pumps are installed and functional. Minor failure if installation is 80-99% complete. |  |  | Attachment A | Minor | Space electrification was not complete. Complete the conversion and provide documentation to verify completion.
Heating and Cooling Package | General | New equipment must meet energy efficiency of project workscope. |  | Verify that new equipment meets efficiency requirement of project workscope and program requirements. Major failure if efficiency is <90% of efficiency proposed in workscope. |  |  | Attachment A | Major | New equipment efficiency is less than workscope.
Heating and Cooling Package | General | New equipment must meet energy efficiency of project workscope. |  | Verify that new equipment meets efficiency requirement of project workscope and program requirements. Minor failure if efficiency is 90-99% of efficiency proposed in workscope |  |  | Attachment A | Minor | New equipment efficiency is less than workscope.
Heating and Cooling Package | General | Partial Electrification only: high-efficiency electric system must be installed to meet full heating and cooling loads down to 30F. |  | Verify that the heat pumps can meet the building load down to an outdoor temperature of 30F. |  |  | Attachment A | Major | Installed heat pumps cannot meet building heating load to 30F. Complete the work and submit documentation to verify completion.
Heating and Cooling Package | General | Partial Electrification only: second heat source does not prevent future full load electrification. |  | Verify that the supplemental heat source does not prevent full load electrification in the future. |  |  | Attachment A | Minor | Installed supplemental heat source prevents full load electrification in the future. Rectify and submit documentation to verify.
Heating and Cooling Package | General | Full Electrification only: for water-to-water heat pumps, the initial heating source is not a fluid that was previously heated by fossil fuel (unless from waste heat recovery from service hot water, heat-recovery chillers, or other building equipment). |  | Verify that the initial heating source for water-to-water heat pumps is not a fluid that was previously heated by fossil fuel. |  |  | Attachment A | Critical | The initial heating source for the water-to-water heat pumps was previously heated by fossil fuel. Reinstall with a different initial heating source and submit documentation showing completion.
Heating and Cooling Package | General | Heat pump installation must comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | Verify that system and system components were installed in accordance with manufacturer requirements and relevant permit/code requirements. |  |  | Manufacturer's instructions. | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Heating and Cooling Package | General | Cutsheets must be submitted for installed equipment. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A | Incidental | Cutsheet for _________ was not submitted. Submit cutsheet.
Heating and Cooling Package | Condensate lines | Condensate lines meet program requirements. |  | Observe condensate line where accessible for leaks. Confirm condensate lines terminate in either a domestic drain or external location. External locations must not terminate onto another heat pump unit or onto a walking surface that could cause slips if condensate freezes. |  |  | Clean Heat Checklist | Major | Condensate lines do not meet program requirements. Reinstall and submit photo documentation showing correct installation.
Heating and Cooling Package | Controls | If the equipment includes integrated electric resistance, the control sequence for the electric resistance must be set to ensure the electric resistance is only used as back-up for when the equipment cannot maintain adequate space temperature. |  | Verify that controls are properly set to control any integral electric resistance: - the electric resistance is used for back-up only when the equipment cannot maintain adequate space temperature - the system must include a time delay allowing adequate time for equipment to bring space temperature up - back-up electric resistance cannot be used to bring up a space to temperature. |  |  | Attachment A | Major | The integral resistance heat is not properly controlled. Install controls that meet program requirements, then submit documentation to show compliance.
Heating and Cooling Package | Controls | Integrated control system has been installed if required by workscope. |  | Confirm integrated control system has been installed and is operational. |  |  | Attachment A | Major | Integrated control system was not installed. Install and submit documentation verifying that installation is complete.
Heating and Cooling Package | Controls | Integrated control system documentation was provided and specifies the settings, referencing set points, and control type. |  | Confirm integrated control system documentation was submitted and specifies the controls settings, referencing set points, and control type. |  |  | Attachment A | Minor | Documentation for integrated control system was not submitted OR does not have all required information. [Re]submit the control documentation.
Heating and Cooling Package | Decommissioning | If fossil fuel equipment is removed, fuel source must be safely removed or terminated. |  | Verify that old fossil fuel system connections have been removed or capped off, if fossil fuel equipment has been removed. |  |  | Attachment A | Major | Complete the work and provide documentation to verify completion.
Heating and Cooling Package | Decommissioning | If fossil fuel equipment is removed, hole in chimney must be sealed. |  | Verify that any abandoned boiler exhaust connection to chimney was sealed, if fossil fuel equipment is removed. |  |  | Energy Conservation Construction Code2, Sections R402.4 and C402.5.1. | Minor | Abandoned connection to chimney no longer needed for fossil fuel equipment has not been sealed. Return to complete sealing and provide photographs to document.
Heating and Cooling Package | Decommissioning | The fossil fuel heating thermostat shall be removed or used to control the heat pump system. |  | Verify the thermostat controlling the fossil fuel heating appliance has been removed or confirm it will be used to control the heat pump system. |  |  | Clean Heat Checklist | Minor | The pre-construction thermostat is still installed. Remove it or submit documentation showing that it is being used to control the heat pump system.
Heating and Cooling Package | Decommissioning | If fossil fuel DHW is retained, the exhaust vents shall be resized to prevent carbon monoxide spillage. |  | (In the event that the fossil fuel DHW system is retained) confirm that the contractor attests to adequately resizing exhaust vents as needed to prevent carbon monoxide spillage. - If resizing of the exhaust vents is required, contractor must provide the original and final dimensions of the vents. |  |  | Clean Heat Checklist | Critical | The exhaust vent was not resized. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Decommissioning | All wall and ceiling penetrations shall be sealed where piping related to fossil fuel heating system has been removed. |  | Verify pipe penetrations of walls and ceilings (where visible) have been sealed where piping has been removed. Major failure if fewer than 80% of penetrations were sealed. |  |  | Clean Heat Checklist | Major | [describe where] penetrations were unsealed. Seal them and submit photo documentation showing corrected installation.
Heating and Cooling Package | Decommissioning | All wall and ceiling penetrations shall be sealed where piping related to fossil fuel heating system has been removed. |  | Verify pipe penetrations of walls and ceilings (where visible) have been sealed where piping has been removed. Minor failure if more than 80%, but not all, penetrations were sealed. |  |  | Clean Heat Checklist | Minor | [describe where] penetrations were unsealed. Seal them and submit photo documentation showing corrected installation.
Heating and Cooling Package | Documentation | The owner was delivered a copy of the Operational and Maintenance Handbook, including start-up and test reports |  | The owner was given a copy of the manufacturer Operation and Maintenance manual and provided with contact information for emergency service needs. |  |  | Energy Conservation Construction Code, Sections R303.3 and C408.1.1. | Incidental | The owner was not given a copy of the manufacturer Operation and Maintenance manual and provided with contact information for emergency service needs. Provide manuals and contact information and written confirmation of receipt by the owner.
Heating and Cooling Package | Documentation | Owner understands basic system operation, adjustment of dampers (if applicable), and controls. |  | The owner has been given training by installer, and understands basic system operation, especially heating operation. The owner understands how to program controls and thermostats (as needed). The owner understands basic safety and maintenance. |  |  | Energy Conservation Construction Code, Figure C408.2.4. | Incidental | The owner has not been given training by installer. Provide training to the owner, and written confirmation of receipt of training by the owner. Training to cover: heating operation, controls including programming, basic safety and maintenance.
Heating and Cooling Package | Documentation | Operator has been trained on controls. |  | Confirm customer/operator has been provided instructions on controls integration of supplemental heat sources to provide primacy of the ASHP equipment. |  |  | Clean Heat Checklist | Minor | Operator was not trained on system controls. Ensure that training occurs, then submit confirmation.
Heating and Cooling Package | Documentation | Owner shall be supplied with the Manufacturer's Warranty. |  | Verify Manufacturer's Warranty has been provided to owner |  |  | Clean Heat Checklist | Required | Owner was not given the Manufacturer's Warranty. Send it to the Owner, then submit confirmation that the Owner received it.
Heating and Cooling Package | Ductwork | Ductwork is sealed and insulated. |  | Verify that exposed new or retrofitted ductwork is properly sealed and insulated if located outside the building's thermal envelope. Major failure if less than 80% of the ductwork was sealed. |  |  | Clean Heat Checklist | Major | Ductwork is not sealed or insulated. Fix and submit photo documentation of sealing or insulation.
Heating and Cooling Package | Ductwork | Ductwork is sealed and insulated. |  | Verify that exposed new or retrofitted ductwork is properly sealed and insulated if located outside the building's thermal envelope. Minor failure if more than 80% but not all the ductwork was sealed. |  |  | Clean Heat Checklist | Minor | Ductwork is not sealed or insulated. Fix and submit photo documentation of sealing or insulation.
Heating and Cooling Package | Electrical | Electrical disconnect is accessible. |  | Verify that electrical disconnect is installed in an accessible location for service. |  |  | Clean Heat Checklist | Major | Electrical disconnect is not accessible. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Indoor Units | Air filters are installed. |  | Verify the presence of equipment air filters if applicable |  |  | Manufacturer's instructions. | Minor | Air filters are not installed. Install and submit photo documentation of updated installation.
Heating and Cooling Package | Indoor Units | The terminal units have sufficient clearance above and below. |  | Verify that the top and bottom clearance of ASHP Terminal Units meet the manufacturer's installation requirements, are sufficient for proper function, and that service panels are clearly accessible. |  |  | Manufacturer's instructions. | Major | The terminal units do not have sufficient clearance [describe location]. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Indoor Units | The terminal units have sufficient clearance to the side. |  | Verify that the side clearances of ASHP Terminal Units meet the manufacturer's installation requirements. |  |  | Manufacturer's instructions. | Minor | The terminal units do not have sufficient clearance [describe location]. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Outdoor Units | Outdoor units must be installed above the local snow line. |  | Verify that outdoor units are installed above the local snow line. |  |  | Manufacturer's instructions. | Minor | The outdoor unit is not installed above snow depth. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Outdoor Units | Outdoor units must be installed such that melting defrost condensate does not drip onto other outdoor units. |  | Verify that melting defrost condensate will not drip from one outdoor unit onto any other. |  |  | Manufacturer's instructions. | Minor | Condensate from some outdoor units might drip onto other outdoor units. Install drainage and submit photo documentation to verify.
Heating and Cooling Package | Outdoor Units | Units installed under a roof line/edge must have a rain/snow/ice shield. |  | Verify that if the unit is set under the roof line/edge, rain/snow/ice shield or drain cap is provided. |  |  | Manufacturer's instructions. | Minor | The units are under roof line/edge without shield. Provide shield or drain cap, and document with photos.
Heating and Cooling Package | Outdoor Units | Outdoor units are located per manufacturer's specifications. |  | Outdoor units are located with correct spacing from walls, from other outdoor units, and are not located in spaces such as outdoor stairwells that will prevent adequate air circulation, where applicable (for example, does not apply to ground source heat pumps). |  |  | Manufacturer's instructions. | Minor | Outdoor units are not correctly located. Relocate.
Heating and Cooling Package | Outdoor Units | Equipment is correctly secured. |  | Verify all exposed equipment and pipe supports appear to be properly secured. |  |  | Clean Heat Checklist | Major | Equipment is insufficiently secured. Correct installation and submit photo documentation.
Heating and Cooling Package | Outdoor Units | Outdoor unit is installed with sufficient clearances. |  | Verify outdoor unit is installed with sufficient clearances. |  |  | Manufacturer's instructions. | Major | Outdoor units do not have sufficient clearances. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Outdoor Units | Outdoor unit is installed level. |  | Verify outdoor unit is installed level. |  |  | Manufacturer's instructions. | Major | Outdoor unit is not level. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Outdoor Units | Vibration dampeners are installed. |  | If unit is connected to the building's framing (e.g. wall mounted, or on a connected deck), vibration dampeners are installed. |  |  | Manufacturer's instructions. | Minor | Vibration dampers are not installed. Fix and submit photo documentation showing corrected installation.
Heating and Cooling Package | Refrigerant Piping | New envelope penetrations must be sealed to prevent infiltration and rodents/insects or water penetration. |  | Verify envelope penetrations are sealed: Split system pipe penetrations are well-sealed both on the outside and inside of the penetration, including between pipes. Penetrations for packaged through-wall systems (PTHP, VTHP) are well sealed. |  |  | Attachment A | Minor | Penetrations are not adequately sealed on both the indoor and outdoor side of the penetration. Return to complete sealing and provide photographs to document.
Heating and Cooling Package | Refrigerant Piping | Refrigerant piping insulation is installed per the manufacturer's specifications, meets the correct thickness, and is code compliant. |  | Verify all accessible refrigerant line (indoor and outdoor) set is insulated. |  |  | Manufacturer's instructions. | Minor | Refrigerant piping is not adequately insulated. Insulate piping per code requirements and document with photographs.
Heating and Cooling Package | Refrigerant Piping | Exterior refrigerant pipe insulation is ultraviolet (UV) resistant and/or has a UV resistant covering. |  | Verify that the exterior pipe insulation is UV resistant or has a UV resistant covering or coating. Verify no more than 1" of any refrigerant line is unprotected at the outdoor unit connection. |  |  | Manufacturer's instructions. | Minor | Refrigerant pipes are not sufficiently protected from UV light. Protect exposed outdoor pipe insulation and submit photographs to document completion.
Heating and Cooling Package | Refrigerant Piping | No refrigerant leaks found. |  | Sample for refrigerant leaks at exposed field connections. Verify that no leaks were detected with a leak detector and/or soap bubble test. |  |  | Manufacturer's instructions. | Major | Heat pump system is leaking refrigerant. Identify leak locations, remove refrigerant, re-cut piping and re-make connections, follow pressure testing and vacuum protocol, recharge, and check again for leaks. Mark final refrigerant charge on outdoor unit in indelible marker.
Note on F7: Include night setback settings if applicable.
Note on B66: Total Cost should align with submitted invoices.
Note on B68: Group equipment as appropriate, e.g. duct sealing, HRV, etc.

## DHW Pre-const (hidden)
Domestic Hot Water Pre-Construction Information
Instructions
Complete the blue cells as applicable.
Domestic Hot Water Existing Conditions
| DHW System | Equipment Type | Unitized or Central System? | Qty. of Heaters | DHW from Space Heating Boiler? | Spaces Served | Fuel Source | Rated Efficiency | Rated Efficiency Units | Total Output (Mbh) | Storage Tank? | Additional Notes
* * | DHW System 1
* * | DHW System 2
Required Central DHW Minimum Installation Capacity Based on Project Location
| Climate Zone | Per Bedroom Method |  | Per Dwelling Unit Method
|  | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Bedroom) | Total Minimum Required Capacity (MBH) | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Dwelling Unit) | Total Minimum Required Capacity (MBH)
Domestic Hot Water Proposed Upgrades
| DHW System | Equipment Type | Unitized or Central System? | Qty. of Heaters | Manufacturer | Model | Total Output Capacity (MBH) | Uniform Energy Factor | EnergyStar Labeled? | Tank Capacity (Gal.) | Outdoor Unit Type | Additional Notes
* * | DHW System 1
* * | DHW System 2
| Is the existing fossil fuel equipment being removed? |  |  | Description of fossil fuel removal workscope, if applicable
Proposed Installed Cost Information
| Equipment Type | Total Measure Cost | Additional Notes
Note on J7: AFUE = Annual Fuel Utilization Efficiency Et = Thermal Efficiency COP = Coefficient of Performance
Note on B24: Group equipment as appropriate, e.g. tanks, etc.
Note on C24: Include all costs such as labor and material.

## DHW Const (hidden)
Domestic Hot Water Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Domestic Hot Water
Building Address | Location | Equipment Description | Manufacturer | Model # | Uniform Energy Factor | Total Output Capacity (MBH) | Control Settings | Water Temperature Readings |  | Additional Notes
(Apt #, Room, Floor, Space)
[8 empty] | Faucet Near Heater | Faucet Far from Heater
Partial Installation
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Partial Installation - PROGRAM STAFF COMPLETES
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Construction Completion
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Construction Completion - PROGRAM STAFF COMPLETES
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Homestic Hot Water
Category | Measure | Task |  | Description |  |  | Reference | Non-Conformance Category | Failure Description |  | Pass/Fail | Comment
Domestic Hot Water Package | General | Heat pump domestic hot water heater was installed. |  | Verify that the heat pump hot water heater was installed and is providing hot water per workscope. |  |  | Project workscope | Major | Heat pumps were not installed to heat DHW. Complete installation and submit documentation to verify.
Domestic Hot Water (DHW) | Health and Safety | Ensure that water is delivered at less than 130 degrees, to prevent scalding. Photo documentation submitted. |  | Verify that water is delivered at less than 130 degrees. Measure at tap. |  |  | U.S. Consumer Product Safety Commission, https://www.cpsc.gov/s3fs-public/5098.pdf. | Minor | Reduce hot water storage or mixing valve setpoint to ensure delivered water temperature is below 130 degrees. Submit a photo of the control setting and a photo of the measured DHW temperature at an apartment tap.
Domestic Hot Water Package | DHW Controls | Recirculation control installed. Photo documentation submitted. |  | Verify recirculation control has been installed |  |  | Energy Conservation Construction Code, Sections R403.5.2 and C404.7. | Minor | Recirculation control has not been installed. Install recirculation control and submit documentation to verify completion.
Domestic Hot Water Package | DHW Controls | Recirculation control installed meets energy code requirements. Test results submitted. |  | Verify that pump only operates on flow and is set at 104 F maximum. |  |  | Energy Conservation Construction Code, Sections R403.5.2 and C404.7. | Minor | Recirculation controls do not meet requirements of NYS Energy Code. Update recirculation control settings or update savings calculations.
Domestic Hot Water Package | DHW Controls | For partial electrification: heat pump system must operate weekends and evenings at a minimum. |  | Verify that the heat pump water heaters operate at night and on weekends at a minimum. |  |  | Attachment A - Domestic Hot Water - Required Measure Installation | Minor | Heat pump system is not currently providing DHW on weekends and evenings. Adjust controls and submit documentation to show when heat pump is providing DHW.
Domestic Hot Water Package | DHW Water Heater | Cutsheets submitted. |  | Verify that cutsheets have been provided. |  |  | Project Workscope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Domestic Hot Water Package | DHW Water Heater | Replacement domestic hot water heating plant(s) shall meet program efficiency requirements. Documentation provided. |  | Verify that hot water heater meets program efficiency requirements. If no high-efficiency requirements (e.g. ENERGY STAR) are applicable for the particular application, verify that the rated efficiency is no less than required by the energy code. Minor failure if efficiency is 90%-99% of efficiency in workscope. |  |  | Attachment A - Domestic Hot Water - Required Measure Installation | Minor | Hot water heater efficiency is inadequate.
Domestic Hot Water Package | DHW Water Heater | Replacement domestic hot water heating plant(s) shall meet program efficiency requirements. Documentation provided. |  | Verify that hot water heater meets program efficiency requirements. If no high-efficiency requirements (e.g. ENERGY STAR) are applicable for the particular application, verify that the rated efficiency is no less than required by the energy code. Major failure if efficiency is < 90% of efficiency in workscope. |  |  | Attachment A - Domestic Hot Water - Required Measure Installation | Major | Hot water heater efficiency is inadequate.
Domestic Hot Water Package | DHW Water Heater | Installed capacity meets program requirements. Documentation provided. |  | Verify that the installed capacity meets program minimum requirements (in units of 1000 Btu/hr/bedroom, or in units of 1000 Btu/hr/unit, as applicable). |  |  | Attachment A - Domestic Hot Water - Required Measure Installation | Minor | Installed hot water heating capacity does not meet minimum program requirements.
Domestic Hot Water Package | General | Integrated/hybrid tank type DHW heaters are not permitted. |  | Verify that the DHW heat pump is not an integrated/hybrid tank type. |  |  | Attachment A | Major | Installed DHW heater is not permitted per program requirements. Install an allowable type of DHW heat pump and submit documentation to verify.
Domestic Hot Water Package | General | Partial Electrification only: second heat source does not prevent future full load electrification. |  | Verify that the supplemental heat source does not prevent full load electrification in the future. |  |  | Attachment A | Minor | Installed supplemental heat source prevents full load electrification in the future. Rectify and submit documentation to verify.
Domestic Hot Water Package | General | Water-to-water heat pumps only: heat source is not a fluid that was previously heated by fossil fuels, unless when used for waste heat recovery (e.g. from service hot water or heat-recovery chillers). |  | Verify that the heat source for water-to-water heat pumps was not previously heated by fossil fuels. |  |  | Attachment A | Minor | Heat source is a fluid previously heated by fossil fuels. Install alternative heat source and submit documentation to verify.
Domestic Hot Water Package | General | Heat pump installation must comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | Verify that system and system components were installed in accordance with manufacturer requirements and relevant permit/code requirements. |  |  | Manufacturer's instructions. | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Domestic Hot Water Package | DHW Water Heater | Condensate lines terminate in either a domestic drain or external location. |  | Observe condensate line where accessible for leaks. Confirm condensate lines terminate in either a domestic drain or external location. External locations must not terminate onto another heat pump unit or onto a walking surface that could cause slips if condensate freezes. |  |  | Clean Heat checklist | Major | Condensate lines are improperly installed because _______. Fix installation and submit photos showing new termination of condensate lines.
Domestic Hot Water Package | DHW Water Heater | Temperature and pressure relief valves are installed and the relief valve terminates within 6" of the floor. |  | Verify temperature and pressure relief valves are installed and that the relief valve terminates within 6" of the floor. Verify thermostatic mixing valve (for anti scalding) is installed and set to no higher than 125°F. If using a municipal water supply, verify that the cold-water pressure regulating valve is installed. |  |  | Clean Heat checklist | Minor | _____ valve is incorrectly installed. Fix installation and submit photos showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | Safe access to the equipment is provided. |  | Verify that safe access to the site and associated equipment has been provided |  |  | Clean Heat checklist | Critical | Safe access has not been provided to the equipment. Provide access and submit photos.
Domestic Hot Water Package | DHW Water Heater | Pipe insulation is installed. Photo documentation submitted. |  | All hot water piping in mechanical room and accessible piping in unconditioned spaces shall be insulated to the energy conservation code. Minor defect if 50-99% of the pipe insulation was installed. |  |  | Energy Conservation Construction Code, Sections R403.4 and C403.11.3. | Minor | Not all hot water piping is insulated in required areas. Install the required pipe insulation and submit documentation showing completion.
Domestic Hot Water Package | DHW Water Heater | Pipe insulation is installed. Photo documentation submitted. |  | All hot water piping in mechanical room and accessible piping in unconditioned spaces shall be insulated to the energy conservation code. Major defect if <50% was installed. |  |  | Energy Conservation Construction Code, Sections R403.4 and C403.11.3. | Major | Not all hot water piping is insulated in required areas. Install the required pipe insulation and submit documentation showing completion.
Domestic Hot Water Package | DHW Water Heater | Equipment and pipe supports are properly secured. |  | Verify all exposed equipment and pipe supports appear to be properly secured |  |  | Clean Heat checklist | Major | _______ is not properly secured. Secure and submit photos showing the corrected installation.
Domestic Hot Water Package | DHW Water Heater | System does not leak. |  | Verify water heater connections and system are leak free |  |  | Clean Heat checklist | Major | A leak was found in the following location(s): _________. Fix the leak and submit photos showing the corrected installation.
Domestic Hot Water Package | DHW Water Heater | For ducted indoor units, the air outlet exhausts outside and the duct is appropriately sized. |  | For ducted indoor units, verify air outlet of ducted HPWH exhausts to the outdoors, and that duct size is appropriate |  |  | Clean Heat checklist | Major | Air outlet exhausts into the building. Reinstall to exhaust the air outdoors and submit photos showing the corrected installation. [OR} Duct is too [small/large]. Install appropriately-sized duct and submit photos showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | For ducted indoor units, a booster fan is installed if required in the design documents. |  | For ducted indoor units, verify booster fan installed on outlet duct if required |  |  | Clean Heat checklist | Major | Booster fan is not installed on outlet duct as required. Install fan and submit photos showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | The electrical disconnect is accessible and installed. |  | Verify that electrical disconnect is installed in an accessible location for service. If located outside of view from the unit, the disconnect is lockable. |  |  | Clean Heat checklist | Major | The electrical disconnect is not accessible [OR not installed]. Make it accessible [OR install it] and submit photos showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | For split units, heat trace is installed on water lines to outdoor unit if specified in design documents. |  | For split / outdoor units, verify heat trace has been installed on water lines to the outdoor unit if applicable |  |  | Clean Heat checklist | Major | Heat trace has not been installed on the water lines to the outdoor unit. Install heat trace and submit photos showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | No refrigerant leaks found. |  | For split units, sample for refrigerant leaks at exposed field connections |  |  | Clean Heat checklist | Critical | Heat pump system is leaking refrigerant. Identify leak locations, remove refrigerant, re-cut piping and re-make connections, follow pressure testing and vacuum protocol, recharge, and check again for leaks. Submit phots of test, gauges during test, and final leak test. Mark final refrigerant charge on outdoor unit in indelible marker.
Domestic Hot Water Package | DHW Water Heater | Units installed under a roof line/edge must have a rain/snow/ice shield. Photo documentation submitted. |  | Observe that the outdoor unit is away from or protected from increased sources of water/ice/snow from above (i.e. more than normal precipitation, e.g. beneath drip edge, beneath snow-slide, beneath another heat pump, etc.). The presence of gutters does not provide sufficient protection. |  |  | Manufacturer's instructions. | Major | The units are under roof line/edge without shield. Provide shield or drain cap, and document with photos.
Domestic Hot Water Package | DHW Water Heater | Outdoor units must be installed above the local snow line. |  | Verify that outdoor units are installed above the local snow line. |  |  | Manufacturer's instructions. | Major | The outdoor unit is not installed above snow depth. Fix and submit photo documentation showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | Outdoor unit is installed level. |  | Verify outdoor unit is installed level. |  |  | Manufacturer's instructions. | Major | Outdoor unit is not level. Fix and submit photo documentation showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | Vibration dampers are installed if the unit is connected to the building |  | If unit is connected to the building's framing (e.g. wall mounted, or on a connected deck), vibration dampeners are installed. |  |  | Clean Heat checklist | Minor | Vibration dampers are not installed. Re-install unit with vibration dampers and submit photo documentation showing corrected installation.
Domestic Hot Water Package | DHW Water Heater | Refrigerant line penetrations through the envelope must be sealed to prevent infiltration and rodents/insects or water penetration. Photo documentation submitted. |  | Verify that split system heat pump water heater refrigerant pipe penetrations are well-sealed both on the outside and inside of the penetration, including between pipes. |  |  | Attachment A - Domestic Hot Water - Minimum Installation Standards | Minor | Split system piping penetrations are not adequately sealed on both the indoor and outdoor side of the penetration. Return to complete sealing and provide photographs to document.
Domestic Hot Water Package | DHW Water Heater | Seal penetrations no longer needed for fossil fuel equipment. Photo documentation submitted. |  | Seal outdoor air intake, breaching connection to chimney at bottom, and top of chimney if chimney is abandoned. |  |  | Energy Conservation Construction Code, Sections R402.4 and C402.5.1. | Minor | Abandoned building penetrations no longer needed for fossil fuel equipment have not been sealed. Return to complete sealing and provide photographs to document.
Domestic Hot Water Package | DHW Water Heater | The owner was provided a copy of the Operational and Maintenance Handbook, including start-up and any test reports and preventive maintenance. |  | The owner was given a copy of the manufacturer Operation and Maintenance manual and provided with contact information for emergency service needs. |  |  | Energy Conservation Construction Code, Sections R303.3 and C408.1.1. | Incidental | Documentation has not been provided to the owner. This is important for the long term maintenance of the system. Provide documentation.
Domestic Hot Water Package | DHW Water Heater | Required regular maintenance actions are clearly stated and incorporated on a readily accessible label. |  | The label shall include the title or publication number for the operation and maintenance manual for that particular model and type of product. |  |  | Energy Conservation Construction Code, Sections R303.3 and C408.1.1. | Incidental | Preventive maintenance label is missing or references the incorrect manual. Supply the maintenance label and provide photo documentation of where it is located in the building.
Note on B48: Total Cost should align with submitted invoices.
Note on B50: Group equipment as appropriate, e.g. storage tanks, etc.

## Appliances Pre-const (hidden)
Induction Stove Pre-Construction Information
Instructions
Complete the blue cells as applicable.
Stove/Range Existing Conditions
| Qty. | Number of Burners | Manufacturer | Year Manufactured | Confirm if Induction | Fuel Source | Additional Notes
Stove/Range 1
Stove/Range 2
Stove/Range 3
Stove/Range Proposed Upgrade
| Qty. | Number of Burners | Manufacturer | Model | Confirm if Induction | Additional Notes
Stove/Range 1
Stove/Range 2
Stove/Range 3
Dryer Existing Conditions
| Qty. | Frequency of Use (Loads/wk.) | Manufacturer | Year Manufactured | Confirm if ENERGY STAR | Fuel Source | Additional Notes
Dryer 1
Dryer 2
Dryer 3
Heat Pump Dryer Proposed Upgrade
| Qty. | Estimated Annual Energy Use (kWh/yr) | Manufacturer | Model | Confirm if ENERGY STAR | Additional Notes
Dryer 1
Dryer 2
Dryer 3
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on C32: Include all costs such as labor and material.

## Appliances Const (hidden)
Induction Stove Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Induction Stove
Building Address | Location | Number of Burners | Manufacturer | Model # | Confirm if Induction | Additional Notes
(Apt #, Room, Floor, Space)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Heat Pump Dryer
Building Address | Location | Estimated Annual Energy Use (kWh/yr) | Confirm if ENERGY STAR | Manufacturer | Model # | Additional Notes
(Apt #, Room, Floor, Space)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Appliances
Category | Measure | Task |  | Description |  |  | Reference | Non-Conformance Category | Failure Description | Pass/Fail | Comment
Appliance Electrification | Induction Stoves | Induction stoves were installed in all inspected apartments. Installation log submitted. |  | Verify that all induction stoves were installed per workscope. Major failure if fewer than 80% of the stoves were installed. |  |  | Project workscope | Major | The number of installed stoves is not correct. Complete the installation and submit documentation showing completion.
Appliance Electrification | Induction Stoves | Induction stoves were installed in all inspected apartments. Installation log submitted. |  | Verify that all induction stoves were installed per workscope. Minor defect if 80-99% of the stoves were installed. |  |  | Project workscope | Minor | The number of installed stoves is not correct. Complete the installation and submit documentation showing completion.
Appliance Electrification | Induction Stoves | New stoves must be comparably sized to old stoves. |  | Verify that new stoves have the same number of burners as the old stoves. |  |  | Attachment A - Appliance Electrification | Incidental | The new stoves are smaller than the old stoves. Re-install appropriately-sized stoves and submit documentation to verify.
Appliance Electrification | Induction Stoves | New stoves must be installed in compliance with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | Induction stoves must be installed in accordance with manufacturer requirements and relevant permit/code requirements. |  |  | Attachment A - Appliance Electrification | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Appliance Electrification | Induction Stoves | Gas pipe to the stove removed or disconnected and capped. |  | Verify that gas pipe is secure and out of the way (no remaining flex pipe), gas valve is shut off, and gas pipe has been securely capped. |  |  | Project Workscope | Major | Abandoned gas pipe has not been left in a safe condition. Complete the work.
Appliance Electrification | Induction Stoves | Cutsheets must be submitted for installed stoves. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A - Appliance Electrification | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Appliance Electrification | Heat Pump Dryers | Heat pump dryers were installed per workscope |  | Verify that heat pump dryers were installed per workscope. Major failure if fewer than 80% of the proposed dryers were installed. |  |  | Project workscope | Major | The number of installed dryers is not correct. Complete the installation and submit documentation showing completion.
Appliance Electrification | Heat Pump Dryers | Heat pump dryers were installed per workscope |  | Verify that heat pump dryers were installed per workscope. Minor failure if 80-99% of the proposed dryers were installed. |  |  | Project workscope | Minor | The number of installed dryers is not correct. Complete the installation and submit documentation showing completion.
Appliance Electrification | Heat Pump Dryers | Heat pump dryers must be comparably sized to old dryers. |  | Verify that new dryers have a minimum of 90% of the capacity of the older dryers. |  |  | Attachment A - Appliance Electrification | Incidental | The new dryers are smaller than the old dryers. Re-install appropriately-sized dryers and submit documentation to verify.
Appliance Electrification | Heat Pump Dryers | Heat pump dryers must be EnergyStar labeled. |  | Verify that new dryers are EnergyStar labeled. |  |  | Attachment A - Appliance Electrification | Minor | The new dryers are not EnergyStar labeled. Re-install labeled dryers and submit documentation to verify.
Appliance Electrification | Heat Pump Dryers | New dryers must be installed in compliance with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | Dryers must be installed in accordance with manufacturer requirements and relevant permit/code requirements. |  |  | Attachment A - Appliance Electrification | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Appliance Electrification | Heat Pump Dryers | Gas pipe to the dryer removed or disconnected and capped. Photo documentation submitted. |  | Verify that gas pipe is secure and out of the way (no remaining flex pipe), gas valve is shut off, and gas pipe has been securely capped. Submit photos of a sample of installations. |  |  | Project Workscope | Minor | Abandoned gas pipe has not been left in a safe condition. Complete the work.
Appliance Electrification | Heat Pump Dryers | Cutsheets must be submitted for installed dryers. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A - Appliance Electrification | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Note on B43: Total Cost should align with submitted invoices.

## Add-On Air Sealing Pre-const
Air Sealing Pre-Construction Information
Instructions
Evaluate all air sealing opportunities listed in the table below. Complete the blue cells as applicable. To be eligible for the full add-on incentive, the project must install all possible air sealing measures in all buildings. An air sealing measure can be deemed "not recommended" only if that component does not exist within the building or if it was previously air sealed.
Air Sealing Workscope Evaluation and Proposed Upgrade
Measure | Evaluation Status | Workscope Description | Qty. | Material | Explanation of why measure is not recommended or not applicable
Tops of shafts/bulkheads
Exterior doors
Air conditioner sleeves
Windows
Floor of attic or ceiling of top floor penetrations (attic door, hatch, electrical, piping, ventilation, etc.)
Plumbing and electrical penetrations in the apartments
Penetrations and openings between all mechanical equipment rooms, including boiler room and the conditioned space
Basement perimeter
Fire sprinkler penetrations
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on B19: Group equipment as appropriate, e.g. doors, plumbing penetrations, etc.
Note on C19: Include all costs such as labor and material.

## Add-On Air Sealing Const
Air Sealing Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Air Sealing
Building Address | Location | Location of Leakage | Type of Sealing Performed | Air Sealing Complete | Quantity (SF, LF, # of units, etc. - list for each line item) | Additional Notes
(Apt #, Room, Floor, Space)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Air Sealing
Category | Measure | Task | Description |  | Reference | Non-Conformance Category | Failure Description | Pass/Fail | Comment
Optional Recommended Measures | Air Sealing | All required air sealing is complete per workscope. | Verify that all required air sealing is complete: Tops of shafts/bulkheads, existing exterior doors, AC sleeves, existing windows, floor of attic or ceiling of top floor penetrations (including but not limited to attic door, hatch, electrical piping, ventilation, duct penetrations, uncapped wall cavities, etc.), plumbing and electrical penetrations in apartments, penetrations and openings between mechanical rooms and the conditioned space, basement perimeter, fire sprinkler penetrations, makeup air opening in mechanical room if fossil fuel equipment is removed, top of chimney if fossil fuel equipment is removed, and any other areas identified in the workscope. Critical failure if no air sealing was done. |  | Attachment A | Critical | Air sealing has not been completed in these areas: ________. Complete the work and submit documentation verifying completion.
Optional Recommended Measures | Air Sealing | All required air sealing is complete per workscope. | Verify that all required air sealing is complete: Tops of shafts/bulkheads, existing exterior doors, AC sleeves, existing windows, floor of attic or ceiling of top floor penetrations (including but not limited to attic door, hatch, electrical piping, ventilation, duct penetrations, uncapped wall cavities, etc.), plumbing and electrical penetrations in apartments, penetrations and openings between mechanical rooms and the conditioned space, basement perimeter, fire sprinkler penetrations, makeup air opening in mechanical room if fossil fuel equipment is removed, top of chimney if fossil fuel equipment is removed, and any other areas identified in the workscope. Major failure if air sealing is less than 80% complete. |  | Attachment A | Major | Air sealing has not been completed in these areas: ________. Complete the work and submit documentation verifying completion.
Optional Recommended Measures | Air Sealing | All required air sealing is complete per workscope. | Verify that all required air sealing is complete: Tops of shafts/bulkheads, existing exterior doors, AC sleeves, existing windows, floor of attic or ceiling of top floor penetrations (including but not limited to attic door, hatch, electrical piping, ventilation, duct penetrations, uncapped wall cavities, etc.), plumbing and electrical penetrations in apartments, penetrations and openings between mechanical rooms and the conditioned space, basement perimeter, fire sprinkler penetrations, makeup air opening in mechanical room if fossil fuel equipment is removed, top of chimney if fossil fuel equipment is removed, and any other areas identified in the workscope. Minor failure if air sealing is 80-99% complete. |  | Attachment A | Minor | Air sealing has not been completed in these areas: ________. Complete the work and submit documentation verifying completion.
Optional Recommended Measures | Air Sealing | Movable surfaces that have been weather-stripped move freely (windows, doors, hatches, etc.). | Verify that weather stripping does not restrict movement of windows, doors, hatches, etc. |  | Attachment A | Minor | Movable surfaces do not move freely. Adjust air sealing such as weatherstripping to allow free movement. Document with video.
Optional Recommended Measures | Air Sealing | Attic insulation must be removed to complete air sealing scope. Submit photo documentation. | Verify that attic insulation was removed so that attic floor could be thoroughly air sealed. Once air sealing has been completed, insulation shall be replaced to provide continuous coverage of an even depth throughout the attic. |  | Attachment A | Minor | Attic insulation was not moved to facilitate air sealing. Move insulation, air seal, and replace insulation to provide continuous coverage of an even depth throughout the attic. Submit photo documentation to verify. OR Attic insulation does not provide continuous coverage [or an even depth] throughout the attic. Install sufficient insulation to ensure continuous coverage [or an even depth]. Submit photo documentation to verify.
Optional Recommended Measures | Air Sealing | Weatherstripping is mechanically fastened. | Verify that weatherstripping is mechanically fastened, foam-filled tubular gasket vinyl. Self-adhesive weatherstripping is not acceptable. |  | Attachment A | Minor | Weatherstripping is not mechanically fastened, foam-filled tubular gasket vinyl. Fasten weatherstripping [or install appropriate type of weatherstripping] and submit photos to verify.
Optional Recommended Measures | Air Sealing | Weatherstripping is installed along all sides and tops of all doors | Verify that weatherstripping was installed along all sides and tops of all doors. |  | Attachment A | Minor | Weatherstripping was not installed on the following doors: __________________. Install weatherstripping, and submit photos to verify.
Optional Recommended Measures | Air Sealing | Cutsheets must be submitted for all materials used in air sealing work. | Verify that submitted cutsheets match what was observed on site. |  | Attachment A | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Optional Recommended Measures | Air Sealing | System and system components must comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. | Verify that system and system components were installed in accordance with manufacturer requirements and relevant permit/code requirements. |  | Manufacturer's instructions. | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Optional Recommended Measures | Air Sealing | Large openings shall be sealed with an appropriate air sealing strategy (not spray foam). | Verify that large openings that cannot be sealed with spray foam were sealed with another appropriate air sealing strategy such as rigid foamboard or caulk. |  | Attachment A | Minor | Large openings that cannot be sealed with spray foam are not sealed with another appropriate air sealing strategy such as rigid foamboard or caulk. Seal this opening and submit photos to verify.
Note on B24: Total Cost should align with submitted invoices.
Note on B26: Group equipment as appropriate, e.g. doors, plumbing penetrations, etc.

## ARCHIVED Add-On Steam Pre-const (hidden)
Steam Heating Pre-Construction Information
Instructions
Evaluate all air sealing opportunities listed in the table below. Complete the blue cells as applicable. To be eligible for the full add-on incentive, the project must install all possible components of the package in all buildings. A steam system measure can be deemed "not recommended" only if that component does not exist within the building or if it was previously installed (e.g. the building no longer has steam traps).
Steam Heating System Workscope Evaluation and Proposed Upgrade
Measure | Evaluation Status | Workscope Description | Qty. | Material | Explanation of why measure is not recommended or not applicable
Energy Management System
Radiant Heat Barriers
Thermostatic radiator valves or other thermostatic controls on every radiator or fan coil unit
Inlet orifice plate on all radiators
Master venting on all mains and risers
Functional steam traps (for those remaining in service) including all traps in the basement and boiler room
Burner clean and tune
Proposed Installed Cost Information
Equipment Type | Total Measure Cost
Note on B17: Group equipment as appropriate, e.g. tanks, etc.
Note on C17: Include all costs such as labor and material.

## ARCHIVED Add-On Steam Const (hidden)
Steam Heating Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Energy Management System
Building Address | Location | In-Unit |  | Central Control |  |  |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Location of Sensor | Measured Temperature | Manufacturer | Model | Settings
[6 empty] | Day (temp) | Night (temp) | Night (hours)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Radiant Heat Barrier
Building Address | Location | Radiant Heat Barrier Installed? |  |  | Radiant Heat Barrier Manufacturer and Model # |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Thermostatic Radiator Valves
Building Address | Location | TRVs Installed? |  |  | TRV Manufacturer and Model # |  |  | TRV Setpoint |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Orifice Plates
Building Address | Location | Orifice Plates Installed? |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Optional Recommended Measures
Measure | Task |  |  | Task Description |  |  | Refrence | Non-Conformance Category | Pass/Fail | Comment
Steam components | Components installed; Photo documentation submitted |  |  | Verify that steam components have been installed: Energy Management System, radiant heat barriers, thermostatic radiator valves (TRVs), inlet orifice plates, master venting, steam traps; Submit photos |  |  | Attachment A - Optional Measures: Steam Upgrades - Required Measure Installation | Major
Air vents | Air vent orientation and location; Photo documentation submitted |  |  | Air vents must be installed in the vertical direction and at least 15" away from any elbows |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards | Minor
| Air vents on mains and risers; Photo documentation submitted |  |  | Air vents must be installed on 100% of mains and risers |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards | Major
Note on B72: Total Cost should align with submitted invoices.
Note on B74: Group equipment as appropriate, e.g. orifice plates, steam traps, etc.

## Add-On Vent Pre-const
Ventilation Pre-Construction Information
Instructions
Complete the blue cells as applicable. To be eligible for the full add-on incentive, the project must install all possible ventilation measures in all buildings. A ventilation measure can be deemed "not recommended" only if that component does not exist within the building or if it was previously installed and aligns with program requirements.
Ventilation Existing Conditions
Ventilation | Equipment Type |  | System Type | Qty. | Location of Equipment |  | Total CFM | Method for Total CFM Calculation | Annual Hours | Conditioned Supply? | % Outdoor Air | Duct Leakiness | System Operational? | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
[other]
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/Commercial Kitchen
Garage
Laundry
[other]
Ventilation Proposed Upgrades
Ventilation | Equipment Type |  | System Type | Manufacturer | Model | Qty. | Location of Equipment |  | Total Fan Power | Sensible Heat Recovery Efficiency | CFM /Register | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
[other]
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/Commercial Kitchen
Garage
Laundry
[other]
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on C7: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on P7: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B12: For other areas as needed, overwrite the header with an appropriate description.
Note on B21: For other areas as needed, overwrite the header with an appropriate description.
Note on C24: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on K24: At design external static pressure and design CFM
Note on L24: At manufacturer rated design conditions
Note on N24: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B29: For other areas as needed, overwrite the header with an appropriate description.
Note on B38: For other areas as needed, overwrite the header with an appropriate description.
Note on B41: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.
Note on C41: Include all costs such as labor and material.

## Add-On Vent Const
Ventilation Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Ventilation Equipment
Building Address | Location | Equipment Type | Manufacturer | Model # | Spaces Served | Pre-retrofit Flow Rate (CFM) | Post-retrofit Flow Rate (CFM) | Rated Heat Exchange Efficiency | Supply |  |  |  | Exhaust |  | Filter MERV Rating | Calculated Efficiency | Additional Notes
| (Apt #, Room, Floor, Space) | [7 empty] | Outside Air Temp | Temp After Heat Exchange | Design/ Rated Air Flow (CFM) | Intake location complies with Program Req's? | Inside Air Temp | Leaving Air Temp
[10 empty] | Temp After Heat Exchange | Design/Rated Air Flow (CFM) |  | Inside Air Temp | Leaving Air Temp
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Ventilation Distribution
Building Address | Location | Ductwork |  | Insulation |  |  | Sealing |  |  |  | Automatic Damper? | Additional Notes
| (Apt #, Room, Floor, Space) | System Designation | Linear Feet (insulated/ replaced) | Material Type | Thickness (inches) | R-Value | Sealant Used | Pre Duct Leakage (CFM25) | Post Duct Leakage (CFM25) | Exterior Penetrations Sealed?
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Category | Measure | Task |  | Description |  |  | Reference | Non-Conformance Category | Failure Description |  | Pass/Fail | Comment
Ventilation Package | ERV or HRV | Supply and exhaust ventilation CFM are within 10%. |  | Verify that overall balancing of supply and exhaust is within 10%. |  |  | Attachment A | Major | Ventilation system is not balanced. Rebalance and submit balanced ventilation test results.
Ventilation Package | ERV or HRV | ERV/HRV sensible efficiency is 77% minimum. |  | Verify that ERV/HRV sensible efficiency is 77% minimum. |  |  | Attachment A | Major | ERV/HRV sensible efficiency does not meet 77% minimum. Rebalance to deliver 77% efficiency.
Ventilation Package | ERV or HRV | Fan power must be less than 1 watt/CFM for all ERVs/HRVs installed. |  | Verify that ERV/HRV less than 1 Watt per CFM. |  |  | Attachment A | Minor | ERV/HRV fan power exceeds 1 watt per CFM. Replace fan motor or modify to meet efficiency requirement.
Ventilation Package | ERV or HRV | Cutsheets must be submitted for ERV or HRV. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Ventilation | Central Exhaust | Ductwork must be cleaned. |  | Verify that ductwork was cleaned. |  |  | Attachment A - Envelope | Incidental | Ductwork was not cleaned. Clean ductwork and submit photos before and after to demonstration cleaning.
Envelope - Ventilation | Central Exhaust | Ductwork must be sealed to program requirements. |  | Verify that all central ventilation duct work was sealed (e.g. with an aerosolized sealant product) to meet duct leakage limit of 5 CFM50 per register + 5 CFM50/floor leakage OR a maximum leakage of 10% of total design air flow for system, whichever is lower. Major failure if no evidence of sealing or sealing is highly inadequate. |  |  | Attachment A - Envelope | Major | Ductwork was not sealed or sealing did not meet program requirements. Seal ductwork and submit photos test-out results.
Envelope - Ventilation | Central Exhaust | Ductwork must be sealed to program requirements. |  | Verify that all central ventilation duct work was sealed (e.g. with an aerosolized sealant product) to meet duct leakage limit of 5 CFM50 per register + 5 CFM50/floor leakage OR a maximum leakage of 10% of total design air flow for system, whichever is lower. Minor failure if sealing was performed but some minor holes/gaps remain. |  |  | Attachment A - Envelope | Minor | Ductwork was not sealed or sealing did not meet program requirements. Seal ductwork and submit photos test-out results.
Envelope - Ventilation | Cutsheets | Cutsheets must be submitted for duct sealant. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Ventilation | Central Exhaust | System must exhaust airflow per program requirements for central exhaust systems. Testing and balancing results have been submitted. |  | 25 cubic feet per minute (CFM) continuous for each kitchen, 20 CFM continuous for each bathroom. Major failure if ventilation flow rate is <80% or >150% of target. |  |  | Attachment A - Envelope | Major | Central exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Central Exhaust | System must exhaust airflow per program requirements for central exhaust systems. Testing and balancing results have been submitted. |  | 25 cubic feet per minute (CFM) continuous for each kitchen, 20 CFM continuous for each bathroom. Minor failure if ventilation flow rate is 80-150% of target. |  |  | Attachment A - Envelope | Minor | Central exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Unitized Exhaust | System must exhaust airflow per program requirements for unitized exhaust systems. Testing and balancing results have been submitted. |  | 25 CFM continuous or 100 CFM intermittent for each kitchen; 20 CFM continuous or 50 CFM intermittent for each bathroom. Major failure if ventilation flow rate is <80% or >150% of target. |  |  | Attachment A - Envelope | Major | Unitized exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Unitized Exhaust | System must exhaust airflow per program requirements for unitized exhaust systems. Testing and balancing results have been submitted. |  | 25 CFM continuous or 100 CFM intermittent for each kitchen; 20 CFM continuous or 50 CFM intermittent for each bathroom. Minor failure of ventilation flow rate is 80-150% of target. |  |  | Attachment A - Envelope | Minor | Unitized exhaust airflow does not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Envelope - Ventilation | Cutsheets | Cutsheets must be submitted for exhaust fans. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A - Envelope | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Ventilation | Central or Unitized Exhaust | A third-party testing and balancing (TAB) contractor must balance and verify flow rates. |  | Testing and Balancing (TAB) contractor must be independent, hired by owner, not by energy contractor. |  |  | Attachment A - Envelope | Incidental | TAB contractor is not independent. Submit contract showing that TAB contractor is hired by owner.
Envelope - Ventilation | Central or Unitized Exhaust | The flow rates must be verified by the TAB contractor. |  | Verify that a TAB report has been submitted. |  |  | Attachment A - Envelope | Minor | No TAB report submitted. Submit report.
Envelope - Ventilation | Central or Unitized Exhaust | Flow measuring equipment must capable of measuring within a +/1 CFM tolerance at flow rates as low as 20 CFM. |  | Equipment meets program accuracy requirements. |  |  | Attachment A - Envelope | Incidental | Ventilation testing equipment does not meet program requirements. Re-submit ventilation testing equipment that meets program requirements. If testing was performed with equipment that does not meet program requirements, re-do all tests and re-submit the final report.
Envelope - Ventilation | Central or Unitized Exhaust | Flow measuring equipment must capable of measuring within a +/1 CFM tolerance at flow rates as low as 20 CFM. |  | Testing was performed with equipment that does not meet program requirements |  |  | Attachment A - Envelope | Major | Ventilation testing equipment does not meet program requirements. Re-do all tests using test equipment that meets program requirements, and re-submit the final report.
Envelope - Ventilation | Unitized Exhaust | If project installed new unitized exhaust fans, submit duct sizing information in lieu of testing flows. |  | Duct sizes information must be submitted if the actual airflow is not tested in a sample of apartments. |  |  | Energy Star Multifamily New Construction - https://www.energystar.gov/sites/default/files/asset/document/Kitchen%20Exhaust%20Reference%20Guide%20ENERGY%20STAR%20Single-Family%20New%20Homes_Rev12.pdf | Incidental | Duct sizing information was not submitted. Submit all information required by Energy Star.
Envelope - Ventilation | Unitized Exhaust | Duct sizing meets Energy Star Multifamily New Construction requirements. |  | Duct sizes must comply with the prescriptive path of Energy Star Multifamily New Construction requirements. |  |  | Energy Star Multifamily New Construction - https://www.energystar.gov/sites/default/files/asset/document/Kitchen%20Exhaust%20Reference%20Guide%20ENERGY%20STAR%20Single-Family%20New%20Homes_Rev12.pdf | Minor | Duct sizing does not comply with Energy Star Multifamily New Construction requirements. Submit test results showing that airflow is adequate or re-install ducts that meet the sizing requirements.
Envelope - Ventilation | Exhaust penetrations | New exhaust penetrations must be air sealed at envelope. Photo documentation has been submitted. |  | New exhaust penetrations must be air sealed. |  |  | Attachment A - Envelope | Minor | Exhaust penetrations are not air sealed. Seal and provide photo documentation.
Envelope - Ventilation | Exhaust | Ventilation exhaust must vent to outside. Photo documentation has been submitted. |  | Exhaust must vent to outside. |  |  | Attachment A - Envelope | Major | Exhaust does not vent to the outside. Vent to the outside and provide photo documentation.
Envelope - Ventilation | Owner training and documentation | Owner's representative and onsite staff must trained in the use of the new ventilation system, and an owner's manual must be provided. |  | Training and documentation must be provided to site staff on how to use and maintain the new ventilation equipment. |  |  | Attachment A - Envelope | Minor | Site staff was not trained in the use of the new ventilation equipment. Provide training. OR An owner's manual detailing the new ventilation equipment was not provided to site staff. Provide owner's manual.
Ventilation Package | Energy Recovery Ventilator (ERV) or Heat Recovery Ventilator (HRV) | CAR dampers are installed on all exhaust registers. |  | Verify Constant Airflow Regulator (CAR) dampers were installed to allow automatic balancing of individual airflows. Major failure if <80% of CAR dampers were installed. |  |  | Attachment A | Major | Not all CAR dampers were installed. Install per scope of work and submit documentation to verify.
Ventilation Package | Energy Recovery Ventilator (ERV) or Heat Recovery Ventilator (HRV) | CAR dampers are installed on all exhaust registers. |  | Verify Constant Airflow Regulator (CAR) dampers were installed to allow automatic balancing of individual airflows. Minor failure if 80-99% of CAR dampers were installed. |  |  | Attachment A | Minor | Not all CAR dampers were installed. Install per scope of work and submit documentation to verify.
Ventilation Package | Constant airflow regulator (CAR) dampers | Airflow on CARs must be set per workscope. |  | Verify airflow settings match workscope, either from balancing report or by examining CARs. |  |  | Attachment A | Minor | Airflow has not been set correctly. Correct settings and provide documentation verifying new settings.
Ventilation Package | CAR dampers | Cutsheets must be submitted for CAR dampers. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Envelope - Ventilation | Cutsheets | System and system components must comply with manufacturer's requirements and codes. Requirements and codes have been reviewed. |  | Verify that system and system components were installed in accordance with manufacturer requirements and relevant permit/code requirements. |  |  | Manufacturer's instructions. | Minor | The following manufacturer's instructions or permit/code requirements were not followed: ________________________________________. Address and submit documentation to verify compliance.
Ventilation Package | Airflows | System must deliver airflow per program requirements. Test results submitted. |  | Verify that delivered airflow meets program and design requirements. Program requires: Typical 24/7 operation total supply and exhaust flows must be within +15% of required airflow at each terminal, +/- 15% of total required design flows at the system level, and within 10% of each other on a per dwelling unit basis. |  |  | Attachment A | Major | Ventilation airflows do not meet program requirements. Adjust system to deliver required airflow and submit testing and balancing results.
Ventilation Package | Health and Safety | Intake air must be clear of possible contaminant sources. |  | Verify that the intake air is clear of possible contaminant sources: Exterior outdoor air intake louver must be at least 4 feet above grade or roof deck, at least 10 feet away from known contamination sources (dryer, garage exhaust, etc.), and no closer to the exhaust port than recommended by the manufacturer. |  |  | Attachment A | Minor | Intake air does not meet minimum clearance requirements from contaminant sources. Move intake.
Ventilation Package | Duct insulation | Duct insulation must meet program requirements |  | Verify that duct insulation meets program requirements: a) Ducts between an interior HRV or ERV and the exterior must be insulated to a minimum of R-8 and covered with an airtight vapor tight material that is carefully sealed to the exterior wall. b) Ducts between an exterior mounted HRV or ERV and the building envelope must be insulated to a minimum of R-8. |  |  | Attachment A | Minor | Duct insulation does not meet program requirements. Add insulation.
Ventilation Package | Central Ductwork | Cutsheets must be submitted for materials used to insulate ducts. |  | Verify that submitted cutsheets match what was observed on site. |  |  | Attachment A | Incidental | Cutsheets for _________ was not submitted. Submit cutsheet. [OR] Cutsheets for _________ was submitted, however ________does not match what was observed on site. Please submit a cutsheet that reflects _________ which was observed on site.
Ventilation Package | Frost protection | Frost protection must be installed in Energy Recovery Ventilator (ERV) or Heat Recovery Ventilator (HRV). |  | Verify that the h eat exchanger core is protected from frost |  |  | Attachment A | Minor | Heat exchanger core is not protected from frost. Add frost protection.
Ventilation Package | Filter | MERV 8 filter or better must be installed. Photo documentation submitted. |  | ERV/HRV must be protected by minimum MERV 8 filter on both intake and exhaust airstreams (MERV 13 recommended but not required) |  |  | Attachment A | Minor | ERV/HRV is not protected by minimum MERV 8 filter on both intake and exhaust airstreams. Add MERV 8 filter(s), provide photo documentation.
Ventilation Package | Heater | Electric heater temperature rise must be 5 F or less (supply air temperature 62 F or higher recommended but not required). |  | Verify electric heater temperature rise is 5F or less. |  |  | Attachment A | Minor | Electric heater temperature rise exceeds 5 F. Resize electric heater.
Ventilation Package | Heater | Electric heater temperature rise must be 5 F or less (supply air temperature 62 F or higher recommended but not required). |  | Verify electric heater temperature rise is 5F or less. |  |  | Attachment A | Minor | Electric heater temperature rise exceeds 5 F. Resize electric heater.
Note on D7: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on N8: Exterior outdoor air intake louver must be at least 4 feet above grade or roof deck, at least 10 feet away from known contamination sources (dryer, garage exhaust, etc.), and no closer to the exhaust port than recommended by the manufacturer.
Note on M37: If the system does not operate 24/7, is there an automatic damper that shuts outdoor air intake when the unit is off? e.g. hallways, laundry rooms, common areas.
Note on D38: e.g. supply, exhaust, ERV, etc
Note on B66: Total Cost should align with submitted invoices.
Note on B68: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.

## Pre-const QC Feedback
Pre-construction QC Review Feedback Form
Reviewer Name:
Review Date:
Approval Status:
Program Approval Notes:
General Comments | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Has all required documentation been submitted (including owner and resident DRAFs and/or copies of billing and/or delivery records)?
General Portfolio Info Tab: Is the tab complete and, if applicable, aligned with the FlexTech study?
General Project Info Tab: Is the tab complete for all building types?
General Project Info Tab: Will program staff be able to set a utility baseline with this information?
Required Measures (e.g. Envelope, Heating & Cooling, Domestic Hot Water, or Appliances tabs) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Is there a tab completed for each building type?
Are existing conditions thoroughly described?
Are proposed measure descriptions thoroughly described?
Bonus Measures, if applicable (e.g. Air Sealing and Ventilation) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Is there a tab completed for each building type?
Are existing conditions thoroughly described?
Are proposed measure descriptions thoroughly described?

## Const QC Feedback
Partial Installation and Construction Complete QC Review Feedback Form
Inspector Name:
Inspection Type (Desk/Field)
Program Stage (Partial, Complete)
Inspection Date:
Approval Status:
Program Approval Notes:
General Comments | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Has all required documentation been submitted (including owner and resident DRAFs)?
Required Measures (e.g. Envelope, Heating & Cooling, Domestic Hot Water, or Appliances tabs) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Do the installation comply with program requirements?
Bonus Measures, if applicable (e.g. Air Sealing and Ventilation) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Do the installation comply with program requirements?
Standards and Quality Assurance Checklist Specifications Comments | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)

## Data Validation (hidden)
GENERAL PROJECT SPECIFIC INFO TAB
Demographic | ElecUtil | GasUtil | MeterConf | MeterConf Gas | YES/NO | Heating Fuel | Heating Equipment Type | Heating Spaces Served | Heading End Use Equipment Type | Central Distribution Type - Heat | Cooling Fuel Source | Cooling Equipment Type | Cooling Spaces Served | Cooling Controls | Cooling Ownership | DHW | DHW Fuel | DHW Equipment | DHW Spaces Served | DHW Location | Central or in unit
Families | Central Hudson | Central Hudson | Direct Metered | Direct Metered | Yes | Electric | Electric Resistance | Entire Building | Baseboard | 1-pipe steam | Natural Gas | Individual window-mounted AC | Entire Building | Thermostat | Resident Owned | No | Natural Gas | Immersion coil in heating boiler - no storage tank | Whole Building | In-unit | In-unit
Seniors | Con Edison | Con Edison | Submetered | Master Metered | No | Gas | Steam boiler(s) | Common Spaces | Radiator | 2-pipe steam | Oil | Individual wall-mounted AC | Common Spaces | Programmable Thermostat | Building Owned | Yes, year-round | Electricity | Immersion coil in heating boiler - separate storage tank | Apartments Only | Central Mechanical Room | Central Mechanical Room
Single-occupancy | PSEG LI | KEDLI | Master Metered | No Gas |  | Oil | Hydronic boiler(s) - Non-Condensing | Apartments | Fan Coil | Vacuum steam | Dual Fuel | PTAC / PTHP | Apartments | Energy Management System (EMS) | Other (Please describe in Additional Notes) | Yes, heating season only | Oil | Indirect from space heating boiler | Common Area Only | Other (Please describe in Additional Notes) | Other (Please describe in Additional Notes)
Mixed Population | National Grid | KEDNY |  |  |  | Propane | Hydronic boiler(s) - Condensing | Other (Please describe in Additional Notes) | Duct | Hydronic radiation | District Steam | Split system | Other (Please describe in Additional Notes) | Chilled Water Temperature Sensor |  |  | District Steam | Direct-fired storage water heater(s) | Laundry Only
Other (Please describe in Additional Notes) | NYSEG | National Fuel Gas |  |  |  | District Steam | Forced Air Furnace - Non-Condensing |  | Radiant Floor | Electric Baseboard | Electric | Heat Pump - Ground Source |  | NA |  |  | Propane | Dedicated DHW boiler with separate storage tank | Apartments & Laundry
| O&R | National Grid |  |  |  | Dual Fuel | Forced Air Furnace - Condensing |  | PTAC | Fan coil/PTAC | Propane | Heat Pump - Water Loop |  |  |  |  | Other (Please describe in Additional Notes) | Tankless instantaneous | Common Area & Laundry
| RG&E | NYSEG |  |  |  | Other (Please describe in Additional Notes) | Heat Pump - Water Loop |  | Other (Please describe in Additional Notes) | Heat pump – Water loop | Other (Please describe in Additional Notes) | Absorption Chiller – gas fired | [5 empty] | Heat pump water heaters | Other (Please describe in Additional Notes)
| Other | O&R |  |  |  |  | Heat Pump - Air Source |  |  | Mini split / ductless |  | Absorption Chiller – indirect fired | [5 empty] | Other (Please describe in Additional Notes)
|  | RG&E |  |  |  |  | Heat Pump - Ground Source |  |  | Forced Hot Air |  | Electric Chiller
|  | Other |  |  |  |  | District Steam |  |  | Other (Please describe in Additional Notes) |  | Other (Please describe in Additional Notes)
|  | None |  |  |  |  | Other (Please describe in Additional Notes)
ENVELOPE TAB
NYS County | IECC Climate Zone | Garden Style U Target | Non-Garden Style U Target |  | Section: | Windows | Windows | Windows | Windows | Envelope | Windows | Windows | Windows | Exterior Doors | Exterior Doors | Exterior Doors | Air Infiltration
Albany | 5A | 0.06 | 0.1 |  | Subsection:
Allegany | 6A | 0.05 | 0.09 |  | Range Name: | DD_Windows_OperationType | DD_Windows_FramingMaterial | DD_Windows_ThermalBreak | DD_Windows_NumOfPanes | DD_Envelope_VerificationMethod | DD_Windows_GlassCoating | DD_Windows_GasFilled | DD_Windows_WeatherStripping | DD_ExteriorDoors_Material | DD_ExteriorDoors_GlazingType | DD_ExteriorDoors_WeatherStripping | DD_AirInfiltration_Tightness
Bronx | 4A | 0.07 | 0.13 |  | Title: | Operation Type | Framing Material | Thermal Break | # of Panes | Verification Method | Glass Coating | Gas Filled | Weather-stripping | Material | Glazing Type | Weather-stripping | Tightness | Cavity Insulation | General
Broome | 6A | 0.05 | 0.09 |  |  | Awning | Aluminum | Yes | Single | Estimated | Heat Absorbing Tints | Yes | Excellent | Solid Wood | Single Pane | Excellent | Low leakage | Yes | Yes
Cattaraugus | 6A | 0.05 | 0.09 |  |  | Casement | Wood | No | Single w/ Storms | Reported by Site Staff | Reflective Coating | No | Good | Solid Metal | Double Pane | Fair | Some Leakage | No | No
Cayuga | 5A | 0.06 | 0.1 |  |  | Fixed | Fiberglass |  | Double | From Drawings | Low-E Coating |  | Poor | Hollow Wood | Other, (Please describe in Additional Notes) | Poor | Very Leaky | NA | NA
Chautauqua | 5A | 0.06 | 0.1 |  |  | Hopper | Vinyl |  | Triple | Visual Confirmation | None |  | None | Hollow Metal | N/A | None | N/A
Chemung | 5A | 0.06 | 0.1 |  |  | Single Hung | Other, (Please describe in Additional Notes) |  |  | Other, (Please describe in Additional Notes) | Unknown |  |  | Wood, Insulated Core |  | N/A
Chenango | 6A | 0.05 | 0.09 |  |  | Double Hung |  |  |  |  | Other, (Please describe in Additional Notes) |  |  | Metal, Insulated Core
Clinton | 6A | 0.05 | 0.09 |  |  | Single Sliding | [7 empty] | Glass
Columbia | 5A | 0.06 | 0.1 |  |  | Double Sliding | [7 empty] | Glass Slider
Cortland | 5A | 0.06 | 0.1 |  |  | Other, (Please describe in Additional Notes) | [7 empty] | Other, (Please describe in Additional Notes)
Delaware | 6A | 0.05 | 0.09
Dutchess | 5A | 0.06 | 0.1
Erie | 5A | 0.06 | 0.1
Essex | 6A | 0.05 | 0.09
Franklin | 6A | 0.05 | 0.09
Fulton | 6A | 0.05 | 0.09
Genesee | 5A | 0.06 | 0.1
Greene | 5A | 0.06 | 0.1
Hamilton | 6A | 0.05 | 0.09
Herkimer | 6A | 0.05 | 0.09
Jefferson | 6A | 0.05 | 0.09
Kings | 4A | 0.07 | 0.13
Lewis | 6A | 0.05 | 0.09
Livingston | 5A | 0.06 | 0.1
Madison | 6A | 0.05 | 0.09
Monroe | 5A | 0.06 | 0.1
Montgomery | 6A | 0.05 | 0.09
Nassau | 4A | 0.07 | 0.13
New York | 4A | 0.07 | 0.13
Niagara | 5A | 0.06 | 0.1
Oneida | 6A | 0.05 | 0.09
Onondaga | 5A | 0.06 | 0.1
Ontario | 5A | 0.06 | 0.1
Orange | 5A | 0.06 | 0.1
Orleans | 5A | 0.06 | 0.1
Oswego | 5A | 0.06 | 0.1
Otsego | 6A | 0.05 | 0.09
Putnam | 5A | 0.06 | 0.1
Queens | 4A | 0.07 | 0.13
Rensselaer | 5A | 0.06 | 0.1
Richmond | 4A | 0.07 | 0.13
Rockland | 5A | 0.06 | 0.1
Saratoga | 5A | 0.06 | 0.1
Schenectady | 5A | 0.06 | 0.1
Schoharie | 6A | 0.05 | 0.09
Schuyler | 6A | 0.05 | 0.09
Seneca | 5A | 0.06 | 0.1
St. Lawrence | 6A | 0.05 | 0.09
Steuben | 6A | 0.05 | 0.09
Suffolk | 4A | 0.07 | 0.13
Sullivan | 6A | 0.05 | 0.09
Tioga | 5A | 0.06 | 0.1
Tompkins | 6A | 0.05 | 0.09
Ulster | 6A | 0.05 | 0.09
Warren | 6A | 0.05 | 0.09
Washington | 5A | 0.06 | 0.1
Wayne | 5A | 0.06 | 0.1
Westchester | 4A | 0.07 | 0.13
Wyoming | 6A | 0.05 | 0.09
Yates | 5A | 0.06 | 0.1
DHW TAB
Existing Conditions | DHW Load Displacement | Equipment Requirement | Performance Requirement | Climate Zone | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Bedroom) | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Dwelling Unit) |  | Section: | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW
Unitized | 100% | Air-to-Water Heat Pump | EnergyStar labeled | 4A | 1.7 | 2 |  | Subsection:
Central | Minimum 30% | Water-to-Water Heat Pump | Heating COP 2.2-2.5 | 4B | 1.7 | 2 |  | Range Name: | DD_DHW_DHWfromSpaceHeatingBoiler | DD_DHW_ExternalHeatExchanger | DD_DHW_TanklessCoil | DD_DHW_MixingValve | DD_DHW_RecirculationPump | DD_DHW_StorageTank | DD_DHW_HeatingElementonStorageTank | DD_DHW_StorageTankInsulated | DD_DHW_SpacesServed | DD_DHW_EStar | DD_DHW_FuelSource | DD_DHW_RatedEfficiencyUnits | DD_DHW_VentingType | DD_DHW_Controls
| Minimum 30% |  | Heating COP 3.1 | 4C | 1.7 | 2 |  | Title: | DHW from Space Heating Boiler? | External Heat Exchanger? | Tankless Coil? | Mixing Valve | Recirculation Pump | Storage Tank? | Heating Element on Storage Tank? | Storage Tank Insulated? | Spaces Served | EStar | Fuel Source | Rated Efficiency (Units) | Venting Type | Controls | General Y/N
|  |  |  | 5A | 1.8 | 2.2 |  |  | Yes - Year Round | Yes | Yes | Yes - Thermostatic | Yes | Yes | Yes | Yes | Whole Building | Yes | Natural Gas | AFUE | Condensing | N/A | Yes
|  |  |  | 5B | 1.8 | 2.2 |  |  | Yes - Heating Season Only | No | No | Yes - Motorized | No | No | No | No | Apartments Only | No | Oil | Et | Near Condensing | Timer | No
|  |  |  | 5C | 1.8 | 2.2 |  |  | No | N/A | N/A | No | N/A | N/A | N/A | N/A | Common Area Only | N/A | Dual Fuel | Energy Factor | Forced Draft | Demand
|  |  |  | 6A | 1.8 | 2.2 | [5 empty] | N/A |  |  |  |  | Laundry Only |  | District Steam | N/A | Atmospheric | Aquastat
|  |  |  | 6B | 1.8 | 2.2 | [10 empty] | Apartments & Laundry |  | Electric | COP | N/A | None
|  |  |  | 6C | 1.8 | 2.2 | [10 empty] | Common Area & Laundry |  | Propane
Other
N/A
Heating/Cooling TAB
Technology Type | Heating COP | Cooling COP | Electric | Chilled Water | Electrical Service | Section: | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Distribution | Distribution | Heating/Cooling | Motors Pumps Fans
VRF | 3.3 @ 47°F | 4.4 | Forced Air | Forced Air | Yes | Subsection: | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Burner | End Use | End Use | [9 empty] | Temperature Measurements
Low-temp hydronic w/ AWHP | 2.3 | 2.2 | Hydronic | N/A | No | Range Name: | DD_HeatingComponents_EquipmentType | DD_HeatingComponents_SpacesServed | DD_HeatingComponents_EStar | DD_HeatingComponents_FuelSource | DD_HeatingComponents_RatedEfficiencyUnits | DD_HeatingComponents_VentingType | DD_HeatingComponents_HeatTimer | DD_HeatingComponents_EnergyMgtSystem | DD_HeatingComponents_OutdoorAirReset | DD_HeatingComponents_NightSetback | DD_HeatingComponents_SequencingControls | DD_HeatingComponents_Aquastat | DD_HeatingComponents_Burner_EquipmentType | DD_HeatingComponents_EndUse_EquipmentType | DD_HeatingComponents_EndUse_Controls | DD_CoolingComponents_EquipmentType | DD_CoolingComponents_SpacesServed | DD_CoolingComponents_EStar | DD_CoolingComponents_FuelSource | DD_CoolingComponents_RatedEfficiencyUnit | DD_CoolingComponents_Controls | DD_CoolingComponents_Ownership | DD_Distribution_CentralDistributionTypeHeat | DD_Distribution_CentralDistributionTypeCooling | DD_HeatCool_TempMeas | DD_MotorsPumpsFans_Type
PTHP | 3.2 @ 47°F | 4.4 | 1-pipe Steam |  |  | Title: | Equipment Type | Spaces Served | EStar | Fuel Source | Rated Efficiency (units) | Venting Type | Heat Timer | Energy Mgt. System (EMS) | Outdoor Air Reset | Night Setback | Sequencing Controls | Aquastat/Pressuretrol | Equipment Type | Equipment Type | Controls | Equipment Type | Spaces Served | EStar | Fuel Source | Rated Efficiency Unit | Controls | Ownership | Central Distribution Type - Heat | Central Distribution Type - Cooling | System Operational? | Type | Upgrade Equipment Type | Outdoor Unit type | General Y/N
Mini/multi-split ASHP | 3.3 @ 47°F | 4.4 | 2-pipe Steam |  |  |  | Hot Water Boiler | Entire Building | Yes | Natural Gas | AFUE | Condensing | Yes | Yes | Yes | Yes | Yes | Yes | Full Modulation - Set to Manual | Baseboard | TRV | Absorption Chiller - 1 Stage | Entire Building | Yes | Natural Gas | SEER | Thermostat | Resident Owned | Electric | Chilled Water | Heating | Single Speed | Variable Refrigerant Flow (VRF) | Air Source | Yes
Water-to-water | 3.1 @ 47°F | - | Vacuum Steam |  |  |  | Steam Boiler | Common Spaces | No | Oil | Et | Near-Condensing | No | No | No | No | No | No | Full Modulation - Set to Modulate | Radiator | Thermostat | Absorption Chiller - 2 Stage | Common Spaces | No | Oil | EER | Programmable Thermostat | Building Owned | Forced Air | Forced Air | Cooling | Variable Speed | Mini/multi-split Air Source Heat Pump (ASHP) | Ground Source | No
GSHP | [6 empty] | Electric Resistance | Apartments | N/A | Dual Fuel | HSPF | Forced Draft | N/A | N/A | N/A | N/A | N/A | N/A | Hi-Lo Operation | Fan Coil | Programmable Thermostat | Gas Engine Chiller | Apartments | N/A | Dual Fuel | COP | Energy Management System (EMS) | Other | Hydronic | N/A | Neither | ECM | Low-temp Hydronic with Air-to-Water Pump (AWHP) | Other, (Please describe in Additional Notes)
[7 empty] | Air Source Heat Pump | Other |  | District Steam | COP | Atmospheric | [6 empty] | On/Off | Duct | On/Off Valve | Electric Chiller | Other |  | District Steam |  | Chilled Water Temperature Sensor |  | 1-pipe Steam |  |  | Other | Package Heat Pump
[7 empty] | Ground Source Heat Pump |  |  | Electric |  | N/A | [6 empty] | N/A | Radiant Floor | Fan Speed Control | Window A/C |  |  | Electric |  |  |  | 2-pipe Steam |  |  |  | Water-to-Water Heat Pump (WWHP)
[7 empty] | Water Source Heat Pump |  |  | Propane | [9 empty] | PTAC | None | Through Wall A/C |  |  | Propane |  |  |  | Vacuum Steam |  |  |  | Ground Source Heat Pump (GSHP)
[7 empty] | Furnace |  |  | Other | [9 empty] | Other |  | PTAC |  |  | Other
[7 empty] | Combined Heat and Power | [14 empty] | Ductless Mini Split System
[7 empty] | Other | [14 empty] | Split System Central Air
Other
Ventilation TAB
Section: | Ventilation | Ventilation | Ventilation | Ventilation | Ventilation | Ventilation
Subsection:
Range Name: | DD_Ventilation_SystemType | DD_Ventilation_LocationofEquipment | DD_Ventilation_Estar | DD_Ventilation_ConditionedSupply | DD_Ventilation_DuctLeakiness | DD_Ventilation_SystemOperational
Title: | System Type | Location of Equipment | EStar? | Conditioned Supply? | Duct Leakiness | System Operational? |  | Controls | CAR installed
| Centralized | Rooftop | Yes | Yes - MAU | Extremely Leaky | Yes | Measured at Fan | Switch | Yes, adjustable | Yes | Yes, EnergyStar
| Unitized | In-unit | No | Yes - ERV/HRV | Moderately Leaky | Yes, but not used | Measured at Register | Timer Switch | Yes, fixed | No | Yes, Non EnergyStar
| Naturally-ventilated | Basement | N/A | Yes - Economizer | Minimally Leaky | Partially | From Drawings | Humidistat Switch | No |  | No
|  | Other, (Please describe in Additional Notes) |  | No | N/A | No | Other, (Please describe in Additional Notes) | None - Continuous
Other
Recommended Measures TABs
Evaluated & Recommended |  | Natural Gas |  | Yes | Yes
Evaluated & Not Applicable |  | Propane |  | No | No
NA
Review TABs
Not Approved
Approved
Approved with comments

## Version Track (hidden)
Version | Released | Notes
Master Tool v5 Final = v1 individual released tools | 2021-07-01
Master Tool v6 Final = v2 individual released tools | 2021-11-20
Master Tool v6 Final w/ February 2024 release date = v3 tools | 2024-02-01