## Instructions
Low Carbon Pathways Workscope Tool Instructions
Tool Version 2, Released December 2023
1. Complete one tool for each building within a project. If there are multiple buildings with the SAME height, heating fuel, type of heating equipment, and DHW equipment, the information for those buildings may be combined into one tool. In that instance, information should be aggregated accordingly (e.g. number of 1-bedroom units should represent the number across all buildings represented).
2. During the Pre-Construction stage, complete the 'General Project Info' tab and applicable 'Pre-const' tab(s).
3. During the Partial and Construction complete stages, complete the applicable sections in the 'Const' tab(s).
4. Complete all applicable tabs and blue cells within those tabs.
5. Throughout the tool there are comments embedded in some cells to assist in data entry. Hover over the cell to read the comments.
6. Program staff will provide comments in the applicable 'QC Feedback' tabs. Please review and respond within those tabs and update the tool as requested.

## General Project Info
General Project Information
Instructions
Complete the blue cells as applicable.
Project Name (as listed in application)
Total number of buildings in entire project
Total number of units in entire project
Building Information
Building Name, if applicable
Building Street Address
Building city
Building State
Building Zip Code
Building County
Borough-Block-Lot (BBL) Number (NYC Only) |  | Additional Notes
Year building was constructed (approximate is acceptable)
Number of stories (if multiple buildings, please enter the stories of the building(s) with the greatest number of units)
Number of buildings described in this tool
Are there non-residential uses at this property?
Total gross floor area within the thermal envelope (include commercial/retail spaces and conditioned garages)
Gross floor area for commercial/retail spaces, if any
Gross floor area of conditioned garage, if any
Dwelling Units and Occupancy
Number of studio units
Number of 1-bedroom units
Number of 2-bedroom units
Number of 3-bedroom units
Number of 4-bedroom units
Number of 5-bedroom units
Total number of units | 0
Total number of bedrooms | 0
Primary residential demographic
Full-year average vacancy rate for most recent 12 months
Full-year average vacancy rate for the year before last (24-12 months ago)
Utility Information
Electric Utility Company
Gas Utility Company
Other Utility (if not mentioned in list)
Electric Metering Configuration
Are 100% of the apartments metered for electricity as described above? If not, how many are not?
Gas Metering Configuration
Are 100% of the apartments metered for gas as described above? If not, how many are not?
If the property has natural gas, what options best describe how it is used in the building? Mark with an "X" all that apply.
Space Heating
DHW Heating
Cooking
Other, please describe
On-site Solar (If a project has on-site solar, daily solar production must be submitted. See Appendix B in Attachment A for details.)
Does the property have a behind-the-meter solar PV system?
If yes, what is the rated total DC wattage of the system? (in kW)
Combined Heat and Power (If a project has CHP, daily electricity and useful heat production must be submitted. See Appendix B in Attachment A for details.)
Does the property have a cogeneration (combined heat and power) system?
If yes, please describe what the recovered heat is used for (e.g. space heating; DHW; etc.).
Space Heating Information
Primary Space Heating System
Space Heating Fuel
Equipment Type
Is the heating equipment central or in-unit?
How many heaters (boilers/furnaces/etc.) are there?
Spaces Served
End Use Equipment
Distribution Type
Secondary Space Heating System, if applicable
Space Heating Fuel
Equipment Type
Is the heating equipment central or in-unit?
How many heaters (boilers/furnaces/etc.) are there?
Spaces Served
End Use Equipment
Distribution Type
Space Cooling Information
Primary Cooling System
Space Cooling Fuel
Equipment Type
Equipment Quantity
Spaces Served
Controls
Distribution Type
Equipment Ownership
Secondary Cooling System, if applicable
Space Cooling Fuel
Equipment Type
Equipment Quantity
Spaces Served
Controls
Distribution Type
Equipment Ownership
Domestic Hot Water (DHW) Information
DHW System 1
Is DHW heated by the space heating boiler?
DHW Fuel Type
DHW Equipment Type
Quantity of DHW Heaters
Location of DHW Heaters
Spaces Served
DHW System 2, if applicable
Is DHW heated by the space heating boiler?
DHW Fuel Type
DHW Equipment Type
Quantity of DHW Heaters
Location of DHW Heaters
Spaces Served
Other Project Information
If applicable, please provide any additional info about the heating, cooling, and DHW systems to assist us in understanding the energy usage patterns in the building(s).
Note on B9: Complete one tool for each building within a project. If there are multiple buildings with the SAME height, heating fuel, type of heating equipment, and DHW equipment, the information for those buildings may be combined into one tool. In that instance, information should be aggregated accordingly (e.g. number of 1-bedroom units should represent the number across all buildings represented).

## Env Pre-const (hidden)
Envelope Pre-Construction Information
Instructions
This tab calculates existing and proposed area weighted U-value. Complete the blue cells as applicable.
Envelope Existing Conditions
Describe General Envelope Condition and Construction
Envelope Components | Description of Existing Construction (include depths, dimensions, and material) |  |  | Verification Method | Existing R-Value | Existing U-Value | Area (sqft) | Existing Area Weighted U-Value | Additional Notes
Roof 1
Roof 2
Wall 1
Wall 2
Wall 3
Other 1
Other 2
Windows | Describe Existing Construction | Existing Operation Type | Existing Framing Material | # of Panes | Qty. | Existing U-Value | Total Area (sqft) for all the Windows per Type | Existing Area Weighted U-Value per Window Type | Additional Notes
Window 1
Window 2
Window 3
Sliding Glass Door 1
Sliding Glass Door 2
Sliding Glass Door 3
Opaque Door 1
Opaque Door 2
Opaque Door 3
Window-to-Wall Ratio
[7 empty] | Area (sqft) | Existing Area Weighted U-Value
[6 empty] | Whole Building Envelope Total | 0 | 0
Envelope Proposed Upgrade
Envelope Components | Description of Proposed Construction (include depths, dimensions, and material) |  |  | Proposed Added R-Value | Total Proposed R-Value | Proposed Total U-Value | Area (sqft) | Proposed Area Weighted U-Value | Additional Notes
Roof 1 |  |  |  |  | 0
Roof 2 |  |  |  |  | 0
Wall 1 |  |  |  |  | 0
Wall 2 |  |  |  |  | 0
Wall 3 |  |  |  |  | 0
Other 1 |  |  |  |  | 0
Other 2 |  |  |  |  | 0
Windows | Describe Proposed Construction | Proposed Operation Type | Proposed Framing Material | # of Panes | Qty. | Proposed U-Value | Total Area (sqft) for all the Windows per Type | Proposed Area Weighted U-Value | Additional Notes
Window 1
Window 2
Window 3
Sliding Glass Door 1
Sliding Glass Door 2
Sliding Glass Door 3
Opaque Door 1
Opaque Door 2
Opaque Door 3
Window-to-Wall Ratio
[7 empty] | Area (sqft) | Proposed Area Weighted U-Value | Weighted U-Value Target based on building type
[6 empty] | Whole Building Envelope Total | 0 | 0 | #N/A
Proposed Thermal Bridging Mitigation
Area | Please explain how thermal bridging will be mitigated
Slab Edges
Bulkheads
Rim Joists
Roof-to-Wall Connections
Proposed Installed Cost Information
Component Type | Total Measure Cost | Additional Notes
Note on G8: If R-Value is estimated, be sure to select "estimated" in the Verification Method column.
Note on I8: Area should only include the applicable envelope component. E.g. wall area should exclude doors and windows, etc.
Note on H16: If unknown, use ASHRAE-estimated U-Value
Note on I32: Area should only include the applicable envelope component. E.g. wall area should exclude doors and windows, etc.
Note on B62: Group components as appropriate, e.g. windows, wall insulation, etc.
Note on C62: Include all costs such as labor and material.

## Env Const (hidden)
Envelope Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Roof and Wall Insulation
Building Address | Location | Envelope Component | Type of Insulation Installed | Cavity insulation installed without compression or slumping? | Wall Section Description |  |  | Area Insulated (sqft) | Effective R-Value of Envelope Component | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 30% of the wall insulation installed? |  |  | #DIV/0!
Partial Installation - PROGRAM STAFF COMPLETES
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 30% of the wall insulation installed? |  |  | #DIV/0!
Construction Complete
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 100% of the wall insulation installed? |  |  | #DIV/0!
Construction Complete - PROGRAM STAFF COMPLETES
[5 empty] | Total Wall Area Insulated |  |  | 0
[5 empty] | Total Wall Area |  |  | 0
[5 empty] | % Wall Area Insulated |  |  | #DIV/0!
[5 empty] | Is 100% of the wall insulation installed? |  |  | #DIV/0!
Door Replacement
Building Address | Location | Door Type (Slider, Patio, Garage, etc.) | Energy Star? | U-Value | Properly Air Sealed? | % Glazing | Low-E? | Additional Notes |  |  | Quantity Inspected
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Window Replacement
Building Address | Location | Window Operation Type | # of Panes | Frame Material | U-Value | SHGC | Gas Fill | Low-E? | Energy Star? | Properly Air Sealed? | Quantity Inspected | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Component Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Envelope
Measure | Task |  |  | Task Description |  |  | Refrence | Non-Conformance Category | Pass/Fail | Comment
Insulation | Whole-building U-factor target is met, confirmed with as-built workscope tool; Final envelope R-values and U-factors checked |  |  | Verify that actual/installed project U-factor target is met per envelope workscope tool |  |  | Attachment A - Envelope - Required Measure Installation | Minor if U = 100-105% of target; major if U = 105-110% of target; Critical if U > 110% of target
General | Envelope: Comply with manufacturer's requirements and codes; Requirements and codes have been reviewed |  |  | System and system components must be installed in accordance with manufacturer requirements and relevant permit/code requirements |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor
Thermal bridging | Thermal bridging must be mitigated; Photo documentation has been submitted |  |  | Thermal bridging must be mitigated; Photo documentation has been submitted |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor
Continuous insulation | Exterior insulation must be continuous; Photo documentation has been submitted |  |  | Exterior insulation is continuous, metal Z-girts are not allowed |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor
Air barrier, continuous | Continuous air barrier must be provided; Photo documentation has been submitted |  |  | Continuous air barrier |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor
Cavity insulation | Cerify that cavity insulation does not compress or slump; Photo documentation has been submitted |  |  | Cavity insulation does not compress or slump, refer to grade 1 condition according latest RESNET standards |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor
Windows | Windows - Sealing; Photo documentation has been submitted |  |  | If new windows are installed, seal windows to the opening with 2x backer rod and caulk sealant joints or applicable tape |  |  | Attachment A - Envelope - Minimum Installation Standards | Major if not sealed or sealing is clearly inadequate or was not done at all; minor if sealing is minorly deficient
Note on G7: List each component of the wall section from the exterior surface to the interior surface. Include the thickness of each component in inches.
Note on L83: Per the Program's minimum installation standards, windows must be air sealed with either 2x backer rod and caulk sealant joints or applicable tapes
Note on B112: Total Cost should align with submitted invoices.
Note on B114: Group components as appropriate, e.g. windows, wall insulation, etc.

## Code Vent Pre-const (hidden)
Envelope Package Ventilation Pre-Construction Information
Instructions
Complete the blue cells as applicable. Please see Attachment A for ventilation test-out option requirements. If the project is not pursuing the ventilation test out option, then please complete the ventilation proposed upgrades table. If the project is pursuing the ventilation test out option, then please complete the duct sealing table in the Test Out tab.
Will the add-on incentive ventilation option also be pursued?
Ventilation Existing Conditions
Ventilation | Equipment Type |  | System Type | Qty. | Location of Equipment |  | Total CFM | Method for Total CFM Calculation | If Other method was used, please describe |  | Duct Leakiness | System Operational? | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
[other]
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/ Commercial Kitchen
Garage
Laundry
[other]
Ventilation Test Out Option
Is the project pursuing the ventilation test out compliance option?
If yes, what equipment will be used for testing? Include manufacturer, model number, and date of last calibration.
Ventilation Proposed Upgrades
Ventilation | Equipment Type |  | System Type | Qty. | Manufacturer | Model | Location of Equipment |  | Controls | Total Fan Power (W) | Sensible Heat Recovery Efficiency | CFM/ Register | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
[other]
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/ Commercial Kitchen
Garage
Laundry
[other]
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on C9: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on O9: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B14: For other areas as needed, overwrite the header with an appropriate description.
Note on B23: For other areas as needed, overwrite the header with an appropriate description.
Note on C30: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on L30: At design external static pressure and design CFM
Note on M30: At manufacturer rated design conditions
Note on O30: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B35: For other areas as needed, overwrite the header with an appropriate description.
Note on B44: For other areas as needed, overwrite the header with an appropriate description.
Note on B47: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.
Note on C47: Include all costs such as labor and material.

## Code Vent TestOut & Const (hidden)
Envelope Package Ventilation Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable.
Kitchen
Building Address | Location | Measured CFM | CAR installed? | Duct-to-Sheetrock connection air sealed? | New exhaust fan installed? | New exhaust fan make and model | Controls for new fan | Exterior penetrations air sealed? | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Bathroom
Building Address | Location | Measured CFM | CAR installed? | Duct-to-Sheetrock connection air sealed? | New exhaust fan installed? | New exhaust fan make and model | Controls for new fan | Exterior penetrations air sealed? | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Ventilation Ductwork Sealing
Building Address | Shaft Description |  |  | # of Registers Served | # of Floors Served | Total Allowable Leakage (CFM50) | Total Measured Leakage (CFM50) | Additional Notes
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Ventilation
Measure | Task |  |  | Task Description |  |  | Refrence | Non-Conformance Category | Pass/Fail | Comment
Central Exhaust | Demonstrate operation of existing ventilation system - exhaust; Test results have been submitted |  |  | 25 CFM continuous or 100 CFM intermittent for each kitchen; 20 CFM continuous or 50 CFM intermittent for each bathroom |  |  | Attachment A - Envelope - Required Measure Installation | Major if ventilation is < 80% of target; minor if ventilation is 80-100% of target
| Ductwork must be cleaned; Photos have been submitted to show clean ductwork |  |  | Verify that ductwork was cleaned |  |  | Attachment A - Envelope - Required Measure Installation | Incidental
| Ductwork must be sealed to program requirements; Test-out results have been submitted |  |  | Verify that ductwork was sealed; Review test-out results |  |  | Attachment A - Envelope - Required Measure Installation | Major if no evidence of sealing or sealing is highly inadequate; minor if minor sealing was not completed
| System must exhaust airflow per program requirements - central exhaust; Testing and balancing results have been submitted |  |  | Verify that delivered airflow meets program requirements |  |  | Attachment A - Envelope - Required Measure Installation | Minor
Unitized Exhaust | System must exhaust airflow per program requirements - unitized exhaust; Testing and balancing results have been submitted |  |  | Verify that delivered airflow meets program requirements |  |  | Attachment A - Envelope - Required Measure Installation | Minor
| If replacing windows in a building without exhaust, install exhaust in each bathroom and kitchen; Contractor's log of installed exhaust fans by apartment number has been submitted |  |  | Verify that an exhaust system was installed |  |  | Attachment A - Envelope - Required Measure Installation | Minor
Central or Unitized | Ventilation testing and balancing (Option 1); TAB contractor's contract has been submitted |  |  | Testing and Balancing (TAB) contractor must be independent, hired by owner, not by energy contractor |  |  | Attachment A - Envelope - Minimum Installation Standards | Incidental
| Ventilation - Follow Residential Energy Services Network (RESNET) sampling protocols; Test results with sampling protocol has been submitted |  |  | Follow RESNET sampling protocols; for central systems, include at minimum top and bottom floors served by a riser |  |  | Attachment A - Envelope - Operational Test Out Specifications | Minor
| Ventilation testing and balancing (Option 2); Equipment accuracy has been submitted |  |  | Equipment meets program accuracy requirements |  |  | Attachment A - Envelope - Operational Test Out Specifications | Incidental
| Ventilation (as part of envelope) - Program notification of testing; Notification has been submitted |  |  | Notify program staff at least two weeks prior to testing |  |  | Attachment A - Envelope - Operational Test Out Specifications | Incidental
Exhaust penetrations | Ventilation - exhaust penetrations: Sealing; Photo documentation has been submitted |  |  | Exhaust penetrations must be air sealed |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor
Exhaust | Vent to outside; Photo documentation has been submitted |  |  | Exhaust must vent to outside |  |  | Attachment A - Envelope - Minimum Installation Standards | Minor

## H&C Pre-const
Heating and Cooling Pre-Construction Information
Instructions
Complete the blue cells as applicable.
Heating and Cooling Existing Conditions
| Heating Systems | Equipment Type | Qty. | Spaces Served | Fuel Source | Rated Efficiency | Rated Efficiency Units | Total System Output (Mbh) | Distribution Type | End Use Equipment | Additional Notes
* * | Primary Heating System
* * | Secondary Heating System
| Cooling Components | Equipment Type | Qty. | Spaces Served | Fuel Source | Rated Efficiency | Rated Efficiency Units | Distribution Type | Additional Notes
* * | Primary Cooling System
* * | Secondary Cooling System
Heating and Cooling Proposed Upgrade
| Heating System | Equipment Type | Spaces Served | Condenser Information | [7 empty] | Indoor Unit Information |  |  |  | Initial Heat Source for Water Loop (WWHP only) | Initial Cooling Source for Water Loop (WWHP only) | Additional Notes
|  |  |  | Qty. | Make | Model | Outdoor Unit Type | Rated Heating Capacity (Btu/hr.) | Required Heating Capacity (Btu/hr.) | Rated Efficiency | Required Efficiency | Indoor Unit Type | Qty. | Rated Efficiency | Required Efficiency
* * | System 1
* * | System 2
* * | System 3
| Electrical Service Upgrade Required? |  |  | Description of electric service upgrade, if applicable
| Is the existing fossil fuel equipment being removed? |  |  | Description of fossil fuel removal workscope, if applicable
Proposed Installed Cost Information
| Equipment Type | Total Measure Cost | Additional Notes
Note on H7: AFUE = Annual Fuel Utilization Efficiency Et = Thermal Efficiency HSPF = Heating Season Performance Factor COP = Coefficient of Performance
Note on L7: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on H11: SEER = Seasonal Energy Efficiency Ratio EER = Energy Efficiency Ratio COP = Coefficient of Performance
Note on J11: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on J17: Enter the efficiency required by in Attachment A. Include the units of the efficiency.
Note on K17: Include the units of the efficiency you provide.
Note on L17: Enter the efficiency required by in Attachment A. Include the units of the efficiency.
Note on O17: Include the units of the efficiency you provide.
Note on P17: Include the units of the efficiency.
Note on B25: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.
Note on C25: Include all costs such as labor and material.

## H&C Const
Heating and Cooling Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Indoor Units
Building Address | Location | Manufacturer | Model # | Thermostat Setpoints | Space Temperature (F) | Outdoor Temp at Inspection (F) | Electric Resistance Control Set Correctly? | Additional Notes
(Apt #, Room, Floor, Space)
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Outdoor Units
Building Address | Space(s) Served | Manufacturer | Model # | Uniform Energy Factor | Rated Heating Capacity (Btu/hr) | Additional Notes
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Heating and Cooling
Measure | Task |  |  | Task Description |  |  | Refrence |  | Non-Conformance Category | Pass/Fail | Comment
Space Electrification | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope | Incidental | Incidental
| New envelope penetrations sealed to prevent infiltration and rodents/insects or water penetration; Photo documentation submitted |  |  | Split system pipe penetrations are well-sealed both on the outside and inside of the penetration, including between pipes; Penetrations for packaged through- wall systems (PTHP, VTHP) are well sealed |  |  | Attachment A - Heating and Cooling - Minimum Installation Standards |  | Minor
| Piping insulation is installed per the manufacturer's specifications, meets the correct thickness, and is code compliant; Photo documentation submitted |  |  | Pipes are insulated (no exposed copper); Insulation is installed correctly, of the correct thickness, and meets code and manufacturer requirements |  |  | Energy Conservation Construction Code2, Sections R403.4 and C403.11.3 |  | Minor
| Exterior pipe insulation is ultraviolet (UV) resistant and/or has a UV resistant covering; Photo documentation submitted |  |  | The exterior pipe insulation is UV resistant or has a UV resistant covering or coating, where applicable (for example, may not apply to ground source heat pumps) |  |  | Energy Conservation Construction Code2, Sections R403.4.1 and C403.11.3.1 |  | Minor
| Seal hole in chimney, if fossil fuel equipment is removed; Photo documentation submitted |  |  | Seal abandoned boiler exhaust connection to chimney, if fossil fuel equipment is removed |  |  | Energy Conservation Construction Code2, Sections R402.4 and C402.5.1 |  | Minor
| Units installed under a roof line/edge must have a rain/snow/ ice shield; Photo documentation submitted |  |  | If the unit is set under the roof line/edge, rain/snow/ice shield or drain cap is provided; Outdoor units must be installed such that melting defrost condensate does not drip onto other outdoor units |  |  | Manufacturer's instructions |  | Incidental
| The owner was delivered a copy of the Operational and Maintenance Handbook, including start-up and test reports |  |  | The owner was given a copy of the manufacturer Operation and Maintenance manual and provided with contact information for emergency service needs |  |  | Energy Conservation Construction Code2, Sections R303.3 and C408.1.1 |  | Incidental
| Owner understands basic system operation, adjustment of dampers (if applicable), and controls |  |  | The owner has been given training by installer, and understands basic system operation, especially heating operation; The owner understands how to program controls and thermostats (as needed); The owner understands basic safety and maintenance |  |  | Energy Conservation Construction Code2, Figure C408.2.4 |  | Incidental
| Outdoor unit location; Photo documentation submitted |  |  | Outdoor units are located with correct spacing from walls, from other outdoor units, and are not located in spaces such as outdoor stairwells that will prevent adequate air circulation, where applicable (for example, does not apply to ground source heat pumps) |  |  | Manufacturer's instructions |  | Minor
| Refrigerant leak prevention; Final system charge in system is marked clearly on unit |  |  | Units were charged with refrigerant and the system sealed to prevent leaks; No leaks were detected with a leak detector and/or soap bubble test |  |  | Manufacturer's instructions |  | Critical
| Required regular maintenance actions are clearly stated and incorporated on a readily accessible label; Photo documentation submitted |  |  | The label shall include the title or publication number for the operation and maintenance manual for that particular model and type of product |  |  | Energy Conservation Construction Code2, Sections R303.3 and C408.1.1 |  | Incidental
| Receptacle for each heat pump outdoor unit; Photo documentation submitted |  |  | Each heat pump outdoor unit has a 110 volt receptacle within 25' horizontally, where applicable (for example, does not apply to ground source heat pumps installed indoors) |  |  | National Electrical Code, Section 210.63 |  | Incidental
| Data Release Authorization Form (DRAF) with new heating electric account(s) shall be provided, if any; DRAF(s) submitted |  |  | Verify that a signed DRAF that includes the electric account has been provided. |  |  | Attachment A - Heating and Cooling - Required Deliverables: Pre-Construction |  | Minor
| Electrification completed per workscope (heat pumps installed); Photo documentation submitted |  |  | Verify that electrification is complete (heat pumps installed) |  |  | Project workscope |  | Critical
| If fossil fuel equipment is removed, fuel source is safely removed or terminated; Photo documentation submitted |  |  | Verify that old connections have been removed or capped off, if fossil fuel equipment has been removed |  |  | Project workscope |  | Major
| New equipment must meet energy efficiency of project workscope; Photo documentation submitted |  |  | Verify that new equipment meets efficiency requirement of project workscope; Minor defect if new equipment is at least 90% of the energy efficiency in the workscope; Major defect if new equipment is less than 90% of the energy efficiency in the workscope |  |  | Project workscope |  | Minor if efficiency is 90%-99% of efficiency in workscope; major if efficiency is < 90% of efficiency in workscope
Optional Recommended Measures
Measure | Task |  |  | Task Description |  |  | Refrence |  | Non-Conformance Category | Pass/Fail | Comment
Energy Management System (EMS) | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope | Incidental | Incidental
| EMS controls are set properly; EMS settings submitted |  |  | Review the plan for the new controls, including a careful examination of sensor locations, set points, and zones; Review the EMS settings; Make sure they have been adjusted to reflect the needs of the building and the settings in the workscope; Ensure that the installed EMS provides a significantly different control strategy than the old control system–otherwise, savings will not be achieved; Minor defect if at least 50% of the energy savings will be achieved; major defect if less than 50% of energy savings will be achieved |  |  | Attachment A - Optional Measures: Steam Upgrades - Required Measure Installation |  | Minor if savings are anticipated to be 50%- 99%; major if savings are anticipated to be < 50% of expected savings
| EMS sensors are installed; Installation log submitted |  |  | In 2-pipe and hot water systems, sensors should be installed in no fewer than 10% of apartments and on a variety of floors and in a variety of apartment lines; In 1-pipe steam systems, sensors should be installed in no fewer than 25% of apartments and on a variety of floors, and there must be a sensor in the apartment at the end of each steam line |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards |  | Minor
Orifice plates | Orifice plates are correctly sized; Documentation submitted |  |  | Review heat loss calculation and target radiator outputs; If orifice plates are sized to reduce the output of the terminal unit, the output of the unit must not be less than 100% of the heat load of the room it serves |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards |  | Minor
Air vents | Air vent orientation and location; Photo documentation submitted |  |  | Air vents must be installed in the vertical direction and at least 15" away from any elbows |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards |  | Minor
| Air vents on mains and risers; Photo documentation submitted |  |  | Air vents must be installed on 100% of mains and risers |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards |  | Major
Note on F7: Include night setback settings if applicable.
Note on B66: Total Cost should align with submitted invoices.
Note on B68: Group equipment as appropriate, e.g. duct sealing, HRV, etc.

## DHW Pre-const (hidden)
Domestic Hot Water Pre-Construction Information
Instructions
Complete the blue cells as applicable.
Domestic Hot Water Existing Conditions
| DHW System | Equipment Type | Unitized or Central System? | Qty. of Heaters | DHW from Space Heating Boiler? | Spaces Served | Fuel Source | Rated Efficiency | Rated Efficiency Units | Total Output (Mbh) | Storage Tank? | Additional Notes
* * | DHW System 1
* * | DHW System 2
Required Central DHW Minimum Installation Capacity Based on Project Location
| Climate Zone | Per Bedroom Method |  | Per Dwelling Unit Method
|  | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Bedroom) | Total Minimum Required Capacity (MBH) | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Dwelling Unit) | Total Minimum Required Capacity (MBH)
Domestic Hot Water Proposed Upgrades
| DHW System | Equipment Type | Unitized or Central System? | Qty. of Heaters | Manufacturer | Model | Total Output Capacity (MBH) | Uniform Energy Factor | EnergyStar Labeled? | Tank Capacity (Gal.) | Outdoor Unit Type | Additional Notes
* * | DHW System 1
* * | DHW System 2
| Is the existing fossil fuel equipment being removed? |  |  | Description of fossil fuel removal workscope, if applicable
Proposed Installed Cost Information
| Equipment Type | Total Measure Cost | Additional Notes
Note on J7: AFUE = Annual Fuel Utilization Efficiency Et = Thermal Efficiency COP = Coefficient of Performance
Note on B24: Group equipment as appropriate, e.g. tanks, etc.
Note on C24: Include all costs such as labor and material.

## DHW Const (hidden)
Domestic Hot Water Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Domestic Hot Water
Building Address | Location | Equipment Description | Manufacturer | Model # | Uniform Energy Factor | Total Output Capacity (MBH) | Control Settings | Water Temperature Readings |  | Additional Notes
(Apt #, Room, Floor, Space)
[8 empty] | Faucet Near Heater | Faucet Far from Heater
Partial Installation
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Partial Installation - PROGRAM STAFF COMPLETES
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Construction Completion
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Construction Completion - PROGRAM STAFF COMPLETES
|  |  | Total Capacity (MBH) |  |  | 0
|  |  | Total Minimum Required Capacity (MBH) |  |  | 0
|  |  | Is minimum required capacity met? |  |  | Fail
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Homestic Hot Water
Measure | Task |  |  | Task Description |  |  | Refrence |  | Non-Conformance Category |  | Pass/Fail | Comment
Health and Safety | Ensure that water is delivered at less than 130 degrees, to prevent scalding; Photo documentation submitted |  |  | Verify that water is delivered at less than 130 degrees |  |  | U.S. Consumer Product Safety Commission, https:// www.cpsc.gov/s3fs- public/5098.pdf |  | Minor
DHW Controls | DHW temperature meets project workscope target; Test results submitted |  |  | Verify DHW water temperature |  |  | Project workscope |  | Minor
| Recirculation control installed; Photo documentation submitted |  |  | Verify recirculation control has been installed |  |  | Project workscope |  | Minor
| Recirculation control installed meets energy code requirements; Test results submitted |  |  | Verify that pump only operates on flow and is set at 104 F maximum |  |  | Energy Conservation Construction Code1, Sections R403.5.2 and C404.7 |  | Minor
DHW Water Heater | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope |  | Incidental
| Replacement domestic hot water heating plant(s) shall meet program efficiency requirements; Documentation provided |  |  | Verify that hot water heater meets program efficiency requirements; If no high-efficiency requirements (e.g. ENERGY STAR) are applicable for the particular application, verify that the rated efficiency is no less than required by the energy code |  |  | Attachment A - Domestic Hot Water - Required Measure Installation |  | Minor if efficiency is 90%-99% of efficiency in workscope; major if efficiency is < 90% of efficiency in workscope
| Installed capacity meets program requirements; Documentation provided |  |  | Verify that the installed capacity meets program minimum requirements (in units of 1000 Btu/hr/bedroom, or in units of 1000 Btu/hr/unit, as applicable) |  |  | Attachment A - Domestic Hot Water - Required Measure Installation |  | Minor
| Pipe insulation is installed; Photo documentation submitted |  |  | All hot water piping in mechanical room and accessible piping in unconditioned spaces shall be insulated to the energy conservation code; Minor defect if at least 50% of the piping insulation was installed |  |  | Energy Conservation Construction Code1, Sections R403.4 and C403.11.3 |  | Minor
| Penetrations sealed to prevent infiltration and rodents/insects or water penetration; Photo documentation submitted |  |  | Split system heat pump water heater refrigerant pipe penetrations are well-sealed both on the outside and inside of the penetration, including between pipes |  |  | Attachment A - Domestic Hot Water - Minimum Installation Standards |  | Minor
| Seal penetrations no longer needed for fossil fuel equipment; Photo documentation submitted |  |  | Seal outdoor air intake, breaching connection to chimney at bottom, and top of chimney if chimney is abandoned |  |  | Energy Conservation Construction Code1, Sections R402.4 and C402.5.1 |  | Minor
| The owner was provided a copy of the Operational and Maintenance Handbook, including start-up and any test reports and preventive maintenance |  |  | The owner was given a copy of the manufacturer operation and maintenance manual and provided with contact information for emergency service needs |  |  | Energy Conservation Construction Code1, Sections R303.3 and C408.1.1 |  | Incidental
| Required regular maintenance actions are clearly stated and incorporated on a readily accessible label |  |  | The label shall include the title or publication number for the operation and maintenance manual for that particular model and type of product |  |  | Energy Conservation Construction Code1, Sections R303.3 and C408.1.1 |  | Incidental
Note on B48: Total Cost should align with submitted invoices.
Note on B50: Group equipment as appropriate, e.g. storage tanks, etc.

## Appliances Pre-const (hidden)
Induction Stove Pre-Construction Information
Instructions
Complete the blue cells as applicable.
Stove/Range Existing Conditions
| Qty. | Number of Burners | Manufacturer | Year Manufactured | Confirm if Induction | Fuel Source | Additional Notes
Stove/Range 1
Stove/Range 2
Stove/Range 3
Stove/Range Proposed Upgrade
| Qty. | Number of Burners | Manufacturer | Model | Confirm if Induction | Additional Notes
Stove/Range 1
Stove/Range 2
Stove/Range 3
Dryer Existing Conditions
| Qty. | Frequency of Use (Loads/wk.) | Manufacturer | Year Manufactured | Confirm if ENERGY STAR | Fuel Source | Additional Notes
Dryer 1
Dryer 2
Dryer 3
Heat Pump Dryer Proposed Upgrade
| Qty. | Estimated Annual Energy Use (kWh/yr) | Manufacturer | Model | Confirm if ENERGY STAR | Additional Notes
Dryer 1
Dryer 2
Dryer 3
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on C32: Include all costs such as labor and material.

## Appliances Const (hidden)
Induction Stove Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Induction Stove
Building Address | Location | Number of Burners | Manufacturer | Model # | Confirm if Induction | Additional Notes
(Apt #, Room, Floor, Space)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Heat Pump Dryer
Building Address | Location | Estimated Annual Energy Use (kWh/yr) | Confirm if ENERGY STAR | Manufacturer | Model # | Additional Notes
(Apt #, Room, Floor, Space)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Appliances
Measure | Task |  |  | Task Description |  |  | Refrence | Non-Conformance Category | Pass/Fail | Comment
Induction Stoves | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope | Incidental
| Gas pipe to the stove removed or disconnected and capped; Photo documentation submitted |  |  | Verify that gas pipe is secure and out of the way (no remaining flex pipe), gas valve is shut off, and gas pipe has been securely capped; Submit photos of a sample of installations |  |  | Project Workscope | Minor
| Installed in all inspected apartments; Installation log submitted |  |  | Verify that all induction stoves were installed per workscope; Major defect if fewer than 75% of the stoves were installed; Submit contractor's log of installations by apartment |  |  | Project workscope | Major
Heat Pump Dryers | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope | Incidental
| Heat pump dryers are ENERGY STAR rated |  |  | Verify ENERGY STAR clothes washers are installed, per workscope. |  |  | Project Workscope | Minor
| Heat pump dryers were Installed per workscope |  |  | Verify that all clothes dryers were installed per workscope. | Project workscope |  | Project Workscope | Minor
Note on B43: Total Cost should align with submitted invoices.

## Add-On Air Sealing Pre-const
Air Sealing Pre-Construction Information
Instructions
Evaluate all air sealing opportunities listed in the table below. Complete the blue cells as applicable. To be eligible for the full add-on incentive, the project must install all possible air sealing measures in all buildings. An air sealing measure can be deemed "not recommended" only if that component does not exist within the building or if it was previously air sealed.
Air Sealing Workscope Evaluation and Proposed Upgrade
Measure | Evaluation Status | Workscope Description | Qty. | Material | Explanation of why measure is not recommended or not applicable
Tops of shafts/bulkheads
Exterior doors
Air conditioner sleeves
Windows
Floor of attic or ceiling of top floor penetrations (attic door, hatch, electrical, piping, ventilation, etc.)
Plumbing and electrical penetrations in the apartments
Penetrations and openings between all mechanical equipment rooms, including boiler room and the conditioned space
Basement perimeter
Fire sprinkler penetrations
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on B19: Group equipment as appropriate, e.g. doors, plumbing penetrations, etc.
Note on C19: Include all costs such as labor and material.

## Add-On Air Sealing Const
Air Sealing Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Air Sealing
Building Address | Location | Location of Leakage | Type of Sealing Performed | Air Sealing Complete | Quantity (SF, LF, # of units, etc. - list for each line item) | Additional Notes
(Apt #, Room, Floor, Space)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Air Sealing
Measure | Task |  |  | Task Description |  |  | Refrence | Non-Conformance Category | Pass/Fail | Comment
Air Sealing | Air sealing: fixed openings; Photo documentation submitted |  |  | Verify that all required air sealing is complete: Tops of shafts/bulkheads, existing exterior doors, AC sleeves, existing windows, floor of attic or ceiling of top floor penetrations (including but not limited to attic door, hatch, electrical piping, ventilation, duct penetrations, uncapped wall cavities, etc.), plumbing and electrical penetrations in apartments, penetrations and openings between mechanical rooms and the conditioned space, basement perimeter, fire sprinkler penetrations, makeup air opening in mechanical room if fossil fuel equipment is removed, top of chimney if fossil fuel equipment is removed, and any other areas identified in the workscope; Minor defect if at least 75% of the air sealing is complete in all required locations; Major defect if less than 75% of the air sealing is complete in all required locations; Critical defect if no air sealing was done |  |  | Attachment A - Optional Measures: Air Sealing - Required Measure Installation, and project workscope | Minor if air sealing is 75%-99% complete; major if air sealing is less than 75% complete; critical if no air sealing was done
| Air sealing: movable surfaces; Photo documentation submitted |  |  | Movable surfaces that have been weatherstripped move freely (windows, doors, hatches, etc.) |  |  | Attachment A - Optional Measures: Air Sealing - Minimum Installation Standards | Minor
| Weatherstripping: mechanical fastening; Photo documentation submitted |  |  | Weatherstripping is mechanically fastened. Submit photos of a sample of weatherstripping. Self-adhesive weatherstripping is not acceptable. |  |  | Attachment A - Optional Measures: Air Sealing - Minimum Installation Standards | Minor
Note on B24: Total Cost should align with submitted invoices.
Note on B26: Group equipment as appropriate, e.g. doors, plumbing penetrations, etc.

## ARCHIVED Add-On Steam Pre-const (hidden)
Steam Heating Pre-Construction Information
Instructions
Evaluate all air sealing opportunities listed in the table below. Complete the blue cells as applicable. To be eligible for the full add-on incentive, the project must install all possible components of the package in all buildings. A steam system measure can be deemed "not recommended" only if that component does not exist within the building or if it was previously installed (e.g. the building no longer has steam traps).
Steam Heating System Workscope Evaluation and Proposed Upgrade
Measure | Evaluation Status | Workscope Description | Qty. | Material | Explanation of why measure is not recommended or not applicable
Energy Management System
Radiant Heat Barriers
Thermostatic radiator valves or other thermostatic controls on every radiator or fan coil unit
Inlet orifice plate on all radiators
Master venting on all mains and risers
Functional steam traps (for those remaining in service) including all traps in the basement and boiler room
Burner clean and tune
Proposed Installed Cost Information
Equipment Type | Total Measure Cost
Note on B17: Group equipment as appropriate, e.g. tanks, etc.
Note on C17: Include all costs such as labor and material.

## ARCHIVED Add-On Steam Const (hidden)
Steam Heating Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Energy Management System
Building Address | Location | In-Unit |  | Central Control |  |  |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Location of Sensor | Measured Temperature | Manufacturer | Model | Settings
[6 empty] | Day (temp) | Night (temp) | Night (hours)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Radiant Heat Barrier
Building Address | Location | Radiant Heat Barrier Installed? |  |  | Radiant Heat Barrier Manufacturer and Model # |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Thermostatic Radiator Valves
Building Address | Location | TRVs Installed? |  |  | TRV Manufacturer and Model # |  |  | TRV Setpoint |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Orifice Plates
Building Address | Location | Orifice Plates Installed? |  |  | Additional Notes
| (Apt #, Room, Floor, Space) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s) | Living Room Radiator(s) | Bedroom Radiator(s) | Other Radiator(s)
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Optional Recommended Measures
Measure | Task |  |  | Task Description |  |  | Refrence | Non-Conformance Category | Pass/Fail | Comment
Steam components | Components installed; Photo documentation submitted |  |  | Verify that steam components have been installed: Energy Management System, radiant heat barriers, thermostatic radiator valves (TRVs), inlet orifice plates, master venting, steam traps; Submit photos |  |  | Attachment A - Optional Measures: Steam Upgrades - Required Measure Installation | Major
Air vents | Air vent orientation and location; Photo documentation submitted |  |  | Air vents must be installed in the vertical direction and at least 15" away from any elbows |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards | Minor
| Air vents on mains and risers; Photo documentation submitted |  |  | Air vents must be installed on 100% of mains and risers |  |  | Attachment A - Optional Measures: Steam Upgrades - Minimum Installation Standards | Major
Note on B72: Total Cost should align with submitted invoices.
Note on B74: Group equipment as appropriate, e.g. orifice plates, steam traps, etc.

## Add-On Vent Pre-const
Ventilation Pre-Construction Information
Instructions
Complete the blue cells as applicable. To be eligible for the full add-on incentive, the project must install all possible ventilation measures in all buildings. A ventilation measure can be deemed "not recommended" only if that component does not exist within the building or if it was previously installed and aligns with program requirements.
Ventilation Existing Conditions
Ventilation | Equipment Type |  | System Type | Qty. | Location of Equipment |  | Total CFM | Method for Total CFM Calculation | Annual Hours | Conditioned Supply? | % Outdoor Air | Duct Leakiness | System Operational? | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/Commercial Kitchen
Garage
Laundry
Ventilation Proposed Upgrades
Ventilation | Equipment Type |  | System Type | Manufacturer | Model | Qty. | Location of Equipment |  | Total Fan Power | Sensible Heat Recovery Efficiency | CFM /Register | Additional Notes
Supply Location
Corridors
Apartments
Whole Building
Exhaust Location
Corridors
Apartment Bathrooms
Apartment Kitchens
Common Area Bathrooms
Common Area/Commercial Kitchen
Garage
Laundry
Proposed Installed Cost Information
Equipment Type | Total Measure Cost | Additional Notes
Note on C7: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on P7: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B12: For other areas as needed, overwrite the header with an appropriate description.
Note on B21: For other areas as needed, overwrite the header with an appropriate description.
Note on C24: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on K24: At design external static pressure and design CFM
Note on L24: At manufacturer rated design conditions
Note on N24: If "Other" or "N/A" was selected for any of the drop-down items in this section, indicate what "other" is or why the selection is "N/A" here.
Note on B29: For other areas as needed, overwrite the header with an appropriate description.
Note on B38: For other areas as needed, overwrite the header with an appropriate description.
Note on B41: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.
Note on C41: Include all costs such as labor and material.

## Add-On Vent Const
Ventilation Partial Installation and Construction Complete Information
Instructions
Complete the blue cells as applicable below based on the installed conditions. Please reference the program requirements for sampling and testing instructions.
Ventilation Equipment
Building Address | Location | Equipment Type | Manufacturer | Model # | Spaces Served | Pre-retrofit Flow Rate (CFM) | Post-retrofit Flow Rate (CFM) | Rated Heat Exchange Efficiency | Supply |  |  |  | Exhaust |  | Filter MERV Rating | Calculated Efficiency | Additional Notes
| (Apt #, Room, Floor, Space) | [7 empty] | Outside Air Temp | Temp After Heat Exchange | Design/ Rated Air Flow (CFM) | Intake location complies with Program Req's? | Inside Air Temp | Leaving Air Temp
[10 empty] | Temp After Heat Exchange | Design/Rated Air Flow (CFM) |  | Inside Air Temp | Leaving Air Temp
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Ventilation Distribution
Building Address | Location | Ductwork |  | Insulation |  |  | Sealing |  |  |  | Automatic Damper? | Additional Notes
| (Apt #, Room, Floor, Space) | System Designation | Linear Feet (insulated/ replaced) | Material Type | Thickness (inches) | R-Value | Sealant Used | Pre Duct Leakage (CFM25) | Post Duct Leakage (CFM25) | Exterior Penetrations Sealed?
Partial Installation
Partial Installation - PROGRAM STAFF COMPLETES
Construction Complete
Construction Complete - PROGRAM STAFF COMPLETES
Actual Installed Cost Information
Construction Complete
Equipment Type | Equipment Cost | Labor Cost | Total Cost | Additional Notes
0
0
0
0
0
0
0
Reviewer Section - Standards and Quality Assurance Checklist Specifications
Instructions
This section is for the reviewer to fill out. Complete the orange cells as applicable below based on your review of the information provided.
Ventilation
Measure | Task |  |  | Task Description |  |  | Refrence |  | Non-Conformance Category |  | Pass/Fail | Comment
Energy Recovery Ventilator (ERV) or Heat Recovery Ventilator | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope |  | Incidental
| Ventilation supply/exhaust balance; Log of installation of CAR dampers submitted, by apartment; Photo documentation submitted |  |  | Overall balancing of supply and exhaust must be within 10%; Constant Airflow Regulator (CAR) dampers must be installed to allow automatic balancing of individual airflows |  |  | Attachment A - Ventilation - Required Measure Installation |  | Minor if 75-99% of CAR dampers installed; major if < 75% of CAR dampers installed
| Program ventilation efficiency requirements; Test results submitted |  |  | Verify that ERV/HRV sensible efficiency is 77% minimum |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Major
| Fan power program requirements; Test results submitted |  |  | Verify that ERV/HRV less than 1 Watt per CFM |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
| Kitchen and bathroom ventilation; Test results and photo documentation submitted |  |  | Kitchens exhausted to minimum 25 CFM continuously, bathrooms 20 CFM continuously |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Major
Constant airflow regulator (CAR) dampers | Cutsheets submitted |  |  | Verify that cutsheets have been provided |  |  | Project Workscope |  | Incidental
| Set airflow on CAR dampers; Documentation submitted |  |  | Verify airflow settings match workscope, either from balancing report or by examining CARs |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Central Ductwork | Ductwork must be sealed to program requirements; Test-out results submitted |  |  | Verify that ductwork was sealed; review test-out results; Seal duct to sheetrock connection prior to installing grilles |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Major
Airflows | System must deliver airflow per program requirements; Test results submitted |  |  | Verify that delivered airflow meets program and design requirements |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Major
| Testing and balancing: Independent contractor; Contract for TAB contractor submitted |  |  | Testing and Balancing (TAB) contractor must be independent, hired by owner, not by energy contractor |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Testing equipment | Testing and balancing: Accuracy; Equipment accuracy has been submitted |  |  | Equipment meets program accuracy requirements |  |  | Program requirements |  | Incidental
Health and Safety | Location of intake air; Photo documentation submitted |  |  | Intake air must be clear of possible contaminant sources |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Duct insulation | Insulate ductwork; Photo documentation submitted |  |  | Duct insulation must meet program requirements |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Frost protection | Frost protection must be installed in Energy Recovery Ventilator (ERV) or Heat Recovery Ventilator (HRV) |  |  | Heat exchanger core must be protected from frost |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Filter | Install MERV 8 filter (MERV 13 recommended but not required); Photo documentation submitted |  |  | ERV/HRV must be protected by mininum MERV 8 filter on both intake and exhaust airstreams (MERV 13 recommended but not required) |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Heater | Electric heater temperature rise limitation |  |  | Electric heater temperature rise must be 5 F or less (supply air temperature 62 F or higher recommended but not required) |  |  | Attachment A - Ventilation - Minimum Installation Standards |  | Minor
Note on D7: e.g. Fan only, Fan with heating/cooling coil, ERV, HRV, etc.
Note on N8: Exterior outdoor air intake louver must be at least 4 feet above grade or roof deck, at least 10 feet away from known contamination sources (dryer, garage exhaust, etc.), and no closer to the exhaust port than recommended by the manufacturer.
Note on M37: If the system does not operate 24/7, is there an automatic damper that shuts outdoor air intake when the unit is off? e.g. hallways, laundry rooms, common areas.
Note on D38: e.g. supply, exhaust, ERV, etc
Note on B66: Total Cost should align with submitted invoices.
Note on B68: Group equipment as appropriate, e.g. duct sealing, HRVs, etc.

## Pre-const QC Feedback
Pre-construction QC Review Feedback Form
Reviewer Name:
Review Date:
Approval Status:
Program Approval Notes:
General Comments | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Has all required documentation been submitted?
General Portfolio Info Tab: Is the tab complete and, if applicable, aligned with the FlexTech study?
General Project Info Tab: Is the tab complete for all building types?
General Project Info Tab: Will program staff be able to set a utility baseline with this information?
Required Measures (e.g. Envelope, Heating & Cooling, Domestic Hot Water, or Appliances tabs) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Is there a tab completed for each building type?
Are existing conditions thoroughly described?
Are proposed measure descriptions thoroughly described?
Bonus Measures, if applicable (e.g. Air Sealing and Ventilation) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Is there a tab completed for each building type?
Are existing conditions thoroughly described?
Are proposed measure descriptions thoroughly described?

## Const QC Feedback
Partial Installation and Construction Complete QC Review Feedback Form
Inspector Name:
Inspection Type (Desk/Field)
Program Stage (Partial, Complete)
Inspection Date:
Approval Status:
Program Approval Notes:
General Comments | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Has all required documentation been submitted?
Required Measures (e.g. Envelope, Heating & Cooling, Domestic Hot Water, or Appliances tabs) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Do the installation comply with program requirements?
Bonus Measures, if applicable (e.g. Air Sealing and Ventilation) | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)
Do the installation comply with program requirements?
Standards and Quality Assurance Checklist Specifications Comments | Reviewer Comments (Rev0) | Provider Comments (Rev0) | Reviewer Comments (Rev1)

## Data Validation (hidden)
GENERAL PROJECT SPECIFIC INFO TAB
Demographic | ElecUtil | GasUtil | MeterConf | MeterConf Gas | YES/NO | Heating Fuel | Heating Equipment Type | Heating Spaces Served | Heading End Use Equipment Type | Central Distribution Type - Heat | Cooling Fuel Source | Cooling Equipment Type | Cooling Spaces Served | Cooling Controls | Cooling Ownership | DHW | DHW Fuel | DHW Equipment | DHW Spaces Served | DHW Location | Central or in unit
Families | Central Hudson | Central Hudson | Direct Metered | Direct Metered | Yes | Electric | Electric Resistance | Entire Building | Baseboard | 1-pipe steam | Natural Gas | Individual window-mounted AC | Entire Building | Thermostat | Resident Owned | No | Natural Gas | Immersion coil in heating boiler - no storage tank | Whole Building | In-unit | In-unit
Seniors | Con Edison | Con Edison | Submetered | Master Metered | No | Gas | Steam boiler(s) | Common Spaces | Radiator | 2-pipe steam | Oil | Individual wall-mounted AC | Common Spaces | Programmable Thermostat | Building Owned | Yes, year-round | Electricity | Immersion coil in heating boiler - separate storage tank | Apartments Only | Central Mechanical Room | Central Mechanical Room
Single-occupancy | PSEG LI | KEDLI | Master Metered | No Gas |  | Oil | Hydronic boiler(s) - Non-Condensing | Apartments | Fan Coil | Vacuum steam | Dual Fuel | PTAC / PTHP | Apartments | Energy Management System (EMS) | Other (Please describe in Additional Notes) | Yes, heating season only | Oil | Indirect from space heating boiler | Common Area Only | Other (Please describe in Additional Notes) | Other (Please describe in Additional Notes)
Mixed Population | National Grid | KEDNY |  |  |  | Propane | Hydronic boiler(s) - Condensing | Other (Please describe in Additional Notes) | Duct | Hydronic radiation | District Steam | Split system | Other (Please describe in Additional Notes) | Chilled Water Temperature Sensor |  |  | District Steam | Direct-fired storage water heater(s) | Laundry Only
Other (Please describe in Additional Notes) | NYSEG | National Fuel Gas |  |  |  | District Steam | Forced Air Furnace - Non-Condensing |  | Radiant Floor | Electric Baseboard | Electric | Heat Pump - Ground Source |  | NA |  |  | Propane | Dedicated DHW boiler with separate storage tank | Apartments & Laundry
| O&R | National Grid |  |  |  | Dual Fuel | Forced Air Furnace - Condensing |  | PTAC | Fan coil/PTAC | Propane | Heat Pump - Water Loop |  |  |  |  | Other (Please describe in Additional Notes) | Tankless instantaneous | Common Area & Laundry
| RG&E | NYSEG |  |  |  | Other (Please describe in Additional Notes) | Heat Pump - Water Loop |  | Other (Please describe in Additional Notes) | Heat pump – Water loop | Other (Please describe in Additional Notes) | Absorption Chiller – gas fired | [5 empty] | Heat pump water heaters | Other (Please describe in Additional Notes)
| Other | O&R |  |  |  |  | Heat Pump - Air Source |  |  | Mini split / ductless |  | Absorption Chiller – indirect fired | [5 empty] | Other (Please describe in Additional Notes)
|  | RG&E |  |  |  |  | Heat Pump - Ground Source |  |  | Forced Hot Air |  | Electric Chiller
|  | Other |  |  |  |  | District Steam |  |  | Other (Please describe in Additional Notes) |  | Other (Please describe in Additional Notes)
|  | None |  |  |  |  | Other (Please describe in Additional Notes)
ENVELOPE TAB
NYS County | IECC Climate Zone | Garden Style U Target | Non-Garden Style U Target |  | Section: | Windows | Windows | Windows | Windows | Envelope | Windows | Windows | Windows | Exterior Doors | Exterior Doors | Exterior Doors | Air Infiltration
Albany | 5A | 0.06 | 0.1 |  | Subsection:
Allegany | 6A | 0.05 | 0.09 |  | Range Name: | DD_Windows_OperationType | DD_Windows_FramingMaterial | DD_Windows_ThermalBreak | DD_Windows_NumOfPanes | DD_Envelope_VerificationMethod | DD_Windows_GlassCoating | DD_Windows_GasFilled | DD_Windows_WeatherStripping | DD_ExteriorDoors_Material | DD_ExteriorDoors_GlazingType | DD_ExteriorDoors_WeatherStripping | DD_AirInfiltration_Tightness
Bronx | 4A | 0.07 | 0.13 |  | Title: | Operation Type | Framing Material | Thermal Break | # of Panes | Verification Method | Glass Coating | Gas Filled | Weather-stripping | Material | Glazing Type | Weather-stripping | Tightness | Cavity Insulation | General
Broome | 6A | 0.05 | 0.09 |  |  | Awning | Aluminum | Yes | Single | Estimated | Heat Absorbing Tints | Yes | Excellent | Solid Wood | Single Pane | Excellent | Low leakage | Yes | Yes
Cattaraugus | 6A | 0.05 | 0.09 |  |  | Casement | Wood | No | Single w/ Storms | Reported by Site Staff | Reflective Coating | No | Good | Solid Metal | Double Pane | Fair | Some Leakage | No | No
Cayuga | 5A | 0.06 | 0.1 |  |  | Fixed | Fiberglass |  | Double | From Drawings | Low-E Coating |  | Poor | Hollow Wood | Other, (Please describe in Additional Notes) | Poor | Very Leaky | NA | NA
Chautauqua | 5A | 0.06 | 0.1 |  |  | Hopper | Vinyl |  | Triple | Visual Confirmation | None |  | None | Hollow Metal | N/A | None | N/A
Chemung | 5A | 0.06 | 0.1 |  |  | Single Hung | Other, (Please describe in Additional Notes) |  |  | Other, (Please describe in Additional Notes) | Unknown |  |  | Wood, Insulated Core |  | N/A
Chenango | 6A | 0.05 | 0.09 |  |  | Double Hung |  |  |  |  | Other, (Please describe in Additional Notes) |  |  | Metal, Insulated Core
Clinton | 6A | 0.05 | 0.09 |  |  | Single Sliding | [7 empty] | Glass
Columbia | 5A | 0.06 | 0.1 |  |  | Double Sliding | [7 empty] | Glass Slider
Cortland | 5A | 0.06 | 0.1 |  |  | Other, (Please describe in Additional Notes) | [7 empty] | Other, (Please describe in Additional Notes)
Delaware | 6A | 0.05 | 0.09
Dutchess | 5A | 0.06 | 0.1
Erie | 5A | 0.06 | 0.1
Essex | 6A | 0.05 | 0.09
Franklin | 6A | 0.05 | 0.09
Fulton | 6A | 0.05 | 0.09
Genesee | 5A | 0.06 | 0.1
Greene | 5A | 0.06 | 0.1
Hamilton | 6A | 0.05 | 0.09
Herkimer | 6A | 0.05 | 0.09
Jefferson | 6A | 0.05 | 0.09
Kings | 4A | 0.07 | 0.13
Lewis | 6A | 0.05 | 0.09
Livingston | 5A | 0.06 | 0.1
Madison | 6A | 0.05 | 0.09
Monroe | 5A | 0.06 | 0.1
Montgomery | 6A | 0.05 | 0.09
Nassau | 4A | 0.07 | 0.13
New York | 4A | 0.07 | 0.13
Niagara | 5A | 0.06 | 0.1
Oneida | 6A | 0.05 | 0.09
Onondaga | 5A | 0.06 | 0.1
Ontario | 5A | 0.06 | 0.1
Orange | 5A | 0.06 | 0.1
Orleans | 5A | 0.06 | 0.1
Oswego | 5A | 0.06 | 0.1
Otsego | 6A | 0.05 | 0.09
Putnam | 5A | 0.06 | 0.1
Queens | 4A | 0.07 | 0.13
Rensselaer | 5A | 0.06 | 0.1
Richmond | 4A | 0.07 | 0.13
Rockland | 5A | 0.06 | 0.1
Saratoga | 5A | 0.06 | 0.1
Schenectady | 5A | 0.06 | 0.1
Schoharie | 6A | 0.05 | 0.09
Schuyler | 6A | 0.05 | 0.09
Seneca | 5A | 0.06 | 0.1
St. Lawrence | 6A | 0.05 | 0.09
Steuben | 6A | 0.05 | 0.09
Suffolk | 4A | 0.07 | 0.13
Sullivan | 6A | 0.05 | 0.09
Tioga | 5A | 0.06 | 0.1
Tompkins | 6A | 0.05 | 0.09
Ulster | 6A | 0.05 | 0.09
Warren | 6A | 0.05 | 0.09
Washington | 5A | 0.06 | 0.1
Wayne | 5A | 0.06 | 0.1
Westchester | 4A | 0.07 | 0.13
Wyoming | 6A | 0.05 | 0.09
Yates | 5A | 0.06 | 0.1
DHW TAB
Existing Conditions | DHW Load Displacement | Equipment Requirement | Performance Requirement | Climate Zone | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Bedroom) | Min Installed Capacity to Meet 30% of Domestic Hot Water Load (MBH/Dwelling Unit) |  | Section: | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW | DHW
Unitized | 100% | Air-to-Water Heat Pump | EnergyStar labeled | 4A | 1.7 | 2 |  | Subsection:
Central | Minimum 30% | Water-to-Water Heat Pump | Heating COP 2.2-2.5 | 4B | 1.7 | 2 |  | Range Name: | DD_DHW_DHWfromSpaceHeatingBoiler | DD_DHW_ExternalHeatExchanger | DD_DHW_TanklessCoil | DD_DHW_MixingValve | DD_DHW_RecirculationPump | DD_DHW_StorageTank | DD_DHW_HeatingElementonStorageTank | DD_DHW_StorageTankInsulated | DD_DHW_SpacesServed | DD_DHW_EStar | DD_DHW_FuelSource | DD_DHW_RatedEfficiencyUnits | DD_DHW_VentingType | DD_DHW_Controls
| Minimum 30% |  | Heating COP 3.1 | 4C | 1.7 | 2 |  | Title: | DHW from Space Heating Boiler? | External Heat Exchanger? | Tankless Coil? | Mixing Valve | Recirculation Pump | Storage Tank? | Heating Element on Storage Tank? | Storage Tank Insulated? | Spaces Served | EStar | Fuel Source | Rated Efficiency (Units) | Venting Type | Controls | General Y/N
|  |  |  | 5A | 1.8 | 2.2 |  |  | Yes - Year Round | Yes | Yes | Yes - Thermostatic | Yes | Yes | Yes | Yes | Whole Building | Yes | Natural Gas | AFUE | Condensing | N/A | Yes
|  |  |  | 5B | 1.8 | 2.2 |  |  | Yes - Heating Season Only | No | No | Yes - Motorized | No | No | No | No | Apartments Only | No | Oil | Et | Near Condensing | Timer | No
|  |  |  | 5C | 1.8 | 2.2 |  |  | No | N/A | N/A | No | N/A | N/A | N/A | N/A | Common Area Only | N/A | Dual Fuel | Energy Factor | Forced Draft | Demand
|  |  |  | 6A | 1.8 | 2.2 | [5 empty] | N/A |  |  |  |  | Laundry Only |  | District Steam | N/A | Atmospheric | Aquastat
|  |  |  | 6B | 1.8 | 2.2 | [10 empty] | Apartments & Laundry |  | Electric | COP | N/A | None
|  |  |  | 6C | 1.8 | 2.2 | [10 empty] | Common Area & Laundry |  | Propane
Other
N/A
Heating/Cooling TAB
Technology Type | Heating COP | Cooling COP | Electric | Chilled Water | Electrical Service | Section: | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Heating Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Cooling Components | Distribution | Distribution | Heating/Cooling | Motors Pumps Fans
VRF | 3.3 @ 47°F | 4.4 | Forced Air | Forced Air | Yes | Subsection: | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Heating System | Burner | End Use | End Use | [9 empty] | Temperature Measurements
Low-temp hydronic w/ AWHP | 2.3 | 2.2 | Hydronic | N/A | No | Range Name: | DD_HeatingComponents_EquipmentType | DD_HeatingComponents_SpacesServed | DD_HeatingComponents_EStar | DD_HeatingComponents_FuelSource | DD_HeatingComponents_RatedEfficiencyUnits | DD_HeatingComponents_VentingType | DD_HeatingComponents_HeatTimer | DD_HeatingComponents_EnergyMgtSystem | DD_HeatingComponents_OutdoorAirReset | DD_HeatingComponents_NightSetback | DD_HeatingComponents_SequencingControls | DD_HeatingComponents_Aquastat | DD_HeatingComponents_Burner_EquipmentType | DD_HeatingComponents_EndUse_EquipmentType | DD_HeatingComponents_EndUse_Controls | DD_CoolingComponents_EquipmentType | DD_CoolingComponents_SpacesServed | DD_CoolingComponents_EStar | DD_CoolingComponents_FuelSource | DD_CoolingComponents_RatedEfficiencyUnit | DD_CoolingComponents_Controls | DD_CoolingComponents_Ownership | DD_Distribution_CentralDistributionTypeHeat | DD_Distribution_CentralDistributionTypeCooling | DD_HeatCool_TempMeas | DD_MotorsPumpsFans_Type
PTHP | 3.2 @ 47°F | 4.4 | 1-pipe Steam |  |  | Title: | Equipment Type | Spaces Served | EStar | Fuel Source | Rated Efficiency (units) | Venting Type | Heat Timer | Energy Mgt. System (EMS) | Outdoor Air Reset | Night Setback | Sequencing Controls | Aquastat/Pressuretrol | Equipment Type | Equipment Type | Controls | Equipment Type | Spaces Served | EStar | Fuel Source | Rated Efficiency Unit | Controls | Ownership | Central Distribution Type - Heat | Central Distribution Type - Cooling | System Operational? | Type | Upgrade Equipment Type | Outdoor Unit type | General Y/N
Mini/multi-split ASHP | 3.3 @ 47°F | 4.4 | 2-pipe Steam |  |  |  | Hot Water Boiler | Entire Building | Yes | Natural Gas | AFUE | Condensing | Yes | Yes | Yes | Yes | Yes | Yes | Full Modulation - Set to Manual | Baseboard | TRV | Absorption Chiller - 1 Stage | Entire Building | Yes | Natural Gas | SEER | Thermostat | Resident Owned | Electric | Chilled Water | Heating | Single Speed | Variable Refrigerant Flow (VRF) | Air Source | Yes
Water-to-water | 3.1 @ 47°F | - | Vacuum Steam |  |  |  | Steam Boiler | Common Spaces | No | Oil | Et | Near-Condensing | No | No | No | No | No | No | Full Modulation - Set to Modulate | Radiator | Thermostat | Absorption Chiller - 2 Stage | Common Spaces | No | Oil | EER | Programmable Thermostat | Building Owned | Forced Air | Forced Air | Cooling | Variable Speed | Mini/multi-split Air Source Heat Pump (ASHP) | Ground Source | No
GSHP | [6 empty] | Electric Resistance | Apartments | N/A | Dual Fuel | HSPF | Forced Draft | N/A | N/A | N/A | N/A | N/A | N/A | Hi-Lo Operation | Fan Coil | Programmable Thermostat | Gas Engine Chiller | Apartments | N/A | Dual Fuel | COP | Energy Management System (EMS) | Other | Hydronic | N/A | Neither | ECM | Low-temp Hydronic with Air-to-Water Pump (AWHP) | Other, (Please describe in Additional Notes)
[7 empty] | Air Source Heat Pump | Other |  | District Steam | COP | Atmospheric | [6 empty] | On/Off | Duct | On/Off Valve | Electric Chiller | Other |  | District Steam |  | Chilled Water Temperature Sensor |  | 1-pipe Steam |  |  | Other | Package Heat Pump
[7 empty] | Ground Source Heat Pump |  |  | Electric |  | N/A | [6 empty] | N/A | Radiant Floor | Fan Speed Control | Window A/C |  |  | Electric |  |  |  | 2-pipe Steam |  |  |  | Water-to-Water Heat Pump (WWHP)
[7 empty] | Water Source Heat Pump |  |  | Propane | [9 empty] | PTAC | None | Through Wall A/C |  |  | Propane |  |  |  | Vacuum Steam |  |  |  | Ground Source Heat Pump (GSHP)
[7 empty] | Furnace |  |  | Other | [9 empty] | Other |  | PTAC |  |  | Other
[7 empty] | Combined Heat and Power | [14 empty] | Ductless Mini Split System
[7 empty] | Other | [14 empty] | Split System Central Air
Other
Ventilation TAB
Section: | Ventilation | Ventilation | Ventilation | Ventilation | Ventilation | Ventilation
Subsection:
Range Name: | DD_Ventilation_SystemType | DD_Ventilation_LocationofEquipment | DD_Ventilation_Estar | DD_Ventilation_ConditionedSupply | DD_Ventilation_DuctLeakiness | DD_Ventilation_SystemOperational
Title: | System Type | Location of Equipment | EStar? | Conditioned Supply? | Duct Leakiness | System Operational? |  | Controls | CAR installed
| Centralized | Rooftop | Yes | Yes - MAU | Extremely Leaky | Yes | Measured at Fan | Switch | Yes, adjustable | Yes | Yes, EnergyStar
| Unitized | In-unit | No | Yes - ERV/HRV | Moderately Leaky | Yes, but not used | Measured at Register | Timer Switch | Yes, fixed | No | Yes, Non EnergyStar
| Naturally-ventilated | Basement | N/A | Yes - Economizer | Minimally Leaky | Partially | From Drawings | Humidistat Switch | No |  | No
|  | Other, (Please describe in Additional Notes) |  | No | N/A | No | Other, (Please describe in Additional Notes) | None - Continuous
Other
Recommended Measures TABs
Evaluated & Recommended |  | Natural Gas |  | Yes | Yes
Evaluated & Not Applicable |  | Propane |  | No | No
NA
Review TABs
Not Approved
Approved
Approved with comments

## Version Track (hidden)
Version | Released | Notes
Master Tool v5 Final = v1 individual released tools | 2021-07-01
Master Tool v6 Final = v2 individual released tools | 2021-11-20