## Instructions
Field Definitions:
Inspection Category | The Category field represents the highest level of the inspection checklist hierarchy and may include one or more measures
Measure | The Measure field falls under a Category and represents a specific component that you are inspecting
Task Requirement | The Task Requirement field falls under a Measure and represent the specific inspection checkpoints that an inspector would rate as Pass or Fail for a given component
Code/IGSPA/Program Ref | Each task requirement needs to be tied back to either a code reference, the IGSPA standard, Program requirement, or Manufacturer instructions
Deficiency Category | Each task requirement is assigned a deficiency category of either incidental, minor, major or critical. Refer to the Deficiency Category Descriptions section below for additional detail. Generally speaking, NYSERDA will require an applicant to document through pictures and/or notes verification of resolution of all major and critical deficiencies. Minor and Incidental deficiencies need to be corrected but NYSERDA will not be verifying resolution.
Canned Failure Description | Deficiency descriptions developed by the mini-bid contractors will be made available to the inspector to select from when a specific Task Requirement is rated as Failed. To the extent possible, NYSERDA prefers to use canned deficiency descriptions to describe to the applicant why a given task has failed.
>75 Tons Only | If a Task Requirement is applicable only to projects over >75 Tons, indicate so with a "Yes"
Deficiency Category Descriptions: |  | QA Scoring Matrix
Incidental | not expected, on its own, to pose a substantial risk of system failure or hazard. | Score | Incidental | Minor | Major | Critical
Minor | may require re-wiring or re-piping to address but are not expected to pose a substantial risk of system failure or hazard. | 5 | Up to 3 | Up to 2 | 0 | 0
Major | present an increased risk of system failure or hazard but are not determined to be in imminent danger of failure or hazard. | 4 | More than 3 | Up to 3 | 0 | 0
Critical | present an imminent hazard and/or probability of system failure. | 3 | N/A | More than 3 | 0 | 0
|  | 2 | N/A | N/A | Up to 1 | 0
|  | 1 | N/A | N/A | More than 1 | More than 0

## Design Review
Project Information
Application # | 123456
Customer | XYZ Institution
Site Address | 17 Columbia Circle, Fort Orange NY 12203
System Capacity (tons) | 43
Loop Field Type | Vertical Borehole
HP Make & Rep | ABC Pump, J. Doe
|  |  | Contact | e-mail | Office Phone | Cell Phone
Applicant | DEF Enterprises
Designer | GHI Engineering, LLP
Installer | JKL Mechanical, LLC
Driller | MNO Drilling, LLC
Reviewer | S. Smith, PQR Earth Storage, LLP
Date of Review | 2017-12-25
Item # | Category | Measure | Applies to: Large, Small, Both | Task Requirement | Code/IGSHPA/Program Ref | Deficiency Category | Canned Failure Description | Document Needed | Pass | Fail | N/A
1 | Sizing | Small systems | Small | Use Manual J software for residential heating and cooling load calculations. Review summary page of the ACCA Manual J. For non-residential systems provide heating and cooling load calculations performed in accordance with ASHRAE/ACCA Standard 183. | Program Manual, page 9 | Major | Load calculations have revealed these concerns that require addressing: _____ | ACCA Manual J (Residential Load Calculation) Summary calculation page base on ASHRAE/ACCA Standard 183
2 | Sizing | Large Systems | Large | Provide heating and cooling load calculations in accordance with the procedures described in the ASHRAE/ACCA Standard 183. Using software that complies with one of the methodologies Standard 183 is acceptable. | Program Manual, page 9; Section 312 of the NYS Mechanical Code. | Major | Load calculations have revealed these concerns that require addressing: _____ | Summary calculation page based on ASHRAE/ACCA Standard 183.
3 | Layout | Well Locations Note: doesn't apply if only heat pumps being replaced with existing loop field | Large (>75 Ton) | Review the spacing of the vertical wells in proximity to each other and other site constraints. Confirm the thermal dispersion/well spacing is adequate. | 5.1.2.1 in the IGSHPA design and installation guide | Major | Well spacing and thermal dispersion have revealed these concerns that require addressing: ______ | Bore/Well Field Plans.
4 | Loop/Bore | Min & Max EWT | Both | Loop Design must be sufficient to provide a minimum entering water temperature of 30F in heating mode and maximum entering water temperature of 90F in cooling mode | Program Manual, page 8 | Critical | Loop design provided has a minimum EWT below 30F in heating mode and / or a maximum EWT of 90F in cooling mode. | Equipment schedules
5 | Loop/Bore | Test Borehole, Soil thermal values Note: Doesn't apply if only heat pumps being replaced with existing loop field | Large (>30 Ton) | Conductivity test must be conducted for systems larger than 30 tons to accurately determine the site specific geology and thermal characteristics | Program Manual, page 6 | Major | No conductivity testing has been performed. | Provide conductivity test result.
6 | Loop/Bore | No test borehole, soil thermal values | Small | Horizontal - use IGSHPA Soil and Rock Classification Manual and Soil Conservation Service Survey for county data | IGSHPA Design & Installation Standards Section 1B.3 | Minor | Thermal conductivity for project does not match with average local data from either IGSHPA or the ASHRAE Handbook. | Documented source for soil thermal value.
7 | Loop/Bore | Standing Column Well | Both | Must include a bleed circuit, drywell or approved receptor to maximize thermal efficiency | Program Manual, page 8 | Minor | Either a bleed circuit, drywell, or approved receptor has not been included in the design. | Bore/Well Field Plans.
8 | Loop/Bore | Pipe Material | Both | HDPE with any transition to other materials located indoors | IGSHPA Design & Installation Standards Section 1C & 3A.4 | Minor | A transition from HDPE piping to other materials should be done indoors. | Piping schematic(s) for piping in loop field.
9 | Loop/Bore | Loop Field Design | Both | A loop field design must consist of the following: - Loop/Site Plan - Loop Sizing Report - Antifreeze (type & concentration) | Program Manual, page 8 Reference 7.3 in IGSHPA Design and Installation Guide | Major | One or more of the following have not been provided: _____ | Loop/Site Plan Loop Sizing Report (flexible) Loop Field Pressured Drop Calculations < 30 tons
10 | Loop/Bore | DX requirement | Both | Verify Min borehole depth of 100 ft per 12,000 Btu/hr. of heating capacity | Program Manual, page 9 | Minor | The minimum borehole depth of 1200 ft per 12,000 Btu/hr. of heating capacity has not been reached with the design. | Bore/Well Field Plans.
11 | Loop/Bore | DX requirement | Both | Verify cathodic protection on wells | Program Manual, page 9 | Major | Cathodic protection has not been provided on the wells. | Bore/Well Field Plans.
12 | Loop/Bore | DX requirement | Both | Wells grouted with thermally enhanced grout that achieves hydraulic conductivity of 10-7cm/sec or less | Program Manual, page 9 | Major | Thermally enhanced grout in the wells that achieves a hydraulic conductivity of 10-7 cm/sec or less is required. | Grout specifications
13 | Loop/Bore | DX requirement | Both | Ensure the design requires evacuation (250 microns or as required by manufacturer), and leak testing with nitrogen of the entire refrigeration system. | IGSHPA 7C; Sections 1108 and 1101.6 of NYS MC - ASHRAE 15 | Major | Design specifications do not include the evacuation, and/or leak testing with nitrogen of the entire refrigeration system. | Documentation of evacuation and leak testing.
14 | Interior Piping | Water Quality | Both | Unless municipal water is used and the interior above grade piping is HDPE, the following shall be performed: Verify water samples have been taken and tested. Verify water quality analysis has been provided. Verify water treatment protocol and filtration is being provided to match water quality analysis. Verify that the water quality conforms to the manufacturer's recommendations. Verify material is compatible with specified water treatment protocol. | IGSHPA 3B & 3C | Major | The following potential water quality issues exist: ____ | Water sample test report and quality analysis.
15 | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED
16 | Equipment | Heat Pumps | Both | If standalone heating source, system must be designed with full load heating capacity between 90% and 120% of peak heating load. Systems sized for heating mode may exceed the 120% limit for cooling. Multi-stage or variable refrigerant flow heat pumps being installed in one or two-family dwellings or townhouses (governed by the NYS Residential Code), need to meet the 90% minimum sizing requirement and may be sized to exceed the 120% requirement. All other projects (governed by the NYS Building Code) must be sized for the primary Mode to be not greater than the load calculations. | Program Manual, page 7 | Major | As the standalone heating source is the geothermal system, the system is not adequately sized per the NYSERDA Program Manual, which is between 90% and 120% of the peak heating load. | Heating load calculations.
17 | Equipment | Heat Pumps | Large and non-single family residential systems | If standalone cooling source, system must be designed with full load cooling capacity between 90% and 120% of peak cooling load. Systems sized for cooling mode may exceed the 120% limit for heating. Multi-stage or variable refrigerant flow heat pumps being installed in one or two-family dwellings or townhouses (governed by the NYS Residential Code), need to meet the 90% minimum sizing requirement and may be sized to exceed the 120% requirement. All other projects (governed by the NYS Building Code) must be sized for the primary Mode to be not greater than the load calculations. | Program Manual, page 7 | Major | As the site has been determined as a cooling dominant site, the geothermal system is not adequately sized per the NYSERDA Program Manual, which is between 90% and 120% of the peak cooling load. | Cooling load calculations.
18 | Equipment | Pumps | Both | Pumping Power at design conditions (rated power based on duty point and includes all pumps used to move energy to/from source/sink) must not exceed 85 Watts per AHRI rated cooling ton for systems >10 tons. For small systems <=10 tons, pumping power shall not exceed 100 Watts per ton. | NYSERDA Program Manual, page 14 of draft 2.0. IGSHPA Table 3.1 | Minor | Source Water Pump Power exceeds the maximum permitted by this Program. Replace or modify the pump(s). | Equipment schedules
19 | System | Schematic | Large | Must clearly and accurately represent system piping strategy | Program Manual, page 8 and page 9 | Major | Failure to submit system schematic | Piping schematic(s) for GSHP system(s) Detail/specification for firestopping of through penetrations if fire rated construction exists on project
20 | System | Anti-freeze additives | Both | Propylene glycol (CAS No. 57-55-6), methanol (CAS No. 64-56-1), and ethanol (CAS No. 64-17-5) are acceptable. Verify one of these is specified and its design concentration. Verify the Program Manual requirements are being met. Specifically: Large systems with ethanol and methanol must comply with Section 1207 of the 2015 International Mechanical code and all systems must comply with section 3d.2.4 of the IGSHPA Design and Installation Standard. Therefore, loops must maintain a minimum temperature differential between the loop and the flash point of the antifreeze solution of 50 degrees at all times. The maximum allowable concentration of methanol is 12.5% by weight. The maximum allowable loop field temperature in Small System using methanol as an antifreeze is 75 degrees F. In addition, the designer and installer should ensure that the loop field operating temperature is at least 50 degrees lower than the flash point of methanol at all times. The maximum allowable concentration of ethanol is 10% by weight. The maximum allowable loop field temperature in Small System using ethanol as an antifreeze is 70 degrees F. In addition, the designer and installer should ensure that the loop field operating temperature is at least 50 degrees lower than the flash point of ethanol at all times. | Program Manual, page 8 | Critical | Failure to comply with acceptable type or concentration of anti-freeze | Anti-freeze type, concentration supported by volume/volume of fluid in pipes; ethanol denaturants
21 | System | Heat Pumps | Large | Review control schematic and sequence of operation. Verify controls and sequence match the heat pump manufacturer's requirements and the design intent. | IGSHPA 5B.1.11 | Critical | Sequence of Operations is not acceptable | GSHP system control schematic and sequence of operations.
22 | Equipment | Ancillary Items | Large | Ensure cross connection control devices are provided for make up to water quality management equipment, including glycol injection equipment where potable water is connected | NYS DOH Cross Connection Control Guideline/NYS PC | Major | Project fails to conform to Plumbing Code in regards to backflow/cross contamination of make-up water detail | Plumbing drawings showing water make-up to GSHP system.
23 | Equipment | Refrigerant Volume | Large (>75 Ton) | For commercial applications where the Mechanical Code applies, verify compliance with Chapter 11 of the NYS MC (ASHRAE 15). Review refrigerant type and confirm that maximum allowable refrigerant in the mechanical space, or any space the refrigerant pipe communicates, is not exceeded. | Chapter 11 NYS MC | Critical | The maximum allowable refrigerant is exceeded in the mechanical space or spaces where the refrigerant pipe communicates per Chapter 11 of the NYS Mechanical Code. | Provide documents demonstrating compliance with ASHRAE 15 (Chapter 11 NYS MC)
24 | System | Electrical | Both | Review documents for compliance with the NEC and Manufacturer's Requirements | Program Manual, page 8 | Major | The design does not conform to the NEC or manufacturer's requirements. Correct the following ______________. | Electrical design
25 | Equipment | Access | Large | Ensure service clearance is provided to maintain the heat pump including filter changes if applicable. | NYS MC 306; Manufacturer's Installation Instructions | Minor | There is inadequate service clearance to properly maintain the heat pump.
26 | Loop/Bore | Open and SCW - Setbacks | Both | Verify Setbacks required by IGSHPA | CSA 448.6.4.4 & 448.7.4.5 | Major | The design does not meet the required setbacks. Please advise as to corrective action. | Bore/Field Plans
27 | Loop/Bore | Open | Both | Documentation that flow rates to wells, or discharge system, are sustainable at maximum pumping flow rates | CSA 448.6.4.5.3 b | Major | Adequate proof has not been provided to demonstrate that flow rates are sustainable, as required by IGSHPA | Flow tests
28 | Loop/Bore | Standing Column Well - Draw Down Test | Both | Verify that the specifications clearly identify Well Draw Down Test requirements or included results of Well Draw Down Test. | CSA 448.7.4.6 | Major | Well Draw Down Test has not been incorporated into the design or requirements have not been specified as required by IGSHPA. | Well draw down test report
29 | Equipment | Buffer Tank | Both | On Water to Water Systems, verify provisions for and the sizing of the buffer tank conforms to HP manufacturer's requirements. | Program Manual, page 8 (page 12 of draft 2.0) | Minor | The buffer tank sizing is inconsistent with acceptable practices. Please review and revise. | Buffer tank specifications
30 | Loop/Bore | Horizontal Loop | Both | Rebate applications must include the file from the horizontal-loop design software showing inputs and system design specifications. Review the file to ensure the loop design is adequate an meet the building load requirements. | Program Manual, page 14 of draft 2.0 | Minor | Provide output from horizontal-loop design software demonstrating design is adequate.

## Loop Field_Photo Ins
Category | Measure | Task Description (appears in the photo insp. Report, and is emailed to Contractor)(accompanies a failure desc.) | Task Hover Description | Photo Submittal Instructions (this text displays on the specific measure for the Contractor to see) | Deficiency Category | Code/Program Reference | Canned Failure Description | Could Not Verify Canned Description
Documentation | Design and Commissioning documents | System design and loop field commissioning documents submitted are complete, reflect as-built condition,s and have no significant deficiencies. |  | Submit a complete set of system design and loop-field commissioning documents if not already submitted. | Incidental | Program Manual (p. 13, Milestone # 2) | The design documents do not reflect as-built conditions. | There are commissioning documents (testing, flushing, and disinfection) missing. Provide the following: ______________________.
Materials | Piping Materials | Piping on systems other than Direct Exchange must be HDPE and correspond to the design specifications. Direct Exchange piping must conform to ASTM B280. | Piping on systems must be HDPE, or B280 copper, and correspond to the design specifications. | Photos must show the manufacturer's stamp identifying the pipe material for all types of piping used in the installation. | Major | Program Manual (p. 10, para. 8), IGSPHA 2016 Standards Sec. 1C.2 | The piping material used ____________________. This is non-compliant with the design specifications or the NYSERDA requirements. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Materials | Grouting Materials | Grouting materials conform with design specifications and NYSERDA requirements. | Mark "N/I" if not inspecting a closed-loop vertical or horizontally bored system. Grouting materials used must conform with the design specifications and meet or surpass IGSHPA 2016 requirements. The hydraulic conductivity of the grouting mixture must be independently verified by a laboratory. | Photos only required if a closed-loop vertical and horizontal (bored) system was used. Photos must show the manufacturer's label identifying the grout product and identify the type and grade of admixture delivered. | Major | IGSHPA 2016 Standards, Sec 2B.1.2, PM | The grout and admixture(s) used are not consistent with the design specifications, are incompatible with each other, or conductivity has not been independently verified. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Well field footprint and borehole spacing | Well field footprint and borehole spacing meet design specifications. | Mark "N/I" if a closed-loop vertical systems was not used. The installed well field should be consistent with the latest approved drawings in shape and dimension, and the spacing of the boreholes must match the design specifications within reasonable tolerances. | Provide photos showing the complete loop field area, with dimensional reference. Provide detail to show the number of boreholes and the distance between holes with a visual scale reference. | Major | Program Manual (p. 8: Well/Borehole Requirements) | The installed well field varies significantly from most recently approved drawings, or the spacing between some boreholes is too small. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Horizontal-Loop design compliance | Horizontal loop field conforms with the design drawings. | Mark "N/I" if a horizontal-loop system was not used.The installed horizontal loop field must conform with the design drawings in overall dimension, circuit quantity, spacing, and be installed below frost line. | Provide photos showing the complete loop field area, with dimensional reference. Provide detail to show the number of circuits and the layout of the loops in the trench, as well as the distance between loops. Show with scale reference the length of the loops and the overlap pattern if a slinky installation. Using scale reference, show the depth of the trench below grade. | Major | Program Manual (p.8, Horizontal-Loop Project Requirements) | The installed horizontal loop field varies significantly from the most recent approved drawings in ____________________, or sections of the loop field were ___ found to be installed above the frost line. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Open-Loop design compliance | Standing column open-loop system bleed provision is compliant with design. | Mark "N/I" if an open-loop (standing column well) sytem was not used. Standing column open-loop systems must include a bleed circuit, drywell, or locally approved receptor. | Provide photos to show the location and features of the bleed provision. | Major | Program Manual (p.8, Horizontal-Loop Project Requirements) | The installed system was not found to have an approved receptor or NYSERDA-compliant bleed provision. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Direct Exchange design compliance | Manifold and line sets installation meet IGSHPA requirements. | Mark "N/I" if direct exchange tubing was not used. Manifolds and line sets must be installed at least five feet below grade or 1½ feet below the frost line, whichever is deeper. | Provide photos with scale reference showing the depth below grade of installed manifolds and line sets. | Major | IGSHPA 2016 Standards, Sec 7A.2.3 | Manifolds or line sets were found to be installed above the mandated depth. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Direct Exchange design compliance | Cathodic protection of the well meets NYSERDA requirements. | Mark "N/I" if direct exchange tubing was not used. Direct exchange wells require cathodic protection ensuring a minimum expected well life of 20 years. | Provide photos showing the cathodic protection system installed for direct exchange systems. | Minor | Program Manual (p. 9, Direct Exchange GSHP System Requirements) | The installation was found to have inadequate or no cathodic protection. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Pond or Lake Loop design compliance | Proper materials and procedures were taken as specificed by the manufacturer. | Mark "N/I" if a pond or lake loop systems was not used. On pond or lake loop systems it is necessary to observe the directions from the system manufacturer governing loop installation procedures. These must be provided for the reviewer to determine compliance, as well as the design drawings. | Provide photo evidence that the appropriate materials and procedures have been used as specified by the manufacturer. All critical features must have corresponding photo evidence for verification purposes. | Major | IGSHPA 2016 Standards, Sec 2C; NYS MC 304.1 | The pond or lake loop system was found to have installed features which vary significantly from the design or the directions of the system manufacturer. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Loop Circuiting /Pumping Power | Circuit and pipe sizing are consistent with design specifications. | The number of circuits and pipe sizes for combining circuits should be consistent with the design or the new loop layout must have approximately the same pressure drop characteristics. | Photos from the loop fields requested elsewhere will show the variance of the installation from the design. Provide photo documentation of as-built conditions to support significant design changes that may impact operation of the system, or rebate. | Major | Program Manual (p.7: Pumping power requirements) | The installed configuration of the ground-loop heat exchanger differs from the design, has excessive pressure drop, and will use more pumping energy. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Design Compliance | Well Layout - Setbacks | Well layout setbacks conform with design specifications | A site survey is required to have been performed identifying all key site elements including structures, existing wells, septic systems, underground services, etc. Verify that any required setbacks to relevant elements have been observed. | Photos should show the well in question and the element with which a setback violation exists. A visual measurement reference should be included demonstrating the deficiency. | Major | CSA 448.6.4.4 | Setbacks from the following site elements have not been adequately maintained: ___________________________________________________________________
Design Compliance | Ground Loop - Setbacks | Ground loop installation setbacks conform with design specifications | Ground loop installations must maintain defined setbacks to foundations, water lines, rainage zones, water wells , septic systems, collection basins and trees. | Photos should show the well in question and the element with which a setback violation exists. A visual measurement reference should be included demonstrating the deficiency. | Major | CSA448.8.4.1.2: a,b,c. | Setbacks from the following site elements have not been adequately maintained: ___________________________________________________________________
Procedures | Pipe Fusing | Joints and fittings comply with piping manufacturer and IGSPHA requirements. | All types of joints and fittings used in the loop field installation must comply with the piping manufacturer's and IGSPHA requirements. Properly fused joints should be in proper alignment, have complete and properly sized melt beads, and be free of cracks, voids, gaps and separations. | Provide photos of a number of fused joints with sufficient resolution, and detail, to show the melt beads and alignment between the joined surfaces. Represent joints for all sizes of piping and all joint types used in the installation. | Major | Program Manual (p. 10, para. 8); IGSPHA 2016 Standards Sec. 1C.2; NYS MC 304.1 | Irregularities are observed in the fusion joints found __________________, or damage was observed in the piping or fitting found _______________. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Grouting Procedures | Grouting materials were mixed and applied properly. | Mark "N/I" if a closed-loop vertical and horizontal (bored) system was not used. Grouting materials must be mixed according to the manufacturer's directions and applied in compliance with approved IGSHPA procedures. | Provide photos showing the grouting procedure. | Major | IGSPHA 2016 Standards Sec 2B.1 and 2B.2 | The application techniques did not comply with the IGSHPA procedures, risking voids and discontinuity of thermal transfer. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Horizontal Boreholes | Borehole drilling procedures prevented formation of air pockets. | Mark "N/I" if a closed-loop horizontal (bored) system was not used. Horizontal boreholes must have water injected in the holes as the drill pipe is withdrawn to prevent the formation of air pockets when the loop is pulled in. | Provide photos showing the horizontal boreholes as the drill pipe is withdrawn from the holes and photos of the procedures used to prevent the formation of air pockets. | Minor | IGSHPA 2016 Standards, Sec 2B.2 and 7B.3 | It was not observed or shown that an approved procedure for preventing air pocketing was used when finishing the horizontal borehole loop installations. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Nitrogen Brazing | Direct exchange tubing must be joined using a nitrogen purge during the brazing process | Mark "N/I" if direct exchange tubing was not used. Direct exchange tubing must be joined using a nitrogen brazing process. | Applicable to direct exchange tubing only. Provide photos showing: - a sampling of brazed joints connecting tubing and component - a label of the brazing alloy used to ensure compliance with IGSHPA requirements - the nitrogen brazing equipment and process. | Major | IGSHPA 2016 Standards, Sec 7A.4 | The required procedure was not followed for making joints in the direct exchange tubing. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Piping installation | Horizontal piping and connection location is detectable | Means must be provided for proper underground detection of the buried piping system. At minimum, metalic detectable tape must be placed 1 to 2 feet above horizontal piping circuits. Verify that the location of underground connections has been recorded and is available to be seen. | Show photos of the metallic detectable tape installed prior to final backfill | Minor | IGSHPA-2016 Section 5C; CSA 448.6.1.3; CSA 448.7.6.4.3; CSA 448.8.6.4.1 | It has not been shown that the underground piping has been adequately marked, and the record of underground connections was not available to be seen
Procedures | Piping installation | Piping is in good condition. | Piping should be kept free from damage, debris and foreign matter in the process of installation. | Provide a sequence of photos to show the consistency of the placement of loops in the trench across the entire loop field installation. Show details at all trench corners to demonstrate that appropriate bend ratios for the size of piping has been maintained. Provide photos of any compromised conditions found during the site inspection, any buried piping passing through wall surfaces showing the sleeving assembly and the interface between the buried pipe and the sleeve, and the installed insulation with identifying product label and R-value. | Minor | Program Manual (TBD) | Damage to piping was observed __________ , or debris was seen to have entered piping _______________. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Piping installation | Horizontal piping bend ratios are appropriate. | Mark "N/I" if a horizontal piping system was not used. Appropriate bend ratios for the size of piping must be maintained at corners and transitions. |  | Minor | IGSHPA 2016 Standards, Sec 2A.1 | The piping is installed tight to the corners of the trench, and is bent too tightly __________. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Piping installation | Only applicable if photo inspection report is submitted after loop field connection to building Buried piping through wall surfaces included sleeving. | Buried piping passing through wall surfaces must be protected by a sleeve, and the interface between pipe and sleeve must be properly sealed. | Provide photos shwing piping passing through wall has a sleeve and interface between pipe and sleeve are properly sealed | Incidental | IGSHPA 2016 Standards, Sec 3A.1 | The piping passing through the wall is not protected by a sleeve, or the piping has not been adequately sealed to the sleeve. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Piping installation | Only applicable if photo inspection report is submitted after loop field connection to building Buried piping with antifreeze are properly insulated when required by IGSHPA. | Buried piping in systems with antifreeze passing parallel within five feet of any wall, structure or water pipe must be insulated with R2 minimum closed cell insulation. | Provide photo showing pipe insulation has minimum R-2 value closed cell | Incidental | IGSHPA 2016 Standards, Sec 2A | The buried piping passing parallel within five feet of a wall, structure, or water pipe has not been adequately insulated. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Buried Manifolds | Manifolds installed underground or in a buried enclosure include proper valves, pressure, and temperature ports. |  | Provide photos showing the critical components listed. | Minor | Program Manual (p. 17, General Requirements) | The buried manifold has not been provided with the following component(s) or has been provided with the following improper component(s): _________________________. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Backfilling | Proper precautions taken prior to backfilling loopfield. | Mark "N/I" if a horizontal-loop system was not used. Care must be taken when backfilling ensuring that the piping is protected from damage, and procedures are used to assure the elimination of air pockets around the pipes. | Provide photos to demonstrate procedures taken to prevent damage to piping before backfilling, and to assure the elimination of air pocketing around the pipe. | Minor | IGSHPA 2016 Standards, Sec 2A.2, NYS Plumbing Code SECTION 306 | It was not documented that a screening procedure was used to remove potentially damaging rocks prior to back filling, or that an approved procedure was used for eliminating air pockets around the installed piping. | The photo(s) submitted did not provide enough information to determine compliance with the task requirement. Submit additional, high resolution photos and provide the proper detail.
Procedures | Disinfection Wells | Only applicable if photo inspection report is submitted after loop field connection to building Wells have been disinfected as required by IGSHPA | Verify that the wells beeen disinfected as required by IGSHPA | Photo of Disinfection apparatus | Minor | CSA 448.6.4.5.8 | There is no evidence that the wells have been disinfected. Revisit required disinfection.
Note on I1: apv: Ryan, is it possible to add these canned descriptions when N/I is checked in a PHOTO inspection only? If you recall, there is a need to send the contractor/builder a Could Not Verify report when there is at least one task marked as N/I.

## Loop Field_Field Ins
Category | Measure | Task | Task Hover Description | Defect Category | Code Reference | Canned Failure Description
Materials | Piping Materials | Piping on systems other than Direct Exchange must be HDPE and correspond to the design specifications. Direct Exchange piping must conform to ASTM B280. | Piping on systems must be HDPE, or B280 copper, and correspond to the design specifications. | Major | Program Manual (p. 10, para. 8), IGSPHA 2016 Standards Sec. 1C.2 | The piping material used ____________________. This is non-compliant with the design specifications or the NYSERDA requirements.
Materials | Grouting Materials | Grouting materials conform with design specifications and NYSERDA requirements. | Mark "N/I" if not inspecting a closed-loop vertical or horizonally bored system. Grouting materials used must conform with the design specifications and meet or surpass IGSHPA 2016 requirements. The hydraulic conductivity of the grouting mixture must be independently verified by a laboratory. | Major | IGSHPA 2016 Standards, Sec 2B.1.2, PM | The grout and admixture(s) used are not consistent with the design specifications, are incompatible with each other, or conductivity has not been independently verified.
Materials | Storage of Materials | Materials on-site are stored properly. | Piping must be stored on-site in a manner that prevents damage and the introduction of foreign matter. Grouting and admixtures must be received and stored in a way that protects them from moisture and contamination. | Minor | Program Manual (TBD) | Dirt and debris were seen to have entered the piping, or the silica admixture has been exposed to wet conditions.
Compliance | Design Compliance | Well layout setbacks conform with design specifications | A site survey is required to have been performed identifying all key site elements including structures, existing wells, septic systems, underground services, etc. Verify that any required setbacks to relevant elements have been observed. | Major | CSA 448.6.4.4 | Setbacks from the following site elements have not been adequately maintained: ___________________________________________________________________
Compliance | Design Compliance | Ground loop installation setbacks conform with design specifications | Ground loop installations must maintain defined setbacks to foundations, water lines, rainage zones, water wells , septic systems, collection basins and trees. | Major | CSA448.8.4.1.2: a,b,c. | Setbacks from the following site elements have not been adequately maintained: ___________________________________________________________________
Compliance | Design Compliance | Well field footprint and borehole spacing meet design specifications. | Mark "N/I" if a closed-loop vertical systems was not used. The installed well field should be consistent with the latest approved drawings in shape and dimension, and the spacing of the boreholes must match the design specifications within reasonable tolerances. | Major | Program Manual (p. 8: Well/Borehole Requirements) | The installed well field varies significantly from most recently approved drawings, or the spacing between some boreholes is too small.
Compliance | Design Compliance | Horizontal loop field conforms with the design drawings. | Mark "N/I" if a horizontal-loop system was not used.The installed horizontal loop field must conform with the design drawings in overall dimension, circuit quantity, spacing, and be installed below frost line. | Major | Program Manual (p.8, Horizontal-Loop Project Requirements) | The installed horizontal loop field varies significantly from the most recent approved drawings in ____________________, or sections of the loop field were ___ found to be installed above the frost line.
Compliance | Design Compliance | Standing column open-loop system bleed provision is compliant with design. | Mark "N/I" if an open-loop (standing column well) sytem was not used. Standing column open-loop systems must include a bleed circuit, drywell, or locally approved receptor. | Major | Program Manual (p.8, Open-Loop Project Requirements) | The installed system was not found to have an approved receptor or NYSERDA-compliant bleed provision.
Compliance | Design Compliance | Manifold and line sets installation meet IGSHPA requirements. | Mark "N/I" if direct exchange tubing was not used. Manifolds and line sets must be installed at least five feet below grade or 1½ feet below the frost line, whichever is deeper. | Major | IGSHPA 2016 Standards, Sec 7A.2.3 | Manifolds or line sets were found to be installed above the mandated depth.
Compliance | Design Compliance | Cathodic protection of the well meets NYSERDA requirements. | Mark "N/I" if direct exchange tubing was not used. Direct exchange wells require cathodic protection ensuring a minimum expected well life of 20 years. | Minor | Program Manual (p. 9, Direct Exchange GSHP System Requirements) | The installation was found to have inadequate or no cathodic protection.
Compliance | Design Compliance | Proper materials and procedures were taken as specificed by the manufacturer. | Mark "N/I" if a pond or lake loop systems was not used. On pond or lake loop systems it is necessary to observe the directions from the system manufacturer governing loop installation procedures. These must be provided for the reviewer to determine compliance, as well as the design drawings. | Major | IGSHPA 2016 Standards, Sec 2C; NYS MC 304.1 | The pond or lake loop system was found to have installed features which vary significantly from the design or the directions of the system manufacturer.
Compliance | Design Compliance | Circuit and pipe sizing are consistent with design specifications. | The number of circuits and pipe sizes for combining circuits should be consistent with the design or the new loop layout must have approximately the same pressure drop characteristics. | Major | Program Manual (p.7: Pumping power requirements) | The installed configuration of the ground-loop heat exchanger differs from the design, has excessive pressure drop, and will use more pumping energy.
Procedures | Pipe Fusing | Joints and fittings comply with piping manufacturer and IGSPHA requirements. | All types of joints and fittings used in the loop field installation must comply with the piping manufacturer's and IGSPHA requirements. Properly fused joints should be in proper alignment, have complete and properly sized melt beads, and be free of cracks, voids, gaps and separations. | Major | Program Manual (p. 10, para. 8); IGSPHA 2016 Standards Sec. 1C.2; NYS MC 304.1 | Irregularities are observed in the fusion joints found __________________, or damage was observed in the piping or fitting found _______________.
Procedures | Grouting Procedures | Grouting materials were mixed and applied properly. | Mark "N/I" if a closed-loop vertical and horizontal (bored) system was not used. Grouting materials must be mixed according to the manufacturer's directions and applied in compliance with approved IGSHPA procedures. | Major | IGSPHA 2016 Standards Sec 2B.1 and 2B.2 | The application techniques did not comply with the IGSHPA procedures, risking voids and discontinuity of thermal transfer.
Procedures | Horizontal Boreholes | Borehole drilling procedures prevented formation of air pockets. | Mark "N/I" if a closed-loop horizontal (bored) system was not used. Horizontal boreholes must have water injected in the holes as the drill pipe is withdrawn to prevent the formation of air pockets when the loop is pulled in. | Minor | IGSHPA 2016 Standards, Sec 2B.2 and 7B.3 | It was not observed or shown that an approved procedure for preventing air pocketing was used when finishing the horizontal borehole loop installations.
Procedures | Nitrogen Brazing | Direct exchange tubing must be joined using a nitrogen purge during the brazing process | Mark "N/I" if direct exchange tubing was not used. Direct exchange tubing must be joined using a nitrogen brazing process. | Major | IGSHPA 2016 Standards, Sec 7A.4 | The required procedure was not followed for making joints in the direct exchange tubing.
Procedures | Piping installation | Piping is in good condition. | Piping should be kept free from damage, debris and foreign matter in the process of installation. | Minor | Program Manual (TBD) | Damage to piping was observed __________ , or debris was seen to have entered piping _______________.
Procedures | Piping installation | Horizontal piping and connection location is detectable | Means must be provided for proper underground detection of the buried piping system. At minimum, metalic detectable tape must be placed 1 to 2 feet above horizontal piping circuits. Verify that the location of underground connections has been recorded and is available to be seen. | Minor | IGSHPA-2016 Section 5C; CSA 448.6.1.3; CSA 448.7.6.4.3; CSA 448.8.6.4.1 | It has not been shown that the underground piping has been adequately marked, and the record of underground connections was not available to be seen
Procedures | Piping installation | Horizontal piping bend ratios are appropriate. | Mark "N/I" if a horizontal piping system was not used. Appropriate bend ratios for the size of piping must be maintained at corners and transitions. | Minor | IGSHPA 2016 Standards, Sec 2A.1 | The piping is installed tight to the corners of the trench, and is bent too tightly __________.
Procedures | Piping installation | Buried piping through wall surfaces included sleeving. | Buried piping passing through wall surfaces must be protected by a sleeve, and the interface between pipe and sleeve must be properly sealed. | Incidental | IGSHPA 2016 Standards, Sec 3A.1 | The piping passing through the wall is not protected by a sleeve, or the piping has not been adequately sealed to the sleeve.
Procedures | Piping installation | Buried piping with antifreeze are properly insulated when required by IGSHPA. | Buried piping in systems with antifreeze passing parallel within five feet of any wall, structure or water pipe must be insulated with R2 minimum closed cell insulation. | Incidental | IGSHPA 2016 Standards, Sec 2A | The buried piping passing parallel within five feet of a wall, structure, or water pipe has not been adequately insulated.
Procedures | Buried Manifolds | Manifolds installed underground or in a buried enclosure include proper valves, pressure, and temperature ports. |  | Minor | Program Manual (TBD) | The buried manifold has not been provided with the following component(s) or has been provided with the following improper component(s): _________________________.
Procedures | Backfilling | Proper precautions taken prior to backfilling loopfield. | Mark "N/I" if a horizontal-loop system was not used. Care must be taken when backfilling ensuring that the piping is protected from damage, and procedures are used to assure the elimination of air pockets around the pipes. | Minor | IGSHPA 2016 Standards, Sec 2A.2, NYS Plumbing Code SECTION 306 | It was not documented that a screening procedure was used to remove potentially damaging rocks prior to back filling, or that an approved procedure was used for eliminating air pockets around the installed piping.
Procedures | Flushing and Purging | Proper flushing and purging procedures were taken. | Each supply and return circuit in the loop field must be flushed in compliance with IGSHPA requirements, and the assembly must be purged to remove any air from the system. Purging for the loop field must be done separately from the purging of the inside system. | Major | IGSHPA 2016 Standards, Sec 1E.2 | The following deficiencies were observed in the conducting of the flushing and purging: ___________________________________
Procedures | Pressure Testing | Loop circuits and the entire field assembly must be pressure tested with water in accordance with mandated procedures. | Loop circuits and the entire field assembly must be pressure tested with water in accordance with mandated procedures. | Major | ASTM F2164 and NYS MC 1210.10., PM p. 13, Milestone # 2, IGGSHPA 2016 Standards Sec 1E.5 to 1E.7, CSA 448.8.13.1 | The following deficiencies were observed in the conducting of the pressure testing: ___________________________________
Procedures | Flow Rate and Pressure Drop | Flow rates and pressure drop measurements meet calculated design values. | Flow rates and pressure drop for the loop field must be measured and compared with calculated design values. | Major | IGGSHPA 2016 Standards Sec 1E.3 | Measured flow rates and pressure drop varies from the calculated design values by more than 10%.
Procedures | Disinfection Wells | Wells have been disinfected as required by IGSHPA | Verify that the wells beeen disinfected as required by IGSHPA | Minor | CSA 448.6.4.5.8 | There is no evidence that the wells have been disinfected. Revisit required disinfection.
Procedures | Equipment and Accessories | Equipment and accessories are installed to professional standards |  | Incidental | Program Manual p. 5 | The following is not installed in to a professional standard:________________. The deficiency noted is: ________________________

## Post Install_Field Ins
Item # | Category | Measure | Task | Task Hover Description | Code Reference | Defect Category | Canned Failure Description
1 | Administrative | System Documentation | As-built records are detailed and complete | Mark "N/I" if inspecting a system less than 10 tons. | IGSHPA 5.B | Incidental | Detailed as-builts were not prepared for this system. Correct on future projects.
2 | Administrative | System Documentation | Commissioning report is complete and/or Manufacturer start-up sheets submitted | Commissioning report and demonstration of start-up (completed commissioning report or manufacturer start-up sheets) were submitted and complete. | Program Manual page 12 & 13 | Major | The commissioning report and/or manufacturer start-up sheet is lacking the following items: - _____ Correct then resubmit.
3 | Administrative | System Documentation | Leakage test reports were furnished and are complete for ground heat exchanger piping, including pipe to well and surface water as applicable. | IGSHPA and Codes require the GSHP Loop to be pressure tested. Reports of this testing should be provided for all systems. IRC M2105.28 states, in part; the assembled loop shall be pressure tested with water at 100 psi (689 kPa) for 15 minutes without observed leaks. Manufacturers may have more stringent requirements. Dx systems addressed elsewhere. | IGSHPA 1E; IRC M2105.28 | Minor | The leakage test reports are missing or incomplete. Correct then resubmit.
4 | Administrative | System Documentation | The owner received all required documentation, including Operations Manual. The owner was educated on all required maintenance and maintenance schedule. | Manual includes a design and operation overview, equipment submittals or description of all major components of system, start-up/commissioning report, warranty information, and operation and maintenance procedures with maintenance schedule. The owner understands how to operate and maintain the system. | IGSHPA Sections 3C.3, 5.B; Program Manual | Incidental | The following information is missing from the Operations manual: - __________________ Correct then resubmit.
5 | Administrative | System Documentation | Tag heat pump, piping and electrical panels. Adhere to IMC labelling requirements. | Mark "N/I" if inspecting a system less than 10 tons. |  | Incidental | Labels are missing from the following equipment:__________. Correct then resubmit.
6 | Administrative | System Documentation | Notice / informational packet includes all required documentation and is attached to or located in DX heat pump unit | Notice / informational packet must be attached to heat pump unit detailing: - loop field refrigerant content, type, and volume - loop location description - loop piping material - required maintenance schedule on loop field, refrigerant, and heat pump - planned decommissioned data and process | Program Manual pg. 9 - par 1 - f. | Minor | System notice / informational packet has not been installed. Install notice / informational packet and resubmit.
7 | Administrative | System Documentation | Dx Replacement - pressure/flow and seal test report were submitted |  | CSA 448.8.10 | Major | Flow or Seal Test reports have not been provided. Perform the tests required by IGSHPA
8 | Administrative | System Documentation | Dx final pressure test and evacuation | Review pressure test report and evacuation report for completed Dx system at at least 165 psi and an evacuation of at least 250 µm, or other test levels required by the manufacturer. | CSA 448.8.14.1.1 | Major | Adequate documentation for the pressure test of the completed Dx system has not been provided. Perform the test and transmit test report.
9 | Administrative | Owner Education | The owner was educated on basic operations of the system | The owner understands basic system operation including the operation and adjustment of dampers, valves, and controls. The owner knows how to program controls and thermostats, understands health and safety aspects, and can verify if system is performing correctly. | IGSHPA 3C.2 | Incidental | The owner/building operator does not understand the system operation. Please provide training.
10 | Equipment | Manifold | Purge and isolation valves are installed as per design or manufacturer'a installation manual. |  | IGSHPA 3.A.3.6 & 3.A.3.7 | Major | Purge/isolation valves are missing or improperly located. Install as per design or manufacturer's installation manual, then resubmit
11 | Equipment | Manifold | Flow (pressure) and temperature-sensing ports are installed properly | Flow (pressure) and temperature-sensing ports are installed for waterside testing. | IGSHPA 3.A.4.2 | Minor | Please install flow/temperature sensor ports at the following locations: - _____ Complete the installation then resubmit.
12 | Equipment | Manifold | Loop charging valve handles were removed and/or ports were plugged | Handles for loop charging valves are removed, and/or ports are plugged to prevent accidental fluid discharge. | IGSHPA 3.A.4.3 | Minor | Handles for loop charging valves have not been removed. Remove and store in a safe place. The following ports have not been plugged to prevent fluid discharge: - _______________ Correct then resubmit.
13 | Equipment | Interior Piping | Loop field pipes and valves are insulated per design, manufacturer's and IGSHPA requirements. | Check insulation type/r-values GSHP system pipes and valves are insulated where condensation may occur. | IGSHPA 3.A.3.8; 3A.2.3 | Minor | Install missing or incorrect pipe/valve insulation at the following locations: - _______________ Correct then resubmit.
14 | Equipment | Interior Piping | Transitions between dissimilar piping materials are located inside and accessible |  | IGSHPA 3.A.4.4 | Major | The transitions between dissimilar piping materials located outside are incorrect. The system must be partially drained and piping replaced. Correct then resubmit.
15 | Equipment | Interior Piping | Pipe supports and spacing conform to code | Both the MC and RC have Code required support spacing. | NYS RC 2101; NYS MC 305 | Incidental | Pipe supports and associated spacing do not conform to the Code. Correct then resubmit.
16 | Equipment | Interior Piping | Distribution piping and associated insulation is installed per design, manufacturer and IGSHPA requirements. | This is for the pipe size and type, and associated insulation, on the piping from the HP to the building terminal devices. This applies to HPs providing hot or chilled water. If the heat pump is located in a conditioned space, then insulation is not required on desuperheater or radiant heating piping. | NYS ECCC Section 403.2.10; NYS RC 1103 | Incidental | Install missing pipe/valve insulation at the following locations: - _______________ Correct then resubmit.
17 | Equipment | Interior Piping | Pipe penetrations of wall and ceiling have been properly firestopped | Mark "N/I" if inspecting a system less than 10 tons. Verify pipe penetrations of rated walls and ceilings have been firestopped with a listed assembly. | Building Code 714 | Minor | There is insufficient evidence that a listed firestopping assembly has been installed at pipe penetration of rated walls. Correct then resubmit.
18 | Equipment | System Circulation Loop | Pumps and flow centers are installed as per design and manufacturer's requirements. |  | IGSHPA 3.A.3.5 | Major | Pumps and flow centers not installed per design and manufacturer's requirements. Install _____ hp pump as called for in the design then resubmit.
19 | Equipment | Heat Pump | Proper access has been provided around the heat pump | Verify that access has been provided around the heat pump per NYS MC and the installation instructions. | NYS RC 1401; NYS MC 306 | Incidental | Maintenance access was provided on the design drawings but is not persent in final design. Future installations must include proper access for maintenance.
20 | Equipment | Heat Pump | Capacity and efficiency of all heat pumps meet the design document AHRI ratings | Confirm that the heat pump models installed match the submitted documents. | Program Manual - page 6 | Major | The installed heat pumps do not meet the capacity/ efficiency specified in the approved design. Correct then resubmit.
21 | Equipment | Heat Pump | Proper strainer installed at inlet of all heat pumps or other means of particle removal was used | Mark "N/I" if inspecting a system less than 10 tons. A strainer is installed at inlet of all heat pumps (and brazed plate Hx if provided). Spot check strainers to ensure screens were cleaned by the installing contractor. Request the applicant to measure the pressure differential across the strainer(s) as part of start-up and repeat during the inspection. If there are a large number of strainers, take a sample approach. | IGSHPA 3.A.4.8 | Minor | A strainer is not installed, or they have not been cleaned. Install/clean strainers to prevent reduction in system flow rate.
22 | Equipment | Heat Pump | If an expansion tank is provided, is it installed as per design and is air side pressure properly adjusted | Request the installer to record the pressure applied to the tank and the inspector will confirm by taking a reading of just the line pressure. A deficiency arises if the tank pressure was less than the line. | IGSHPA 3.A.4.6 | Major | Expansion tank pressures should be adjusted to cold fill pressure or the tank is too small. Correct then resubmit.
23 | Equipment | Heat Pump | Air separator is installed as per design | Mark "N/I" if inspecting a system less than 10 tons. | IGSHPA 3.A.4.7 | Minor | Air separator does not conform to the design requirements.
24 | Equipment | Heat Pump | Adequate provision for condensate removal is made. | Confirm that condensate removal is present as per design or installation manual, and is draining to a suitable place | NYS MC 307.2.3; NYS RC M1411.3 | Minor | Adequate provisions have not been made for condensate removal on heat pump(s). Please install operational and code compliant condensate removal prior to system operation.
25 | Equipment | Heat Pump | Controls are functioning properly and include features specified in the design | For small systems: use the thermostat, check each mode - heating, cooling, auxiliary (if present) | Program Manual page 13 - Startup; NYS RC N1103.1; NYS ECCC C403.2, R403 | Major | The installed controls do not meet the design requirements. Deficiencies: - __________ Correct then resubmit.
26 | Equipment | Electrical | System is properly grounded per the design | Check that ground is properly connected within the heat pump unit and running to the panel. | NEC | Major | The system has not been grounded per system design. Install ground system prior to operating the system then resubmit.
27 | Equipment | Electrical | The maximum overcurrent protection size is appropriate for the maximum circuit capacity | If deficiency exist provide table with overcurrent device number, installed size, and recommended size. | NEC | Critical | Overcurrent protection is oversized. Operation with these devices in place is a potential hazard. Please see the table below for overcurrent device number, installed size and recommended size. Correct then resubmit.
28 | Equipment | Electrical | Suitable disconnect is provided for pump and heat pump and auxiliary |  | NEC | Major | Disconnects have not been provided for pumps/heatpumps and auxiliary per design requirements. Do not operate the system until these disconnects are installed and properly labeled. Correct then resubmit.
29 | Equipment | Buffer Tank | Water to water systems sizing and provisions conform to design and manufacturer's requriements | On Water to Water Systems, verify provisions for and the sizing of the Buffer Tank conforms to Design/HP manufacturer's requirements. | Program Manual, page 8 (page 12 of draft 2.0) | Minor | The buffer tank sizing is inconsistent with acceptable practices. Please review and revise.
30 | Equipment | Equipment and Accessories | Equipment and accessories are installed in a workmanlike manner |  | Program Manual p. 5 | Incidental | The following is not installed in a workmanlike manner ________________.
31 | Testing | Performance Testing | Auxillary heat functions properly | If practicable, verify operation of the auxiliary heat (if present). Also, ensure supplemental electric resistant heat does not operate when heat pump has capacity to handle the load. | (PM) page 12 & 13; ECCC R403.1.2, C403.2.4.1.1 | Minor | System auxilliary heat does not operate. Repair this system and resubmit.
32 | Testing | Performance Testing | Water temperatures, pressure readings, and/or flow rates were recorded during start-up and submitted | Liquid or water temperatures and/or flow rates must be checked and recorded during start-up. These should be on the manufacturers' start-up and/or commissioning report. | Program Manual | Minor | The following liquid flow rates and/or temperatures are missing from the test and balance report. Correct then resubmit.
33 | Testing | Performance Testing | Air temperatures, air pressures and/or flow rates were recorded during start-up and submitted (Water to Air HPs) | Air temperatures, pressures and/or flow rates must be checked and recorded during start-up. These should be on the manufacturer's start-up and/or commissioning report. | Program Manual | Minor | The following air flow rates and/or temperatures are missing from the test and balance report. Correct then resubmit.
34 | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED | RESERVED
35 | Testing | Performance Testing | Open system well flows meet ANSI/CSA/IGSHPA requirements | Verify that the well flow tests occured as required by ANSI/CSA/IGSHPA | CSA 448.6.7 | Major | Provide test report for well flow tests required by aNSI/CSA/IGSHPA for Open systems.
36 | Testing | Performance Testing | Standing column well tests have been performed and test test report has been submitted | Verify that well draw down tests have been performed for SCW systems. | CSA 448.7.4.6 | Major | Provide test report for well flow tests required by IGSHPA for Standing Column Wells.
37 | Testing | Anti-freeze additives | Anti-freeze type and concentration meets IGSHPA requirements | Propylene glycol (CAS No. 57-55-6), methanol (CAS No. 64-56-1), and ethanol (CAS No. 64-17-5) are acceptable. Verify one of these is specified and its design concentration. Verify the Program Manual requirements are being met. Specifically: Large systems with ethanol and methanol must comply with Section 1207 of the 2015 International Mechanical code and all systems must comply with section 3d.2.4 of the IGSHPA Design and Installation Standard. Therefore, loops must maintain a minimum temperature differential between the loop and the flash point of the antifreeze solution of 50 degrees at all times.The maximum allowable concentration of methanol is 12.5% by weight. The maximum allowable loop field temperature in Small System using methanol as an antifreeze is 75 degrees F. In addition, the designer and installer should ensure that the loop field operating temperature is at least 50 degrees lower than the flash point of methanol at all times.The maximum allowable concentration of ethanol is 10% by weight. The maximum allowable loop field temperature in Small System using ethanol as an antifreeze is 70 degrees F. In addition, the designer and installer should ensure that the loop field operating temperature is at least 50 degrees lower than the flash point of ethanol at all times. | IGSHPA 3D.2.4.3 | Major | Anti-freeze type or concentration is inconsistent with the design. Correct and resubmit.
38 | Testing | Anti-freeze additives | Confirmation from installer that pipe systems containing Propylene glycol have beeen disinfected prior to filling | Mark "N/I" if inspecting a system less than 10 tons. | Program Manual, p. 13; Milestone #2 | Major | Resubmit with documentation that loop field piping/ancillary equipment has been disinfected; or remove fluid, disinfect, flush and install clean fluid.
39 | Testing | Anti-freeze additives | Pipe systems containing Kilfrost have beeen disinfected prior to filling | Mark "N/I" if inspecting a system less than 10 tons. Review documentation that ground heat exchanger piping was disinfected. | mfg requirement | Major | Resubmit with documentation that loop field piping/ancillary equipment has been disinfected; or remove fluid, disinfect, flush and install clean fluid.

## Documents Needed for Review
Documents needed for GSHP Design Review
Both
Bore/Well Field Plans.
Documented source for soil thermal value.
Equipment schedules
Piping schematic(s) for piping in loop field.
Refrigeration and corrosion protection specification for DX systems.
Specifications for all GSHP system elements. Minimally, this includes HP, loop piping, non-loop piping, pipe insulation, pump assemblies, water treatment, glycol, grout, trenching, drilling, underground structures.
Electrical drawings showing all electric work for GSHP system.
Heating load calculations.
Cooling load calculations.
Above Grade Mechanical Plan and Details.
Field Heat Exchanger Calculations (Small). This includes EWT, LWT, Pressure Drop, Flow rate, pump sizing. If wells, provide water depth and other relevant information
Provide Modeling for all Horizontal Systems
As-Built Drawings (large systems (CLOSED LOOP OR DX), and all Open Loop & SCWs regardless of size)
Dx- Replacements - Flow, Pressure and Seal Test Report
Report of Open Loop Flow Tests or Standing Column Well Draw Down Tests
Water sample test report and quality analysis for closed loop systems (unless only using municipal water), all Open Systems, and all Standing Column Well systems.
Large
GSHP system control schematic and sequence of operations.
Piping schematic(s) for GSHP system(s) Detail/specification for firestopping of through penetrations if fire rated construction exists on project
Loop/Site Plan Loop Sizing Report (flexible) Loop Field Pressured Drop Calculations < 30 tons; source of conductivity data
Plumbing drawings showing water make-up to GSHP system.
Large (>30 Ton)
Provide conductivity test result.
Large (>75 Ton)
Provide documents demonstrating compliance with ASHRAE 15 (Chapter 11 NYS MC)

## Minimum Required Photos
Item # | Loop Type | Description
General
1 | All | Overall heat pump
2 | All | Connection between the flow center and loop field
3 | All | Pipe connections at Heat Pump
4 | All | Duct connections to heat pump (if applicable)
Loop Field
5 | All | Photos showing any variance of the installation from the design
6 | All | Manufacturer's stamp identifying the pipe material for all types of piping used in the installation
7 | All | Manufacturer's label identifying the grout product and identify the type and grade of admixture delivered, when grout is used.
8 | All | Location and storage conditions for all materials that are delivered to the site, including piping, grout, sand, additives, and other necessary system components that will be stored on site for more than one day
9 | All | Complete loop field area, with dimensional reference
10 | All | A number of fused joints with sufficient resolution and detail to show the melt beads and alignment between the joined surfaces. Represent joints for all sizes of piping and all joint types used in the installation.
11 | All | Backfilling operations
12 | All | Buried piping passing through wall (or floor) surfaces showing the sleeving assembly and the interface between the buried pipe and the sleeve
13 | All | The buried piping passing parallel within five feet of a wall, structure or water pipe has not been adequately insulated. Show insulation with identifying product label and R-value.
14 | All | Demonstrate procedures taken to prevent damage to piping before backfilling, and to assure the elimination of air pocketing around the pipe.
15 | Closed | Detail to show the number of boreholes and the distance between holes with a visual scale reference. N/A for horizontal trench.
16 | Closed | Sequence of photos to show the consistency of the placement of the loops in the trench across the entire loop field installation. Show details at all trench corners to demonstrate that appropriate bend ratios for the size of piping has been maintained.
17 | Closed | Underground Manifolds: Valves, pressure and temperature ports
18 | Closed | Top of borehole/top of grout
19 | Closed | Photos showing the grouting procedure
20 | DX | Photos with scale reference showing the depth below grade of installed manifolds and line sets.
21 | DX | Cathodic protection system
22 | DX | Sampling of brazed joints connecting tubing and components. Provide a photo showing a label of the brazing alloy used to ensure compliance with IGSHPA requirements. Include a photo showing the nitrogen brazing equipment and process.
23 | Horizontal | Horizontal fields: Detail to show the number of circuits and the layout of the loops in the trench, as well as the distance between loops. Show with scale reference the length of the loops and the overlap pattern if a "Slinky" installation if used. Show with scale reference the depth of the trench below grade .
24 | Horizontal | Photos showing the horizontal boreholes as the drill pipe is withdrawn from the holes and the procedures used to prevent the formation of air pockets
25 | Open | Standing Column: Location and features of the bleed provision
26 | Open | Photo of disinfection apparatus of wells
27 | Lake | Pond/Lake: Appropriate materials and procedures have been used as specified by the manufacturer. All critical features must have corresponding photo evidence for verification purposes