## Central Plant Sizing
Location | Buildling | Square Feet | Space Type | Peak Cooling | Annual ton-hrs | Annual Cooling | Peak Heating | Annual Heating
|  |  |  | (ton) |  | (kWh) | (kBtu/hr) | (MMBtu)
Downtown | Phase A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load Constant | 500
Downtown | Barclay Damon | 330000 | Large Office | 309.742 | 352221.5995 | 1238762.9524 | 3582095.5032 | 1460.7473 | Conversion | 15 | MBH per ton
Downtown | State Tower | 1200000 | Large Office | 1126.3346 | 1280805.8162 | 4504592.554 | 13025.8018 | 5311.8082
Downtown | Courtyard Marriott | 40000 | Hotel | 70.5436 | 52730.834 | 185454.2815 | 985.6521 | 1420.059
Downtown | US Social Security Admin | 287000 | Large Office | 269.3817 | 306326.0577 | 1077348.3858 | 3115.3376 | 1270.4075 | [8 empty] | Minimum Load Scenario - Inner Harbor First
Downtown | M&T Bank | 365000 | Large Office | 342.5934 | 389578.4358 | 1370146.9019 | 3962.0147 | 1615.675 | Cooling - Buildings |  |  |  | Winter | Loop LWT | 75 |  | Cooling - Buildings |  | Buidling COP | 3.5
Downtown | State Office Building | 360000 | Large Office | 337.9004 | 384241.7449 | 1351377.7662 | 3907.7405 | 1593.5425 | Peak Cooling | 10951.1026 | Tons |  |  | Loop EWT | 60 |  | Peak Cooling | 2366.7712 | Heat Add % | 71.43%
Downtown | SU-Warehouse | 72000 | Medium Office | 148.44 | 134233.0089 | 472097.335 | 1420.8084 | 1054.1906 |  | 131413.2316 | MBH |  |  | Building EWT | 68 |  |  | 28401.2539
Downtown | 300 S State St | 252910 | Large Office | 237.3844 | 269940.4991 | 949380.419 | 2745.2963 | 1119.5078 | Heat Rejection | 164266.5395 | MBH |  |  | Building LWT | 58 |  | Heat Rejection | 35501.5674
Downtown | Key Bank Building | 132000 | Large Office | 123.8968 | 140888.6398 | 495505.1809 | 1432.8382 | 584.2989 | Flow Required¹ | 27377.7566 | gpm |  | Summer | Loop LWT | 76 |  | Flow Required¹ | 5916.9279
Downtown | 100 East Washington St | 50000 | Midrise Apartment | 82.6823 | 31084.3225 | 109323.5258 | 929.809 | 1189.2121 | Design Cooling - Central Plant |  |  |  |  | Loop EWT | 88 |  | Design Cooling - Central Plant
Downtown | Ramboll | 137000 | Large Office | 128.5899 | 146225.3307 | 514274.3166 | 1487.1124 | 606.4314 | Peak Available⁴ | 30000 | gpm |  |  | Building EWT | 80 |  | Peak Available⁴ | 30000
Downtown | City Hall | 84555 | Medium Office | 174.3242 | 157639.8898 | 554419.3078 | 1668.5619 | 1238.0151 | % Load Covered | 109.6% |  |  |  | Building LWT | 90 |  | % Load Covered | 507%
Downtown | 1 Lincoln Center | 367500 | Large Office | 344.94 | 392246.7812 | 1379531.4697 | 3989.1518 | 1626.7413 | Heat Rejection¹ | 180000 | MBH |  | Outfall | Winter EWT | 50 |  | Heat Rejection¹ | 0
Downtown | SUNY Oswego MetroCenter | 185530 | Large Office | 174.1407 | 198023.2526 | 696447.5471 | 2013.8975 | 821.2498 | Cooling Load | 12000 | Tons |  |  | Winter LWT | 40 |  | Cooling Load | #DIV/0!
Downtown | 217 Montgomery St | 50000 | Medium Office | 103.0833 | 93217.3673 | 327845.3715 | 986.6725 | 732.0768 | Heating - Buildings |  |  |  |  | Summer EWT | 75 |  | Heating - Buildings
Downtown | City Hall Commons | 52957 | Medium Office | 109.1797 | 98730.2424 | 347234.1468 | 1045.0243 | 775.3718 | Peak Heating⁵ | 77500 | MBH |  |  | Summer LWT | 85 |  | Peak Heating⁵ | 28474.685
Downtown | Salinas Place | 50000 | Midrise Apartment | 74.8784 | 46126.9046 | 162228.2695 | 650.7799 | 903.4281 | Central Plant Needed Output | 60277.7778 | MBH |  | Building COP |  | 4.5 |  | Central Plant Needed Output | 0
Downtown | SU-Peck Hall | 25920 | Medium Office | 53.4384 | 48323.8832 | 169955.0406 | 511.491 | 379.5086 | Loop Flow² | 9176.1851 | GPM |  | Heat Add % |  | 77.78% |  | Loop Flow² | 4067.8121
Downtown | Phase B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Design Heating - Central Plant |  |  |  | HP COP (Central Plant) |  | 8.93 |  | Design Heating - Central Plant
Downtown | Atrium | 170000 | Large Office | 159.5641 | 181447.4906 | 638150.6118 | 1845.3219 | 752.5062 | Outfall Flow³ | 10705.5493 | GPM |  | Heat Add % |  | 88.8% |  | Outfall Flow³ | 4067.8121
Downtown | AXA Towers | 653177 | Large Office | 613.0799 | 697160.7505 | 2451913.5422 | 7090.1285 | 2891.2924 | Outfall Output | 53527.7467 | MBH | [5 empty] | Outfall Output | 0
Downtown | Hotel Syracuse | 720000 | Hotel | 1269.7841 | 949155.0126 | 3338177.0664 | 17741.7384 | 25561.0628 | CDH Output | 27220 | MBH | chiller output
Downtown | Tech Garden | 35550 | Medium Office | 73.2922 | 66277.5481 | 233098.0591 | 701.5242 | 520.5066 | Number of Units | 3
Downtown | Bank of America | 45000 | Midrise Apartment | 107.3384 | 40417.6807 | 142148.9355 | 1426.3099 | 1336.9322 | 1: Utilizing summer loop temperatures
Downtown | Clinton Exchange | 180000 | Large Office | 168.9502 | 192120.8724 | 675688.8831 | 1953.8703 | 796.7712 | 2: Utilizing winter loop temperatures
Downtown | National Grid | 511200 | Large Office | 479.8185 | 545623.2777 | 1918956.428 | 5548.9916 | 2262.8303 | 3: Utilizing winter outfall temperatures
Downtown | Post Standard | 179000 | Large Office | 168.0116 | 191053.5342 | 671935.056 | 1943.0154 | 792.3447 | 4: Estimated consistent peak diverted flow
Downtown | Galleries of Syracuse | 219000 | Large Office | 205.5561 | 233747.0615 | 822088.1411 | 2377.2088 | 969.405 | 5: 125% of design heating day average
Downtown | 100 Clinton Sq | 120000 | Large Office | 112.6335 | 128080.5816 | 450459.2554 | 1302.5802 | 531.1808
Downtown | City of Syr Criminal Court House | 95977 | Medium Office | 197.8726 | 178934.4652 | 629312.3044 | 1893.9573 | 1405.2507
Downtown | 550 Harrison Building | 252000 | Retail | 0 | 0 | 0 | 13489.1654 | 9975.473
Downtown | Jefferson Clinton Hotel | 42204 | Hotel | 74.4305 | 55636.303 | 195672.8124 | 1039.9616 | 1498.3043
Downtown | Sky Armory | 40700 | Medium Office | 83.9098 | 75878.937 | 266866.1324 | 803.1514 | 595.9105
Downtown | Clinton Plaza | 254690 | Midrise Apartment | 307.4038 | 111392.1426 | 391766.0348 | 2624.2339 | 5051.5213
Downtown | MOST | 40000 | Medium Office | 82.4667 | 74573.8938 | 262276.2972 | 789.338 | 585.6614 |  | QTY (N+1) | Flow | Head | bhp | Motor HP | kW Demand | Amps
Downtown | 600 Montgomery St | 36684 | Medium Office | 75.6302 | 68391.718 | 240533.5922 | 723.9019 | 537.1101 | Pupms - Outfall to Chillers | 4 | 7500 | 50 | 112 | 125 | 334.208 | 419.4676
Inner Harbor | Medical Office Bldg | 25056 | Retail | 0 | 0 | 0 | 1341.2084 | 991.847 | Pumps - DES Loop | 5 | 6000 | 110 | 195 | 300 | 727.35 | 912.9037
Inner Harbor | Phase C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Chillers | 4 |  |  |  |  | 1977.7413 | 2482.2815
Inner Harbor | Parcel 1 | 180000 | Medium Office | 453.6785 | 305260.3456 | 1073600.2776 | 5149.8606 | 4132.0969 | Elec Boiler | 1 |  |  |  |  | 8000 | 10040.8742
Inner Harbor | Parcel 2 | 120000 | Retail | 268.2646 | 146427.5484 | 514985.5159 | 3143.6724 | 2962.4298 |  | Sq ft | W/ft
Inner Harbor | Parcel 3 | 45000 | Midrise Apartment | 89.0471 | 33505.5749 | 117839.0676 | 1098.82 | 1188.7981 | Misc Systems | 20000 | 3 |  |  |  | 60 | 75.3066
Inner Harbor | Parcel 4 | 110000 | Retail | 245.9092 | 134225.2527 | 472070.0563 | 2881.6997 | 2715.5607 | [6 empty] | 3099.2993 | 3889.9593 | Total System (excluding electric boiler)
Inner Harbor | Parcel 5 | 30000 | Midrise Apartment | 59.3647 | 22337.0499 | 78559.3784 | 732.5467 | 792.5321 | System COP | 5.811
Inner Harbor | Parcel 6 | 225000 | Midrise Apartment | 271.5688 | 98406.8164 | 346096.658 | 2318.3188 | 4462.6498
Inner Harbor | Parcel 7 | 320000 | Retail | 715.3722 | 390473.4623 | 1373294.7092 | 8383.1264 | 7899.8129
Inner Harbor | Parcel 8 | 120000 | Midrise Apartment | 144.8367 | 52483.6354 | 184584.8843 | 1236.4367 | 2380.0799
Inner Harbor | Parcel 9 | 60000 | Midrise Apartment | 118.7295 | 44674.0998 | 157118.7567 | 1465.0933 | 1585.0642
Downtown | Parcel 10 | 160000 | Midrise Apartment | 193.1156 | 69978.1806 | 246113.179 | 1648.5823 | 3173.4399
|  | 11904002 |  | 14624.0048 | 0 | 0 | 7.0733 | MBH