## Hourly Calculations
District Central Plant Calculator
[7 empty] | MBH | MBH | MBH |  |  | MBH |  | MBH | MBH |  | kW | MBH | MBH | MBH |  | kW | [7 empty] | kW | kW | kW | kW | kW | MBH | MBH | [6 empty] | kW | kW | kW | kW | kW
Pick (Max) |  |  |  |  | Max |  | 18348.4894 | 19398.9563 | 19398.9563 |  |  | 16189.8436 |  | 16189.8436 | 0 |  | 0 | 23709.8354 | 23709.8354 | 0 |  | 0 | 3951.6392 | [6 empty] | 81.056 | 47.4351 | 0 | 0 | 94.8702 | 16520.2485 | 23235.6387 | 4647.1277 | [5 empty] | 15.6302 | 6.9926 | 0 | 15.6302 | 108.8554
Average |  |  |  |  | Avg |  | 1941.3269 | 1068.2936 | 1068.2936 |  |  | 1699.6597 |  | 1699.6597 | 0 |  | 0 | 1294.3552 | 1294.3552 | 0 |  | 0 | 1.5807 | [6 empty] | 18.6937 | 0.383 | 0 | 0 | 19.0767 |  |  | 600.5629 | [5 empty] | 8.1309 | 0.028455 | 0 | 8.1593 | 27.236
Annual Energy |  |  |  |  | Sum |  | 17006023.4722 | 9358251.8818 | 9358251.8818 |  |  | 14889018.9156 |  | 14889018.9156 | 0 |  | 0 | 11338551.2183 | 11338551.2183 | 0 |  | 0 | [7 empty] | 163756.9777 | 3355.0953 | 0 | 0 | 167112.073 |  |  | 5260931.3277 | [5 empty] | 71226.4386 | 249.268 | 0 | 71475.7065 | 238587.7795
DATE/TIME | [6 empty] | LOADS |  |  |  |  | Heating | [5 empty] | Cooling |  |  |  |  | LOOP FLOW |  | LOOP PUMP OPERATION/SPEED |  |  |  |  | LOOP PUMP DEMAND | [6 empty] | OUTFALL FLOW |  | OUTFALL PUMP OPERATION/SPEED |  |  |  | OUTFALL PUMP DEMANDS
Date | Month | Day | Hour | Day of Year | Hour of Year | Dry Bulb Temperature (°F) | Heating Load (MBH) | Heat Pump Cooling Load (MBH) | Total Cooling Load (MBH) | Total Load (MBH) | Mode (Heating/ Cooling) | Heat Required from Loop (MBH) | Central Plant Chiller COP | Heat Absorbed from WWTP Outfall (MBH) | Heat Required from Central Plant Chiller (MBH) | Loop Heat Pump COP | Loop Heat Pump Electric Demand (kW) | Heat Rejected to District Loop (MBH) | Heat Rejected to WWTP Outfall (MBH) | Heat Rejection Required from Central Plant Chiller | Loop Heat Pump COP | Loop Heat Pump Electric Demand (kW) | Loop Flow (GPM) | % Loop Design Flow | Loop No. Pumps Operating | Loop Pump 1 Speed | Loop Pump 2 Speed | Looop Pump 3 Speed | Looop Pump 4 Speed | Loop Pump 1 Demand (kW) | Loop Pump 2 Demand (kW) | Loop Pump 3 Demand (kW) | Loop Pump 4 Demand (kW) | Total Loop Pump Demand (kW) | Heat Absorbed from WWTP Outfall (MBH) | Heat Rejected to WWTP Outfall (MBH) | Outfall Flowrate (GPM) | % Outfall Design Flow | Outfall No. Pumps Operating | Outfall Pump 1 Speed | Outfall Pump 2 Speed | Outfall Pump 3 Speed | Outfall Pump 1 Demand (kW) | Outfall Pump 2 Demand (kW) | Outfall Pump 3 Demand (kW) | Total Outfall Pump Demand (kW) | Total Electric Demand (kW)
2007-01-01 01:00 | 1 | 1 | 1 | 1 | 1 | 35.96 | 1256.981 | 0 | 0 | 1256.981 | Heating | 1109.1009 | 8.5 | 1109.1009 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.8202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1131.7356 | 0 | 226.3471 | 2.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 02:00 | 1 | 1 | 2 | 1 | 2 | 35.96 | 1668.0148 | 0 | 0 | 1668.0148 | Heating | 1471.7778 | 8.5 | 1471.7778 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 294.3556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1501.8141 | 0 | 300.3628 | 3.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 03:00 | 1 | 1 | 3 | 1 | 3 | 35.96 | 1766.93 | 0 | 0 | 1766.93 | Heating | 1559.0559 | 8.5 | 1559.0559 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.8112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1590.8734 | 0 | 318.1747 | 3.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 04:00 | 1 | 1 | 4 | 1 | 4 | 37.4 | 1881.2621 | 0 | 0 | 1881.2621 | Heating | 1659.9371 | 8.5 | 1659.9371 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 331.9874 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1693.8134 | 0 | 338.7627 | 3.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 05:00 | 1 | 1 | 5 | 1 | 5 | 37.04 | 2019.8669 | 0 | 0 | 2019.8669 | Heating | 1782.2355 | 8.5 | 1782.2355 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 356.4471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1818.6077 | 0 | 363.7215 | 3.637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 06:00 | 1 | 1 | 6 | 1 | 6 | 37.4 | 2105.5583 | 0 | 0 | 2105.5583 | Heating | 1857.8456 | 8.5 | 1857.8456 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 371.5691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1895.7608 | 0 | 379.1522 | 3.792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 07:00 | 1 | 1 | 7 | 1 | 7 | 37.94 | 10111.2369 | 0 | 0 | 10111.2369 | Heating | 8921.6796 | 8.5 | 8921.6796 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1784.3359 | 35.69% | 1 | 71.37% | 0% | 0% | 0% | 37.5212 | 0 | 0 | 0 | 37.5212 | 9103.7547 | 0 | 1820.7509 | 18.21% | 1 | 36.42% | 0% | 0% | 3.9908 | 0 | 0 | 3.9908 | 41.512
2007-01-01 08:00 | 1 | 1 | 8 | 1 | 8 | 37.94 | 8091.3203 | 0 | 0 | 8091.3203 | Heating | 7139.4003 | 8.5 | 7139.4003 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1427.8801 | 30% | 1 | 57.12% | 0% | 0% | 0% | 22.4736 | 0 | 0 | 0 | 22.4736 | 7285.1023 | 0 | 1457.0205 | 14.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.7481
2007-01-01 09:00 | 1 | 1 | 9 | 1 | 9 | 39.02 | 7307.0774 | 0 | 0 | 7307.0774 | Heating | 6447.4213 | 8.5 | 6447.4213 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1289.4843 | 30% | 1 | 51.58% | 0% | 0% | 0% | 17.7762 | 0 | 0 | 0 | 17.7762 | 6579.0013 | 0 | 1315.8003 | 13.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.0507
2007-01-01 10:00 | 1 | 1 | 10 | 1 | 10 | 39.2 | 6316.7775 | 0 | 0 | 6316.7775 | Heating | 5573.6272 | 8.5 | 5573.6272 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1114.7254 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5687.3747 | 0 | 1137.4749 | 11.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 11:00 | 1 | 1 | 11 | 1 | 11 | 41 | 5764.988 | 0 | 0 | 5764.988 | Heating | 5086.7541 | 8.5 | 5086.7541 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1017.3508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5190.5654 | 0 | 1038.1131 | 10.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 12:00 | 1 | 1 | 12 | 1 | 12 | 44.6 | 5222.0518 | 0 | 0 | 5222.0518 | Heating | 4607.6928 | 8.5 | 4607.6928 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 921.5386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4701.7273 | 0 | 940.3455 | 9.403% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 13:00 | 1 | 1 | 13 | 1 | 13 | 44.96 | 4591.8812 | 0 | 0 | 4591.8812 | Heating | 4051.6599 | 8.5 | 4051.6599 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 810.332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4134.3468 | 0 | 826.8694 | 8.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 14:00 | 1 | 1 | 14 | 1 | 14 | 44.96 | 4103.5029 | 0 | 0 | 4103.5029 | Heating | 3620.7378 | 8.5 | 3620.7378 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 724.1476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3694.6305 | 0 | 738.9261 | 7.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 15:00 | 1 | 1 | 15 | 1 | 15 | 46.94 | 3756.724 | 0 | 0 | 3756.724 | Heating | 3314.7565 | 8.5 | 3314.7565 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 662.9513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3382.4046 | 0 | 676.4809 | 6.765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 16:00 | 1 | 1 | 16 | 1 | 16 | 46.04 | 3341.8226 | 0 | 0 | 3341.8226 | Heating | 2948.667 | 8.5 | 2948.667 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 589.7334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3008.8439 | 0 | 601.7688 | 6.018% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 17:00 | 1 | 1 | 17 | 1 | 17 | 46.04 | 3118.5556 | 0 | 0 | 3118.5556 | Heating | 2751.6667 | 8.5 | 2751.6667 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.3333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2807.8231 | 0 | 561.5646 | 5.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 18:00 | 1 | 1 | 18 | 1 | 18 | 44.6 | 2989.2951 | 0 | 0 | 2989.2951 | Heating | 2637.6133 | 8.5 | 2637.6133 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 527.5227 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2691.4422 | 0 | 538.2884 | 5.383% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 19:00 | 1 | 1 | 19 | 1 | 19 | 41 | 2894.043 | 0 | 0 | 2894.043 | Heating | 2553.5673 | 8.5 | 2553.5673 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 510.7135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2605.6809 | 0 | 521.1362 | 5.211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 20:00 | 1 | 1 | 20 | 1 | 20 | 41 | 2700.6271 | 0 | 0 | 2700.6271 | Heating | 2382.9062 | 8.5 | 2382.9062 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.5812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2431.537 | 0 | 486.3074 | 4.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 21:00 | 1 | 1 | 21 | 1 | 21 | 41 | 2483.4379 | 0 | 0 | 2483.4379 | Heating | 2191.2687 | 8.5 | 2191.2687 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.2537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2235.9885 | 0 | 447.1977 | 4.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 22:00 | 1 | 1 | 22 | 1 | 22 | 42.98 | 802.3528 | 0 | 0 | 802.3528 | Heating | 707.9583 | 8.5 | 707.9583 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.5917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 722.4065 | 0 | 144.4813 | 1.445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-01 23:00 | 1 | 1 | 23 | 1 | 23 | 42.98 | 745.4465 | 0 | 0 | 745.4465 | Heating | 657.7469 | 8.5 | 657.7469 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.5494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 671.1703 | 0 | 134.2341 | 1.342% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 | 1 | 2 | 0 | 2 | 24 | 42.98 | 724.2447 | 0 | 0 | 724.2447 | Heating | 639.0395 | 8.5 | 639.0395 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.8079 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 652.0811 | 0 | 130.4162 | 1.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 01:00 | 1 | 2 | 1 | 2 | 25 | 42.8 | 737.5426 | 0 | 0 | 737.5426 | Heating | 650.7729 | 8.5 | 650.7729 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.1546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 664.054 | 0 | 132.8108 | 1.328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 02:00 | 1 | 2 | 2 | 2 | 26 | 42.98 | 900.1883 | 0 | 0 | 900.1883 | Heating | 794.2838 | 8.5 | 794.2838 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.8568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 810.4937 | 0 | 162.0987 | 1.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 03:00 | 1 | 2 | 3 | 2 | 27 | 42.98 | 1104.4504 | 0 | 0 | 1104.4504 | Heating | 974.515 | 8.5 | 974.515 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 194.903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 994.4031 | 0 | 198.8806 | 1.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 04:00 | 1 | 2 | 4 | 2 | 28 | 42.08 | 1237.0355 | 0 | 0 | 1237.0355 | Heating | 1091.5019 | 8.5 | 1091.5019 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.3004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1113.7775 | 0 | 222.7555 | 2.228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 05:00 | 1 | 2 | 5 | 2 | 29 | 42.08 | 1337.4697 | 0 | 0 | 1337.4697 | Heating | 1180.1203 | 8.5 | 1180.1203 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 236.0241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1204.2044 | 0 | 240.8409 | 2.408% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 06:00 | 1 | 2 | 6 | 2 | 30 | 37.94 | 1416.6972 | 0 | 0 | 1416.6972 | Heating | 1250.027 | 8.5 | 1250.027 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 250.0054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1275.5377 | 0 | 255.1075 | 2.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 07:00 | 1 | 2 | 7 | 2 | 31 | 35.96 | 8939.3319 | 0 | 0 | 8939.3319 | Heating | 7887.6458 | 8.5 | 7887.6458 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1577.5292 | 31.55% | 1 | 63.1% | 0% | 0% | 0% | 28.2637 | 0 | 0 | 0 | 28.2637 | 8048.6181 | 0 | 1609.7236 | 16.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.5382
2007-01-02 08:00 | 1 | 2 | 8 | 2 | 32 | 35.96 | 6978.6798 | 0 | 0 | 6978.6798 | Heating | 6157.6586 | 8.5 | 6157.6586 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1231.5317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6283.3251 | 0 | 1256.665 | 12.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 09:00 | 1 | 2 | 9 | 2 | 33 | 35.96 | 5874.0245 | 0 | 0 | 5874.0245 | Heating | 5182.9628 | 8.5 | 5182.9628 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1036.5926 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5288.7376 | 0 | 1057.7475 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 10:00 | 1 | 2 | 10 | 2 | 34 | 37.04 | 4825.3632 | 0 | 0 | 4825.3632 | Heating | 4257.6734 | 8.5 | 4257.6734 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 851.5347 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4344.5647 | 0 | 868.9129 | 8.689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 11:00 | 1 | 2 | 11 | 2 | 35 | 37.04 | 4386.015 | 0 | 0 | 4386.015 | Heating | 3870.0133 | 8.5 | 3870.0133 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 774.0027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3948.9931 | 0 | 789.7986 | 7.898% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 12:00 | 1 | 2 | 12 | 2 | 36 | 39.02 | 4113.5041 | 0 | 0 | 4113.5041 | Heating | 3629.5624 | 8.5 | 3629.5624 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 725.9125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3703.6351 | 0 | 740.727 | 7.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 13:00 | 1 | 2 | 13 | 2 | 37 | 39.02 | 3996.4649 | 0 | 0 | 3996.4649 | Heating | 3526.2926 | 8.5 | 3526.2926 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 705.2585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3598.2577 | 0 | 719.6515 | 7.197% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 14:00 | 1 | 2 | 14 | 2 | 38 | 39.02 | 3854.2952 | 0 | 0 | 3854.2952 | Heating | 3400.8487 | 8.5 | 3400.8487 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 680.1697 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3470.2538 | 0 | 694.0508 | 6.941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 15:00 | 1 | 2 | 15 | 2 | 39 | 39.92 | 3800.5815 | 0 | 0 | 3800.5815 | Heating | 3353.4543 | 8.5 | 3353.4543 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 670.6909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3421.8921 | 0 | 684.3784 | 6.844% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 16:00 | 1 | 2 | 16 | 2 | 40 | 39.02 | 3755.7432 | 0 | 0 | 3755.7432 | Heating | 3313.8911 | 8.5 | 3313.8911 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 662.7782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3381.5215 | 0 | 676.3043 | 6.763% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 17:00 | 1 | 2 | 17 | 2 | 41 | 39.02 | 3907.4734 | 0 | 0 | 3907.4734 | Heating | 3447.7707 | 8.5 | 3447.7707 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 689.5541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3518.1333 | 0 | 703.6267 | 7.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 18:00 | 1 | 2 | 18 | 2 | 42 | 35.96 | 4114.6453 | 0 | 0 | 4114.6453 | Heating | 3630.5694 | 8.5 | 3630.5694 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 726.1139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3704.6627 | 0 | 740.9325 | 7.409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 19:00 | 1 | 2 | 19 | 2 | 43 | 35.06 | 4124.4459 | 0 | 0 | 4124.4459 | Heating | 3639.2169 | 8.5 | 3639.2169 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.8434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3713.4867 | 0 | 742.6973 | 7.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 20:00 | 1 | 2 | 20 | 2 | 44 | 35.06 | 4251.3482 | 0 | 0 | 4251.3482 | Heating | 3751.1896 | 8.5 | 3751.1896 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.2379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3827.7444 | 0 | 765.5489 | 7.655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 21:00 | 1 | 2 | 21 | 2 | 45 | 30.02 | 4660.704 | 0 | 0 | 4660.704 | Heating | 4112.3859 | 8.5 | 4112.3859 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 822.4772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4196.3121 | 0 | 839.2624 | 8.393% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 22:00 | 1 | 2 | 22 | 2 | 46 | 28.94 | 1520.0105 | 0 | 0 | 1520.0105 | Heating | 1341.1858 | 8.5 | 1341.1858 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.2372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1368.5569 | 0 | 273.7114 | 2.737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-02 23:00 | 1 | 2 | 23 | 2 | 47 | 28.94 | 1422.2497 | 0 | 0 | 1422.2497 | Heating | 1254.9262 | 8.5 | 1254.9262 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 250.9852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1280.537 | 0 | 256.1074 | 2.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 | 1 | 3 | 0 | 3 | 48 | 26.06 | 1677.5908 | 0 | 0 | 1677.5908 | Heating | 1480.2272 | 8.5 | 1480.2272 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.0454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1510.4359 | 0 | 302.0872 | 3.021% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 01:00 | 1 | 3 | 1 | 3 | 49 | 26.96 | 1838.8304 | 0 | 0 | 1838.8304 | Heating | 1622.4974 | 8.5 | 1622.4974 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.4995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1655.6096 | 0 | 331.1219 | 3.311% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 02:00 | 1 | 3 | 2 | 3 | 50 | 26.96 | 2051.6181 | 0 | 0 | 2051.6181 | Heating | 1810.2512 | 8.5 | 1810.2512 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.0502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1847.1951 | 0 | 369.439 | 3.694% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 03:00 | 1 | 3 | 3 | 3 | 51 | 26.96 | 2138.5581 | 0 | 0 | 2138.5581 | Heating | 1886.963 | 8.5 | 1886.963 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 377.3926 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1925.4725 | 0 | 385.0945 | 3.851% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 04:00 | 1 | 3 | 4 | 3 | 52 | 28.04 | 2183.8099 | 0 | 0 | 2183.8099 | Heating | 1926.891 | 8.5 | 1926.891 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.3782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1966.2154 | 0 | 393.2431 | 3.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 05:00 | 1 | 3 | 5 | 3 | 53 | 28.04 | 2280.5824 | 0 | 0 | 2280.5824 | Heating | 2012.2785 | 8.5 | 2012.2785 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.4557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2053.3455 | 0 | 410.6691 | 4.107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 06:00 | 1 | 3 | 6 | 3 | 54 | 28.94 | 2329.3168 | 0 | 0 | 2329.3168 | Heating | 2055.2796 | 8.5 | 2055.2796 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.0559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2097.2241 | 0 | 419.4448 | 4.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 07:00 | 1 | 3 | 7 | 3 | 55 | 28.94 | 12745.9774 | 0 | 0 | 12745.9774 | Heating | 11246.4506 | 8.5 | 11246.4506 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2249.2901 | 44.99% | 1 | 89.97% | 0% | 0% | 0% | 63.9125 | 0 | 0 | 0 | 63.9125 | 11475.97 | 0 | 2295.194 | 22.95% | 1 | 45.9% | 0% | 0% | 6.7978 | 0 | 0 | 6.7978 | 70.7102
2007-01-03 08:00 | 1 | 3 | 8 | 3 | 56 | 28.94 | 9897.8125 | 0 | 0 | 9897.8125 | Heating | 8733.364 | 8.5 | 8733.364 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1746.6728 | 34.93% | 1 | 69.87% | 0% | 0% | 0% | 35.7246 | 0 | 0 | 0 | 35.7246 | 8911.5959 | 0 | 1782.3192 | 17.82% | 1 | 35.65% | 0% | 0% | 3.7997 | 0 | 0 | 3.7997 | 39.5243
2007-01-03 09:00 | 1 | 3 | 9 | 3 | 57 | 30.92 | 8216.0202 | 0 | 0 | 8216.0202 | Heating | 7249.4296 | 8.5 | 7249.4296 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1449.8859 | 30% | 1 | 58% | 0% | 0% | 0% | 23.2782 | 0 | 0 | 0 | 23.2782 | 7397.3771 | 0 | 1479.4754 | 14.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.5527
2007-01-03 10:00 | 1 | 3 | 10 | 3 | 58 | 33.98 | 6950.0968 | 0 | 0 | 6950.0968 | Heating | 6132.4384 | 8.5 | 6132.4384 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1226.4877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6257.5902 | 0 | 1251.518 | 12.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 11:00 | 1 | 3 | 11 | 3 | 59 | 33.98 | 6183.6601 | 0 | 0 | 6183.6601 | Heating | 5456.1707 | 8.5 | 5456.1707 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1091.2341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5567.5211 | 0 | 1113.5042 | 11.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 12:00 | 1 | 3 | 12 | 3 | 60 | 39.02 | 5598.4121 | 0 | 0 | 5598.4121 | Heating | 4939.7754 | 8.5 | 4939.7754 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 987.9551 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5040.5871 | 0 | 1008.1174 | 10.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 13:00 | 1 | 3 | 13 | 3 | 61 | 42.98 | 5121.3579 | 0 | 0 | 5121.3579 | Heating | 4518.8452 | 8.5 | 4518.8452 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 903.769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4611.0666 | 0 | 922.2133 | 9.222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 14:00 | 1 | 3 | 14 | 3 | 62 | 42.98 | 4715.1426 | 0 | 0 | 4715.1426 | Heating | 4160.4199 | 8.5 | 4160.4199 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 832.084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4245.3265 | 0 | 849.0653 | 8.491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 15:00 | 1 | 3 | 15 | 3 | 63 | 46.94 | 4453.9446 | 0 | 0 | 4453.9446 | Heating | 3929.9511 | 8.5 | 3929.9511 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 785.9902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4010.1542 | 0 | 802.0308 | 8.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 16:00 | 1 | 3 | 16 | 3 | 64 | 44.96 | 4758.2466 | 0 | 0 | 4758.2466 | Heating | 4198.4529 | 8.5 | 4198.4529 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 839.6906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4284.1356 | 0 | 856.8271 | 8.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 17:00 | 1 | 3 | 17 | 3 | 65 | 44.96 | 5152.0593 | 0 | 0 | 5152.0593 | Heating | 4545.9347 | 8.5 | 4545.9347 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 909.1869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4638.7089 | 0 | 927.7418 | 9.277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 18:00 | 1 | 3 | 18 | 3 | 66 | 42.98 | 5504.9261 | 0 | 0 | 5504.9261 | Heating | 4857.2877 | 8.5 | 4857.2877 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 971.4575 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4956.416 | 0 | 991.2832 | 9.913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 19:00 | 1 | 3 | 19 | 3 | 67 | 42.98 | 5671.0168 | 0 | 0 | 5671.0168 | Heating | 5003.8384 | 8.5 | 5003.8384 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1000.7677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5105.9575 | 0 | 1021.1915 | 10.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 20:00 | 1 | 3 | 20 | 3 | 68 | 42.98 | 6096.2824 | 0 | 0 | 6096.2824 | Heating | 5379.0727 | 8.5 | 5379.0727 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1075.8145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5488.8497 | 0 | 1097.7699 | 10.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 21:00 | 1 | 3 | 21 | 3 | 69 | 41 | 6554.6803 | 0 | 0 | 6554.6803 | Heating | 5783.5414 | 8.5 | 5783.5414 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1156.7083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5901.5729 | 0 | 1180.3146 | 11.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 22:00 | 1 | 3 | 22 | 3 | 70 | 39.02 | 1999.6018 | 0 | 0 | 1999.6018 | Heating | 1764.3546 | 8.5 | 1764.3546 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 352.8709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1800.3618 | 0 | 360.0724 | 3.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-03 23:00 | 1 | 3 | 23 | 3 | 71 | 39.02 | 1917.1231 | 0 | 0 | 1917.1231 | Heating | 1691.5792 | 8.5 | 1691.5792 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 338.3158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1726.1013 | 0 | 345.2203 | 3.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 | 1 | 4 | 0 | 4 | 72 | 33.98 | 2197.806 | 0 | 0 | 2197.806 | Heating | 1939.2406 | 8.5 | 1939.2406 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.8481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1978.8169 | 0 | 395.7634 | 3.958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 01:00 | 1 | 4 | 1 | 4 | 73 | 33.98 | 2551.9975 | 0 | 0 | 2551.9975 | Heating | 2251.7625 | 8.5 | 2251.7625 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 450.3525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2297.7168 | 0 | 459.5434 | 4.595% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 02:00 | 1 | 4 | 2 | 4 | 74 | 33.98 | 2681.7466 | 0 | 0 | 2681.7466 | Heating | 2366.247 | 8.5 | 2366.247 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 473.2494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2414.5378 | 0 | 482.9076 | 4.829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 03:00 | 1 | 4 | 3 | 4 | 75 | 37.94 | 2695.0365 | 0 | 0 | 2695.0365 | Heating | 2377.9734 | 8.5 | 2377.9734 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 475.5947 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2426.5035 | 0 | 485.3007 | 4.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 04:00 | 1 | 4 | 4 | 4 | 76 | 37.94 | 2751.4477 | 0 | 0 | 2751.4477 | Heating | 2427.748 | 8.5 | 2427.748 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 485.5496 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2477.2938 | 0 | 495.4588 | 4.955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 05:00 | 1 | 4 | 5 | 4 | 77 | 37.94 | 2840.9879 | 0 | 0 | 2840.9879 | Heating | 2506.754 | 8.5 | 2506.754 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 501.3508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2557.9123 | 0 | 511.5825 | 5.116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 06:00 | 1 | 4 | 6 | 4 | 78 | 32 | 2892.2162 | 0 | 0 | 2892.2162 | Heating | 2551.9554 | 8.5 | 2551.9554 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 510.3911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2604.0362 | 0 | 520.8072 | 5.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 07:00 | 1 | 4 | 7 | 4 | 79 | 32 | 14462.4776 | 0 | 0 | 14462.4776 | Heating | 12761.0096 | 8.5 | 12761.0096 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2552.2019 | 51.04% | 2 | 51.04% | 51.04% | 0% | 0% | 17.3547 | 17.3547 | 0 | 0 | 34.7094 | 13021.4384 | 0 | 2604.2877 | 26.04% | 1 | 52.09% | 0% | 0% | 9.0901 | 0 | 0 | 9.0901 | 43.7994
2007-01-04 08:00 | 1 | 4 | 8 | 4 | 80 | 32 | 11935.9063 | 0 | 0 | 11935.9063 | Heating | 10531.682 | 8.5 | 10531.682 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2106.3364 | 42.13% | 1 | 84.25% | 0% | 0% | 0% | 54.9534 | 0 | 0 | 0 | 54.9534 | 10746.6143 | 0 | 2149.3229 | 21.49% | 1 | 42.99% | 0% | 0% | 5.8449 | 0 | 0 | 5.8449 | 60.7983
2007-01-04 09:00 | 1 | 4 | 9 | 4 | 81 | 35.96 | 9692.7476 | 0 | 0 | 9692.7476 | Heating | 8552.4244 | 8.5 | 8552.4244 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1710.4849 | 34.21% | 1 | 68.42% | 0% | 0% | 0% | 34.0452 | 0 | 0 | 0 | 34.0452 | 8726.9636 | 0 | 1745.3927 | 17.45% | 1 | 34.91% | 0% | 0% | 3.6211 | 0 | 0 | 3.6211 | 37.6662
2007-01-04 10:00 | 1 | 4 | 10 | 4 | 82 | 39.92 | 7843.3882 | 0 | 0 | 7843.3882 | Heating | 6920.6366 | 8.5 | 6920.6366 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1384.1273 | 30% | 1 | 55.37% | 0% | 0% | 0% | 20.9212 | 0 | 0 | 0 | 20.9212 | 7061.8741 | 0 | 1412.3748 | 14.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.1957
2007-01-04 11:00 | 1 | 4 | 11 | 4 | 83 | 39.92 | 6756.3521 | 0 | 0 | 6756.3521 | Heating | 5961.4872 | 8.5 | 5961.4872 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1192.2974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6083.1502 | 0 | 1216.63 | 12.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 12:00 | 1 | 4 | 12 | 4 | 84 | 44.06 | 5658.8731 | 0 | 0 | 5658.8731 | Heating | 4993.1233 | 8.5 | 4993.1233 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 998.6247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5095.0238 | 0 | 1019.0048 | 10.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 13:00 | 1 | 4 | 13 | 4 | 85 | 46.94 | 5239.1697 | 0 | 0 | 5239.1697 | Heating | 4622.7968 | 8.5 | 4622.7968 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 924.5594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4717.1396 | 0 | 943.4279 | 9.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 14:00 | 1 | 4 | 14 | 4 | 86 | 46.94 | 5060.4202 | 0 | 0 | 5060.4202 | Heating | 4465.0766 | 8.5 | 4465.0766 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 893.0153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4556.2006 | 0 | 911.2401 | 9.112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 15:00 | 1 | 4 | 15 | 4 | 87 | 50 | 4879.0499 | 0 | 0 | 4879.0499 | Heating | 4305.044 | 8.5 | 4305.044 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 861.0088 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4392.9021 | 0 | 878.5804 | 8.786% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 16:00 | 1 | 4 | 16 | 4 | 88 | 48.02 | 4804.8287 | 0 | 0 | 4804.8287 | Heating | 4239.5547 | 8.5 | 4239.5547 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 847.9109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4326.0763 | 0 | 865.2153 | 8.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 17:00 | 1 | 4 | 17 | 4 | 89 | 48.02 | 4960.0602 | 0 | 0 | 4960.0602 | Heating | 4376.5237 | 8.5 | 4376.5237 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 875.3047 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4465.8405 | 0 | 893.1681 | 8.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 18:00 | 1 | 4 | 18 | 4 | 90 | 44.96 | 5079.3677 | 0 | 0 | 5079.3677 | Heating | 4481.795 | 8.5 | 4481.795 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 896.359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4573.2602 | 0 | 914.652 | 9.147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 19:00 | 1 | 4 | 19 | 4 | 91 | 44.06 | 4979.138 | 0 | 0 | 4979.138 | Heating | 4393.357 | 8.5 | 4393.357 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 878.6714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4483.0174 | 0 | 896.6035 | 8.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 20:00 | 1 | 4 | 20 | 4 | 92 | 44.06 | 5039.2069 | 0 | 0 | 5039.2069 | Heating | 4446.359 | 8.5 | 4446.359 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 889.2718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4537.1011 | 0 | 907.4202 | 9.074% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 21:00 | 1 | 4 | 21 | 4 | 93 | 46.94 | 5347.897 | 0 | 0 | 5347.897 | Heating | 4718.7327 | 8.5 | 4718.7327 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 943.7465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4815.0334 | 0 | 963.0067 | 9.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 22:00 | 1 | 4 | 22 | 4 | 94 | 48.02 | 1562.0824 | 0 | 0 | 1562.0824 | Heating | 1378.308 | 8.5 | 1378.308 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 275.6616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1406.4367 | 0 | 281.2873 | 2.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-04 23:00 | 1 | 4 | 23 | 4 | 95 | 48.02 | 1345.1009 | 0 | 0 | 1345.1009 | Heating | 1186.8537 | 8.5 | 1186.8537 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.3707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1211.0752 | 0 | 242.215 | 2.422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 | 1 | 5 | 0 | 5 | 96 | 50 | 1559.8756 | 0 | 0 | 1559.8756 | Heating | 1376.3608 | 8.5 | 1376.3608 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 275.2722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1404.4498 | 0 | 280.89 | 2.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 01:00 | 1 | 5 | 1 | 5 | 97 | 50 | 1680.6397 | 0 | 0 | 1680.6397 | Heating | 1482.9173 | 8.5 | 1482.9173 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.5835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1513.181 | 0 | 302.6362 | 3.026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 02:00 | 1 | 5 | 2 | 5 | 98 | 50 | 1685.8505 | 0 | 0 | 1685.8505 | Heating | 1487.5151 | 8.5 | 1487.5151 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1517.8726 | 0 | 303.5745 | 3.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 03:00 | 1 | 5 | 3 | 5 | 99 | 50 | 1813.1312 | 0 | 0 | 1813.1312 | Heating | 1599.8216 | 8.5 | 1599.8216 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 319.9643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1632.471 | 0 | 326.4942 | 3.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 04:00 | 1 | 5 | 4 | 5 | 100 | 50 | 1993.4031 | 0 | 0 | 1993.4031 | Heating | 1758.8851 | 8.5 | 1758.8851 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 351.777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1794.7807 | 0 | 358.9561 | 3.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 05:00 | 1 | 5 | 5 | 5 | 101 | 50 | 2072.5462 | 0 | 0 | 2072.5462 | Heating | 1828.7172 | 8.5 | 1828.7172 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 365.7434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1866.038 | 0 | 373.2076 | 3.732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 06:00 | 1 | 5 | 6 | 5 | 102 | 50 | 2099.62 | 0 | 0 | 2099.62 | Heating | 1852.6059 | 8.5 | 1852.6059 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 370.5212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1890.4142 | 0 | 378.0828 | 3.781% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 07:00 | 1 | 5 | 7 | 5 | 103 | 51.98 | 11280.8654 | 0 | 0 | 11280.8654 | Heating | 9953.7048 | 8.5 | 9953.7048 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1990.741 | 39.81% | 1 | 79.63% | 0% | 0% | 0% | 48.2631 | 0 | 0 | 0 | 48.2631 | 10156.8416 | 0 | 2031.3683 | 20.31% | 1 | 40.63% | 0% | 0% | 5.1333 | 0 | 0 | 5.1333 | 53.3964
2007-01-05 08:00 | 1 | 5 | 8 | 5 | 104 | 51.98 | 8726.8752 | 0 | 0 | 8726.8752 | Heating | 7700.184 | 8.5 | 7700.184 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1540.0368 | 30.8% | 1 | 61.6% | 0% | 0% | 0% | 26.7425 | 0 | 0 | 0 | 26.7425 | 7857.3306 | 0 | 1571.4661 | 15.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.0171
2007-01-05 09:00 | 1 | 5 | 9 | 5 | 105 | 53.06 | 7688.6315 | 0 | 0 | 7688.6315 | Heating | 6784.0866 | 8.5 | 6784.0866 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1356.8173 | 30% | 1 | 54.27% | 0% | 0% | 0% | 19.9839 | 0 | 0 | 0 | 19.9839 | 6922.5373 | 0 | 1384.5075 | 13.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.2584
2007-01-05 10:00 | 1 | 5 | 10 | 5 | 106 | 53.96 | 6643.107 | 0 | 0 | 6643.107 | Heating | 5861.565 | 8.5 | 5861.565 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1172.313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5981.1888 | 0 | 1196.2378 | 11.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 11:00 | 1 | 5 | 11 | 5 | 107 | 53.96 | 5555.1701 | 0 | 0 | 5555.1701 | Heating | 4901.6207 | 8.5 | 4901.6207 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 980.3241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5001.6538 | 0 | 1000.3308 | 10% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 12:00 | 1 | 5 | 12 | 5 | 108 | 55.94 | 4754.4708 | 0 | 0 | 4754.4708 | Heating | 4195.1213 | 8.5 | 4195.1213 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 839.0243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4280.736 | 0 | 856.1472 | 8.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 13:00 | 1 | 5 | 13 | 5 | 109 | 57.02 | 4581.637 | 0 | 0 | 4581.637 | Heating | 4042.6208 | 8.5 | 4042.6208 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 808.5242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4125.1233 | 0 | 825.0247 | 8.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 14:00 | 1 | 5 | 14 | 5 | 110 | 57.02 | 4618.2294 | 0 | 0 | 4618.2294 | Heating | 4074.9083 | 8.5 | 4074.9083 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 814.9817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4158.0697 | 0 | 831.6139 | 8.316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 15:00 | 1 | 5 | 15 | 5 | 111 | 57.02 | 4690.1347 | 0 | 0 | 4690.1347 | Heating | 4138.3541 | 8.5 | 4138.3541 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 827.6708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4222.8103 | 0 | 844.5621 | 8.446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 16:00 | 1 | 5 | 16 | 5 | 112 | 57.02 | 4838.0394 | 0 | 0 | 4838.0394 | Heating | 4268.8583 | 8.5 | 4268.8583 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 853.7717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4355.9779 | 0 | 871.1956 | 8.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 17:00 | 1 | 5 | 17 | 5 | 113 | 57.02 | 5385.7005 | 0 | 0 | 5385.7005 | Heating | 4752.0886 | 8.5 | 4752.0886 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 950.4177 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4849.07 | 0 | 969.814 | 9.698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 18:00 | 1 | 5 | 18 | 5 | 114 | 55.4 | 5964.391 | 0 | 0 | 5964.391 | Heating | 5262.6979 | 8.5 | 5262.6979 | 0 | 5.0667 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1052.5396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5370.0999 | 0 | 1074.02 | 10.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 19:00 | 1 | 5 | 19 | 5 | 115 | 55.4 | 6626.0659 | 0 | 0 | 6626.0659 | Heating | 5846.5288 | 8.5 | 5846.5288 | 0 | 5.0667 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1169.3058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5965.8457 | 0 | 1193.1691 | 11.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-05 20:00 | 1 | 5 | 20 | 5 | 116 | 55.94 | 7224.7334 | 0 | 0 | 7224.7334 | Heating | 6374.7648 | 8.5 | 6374.7648 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1274.953 | 30% | 1 | 51% | 0% | 0% | 0% | 17.3188 | 0 | 0 | 0 | 17.3188 | 6504.862 | 0 | 1300.9724 | 13.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.5933
2007-01-05 21:00 | 1 | 5 | 21 | 5 | 117 | 57.02 | 7657.1586 | 0 | 0 | 7657.1586 | Heating | 6756.3164 | 8.5 | 6756.3164 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1351.2633 | 30% | 1 | 54.05% | 0% | 0% | 0% | 19.7963 | 0 | 0 | 0 | 19.7963 | 6894.2004 | 0 | 1378.8401 | 13.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.0708
2007-01-05 22:00 | 1 | 5 | 22 | 5 | 118 | 57.02 | 8189.6409 | 0 | 0 | 8189.6409 | Heating | 7226.1537 | 8.5 | 7226.1537 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1445.2307 | 30% | 1 | 57.81% | 0% | 0% | 0% | 23.1066 | 0 | 0 | 0 | 23.1066 | 7373.6262 | 0 | 1474.7252 | 14.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.3812
2007-01-05 23:00 | 1 | 5 | 23 | 5 | 119 | 57.02 | 2479.29 | 0 | 0 | 2479.29 | Heating | 2187.6088 | 8.5 | 2187.6088 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 437.5218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2232.2539 | 0 | 446.4508 | 4.465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 | 1 | 6 | 0 | 6 | 120 | 57.2 | 2463.554 | 0 | 0 | 2463.554 | Heating | 2173.7241 | 8.5 | 2173.7241 | 0 | 5.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 434.7448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2218.0858 | 0 | 443.6172 | 4.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 01:00 | 1 | 6 | 1 | 6 | 121 | 59 | 2490.5163 | 0 | 0 | 2490.5163 | Heating | 2197.5144 | 8.5 | 2197.5144 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 439.5029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2242.3616 | 0 | 448.4723 | 4.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 02:00 | 1 | 6 | 2 | 6 | 122 | 59 | 2569.6651 | 0 | 0 | 2569.6651 | Heating | 2267.3515 | 8.5 | 2267.3515 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 453.4703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2313.624 | 0 | 462.7248 | 4.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 03:00 | 1 | 6 | 3 | 6 | 123 | 59 | 2699.4133 | 0 | 0 | 2699.4133 | Heating | 2381.8353 | 8.5 | 2381.8353 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.3671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2430.4442 | 0 | 486.0888 | 4.861% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 04:00 | 1 | 6 | 4 | 6 | 124 | 59 | 2673.1878 | 0 | 0 | 2673.1878 | Heating | 2358.6951 | 8.5 | 2358.6951 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.739 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2406.8318 | 0 | 481.3664 | 4.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 05:00 | 1 | 6 | 5 | 6 | 125 | 59 | 2499.6736 | 0 | 0 | 2499.6736 | Heating | 2205.5944 | 8.5 | 2205.5944 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 441.1189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2250.6065 | 0 | 450.1213 | 4.501% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 06:00 | 1 | 6 | 6 | 6 | 126 | 60.08 | 2374.5374 | 0 | 0 | 2374.5374 | Heating | 2095.1801 | 8.5 | 2095.1801 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 419.036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2137.9389 | 0 | 427.5878 | 4.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 07:00 | 1 | 6 | 7 | 6 | 127 | 60.08 | 2295.5819 | 0 | 0 | 2295.5819 | Heating | 2025.5135 | 8.5 | 2025.5135 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 405.1027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2066.8505 | 0 | 413.3701 | 4.134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 08:00 | 1 | 6 | 8 | 6 | 128 | 60.08 | 2250.0713 | 0 | 0 | 2250.0713 | Heating | 1985.357 | 8.5 | 1985.357 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 397.0714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2025.8745 | 0 | 405.1749 | 4.052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 09:00 | 1 | 6 | 9 | 6 | 129 | 60.8 | 11684.1612 | 0 | 0 | 11684.1612 | Heating | 10309.554 | 8.5 | 10309.554 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2061.9108 | 41.24% | 1 | 82.48% | 0% | 0% | 0% | 52.3241 | 0 | 0 | 0 | 52.3241 | 10519.9531 | 0 | 2103.9906 | 21.04% | 1 | 42.08% | 0% | 0% | 5.5652 | 0 | 0 | 5.5652 | 57.8893
2007-01-06 10:00 | 1 | 6 | 10 | 6 | 130 | 62.06 | 8987.2106 | 0 | 0 | 8987.2106 | Heating | 7929.8917 | 8.5 | 7929.8917 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1585.9783 | 31.72% | 1 | 63.44% | 0% | 0% | 0% | 28.6131 | 0 | 0 | 0 | 28.6131 | 8091.7262 | 0 | 1618.3452 | 16.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.8876
2007-01-06 11:00 | 1 | 6 | 11 | 6 | 131 | 62.06 | 7914.5556 | 0 | 0 | 7914.5556 | Heating | 6983.4314 | 8.5 | 6983.4314 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1396.6863 | 30% | 1 | 55.87% | 0% | 0% | 0% | 21.3604 | 0 | 0 | 0 | 21.3604 | 7125.9504 | 0 | 1425.1901 | 14.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.6349
2007-01-06 12:00 | 1 | 6 | 12 | 6 | 132 | 66.02 | 7691.7517 | 0 | 0 | 7691.7517 | Heating | 6786.8397 | 8.5 | 6786.8397 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1357.3679 | 30% | 1 | 54.29% | 0% | 0% | 0% | 20.0026 | 0 | 0 | 0 | 20.0026 | 6925.3466 | 0 | 1385.0693 | 13.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.2771
2007-01-06 13:00 | 1 | 6 | 13 | 6 | 133 | 69.98 | 7339.4772 | 0 | 0 | 7339.4772 | Heating | 6476.0093 | 8.5 | 6476.0093 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1295.2019 | 30% | 1 | 51.81% | 0% | 0% | 0% | 17.958 | 0 | 0 | 0 | 17.958 | 6608.1728 | 0 | 1321.6346 | 13.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.2325
2007-01-06 14:00 | 1 | 6 | 14 | 6 | 134 | 69.98 | 7054.1201 | 0 | 0 | 7054.1201 | Heating | 6224.2236 | 8.5 | 6224.2236 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1244.8447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6351.2486 | 0 | 1270.2497 | 12.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 15:00 | 1 | 6 | 15 | 6 | 135 | 57.92 | 6747.7968 | 0 | 0 | 6747.7968 | Heating | 5953.9383 | 8.5 | 5953.9383 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1190.7877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6075.4473 | 0 | 1215.0895 | 12.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 16:00 | 1 | 6 | 16 | 6 | 136 | 59 | 6696.6847 | 0 | 0 | 6696.6847 | Heating | 5908.8394 | 8.5 | 5908.8394 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1181.7679 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6029.428 | 0 | 1205.8856 | 12.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 17:00 | 1 | 6 | 17 | 6 | 137 | 59 | 6718.9704 | 0 | 0 | 6718.9704 | Heating | 5928.5033 | 8.5 | 5928.5033 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1185.7007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6049.4932 | 0 | 1209.8986 | 12.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 18:00 | 1 | 6 | 18 | 6 | 138 | 55.94 | 8871.0684 | 0 | 0 | 8871.0684 | Heating | 7827.4133 | 8.5 | 7827.4133 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1565.4827 | 31.31% | 1 | 62.62% | 0% | 0% | 0% | 27.7698 | 0 | 0 | 0 | 27.7698 | 7987.1564 | 0 | 1597.4313 | 15.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.0443
2007-01-06 19:00 | 1 | 6 | 19 | 6 | 139 | 53.06 | 9315.2374 | 0 | 0 | 9315.2374 | Heating | 8219.3271 | 8.5 | 8219.3271 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1643.8654 | 32.88% | 1 | 65.75% | 0% | 0% | 0% | 31.0723 | 0 | 0 | 0 | 31.0723 | 8387.0684 | 0 | 1677.4137 | 16.77% | 1 | 33.55% | 0% | 0% | 3.3049 | 0 | 0 | 3.3049 | 34.3772
2007-01-06 20:00 | 1 | 6 | 20 | 6 | 140 | 53.06 | 2438.8869 | 0 | 0 | 2438.8869 | Heating | 2151.9591 | 8.5 | 2151.9591 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 430.3918 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2195.8766 | 0 | 439.1753 | 4.392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 21:00 | 1 | 6 | 21 | 6 | 141 | 46.94 | 2455.9922 | 0 | 0 | 2455.9922 | Heating | 2167.0519 | 8.5 | 2167.0519 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 433.4104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2211.2775 | 0 | 442.2555 | 4.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 22:00 | 1 | 6 | 22 | 6 | 142 | 44.96 | 2573.4817 | 0 | 0 | 2573.4817 | Heating | 2270.7192 | 8.5 | 2270.7192 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 454.1438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2317.0604 | 0 | 463.4121 | 4.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-06 23:00 | 1 | 6 | 23 | 6 | 143 | 44.96 | 2658.4621 | 0 | 0 | 2658.4621 | Heating | 2345.7018 | 8.5 | 2345.7018 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 469.1404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2393.5733 | 0 | 478.7147 | 4.787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 | 1 | 7 | 0 | 7 | 144 | 44.06 | 2745.0962 | 0 | 0 | 2745.0962 | Heating | 2422.1437 | 8.5 | 2422.1437 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 484.4287 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2471.5752 | 0 | 494.315 | 4.943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 01:00 | 1 | 7 | 1 | 7 | 145 | 44.06 | 2781.7456 | 0 | 0 | 2781.7456 | Heating | 2454.4814 | 8.5 | 2454.4814 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 490.8963 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2504.5729 | 0 | 500.9146 | 5.009% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 02:00 | 1 | 7 | 2 | 7 | 146 | 44.06 | 2822.1373 | 0 | 0 | 2822.1373 | Heating | 2490.1211 | 8.5 | 2490.1211 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 498.0242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2540.9399 | 0 | 508.188 | 5.082% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 03:00 | 1 | 7 | 3 | 7 | 147 | 41 | 2888.0087 | 0 | 0 | 2888.0087 | Heating | 2548.243 | 8.5 | 2548.243 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 509.6486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2600.2479 | 0 | 520.0496 | 5.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 04:00 | 1 | 7 | 4 | 7 | 148 | 41 | 2998.3715 | 0 | 0 | 2998.3715 | Heating | 2645.6219 | 8.5 | 2645.6219 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 529.1244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2699.6142 | 0 | 539.9228 | 5.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 05:00 | 1 | 7 | 5 | 7 | 149 | 41 | 3057.8832 | 0 | 0 | 3057.8832 | Heating | 2698.1323 | 8.5 | 2698.1323 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 539.6265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2753.1962 | 0 | 550.6392 | 5.506% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 06:00 | 1 | 7 | 6 | 7 | 150 | 39.92 | 3143.3988 | 0 | 0 | 3143.3988 | Heating | 2773.5872 | 8.5 | 2773.5872 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 554.7174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2830.191 | 0 | 566.0382 | 5.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 07:00 | 1 | 7 | 7 | 7 | 151 | 41 | 14470.1748 | 0 | 0 | 14470.1748 | Heating | 12767.8013 | 8.5 | 12767.8013 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2553.5603 | 51.07% | 2 | 51.07% | 51.07% | 0% | 0% | 17.3759 | 17.3759 | 0 | 0 | 34.7519 | 13028.3687 | 0 | 2605.6737 | 26.06% | 1 | 52.11% | 0% | 0% | 9.1012 | 0 | 0 | 9.1012 | 43.8531
2007-01-07 08:00 | 1 | 7 | 8 | 7 | 152 | 41 | 12030.3488 | 0 | 0 | 12030.3488 | Heating | 10615.0136 | 8.5 | 10615.0136 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2123.0027 | 42.46% | 1 | 84.92% | 0% | 0% | 0% | 55.9587 | 0 | 0 | 0 | 55.9587 | 10831.6465 | 0 | 2166.3293 | 21.66% | 1 | 43.33% | 0% | 0% | 5.9518 | 0 | 0 | 5.9518 | 61.9105
2007-01-07 09:00 | 1 | 7 | 9 | 7 | 153 | 42.08 | 10403.5055 | 0 | 0 | 10403.5055 | Heating | 9179.5637 | 8.5 | 9179.5637 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1835.9127 | 36.72% | 1 | 73.44% | 0% | 0% | 0% | 40.0627 | 0 | 0 | 0 | 40.0627 | 9366.9017 | 0 | 1873.3803 | 18.73% | 1 | 37.47% | 0% | 0% | 4.2611 | 0 | 0 | 4.2611 | 44.3238
2007-01-07 10:00 | 1 | 7 | 10 | 7 | 154 | 42.98 | 8955.3592 | 0 | 0 | 8955.3592 | Heating | 7901.7875 | 8.5 | 7901.7875 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1580.3575 | 31.61% | 1 | 63.21% | 0% | 0% | 0% | 28.3804 | 0 | 0 | 0 | 28.3804 | 8063.0485 | 0 | 1612.6097 | 16.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.6549
2007-01-07 11:00 | 1 | 7 | 11 | 7 | 155 | 42.98 | 8109.7015 | 0 | 0 | 8109.7015 | Heating | 7155.619 | 8.5 | 7155.619 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1431.1238 | 30% | 1 | 57.24% | 0% | 0% | 0% | 22.5912 | 0 | 0 | 0 | 22.5912 | 7301.6521 | 0 | 1460.3304 | 14.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.8657
2007-01-07 12:00 | 1 | 7 | 12 | 7 | 156 | 44.96 | 7483.7989 | 0 | 0 | 7483.7989 | Heating | 6603.3519 | 8.5 | 6603.3519 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1320.6704 | 30% | 1 | 52.83% | 0% | 0% | 0% | 18.7805 | 0 | 0 | 0 | 18.7805 | 6738.1142 | 0 | 1347.6228 | 13.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.0551
2007-01-07 13:00 | 1 | 7 | 13 | 7 | 157 | 46.04 | 7175.2689 | 0 | 0 | 7175.2689 | Heating | 6331.1196 | 8.5 | 6331.1196 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1266.2239 | 30% | 1 | 50.65% | 0% | 0% | 0% | 17.0473 | 0 | 0 | 0 | 17.0473 | 6460.3262 | 0 | 1292.0652 | 12.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3218
2007-01-07 14:00 | 1 | 7 | 14 | 7 | 158 | 46.04 | 6844.281 | 0 | 0 | 6844.281 | Heating | 6039.0715 | 8.5 | 6039.0715 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1207.8143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6162.3178 | 0 | 1232.4636 | 12.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 15:00 | 1 | 7 | 15 | 7 | 159 | 46.04 | 6582.0558 | 0 | 0 | 6582.0558 | Heating | 5807.6963 | 8.5 | 5807.6963 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1161.5393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5926.2207 | 0 | 1185.2441 | 11.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 16:00 | 1 | 7 | 16 | 7 | 160 | 44.96 | 6563.2599 | 0 | 0 | 6563.2599 | Heating | 5791.1117 | 8.5 | 5791.1117 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1158.2223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5909.2977 | 0 | 1181.8595 | 11.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 17:00 | 1 | 7 | 17 | 7 | 161 | 44.96 | 6618.2238 | 0 | 0 | 6618.2238 | Heating | 5839.6092 | 8.5 | 5839.6092 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1167.9218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5958.7849 | 0 | 1191.757 | 11.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 18:00 | 1 | 7 | 18 | 7 | 162 | 44.06 | 6763.0497 | 0 | 0 | 6763.0497 | Heating | 5967.3968 | 8.5 | 5967.3968 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1193.4794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6089.1804 | 0 | 1217.8361 | 12.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 19:00 | 1 | 7 | 19 | 7 | 163 | 42.98 | 6786.8053 | 0 | 0 | 6786.8053 | Heating | 5988.3577 | 8.5 | 5988.3577 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1197.6715 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6110.569 | 0 | 1222.1138 | 12.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 20:00 | 1 | 7 | 20 | 7 | 164 | 42.98 | 6934.587 | 0 | 0 | 6934.587 | Heating | 6118.7532 | 8.5 | 6118.7532 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1223.7506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6243.6258 | 0 | 1248.7252 | 12.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 21:00 | 1 | 7 | 21 | 7 | 165 | 44.06 | 7087.7924 | 0 | 0 | 7087.7924 | Heating | 6253.9344 | 8.5 | 6253.9344 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1250.7869 | 30% | 1 | 50.03% | 0% | 0% | 0% | 16.5731 | 0 | 0 | 0 | 16.5731 | 6381.5658 | 0 | 1276.3132 | 12.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8476
2007-01-07 22:00 | 1 | 7 | 22 | 7 | 166 | 44.96 | 2249.4669 | 0 | 0 | 2249.4669 | Heating | 1984.8237 | 8.5 | 1984.8237 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 396.9647 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2025.3303 | 0 | 405.0661 | 4.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-07 23:00 | 1 | 7 | 23 | 7 | 167 | 44.96 | 2293.8017 | 0 | 0 | 2293.8017 | Heating | 2023.9427 | 8.5 | 2023.9427 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.7885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2065.2476 | 0 | 413.0495 | 4.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 | 1 | 8 | 0 | 8 | 168 | 42.08 | 2564.0076 | 0 | 0 | 2564.0076 | Heating | 2262.3597 | 8.5 | 2262.3597 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 452.4719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2308.5303 | 0 | 461.7061 | 4.617% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 01:00 | 1 | 8 | 1 | 8 | 169 | 39.02 | 2541.3136 | 0 | 0 | 2541.3136 | Heating | 2242.3355 | 8.5 | 2242.3355 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 448.4671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2288.0975 | 0 | 457.6195 | 4.576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 02:00 | 1 | 8 | 2 | 8 | 170 | 39.02 | 2522.22 | 0 | 0 | 2522.22 | Heating | 2225.4882 | 8.5 | 2225.4882 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.0976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2270.9064 | 0 | 454.1813 | 4.542% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 03:00 | 1 | 8 | 3 | 8 | 171 | 39.2 | 2677.608 | 0 | 0 | 2677.608 | Heating | 2362.5953 | 8.5 | 2362.5953 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 472.5191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2410.8116 | 0 | 482.1623 | 4.822% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 04:00 | 1 | 8 | 4 | 8 | 172 | 39.2 | 2824.2283 | 0 | 0 | 2824.2283 | Heating | 2491.9661 | 8.5 | 2491.9661 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 498.3932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2542.8226 | 0 | 508.5645 | 5.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 05:00 | 1 | 8 | 5 | 8 | 173 | 39.02 | 2921.1836 | 0 | 0 | 2921.1836 | Heating | 2577.5149 | 8.5 | 2577.5149 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 515.503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2630.1173 | 0 | 526.0235 | 5.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 06:00 | 1 | 8 | 6 | 8 | 174 | 39.92 | 2838.4642 | 0 | 0 | 2838.4642 | Heating | 2504.5272 | 8.5 | 2504.5272 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 500.9054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2555.64 | 0 | 511.128 | 5.111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 07:00 | 1 | 8 | 7 | 8 | 175 | 41 | 13594.6413 | 0 | 0 | 13594.6413 | Heating | 11995.2717 | 8.5 | 11995.2717 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2399.0543 | 47.98% | 1 | 95.96% | 0% | 0% | 0% | 74.1265 | 0 | 0 | 0 | 74.1265 | 12240.0732 | 0 | 2448.0146 | 24.48% | 1 | 48.96% | 0% | 0% | 7.8841 | 0 | 0 | 7.8841 | 82.0106
2007-01-08 08:00 | 1 | 8 | 8 | 8 | 176 | 41 | 11457.2025 | 0 | 0 | 11457.2025 | Heating | 10109.2963 | 8.5 | 10109.2963 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2021.8593 | 40.44% | 1 | 80.87% | 0% | 0% | 0% | 50.0159 | 0 | 0 | 0 | 50.0159 | 10315.6085 | 0 | 2063.1217 | 20.63% | 1 | 41.26% | 0% | 0% | 5.3197 | 0 | 0 | 5.3197 | 55.3356
2007-01-08 09:00 | 1 | 8 | 9 | 8 | 177 | 42.8 | 10676.814 | 0 | 0 | 10676.814 | Heating | 9420.7182 | 8.5 | 9420.7182 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1884.1436 | 37.68% | 1 | 75.37% | 0% | 0% | 0% | 42.5249 | 0 | 0 | 0 | 42.5249 | 9612.9778 | 0 | 1922.5956 | 19.23% | 1 | 38.45% | 0% | 0% | 4.523 | 0 | 0 | 4.523 | 47.0479
2007-01-08 10:00 | 1 | 8 | 10 | 8 | 178 | 44.6 | 9725.9313 | 0 | 0 | 9725.9313 | Heating | 8581.7041 | 8.5 | 8581.7041 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1716.3408 | 34.33% | 1 | 68.65% | 0% | 0% | 0% | 34.3138 | 0 | 0 | 0 | 34.3138 | 8756.8409 | 0 | 1751.3682 | 17.51% | 1 | 35.03% | 0% | 0% | 3.6496 | 0 | 0 | 3.6496 | 37.9635
2007-01-08 11:00 | 1 | 8 | 11 | 8 | 179 | 44.06 | 8926.5467 | 0 | 0 | 8926.5467 | Heating | 7876.3647 | 8.5 | 7876.3647 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1575.2729 | 31.51% | 1 | 63.01% | 0% | 0% | 0% | 28.1708 | 0 | 0 | 0 | 28.1708 | 8037.1069 | 0 | 1607.4214 | 16.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.4454
2007-01-08 12:00 | 1 | 8 | 12 | 8 | 180 | 44.6 | 8197.6168 | 0 | 0 | 8197.6168 | Heating | 7233.1913 | 8.5 | 7233.1913 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1446.6383 | 30% | 1 | 57.87% | 0% | 0% | 0% | 23.1584 | 0 | 0 | 0 | 23.1584 | 7380.8075 | 0 | 1476.1615 | 14.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.433
2007-01-08 13:00 | 1 | 8 | 13 | 8 | 181 | 44.6 | 7697.8719 | 0 | 0 | 7697.8719 | Heating | 6792.2399 | 8.5 | 6792.2399 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1358.448 | 30% | 1 | 54.34% | 0% | 0% | 0% | 20.0392 | 0 | 0 | 0 | 20.0392 | 6930.857 | 0 | 1386.1714 | 13.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.3137
2007-01-08 14:00 | 1 | 8 | 14 | 8 | 182 | 44.06 | 7259.2633 | 0 | 0 | 7259.2633 | Heating | 6405.2324 | 8.5 | 6405.2324 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1281.0465 | 30% | 1 | 51.24% | 0% | 0% | 0% | 17.5098 | 0 | 0 | 0 | 17.5098 | 6535.9514 | 0 | 1307.1903 | 13.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7843
2007-01-08 15:00 | 1 | 8 | 15 | 8 | 183 | 46.04 | 7092.0546 | 0 | 0 | 7092.0546 | Heating | 6257.6952 | 8.5 | 6257.6952 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1251.539 | 30% | 1 | 50.06% | 0% | 0% | 0% | 16.596 | 0 | 0 | 0 | 16.596 | 6385.4033 | 0 | 1277.0807 | 12.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8705
2007-01-08 16:00 | 1 | 8 | 16 | 8 | 184 | 44.06 | 7266.6171 | 0 | 0 | 7266.6171 | Heating | 6411.7209 | 8.5 | 6411.7209 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1282.3442 | 30% | 1 | 51.29% | 0% | 0% | 0% | 17.5506 | 0 | 0 | 0 | 17.5506 | 6542.5724 | 0 | 1308.5145 | 13.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.8251
2007-01-08 17:00 | 1 | 8 | 17 | 8 | 185 | 44.06 | 7798.629 | 0 | 0 | 7798.629 | Heating | 6881.1432 | 8.5 | 6881.1432 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1376.2286 | 30% | 1 | 55.05% | 0% | 0% | 0% | 20.6476 | 0 | 0 | 0 | 20.6476 | 7021.5747 | 0 | 1404.3149 | 14.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.9221
2007-01-08 18:00 | 1 | 8 | 18 | 8 | 186 | 39.92 | 8244.1816 | 0 | 0 | 8244.1816 | Heating | 7274.2778 | 8.5 | 7274.2778 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1454.8556 | 30% | 1 | 58.19% | 0% | 0% | 0% | 23.4621 | 0 | 0 | 0 | 23.4621 | 7422.7325 | 0 | 1484.5465 | 14.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.7366
2007-01-08 19:00 | 1 | 8 | 19 | 8 | 187 | 39.02 | 8334.1508 | 0 | 0 | 8334.1508 | Heating | 7353.6625 | 8.5 | 7353.6625 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1470.7325 | 30% | 1 | 58.83% | 0% | 0% | 0% | 24.0552 | 0 | 0 | 0 | 24.0552 | 7503.7372 | 0 | 1500.7474 | 15.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.3297
2007-01-08 20:00 | 1 | 8 | 20 | 8 | 188 | 39.02 | 8726.6709 | 0 | 0 | 8726.6709 | Heating | 7700.0038 | 8.5 | 7700.0038 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1540.0008 | 30.8% | 1 | 61.6% | 0% | 0% | 0% | 26.7411 | 0 | 0 | 0 | 26.7411 | 7857.1467 | 0 | 1571.4293 | 15.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.0156
2007-01-08 21:00 | 1 | 8 | 21 | 8 | 189 | 37.04 | 9141.0227 | 0 | 0 | 9141.0227 | Heating | 8065.6083 | 8.5 | 8065.6083 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1613.1217 | 32.26% | 1 | 64.52% | 0% | 0% | 0% | 29.7519 | 0 | 0 | 0 | 29.7519 | 8230.2125 | 0 | 1646.0425 | 16.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.0265
2007-01-08 22:00 | 1 | 8 | 22 | 8 | 190 | 37.04 | 2997.8748 | 0 | 0 | 2997.8748 | Heating | 2645.1836 | 8.5 | 2645.1836 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 529.0367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2699.167 | 0 | 539.8334 | 5.398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-08 23:00 | 1 | 8 | 23 | 8 | 191 | 37.04 | 3562.7246 | 0 | 0 | 3562.7246 | Heating | 3143.5806 | 8.5 | 3143.5806 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 628.7161 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3207.7353 | 0 | 641.5471 | 6.415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 | 1 | 9 | 0 | 9 | 192 | 35.96 | 3703.6085 | 0 | 0 | 3703.6085 | Heating | 3267.8898 | 8.5 | 3267.8898 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 653.578 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3334.5815 | 0 | 666.9163 | 6.669% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 01:00 | 1 | 9 | 1 | 9 | 193 | 35.06 | 3804.183 | 0 | 0 | 3804.183 | Heating | 3356.6321 | 8.5 | 3356.6321 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 671.3264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3425.1348 | 0 | 685.027 | 6.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 02:00 | 1 | 9 | 2 | 9 | 194 | 35.06 | 4042.6364 | 0 | 0 | 4042.6364 | Heating | 3567.0322 | 8.5 | 3567.0322 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 713.4064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3639.8287 | 0 | 727.9657 | 7.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 03:00 | 1 | 9 | 3 | 9 | 195 | 33.08 | 4206.3995 | 0 | 0 | 4206.3995 | Heating | 3711.529 | 8.5 | 3711.529 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 742.3058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3787.2744 | 0 | 757.4549 | 7.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 04:00 | 1 | 9 | 4 | 9 | 196 | 32 | 4372.4342 | 0 | 0 | 4372.4342 | Heating | 3858.0302 | 8.5 | 3858.0302 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 771.606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3936.7655 | 0 | 787.3531 | 7.874% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 05:00 | 1 | 9 | 5 | 9 | 197 | 32 | 4628.7386 | 0 | 0 | 4628.7386 | Heating | 4084.1811 | 8.5 | 4084.1811 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 816.8362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4167.5318 | 0 | 833.5064 | 8.335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 06:00 | 1 | 9 | 6 | 9 | 198 | 30.92 | 4750.4484 | 0 | 0 | 4750.4484 | Heating | 4191.5721 | 8.5 | 4191.5721 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 838.3144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4277.1144 | 0 | 855.4229 | 8.554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 07:00 | 1 | 9 | 7 | 9 | 199 | 30.92 | 17930.9157 | 0 | 0 | 17930.9157 | Heating | 15821.3962 | 8.5 | 15821.3962 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3164.2792 | 63.29% | 2 | 63.29% | 63.29% | 0% | 0% | 28.454 | 28.454 | 0 | 0 | 56.9081 | 16144.2818 | 0 | 3228.8564 | 32.29% | 1 | 64.58% | 0% | 0% | 14.9037 | 0 | 0 | 14.9037 | 71.8118
2007-01-09 08:00 | 1 | 9 | 8 | 9 | 200 | 30.92 | 15217.6642 | 0 | 0 | 15217.6642 | Heating | 13427.3508 | 8.5 | 13427.3508 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2685.4702 | 53.71% | 2 | 53.71% | 53.71% | 0% | 0% | 19.5101 | 19.5101 | 0 | 0 | 39.0201 | 13701.3783 | 0 | 2740.2757 | 27.4% | 1 | 54.81% | 0% | 0% | 10.219 | 0 | 0 | 10.219 | 49.2391
2007-01-09 09:00 | 1 | 9 | 9 | 9 | 201 | 35.06 | 12929.3702 | 0 | 0 | 12929.3702 | Heating | 11408.2678 | 8.5 | 11408.2678 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2281.6536 | 45.63% | 1 | 91.27% | 0% | 0% | 0% | 66.0473 | 0 | 0 | 0 | 66.0473 | 11641.0896 | 0 | 2328.2179 | 23.28% | 1 | 46.56% | 0% | 0% | 7.0248 | 0 | 0 | 7.0248 | 73.0722
2007-01-09 10:00 | 1 | 9 | 10 | 9 | 202 | 35.96 | 10916.8897 | 0 | 0 | 10916.8897 | Heating | 9632.5498 | 8.5 | 9632.5498 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1926.51 | 38.53% | 1 | 77.06% | 0% | 0% | 0% | 44.7564 | 0 | 0 | 0 | 44.7564 | 9829.1324 | 0 | 1965.8265 | 19.66% | 1 | 39.32% | 0% | 0% | 4.7603 | 0 | 0 | 4.7603 | 49.5167
2007-01-09 11:00 | 1 | 9 | 11 | 9 | 203 | 35.96 | 9577.212 | 0 | 0 | 9577.212 | Heating | 8450.4812 | 8.5 | 8450.4812 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1690.0962 | 33.8% | 1 | 67.6% | 0% | 0% | 0% | 33.119 | 0 | 0 | 0 | 33.119 | 8622.94 | 0 | 1724.588 | 17.25% | 1 | 34.49% | 0% | 0% | 3.5226 | 0 | 0 | 3.5226 | 36.6416
2007-01-09 12:00 | 1 | 9 | 12 | 9 | 204 | 39.02 | 8506.29 | 0 | 0 | 8506.29 | Heating | 7505.55 | 8.5 | 7505.55 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1501.11 | 30.02% | 1 | 60.04% | 0% | 0% | 0% | 25.2133 | 0 | 0 | 0 | 25.2133 | 7658.7244 | 0 | 1531.7449 | 15.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.4879
2007-01-09 13:00 | 1 | 9 | 13 | 9 | 205 | 39.02 | 7844.9788 | 0 | 0 | 7844.9788 | Heating | 6922.0401 | 8.5 | 6922.0401 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1384.408 | 30% | 1 | 55.38% | 0% | 0% | 0% | 20.9309 | 0 | 0 | 0 | 20.9309 | 7063.3062 | 0 | 1412.6612 | 14.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.2055
2007-01-09 14:00 | 1 | 9 | 14 | 9 | 206 | 39.02 | 7418.803 | 0 | 0 | 7418.803 | Heating | 6546.0026 | 8.5 | 6546.0026 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1309.2005 | 30% | 1 | 52.37% | 0% | 0% | 0% | 18.4075 | 0 | 0 | 0 | 18.4075 | 6679.5945 | 0 | 1335.9189 | 13.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.6821
2007-01-09 15:00 | 1 | 9 | 15 | 9 | 207 | 39.02 | 7238.5731 | 0 | 0 | 7238.5731 | Heating | 6386.9763 | 8.5 | 6386.9763 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1277.3953 | 30% | 1 | 51.1% | 0% | 0% | 0% | 17.3952 | 0 | 0 | 0 | 17.3952 | 6517.3228 | 0 | 1303.4646 | 13.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.6697
2007-01-09 16:00 | 1 | 9 | 16 | 9 | 208 | 37.94 | 7119.7917 | 0 | 0 | 7119.7917 | Heating | 6282.1692 | 8.5 | 6282.1692 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1256.4338 | 30% | 1 | 50.26% | 0% | 0% | 0% | 16.7457 | 0 | 0 | 0 | 16.7457 | 6410.3767 | 0 | 1282.0753 | 12.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.0202
2007-01-09 17:00 | 1 | 9 | 17 | 9 | 209 | 37.94 | 7399.7876 | 0 | 0 | 7399.7876 | Heating | 6529.2244 | 8.5 | 6529.2244 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1305.8449 | 30% | 1 | 52.23% | 0% | 0% | 0% | 18.2992 | 0 | 0 | 0 | 18.2992 | 6662.4739 | 0 | 1332.4948 | 13.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.5737
2007-01-09 18:00 | 1 | 9 | 18 | 9 | 210 | 33.98 | 7718.4334 | 0 | 0 | 7718.4334 | Heating | 6810.3824 | 8.5 | 6810.3824 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1362.0765 | 30% | 1 | 54.48% | 0% | 0% | 0% | 20.1625 | 0 | 0 | 0 | 20.1625 | 6949.3698 | 0 | 1389.874 | 13.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.437
2007-01-09 19:00 | 1 | 9 | 19 | 9 | 211 | 33.98 | 7699.8967 | 0 | 0 | 7699.8967 | Heating | 6794.0265 | 8.5 | 6794.0265 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1358.8053 | 30% | 1 | 54.35% | 0% | 0% | 0% | 20.0513 | 0 | 0 | 0 | 20.0513 | 6932.6801 | 0 | 1386.536 | 13.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.3258
2007-01-09 20:00 | 1 | 9 | 20 | 9 | 212 | 33.98 | 8013.189 | 0 | 0 | 8013.189 | Heating | 7070.4609 | 8.5 | 7070.4609 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1414.0922 | 30% | 1 | 56.56% | 0% | 0% | 0% | 21.9776 | 0 | 0 | 0 | 21.9776 | 7214.756 | 0 | 1442.9512 | 14.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.2521
2007-01-09 21:00 | 1 | 9 | 21 | 9 | 213 | 30.02 | 8359.0096 | 0 | 0 | 8359.0096 | Heating | 7375.5967 | 8.5 | 7375.5967 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1475.1193 | 30% | 1 | 59% | 0% | 0% | 0% | 24.2205 | 0 | 0 | 0 | 24.2205 | 7526.1191 | 0 | 1505.2238 | 15.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.4951
2007-01-09 22:00 | 1 | 9 | 22 | 9 | 214 | 30.92 | 2663.5601 | 0 | 0 | 2663.5601 | Heating | 2350.2001 | 8.5 | 2350.2001 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 470.04 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2398.1634 | 0 | 479.6327 | 4.796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-09 23:00 | 1 | 9 | 23 | 9 | 215 | 30.92 | 3015.3371 | 0 | 0 | 3015.3371 | Heating | 2660.5916 | 8.5 | 2660.5916 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 532.1183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2714.8894 | 0 | 542.9779 | 5.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 | 1 | 10 | 0 | 10 | 216 | 30.2 | 3267.5416 | 0 | 0 | 3267.5416 | Heating | 2883.1249 | 8.5 | 2883.1249 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 576.625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2941.9642 | 0 | 588.3928 | 5.884% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 01:00 | 1 | 10 | 1 | 10 | 217 | 30.2 | 3411.7912 | 0 | 0 | 3411.7912 | Heating | 3010.404 | 8.5 | 3010.404 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 602.0808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3071.8408 | 0 | 614.3682 | 6.144% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 02:00 | 1 | 10 | 2 | 10 | 218 | 28.94 | 3550.975 | 0 | 0 | 3550.975 | Heating | 3133.2132 | 8.5 | 3133.2132 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 626.6426 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3197.1564 | 0 | 639.4313 | 6.394% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 03:00 | 1 | 10 | 3 | 10 | 219 | 28.04 | 3614.8333 | 0 | 0 | 3614.8333 | Heating | 3189.5588 | 8.5 | 3189.5588 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 637.9118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3254.6519 | 0 | 650.9304 | 6.509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 04:00 | 1 | 10 | 4 | 10 | 220 | 28.04 | 3673.3262 | 0 | 0 | 3673.3262 | Heating | 3241.1702 | 8.5 | 3241.1702 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 648.234 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3307.3165 | 0 | 661.4633 | 6.615% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 05:00 | 1 | 10 | 5 | 10 | 221 | 28.04 | 3835.5534 | 0 | 0 | 3835.5534 | Heating | 3384.3118 | 8.5 | 3384.3118 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 676.8624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3453.3794 | 0 | 690.6759 | 6.907% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 06:00 | 1 | 10 | 6 | 10 | 222 | 28.4 | 3945.8526 | 0 | 0 | 3945.8526 | Heating | 3481.6346 | 8.5 | 3481.6346 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 696.3269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3552.6884 | 0 | 710.5377 | 7.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 07:00 | 1 | 10 | 7 | 10 | 223 | 28.04 | 16203.0084 | 0 | 0 | 16203.0084 | Heating | 14296.7721 | 8.5 | 14296.7721 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2859.3544 | 57.19% | 2 | 57.19% | 57.19% | 0% | 0% | 22.5387 | 22.5387 | 0 | 0 | 45.0774 | 14588.543 | 0 | 2917.7086 | 29.18% | 1 | 58.35% | 0% | 0% | 11.8053 | 0 | 0 | 11.8053 | 56.8827
2007-01-10 08:00 | 1 | 10 | 8 | 10 | 224 | 28.04 | 13587.7371 | 0 | 0 | 13587.7371 | Heating | 11989.1798 | 8.5 | 11989.1798 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2397.836 | 47.96% | 1 | 95.91% | 0% | 0% | 0% | 74.0399 | 0 | 0 | 0 | 74.0399 | 12233.8569 | 0 | 2446.7714 | 24.47% | 1 | 48.94% | 0% | 0% | 7.8749 | 0 | 0 | 7.8749 | 81.9148
2007-01-10 09:00 | 1 | 10 | 9 | 10 | 225 | 26.06 | 11580.4788 | 0 | 0 | 11580.4788 | Heating | 10218.0695 | 8.5 | 10218.0695 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2043.6139 | 40.87% | 1 | 81.74% | 0% | 0% | 0% | 51.2623 | 0 | 0 | 0 | 51.2623 | 10426.6016 | 0 | 2085.3203 | 20.85% | 1 | 41.71% | 0% | 0% | 5.4523 | 0 | 0 | 5.4523 | 56.7146
2007-01-10 10:00 | 1 | 10 | 10 | 10 | 226 | 26.96 | 9864.7978 | 0 | 0 | 9864.7978 | Heating | 8704.2333 | 8.5 | 8704.2333 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1740.8467 | 34.82% | 1 | 69.63% | 0% | 0% | 0% | 35.4511 | 0 | 0 | 0 | 35.4511 | 8881.8708 | 0 | 1776.3742 | 17.76% | 1 | 35.53% | 0% | 0% | 3.7706 | 0 | 0 | 3.7706 | 39.2217
2007-01-10 11:00 | 1 | 10 | 11 | 10 | 227 | 26.96 | 8922.8781 | 0 | 0 | 8922.8781 | Heating | 7873.1277 | 8.5 | 7873.1277 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1574.6255 | 31.49% | 1 | 62.99% | 0% | 0% | 0% | 28.1442 | 0 | 0 | 0 | 28.1442 | 8033.8038 | 0 | 1606.7608 | 16.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.4187
2007-01-10 12:00 | 1 | 10 | 12 | 10 | 228 | 28.04 | 8119.0202 | 0 | 0 | 8119.0202 | Heating | 7163.8414 | 8.5 | 7163.8414 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1432.7683 | 30% | 1 | 57.31% | 0% | 0% | 0% | 22.6509 | 0 | 0 | 0 | 22.6509 | 7310.0422 | 0 | 1462.0084 | 14.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.9255
2007-01-10 13:00 | 1 | 10 | 13 | 10 | 229 | 28.04 | 7606.1753 | 0 | 0 | 7606.1753 | Heating | 6711.3312 | 8.5 | 6711.3312 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1342.2662 | 30% | 1 | 53.69% | 0% | 0% | 0% | 19.4944 | 0 | 0 | 0 | 19.4944 | 6848.2971 | 0 | 1369.6594 | 13.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.7689
2007-01-10 14:00 | 1 | 10 | 14 | 10 | 230 | 28.04 | 7232.5098 | 0 | 0 | 7232.5098 | Heating | 6381.6263 | 8.5 | 6381.6263 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1276.3253 | 30% | 1 | 51.05% | 0% | 0% | 0% | 17.3617 | 0 | 0 | 0 | 17.3617 | 6511.8636 | 0 | 1302.3727 | 13.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.6362
2007-01-10 15:00 | 1 | 10 | 15 | 10 | 231 | 28.04 | 6948.7627 | 0 | 0 | 6948.7627 | Heating | 6131.2612 | 8.5 | 6131.2612 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1226.2522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6256.389 | 0 | 1251.2778 | 12.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 16:00 | 1 | 10 | 16 | 10 | 232 | 26.06 | 6901.2266 | 0 | 0 | 6901.2266 | Heating | 6089.3176 | 8.5 | 6089.3176 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1217.8635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6213.5894 | 0 | 1242.7179 | 12.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 17:00 | 1 | 10 | 17 | 10 | 233 | 26.06 | 7113.288 | 0 | 0 | 7113.288 | Heating | 6276.4306 | 8.5 | 6276.4306 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1255.2861 | 30% | 1 | 50.21% | 0% | 0% | 0% | 16.7105 | 0 | 0 | 0 | 16.7105 | 6404.521 | 0 | 1280.9042 | 12.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.985
2007-01-10 18:00 | 1 | 10 | 18 | 10 | 234 | 24.08 | 7328.776 | 0 | 0 | 7328.776 | Heating | 6466.5671 | 8.5 | 6466.5671 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1293.3134 | 30% | 1 | 51.73% | 0% | 0% | 0% | 17.8978 | 0 | 0 | 0 | 17.8978 | 6598.5378 | 0 | 1319.7076 | 13.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.1723
2007-01-10 19:00 | 1 | 10 | 19 | 10 | 235 | 23 | 7470.3874 | 0 | 0 | 7470.3874 | Heating | 6591.5183 | 8.5 | 6591.5183 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1318.3037 | 30% | 1 | 52.73% | 0% | 0% | 0% | 18.7032 | 0 | 0 | 0 | 18.7032 | 6726.0391 | 0 | 1345.2078 | 13.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.9778
2007-01-10 20:00 | 1 | 10 | 20 | 10 | 236 | 23 | 7979.9095 | 0 | 0 | 7979.9095 | Heating | 7041.0967 | 8.5 | 7041.0967 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1408.2193 | 30% | 1 | 56.33% | 0% | 0% | 0% | 21.7682 | 0 | 0 | 0 | 21.7682 | 7184.7925 | 0 | 1436.9585 | 14.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.0428
2007-01-10 21:00 | 1 | 10 | 21 | 10 | 237 | 21.02 | 8625.327 | 0 | 0 | 8625.327 | Heating | 7610.5826 | 8.5 | 7610.5826 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1522.1165 | 30.44% | 1 | 60.88% | 0% | 0% | 0% | 26.0322 | 0 | 0 | 0 | 26.0322 | 7765.9006 | 0 | 1553.1801 | 15.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.3068
2007-01-10 22:00 | 1 | 10 | 22 | 10 | 238 | 21.02 | 2808.4851 | 0 | 0 | 2808.4851 | Heating | 2478.0751 | 8.5 | 2478.0751 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 495.615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2528.648 | 0 | 505.7296 | 5.057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-10 23:00 | 1 | 10 | 23 | 10 | 239 | 21.02 | 3089.6912 | 0 | 0 | 3089.6912 | Heating | 2726.1981 | 8.5 | 2726.1981 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 545.2396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2781.8348 | 0 | 556.367 | 5.564% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 | 1 | 11 | 0 | 11 | 240 | 19.04 | 3476.5096 | 0 | 0 | 3476.5096 | Heating | 3067.5085 | 8.5 | 3067.5085 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 613.5017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3130.1107 | 0 | 626.0221 | 6.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 01:00 | 1 | 11 | 1 | 11 | 241 | 19.04 | 3700.8988 | 0 | 0 | 3700.8988 | Heating | 3265.499 | 8.5 | 3265.499 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 653.0998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3332.1418 | 0 | 666.4284 | 6.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 02:00 | 1 | 11 | 2 | 11 | 242 | 19.04 | 3714.8101 | 0 | 0 | 3714.8101 | Heating | 3277.7736 | 8.5 | 3277.7736 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 655.5547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3344.667 | 0 | 668.9334 | 6.689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 03:00 | 1 | 11 | 3 | 11 | 243 | 17.06 | 3757.9502 | 0 | 0 | 3757.9502 | Heating | 3315.8384 | 8.5 | 3315.8384 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 663.1677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3383.5086 | 0 | 676.7017 | 6.767% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 04:00 | 1 | 11 | 4 | 11 | 244 | 14 | 3827.0655 | 0 | 0 | 3827.0655 | Heating | 3376.8225 | 8.5 | 3376.8225 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 675.3645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3445.7372 | 0 | 689.1474 | 6.891% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 05:00 | 1 | 11 | 5 | 11 | 245 | 14 | 3886.5247 | 0 | 0 | 3886.5247 | Heating | 3429.2865 | 8.5 | 3429.2865 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 685.8573 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3499.272 | 0 | 699.8544 | 6.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 06:00 | 1 | 11 | 6 | 11 | 246 | 14 | 4037.7815 | 0 | 0 | 4037.7815 | Heating | 3562.7483 | 8.5 | 3562.7483 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 712.5497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3635.4575 | 0 | 727.0915 | 7.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 07:00 | 1 | 11 | 7 | 11 | 247 | 17.96 | 17266.2479 | 0 | 0 | 17266.2479 | Heating | 15234.9246 | 8.5 | 15234.9246 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3046.9849 | 60.94% | 2 | 60.94% | 60.94% | 0% | 0% | 26.0864 | 26.0864 | 0 | 0 | 52.1728 | 15545.8414 | 0 | 3109.1683 | 31.09% | 1 | 62.18% | 0% | 0% | 13.6636 | 0 | 0 | 13.6636 | 65.8363
2007-01-11 08:00 | 1 | 11 | 8 | 11 | 248 | 19.04 | 14305.6268 | 0 | 0 | 14305.6268 | Heating | 12622.6119 | 8.5 | 12622.6119 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2524.5224 | 50.49% | 2 | 50.49% | 50.49% | 0% | 0% | 16.9248 | 16.9248 | 0 | 0 | 33.8497 | 12880.2162 | 0 | 2576.0432 | 25.76% | 1 | 51.52% | 0% | 0% | 8.8649 | 0 | 0 | 8.8649 | 42.7146
2007-01-11 09:00 | 1 | 11 | 9 | 11 | 249 | 21.92 | 12053.4598 | 0 | 0 | 12053.4598 | Heating | 10635.4057 | 8.5 | 10635.4057 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2127.0811 | 42.54% | 1 | 85.08% | 0% | 0% | 0% | 56.2062 | 0 | 0 | 0 | 56.2062 | 10852.4548 | 0 | 2170.491 | 21.7% | 1 | 43.41% | 0% | 0% | 5.9781 | 0 | 0 | 5.9781 | 62.1843
2007-01-11 10:00 | 1 | 11 | 10 | 11 | 250 | 21.92 | 10219.2646 | 0 | 0 | 10219.2646 | Heating | 9016.9981 | 8.5 | 9016.9981 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1803.3996 | 36.07% | 1 | 72.14% | 0% | 0% | 0% | 38.4497 | 0 | 0 | 0 | 38.4497 | 9201.0185 | 0 | 1840.2037 | 18.4% | 1 | 36.8% | 0% | 0% | 4.0895 | 0 | 0 | 4.0895 | 42.5392
2007-01-11 11:00 | 1 | 11 | 11 | 11 | 251 | 21.92 | 9016.5468 | 0 | 0 | 9016.5468 | Heating | 7955.7766 | 8.5 | 7955.7766 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1591.1553 | 31.82% | 1 | 63.65% | 0% | 0% | 0% | 28.8284 | 0 | 0 | 0 | 28.8284 | 8118.1394 | 0 | 1623.6279 | 16.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.1029
2007-01-11 12:00 | 1 | 11 | 12 | 11 | 252 | 28.04 | 8117.2579 | 0 | 0 | 8117.2579 | Heating | 7162.2864 | 8.5 | 7162.2864 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1432.4573 | 30% | 1 | 57.3% | 0% | 0% | 0% | 22.6396 | 0 | 0 | 0 | 22.6396 | 7308.4555 | 0 | 1461.6911 | 14.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.9142
2007-01-11 13:00 | 1 | 11 | 13 | 11 | 253 | 28.94 | 7470.6037 | 0 | 0 | 7470.6037 | Heating | 6591.7091 | 8.5 | 6591.7091 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1318.3418 | 30% | 1 | 52.73% | 0% | 0% | 0% | 18.7045 | 0 | 0 | 0 | 18.7045 | 6726.2338 | 0 | 1345.2468 | 13.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.979
2007-01-11 14:00 | 1 | 11 | 14 | 11 | 254 | 28.94 | 6985.9022 | 0 | 0 | 6985.9022 | Heating | 6164.0313 | 8.5 | 6164.0313 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1232.8063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6289.8279 | 0 | 1257.9656 | 12.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 15:00 | 1 | 11 | 15 | 11 | 255 | 32 | 6306.7018 | 0 | 0 | 6306.7018 | Heating | 5564.7369 | 8.5 | 5564.7369 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1112.9474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5678.303 | 0 | 1135.6606 | 11.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 16:00 | 1 | 11 | 16 | 11 | 256 | 33.08 | 6244.3246 | 0 | 0 | 6244.3246 | Heating | 5509.6982 | 8.5 | 5509.6982 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1101.9396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5622.141 | 0 | 1124.4282 | 11.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 17:00 | 1 | 11 | 17 | 11 | 257 | 33.08 | 6684.1389 | 0 | 0 | 6684.1389 | Heating | 5897.7697 | 8.5 | 5897.7697 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1179.5539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6018.1323 | 0 | 1203.6265 | 12.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 18:00 | 1 | 11 | 18 | 11 | 258 | 33.08 | 7128.1425 | 0 | 0 | 7128.1425 | Heating | 6289.5375 | 8.5 | 6289.5375 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1257.9075 | 30% | 1 | 50.32% | 0% | 0% | 0% | 16.7909 | 0 | 0 | 0 | 16.7909 | 6417.8954 | 0 | 1283.5791 | 12.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.0654
2007-01-11 19:00 | 1 | 11 | 19 | 11 | 259 | 33.98 | 7113.7912 | 0 | 0 | 7113.7912 | Heating | 6276.8746 | 8.5 | 6276.8746 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1255.3749 | 30% | 1 | 50.21% | 0% | 0% | 0% | 16.7132 | 0 | 0 | 0 | 16.7132 | 6404.9741 | 0 | 1280.9948 | 12.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9878
2007-01-11 20:00 | 1 | 11 | 20 | 11 | 260 | 33.98 | 7383.0432 | 0 | 0 | 7383.0432 | Heating | 6514.4499 | 8.5 | 6514.4499 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1302.89 | 30% | 1 | 52.12% | 0% | 0% | 0% | 18.2041 | 0 | 0 | 0 | 18.2041 | 6647.3979 | 0 | 1329.4796 | 13.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.4786
2007-01-11 21:00 | 1 | 11 | 21 | 11 | 261 | 33.08 | 7779.6273 | 0 | 0 | 7779.6273 | Heating | 6864.377 | 8.5 | 6864.377 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1372.8754 | 30% | 1 | 54.92% | 0% | 0% | 0% | 20.5321 | 0 | 0 | 0 | 20.5321 | 7004.4663 | 0 | 1400.8933 | 14.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.8066
2007-01-11 22:00 | 1 | 11 | 22 | 11 | 262 | 33.98 | 2517.7187 | 0 | 0 | 2517.7187 | Heating | 2221.5165 | 8.5 | 2221.5165 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 444.3033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2266.8536 | 0 | 453.3707 | 4.534% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-11 23:00 | 1 | 11 | 23 | 11 | 263 | 33.98 | 2840.243 | 0 | 0 | 2840.243 | Heating | 2506.0968 | 8.5 | 2506.0968 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 501.2194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2557.2416 | 0 | 511.4483 | 5.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 | 1 | 12 | 0 | 12 | 264 | 33.08 | 3096.6842 | 0 | 0 | 3096.6842 | Heating | 2732.3684 | 8.5 | 2732.3684 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 546.4737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2788.131 | 0 | 557.6262 | 5.576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 01:00 | 1 | 12 | 1 | 12 | 265 | 33.08 | 3121.3798 | 0 | 0 | 3121.3798 | Heating | 2754.1586 | 8.5 | 2754.1586 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.8317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2810.366 | 0 | 562.0732 | 5.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 02:00 | 1 | 12 | 2 | 12 | 266 | 33.08 | 3281.4865 | 0 | 0 | 3281.4865 | Heating | 2895.4293 | 8.5 | 2895.4293 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 579.0859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2954.5197 | 0 | 590.9039 | 5.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 03:00 | 1 | 12 | 3 | 12 | 267 | 33.08 | 3293.2841 | 0 | 0 | 3293.2841 | Heating | 2905.8389 | 8.5 | 2905.8389 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 581.1678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2965.1417 | 0 | 593.0283 | 5.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 04:00 | 1 | 12 | 4 | 12 | 268 | 33.98 | 3309.2727 | 0 | 0 | 3309.2727 | Heating | 2919.9465 | 8.5 | 2919.9465 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 583.9893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2979.5372 | 0 | 595.9074 | 5.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 05:00 | 1 | 12 | 5 | 12 | 269 | 33.98 | 3465.028 | 0 | 0 | 3465.028 | Heating | 3057.3776 | 8.5 | 3057.3776 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 611.4755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3119.7731 | 0 | 623.9546 | 6.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 06:00 | 1 | 12 | 6 | 12 | 270 | 33.98 | 3600.463 | 0 | 0 | 3600.463 | Heating | 3176.8791 | 8.5 | 3176.8791 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 635.3758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3241.7134 | 0 | 648.3427 | 6.483% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 07:00 | 1 | 12 | 7 | 12 | 271 | 33.98 | 15921.0697 | 0 | 0 | 15921.0697 | Heating | 14048.0027 | 8.5 | 14048.0027 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2809.6005 | 56.19% | 2 | 56.19% | 56.19% | 0% | 0% | 21.6468 | 21.6468 | 0 | 0 | 43.2937 | 14334.6966 | 0 | 2866.9393 | 28.67% | 1 | 57.34% | 0% | 0% | 11.3382 | 0 | 0 | 11.3382 | 54.6319
2007-01-12 08:00 | 1 | 12 | 8 | 12 | 272 | 33.98 | 13744.007 | 0 | 0 | 13744.007 | Heating | 12127.065 | 8.5 | 12127.065 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2425.413 | 48.51% | 1 | 97.02% | 0% | 0% | 0% | 76.013 | 0 | 0 | 0 | 76.013 | 12374.5561 | 0 | 2474.9112 | 24.75% | 1 | 49.5% | 0% | 0% | 8.0848 | 0 | 0 | 8.0848 | 84.0978
2007-01-12 09:00 | 1 | 12 | 9 | 12 | 273 | 33.8 | 11886.9973 | 0 | 0 | 11886.9973 | Heating | 10488.527 | 8.5 | 10488.527 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2097.7054 | 41.95% | 1 | 83.91% | 0% | 0% | 0% | 54.4369 | 0 | 0 | 0 | 54.4369 | 10702.5786 | 0 | 2140.5157 | 21.41% | 1 | 42.81% | 0% | 0% | 5.7899 | 0 | 0 | 5.7899 | 60.2268
2007-01-12 10:00 | 1 | 12 | 10 | 12 | 274 | 35.96 | 9730.6558 | 0 | 0 | 9730.6558 | Heating | 8585.8728 | 8.5 | 8585.8728 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1717.1746 | 34.34% | 1 | 68.69% | 0% | 0% | 0% | 34.3522 | 0 | 0 | 0 | 34.3522 | 8761.0947 | 0 | 1752.2189 | 17.52% | 1 | 35.04% | 0% | 0% | 3.6537 | 0 | 0 | 3.6537 | 38.0059
2007-01-12 11:00 | 1 | 12 | 11 | 12 | 275 | 35.96 | 8044.6025 | 0 | 0 | 8044.6025 | Heating | 7098.1787 | 8.5 | 7098.1787 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1419.6357 | 30% | 1 | 56.79% | 0% | 0% | 0% | 22.1762 | 0 | 0 | 0 | 22.1762 | 7243.0395 | 0 | 1448.6079 | 14.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.4508
2007-01-12 12:00 | 1 | 12 | 12 | 12 | 276 | 37.94 | 6999.5497 | 0 | 0 | 6999.5497 | Heating | 6176.0732 | 8.5 | 6176.0732 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1235.2146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6302.1155 | 0 | 1260.4231 | 12.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 13:00 | 1 | 12 | 13 | 12 | 277 | 41 | 6493.3196 | 0 | 0 | 6493.3196 | Heating | 5729.3997 | 8.5 | 5729.3997 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1145.8799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5846.3262 | 0 | 1169.2652 | 11.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 14:00 | 1 | 12 | 14 | 12 | 278 | 41 | 6004.2771 | 0 | 0 | 6004.2771 | Heating | 5297.8915 | 8.5 | 5297.8915 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1059.5783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5406.0118 | 0 | 1081.2024 | 10.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 15:00 | 1 | 12 | 15 | 12 | 279 | 44.06 | 5721.8094 | 0 | 0 | 5721.8094 | Heating | 5048.6554 | 8.5 | 5048.6554 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1009.7311 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5151.6891 | 0 | 1030.3378 | 10.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 16:00 | 1 | 12 | 16 | 12 | 280 | 44.06 | 5764.2342 | 0 | 0 | 5764.2342 | Heating | 5086.089 | 8.5 | 5086.089 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1017.2178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5189.8868 | 0 | 1037.9774 | 10.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 17:00 | 1 | 12 | 17 | 12 | 281 | 44.06 | 6020.3676 | 0 | 0 | 6020.3676 | Heating | 5312.089 | 8.5 | 5312.089 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1062.4178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5420.499 | 0 | 1084.0998 | 10.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 18:00 | 1 | 12 | 18 | 12 | 282 | 42.98 | 6343.9995 | 0 | 0 | 6343.9995 | Heating | 5597.6467 | 8.5 | 5597.6467 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1119.5293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5711.8843 | 0 | 1142.3769 | 11.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 19:00 | 1 | 12 | 19 | 12 | 283 | 44.06 | 6571.8149 | 0 | 0 | 6571.8149 | Heating | 5798.6602 | 8.5 | 5798.6602 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1159.732 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5917.0002 | 0 | 1183.4 | 11.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 20:00 | 1 | 12 | 20 | 12 | 284 | 44.06 | 6915.3212 | 0 | 0 | 6915.3212 | Heating | 6101.754 | 8.5 | 6101.754 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1220.3508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6226.2796 | 0 | 1245.2559 | 12.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 21:00 | 1 | 12 | 21 | 12 | 285 | 44.96 | 6884.1624 | 0 | 0 | 6884.1624 | Heating | 6074.2609 | 8.5 | 6074.2609 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1214.8522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6198.2254 | 0 | 1239.6451 | 12.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-12 22:00 | 1 | 12 | 22 | 12 | 286 | 44.96 | 7170.6467 | 0 | 0 | 7170.6467 | Heating | 6327.0412 | 8.5 | 6327.0412 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1265.4082 | 30% | 1 | 50.62% | 0% | 0% | 0% | 17.022 | 0 | 0 | 0 | 17.022 | 6456.1645 | 0 | 1291.2329 | 12.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2966
2007-01-12 23:00 | 1 | 12 | 23 | 12 | 287 | 44.96 | 2142.3273 | 0 | 0 | 2142.3273 | Heating | 1890.2888 | 8.5 | 1890.2888 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.0578 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1928.8661 | 0 | 385.7732 | 3.858% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 | 1 | 13 | 0 | 13 | 288 | 44.06 | 2139.8194 | 0 | 0 | 2139.8194 | Heating | 1888.076 | 8.5 | 1888.076 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 377.6152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1926.6081 | 0 | 385.3216 | 3.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 01:00 | 1 | 13 | 1 | 13 | 289 | 44.06 | 2124.2366 | 0 | 0 | 2124.2366 | Heating | 1874.3264 | 8.5 | 1874.3264 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.8653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1912.578 | 0 | 382.5156 | 3.825% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 02:00 | 1 | 13 | 2 | 13 | 290 | 44.06 | 2093.5876 | 0 | 0 | 2093.5876 | Heating | 1847.2832 | 8.5 | 1847.2832 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.4566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1884.9828 | 0 | 376.9966 | 3.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 03:00 | 1 | 13 | 3 | 13 | 291 | 42.08 | 2118.5074 | 0 | 0 | 2118.5074 | Heating | 1869.2712 | 8.5 | 1869.2712 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.8542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1907.4196 | 0 | 381.4839 | 3.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 04:00 | 1 | 13 | 4 | 13 | 292 | 42.08 | 2109.7381 | 0 | 0 | 2109.7381 | Heating | 1861.5336 | 8.5 | 1861.5336 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.3067 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1899.5241 | 0 | 379.9048 | 3.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 05:00 | 1 | 13 | 5 | 13 | 293 | 42.08 | 2067.9126 | 0 | 0 | 2067.9126 | Heating | 1824.6288 | 8.5 | 1824.6288 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 364.9258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1861.8661 | 0 | 372.3732 | 3.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 06:00 | 1 | 13 | 6 | 13 | 294 | 44.06 | 2049.943 | 0 | 0 | 2049.943 | Heating | 1808.7733 | 8.5 | 1808.7733 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.7547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1845.687 | 0 | 369.1374 | 3.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 07:00 | 1 | 13 | 7 | 13 | 295 | 44.06 | 1984.2603 | 0 | 0 | 1984.2603 | Heating | 1750.8179 | 8.5 | 1750.8179 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 350.1636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1786.5489 | 0 | 357.3098 | 3.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 08:00 | 1 | 13 | 8 | 13 | 296 | 44.06 | 1955.3079 | 0 | 0 | 1955.3079 | Heating | 1725.2717 | 8.5 | 1725.2717 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 345.0543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1760.4813 | 0 | 352.0963 | 3.521% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 09:00 | 1 | 13 | 9 | 13 | 297 | 42.8 | 10382.4979 | 0 | 0 | 10382.4979 | Heating | 9161.0275 | 8.5 | 9161.0275 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1832.2055 | 36.64% | 1 | 73.29% | 0% | 0% | 0% | 39.8769 | 0 | 0 | 0 | 39.8769 | 9347.9873 | 0 | 1869.5975 | 18.7% | 1 | 37.39% | 0% | 0% | 4.2413 | 0 | 0 | 4.2413 | 44.1183
2007-01-13 10:00 | 1 | 13 | 10 | 13 | 298 | 42.98 | 8272.4035 | 0 | 0 | 8272.4035 | Heating | 7299.1795 | 8.5 | 7299.1795 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1459.8359 | 30% | 1 | 58.39% | 0% | 0% | 0% | 23.6472 | 0 | 0 | 0 | 23.6472 | 7448.1424 | 0 | 1489.6285 | 14.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.9218
2007-01-13 11:00 | 1 | 13 | 11 | 13 | 299 | 42.98 | 7146.4349 | 0 | 0 | 7146.4349 | Heating | 6305.6778 | 8.5 | 6305.6778 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1261.1356 | 30% | 1 | 50.45% | 0% | 0% | 0% | 16.8901 | 0 | 0 | 0 | 16.8901 | 6434.3651 | 0 | 1286.873 | 12.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.1647
2007-01-13 12:00 | 1 | 13 | 12 | 13 | 300 | 42.8 | 6433.1272 | 0 | 0 | 6433.1272 | Heating | 5676.2887 | 8.5 | 5676.2887 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1135.2577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5792.1314 | 0 | 1158.4263 | 11.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 13:00 | 1 | 13 | 13 | 13 | 301 | 39.2 | 5784.7252 | 0 | 0 | 5784.7252 | Heating | 5104.1693 | 8.5 | 5104.1693 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1020.8339 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5208.336 | 0 | 1041.6672 | 10.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 14:00 | 1 | 13 | 14 | 13 | 302 | 37.04 | 5483.3188 | 0 | 0 | 5483.3188 | Heating | 4838.2225 | 8.5 | 4838.2225 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 967.6445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4936.9617 | 0 | 987.3923 | 9.874% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 15:00 | 1 | 13 | 15 | 13 | 303 | 33.98 | 5279.6398 | 0 | 0 | 5279.6398 | Heating | 4658.5057 | 8.5 | 4658.5057 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 931.7011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4753.5773 | 0 | 950.7155 | 9.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 16:00 | 1 | 13 | 16 | 13 | 304 | 33.8 | 5272.6956 | 0 | 0 | 5272.6956 | Heating | 4652.3785 | 8.5 | 4652.3785 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 930.4757 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4747.325 | 0 | 949.465 | 9.495% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 17:00 | 1 | 13 | 17 | 13 | 305 | 32 | 5352.2903 | 0 | 0 | 5352.2903 | Heating | 4722.6091 | 8.5 | 4722.6091 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 944.5218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4818.9888 | 0 | 963.7978 | 9.638% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 18:00 | 1 | 13 | 18 | 13 | 306 | 30.2 | 7387.2563 | 0 | 0 | 7387.2563 | Heating | 6518.1673 | 8.5 | 6518.1673 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1303.6335 | 30% | 1 | 52.15% | 0% | 0% | 0% | 18.228 | 0 | 0 | 0 | 18.228 | 6651.1911 | 0 | 1330.2382 | 13.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.5025
2007-01-13 19:00 | 1 | 13 | 19 | 13 | 307 | 28.94 | 7874.0238 | 0 | 0 | 7874.0238 | Heating | 6947.6681 | 8.5 | 6947.6681 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1389.5336 | 30% | 1 | 55.58% | 0% | 0% | 0% | 21.1096 | 0 | 0 | 0 | 21.1096 | 7089.4572 | 0 | 1417.8914 | 14.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.3841
2007-01-13 20:00 | 1 | 13 | 20 | 13 | 308 | 28.94 | 2047.9016 | 0 | 0 | 2047.9016 | Heating | 1806.972 | 8.5 | 1806.972 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.3944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1843.849 | 0 | 368.7698 | 3.688% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 21:00 | 1 | 13 | 21 | 13 | 309 | 28.04 | 2050.7107 | 0 | 0 | 2050.7107 | Heating | 1809.4507 | 8.5 | 1809.4507 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.8901 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1846.3782 | 0 | 369.2756 | 3.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 22:00 | 1 | 13 | 22 | 13 | 310 | 28.04 | 2061.6485 | 0 | 0 | 2061.6485 | Heating | 1819.1016 | 8.5 | 1819.1016 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.8203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1856.2261 | 0 | 371.2452 | 3.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-13 23:00 | 1 | 13 | 23 | 13 | 311 | 28.04 | 2273.0296 | 0 | 0 | 2273.0296 | Heating | 2005.6144 | 8.5 | 2005.6144 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 401.1229 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2046.5453 | 0 | 409.3091 | 4.093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 | 1 | 14 | 0 | 14 | 312 | 26.6 | 2533.0076 | 0 | 0 | 2533.0076 | Heating | 2235.0067 | 8.5 | 2235.0067 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 447.0013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2280.6191 | 0 | 456.1238 | 4.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 01:00 | 1 | 14 | 1 | 14 | 313 | 26.6 | 2766.5708 | 0 | 0 | 2766.5708 | Heating | 2441.0919 | 8.5 | 2441.0919 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 488.2184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2490.9101 | 0 | 498.182 | 4.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 02:00 | 1 | 14 | 2 | 14 | 314 | 26.96 | 2973.8897 | 0 | 0 | 2973.8897 | Heating | 2624.0203 | 8.5 | 2624.0203 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 524.8041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2677.5718 | 0 | 535.5144 | 5.355% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 03:00 | 1 | 14 | 3 | 14 | 315 | 26.6 | 2775.9811 | 0 | 0 | 2775.9811 | Heating | 2449.3951 | 8.5 | 2449.3951 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 489.879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2499.3828 | 0 | 499.8766 | 4.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 04:00 | 1 | 14 | 4 | 14 | 316 | 26.6 | 2610.6898 | 0 | 0 | 2610.6898 | Heating | 2303.5498 | 8.5 | 2303.5498 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 460.71 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2350.561 | 0 | 470.1122 | 4.701% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 05:00 | 1 | 14 | 5 | 14 | 317 | 26.06 | 2648.6791 | 0 | 0 | 2648.6791 | Heating | 2337.0698 | 8.5 | 2337.0698 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.414 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2384.7651 | 0 | 476.953 | 4.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 06:00 | 1 | 14 | 6 | 14 | 318 | 26.6 | 2704.1509 | 0 | 0 | 2704.1509 | Heating | 2386.0155 | 8.5 | 2386.0155 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 477.2031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2434.7097 | 0 | 486.9419 | 4.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 07:00 | 1 | 14 | 7 | 14 | 319 | 26.6 | 13845.8759 | 0 | 0 | 13845.8759 | Heating | 12216.9494 | 8.5 | 12216.9494 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2443.3899 | 48.87% | 1 | 97.74% | 0% | 0% | 0% | 77.3151 | 0 | 0 | 0 | 77.3151 | 12466.2749 | 0 | 2493.255 | 24.93% | 1 | 49.87% | 0% | 0% | 8.2233 | 0 | 0 | 8.2233 | 85.5384
2007-01-14 08:00 | 1 | 14 | 8 | 14 | 320 | 26.96 | 10971.0883 | 0 | 0 | 10971.0883 | Heating | 9680.3721 | 8.5 | 9680.3721 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1936.0744 | 38.72% | 1 | 77.44% | 0% | 0% | 0% | 45.2691 | 0 | 0 | 0 | 45.2691 | 9877.9307 | 0 | 1975.5861 | 19.76% | 1 | 39.51% | 0% | 0% | 4.8149 | 0 | 0 | 4.8149 | 50.0839
2007-01-14 09:00 | 1 | 14 | 9 | 14 | 321 | 26.6 | 9273.8638 | 0 | 0 | 9273.8638 | Heating | 8182.821 | 8.5 | 8182.821 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1636.5642 | 32.73% | 1 | 65.46% | 0% | 0% | 0% | 30.7558 | 0 | 0 | 0 | 30.7558 | 8349.8173 | 0 | 1669.9635 | 16.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 39.0303
2007-01-14 10:00 | 1 | 14 | 10 | 14 | 322 | 28.4 | 7772.7978 | 0 | 0 | 7772.7978 | Heating | 6858.351 | 8.5 | 6858.351 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1371.6702 | 30% | 1 | 54.87% | 0% | 0% | 0% | 20.4906 | 0 | 0 | 0 | 20.4906 | 6998.3173 | 0 | 1399.6635 | 14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.7652
2007-01-14 11:00 | 1 | 14 | 11 | 14 | 323 | 28.04 | 6907.8563 | 0 | 0 | 6907.8563 | Heating | 6095.1673 | 8.5 | 6095.1673 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1219.0335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6219.5585 | 0 | 1243.9117 | 12.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 12:00 | 1 | 14 | 12 | 14 | 324 | 28.4 | 6135.2364 | 0 | 0 | 6135.2364 | Heating | 5413.4439 | 8.5 | 5413.4439 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1082.6888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5523.9223 | 0 | 1104.7845 | 11.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 13:00 | 1 | 14 | 13 | 14 | 325 | 30.2 | 5481.1196 | 0 | 0 | 5481.1196 | Heating | 4836.282 | 8.5 | 4836.282 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 967.2564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4934.9816 | 0 | 986.9963 | 9.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 14:00 | 1 | 14 | 14 | 14 | 326 | 30.02 | 4788.4035 | 0 | 0 | 4788.4035 | Heating | 4225.0619 | 8.5 | 4225.0619 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 845.0124 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4311.2876 | 0 | 862.2575 | 8.623% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 15:00 | 1 | 14 | 15 | 14 | 327 | 30.2 | 4403.0199 | 0 | 0 | 4403.0199 | Heating | 3885.0175 | 8.5 | 3885.0175 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 777.0035 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3964.3036 | 0 | 792.8607 | 7.929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 16:00 | 1 | 14 | 16 | 14 | 328 | 32 | 4213.7282 | 0 | 0 | 4213.7282 | Heating | 3717.9955 | 8.5 | 3717.9955 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 743.5991 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3793.873 | 0 | 758.7746 | 7.588% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 17:00 | 1 | 14 | 17 | 14 | 329 | 32 | 4202.6587 | 0 | 0 | 4202.6587 | Heating | 3708.2283 | 8.5 | 3708.2283 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 741.6457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3783.9064 | 0 | 756.7813 | 7.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 18:00 | 1 | 14 | 18 | 14 | 330 | 32 | 4329.5657 | 0 | 0 | 4329.5657 | Heating | 3820.205 | 8.5 | 3820.205 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 764.041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3898.1684 | 0 | 779.6337 | 7.796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 19:00 | 1 | 14 | 19 | 14 | 331 | 32 | 4578.8965 | 0 | 0 | 4578.8965 | Heating | 4040.2028 | 8.5 | 4040.2028 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 808.0406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4122.6559 | 0 | 824.5312 | 8.245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 20:00 | 1 | 14 | 20 | 14 | 332 | 30.92 | 4878.8123 | 0 | 0 | 4878.8123 | Heating | 4304.8344 | 8.5 | 4304.8344 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 860.9669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4392.6881 | 0 | 878.5376 | 8.785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 21:00 | 1 | 14 | 21 | 14 | 333 | 28.94 | 5139.8384 | 0 | 0 | 5139.8384 | Heating | 4535.1516 | 8.5 | 4535.1516 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 907.0303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4627.7057 | 0 | 925.5411 | 9.255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 22:00 | 1 | 14 | 22 | 14 | 334 | 28.94 | 1555.0851 | 0 | 0 | 1555.0851 | Heating | 1372.1339 | 8.5 | 1372.1339 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.4268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1400.1366 | 0 | 280.0273 | 2.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-14 23:00 | 1 | 14 | 23 | 14 | 335 | 28.94 | 1404.4424 | 0 | 0 | 1404.4424 | Heating | 1239.2139 | 8.5 | 1239.2139 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.8428 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1264.5039 | 0 | 252.9008 | 2.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 | 1 | 15 | 0 | 15 | 336 | 28.04 | 1672.9382 | 0 | 0 | 1672.9382 | Heating | 1476.1219 | 8.5 | 1476.1219 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.2244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1506.2469 | 0 | 301.2494 | 3.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 01:00 | 1 | 15 | 1 | 15 | 337 | 28.04 | 1694.7366 | 0 | 0 | 1694.7366 | Heating | 1495.3558 | 8.5 | 1495.3558 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 299.0712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1525.8733 | 0 | 305.1747 | 3.052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 02:00 | 1 | 15 | 2 | 15 | 338 | 28.04 | 1794.2712 | 0 | 0 | 1794.2712 | Heating | 1583.1805 | 8.5 | 1583.1805 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 316.6361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1615.4903 | 0 | 323.0981 | 3.231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 03:00 | 1 | 15 | 3 | 15 | 339 | 26.06 | 1835.5339 | 0 | 0 | 1835.5339 | Heating | 1619.5888 | 8.5 | 1619.5888 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.9178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1652.6416 | 0 | 330.5283 | 3.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 04:00 | 1 | 15 | 4 | 15 | 340 | 26.6 | 1835.4316 | 0 | 0 | 1835.4316 | Heating | 1619.4985 | 8.5 | 1619.4985 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.8997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1652.5495 | 0 | 330.5099 | 3.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 05:00 | 1 | 15 | 5 | 15 | 341 | 26.06 | 1862.1521 | 0 | 0 | 1862.1521 | Heating | 1643.0754 | 8.5 | 1643.0754 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.6151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1676.6076 | 0 | 335.3215 | 3.353% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 06:00 | 1 | 15 | 6 | 15 | 342 | 26.6 | 1870.4811 | 0 | 0 | 1870.4811 | Heating | 1650.4245 | 8.5 | 1650.4245 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 330.0849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1684.1066 | 0 | 336.8213 | 3.368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 07:00 | 1 | 15 | 7 | 15 | 343 | 26.96 | 11700.8088 | 0 | 0 | 11700.8088 | Heating | 10324.2431 | 8.5 | 10324.2431 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2064.8486 | 41.3% | 1 | 82.59% | 0% | 0% | 0% | 52.4957 | 0 | 0 | 0 | 52.4957 | 10534.9419 | 0 | 2106.9884 | 21.07% | 1 | 42.14% | 0% | 0% | 5.5835 | 0 | 0 | 5.5835 | 58.0792
2007-01-15 08:00 | 1 | 15 | 8 | 15 | 344 | 26.96 | 8734.8361 | 0 | 0 | 8734.8361 | Heating | 7707.2083 | 8.5 | 7707.2083 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1541.4417 | 30.83% | 1 | 61.66% | 0% | 0% | 0% | 26.7987 | 0 | 0 | 0 | 26.7987 | 7864.4983 | 0 | 1572.8997 | 15.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.0732
2007-01-15 09:00 | 1 | 15 | 9 | 15 | 345 | 28.4 | 7325.0015 | 0 | 0 | 7325.0015 | Heating | 6463.2366 | 8.5 | 6463.2366 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1292.6473 | 30% | 1 | 51.71% | 0% | 0% | 0% | 17.8766 | 0 | 0 | 0 | 17.8766 | 6595.1394 | 0 | 1319.0279 | 13.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.1512
2007-01-15 10:00 | 1 | 15 | 10 | 15 | 346 | 28.4 | 6722.7417 | 0 | 0 | 6722.7417 | Heating | 5931.8309 | 8.5 | 5931.8309 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1186.3662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6052.8887 | 0 | 1210.5777 | 12.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 11:00 | 1 | 15 | 11 | 15 | 347 | 30.2 | 6652.6391 | 0 | 0 | 6652.6391 | Heating | 5869.9756 | 8.5 | 5869.9756 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1173.9951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5989.7711 | 0 | 1197.9542 | 11.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 12:00 | 1 | 15 | 12 | 15 | 348 | 33.8 | 6385.0524 | 0 | 0 | 6385.0524 | Heating | 5633.8698 | 8.5 | 5633.8698 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1126.774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5748.8467 | 0 | 1149.7693 | 11.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 13:00 | 1 | 15 | 13 | 15 | 349 | 33.08 | 6320.1332 | 0 | 0 | 6320.1332 | Heating | 5576.5881 | 8.5 | 5576.5881 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1115.3176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5690.3961 | 0 | 1138.0792 | 11.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 14:00 | 1 | 15 | 14 | 15 | 350 | 33.08 | 6358.2131 | 0 | 0 | 6358.2131 | Heating | 5610.188 | 8.5 | 5610.188 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1122.0376 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5724.6817 | 0 | 1144.9363 | 11.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 15:00 | 1 | 15 | 15 | 15 | 351 | 35.06 | 6496.3609 | 0 | 0 | 6496.3609 | Heating | 5732.0832 | 8.5 | 5732.0832 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1146.4166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5849.0645 | 0 | 1169.8129 | 11.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 16:00 | 1 | 15 | 16 | 15 | 352 | 35.06 | 6972.3193 | 0 | 0 | 6972.3193 | Heating | 6152.0465 | 8.5 | 6152.0465 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1230.4093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6277.5984 | 0 | 1255.5197 | 12.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 17:00 | 1 | 15 | 17 | 15 | 353 | 35.06 | 7661.4881 | 0 | 0 | 7661.4881 | Heating | 6760.1365 | 8.5 | 6760.1365 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1352.0273 | 30% | 1 | 54.08% | 0% | 0% | 0% | 19.822 | 0 | 0 | 0 | 19.822 | 6898.0985 | 0 | 1379.6197 | 13.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.0965
2007-01-15 18:00 | 1 | 15 | 18 | 15 | 354 | 35.96 | 8190.011 | 0 | 0 | 8190.011 | Heating | 7226.4803 | 8.5 | 7226.4803 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1445.2961 | 30% | 1 | 57.81% | 0% | 0% | 0% | 23.109 | 0 | 0 | 0 | 23.109 | 7373.9595 | 0 | 1474.7919 | 14.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.3836
2007-01-15 19:00 | 1 | 15 | 19 | 15 | 355 | 37.4 | 8352.0118 | 0 | 0 | 8352.0118 | Heating | 7369.4222 | 8.5 | 7369.4222 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1473.8844 | 30% | 1 | 58.96% | 0% | 0% | 0% | 24.1739 | 0 | 0 | 0 | 24.1739 | 7519.8185 | 0 | 1503.9637 | 15.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.4485
2007-01-15 20:00 | 1 | 15 | 20 | 15 | 356 | 37.04 | 8759.058 | 0 | 0 | 8759.058 | Heating | 7728.5806 | 8.5 | 7728.5806 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1545.7161 | 30.91% | 1 | 61.83% | 0% | 0% | 0% | 26.9699 | 0 | 0 | 0 | 26.9699 | 7886.3067 | 0 | 1577.2613 | 15.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.2444
2007-01-15 21:00 | 1 | 15 | 21 | 15 | 357 | 37.04 | 9138.1695 | 0 | 0 | 9138.1695 | Heating | 8063.0907 | 8.5 | 8063.0907 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1612.6181 | 32.25% | 1 | 64.5% | 0% | 0% | 0% | 29.7306 | 0 | 0 | 0 | 29.7306 | 8227.6436 | 0 | 1645.5287 | 16.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.0051
2007-01-15 22:00 | 1 | 15 | 22 | 15 | 358 | 37.4 | 2978.8962 | 0 | 0 | 2978.8962 | Heating | 2628.4378 | 8.5 | 2628.4378 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 525.6876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2682.0794 | 0 | 536.4159 | 5.364% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-15 23:00 | 1 | 15 | 23 | 15 | 359 | 37.04 | 3469.7049 | 0 | 0 | 3469.7049 | Heating | 3061.5044 | 8.5 | 3061.5044 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 612.3009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3123.984 | 0 | 624.7968 | 6.248% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 | 1 | 16 | 0 | 16 | 360 | 37.04 | 3995.0066 | 0 | 0 | 3995.0066 | Heating | 3525.0058 | 8.5 | 3525.0058 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 705.0012 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3596.9447 | 0 | 719.3889 | 7.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 01:00 | 1 | 16 | 1 | 16 | 361 | 37.04 | 4181.4039 | 0 | 0 | 4181.4039 | Heating | 3689.474 | 8.5 | 3689.474 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 737.8948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3764.7694 | 0 | 752.9539 | 7.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 02:00 | 1 | 16 | 2 | 16 | 362 | 37.04 | 4260.4604 | 0 | 0 | 4260.4604 | Heating | 3759.2298 | 8.5 | 3759.2298 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 751.846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3835.9488 | 0 | 767.1898 | 7.672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 03:00 | 1 | 16 | 3 | 16 | 363 | 35.6 | 4468.0696 | 0 | 0 | 4468.0696 | Heating | 3942.4143 | 8.5 | 3942.4143 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 788.4829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4022.8718 | 0 | 804.5744 | 8.046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 04:00 | 1 | 16 | 4 | 16 | 364 | 30.92 | 4658.4325 | 0 | 0 | 4658.4325 | Heating | 4110.3816 | 8.5 | 4110.3816 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 822.0763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4194.267 | 0 | 838.8534 | 8.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 05:00 | 1 | 16 | 5 | 16 | 365 | 30.92 | 4839.4398 | 0 | 0 | 4839.4398 | Heating | 4270.0939 | 8.5 | 4270.0939 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 854.0188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4357.2387 | 0 | 871.4477 | 8.714% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 06:00 | 1 | 16 | 6 | 16 | 366 | 28.04 | 4853.0102 | 0 | 0 | 4853.0102 | Heating | 4282.0678 | 8.5 | 4282.0678 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 856.4136 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4369.457 | 0 | 873.8914 | 8.739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 07:00 | 1 | 16 | 7 | 16 | 367 | 26.6 | 18348.4894 | 0 | 0 | 18348.4894 | Heating | 16189.8436 | 8.5 | 16189.8436 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3237.9687 | 64.76% | 2 | 64.76% | 64.76% | 0% | 0% | 30.0012 | 30.0012 | 0 | 0 | 60.0025 | 16520.2485 | 0 | 3304.0497 | 33.04% | 1 | 33.04% | 33.04% | 0% | 3.191 | 3.191 | 0 | 6.3819 | 66.3844
2007-01-16 08:00 | 1 | 16 | 8 | 16 | 368 | 26.96 | 16076.582 | 0 | 0 | 16076.582 | Heating | 14185.2194 | 8.5 | 14185.2194 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2837.0439 | 56.74% | 2 | 56.74% | 56.74% | 0% | 0% | 22.1362 | 22.1362 | 0 | 0 | 44.2725 | 14474.7137 | 0 | 2894.9427 | 28.95% | 1 | 57.9% | 0% | 0% | 11.5946 | 0 | 0 | 11.5946 | 55.867
2007-01-16 09:00 | 1 | 16 | 9 | 16 | 369 | 26.6 | 13843.4868 | 0 | 0 | 13843.4868 | Heating | 12214.8413 | 8.5 | 12214.8413 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2442.9683 | 48.86% | 1 | 97.72% | 0% | 0% | 0% | 77.2844 | 0 | 0 | 0 | 77.2844 | 12464.1237 | 0 | 2492.8247 | 24.93% | 1 | 49.86% | 0% | 0% | 8.22 | 0 | 0 | 8.22 | 85.5045
2007-01-16 10:00 | 1 | 16 | 10 | 16 | 370 | 24.98 | 11752.0408 | 0 | 0 | 11752.0408 | Heating | 10369.4478 | 8.5 | 10369.4478 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2073.8896 | 41.48% | 1 | 82.96% | 0% | 0% | 0% | 53.0259 | 0 | 0 | 0 | 53.0259 | 10581.0692 | 0 | 2116.2138 | 21.16% | 1 | 42.32% | 0% | 0% | 5.6399 | 0 | 0 | 5.6399 | 58.6658
2007-01-16 11:00 | 1 | 16 | 11 | 16 | 371 | 24.98 | 10211.8251 | 0 | 0 | 10211.8251 | Heating | 9010.4339 | 8.5 | 9010.4339 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1802.0868 | 36.04% | 1 | 72.08% | 0% | 0% | 0% | 38.3853 | 0 | 0 | 0 | 38.3853 | 9194.3203 | 0 | 1838.8641 | 18.39% | 1 | 36.78% | 0% | 0% | 4.0827 | 0 | 0 | 4.0827 | 42.468
2007-01-16 12:00 | 1 | 16 | 12 | 16 | 372 | 24.8 | 9165.8395 | 0 | 0 | 9165.8395 | Heating | 8087.5054 | 8.5 | 8087.5054 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1617.5011 | 32.35% | 1 | 64.7% | 0% | 0% | 0% | 29.9381 | 0 | 0 | 0 | 29.9381 | 8252.5565 | 0 | 1650.5113 | 16.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.2126
2007-01-16 13:00 | 1 | 16 | 13 | 16 | 373 | 24.8 | 8447.6027 | 0 | 0 | 8447.6027 | Heating | 7453.767 | 8.5 | 7453.767 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1490.7534 | 30% | 1 | 59.63% | 0% | 0% | 0% | 24.815 | 0 | 0 | 0 | 24.815 | 7605.8847 | 0 | 1521.1769 | 15.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.0896
2007-01-16 14:00 | 1 | 16 | 14 | 16 | 374 | 24.98 | 7777.7055 | 0 | 0 | 7777.7055 | Heating | 6862.6813 | 8.5 | 6862.6813 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1372.5363 | 30% | 1 | 54.9% | 0% | 0% | 0% | 20.5204 | 0 | 0 | 0 | 20.5204 | 7002.736 | 0 | 1400.5472 | 14.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.7949
2007-01-16 15:00 | 1 | 16 | 15 | 16 | 375 | 21.92 | 7437.339 | 0 | 0 | 7437.339 | Heating | 6562.3579 | 8.5 | 6562.3579 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1312.4716 | 30% | 1 | 52.5% | 0% | 0% | 0% | 18.5135 | 0 | 0 | 0 | 18.5135 | 6696.2836 | 0 | 1339.2567 | 13.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.788
2007-01-16 16:00 | 1 | 16 | 16 | 16 | 376 | 21.2 | 7257.5419 | 0 | 0 | 7257.5419 | Heating | 6403.7134 | 8.5 | 6403.7134 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1280.7427 | 30% | 1 | 51.23% | 0% | 0% | 0% | 17.5002 | 0 | 0 | 0 | 17.5002 | 6534.4014 | 0 | 1306.8803 | 13.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7748
2007-01-16 17:00 | 1 | 16 | 17 | 16 | 377 | 21.92 | 7661.5641 | 0 | 0 | 7661.5641 | Heating | 6760.2036 | 8.5 | 6760.2036 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1352.0407 | 30% | 1 | 54.08% | 0% | 0% | 0% | 19.8225 | 0 | 0 | 0 | 19.8225 | 6898.1669 | 0 | 1379.6334 | 13.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.097
2007-01-16 18:00 | 1 | 16 | 18 | 16 | 378 | 19.04 | 8142.7086 | 0 | 0 | 8142.7086 | Heating | 7184.7429 | 8.5 | 7184.7429 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1436.9486 | 30% | 1 | 57.48% | 0% | 0% | 0% | 22.8032 | 0 | 0 | 0 | 22.8032 | 7331.3703 | 0 | 1466.2741 | 14.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.0777
2007-01-16 19:00 | 1 | 16 | 19 | 16 | 379 | 19.04 | 8229.0752 | 0 | 0 | 8229.0752 | Heating | 7260.9487 | 8.5 | 7260.9487 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1452.1897 | 30% | 1 | 58.09% | 0% | 0% | 0% | 23.3633 | 0 | 0 | 0 | 23.3633 | 7409.1314 | 0 | 1481.8263 | 14.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.6379
2007-01-16 20:00 | 1 | 16 | 20 | 16 | 380 | 19.04 | 8581.3197 | 0 | 0 | 8581.3197 | Heating | 7571.7527 | 8.5 | 7571.7527 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1514.3505 | 30.29% | 1 | 60.57% | 0% | 0% | 0% | 25.7277 | 0 | 0 | 0 | 25.7277 | 7726.2783 | 0 | 1545.2557 | 15.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.0023
2007-01-16 21:00 | 1 | 16 | 21 | 16 | 381 | 17.06 | 8703.0651 | 0 | 0 | 8703.0651 | Heating | 7679.1751 | 8.5 | 7679.1751 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1535.835 | 30.72% | 1 | 61.43% | 0% | 0% | 0% | 26.575 | 0 | 0 | 0 | 26.575 | 7835.893 | 0 | 1567.1786 | 15.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.8496
2007-01-16 22:00 | 1 | 16 | 22 | 16 | 382 | 15.08 | 2701.8081 | 0 | 0 | 2701.8081 | Heating | 2383.9484 | 8.5 | 2383.9484 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.7897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2432.6004 | 0 | 486.5201 | 4.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-16 23:00 | 1 | 16 | 23 | 16 | 383 | 15.08 | 2841.9195 | 0 | 0 | 2841.9195 | Heating | 2507.576 | 8.5 | 2507.576 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 501.5152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2558.7511 | 0 | 511.7502 | 5.118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 | 1 | 17 | 0 | 17 | 384 | 12.92 | 3005.5816 | 0 | 0 | 3005.5816 | Heating | 2651.9838 | 8.5 | 2651.9838 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 530.3968 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2706.1059 | 0 | 541.2212 | 5.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 01:00 | 1 | 17 | 1 | 17 | 385 | 12.02 | 3089.0984 | 0 | 0 | 3089.0984 | Heating | 2725.6751 | 8.5 | 2725.6751 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 545.135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2781.3011 | 0 | 556.2602 | 5.563% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 02:00 | 1 | 17 | 2 | 17 | 386 | 12.02 | 3174.0163 | 0 | 0 | 3174.0163 | Heating | 2800.6027 | 8.5 | 2800.6027 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 560.1205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2857.7578 | 0 | 571.5516 | 5.716% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 03:00 | 1 | 17 | 3 | 17 | 387 | 8.96 | 3220.563 | 0 | 0 | 3220.563 | Heating | 2841.6733 | 8.5 | 2841.6733 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 568.3347 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2899.6666 | 0 | 579.9333 | 5.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 04:00 | 1 | 17 | 4 | 17 | 388 | 6.08 | 3147.9075 | 0 | 0 | 3147.9075 | Heating | 2777.5655 | 8.5 | 2777.5655 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 555.5131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2834.2505 | 0 | 566.8501 | 5.669% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 05:00 | 1 | 17 | 5 | 17 | 389 | 6.08 | 3114.8263 | 0 | 0 | 3114.8263 | Heating | 2748.3761 | 8.5 | 2748.3761 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 549.6752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2804.4655 | 0 | 560.8931 | 5.609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 06:00 | 1 | 17 | 6 | 17 | 390 | 3.92 | 3221.0277 | 0 | 0 | 3221.0277 | Heating | 2842.0832 | 8.5 | 2842.0832 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 568.4166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2900.0849 | 0 | 580.017 | 5.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 07:00 | 1 | 17 | 7 | 17 | 391 | 3.02 | 15307.3316 | 0 | 0 | 15307.3316 | Heating | 13506.469 | 8.5 | 13506.469 | 0 | 2.6241 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2701.2938 | 54.03% | 2 | 54.03% | 54.03% | 0% | 0% | 19.7755 | 19.7755 | 0 | 0 | 39.551 | 13782.1113 | 0 | 2756.4223 | 27.56% | 1 | 55.13% | 0% | 0% | 10.358 | 0 | 0 | 10.358 | 49.909
2007-01-17 08:00 | 1 | 17 | 8 | 17 | 392 | 3.02 | 12665.8719 | 0 | 0 | 12665.8719 | Heating | 11175.7693 | 8.5 | 11175.7693 | 0 | 2.6241 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2235.1539 | 44.7% | 1 | 89.41% | 0% | 0% | 0% | 62.9924 | 0 | 0 | 0 | 62.9924 | 11403.8463 | 0 | 2280.7693 | 22.81% | 1 | 45.62% | 0% | 0% | 6.6999 | 0 | 0 | 6.6999 | 69.6923
2007-01-17 09:00 | 1 | 17 | 9 | 17 | 393 | 6.08 | 10815.859 | 0 | 0 | 10815.859 | Heating | 9543.405 | 8.5 | 9543.405 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1908.681 | 38.17% | 1 | 76.35% | 0% | 0% | 0% | 43.8094 | 0 | 0 | 0 | 43.8094 | 9738.1684 | 0 | 1947.6337 | 19.48% | 1 | 38.95% | 0% | 0% | 4.6596 | 0 | 0 | 4.6596 | 48.469
2007-01-17 10:00 | 1 | 17 | 10 | 17 | 394 | 8.06 | 9464.9315 | 0 | 0 | 9464.9315 | Heating | 8351.4102 | 8.5 | 8351.4102 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1670.282 | 33.41% | 1 | 66.81% | 0% | 0% | 0% | 32.2328 | 0 | 0 | 0 | 32.2328 | 8521.8471 | 0 | 1704.3694 | 17.04% | 1 | 34.09% | 0% | 0% | 3.4283 | 0 | 0 | 3.4283 | 35.6611
2007-01-17 11:00 | 1 | 17 | 11 | 17 | 395 | 8.06 | 8288.516 | 0 | 0 | 8288.516 | Heating | 7313.3965 | 8.5 | 7313.3965 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1462.6793 | 30% | 1 | 58.51% | 0% | 0% | 0% | 23.7533 | 0 | 0 | 0 | 23.7533 | 7462.6495 | 0 | 1492.5299 | 14.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.0278
2007-01-17 12:00 | 1 | 17 | 12 | 17 | 396 | 12.92 | 7219.6851 | 0 | 0 | 7219.6851 | Heating | 6370.3104 | 8.5 | 6370.3104 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1274.0621 | 30% | 1 | 50.96% | 0% | 0% | 0% | 17.291 | 0 | 0 | 0 | 17.291 | 6500.3167 | 0 | 1300.0633 | 13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.5655
2007-01-17 13:00 | 1 | 17 | 13 | 17 | 397 | 15.98 | 6651.0699 | 0 | 0 | 6651.0699 | Heating | 5868.5911 | 8.5 | 5868.5911 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1173.7182 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5988.3583 | 0 | 1197.6717 | 11.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 14:00 | 1 | 17 | 14 | 17 | 398 | 15.98 | 6318.2502 | 0 | 0 | 6318.2502 | Heating | 5574.9266 | 8.5 | 5574.9266 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1114.9853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5688.7007 | 0 | 1137.7401 | 11.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 15:00 | 1 | 17 | 15 | 17 | 399 | 17.96 | 6183.8511 | 0 | 0 | 6183.8511 | Heating | 5456.3392 | 8.5 | 5456.3392 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1091.2678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5567.6931 | 0 | 1113.5386 | 11.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 16:00 | 1 | 17 | 16 | 17 | 400 | 17.96 | 5986.9169 | 0 | 0 | 5986.9169 | Heating | 5282.5737 | 8.5 | 5282.5737 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1056.5147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5390.3813 | 0 | 1078.0763 | 10.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 17:00 | 1 | 17 | 17 | 17 | 401 | 17.96 | 5957.7991 | 0 | 0 | 5957.7991 | Heating | 5256.8816 | 8.5 | 5256.8816 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1051.3763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5364.1649 | 0 | 1072.833 | 10.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 18:00 | 1 | 17 | 18 | 17 | 402 | 15.08 | 6012.4496 | 0 | 0 | 6012.4496 | Heating | 5305.1026 | 8.5 | 5305.1026 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1061.0205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5413.37 | 0 | 1082.674 | 10.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 19:00 | 1 | 17 | 19 | 17 | 403 | 15.08 | 6026.9856 | 0 | 0 | 6026.9856 | Heating | 5317.9285 | 8.5 | 5317.9285 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1063.5857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5426.4577 | 0 | 1085.2915 | 10.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 20:00 | 1 | 17 | 20 | 17 | 404 | 15.08 | 6141.7119 | 0 | 0 | 6141.7119 | Heating | 5419.1576 | 8.5 | 5419.1576 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1083.8315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5529.7527 | 0 | 1105.9505 | 11.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 21:00 | 1 | 17 | 21 | 17 | 405 | 14 | 6418.0925 | 0 | 0 | 6418.0925 | Heating | 5663.0228 | 8.5 | 5663.0228 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1132.6046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5778.5947 | 0 | 1155.7189 | 11.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 22:00 | 1 | 17 | 22 | 17 | 406 | 14 | 1925.7357 | 0 | 0 | 1925.7357 | Heating | 1699.1786 | 8.5 | 1699.1786 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.8357 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1733.8557 | 0 | 346.7711 | 3.468% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-17 23:00 | 1 | 17 | 23 | 17 | 407 | 14 | 1812.8857 | 0 | 0 | 1812.8857 | Heating | 1599.605 | 8.5 | 1599.605 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 319.921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1632.25 | 0 | 326.45 | 3.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 | 1 | 18 | 0 | 18 | 408 | 12.92 | 2122.3409 | 0 | 0 | 2122.3409 | Heating | 1872.6537 | 8.5 | 1872.6537 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.5307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1910.8712 | 0 | 382.1742 | 3.822% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 01:00 | 1 | 18 | 1 | 18 | 409 | 12.92 | 2204.5692 | 0 | 0 | 2204.5692 | Heating | 1945.2082 | 8.5 | 1945.2082 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 389.0416 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1984.9063 | 0 | 396.9813 | 3.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 02:00 | 1 | 18 | 2 | 18 | 410 | 12.92 | 2181.1575 | 0 | 0 | 2181.1575 | Heating | 1924.5508 | 8.5 | 1924.5508 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.9102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1963.8273 | 0 | 392.7655 | 3.928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 03:00 | 1 | 18 | 3 | 18 | 411 | 14 | 2261.9968 | 0 | 0 | 2261.9968 | Heating | 1995.8795 | 8.5 | 1995.8795 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 399.1759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2036.6118 | 0 | 407.3224 | 4.073% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 04:00 | 1 | 18 | 4 | 18 | 412 | 15.08 | 2331.7089 | 0 | 0 | 2331.7089 | Heating | 2057.3902 | 8.5 | 2057.3902 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2099.3778 | 0 | 419.8756 | 4.199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 05:00 | 1 | 18 | 5 | 18 | 413 | 15.08 | 2371.3719 | 0 | 0 | 2371.3719 | Heating | 2092.387 | 8.5 | 2092.387 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 418.4774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2135.0888 | 0 | 427.0178 | 4.27% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 06:00 | 1 | 18 | 6 | 18 | 414 | 15.98 | 2345.9386 | 0 | 0 | 2345.9386 | Heating | 2069.9458 | 8.5 | 2069.9458 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 413.9892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2112.1896 | 0 | 422.4379 | 4.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 07:00 | 1 | 18 | 7 | 18 | 415 | 17.06 | 13229.3985 | 0 | 0 | 13229.3985 | Heating | 11672.9987 | 8.5 | 11672.9987 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2334.5997 | 46.69% | 1 | 93.38% | 0% | 0% | 0% | 69.6257 | 0 | 0 | 0 | 69.6257 | 11911.2232 | 0 | 2382.2446 | 23.82% | 1 | 47.64% | 0% | 0% | 7.4054 | 0 | 0 | 7.4054 | 77.0311
2007-01-18 08:00 | 1 | 18 | 8 | 18 | 416 | 17.96 | 10842.0564 | 0 | 0 | 10842.0564 | Heating | 9566.5204 | 8.5 | 9566.5204 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1913.3041 | 38.27% | 1 | 76.53% | 0% | 0% | 0% | 44.0539 | 0 | 0 | 0 | 44.0539 | 9761.7555 | 0 | 1952.3511 | 19.52% | 1 | 39.05% | 0% | 0% | 4.6856 | 0 | 0 | 4.6856 | 48.7395
2007-01-18 09:00 | 1 | 18 | 9 | 18 | 417 | 21.92 | 9402.2631 | 0 | 0 | 9402.2631 | Heating | 8296.1145 | 8.5 | 8296.1145 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1659.2229 | 33.18% | 1 | 66.37% | 0% | 0% | 0% | 31.744 | 0 | 0 | 0 | 31.744 | 8465.423 | 0 | 1693.0846 | 16.93% | 1 | 33.86% | 0% | 0% | 3.3763 | 0 | 0 | 3.3763 | 35.1203
2007-01-18 10:00 | 1 | 18 | 10 | 18 | 418 | 24.08 | 7220.4164 | 0 | 0 | 7220.4164 | Heating | 6370.9556 | 8.5 | 6370.9556 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1274.1911 | 30% | 1 | 50.97% | 0% | 0% | 0% | 17.295 | 0 | 0 | 0 | 17.295 | 6500.9751 | 0 | 1300.195 | 13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.5695
2007-01-18 11:00 | 1 | 18 | 11 | 18 | 419 | 24.08 | 5983.4483 | 0 | 0 | 5983.4483 | Heating | 5279.5132 | 8.5 | 5279.5132 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1055.9026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5387.2583 | 0 | 1077.4517 | 10.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 12:00 | 1 | 18 | 12 | 18 | 420 | 28.94 | 5138.813 | 0 | 0 | 5138.813 | Heating | 4534.2468 | 8.5 | 4534.2468 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 906.8494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4626.7824 | 0 | 925.3565 | 9.254% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 13:00 | 1 | 18 | 13 | 18 | 421 | 28.94 | 4448.8985 | 0 | 0 | 4448.8985 | Heating | 3925.4987 | 8.5 | 3925.4987 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 785.0997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4005.6109 | 0 | 801.1222 | 8.011% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 14:00 | 1 | 18 | 14 | 18 | 422 | 28.94 | 4028.4517 | 0 | 0 | 4028.4517 | Heating | 3554.5162 | 8.5 | 3554.5162 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 710.9032 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3627.0574 | 0 | 725.4115 | 7.254% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 15:00 | 1 | 18 | 15 | 18 | 423 | 32 | 4081.3217 | 0 | 0 | 4081.3217 | Heating | 3601.1662 | 8.5 | 3601.1662 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 720.2332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3674.6594 | 0 | 734.9319 | 7.349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 16:00 | 1 | 18 | 16 | 18 | 424 | 33.98 | 4216.3397 | 0 | 0 | 4216.3397 | Heating | 3720.2997 | 8.5 | 3720.2997 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 744.0599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3796.2242 | 0 | 759.2448 | 7.592% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 17:00 | 1 | 18 | 17 | 18 | 425 | 33.98 | 4366.9703 | 0 | 0 | 4366.9703 | Heating | 3853.2091 | 8.5 | 3853.2091 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 770.6418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3931.846 | 0 | 786.3692 | 7.864% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 18:00 | 1 | 18 | 18 | 18 | 426 | 33.98 | 4649.4375 | 0 | 0 | 4649.4375 | Heating | 4102.4449 | 8.5 | 4102.4449 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 820.489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4186.1682 | 0 | 837.2336 | 8.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 19:00 | 1 | 18 | 19 | 18 | 427 | 33.08 | 5172.2865 | 0 | 0 | 5172.2865 | Heating | 4563.7822 | 8.5 | 4563.7822 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 912.7564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4656.9206 | 0 | 931.3841 | 9.314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 20:00 | 1 | 18 | 20 | 18 | 428 | 33.08 | 5885.2163 | 0 | 0 | 5885.2163 | Heating | 5192.8379 | 8.5 | 5192.8379 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1038.5676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5298.8142 | 0 | 1059.7628 | 10.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 21:00 | 1 | 18 | 21 | 18 | 429 | 33.08 | 6426.5328 | 0 | 0 | 6426.5328 | Heating | 5670.4701 | 8.5 | 5670.4701 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1134.094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5786.194 | 0 | 1157.2388 | 11.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 22:00 | 1 | 18 | 22 | 18 | 430 | 32 | 1990.6164 | 0 | 0 | 1990.6164 | Heating | 1756.4262 | 8.5 | 1756.4262 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 351.2852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1792.2717 | 0 | 358.4543 | 3.585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-18 23:00 | 1 | 18 | 23 | 18 | 431 | 32 | 1918.1066 | 0 | 0 | 1918.1066 | Heating | 1692.447 | 8.5 | 1692.447 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 338.4894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1726.9868 | 0 | 345.3974 | 3.454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 | 1 | 19 | 0 | 19 | 432 | 32 | 2188.7375 | 0 | 0 | 2188.7375 | Heating | 1931.239 | 8.5 | 1931.239 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 386.2478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1970.652 | 0 | 394.1304 | 3.941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 01:00 | 1 | 19 | 1 | 19 | 433 | 30.92 | 2323.2163 | 0 | 0 | 2323.2163 | Heating | 2049.8967 | 8.5 | 2049.8967 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.9793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2091.7314 | 0 | 418.3463 | 4.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 02:00 | 1 | 19 | 2 | 19 | 434 | 30.92 | 2436.8003 | 0 | 0 | 2436.8003 | Heating | 2150.118 | 8.5 | 2150.118 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 430.0236 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2193.9979 | 0 | 438.7996 | 4.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 03:00 | 1 | 19 | 3 | 19 | 435 | 30.02 | 2527.3718 | 0 | 0 | 2527.3718 | Heating | 2230.0339 | 8.5 | 2230.0339 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 446.0068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2275.5448 | 0 | 455.109 | 4.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 04:00 | 1 | 19 | 4 | 19 | 436 | 30.2 | 2461.5637 | 0 | 0 | 2461.5637 | Heating | 2171.968 | 8.5 | 2171.968 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 434.3936 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2216.2939 | 0 | 443.2588 | 4.433% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 05:00 | 1 | 19 | 5 | 19 | 437 | 30.02 | 2415.5506 | 0 | 0 | 2415.5506 | Heating | 2131.3682 | 8.5 | 2131.3682 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.2736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2174.8655 | 0 | 434.9731 | 4.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 06:00 | 1 | 19 | 6 | 19 | 438 | 28.4 | 2405.6756 | 0 | 0 | 2405.6756 | Heating | 2122.6549 | 8.5 | 2122.6549 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2165.9744 | 0 | 433.1949 | 4.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 07:00 | 1 | 19 | 7 | 19 | 439 | 28.4 | 12560.1563 | 0 | 0 | 12560.1563 | Heating | 11082.4908 | 8.5 | 11082.4908 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2216.4982 | 44.33% | 1 | 88.66% | 0% | 0% | 0% | 61.7897 | 0 | 0 | 0 | 61.7897 | 11308.6641 | 0 | 2261.7328 | 22.62% | 1 | 45.23% | 0% | 0% | 6.572 | 0 | 0 | 6.572 | 68.3617
2007-01-19 08:00 | 1 | 19 | 8 | 19 | 440 | 28.94 | 9785.0175 | 0 | 0 | 9785.0175 | Heating | 8633.839 | 8.5 | 8633.839 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1726.7678 | 34.54% | 1 | 69.07% | 0% | 0% | 0% | 34.7952 | 0 | 0 | 0 | 34.7952 | 8810.0398 | 0 | 1762.008 | 17.62% | 1 | 35.24% | 0% | 0% | 3.7008 | 0 | 0 | 3.7008 | 38.496
2007-01-19 09:00 | 1 | 19 | 9 | 19 | 441 | 28.4 | 8107.8952 | 0 | 0 | 8107.8952 | Heating | 7154.0252 | 8.5 | 7154.0252 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1430.805 | 30% | 1 | 57.23% | 0% | 0% | 0% | 22.5796 | 0 | 0 | 0 | 22.5796 | 7300.0257 | 0 | 1460.0051 | 14.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.8541
2007-01-19 10:00 | 1 | 19 | 10 | 19 | 442 | 28.4 | 6932.7071 | 0 | 0 | 6932.7071 | Heating | 6117.0945 | 8.5 | 6117.0945 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1223.4189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6241.9332 | 0 | 1248.3866 | 12.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 11:00 | 1 | 19 | 11 | 19 | 443 | 28.94 | 5904.0375 | 0 | 0 | 5904.0375 | Heating | 5209.4448 | 8.5 | 5209.4448 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1041.889 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5315.76 | 0 | 1063.152 | 10.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 12:00 | 1 | 19 | 12 | 19 | 444 | 32 | 5134.324 | 0 | 0 | 5134.324 | Heating | 4530.2859 | 8.5 | 4530.2859 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 906.0572 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4622.7407 | 0 | 924.5481 | 9.245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 13:00 | 1 | 19 | 13 | 19 | 445 | 35.96 | 4775.6981 | 0 | 0 | 4775.6981 | Heating | 4213.8513 | 8.5 | 4213.8513 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 842.7703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4299.8482 | 0 | 859.9696 | 8.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 14:00 | 1 | 19 | 14 | 19 | 446 | 35.96 | 4581.8115 | 0 | 0 | 4581.8115 | Heating | 4042.7748 | 8.5 | 4042.7748 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 808.555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4125.2805 | 0 | 825.0561 | 8.251% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 15:00 | 1 | 19 | 15 | 19 | 447 | 35.06 | 4814.6389 | 0 | 0 | 4814.6389 | Heating | 4248.2108 | 8.5 | 4248.2108 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 849.6422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4334.9089 | 0 | 866.9818 | 8.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 16:00 | 1 | 19 | 16 | 19 | 448 | 35.06 | 5009.8656 | 0 | 0 | 5009.8656 | Heating | 4420.4697 | 8.5 | 4420.4697 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 884.0939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4510.6834 | 0 | 902.1367 | 9.021% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 17:00 | 1 | 19 | 17 | 19 | 449 | 35.06 | 4912.8792 | 0 | 0 | 4912.8792 | Heating | 4334.8934 | 8.5 | 4334.8934 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 866.9787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4423.3606 | 0 | 884.6721 | 8.847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 18:00 | 1 | 19 | 18 | 19 | 450 | 33.08 | 5122.6577 | 0 | 0 | 5122.6577 | Heating | 4519.9921 | 8.5 | 4519.9921 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 903.9984 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4612.2368 | 0 | 922.4474 | 9.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 19:00 | 1 | 19 | 19 | 19 | 451 | 30.92 | 5527.3033 | 0 | 0 | 5527.3033 | Heating | 4877.0323 | 8.5 | 4877.0323 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 975.4065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4976.5636 | 0 | 995.3127 | 9.953% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 20:00 | 1 | 19 | 20 | 19 | 452 | 30.92 | 6283.8808 | 0 | 0 | 6283.8808 | Heating | 5544.6007 | 8.5 | 5544.6007 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1108.9201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5657.7558 | 0 | 1131.5512 | 11.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 21:00 | 1 | 19 | 21 | 19 | 453 | 30.2 | 6594.8159 | 0 | 0 | 6594.8159 | Heating | 5818.9552 | 8.5 | 5818.9552 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1163.791 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5937.7094 | 0 | 1187.5419 | 11.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-19 22:00 | 1 | 19 | 22 | 19 | 454 | 30.2 | 7256.2896 | 0 | 0 | 7256.2896 | Heating | 6402.6084 | 8.5 | 6402.6084 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1280.5217 | 30% | 1 | 51.22% | 0% | 0% | 0% | 17.4933 | 0 | 0 | 0 | 17.4933 | 6533.2739 | 0 | 1306.6548 | 13.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7678
2007-01-19 23:00 | 1 | 19 | 23 | 19 | 455 | 30.02 | 2407.7909 | 0 | 0 | 2407.7909 | Heating | 2124.5214 | 8.5 | 2124.5214 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.9043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2167.879 | 0 | 433.5758 | 4.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 | 1 | 20 | 0 | 20 | 456 | 28.94 | 2473.831 | 0 | 0 | 2473.831 | Heating | 2182.7921 | 8.5 | 2182.7921 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 436.5584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2227.3389 | 0 | 445.4678 | 4.455% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 01:00 | 1 | 20 | 1 | 20 | 457 | 28.04 | 2608.3876 | 0 | 0 | 2608.3876 | Heating | 2301.5185 | 8.5 | 2301.5185 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 460.3037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2348.4882 | 0 | 469.6976 | 4.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 02:00 | 1 | 20 | 2 | 20 | 458 | 28.04 | 2872.9596 | 0 | 0 | 2872.9596 | Heating | 2534.9643 | 8.5 | 2534.9643 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 506.9929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2586.6983 | 0 | 517.3397 | 5.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 03:00 | 1 | 20 | 3 | 20 | 459 | 26.96 | 3079.1414 | 0 | 0 | 3079.1414 | Heating | 2716.8895 | 8.5 | 2716.8895 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 543.3779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2772.3362 | 0 | 554.4672 | 5.545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 04:00 | 1 | 20 | 4 | 20 | 460 | 26.96 | 3277.8646 | 0 | 0 | 3277.8646 | Heating | 2892.2335 | 8.5 | 2892.2335 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 578.4467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2951.2586 | 0 | 590.2517 | 5.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 05:00 | 1 | 20 | 5 | 20 | 461 | 26.96 | 3382.2697 | 0 | 0 | 3382.2697 | Heating | 2984.3556 | 8.5 | 2984.3556 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 596.8711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3045.2608 | 0 | 609.0522 | 6.091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 06:00 | 1 | 20 | 6 | 20 | 462 | 24.98 | 3488.2981 | 0 | 0 | 3488.2981 | Heating | 3077.9101 | 8.5 | 3077.9101 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 615.582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3140.7246 | 0 | 628.1449 | 6.281% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 07:00 | 1 | 20 | 7 | 20 | 463 | 24.98 | 3493.5204 | 0 | 0 | 3493.5204 | Heating | 3082.518 | 8.5 | 3082.518 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 616.5036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3145.4266 | 0 | 629.0853 | 6.291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 08:00 | 1 | 20 | 8 | 20 | 464 | 24.98 | 3508.6455 | 0 | 0 | 3508.6455 | Heating | 3095.8637 | 8.5 | 3095.8637 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 619.1727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3159.0445 | 0 | 631.8089 | 6.318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 09:00 | 1 | 20 | 9 | 20 | 465 | 23 | 14589.4776 | 0 | 0 | 14589.4776 | Heating | 12873.0685 | 8.5 | 12873.0685 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2574.6137 | 51.49% | 2 | 51.49% | 51.49% | 0% | 0% | 17.7072 | 17.7072 | 0 | 0 | 35.4144 | 13135.7842 | 0 | 2627.1568 | 26.27% | 1 | 52.54% | 0% | 0% | 9.2747 | 0 | 0 | 9.2747 | 44.6891
2007-01-20 10:00 | 1 | 20 | 10 | 20 | 466 | 21.02 | 12455.3227 | 0 | 0 | 12455.3227 | Heating | 10989.9906 | 8.5 | 10989.9906 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2197.9981 | 43.96% | 1 | 87.92% | 0% | 0% | 0% | 60.6099 | 0 | 0 | 0 | 60.6099 | 11214.2761 | 0 | 2242.8552 | 22.43% | 1 | 44.86% | 0% | 0% | 6.4465 | 0 | 0 | 6.4465 | 67.0565
2007-01-20 11:00 | 1 | 20 | 11 | 20 | 467 | 21.02 | 11142.1201 | 0 | 0 | 11142.1201 | Heating | 9831.2824 | 8.5 | 9831.2824 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1966.2565 | 39.33% | 1 | 78.65% | 0% | 0% | 0% | 46.9087 | 0 | 0 | 0 | 46.9087 | 10031.9209 | 0 | 2006.3842 | 20.06% | 1 | 40.13% | 0% | 0% | 4.9892 | 0 | 0 | 4.9892 | 51.8979
2007-01-20 12:00 | 1 | 20 | 12 | 20 | 468 | 19.94 | 10281.0562 | 0 | 0 | 10281.0562 | Heating | 9071.5201 | 8.5 | 9071.5201 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1814.304 | 36.29% | 1 | 72.57% | 0% | 0% | 0% | 38.9865 | 0 | 0 | 0 | 38.9865 | 9256.6532 | 0 | 1851.3306 | 18.51% | 1 | 37.03% | 0% | 0% | 4.1466 | 0 | 0 | 4.1466 | 43.1331
2007-01-20 13:00 | 1 | 20 | 13 | 20 | 469 | 19.94 | 8996.6364 | 0 | 0 | 8996.6364 | Heating | 7938.2086 | 8.5 | 7938.2086 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1587.6417 | 31.75% | 1 | 63.51% | 0% | 0% | 0% | 28.6822 | 0 | 0 | 0 | 28.6822 | 8100.2129 | 0 | 1620.0426 | 16.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.9567
2007-01-20 14:00 | 1 | 20 | 14 | 20 | 470 | 19.94 | 8503.6595 | 0 | 0 | 8503.6595 | Heating | 7503.229 | 8.5 | 7503.229 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1500.6458 | 30.01% | 1 | 60.03% | 0% | 0% | 0% | 25.1954 | 0 | 0 | 0 | 25.1954 | 7656.3561 | 0 | 1531.2712 | 15.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.4699
2007-01-20 15:00 | 1 | 20 | 15 | 20 | 471 | 19.04 | 8476.6478 | 0 | 0 | 8476.6478 | Heating | 7479.3952 | 8.5 | 7479.3952 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1495.879 | 30% | 1 | 59.84% | 0% | 0% | 0% | 25.0117 | 0 | 0 | 0 | 25.0117 | 7632.0359 | 0 | 1526.4072 | 15.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.2862
2007-01-20 16:00 | 1 | 20 | 16 | 20 | 472 | 17.96 | 8711.9699 | 0 | 0 | 8711.9699 | Heating | 7687.0322 | 8.5 | 7687.0322 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1537.4064 | 30.75% | 1 | 61.5% | 0% | 0% | 0% | 26.6376 | 0 | 0 | 0 | 26.6376 | 7843.9104 | 0 | 1568.7821 | 15.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.9121
2007-01-20 17:00 | 1 | 20 | 17 | 20 | 473 | 17.96 | 8842.7424 | 0 | 0 | 8842.7424 | Heating | 7802.4197 | 8.5 | 7802.4197 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1560.4839 | 31.21% | 1 | 62.42% | 0% | 0% | 0% | 27.5662 | 0 | 0 | 0 | 27.5662 | 7961.6528 | 0 | 1592.3306 | 15.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.8408
2007-01-20 18:00 | 1 | 20 | 18 | 20 | 474 | 15.98 | 11697.6013 | 0 | 0 | 11697.6013 | Heating | 10321.4129 | 8.5 | 10321.4129 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2064.2826 | 41.29% | 1 | 82.57% | 0% | 0% | 0% | 52.4626 | 0 | 0 | 0 | 52.4626 | 10532.054 | 0 | 2106.4108 | 21.06% | 1 | 42.13% | 0% | 0% | 5.58 | 0 | 0 | 5.58 | 58.0426
2007-01-20 19:00 | 1 | 20 | 19 | 20 | 475 | 15.08 | 12366.4596 | 0 | 0 | 12366.4596 | Heating | 10911.582 | 8.5 | 10911.582 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2182.3164 | 43.65% | 1 | 87.29% | 0% | 0% | 0% | 59.62 | 0 | 0 | 0 | 59.62 | 11134.2674 | 0 | 2226.8535 | 22.27% | 1 | 44.54% | 0% | 0% | 6.3412 | 0 | 0 | 6.3412 | 65.9612
2007-01-20 20:00 | 1 | 20 | 20 | 20 | 476 | 15.08 | 3613.9406 | 0 | 0 | 3613.9406 | Heating | 3188.7711 | 8.5 | 3188.7711 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 637.7542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3253.8481 | 0 | 650.7696 | 6.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 21:00 | 1 | 20 | 21 | 20 | 477 | 14 | 3800.0379 | 0 | 0 | 3800.0379 | Heating | 3352.9746 | 8.5 | 3352.9746 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 670.5949 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3421.4027 | 0 | 684.2805 | 6.843% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 22:00 | 1 | 20 | 22 | 20 | 478 | 12.92 | 3764.072 | 0 | 0 | 3764.072 | Heating | 3321.24 | 8.5 | 3321.24 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 664.248 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3389.0204 | 0 | 677.8041 | 6.778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-20 23:00 | 1 | 20 | 23 | 20 | 479 | 12.92 | 3722.8066 | 0 | 0 | 3722.8066 | Heating | 3284.8294 | 8.5 | 3284.8294 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 656.9659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3351.8667 | 0 | 670.3733 | 6.704% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 | 1 | 21 | 0 | 21 | 480 | 12.02 | 3963.7331 | 0 | 0 | 3963.7331 | Heating | 3497.4115 | 8.5 | 3497.4115 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 699.4823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3568.7873 | 0 | 713.7575 | 7.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 01:00 | 1 | 21 | 1 | 21 | 481 | 10.94 | 4156.9806 | 0 | 0 | 4156.9806 | Heating | 3667.9241 | 8.5 | 3667.9241 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 733.5848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3742.7797 | 0 | 748.5559 | 7.486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 02:00 | 1 | 21 | 2 | 21 | 482 | 10.94 | 4126.6409 | 0 | 0 | 4126.6409 | Heating | 3641.1538 | 8.5 | 3641.1538 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 728.2308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3715.463 | 0 | 743.0926 | 7.431% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 03:00 | 1 | 21 | 3 | 21 | 483 | 10.04 | 4264.2425 | 0 | 0 | 4264.2425 | Heating | 3762.5669 | 8.5 | 3762.5669 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 752.5134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3839.354 | 0 | 767.8708 | 7.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 04:00 | 1 | 21 | 4 | 21 | 484 | 8.96 | 4463.7385 | 0 | 0 | 4463.7385 | Heating | 3938.5928 | 8.5 | 3938.5928 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 787.7186 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4018.9722 | 0 | 803.7944 | 8.038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 05:00 | 1 | 21 | 5 | 21 | 485 | 8.96 | 4593.181 | 0 | 0 | 4593.181 | Heating | 4052.8068 | 8.5 | 4052.8068 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 810.5614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4135.5171 | 0 | 827.1034 | 8.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 06:00 | 1 | 21 | 6 | 21 | 486 | 6.98 | 4693.1112 | 0 | 0 | 4693.1112 | Heating | 4140.9805 | 8.5 | 4140.9805 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 828.1961 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4225.4903 | 0 | 845.0981 | 8.451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 07:00 | 1 | 21 | 7 | 21 | 487 | 6.08 | 17933.7988 | 0 | 0 | 17933.7988 | Heating | 15823.9401 | 8.5 | 15823.9401 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3164.788 | 63.3% | 2 | 63.3% | 63.3% | 0% | 0% | 28.4646 | 28.4646 | 0 | 0 | 56.9291 | 16146.8777 | 0 | 3229.3755 | 32.29% | 1 | 64.59% | 0% | 0% | 14.9092 | 0 | 0 | 14.9092 | 71.8384
2007-01-21 08:00 | 1 | 21 | 8 | 21 | 488 | 6.08 | 15510.575 | 0 | 0 | 15510.575 | Heating | 13685.8015 | 8.5 | 13685.8015 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2737.1603 | 54.74% | 2 | 54.74% | 54.74% | 0% | 0% | 20.3846 | 20.3846 | 0 | 0 | 40.7692 | 13965.1036 | 0 | 2793.0207 | 27.93% | 1 | 55.86% | 0% | 0% | 10.6771 | 0 | 0 | 10.6771 | 51.4463
2007-01-21 09:00 | 1 | 21 | 9 | 21 | 489 | 8.96 | 13535.2096 | 0 | 0 | 13535.2096 | Heating | 11942.832 | 8.5 | 11942.832 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2388.5664 | 47.77% | 1 | 95.54% | 0% | 0% | 0% | 73.3832 | 0 | 0 | 0 | 73.3832 | 12186.5632 | 0 | 2437.3126 | 24.37% | 1 | 48.75% | 0% | 0% | 7.8051 | 0 | 0 | 7.8051 | 81.1883
2007-01-21 10:00 | 1 | 21 | 10 | 21 | 490 | 12.02 | 11817.1085 | 0 | 0 | 11817.1085 | Heating | 10426.8604 | 8.5 | 10426.8604 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2085.3721 | 41.71% | 1 | 83.41% | 0% | 0% | 0% | 53.7036 | 0 | 0 | 0 | 53.7036 | 10639.6535 | 0 | 2127.9307 | 21.28% | 1 | 42.56% | 0% | 0% | 5.7119 | 0 | 0 | 5.7119 | 59.4155
2007-01-21 11:00 | 1 | 21 | 11 | 21 | 491 | 12.02 | 10706.1608 | 0 | 0 | 10706.1608 | Heating | 9446.6125 | 8.5 | 9446.6125 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1889.3225 | 37.79% | 1 | 75.57% | 0% | 0% | 0% | 42.7942 | 0 | 0 | 0 | 42.7942 | 9639.4005 | 0 | 1927.8801 | 19.28% | 1 | 38.56% | 0% | 0% | 4.5516 | 0 | 0 | 4.5516 | 47.3458
2007-01-21 12:00 | 1 | 21 | 12 | 21 | 492 | 17.06 | 9798.6158 | 0 | 0 | 9798.6158 | Heating | 8645.8375 | 8.5 | 8645.8375 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1729.1675 | 34.58% | 1 | 69.17% | 0% | 0% | 0% | 34.9065 | 0 | 0 | 0 | 34.9065 | 8822.2832 | 0 | 1764.4566 | 17.64% | 1 | 35.29% | 0% | 0% | 3.7127 | 0 | 0 | 3.7127 | 38.6192
2007-01-21 13:00 | 1 | 21 | 13 | 21 | 493 | 17.96 | 9211.0416 | 0 | 0 | 9211.0416 | Heating | 8127.3897 | 8.5 | 8127.3897 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1625.4779 | 32.51% | 1 | 65.02% | 0% | 0% | 0% | 30.2787 | 0 | 0 | 0 | 30.2787 | 8293.2548 | 0 | 1658.651 | 16.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.5533
2007-01-21 14:00 | 1 | 21 | 14 | 21 | 494 | 17.96 | 8527.3972 | 0 | 0 | 8527.3972 | Heating | 7524.174 | 8.5 | 7524.174 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1504.8348 | 30.1% | 1 | 60.19% | 0% | 0% | 0% | 25.3574 | 0 | 0 | 0 | 25.3574 | 7677.7286 | 0 | 1535.5457 | 15.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.632
2007-01-21 15:00 | 1 | 21 | 15 | 21 | 495 | 19.04 | 8351.6592 | 0 | 0 | 8351.6592 | Heating | 7369.1111 | 8.5 | 7369.1111 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1473.8222 | 30% | 1 | 58.95% | 0% | 0% | 0% | 24.1716 | 0 | 0 | 0 | 24.1716 | 7519.5011 | 0 | 1503.9002 | 15.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.4461
2007-01-21 16:00 | 1 | 21 | 16 | 21 | 496 | 19.04 | 8420.0544 | 0 | 0 | 8420.0544 | Heating | 7429.4598 | 8.5 | 7429.4598 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1485.892 | 30% | 1 | 59.44% | 0% | 0% | 0% | 24.6293 | 0 | 0 | 0 | 24.6293 | 7581.0814 | 0 | 1516.2163 | 15.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.9038
2007-01-21 17:00 | 1 | 21 | 17 | 21 | 497 | 19.04 | 8510.3993 | 0 | 0 | 8510.3993 | Heating | 7509.1759 | 8.5 | 7509.1759 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1501.8352 | 30.04% | 1 | 60.07% | 0% | 0% | 0% | 25.2413 | 0 | 0 | 0 | 25.2413 | 7662.4243 | 0 | 1532.4849 | 15.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.5159
2007-01-21 18:00 | 1 | 21 | 18 | 21 | 498 | 19.04 | 8671.0863 | 0 | 0 | 8671.0863 | Heating | 7650.9585 | 8.5 | 7650.9585 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1530.1917 | 30.6% | 1 | 61.21% | 0% | 0% | 0% | 26.351 | 0 | 0 | 0 | 26.351 | 7807.1005 | 0 | 1561.4201 | 15.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.6255
2007-01-21 19:00 | 1 | 21 | 19 | 21 | 499 | 19.04 | 8647.8052 | 0 | 0 | 8647.8052 | Heating | 7630.4164 | 8.5 | 7630.4164 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1526.0833 | 30.52% | 1 | 61.04% | 0% | 0% | 0% | 26.1885 | 0 | 0 | 0 | 26.1885 | 7786.1392 | 0 | 1557.2278 | 15.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.4631
2007-01-21 20:00 | 1 | 21 | 20 | 21 | 500 | 19.04 | 8858.4704 | 0 | 0 | 8858.4704 | Heating | 7816.2974 | 8.5 | 7816.2974 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1563.2595 | 31.27% | 1 | 62.53% | 0% | 0% | 0% | 27.6791 | 0 | 0 | 0 | 27.6791 | 7975.8137 | 0 | 1595.1627 | 15.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.9537
2007-01-21 21:00 | 1 | 21 | 21 | 21 | 501 | 17.96 | 9159.6021 | 0 | 0 | 9159.6021 | Heating | 8082.0019 | 8.5 | 8082.0019 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1616.4004 | 32.33% | 1 | 64.66% | 0% | 0% | 0% | 29.8912 | 0 | 0 | 0 | 29.8912 | 8246.9407 | 0 | 1649.3881 | 16.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.1658
2007-01-21 22:00 | 1 | 21 | 22 | 21 | 502 | 19.04 | 2934.2883 | 0 | 0 | 2934.2883 | Heating | 2589.0779 | 8.5 | 2589.0779 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.8156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2641.9162 | 0 | 528.3832 | 5.284% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-21 23:00 | 1 | 21 | 23 | 21 | 503 | 19.04 | 3195.3603 | 0 | 0 | 3195.3603 | Heating | 2819.4355 | 8.5 | 2819.4355 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 563.8871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2876.975 | 0 | 575.395 | 5.754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 | 1 | 22 | 0 | 22 | 504 | 17.96 | 3458.7546 | 0 | 0 | 3458.7546 | Heating | 3051.8423 | 8.5 | 3051.8423 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 610.3685 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3114.1248 | 0 | 622.825 | 6.228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 01:00 | 1 | 22 | 1 | 22 | 505 | 17.96 | 3524.7075 | 0 | 0 | 3524.7075 | Heating | 3110.036 | 8.5 | 3110.036 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 622.0072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3173.5062 | 0 | 634.7012 | 6.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 02:00 | 1 | 22 | 2 | 22 | 506 | 17.96 | 3489.4274 | 0 | 0 | 3489.4274 | Heating | 3078.9065 | 8.5 | 3078.9065 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 615.7813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3141.7413 | 0 | 628.3483 | 6.283% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 03:00 | 1 | 22 | 3 | 22 | 507 | 17.96 | 3436.3798 | 0 | 0 | 3436.3798 | Heating | 3032.0998 | 8.5 | 3032.0998 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 606.42 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3093.9794 | 0 | 618.7959 | 6.188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 04:00 | 1 | 22 | 4 | 22 | 508 | 17.96 | 3433.1456 | 0 | 0 | 3433.1456 | Heating | 3029.2461 | 8.5 | 3029.2461 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 605.8492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3091.0675 | 0 | 618.2135 | 6.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 05:00 | 1 | 22 | 5 | 22 | 509 | 17.96 | 3635.7007 | 0 | 0 | 3635.7007 | Heating | 3207.9712 | 8.5 | 3207.9712 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 641.5942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3273.44 | 0 | 654.688 | 6.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 06:00 | 1 | 22 | 6 | 22 | 510 | 17.6 | 3792.9613 | 0 | 0 | 3792.9613 | Heating | 3346.7305 | 8.5 | 3346.7305 | 0 | 2.8595 | 0 | 0 | 0 | 0 | 8.5 | 0 | 669.3461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3415.0312 | 0 | 683.0062 | 6.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 07:00 | 1 | 22 | 7 | 22 | 511 | 15.8 | 16104.6099 | 0 | 0 | 16104.6099 | Heating | 14209.9499 | 8.5 | 14209.9499 | 0 | 2.8226 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2841.99 | 56.84% | 2 | 56.84% | 56.84% | 0% | 0% | 22.2251 | 22.2251 | 0 | 0 | 44.4502 | 14499.9489 | 0 | 2899.9898 | 29% | 1 | 58% | 0% | 0% | 11.6411 | 0 | 0 | 11.6411 | 56.0913
2007-01-22 08:00 | 1 | 22 | 8 | 22 | 512 | 15.98 | 13647.0036 | 0 | 0 | 13647.0036 | Heating | 12041.4737 | 8.5 | 12041.4737 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2408.2947 | 48.17% | 1 | 96.33% | 0% | 0% | 0% | 74.7848 | 0 | 0 | 0 | 74.7848 | 12287.2181 | 0 | 2457.4436 | 24.57% | 1 | 49.15% | 0% | 0% | 7.9542 | 0 | 0 | 7.9542 | 82.7389
2007-01-22 09:00 | 1 | 22 | 9 | 22 | 513 | 15.98 | 10835.7765 | 0 | 0 | 10835.7765 | Heating | 9560.9792 | 8.5 | 9560.9792 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1912.1958 | 38.24% | 1 | 76.49% | 0% | 0% | 0% | 43.9952 | 0 | 0 | 0 | 43.9952 | 9756.1012 | 0 | 1951.2202 | 19.51% | 1 | 39.02% | 0% | 0% | 4.6794 | 0 | 0 | 4.6794 | 48.6746
2007-01-22 10:00 | 1 | 22 | 10 | 22 | 514 | 17.96 | 8205.3908 | 0 | 0 | 8205.3908 | Heating | 7240.0507 | 8.5 | 7240.0507 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1448.0101 | 30% | 1 | 57.92% | 0% | 0% | 0% | 23.209 | 0 | 0 | 0 | 23.209 | 7387.8069 | 0 | 1477.5614 | 14.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.4835
2007-01-22 11:00 | 1 | 22 | 11 | 22 | 515 | 17.96 | 6853.3572 | 0 | 0 | 6853.3572 | Heating | 6047.0799 | 8.5 | 6047.0799 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1209.416 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6170.4896 | 0 | 1234.0979 | 12.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 12:00 | 1 | 22 | 12 | 22 | 516 | 21.02 | 5848.8791 | 0 | 0 | 5848.8791 | Heating | 5160.7757 | 8.5 | 5160.7757 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1032.1551 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5266.0976 | 0 | 1053.2195 | 10.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 13:00 | 1 | 22 | 13 | 22 | 517 | 21.92 | 5204.3305 | 0 | 0 | 5204.3305 | Heating | 4592.0563 | 8.5 | 4592.0563 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 918.4113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4685.7717 | 0 | 937.1543 | 9.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 14:00 | 1 | 22 | 14 | 22 | 518 | 21.92 | 4701.0487 | 0 | 0 | 4701.0487 | Heating | 4147.9841 | 8.5 | 4147.9841 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 829.5968 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4232.6368 | 0 | 846.5274 | 8.465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 15:00 | 1 | 22 | 15 | 22 | 519 | 21.92 | 4688.8421 | 0 | 0 | 4688.8421 | Heating | 4137.2137 | 8.5 | 4137.2137 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 827.4427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4221.6466 | 0 | 844.3293 | 8.443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 16:00 | 1 | 22 | 16 | 22 | 520 | 23 | 4699.5306 | 0 | 0 | 4699.5306 | Heating | 4146.6446 | 8.5 | 4146.6446 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 829.3289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4231.27 | 0 | 846.254 | 8.463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 17:00 | 1 | 22 | 17 | 22 | 521 | 23 | 4886.1329 | 0 | 0 | 4886.1329 | Heating | 4311.2937 | 8.5 | 4311.2937 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 862.2587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4399.2793 | 0 | 879.8559 | 8.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 18:00 | 1 | 22 | 18 | 22 | 522 | 21.2 | 5251.3523 | 0 | 0 | 5251.3523 | Heating | 4633.5461 | 8.5 | 4633.5461 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 926.7092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4728.1083 | 0 | 945.6217 | 9.456% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 19:00 | 1 | 22 | 19 | 22 | 523 | 21.2 | 5298.4909 | 0 | 0 | 5298.4909 | Heating | 4675.1391 | 8.5 | 4675.1391 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 935.0278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4770.5501 | 0 | 954.11 | 9.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 20:00 | 1 | 22 | 20 | 22 | 524 | 21.02 | 5546.7353 | 0 | 0 | 5546.7353 | Heating | 4894.1782 | 8.5 | 4894.1782 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 978.8356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4994.0594 | 0 | 998.8119 | 9.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 21:00 | 1 | 22 | 21 | 22 | 525 | 21.02 | 5843.4585 | 0 | 0 | 5843.4585 | Heating | 5155.9928 | 8.5 | 5155.9928 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1031.1986 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5261.2171 | 0 | 1052.2434 | 10.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 22:00 | 1 | 22 | 22 | 22 | 526 | 21.02 | 1774.7077 | 0 | 0 | 1774.7077 | Heating | 1565.9186 | 8.5 | 1565.9186 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.1837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1597.8761 | 0 | 319.5752 | 3.196% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-22 23:00 | 1 | 22 | 23 | 22 | 527 | 21.02 | 1648.017 | 0 | 0 | 1648.017 | Heating | 1454.1327 | 8.5 | 1454.1327 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.8265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1483.8088 | 0 | 296.7618 | 2.968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 | 1 | 23 | 0 | 23 | 528 | 19.94 | 1836.0665 | 0 | 0 | 1836.0665 | Heating | 1620.0586 | 8.5 | 1620.0586 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.0117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1653.1211 | 0 | 330.6242 | 3.306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 01:00 | 1 | 23 | 1 | 23 | 529 | 19.94 | 1922.1337 | 0 | 0 | 1922.1337 | Heating | 1696.0003 | 8.5 | 1696.0003 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.2001 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1730.6126 | 0 | 346.1225 | 3.461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 02:00 | 1 | 23 | 2 | 23 | 530 | 19.94 | 1931.0195 | 0 | 0 | 1931.0195 | Heating | 1703.8408 | 8.5 | 1703.8408 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.7682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1738.613 | 0 | 347.7226 | 3.477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 03:00 | 1 | 23 | 3 | 23 | 531 | 19.4 | 1947.6298 | 0 | 0 | 1947.6298 | Heating | 1718.4969 | 8.5 | 1718.4969 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.6994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1753.5682 | 0 | 350.7136 | 3.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 04:00 | 1 | 23 | 4 | 23 | 532 | 19.4 | 1944.9096 | 0 | 0 | 1944.9096 | Heating | 1716.0967 | 8.5 | 1716.0967 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.2193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1751.1191 | 0 | 350.2238 | 3.502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 05:00 | 1 | 23 | 5 | 23 | 533 | 19.94 | 2035.3254 | 0 | 0 | 2035.3254 | Heating | 1795.8754 | 8.5 | 1795.8754 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 359.1751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1832.5259 | 0 | 366.5052 | 3.665% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 06:00 | 1 | 23 | 6 | 23 | 534 | 14 | 2109.7949 | 0 | 0 | 2109.7949 | Heating | 1861.5838 | 8.5 | 1861.5838 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.3168 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1899.5753 | 0 | 379.9151 | 3.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 07:00 | 1 | 23 | 7 | 23 | 535 | 14 | 11863.5572 | 0 | 0 | 11863.5572 | Heating | 10467.8446 | 8.5 | 10467.8446 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2093.5689 | 41.87% | 1 | 83.74% | 0% | 0% | 0% | 54.1903 | 0 | 0 | 0 | 54.1903 | 10681.474 | 0 | 2136.2948 | 21.36% | 1 | 42.73% | 0% | 0% | 5.7637 | 0 | 0 | 5.7637 | 59.954
2007-01-23 08:00 | 1 | 23 | 8 | 23 | 536 | 12.92 | 9131.6617 | 0 | 0 | 9131.6617 | Heating | 8057.3486 | 8.5 | 8057.3486 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1611.4697 | 32.23% | 1 | 64.46% | 0% | 0% | 0% | 29.6819 | 0 | 0 | 0 | 29.6819 | 8221.7843 | 0 | 1644.3569 | 16.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.9565
2007-01-23 09:00 | 1 | 23 | 9 | 23 | 537 | 15.98 | 7659.7493 | 0 | 0 | 7659.7493 | Heating | 6758.6024 | 8.5 | 6758.6024 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1351.7205 | 30% | 1 | 54.07% | 0% | 0% | 0% | 19.8117 | 0 | 0 | 0 | 19.8117 | 6896.533 | 0 | 1379.3066 | 13.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.0862
2007-01-23 10:00 | 1 | 23 | 10 | 23 | 538 | 21.02 | 6490.5988 | 0 | 0 | 6490.5988 | Heating | 5726.999 | 8.5 | 5726.999 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1145.3998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5843.8765 | 0 | 1168.7753 | 11.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 11:00 | 1 | 23 | 11 | 23 | 539 | 21.02 | 5768.4444 | 0 | 0 | 5768.4444 | Heating | 5089.8039 | 8.5 | 5089.8039 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1017.9608 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5193.6774 | 0 | 1038.7355 | 10.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 12:00 | 1 | 23 | 12 | 23 | 540 | 26.06 | 5151.1247 | 0 | 0 | 5151.1247 | Heating | 4545.11 | 8.5 | 4545.11 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 909.022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4637.8674 | 0 | 927.5735 | 9.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 13:00 | 1 | 23 | 13 | 23 | 541 | 28.4 | 4913.0363 | 0 | 0 | 4913.0363 | Heating | 4335.0321 | 8.5 | 4335.0321 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 867.0064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4423.5021 | 0 | 884.7004 | 8.847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 14:00 | 1 | 23 | 14 | 23 | 542 | 28.04 | 4835.3591 | 0 | 0 | 4835.3591 | Heating | 4266.4934 | 8.5 | 4266.4934 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 853.2987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4353.5647 | 0 | 870.7129 | 8.707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 15:00 | 1 | 23 | 15 | 23 | 543 | 30.02 | 4877.4893 | 0 | 0 | 4877.4893 | Heating | 4303.667 | 8.5 | 4303.667 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 860.7334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4391.497 | 0 | 878.2994 | 8.783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 16:00 | 1 | 23 | 16 | 23 | 544 | 30.02 | 4749.2134 | 0 | 0 | 4749.2134 | Heating | 4190.4824 | 8.5 | 4190.4824 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 838.0965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4276.0025 | 0 | 855.2005 | 8.552% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 17:00 | 1 | 23 | 17 | 23 | 545 | 28.04 | 4932.6503 | 0 | 0 | 4932.6503 | Heating | 4352.3385 | 8.5 | 4352.3385 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 870.4677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4441.1617 | 0 | 888.2323 | 8.882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 18:00 | 1 | 23 | 18 | 23 | 546 | 28.04 | 5308.5428 | 0 | 0 | 5308.5428 | Heating | 4684.0083 | 8.5 | 4684.0083 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 936.8017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4779.6003 | 0 | 955.9201 | 9.559% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 19:00 | 1 | 23 | 19 | 23 | 547 | 28.04 | 5415.7434 | 0 | 0 | 5415.7434 | Heating | 4778.5971 | 8.5 | 4778.5971 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 955.7194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4876.1195 | 0 | 975.2239 | 9.752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 20:00 | 1 | 23 | 20 | 23 | 548 | 28.04 | 5543.5668 | 0 | 0 | 5543.5668 | Heating | 4891.3825 | 8.5 | 4891.3825 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 978.2765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4991.2066 | 0 | 998.2413 | 9.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 21:00 | 1 | 23 | 21 | 23 | 549 | 23 | 5678.3722 | 0 | 0 | 5678.3722 | Heating | 5010.3284 | 8.5 | 5010.3284 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1002.0657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5112.58 | 0 | 1022.516 | 10.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 22:00 | 1 | 23 | 22 | 23 | 550 | 26.06 | 1668.2905 | 0 | 0 | 1668.2905 | Heating | 1472.021 | 8.5 | 1472.021 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 294.4042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1502.0622 | 0 | 300.4124 | 3.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-23 23:00 | 1 | 23 | 23 | 23 | 551 | 26.06 | 1501.151 | 0 | 0 | 1501.151 | Heating | 1324.545 | 8.5 | 1324.545 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1351.5766 | 0 | 270.3153 | 2.703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 | 1 | 24 | 0 | 24 | 552 | 26.06 | 1731.6636 | 0 | 0 | 1731.6636 | Heating | 1527.9385 | 8.5 | 1527.9385 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 305.5877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1559.1209 | 0 | 311.8242 | 3.118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 01:00 | 1 | 24 | 1 | 24 | 553 | 26.06 | 1846.7424 | 0 | 0 | 1846.7424 | Heating | 1629.4786 | 8.5 | 1629.4786 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 325.8957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1662.7333 | 0 | 332.5467 | 3.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 02:00 | 1 | 24 | 2 | 24 | 554 | 26.06 | 1964.3895 | 0 | 0 | 1964.3895 | Heating | 1733.2849 | 8.5 | 1733.2849 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1768.658 | 0 | 353.7316 | 3.537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 03:00 | 1 | 24 | 3 | 24 | 555 | 17.06 | 1963.4239 | 0 | 0 | 1963.4239 | Heating | 1732.4329 | 8.5 | 1732.4329 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.4866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1767.7887 | 0 | 353.5577 | 3.536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 04:00 | 1 | 24 | 4 | 24 | 556 | 21.02 | 1970.3037 | 0 | 0 | 1970.3037 | Heating | 1738.5033 | 8.5 | 1738.5033 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 347.7007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1773.983 | 0 | 354.7966 | 3.548% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 05:00 | 1 | 24 | 5 | 24 | 557 | 21.02 | 1981.6993 | 0 | 0 | 1981.6993 | Heating | 1748.5582 | 8.5 | 1748.5582 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 349.7116 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1784.2431 | 0 | 356.8486 | 3.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 06:00 | 1 | 24 | 6 | 24 | 558 | 24.08 | 1966.91 | 0 | 0 | 1966.91 | Heating | 1735.5088 | 8.5 | 1735.5088 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 347.1018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1770.9273 | 0 | 354.1855 | 3.542% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 07:00 | 1 | 24 | 7 | 24 | 559 | 24.98 | 11752.5136 | 0 | 0 | 11752.5136 | Heating | 10369.8649 | 8.5 | 10369.8649 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2073.973 | 41.48% | 1 | 82.96% | 0% | 0% | 0% | 53.0308 | 0 | 0 | 0 | 53.0308 | 10581.4948 | 0 | 2116.299 | 21.16% | 1 | 42.33% | 0% | 0% | 5.6404 | 0 | 0 | 5.6404 | 58.6712
2007-01-24 08:00 | 1 | 24 | 8 | 24 | 560 | 24.98 | 9017.046 | 0 | 0 | 9017.046 | Heating | 7956.217 | 8.5 | 7956.217 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1591.2434 | 31.82% | 1 | 63.65% | 0% | 0% | 0% | 28.832 | 0 | 0 | 0 | 28.832 | 8118.5888 | 0 | 1623.7178 | 16.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.1066
2007-01-24 09:00 | 1 | 24 | 9 | 24 | 561 | 28.04 | 7439.5213 | 0 | 0 | 7439.5213 | Heating | 6564.2835 | 8.5 | 6564.2835 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1312.8567 | 30% | 1 | 52.51% | 0% | 0% | 0% | 18.526 | 0 | 0 | 0 | 18.526 | 6698.2485 | 0 | 1339.6497 | 13.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.8005
2007-01-24 10:00 | 1 | 24 | 10 | 24 | 562 | 30.92 | 6142.6834 | 0 | 0 | 6142.6834 | Heating | 5420.0148 | 8.5 | 5420.0148 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1084.003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5530.6273 | 0 | 1106.1255 | 11.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 11:00 | 1 | 24 | 11 | 24 | 563 | 30.92 | 5423.0598 | 0 | 0 | 5423.0598 | Heating | 4785.0528 | 8.5 | 4785.0528 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 957.0106 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4882.7069 | 0 | 976.5414 | 9.765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 12:00 | 1 | 24 | 12 | 24 | 564 | 33.08 | 4794.8019 | 0 | 0 | 4794.8019 | Heating | 4230.7075 | 8.5 | 4230.7075 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 846.1415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4317.0485 | 0 | 863.4097 | 8.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 13:00 | 1 | 24 | 13 | 24 | 565 | 33.08 | 4282.2189 | 0 | 0 | 4282.2189 | Heating | 3778.4285 | 8.5 | 3778.4285 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 755.6857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3855.5393 | 0 | 771.1079 | 7.711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 14:00 | 1 | 24 | 14 | 24 | 566 | 33.08 | 3909.7878 | 0 | 0 | 3909.7878 | Heating | 3449.8128 | 8.5 | 3449.8128 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 689.9626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3520.2171 | 0 | 704.0434 | 7.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 15:00 | 1 | 24 | 15 | 24 | 567 | 33.98 | 3731.6613 | 0 | 0 | 3731.6613 | Heating | 3292.6424 | 8.5 | 3292.6424 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 658.5285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3359.8391 | 0 | 671.9678 | 6.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 16:00 | 1 | 24 | 16 | 24 | 568 | 30.02 | 3702.7454 | 0 | 0 | 3702.7454 | Heating | 3267.1283 | 8.5 | 3267.1283 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 653.4257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3333.8044 | 0 | 666.7609 | 6.668% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 17:00 | 1 | 24 | 17 | 24 | 569 | 30.02 | 4036.4847 | 0 | 0 | 4036.4847 | Heating | 3561.6041 | 8.5 | 3561.6041 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 712.3208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3634.2899 | 0 | 726.858 | 7.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 18:00 | 1 | 24 | 18 | 24 | 570 | 28.94 | 4542.7736 | 0 | 0 | 4542.7736 | Heating | 4008.3296 | 8.5 | 4008.3296 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 801.6659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4090.1323 | 0 | 818.0265 | 8.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 19:00 | 1 | 24 | 19 | 24 | 571 | 26.06 | 5186.1694 | 0 | 0 | 5186.1694 | Heating | 4576.0318 | 8.5 | 4576.0318 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 915.2064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4669.4203 | 0 | 933.8841 | 9.339% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 20:00 | 1 | 24 | 20 | 24 | 572 | 26.06 | 5699.1975 | 0 | 0 | 5699.1975 | Heating | 5028.7037 | 8.5 | 5028.7037 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1005.7407 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5131.3303 | 0 | 1026.2661 | 10.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 21:00 | 1 | 24 | 21 | 24 | 573 | 24.08 | 5935.3851 | 0 | 0 | 5935.3851 | Heating | 5237.1045 | 8.5 | 5237.1045 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1047.4209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5343.9842 | 0 | 1068.7968 | 10.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 22:00 | 1 | 24 | 22 | 24 | 574 | 21.92 | 1713.2321 | 0 | 0 | 1713.2321 | Heating | 1511.6754 | 8.5 | 1511.6754 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 302.3351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1542.5259 | 0 | 308.5052 | 3.085% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-24 23:00 | 1 | 24 | 23 | 24 | 575 | 21.92 | 1454.7515 | 0 | 0 | 1454.7515 | Heating | 1283.6043 | 8.5 | 1283.6043 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 256.7209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1309.8003 | 0 | 261.9601 | 2.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 | 1 | 25 | 0 | 25 | 576 | 19.94 | 1709.2518 | 0 | 0 | 1709.2518 | Heating | 1508.1633 | 8.5 | 1508.1633 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.6327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1538.9422 | 0 | 307.7884 | 3.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 01:00 | 1 | 25 | 1 | 25 | 577 | 17.06 | 1823.9607 | 0 | 0 | 1823.9607 | Heating | 1609.3771 | 8.5 | 1609.3771 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.8754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1642.2215 | 0 | 328.4443 | 3.284% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 02:00 | 1 | 25 | 2 | 25 | 578 | 17.06 | 1872.5258 | 0 | 0 | 1872.5258 | Heating | 1652.2286 | 8.5 | 1652.2286 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 330.4457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1685.9476 | 0 | 337.1895 | 3.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 03:00 | 1 | 25 | 3 | 25 | 579 | 14 | 1940.4433 | 0 | 0 | 1940.4433 | Heating | 1712.1559 | 8.5 | 1712.1559 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 342.4312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1747.0978 | 0 | 349.4196 | 3.494% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 04:00 | 1 | 25 | 4 | 25 | 580 | 10.94 | 1931.0408 | 0 | 0 | 1931.0408 | Heating | 1703.8595 | 8.5 | 1703.8595 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.7719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1738.6322 | 0 | 347.7264 | 3.477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 05:00 | 1 | 25 | 5 | 25 | 581 | 10.94 | 1957.6783 | 0 | 0 | 1957.6783 | Heating | 1727.3632 | 8.5 | 1727.3632 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 345.4726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1762.6155 | 0 | 352.5231 | 3.525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 06:00 | 1 | 25 | 6 | 25 | 582 | 8.96 | 2008.1374 | 0 | 0 | 2008.1374 | Heating | 1771.8859 | 8.5 | 1771.8859 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 354.3772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1808.0469 | 0 | 361.6094 | 3.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 07:00 | 1 | 25 | 7 | 25 | 583 | 8.96 | 11618.2907 | 0 | 0 | 11618.2907 | Heating | 10251.433 | 8.5 | 10251.433 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2050.2866 | 41.01% | 1 | 82.01% | 0% | 0% | 0% | 51.6481 | 0 | 0 | 0 | 51.6481 | 10460.6459 | 0 | 2092.1292 | 20.92% | 1 | 41.84% | 0% | 0% | 5.4933 | 0 | 0 | 5.4933 | 57.1415
2007-01-25 08:00 | 1 | 25 | 8 | 25 | 584 | 8.96 | 8782.2785 | 0 | 0 | 8782.2785 | Heating | 7749.0692 | 8.5 | 7749.0692 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1549.8138 | 31% | 1 | 61.99% | 0% | 0% | 0% | 27.1346 | 0 | 0 | 0 | 27.1346 | 7907.2135 | 0 | 1581.4427 | 15.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.4092
2007-01-25 09:00 | 1 | 25 | 9 | 25 | 585 | 10.94 | 7303.7363 | 0 | 0 | 7303.7363 | Heating | 6444.4732 | 8.5 | 6444.4732 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1288.8946 | 30% | 1 | 51.56% | 0% | 0% | 0% | 17.7575 | 0 | 0 | 0 | 17.7575 | 6575.9931 | 0 | 1315.1986 | 13.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.032
2007-01-25 10:00 | 1 | 25 | 10 | 25 | 586 | 12.02 | 6185.3598 | 0 | 0 | 6185.3598 | Heating | 5457.6704 | 8.5 | 5457.6704 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1091.5341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5569.0514 | 0 | 1113.8103 | 11.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 11:00 | 1 | 25 | 11 | 25 | 587 | 12.02 | 5559.3468 | 0 | 0 | 5559.3468 | Heating | 4905.306 | 8.5 | 4905.306 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 981.0612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5005.4143 | 0 | 1001.0829 | 10.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 12:00 | 1 | 25 | 12 | 25 | 588 | 15.08 | 4904.6212 | 0 | 0 | 4904.6212 | Heating | 4327.607 | 8.5 | 4327.607 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 865.5214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4415.9255 | 0 | 883.1851 | 8.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 13:00 | 1 | 25 | 13 | 25 | 589 | 17.06 | 4372.264 | 0 | 0 | 4372.264 | Heating | 3857.88 | 8.5 | 3857.88 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 771.576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3936.6122 | 0 | 787.3224 | 7.873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 14:00 | 1 | 25 | 14 | 25 | 590 | 17.06 | 4040.7304 | 0 | 0 | 4040.7304 | Heating | 3565.3504 | 8.5 | 3565.3504 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 713.0701 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3638.1126 | 0 | 727.6225 | 7.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 15:00 | 1 | 25 | 15 | 25 | 591 | 19.4 | 4002.3665 | 0 | 0 | 4002.3665 | Heating | 3531.4998 | 8.5 | 3531.4998 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 706.3 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3603.5712 | 0 | 720.7142 | 7.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 16:00 | 1 | 25 | 16 | 25 | 592 | 15.98 | 3986.2113 | 0 | 0 | 3986.2113 | Heating | 3517.2453 | 8.5 | 3517.2453 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 703.4491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3589.0258 | 0 | 717.8052 | 7.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 17:00 | 1 | 25 | 17 | 25 | 593 | 15.98 | 4160.197 | 0 | 0 | 4160.197 | Heating | 3670.762 | 8.5 | 3670.762 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 734.1524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3745.6756 | 0 | 749.1351 | 7.491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 18:00 | 1 | 25 | 18 | 25 | 594 | 12.92 | 4519.9715 | 0 | 0 | 4519.9715 | Heating | 3988.2101 | 8.5 | 3988.2101 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 797.642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4069.6022 | 0 | 813.9204 | 8.139% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 19:00 | 1 | 25 | 19 | 25 | 595 | 10.94 | 4934.5194 | 0 | 0 | 4934.5194 | Heating | 4353.9877 | 8.5 | 4353.9877 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 870.7975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4442.8446 | 0 | 888.5689 | 8.886% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 20:00 | 1 | 25 | 20 | 25 | 596 | 10.94 | 5394.0761 | 0 | 0 | 5394.0761 | Heating | 4759.4789 | 8.5 | 4759.4789 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 951.8958 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4856.6111 | 0 | 971.3222 | 9.713% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 21:00 | 1 | 25 | 21 | 25 | 597 | 6.98 | 6174.4249 | 0 | 0 | 6174.4249 | Heating | 5448.022 | 8.5 | 5448.022 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1089.6044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5559.2061 | 0 | 1111.8412 | 11.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 22:00 | 1 | 25 | 22 | 25 | 598 | 5 | 1899.7205 | 0 | 0 | 1899.7205 | Heating | 1676.224 | 8.5 | 1676.224 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 335.2448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1710.4327 | 0 | 342.0865 | 3.421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-25 23:00 | 1 | 25 | 23 | 25 | 599 | 5 | 1838.3862 | 0 | 0 | 1838.3862 | Heating | 1622.1055 | 8.5 | 1622.1055 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.4211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1655.2097 | 0 | 331.0419 | 3.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 | 1 | 26 | 0 | 26 | 600 | 1.94 | 2185.8369 | 0 | 0 | 2185.8369 | Heating | 1928.6796 | 8.5 | 1928.6796 | 0 | 2.6096 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.7359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1968.0404 | 0 | 393.6081 | 3.936% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 01:00 | 1 | 26 | 1 | 26 | 601 | 1.4 | 2554.695 | 0 | 0 | 2554.695 | Heating | 2254.1426 | 8.5 | 2254.1426 | 0 | 2.6024 | 0 | 0 | 0 | 0 | 8.5 | 0 | 450.8285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2300.1455 | 0 | 460.0291 | 4.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 02:00 | 1 | 26 | 2 | 26 | 602 | -0.04 | 2452.9043 | 0 | 0 | 2452.9043 | Heating | 2164.3273 | 8.5 | 2164.3273 | 0 | 2.5829 | 0 | 0 | 0 | 0 | 8.5 | 0 | 432.8655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2208.4973 | 0 | 441.6995 | 4.417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 03:00 | 1 | 26 | 3 | 26 | 603 | -0.04 | 2281.1239 | 0 | 0 | 2281.1239 | Heating | 2012.7564 | 8.5 | 2012.7564 | 0 | 2.5829 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.5513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2053.833 | 0 | 410.7666 | 4.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 04:00 | 1 | 26 | 4 | 26 | 604 | -2.02 | 2333.1041 | 0 | 0 | 2333.1041 | Heating | 2058.6213 | 8.5 | 2058.6213 | 0 | 2.5555 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.7243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2100.634 | 0 | 420.1268 | 4.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 05:00 | 1 | 26 | 5 | 26 | 605 | -2.02 | 2404.8829 | 0 | 0 | 2404.8829 | Heating | 2121.9555 | 8.5 | 2121.9555 | 0 | 2.5555 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.3911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2165.2607 | 0 | 433.0521 | 4.331% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 06:00 | 1 | 26 | 6 | 26 | 606 | -2.2 | 2489.8592 | 0 | 0 | 2489.8592 | Heating | 2196.9346 | 8.5 | 2196.9346 | 0 | 2.553 | 0 | 0 | 0 | 0 | 8.5 | 0 | 439.3869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2241.77 | 0 | 448.354 | 4.484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 07:00 | 1 | 26 | 7 | 26 | 607 | -2.2 | 12709.7444 | 0 | 0 | 12709.7444 | Heating | 11214.4803 | 8.5 | 11214.4803 | 0 | 2.553 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2242.8961 | 44.86% | 1 | 89.72% | 0% | 0% | 0% | 63.4954 | 0 | 0 | 0 | 63.4954 | 11443.3473 | 0 | 2288.6695 | 22.89% | 1 | 45.77% | 0% | 0% | 6.7534 | 0 | 0 | 6.7534 | 70.2488
2007-01-26 08:00 | 1 | 26 | 8 | 26 | 608 | -2.92 | 9983.3605 | 0 | 0 | 9983.3605 | Heating | 8808.8475 | 8.5 | 8808.8475 | 0 | 2.5427 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1761.7695 | 35.24% | 1 | 70.47% | 0% | 0% | 0% | 36.4388 | 0 | 0 | 0 | 36.4388 | 8988.6199 | 0 | 1797.724 | 17.98% | 1 | 35.95% | 0% | 0% | 3.8757 | 0 | 0 | 3.8757 | 40.3144
2007-01-26 09:00 | 1 | 26 | 9 | 26 | 609 | 1.04 | 8535.004 | 0 | 0 | 8535.004 | Heating | 7530.8859 | 8.5 | 7530.8859 | 0 | 2.5975 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1506.1772 | 30.12% | 1 | 60.25% | 0% | 0% | 0% | 25.4095 | 0 | 0 | 0 | 25.4095 | 7684.5774 | 0 | 1536.9155 | 15.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.684
2007-01-26 10:00 | 1 | 26 | 10 | 26 | 610 | 3.2 | 7182.8588 | 0 | 0 | 7182.8588 | Heating | 6337.8166 | 8.5 | 6337.8166 | 0 | 2.6265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1267.5633 | 30% | 1 | 50.7% | 0% | 0% | 0% | 17.0888 | 0 | 0 | 0 | 17.0888 | 6467.1598 | 0 | 1293.432 | 12.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3633
2007-01-26 11:00 | 1 | 26 | 11 | 26 | 611 | 3.92 | 6264.0166 | 0 | 0 | 6264.0166 | Heating | 5527.0735 | 8.5 | 5527.0735 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1105.4147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5639.8709 | 0 | 1127.9742 | 11.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 12:00 | 1 | 26 | 12 | 26 | 612 | 8.06 | 5564.573 | 0 | 0 | 5564.573 | Heating | 4909.9174 | 8.5 | 4909.9174 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 981.9835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5010.1198 | 0 | 1002.024 | 10.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 13:00 | 1 | 26 | 13 | 26 | 613 | 8.96 | 5320.0906 | 0 | 0 | 5320.0906 | Heating | 4694.1976 | 8.5 | 4694.1976 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 938.8395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4789.9975 | 0 | 957.9995 | 9.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 14:00 | 1 | 26 | 14 | 26 | 614 | 8.96 | 5316.7747 | 0 | 0 | 5316.7747 | Heating | 4691.2718 | 8.5 | 4691.2718 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 938.2544 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4787.012 | 0 | 957.4024 | 9.574% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 15:00 | 1 | 26 | 15 | 26 | 615 | 8.96 | 5358.2131 | 0 | 0 | 5358.2131 | Heating | 4727.8351 | 8.5 | 4727.8351 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 945.567 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4824.3215 | 0 | 964.8643 | 9.649% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 16:00 | 1 | 26 | 16 | 26 | 616 | 10.94 | 5413.9595 | 0 | 0 | 5413.9595 | Heating | 4777.0231 | 8.5 | 4777.0231 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 955.4046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4874.5133 | 0 | 974.9027 | 9.749% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 17:00 | 1 | 26 | 17 | 26 | 617 | 10.94 | 5850.6312 | 0 | 0 | 5850.6312 | Heating | 5162.3216 | 8.5 | 5162.3216 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1032.4643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5267.6751 | 0 | 1053.535 | 10.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 18:00 | 1 | 26 | 18 | 26 | 618 | 8.06 | 6340.1413 | 0 | 0 | 6340.1413 | Heating | 5594.2423 | 8.5 | 5594.2423 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1118.8485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5708.4105 | 0 | 1141.6821 | 11.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 19:00 | 1 | 26 | 19 | 26 | 619 | 6.98 | 6889.7437 | 0 | 0 | 6889.7437 | Heating | 6079.1856 | 8.5 | 6079.1856 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1215.8371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6203.2506 | 0 | 1240.6501 | 12.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-26 20:00 | 1 | 26 | 20 | 26 | 620 | 6.98 | 7320.9478 | 0 | 0 | 7320.9478 | Heating | 6459.6599 | 8.5 | 6459.6599 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1291.932 | 30% | 1 | 51.68% | 0% | 0% | 0% | 17.8539 | 0 | 0 | 0 | 17.8539 | 6591.4897 | 0 | 1318.2979 | 13.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.1284
2007-01-26 21:00 | 1 | 26 | 21 | 26 | 621 | 5 | 7718.2251 | 0 | 0 | 7718.2251 | Heating | 6810.1986 | 8.5 | 6810.1986 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1362.0397 | 30% | 1 | 54.48% | 0% | 0% | 0% | 20.1613 | 0 | 0 | 0 | 20.1613 | 6949.1823 | 0 | 1389.8365 | 13.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.4358
2007-01-26 22:00 | 1 | 26 | 22 | 26 | 622 | 3.92 | 8226.6536 | 0 | 0 | 8226.6536 | Heating | 7258.812 | 8.5 | 7258.812 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1451.7624 | 30% | 1 | 58.07% | 0% | 0% | 0% | 23.3475 | 0 | 0 | 0 | 23.3475 | 7406.951 | 0 | 1481.3902 | 14.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.6221
2007-01-26 23:00 | 1 | 26 | 23 | 26 | 623 | 3.92 | 2628.7616 | 0 | 0 | 2628.7616 | Heating | 2319.4956 | 8.5 | 2319.4956 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 463.8991 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2366.8322 | 0 | 473.3664 | 4.734% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 | 1 | 27 | 0 | 27 | 624 | 5 | 2702.9916 | 0 | 0 | 2702.9916 | Heating | 2384.9926 | 8.5 | 2384.9926 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.9985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2433.6659 | 0 | 486.7332 | 4.867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 01:00 | 1 | 27 | 1 | 27 | 625 | 5 | 2889.1746 | 0 | 0 | 2889.1746 | Heating | 2549.2717 | 8.5 | 2549.2717 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 509.8543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2601.2976 | 0 | 520.2595 | 5.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 02:00 | 1 | 27 | 2 | 27 | 626 | 5 | 2934.371 | 0 | 0 | 2934.371 | Heating | 2589.1509 | 8.5 | 2589.1509 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.8302 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2641.9907 | 0 | 528.3981 | 5.284% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 03:00 | 1 | 27 | 3 | 27 | 627 | 6.08 | 2939.6175 | 0 | 0 | 2939.6175 | Heating | 2593.7801 | 8.5 | 2593.7801 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 518.756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2646.7144 | 0 | 529.3429 | 5.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 04:00 | 1 | 27 | 4 | 27 | 628 | 6.98 | 3016.7388 | 0 | 0 | 3016.7388 | Heating | 2661.8283 | 8.5 | 2661.8283 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 532.3657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2716.1513 | 0 | 543.2303 | 5.432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 05:00 | 1 | 27 | 5 | 27 | 629 | 6.98 | 3006.9553 | 0 | 0 | 3006.9553 | Heating | 2653.1958 | 8.5 | 2653.1958 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 530.6392 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2707.3427 | 0 | 541.4685 | 5.415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 06:00 | 1 | 27 | 6 | 27 | 630 | 8.06 | 2931.4774 | 0 | 0 | 2931.4774 | Heating | 2586.5977 | 8.5 | 2586.5977 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.3195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2639.3854 | 0 | 527.8771 | 5.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 07:00 | 1 | 27 | 7 | 27 | 631 | 8.06 | 2892.754 | 0 | 0 | 2892.754 | Heating | 2552.43 | 8.5 | 2552.43 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 510.486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2604.5204 | 0 | 520.9041 | 5.209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 08:00 | 1 | 27 | 8 | 27 | 632 | 8.06 | 2866.1982 | 0 | 0 | 2866.1982 | Heating | 2528.9984 | 8.5 | 2528.9984 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.7997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2580.6106 | 0 | 516.1221 | 5.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 09:00 | 1 | 27 | 9 | 27 | 633 | 8.6 | 13049.3888 | 0 | 0 | 13049.3888 | Heating | 11514.1666 | 8.5 | 11514.1666 | 0 | 2.7014 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2302.8333 | 46.06% | 1 | 92.11% | 0% | 0% | 0% | 67.466 | 0 | 0 | 0 | 67.466 | 11749.1496 | 0 | 2349.8299 | 23.5% | 1 | 47% | 0% | 0% | 7.1757 | 0 | 0 | 7.1757 | 74.6417
2007-01-27 10:00 | 1 | 27 | 10 | 27 | 634 | 8.96 | 10651.0195 | 0 | 0 | 10651.0195 | Heating | 9397.9584 | 8.5 | 9397.9584 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1879.5917 | 37.59% | 1 | 75.18% | 0% | 0% | 0% | 42.289 | 0 | 0 | 0 | 42.289 | 9589.7534 | 0 | 1917.9507 | 19.18% | 1 | 38.36% | 0% | 0% | 4.4979 | 0 | 0 | 4.4979 | 46.7869
2007-01-27 11:00 | 1 | 27 | 11 | 27 | 635 | 8.96 | 9176.3666 | 0 | 0 | 9176.3666 | Heating | 8096.794 | 8.5 | 8096.794 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1619.3588 | 32.39% | 1 | 64.77% | 0% | 0% | 0% | 30.0172 | 0 | 0 | 0 | 30.0172 | 8262.0347 | 0 | 1652.4069 | 16.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.2917
2007-01-27 12:00 | 1 | 27 | 12 | 27 | 636 | 10.4 | 8341.749 | 0 | 0 | 8341.749 | Heating | 7360.3668 | 8.5 | 7360.3668 | 0 | 2.7285 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1472.0734 | 30% | 1 | 58.88% | 0% | 0% | 0% | 24.1056 | 0 | 0 | 0 | 24.1056 | 7510.5784 | 0 | 1502.1157 | 15.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.3802
2007-01-27 13:00 | 1 | 27 | 13 | 27 | 637 | 12.92 | 7395.93 | 0 | 0 | 7395.93 | Heating | 6525.8206 | 8.5 | 6525.8206 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1305.1641 | 30% | 1 | 52.21% | 0% | 0% | 0% | 18.2772 | 0 | 0 | 0 | 18.2772 | 6659.0006 | 0 | 1331.8001 | 13.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.5518
2007-01-27 14:00 | 1 | 27 | 14 | 27 | 638 | 12.92 | 6896.9106 | 0 | 0 | 6896.9106 | Heating | 6085.5094 | 8.5 | 6085.5094 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1217.1019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6209.7035 | 0 | 1241.9407 | 12.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 15:00 | 1 | 27 | 15 | 27 | 639 | 14 | 6645.5188 | 0 | 0 | 6645.5188 | Heating | 5863.6931 | 8.5 | 5863.6931 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1172.7386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5983.3603 | 0 | 1196.6721 | 11.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 16:00 | 1 | 27 | 16 | 27 | 640 | 14 | 6436.1064 | 0 | 0 | 6436.1064 | Heating | 5678.9174 | 8.5 | 5678.9174 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1135.7835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5794.8137 | 0 | 1158.9627 | 11.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 17:00 | 1 | 27 | 17 | 27 | 641 | 14 | 6493.5196 | 0 | 0 | 6493.5196 | Heating | 5729.5762 | 8.5 | 5729.5762 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1145.9152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5846.5063 | 0 | 1169.3013 | 11.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 18:00 | 1 | 27 | 18 | 27 | 642 | 14 | 8992.4166 | 0 | 0 | 8992.4166 | Heating | 7934.4853 | 8.5 | 7934.4853 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1586.8971 | 31.74% | 1 | 63.48% | 0% | 0% | 0% | 28.6512 | 0 | 0 | 0 | 28.6512 | 8096.4135 | 0 | 1619.2827 | 16.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.9258
2007-01-27 19:00 | 1 | 27 | 19 | 27 | 643 | 15.08 | 9860.7416 | 0 | 0 | 9860.7416 | Heating | 8700.6544 | 8.5 | 8700.6544 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1740.1309 | 34.8% | 1 | 69.61% | 0% | 0% | 0% | 35.4176 | 0 | 0 | 0 | 35.4176 | 8878.2187 | 0 | 1775.6437 | 17.76% | 1 | 35.51% | 0% | 0% | 3.767 | 0 | 0 | 3.767 | 39.1847
2007-01-27 20:00 | 1 | 27 | 20 | 27 | 644 | 15.08 | 2522.0739 | 0 | 0 | 2522.0739 | Heating | 2225.3594 | 8.5 | 2225.3594 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.0719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2270.7749 | 0 | 454.155 | 4.542% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 21:00 | 1 | 27 | 21 | 27 | 645 | 15.08 | 2684.2271 | 0 | 0 | 2684.2271 | Heating | 2368.4357 | 8.5 | 2368.4357 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 473.6871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2416.7711 | 0 | 483.3542 | 4.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 22:00 | 1 | 27 | 22 | 27 | 646 | 15.98 | 2669.3856 | 0 | 0 | 2669.3856 | Heating | 2355.3402 | 8.5 | 2355.3402 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2403.4084 | 0 | 480.6817 | 4.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-27 23:00 | 1 | 27 | 23 | 27 | 647 | 15.98 | 2598.5402 | 0 | 0 | 2598.5402 | Heating | 2292.8296 | 8.5 | 2292.8296 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 458.5659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2339.622 | 0 | 467.9244 | 4.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 | 1 | 28 | 0 | 28 | 648 | 15.8 | 2627.2759 | 0 | 0 | 2627.2759 | Heating | 2318.1846 | 8.5 | 2318.1846 | 0 | 2.8226 | 0 | 0 | 0 | 0 | 8.5 | 0 | 463.6369 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2365.4945 | 0 | 473.0989 | 4.731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 01:00 | 1 | 28 | 1 | 28 | 649 | 17.6 | 2675.7451 | 0 | 0 | 2675.7451 | Heating | 2360.9515 | 8.5 | 2360.9515 | 0 | 2.8595 | 0 | 0 | 0 | 0 | 8.5 | 0 | 472.1903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2409.1342 | 0 | 481.8268 | 4.818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 02:00 | 1 | 28 | 2 | 28 | 650 | 17.06 | 2673.559 | 0 | 0 | 2673.559 | Heating | 2359.0226 | 8.5 | 2359.0226 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.8045 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2407.1659 | 0 | 481.4332 | 4.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 03:00 | 1 | 28 | 3 | 28 | 651 | 17.96 | 2643.2532 | 0 | 0 | 2643.2532 | Heating | 2332.2823 | 8.5 | 2332.2823 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 466.4565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2379.8799 | 0 | 475.976 | 4.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 04:00 | 1 | 28 | 4 | 28 | 652 | 17.96 | 2632.9433 | 0 | 0 | 2632.9433 | Heating | 2323.1853 | 8.5 | 2323.1853 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 464.6371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2370.5972 | 0 | 474.1194 | 4.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 05:00 | 1 | 28 | 5 | 28 | 653 | 17.96 | 2650.6359 | 0 | 0 | 2650.6359 | Heating | 2338.7964 | 8.5 | 2338.7964 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.7593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2386.527 | 0 | 477.3054 | 4.773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 06:00 | 1 | 28 | 6 | 28 | 654 | 14 | 2585.5711 | 0 | 0 | 2585.5711 | Heating | 2281.3862 | 8.5 | 2281.3862 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 456.2772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2327.9451 | 0 | 465.589 | 4.656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 07:00 | 1 | 28 | 7 | 28 | 655 | 12.2 | 13603.0995 | 0 | 0 | 13603.0995 | Heating | 12002.7349 | 8.5 | 12002.7349 | 0 | 2.7575 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2400.547 | 48.01% | 1 | 96.02% | 0% | 0% | 0% | 74.2326 | 0 | 0 | 0 | 74.2326 | 12247.6887 | 0 | 2449.5377 | 24.5% | 1 | 48.99% | 0% | 0% | 7.8954 | 0 | 0 | 7.8954 | 82.128
2007-01-28 08:00 | 1 | 28 | 8 | 28 | 656 | 12.92 | 10740.3408 | 0 | 0 | 10740.3408 | Heating | 9476.7713 | 8.5 | 9476.7713 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1895.3543 | 37.91% | 1 | 75.81% | 0% | 0% | 0% | 43.1091 | 0 | 0 | 0 | 43.1091 | 9670.1748 | 0 | 1934.035 | 19.34% | 1 | 38.68% | 0% | 0% | 4.5851 | 0 | 0 | 4.5851 | 47.6942
2007-01-28 09:00 | 1 | 28 | 9 | 28 | 657 | 19.94 | 8953.6914 | 0 | 0 | 8953.6914 | Heating | 7900.3159 | 8.5 | 7900.3159 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1580.0632 | 31.6% | 1 | 63.2% | 0% | 0% | 0% | 28.3682 | 0 | 0 | 0 | 28.3682 | 8061.5469 | 0 | 1612.3094 | 16.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.6428
2007-01-28 10:00 | 1 | 28 | 10 | 28 | 658 | 24.98 | 7004.2644 | 0 | 0 | 7004.2644 | Heating | 6180.2333 | 8.5 | 6180.2333 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1236.0467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6306.3605 | 0 | 1261.2721 | 12.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 11:00 | 1 | 28 | 11 | 28 | 659 | 24.98 | 5773.5313 | 0 | 0 | 5773.5313 | Heating | 5094.2923 | 8.5 | 5094.2923 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1018.8585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5198.2575 | 0 | 1039.6515 | 10.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 12:00 | 1 | 28 | 12 | 28 | 660 | 24.08 | 4756.0434 | 0 | 0 | 4756.0434 | Heating | 4196.5089 | 8.5 | 4196.5089 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 839.3018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4282.1519 | 0 | 856.4304 | 8.564% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 13:00 | 1 | 28 | 13 | 28 | 661 | 24.08 | 4058.7028 | 0 | 0 | 4058.7028 | Heating | 3581.2083 | 8.5 | 3581.2083 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 716.2417 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3654.2942 | 0 | 730.8588 | 7.309% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 14:00 | 1 | 28 | 14 | 28 | 662 | 24.08 | 3837.8081 | 0 | 0 | 3837.8081 | Heating | 3386.3013 | 8.5 | 3386.3013 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 677.2603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3455.4095 | 0 | 691.0819 | 6.911% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 15:00 | 1 | 28 | 15 | 28 | 663 | 26.96 | 4010.892 | 0 | 0 | 4010.892 | Heating | 3539.0224 | 8.5 | 3539.0224 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 707.8045 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3611.2473 | 0 | 722.2495 | 7.222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 16:00 | 1 | 28 | 16 | 28 | 664 | 24.98 | 3943.5484 | 0 | 0 | 3943.5484 | Heating | 3479.6015 | 8.5 | 3479.6015 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 695.9203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3550.6138 | 0 | 710.1228 | 7.101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 17:00 | 1 | 28 | 17 | 28 | 665 | 24.98 | 4163.0043 | 0 | 0 | 4163.0043 | Heating | 3673.2391 | 8.5 | 3673.2391 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 734.6478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3748.2031 | 0 | 749.6406 | 7.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 18:00 | 1 | 28 | 18 | 28 | 666 | 19.94 | 4754.0574 | 0 | 0 | 4754.0574 | Heating | 4194.7565 | 8.5 | 4194.7565 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 838.9513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4280.3638 | 0 | 856.0728 | 8.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 19:00 | 1 | 28 | 19 | 28 | 667 | 17.06 | 5012.5274 | 0 | 0 | 5012.5274 | Heating | 4422.8183 | 8.5 | 4422.8183 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 884.5637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4513.0799 | 0 | 902.616 | 9.026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 20:00 | 1 | 28 | 20 | 28 | 668 | 17.06 | 5330.4202 | 0 | 0 | 5330.4202 | Heating | 4703.312 | 8.5 | 4703.312 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 940.6624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4799.2979 | 0 | 959.8596 | 9.599% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 21:00 | 1 | 28 | 21 | 28 | 669 | 17.06 | 5738.081 | 0 | 0 | 5738.081 | Heating | 5063.0127 | 8.5 | 5063.0127 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1012.6025 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5166.3395 | 0 | 1033.2679 | 10.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 22:00 | 1 | 28 | 22 | 28 | 670 | 17.06 | 1795.7908 | 0 | 0 | 1795.7908 | Heating | 1584.5213 | 8.5 | 1584.5213 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 316.9043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1616.8584 | 0 | 323.3717 | 3.234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-28 23:00 | 1 | 28 | 23 | 28 | 671 | 17.06 | 1809.3189 | 0 | 0 | 1809.3189 | Heating | 1596.4578 | 8.5 | 1596.4578 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 319.2916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1629.0386 | 0 | 325.8077 | 3.258% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 | 1 | 29 | 0 | 29 | 672 | 17.06 | 2114.0254 | 0 | 0 | 2114.0254 | Heating | 1865.3165 | 8.5 | 1865.3165 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.0633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1903.3842 | 0 | 380.6768 | 3.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 01:00 | 1 | 29 | 1 | 29 | 673 | 15.98 | 2374.9361 | 0 | 0 | 2374.9361 | Heating | 2095.5319 | 8.5 | 2095.5319 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 419.1064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2138.2978 | 0 | 427.6596 | 4.277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 02:00 | 1 | 29 | 2 | 29 | 674 | 15.98 | 2688.0262 | 0 | 0 | 2688.0262 | Heating | 2371.7878 | 8.5 | 2371.7878 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 474.3576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2420.1916 | 0 | 484.0383 | 4.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 03:00 | 1 | 29 | 3 | 29 | 675 | 15.08 | 2803.9515 | 0 | 0 | 2803.9515 | Heating | 2474.0748 | 8.5 | 2474.0748 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2524.5662 | 0 | 504.9132 | 5.049% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 04:00 | 1 | 29 | 4 | 29 | 676 | 15.8 | 2834.1378 | 0 | 0 | 2834.1378 | Heating | 2500.7098 | 8.5 | 2500.7098 | 0 | 2.8226 | 0 | 0 | 0 | 0 | 8.5 | 0 | 500.142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2551.7447 | 0 | 510.3489 | 5.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 05:00 | 1 | 29 | 5 | 29 | 677 | 15.08 | 2801.2121 | 0 | 0 | 2801.2121 | Heating | 2471.6577 | 8.5 | 2471.6577 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.3315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2522.0997 | 0 | 504.4199 | 5.044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 06:00 | 1 | 29 | 6 | 29 | 678 | 14 | 2909.5202 | 0 | 0 | 2909.5202 | Heating | 2567.2237 | 8.5 | 2567.2237 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 513.4447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2619.616 | 0 | 523.9232 | 5.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 07:00 | 1 | 29 | 7 | 29 | 679 | 12.2 | 14595.2257 | 0 | 0 | 14595.2257 | Heating | 12878.1403 | 8.5 | 12878.1403 | 0 | 2.7575 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2575.6281 | 51.51% | 2 | 51.51% | 51.51% | 0% | 0% | 17.7232 | 17.7232 | 0 | 0 | 35.4465 | 13140.9595 | 0 | 2628.1919 | 26.28% | 1 | 52.56% | 0% | 0% | 9.2831 | 0 | 0 | 9.2831 | 44.7296
2007-01-29 08:00 | 1 | 29 | 8 | 29 | 680 | 12.02 | 12111.014 | 0 | 0 | 12111.014 | Heating | 10686.1889 | 8.5 | 10686.1889 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2137.2378 | 42.74% | 1 | 85.49% | 0% | 0% | 0% | 56.8254 | 0 | 0 | 0 | 56.8254 | 10904.2743 | 0 | 2180.8549 | 21.81% | 1 | 43.62% | 0% | 0% | 6.044 | 0 | 0 | 6.044 | 62.8694
2007-01-29 09:00 | 1 | 29 | 9 | 29 | 681 | 15.08 | 9910.654 | 0 | 0 | 9910.654 | Heating | 8744.6947 | 8.5 | 8744.6947 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1748.9389 | 34.98% | 1 | 69.96% | 0% | 0% | 0% | 35.8313 | 0 | 0 | 0 | 35.8313 | 8923.1578 | 0 | 1784.6316 | 17.85% | 1 | 35.69% | 0% | 0% | 3.811 | 0 | 0 | 3.811 | 39.6424
2007-01-29 10:00 | 1 | 29 | 10 | 29 | 682 | 17.06 | 8113.926 | 0 | 0 | 8113.926 | Heating | 7159.3464 | 8.5 | 7159.3464 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1431.8693 | 30% | 1 | 57.27% | 0% | 0% | 0% | 22.6182 | 0 | 0 | 0 | 22.6182 | 7305.4556 | 0 | 1461.0911 | 14.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.8928
2007-01-29 11:00 | 1 | 29 | 11 | 29 | 683 | 17.06 | 6447.9588 | 0 | 0 | 6447.9588 | Heating | 5689.3754 | 8.5 | 5689.3754 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1137.8751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5805.4851 | 0 | 1161.097 | 11.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 12:00 | 1 | 29 | 12 | 29 | 684 | 19.04 | 5278.2925 | 0 | 0 | 5278.2925 | Heating | 4657.3169 | 8.5 | 4657.3169 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 931.4634 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4752.3642 | 0 | 950.4728 | 9.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 13:00 | 1 | 29 | 13 | 29 | 685 | 19.94 | 5074.0041 | 0 | 0 | 5074.0041 | Heating | 4477.0625 | 8.5 | 4477.0625 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 895.4125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4568.4311 | 0 | 913.6862 | 9.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 14:00 | 1 | 29 | 14 | 29 | 686 | 19.94 | 4965.6815 | 0 | 0 | 4965.6815 | Heating | 4381.4837 | 8.5 | 4381.4837 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 876.2967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4470.9018 | 0 | 894.1804 | 8.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 15:00 | 1 | 29 | 15 | 29 | 687 | 19.94 | 4652.8261 | 0 | 0 | 4652.8261 | Heating | 4105.4348 | 8.5 | 4105.4348 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 821.087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4189.2191 | 0 | 837.8438 | 8.378% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 16:00 | 1 | 29 | 16 | 29 | 688 | 21.92 | 4514.3312 | 0 | 0 | 4514.3312 | Heating | 3983.2334 | 8.5 | 3983.2334 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 796.6467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4064.5239 | 0 | 812.9048 | 8.129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 17:00 | 1 | 29 | 17 | 29 | 689 | 21.92 | 4905.6447 | 0 | 0 | 4905.6447 | Heating | 4328.51 | 8.5 | 4328.51 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 865.702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4416.847 | 0 | 883.3694 | 8.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 18:00 | 1 | 29 | 18 | 29 | 690 | 17.96 | 5489.7125 | 0 | 0 | 5489.7125 | Heating | 4843.864 | 8.5 | 4843.864 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 968.7728 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4942.7183 | 0 | 988.5437 | 9.885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 19:00 | 1 | 29 | 19 | 29 | 691 | 17.06 | 5637.8817 | 0 | 0 | 5637.8817 | Heating | 4974.6015 | 8.5 | 4974.6015 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 994.9203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5076.124 | 0 | 1015.2248 | 10.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 20:00 | 1 | 29 | 20 | 29 | 692 | 17.06 | 5814.1289 | 0 | 0 | 5814.1289 | Heating | 5130.1137 | 8.5 | 5130.1137 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1026.0227 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5234.8099 | 0 | 1046.962 | 10.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 21:00 | 1 | 29 | 21 | 29 | 693 | 17.06 | 6342.8209 | 0 | 0 | 6342.8209 | Heating | 5596.6066 | 8.5 | 5596.6066 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1119.3213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5710.8231 | 0 | 1142.1646 | 11.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 22:00 | 1 | 29 | 22 | 29 | 694 | 12.92 | 2033.4203 | 0 | 0 | 2033.4203 | Heating | 1794.1944 | 8.5 | 1794.1944 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.8389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1830.8106 | 0 | 366.1621 | 3.662% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-29 23:00 | 1 | 29 | 23 | 29 | 695 | 12.92 | 2184.4296 | 0 | 0 | 2184.4296 | Heating | 1927.4379 | 8.5 | 1927.4379 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.4876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1966.7734 | 0 | 393.3547 | 3.934% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 | 1 | 30 | 0 | 30 | 696 | 10.94 | 2547.022 | 0 | 0 | 2547.022 | Heating | 2247.3724 | 8.5 | 2247.3724 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.4745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2293.2371 | 0 | 458.6474 | 4.586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 01:00 | 1 | 30 | 1 | 30 | 697 | 10.04 | 2762.2977 | 0 | 0 | 2762.2977 | Heating | 2437.3215 | 8.5 | 2437.3215 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 487.4643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2487.0628 | 0 | 497.4126 | 4.974% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 02:00 | 1 | 30 | 2 | 30 | 698 | 10.04 | 2939.5651 | 0 | 0 | 2939.5651 | Heating | 2593.7339 | 8.5 | 2593.7339 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 518.7468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2646.6672 | 0 | 529.3334 | 5.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 03:00 | 1 | 30 | 3 | 30 | 699 | 8.96 | 3097.8855 | 0 | 0 | 3097.8855 | Heating | 2733.4284 | 8.5 | 2733.4284 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 546.6857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2789.2126 | 0 | 557.8425 | 5.578% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 04:00 | 1 | 30 | 4 | 30 | 700 | 8.96 | 3248.9686 | 0 | 0 | 3248.9686 | Heating | 2866.737 | 8.5 | 2866.737 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 573.3474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2925.2419 | 0 | 585.0484 | 5.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 05:00 | 1 | 30 | 5 | 30 | 701 | 8.96 | 3384.8788 | 0 | 0 | 3384.8788 | Heating | 2986.6577 | 8.5 | 2986.6577 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 597.3315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3047.6099 | 0 | 609.522 | 6.095% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 06:00 | 1 | 30 | 6 | 30 | 702 | 10.94 | 3451.118 | 0 | 0 | 3451.118 | Heating | 3045.1042 | 8.5 | 3045.1042 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 609.0208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3107.2491 | 0 | 621.4498 | 6.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 07:00 | 1 | 30 | 7 | 30 | 703 | 8.96 | 15898.1088 | 0 | 0 | 15898.1088 | Heating | 14027.7431 | 8.5 | 14027.7431 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2805.5486 | 56.11% | 2 | 56.11% | 56.11% | 0% | 0% | 21.5751 | 21.5751 | 0 | 0 | 43.1502 | 14314.0235 | 0 | 2862.8047 | 28.63% | 1 | 57.26% | 0% | 0% | 11.3006 | 0 | 0 | 11.3006 | 54.4509
2007-01-30 08:00 | 1 | 30 | 8 | 30 | 704 | 8.96 | 13498.1291 | 0 | 0 | 13498.1291 | Heating | 11910.1139 | 8.5 | 11910.1139 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2382.0228 | 47.64% | 1 | 95.28% | 0% | 0% | 0% | 72.9217 | 0 | 0 | 0 | 72.9217 | 12153.1775 | 0 | 2430.6355 | 24.31% | 1 | 48.61% | 0% | 0% | 7.756 | 0 | 0 | 7.756 | 80.6777
2007-01-30 09:00 | 1 | 30 | 9 | 30 | 705 | 15.98 | 10995.8663 | 0 | 0 | 10995.8663 | Heating | 9702.235 | 8.5 | 9702.235 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1940.447 | 38.81% | 1 | 77.62% | 0% | 0% | 0% | 45.5046 | 0 | 0 | 0 | 45.5046 | 9900.2397 | 0 | 1980.0479 | 19.8% | 1 | 39.6% | 0% | 0% | 4.8399 | 0 | 0 | 4.8399 | 50.3445
2007-01-30 10:00 | 1 | 30 | 10 | 30 | 706 | 19.04 | 8749.8157 | 0 | 0 | 8749.8157 | Heating | 7720.4256 | 8.5 | 7720.4256 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1544.0851 | 30.88% | 1 | 61.76% | 0% | 0% | 0% | 26.9045 | 0 | 0 | 0 | 26.9045 | 7877.9853 | 0 | 1575.5971 | 15.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.179
2007-01-30 11:00 | 1 | 30 | 11 | 30 | 707 | 19.04 | 7245.6925 | 0 | 0 | 7245.6925 | Heating | 6393.2581 | 8.5 | 6393.2581 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1278.6516 | 30% | 1 | 51.15% | 0% | 0% | 0% | 17.4346 | 0 | 0 | 0 | 17.4346 | 6523.7328 | 0 | 1304.7466 | 13.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7091
2007-01-30 12:00 | 1 | 30 | 12 | 30 | 708 | 23 | 5874.2889 | 0 | 0 | 5874.2889 | Heating | 5183.1961 | 8.5 | 5183.1961 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1036.6392 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5288.9756 | 0 | 1057.7951 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 13:00 | 1 | 30 | 13 | 30 | 709 | 26.06 | 5050.1707 | 0 | 0 | 5050.1707 | Heating | 4456.033 | 8.5 | 4456.033 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 891.2066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4546.9724 | 0 | 909.3945 | 9.094% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 14:00 | 1 | 30 | 14 | 30 | 710 | 26.06 | 4322.1207 | 13.6347 | 13.6347 | 4308.486 | Heating | 3801.6053 | 8.5 | 3801.6053 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 760.3211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3879.1891 | 0 | 775.8378 | 7.758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 15:00 | 1 | 30 | 15 | 30 | 711 | 26.96 | 4083.3627 | 35.4253 | 35.4253 | 4047.9374 | Heating | 3571.7095 | 8.5 | 3571.7095 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 714.3419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3644.6015 | 0 | 728.9203 | 7.289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 16:00 | 1 | 30 | 16 | 30 | 712 | 28.04 | 3948.4687 | 34.9635 | 34.9635 | 3913.5052 | Heating | 3453.0928 | 8.5 | 3453.0928 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 690.6186 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3523.5641 | 0 | 704.7128 | 7.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 17:00 | 1 | 30 | 17 | 30 | 713 | 28.04 | 4182.5462 | 9.2592 | 9.2592 | 4173.287 | Heating | 3682.3121 | 8.5 | 3682.3121 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 736.4624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3757.4613 | 0 | 751.4923 | 7.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 18:00 | 1 | 30 | 18 | 30 | 714 | 26.06 | 4790.1301 | 0 | 0 | 4790.1301 | Heating | 4226.5854 | 8.5 | 4226.5854 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 845.3171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4312.8422 | 0 | 862.5684 | 8.626% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 19:00 | 1 | 30 | 19 | 30 | 715 | 24.08 | 5446.7883 | 0 | 0 | 5446.7883 | Heating | 4805.9897 | 8.5 | 4805.9897 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 961.1979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4904.0711 | 0 | 980.8142 | 9.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 20:00 | 1 | 30 | 20 | 30 | 716 | 24.08 | 5952.7106 | 0 | 0 | 5952.7106 | Heating | 5252.3917 | 8.5 | 5252.3917 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1050.4783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5359.5834 | 0 | 1071.9167 | 10.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 21:00 | 1 | 30 | 21 | 30 | 717 | 23 | 6548.3241 | 0 | 0 | 6548.3241 | Heating | 5777.9331 | 8.5 | 5777.9331 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1155.5866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5895.8501 | 0 | 1179.17 | 11.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 22:00 | 1 | 30 | 22 | 30 | 718 | 21.92 | 2037.554 | 0 | 0 | 2037.554 | Heating | 1797.8418 | 8.5 | 1797.8418 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 359.5684 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1834.5324 | 0 | 366.9065 | 3.669% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-30 23:00 | 1 | 30 | 23 | 30 | 719 | 21.92 | 2032.1191 | 0 | 0 | 2032.1191 | Heating | 1793.0463 | 8.5 | 1793.0463 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.6093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1829.639 | 0 | 365.9278 | 3.659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 | 1 | 31 | 0 | 31 | 720 | 21.2 | 2400.3915 | 0 | 0 | 2400.3915 | Heating | 2117.9925 | 8.5 | 2117.9925 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 423.5985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2161.2168 | 0 | 432.2434 | 4.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 01:00 | 1 | 31 | 1 | 31 | 721 | 21.2 | 2695.1839 | 0 | 0 | 2695.1839 | Heating | 2378.1034 | 8.5 | 2378.1034 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 475.6207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2426.6362 | 0 | 485.3272 | 4.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 02:00 | 1 | 31 | 2 | 31 | 722 | 19.94 | 2911.7403 | 0 | 0 | 2911.7403 | Heating | 2569.1827 | 8.5 | 2569.1827 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 513.8365 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2621.615 | 0 | 524.323 | 5.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 03:00 | 1 | 31 | 3 | 31 | 723 | 15.08 | 3237.9994 | 0 | 0 | 3237.9994 | Heating | 2857.0583 | 8.5 | 2857.0583 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 571.4117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2915.3656 | 0 | 583.0731 | 5.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 04:00 | 1 | 31 | 4 | 31 | 724 | 14 | 3336.4174 | 0 | 0 | 3336.4174 | Heating | 2943.8977 | 8.5 | 2943.8977 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 588.7795 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3003.9773 | 0 | 600.7955 | 6.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 05:00 | 1 | 31 | 5 | 31 | 725 | 14 | 3380.5342 | 0 | 0 | 3380.5342 | Heating | 2982.8243 | 8.5 | 2982.8243 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 596.5649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3043.6982 | 0 | 608.7396 | 6.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 06:00 | 1 | 31 | 6 | 31 | 726 | 10.94 | 3402.414 | 0 | 0 | 3402.414 | Heating | 3002.13 | 8.5 | 3002.13 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 600.426 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3063.398 | 0 | 612.6796 | 6.127% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 07:00 | 1 | 31 | 7 | 31 | 727 | 10.94 | 15709.5113 | 0 | 0 | 15709.5113 | Heating | 13861.3335 | 8.5 | 13861.3335 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2772.2667 | 55.45% | 2 | 55.45% | 55.45% | 0% | 0% | 20.991 | 20.991 | 0 | 0 | 41.9819 | 14144.2178 | 0 | 2828.8436 | 28.29% | 1 | 56.58% | 0% | 0% | 10.9947 | 0 | 0 | 10.9947 | 52.9766
2007-01-31 08:00 | 1 | 31 | 8 | 31 | 728 | 10.94 | 13193.2155 | 0 | 0 | 13193.2155 | Heating | 11641.0725 | 8.5 | 11641.0725 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2328.2145 | 46.56% | 1 | 93.13% | 0% | 0% | 0% | 69.1885 | 0 | 0 | 0 | 69.1885 | 11878.6454 | 0 | 2375.7291 | 23.76% | 1 | 47.51% | 0% | 0% | 7.3589 | 0 | 0 | 7.3589 | 76.5474
2007-01-31 09:00 | 1 | 31 | 9 | 31 | 729 | 15.08 | 11328.8493 | 0 | 0 | 11328.8493 | Heating | 9996.0435 | 8.5 | 9996.0435 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1999.2087 | 39.98% | 1 | 79.97% | 0% | 0% | 0% | 48.7365 | 0 | 0 | 0 | 48.7365 | 10200.0444 | 0 | 2040.0089 | 20.4% | 1 | 40.8% | 0% | 0% | 5.1837 | 0 | 0 | 5.1837 | 53.9202
2007-01-31 10:00 | 1 | 31 | 10 | 31 | 730 | 19.94 | 9628.7164 | 0 | 0 | 9628.7164 | Heating | 8495.9263 | 8.5 | 8495.9263 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1699.1853 | 33.98% | 1 | 67.97% | 0% | 0% | 0% | 33.5301 | 0 | 0 | 0 | 33.5301 | 8669.3125 | 0 | 1733.8625 | 17.34% | 1 | 34.68% | 0% | 0% | 3.5663 | 0 | 0 | 3.5663 | 37.0964
2007-01-31 11:00 | 1 | 31 | 11 | 31 | 731 | 19.94 | 8672.537 | 0 | 0 | 8672.537 | Heating | 7652.2385 | 8.5 | 7652.2385 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1530.4477 | 30.61% | 1 | 61.22% | 0% | 0% | 0% | 26.3611 | 0 | 0 | 0 | 26.3611 | 7808.4067 | 0 | 1561.6813 | 15.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.6356
2007-01-31 12:00 | 1 | 31 | 12 | 31 | 732 | 26.06 | 7787.0158 | 0 | 0 | 7787.0158 | Heating | 6870.8963 | 8.5 | 6870.8963 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1374.1793 | 30% | 1 | 54.97% | 0% | 0% | 0% | 20.5769 | 0 | 0 | 0 | 20.5769 | 7011.1187 | 0 | 1402.2237 | 14.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.8515
2007-01-31 13:00 | 1 | 31 | 13 | 31 | 733 | 26.6 | 7141.9893 | 0 | 0 | 7141.9893 | Heating | 6301.7553 | 8.5 | 6301.7553 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1260.3511 | 30% | 1 | 50.41% | 0% | 0% | 0% | 16.866 | 0 | 0 | 0 | 16.866 | 6430.3625 | 0 | 1286.0725 | 12.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.1405
2007-01-31 14:00 | 1 | 31 | 14 | 31 | 734 | 26.06 | 6589.8386 | 0 | 0 | 6589.8386 | Heating | 5814.5635 | 8.5 | 5814.5635 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1162.9127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5933.228 | 0 | 1186.6456 | 11.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 15:00 | 1 | 31 | 15 | 31 | 735 | 28.94 | 6315.1146 | 0 | 0 | 6315.1146 | Heating | 5572.1599 | 8.5 | 5572.1599 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1114.432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5685.8775 | 0 | 1137.1755 | 11.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 16:00 | 1 | 31 | 16 | 31 | 736 | 28.04 | 6215.4784 | 0 | 0 | 6215.4784 | Heating | 5484.2457 | 8.5 | 5484.2457 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1096.8491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5596.1691 | 0 | 1119.2338 | 11.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 17:00 | 1 | 31 | 17 | 31 | 737 | 28.04 | 6275.2195 | 0 | 0 | 6275.2195 | Heating | 5536.9584 | 8.5 | 5536.9584 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1107.3917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5649.9575 | 0 | 1129.9915 | 11.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 18:00 | 1 | 31 | 18 | 31 | 738 | 26.06 | 6442.4519 | 0 | 0 | 6442.4519 | Heating | 5684.5163 | 8.5 | 5684.5163 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1136.9033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5800.5269 | 0 | 1160.1054 | 11.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 19:00 | 1 | 31 | 19 | 31 | 739 | 19.58 | 6377.5258 | 0 | 0 | 6377.5258 | Heating | 5627.2287 | 8.5 | 5627.2287 | 0 | 2.9041 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1125.4457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5742.0701 | 0 | 1148.414 | 11.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 20:00 | 1 | 31 | 20 | 31 | 740 | 17.6 | 6547.868 | 0 | 0 | 6547.868 | Heating | 5777.5306 | 8.5 | 5777.5306 | 0 | 2.8595 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1155.5061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5895.4394 | 0 | 1179.0879 | 11.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 21:00 | 1 | 31 | 21 | 31 | 741 | 16.34 | 6775.1101 | 0 | 0 | 6775.1101 | Heating | 5978.0383 | 8.5 | 5978.0383 | 0 | 2.8333 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1195.6077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6100.0391 | 0 | 1220.0078 | 12.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 22:00 | 1 | 31 | 22 | 31 | 742 | 18.14 | 1843.6822 | 0 | 0 | 1843.6822 | Heating | 1626.7784 | 8.5 | 1626.7784 | 0 | 2.8712 | 0 | 0 | 0 | 0 | 8.5 | 0 | 325.3557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1659.9779 | 0 | 331.9956 | 3.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-01-31 23:00 | 1 | 31 | 23 | 31 | 743 | 20.3 | 1480.7455 | 0 | 0 | 1480.7455 | Heating | 1306.5401 | 8.5 | 1306.5401 | 0 | 2.9214 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1333.2042 | 0 | 266.6408 | 2.666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 | 2 | 1 | 0 | 32 | 744 | 22.64 | 1497.6615 | 0 | 0 | 1497.6615 | Heating | 1321.466 | 8.5 | 1321.466 | 0 | 2.9825 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.2932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1348.4347 | 0 | 269.6869 | 2.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 01:00 | 2 | 1 | 1 | 32 | 745 | 24.08 | 1400.2836 | 0 | 0 | 1400.2836 | Heating | 1235.5444 | 8.5 | 1235.5444 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.1089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1260.7596 | 0 | 252.1519 | 2.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 02:00 | 2 | 1 | 2 | 32 | 746 | 24.08 | 1261.9026 | 0 | 0 | 1261.9026 | Heating | 1113.4435 | 8.5 | 1113.4435 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.6887 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1136.1668 | 0 | 227.2334 | 2.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 03:00 | 2 | 1 | 3 | 32 | 747 | 23.72 | 1109.6386 | 0 | 0 | 1109.6386 | Heating | 979.0929 | 8.5 | 979.0929 | 0 | 3.0132 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.8186 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 999.0743 | 0 | 199.8149 | 1.998% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 04:00 | 2 | 1 | 4 | 32 | 748 | 23.36 | 950.6362 | 0 | 0 | 950.6362 | Heating | 838.7966 | 8.5 | 838.7966 | 0 | 3.0028 | 0 | 0 | 0 | 0 | 8.5 | 0 | 167.7593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 855.9149 | 0 | 171.183 | 1.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 05:00 | 2 | 1 | 5 | 32 | 749 | 22.64 | 883.7069 | 0 | 0 | 883.7069 | Heating | 779.7414 | 8.5 | 779.7414 | 0 | 2.9825 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.9483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 795.6545 | 0 | 159.1309 | 1.591% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 06:00 | 2 | 1 | 6 | 32 | 750 | 23 | 859.7209 | 0 | 0 | 859.7209 | Heating | 758.5773 | 8.5 | 758.5773 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.7155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 774.0585 | 0 | 154.8117 | 1.548% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 07:00 | 2 | 1 | 7 | 32 | 751 | 21.92 | 7615.7336 | 7.6312 | 7.6312 | 7608.1024 | Heating | 6713.0315 | 8.5 | 6713.0315 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1342.6063 | 30% | 1 | 53.7% | 0% | 0% | 0% | 19.5058 | 0 | 0 | 0 | 19.5058 | 6850.0322 | 0 | 1370.0064 | 13.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.7803
2007-02-01 08:00 | 2 | 1 | 8 | 32 | 752 | 21.92 | 5390.816 | 0 | 0 | 5390.816 | Heating | 4756.6024 | 8.5 | 4756.6024 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 951.3205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4853.6759 | 0 | 970.7352 | 9.707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 09:00 | 2 | 1 | 9 | 32 | 753 | 24.98 | 4162.7614 | 0 | 0 | 4162.7614 | Heating | 3673.0248 | 8.5 | 3673.0248 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 734.605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3747.9845 | 0 | 749.5969 | 7.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 10:00 | 2 | 1 | 10 | 32 | 754 | 24.98 | 3103.5633 | 0 | 0 | 3103.5633 | Heating | 2738.4382 | 8.5 | 2738.4382 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 547.6876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2794.3247 | 0 | 558.8649 | 5.589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 11:00 | 2 | 1 | 11 | 32 | 755 | 24.98 | 2581.1997 | 0 | 0 | 2581.1997 | Heating | 2277.5292 | 8.5 | 2277.5292 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 455.5058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2324.0093 | 0 | 464.8019 | 4.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 12:00 | 2 | 1 | 12 | 32 | 756 | 23 | 2089.3772 | 0 | 0 | 2089.3772 | Heating | 1843.5681 | 8.5 | 1843.5681 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.7136 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1881.1919 | 0 | 376.2384 | 3.762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 13:00 | 2 | 1 | 13 | 32 | 757 | 24.98 | 1851.9088 | 0 | 0 | 1851.9088 | Heating | 1634.0372 | 8.5 | 1634.0372 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 326.8074 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1667.3849 | 0 | 333.477 | 3.335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 14:00 | 2 | 1 | 14 | 32 | 758 | 24.98 | 1632.3596 | 0 | 0 | 1632.3596 | Heating | 1440.3173 | 8.5 | 1440.3173 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 288.0635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1469.7115 | 0 | 293.9423 | 2.939% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 15:00 | 2 | 1 | 15 | 32 | 759 | 24.08 | 1496.2981 | 0 | 0 | 1496.2981 | Heating | 1320.263 | 8.5 | 1320.263 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.0526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1347.2071 | 0 | 269.4414 | 2.694% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 16:00 | 2 | 1 | 16 | 32 | 760 | 24.08 | 1415.5709 | 0 | 0 | 1415.5709 | Heating | 1249.0331 | 8.5 | 1249.0331 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.8066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1274.5236 | 0 | 254.9047 | 2.549% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 17:00 | 2 | 1 | 17 | 32 | 761 | 24.08 | 1444.4412 | 0 | 0 | 1444.4412 | Heating | 1274.5069 | 8.5 | 1274.5069 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.9014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1300.5173 | 0 | 260.1035 | 2.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 18:00 | 2 | 1 | 18 | 32 | 762 | 21.02 | 1614.821 | 0 | 0 | 1614.821 | Heating | 1424.8421 | 8.5 | 1424.8421 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 284.9684 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1453.9205 | 0 | 290.7841 | 2.908% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 19:00 | 2 | 1 | 19 | 32 | 763 | 19.94 | 1773.8943 | 0 | 0 | 1773.8943 | Heating | 1565.2009 | 8.5 | 1565.2009 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.0402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1597.1438 | 0 | 319.4288 | 3.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 20:00 | 2 | 1 | 20 | 32 | 764 | 19.94 | 1975.7546 | 0 | 0 | 1975.7546 | Heating | 1743.3129 | 8.5 | 1743.3129 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 348.6626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1778.8907 | 0 | 355.7781 | 3.558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 21:00 | 2 | 1 | 21 | 32 | 765 | 19.94 | 2126.8035 | 0 | 0 | 2126.8035 | Heating | 1876.5913 | 8.5 | 1876.5913 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 375.3183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1914.8891 | 0 | 382.9778 | 3.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 22:00 | 2 | 1 | 22 | 32 | 766 | 19.4 | 588.8891 | 0 | 0 | 588.8891 | Heating | 519.6081 | 8.5 | 519.6081 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 103.9216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 530.2123 | 0 | 106.0425 | 1.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-01 23:00 | 2 | 1 | 23 | 32 | 767 | 19.04 | 548.554 | 0 | 0 | 548.554 | Heating | 484.0183 | 8.5 | 484.0183 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.8037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 493.8962 | 0 | 98.7792 | 0.9878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 | 2 | 2 | 0 | 33 | 768 | 19.4 | 572.5059 | 0 | 0 | 572.5059 | Heating | 505.1523 | 8.5 | 505.1523 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.0305 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 515.4615 | 0 | 103.0923 | 1.031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 01:00 | 2 | 2 | 1 | 33 | 769 | 15.98 | 581.4864 | 0 | 0 | 581.4864 | Heating | 513.0762 | 8.5 | 513.0762 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.6152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 523.5471 | 0 | 104.7094 | 1.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 02:00 | 2 | 2 | 2 | 33 | 770 | 15.98 | 570.2683 | 0 | 0 | 570.2683 | Heating | 503.1779 | 8.5 | 503.1779 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.6356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 513.4469 | 0 | 102.6894 | 1.027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 03:00 | 2 | 2 | 3 | 33 | 771 | 15.98 | 566.6387 | 0 | 0 | 566.6387 | Heating | 499.9753 | 8.5 | 499.9753 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.9951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 510.1789 | 0 | 102.0358 | 1.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 04:00 | 2 | 2 | 4 | 33 | 772 | 12.92 | 569.9756 | 0 | 0 | 569.9756 | Heating | 502.9197 | 8.5 | 502.9197 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.5839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 513.1833 | 0 | 102.6367 | 1.026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 05:00 | 2 | 2 | 5 | 33 | 773 | 12.92 | 568.1907 | 0 | 0 | 568.1907 | Heating | 501.3447 | 8.5 | 501.3447 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.2689 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 511.5762 | 0 | 102.3152 | 1.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 06:00 | 2 | 2 | 6 | 33 | 774 | 10.94 | 543.532 | 0 | 0 | 543.532 | Heating | 479.5871 | 8.5 | 479.5871 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.9174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 489.3746 | 0 | 97.8749 | 0.9787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 07:00 | 2 | 2 | 7 | 33 | 775 | 10.04 | 5341.3411 | 20.059 | 20.059 | 5321.2822 | Heating | 4695.249 | 8.5 | 4695.249 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 939.0498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4791.0704 | 0 | 958.2141 | 9.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 08:00 | 2 | 2 | 8 | 33 | 776 | 10.04 | 4303.3275 | 0 | 0 | 4303.3275 | Heating | 3797.0536 | 8.5 | 3797.0536 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 759.4107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3874.5445 | 0 | 774.9089 | 7.749% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 09:00 | 2 | 2 | 9 | 33 | 777 | 17.06 | 4123.9278 | 0 | 0 | 4123.9278 | Heating | 3638.7598 | 8.5 | 3638.7598 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3713.0202 | 0 | 742.604 | 7.426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 10:00 | 2 | 2 | 10 | 33 | 778 | 19.04 | 3855.9078 | 0 | 0 | 3855.9078 | Heating | 3402.2716 | 8.5 | 3402.2716 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 680.4543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3471.7057 | 0 | 694.3411 | 6.943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 11:00 | 2 | 2 | 11 | 33 | 779 | 19.04 | 3677.2428 | 0 | 0 | 3677.2428 | Heating | 3244.626 | 8.5 | 3244.626 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 648.9252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3310.8428 | 0 | 662.1686 | 6.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 12:00 | 2 | 2 | 12 | 33 | 780 | 24.98 | 3444.8834 | 0 | 0 | 3444.8834 | Heating | 3039.603 | 8.5 | 3039.603 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 607.9206 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3101.6357 | 0 | 620.3271 | 6.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 13:00 | 2 | 2 | 13 | 33 | 781 | 24.98 | 3456.8867 | 0 | 0 | 3456.8867 | Heating | 3050.1942 | 8.5 | 3050.1942 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 610.0388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3112.443 | 0 | 622.4886 | 6.225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 14:00 | 2 | 2 | 14 | 33 | 782 | 24.98 | 3676.6092 | 0 | 0 | 3676.6092 | Heating | 3244.067 | 8.5 | 3244.067 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 648.8134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3310.2724 | 0 | 662.0545 | 6.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 15:00 | 2 | 2 | 15 | 33 | 783 | 26.06 | 3814.7087 | 0 | 0 | 3814.7087 | Heating | 3365.9195 | 8.5 | 3365.9195 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 673.1839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3434.6117 | 0 | 686.9223 | 6.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 16:00 | 2 | 2 | 16 | 33 | 784 | 26.06 | 3902.6514 | 0 | 0 | 3902.6514 | Heating | 3443.5159 | 8.5 | 3443.5159 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 688.7032 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3513.7918 | 0 | 702.7584 | 7.028% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 17:00 | 2 | 2 | 17 | 33 | 785 | 26.06 | 4107.8379 | 0 | 0 | 4107.8379 | Heating | 3624.5629 | 8.5 | 3624.5629 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 724.9126 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3698.5335 | 0 | 739.7067 | 7.397% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 18:00 | 2 | 2 | 18 | 33 | 786 | 24.08 | 4427.3197 | 0 | 0 | 4427.3197 | Heating | 3906.4585 | 8.5 | 3906.4585 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 781.2917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3986.1822 | 0 | 797.2364 | 7.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 19:00 | 2 | 2 | 19 | 33 | 787 | 21.92 | 4880.1145 | 0 | 0 | 4880.1145 | Heating | 4305.9833 | 8.5 | 4305.9833 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 861.1967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4393.8606 | 0 | 878.7721 | 8.788% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 20:00 | 2 | 2 | 20 | 33 | 788 | 21.92 | 5573.7946 | 0 | 0 | 5573.7946 | Heating | 4918.0541 | 8.5 | 4918.0541 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 983.6108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5018.4225 | 0 | 1003.6845 | 10.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 21:00 | 2 | 2 | 21 | 33 | 789 | 19.94 | 6052.1788 | 0 | 0 | 6052.1788 | Heating | 5340.1577 | 8.5 | 5340.1577 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1068.0315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5449.1405 | 0 | 1089.8281 | 10.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 22:00 | 2 | 2 | 22 | 33 | 790 | 19.94 | 6685.2243 | 0 | 0 | 6685.2243 | Heating | 5898.7273 | 8.5 | 5898.7273 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1179.7455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6019.1095 | 0 | 1203.8219 | 12.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-02 23:00 | 2 | 2 | 23 | 33 | 791 | 19.94 | 2077.6786 | 0 | 0 | 2077.6786 | Heating | 1833.2458 | 8.5 | 1833.2458 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 366.6492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1870.659 | 0 | 374.1318 | 3.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 | 2 | 3 | 0 | 34 | 792 | 19.94 | 2207.2702 | 0 | 0 | 2207.2702 | Heating | 1947.5914 | 8.5 | 1947.5914 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 389.5183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1987.3381 | 0 | 397.4676 | 3.975% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 01:00 | 2 | 3 | 1 | 34 | 793 | 21.02 | 2484.452 | 0 | 0 | 2484.452 | Heating | 2192.1635 | 8.5 | 2192.1635 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.4327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2236.9015 | 0 | 447.3803 | 4.474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 02:00 | 2 | 3 | 2 | 34 | 794 | 21.02 | 2721.9951 | 0 | 0 | 2721.9951 | Heating | 2401.7603 | 8.5 | 2401.7603 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 480.3521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2450.7759 | 0 | 490.1552 | 4.902% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 03:00 | 2 | 3 | 3 | 34 | 795 | 21.02 | 2793.5219 | 0 | 0 | 2793.5219 | Heating | 2464.8723 | 8.5 | 2464.8723 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 492.9745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2515.1758 | 0 | 503.0352 | 5.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 04:00 | 2 | 3 | 4 | 34 | 796 | 19.94 | 2860.4004 | 0 | 0 | 2860.4004 | Heating | 2523.8827 | 8.5 | 2523.8827 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 504.7765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2575.3905 | 0 | 515.0781 | 5.151% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 05:00 | 2 | 3 | 5 | 34 | 797 | 19.94 | 2965.6629 | 0 | 0 | 2965.6629 | Heating | 2616.7614 | 8.5 | 2616.7614 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.3523 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2670.1647 | 0 | 534.0329 | 5.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 06:00 | 2 | 3 | 6 | 34 | 798 | 17.06 | 3119.9856 | 0 | 0 | 3119.9856 | Heating | 2752.9285 | 8.5 | 2752.9285 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.5857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2809.1107 | 0 | 561.8221 | 5.618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 07:00 | 2 | 3 | 7 | 34 | 799 | 15.98 | 3243.2101 | 0 | 0 | 3243.2101 | Heating | 2861.656 | 8.5 | 2861.656 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 572.3312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2920.0571 | 0 | 584.0114 | 5.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 08:00 | 2 | 3 | 8 | 34 | 800 | 15.98 | 3282.1666 | 0 | 0 | 3282.1666 | Heating | 2896.0293 | 8.5 | 2896.0293 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 579.2059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2955.132 | 0 | 591.0264 | 5.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 09:00 | 2 | 3 | 9 | 34 | 801 | 19.04 | 13824.7162 | 0 | 0 | 13824.7162 | Heating | 12198.279 | 8.5 | 12198.279 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2439.6558 | 48.79% | 1 | 97.59% | 0% | 0% | 0% | 77.0436 | 0 | 0 | 0 | 77.0436 | 12447.2235 | 0 | 2489.4447 | 24.89% | 1 | 49.79% | 0% | 0% | 8.1944 | 0 | 0 | 8.1944 | 85.238
2007-02-03 10:00 | 2 | 3 | 10 | 34 | 802 | 21.92 | 11069.4307 | 0 | 0 | 11069.4307 | Heating | 9767.1447 | 8.5 | 9767.1447 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1953.4289 | 39.07% | 1 | 78.14% | 0% | 0% | 0% | 46.2078 | 0 | 0 | 0 | 46.2078 | 9966.4742 | 0 | 1993.2948 | 19.93% | 1 | 39.87% | 0% | 0% | 4.9147 | 0 | 0 | 4.9147 | 51.1225
2007-02-03 11:00 | 2 | 3 | 11 | 34 | 803 | 21.92 | 9471.5727 | 0 | 0 | 9471.5727 | Heating | 8357.27 | 8.5 | 8357.27 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1671.454 | 33.43% | 1 | 66.86% | 0% | 0% | 0% | 32.2848 | 0 | 0 | 0 | 32.2848 | 8527.8266 | 0 | 1705.5653 | 17.06% | 1 | 34.11% | 0% | 0% | 3.4338 | 0 | 0 | 3.4338 | 35.7186
2007-02-03 12:00 | 2 | 3 | 12 | 34 | 804 | 23 | 8387.7408 | 0 | 0 | 8387.7408 | Heating | 7400.9478 | 8.5 | 7400.9478 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1480.1896 | 30% | 1 | 59.21% | 0% | 0% | 0% | 24.4124 | 0 | 0 | 0 | 24.4124 | 7551.9875 | 0 | 1510.3975 | 15.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.687
2007-02-03 13:00 | 2 | 3 | 13 | 34 | 805 | 26.96 | 7216.4697 | 0 | 0 | 7216.4697 | Heating | 6367.4732 | 8.5 | 6367.4732 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1273.4946 | 30% | 1 | 50.94% | 0% | 0% | 0% | 17.2733 | 0 | 0 | 0 | 17.2733 | 6497.4217 | 0 | 1299.4843 | 12.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.5478
2007-02-03 14:00 | 2 | 3 | 14 | 34 | 806 | 26.96 | 6774.62 | 0 | 0 | 6774.62 | Heating | 5977.6059 | 8.5 | 5977.6059 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1195.5212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6099.5978 | 0 | 1219.9196 | 12.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 15:00 | 2 | 3 | 15 | 34 | 807 | 28.04 | 6380.4926 | 0 | 0 | 6380.4926 | Heating | 5629.8464 | 8.5 | 5629.8464 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1125.9693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5744.7412 | 0 | 1148.9482 | 11.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 16:00 | 2 | 3 | 16 | 34 | 808 | 28.04 | 6112.4953 | 0 | 0 | 6112.4953 | Heating | 5393.3782 | 8.5 | 5393.3782 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1078.6756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5503.4471 | 0 | 1100.6894 | 11.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 17:00 | 2 | 3 | 17 | 34 | 809 | 28.04 | 6092.9273 | 0 | 0 | 6092.9273 | Heating | 5376.1123 | 8.5 | 5376.1123 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1075.2225 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5485.8289 | 0 | 1097.1658 | 10.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 18:00 | 2 | 3 | 18 | 34 | 810 | 24.98 | 8302.0198 | 0 | 0 | 8302.0198 | Heating | 7325.3116 | 8.5 | 7325.3116 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1465.0623 | 30% | 1 | 58.6% | 0% | 0% | 0% | 23.8424 | 0 | 0 | 0 | 23.8424 | 7474.8077 | 0 | 1494.9615 | 14.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.1169
2007-02-03 19:00 | 2 | 3 | 19 | 34 | 811 | 23 | 8784.9295 | 0 | 0 | 8784.9295 | Heating | 7751.4084 | 8.5 | 7751.4084 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1550.2817 | 31.01% | 1 | 62.01% | 0% | 0% | 0% | 27.1535 | 0 | 0 | 0 | 27.1535 | 7909.6004 | 0 | 1581.9201 | 15.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.428
2007-02-03 20:00 | 2 | 3 | 20 | 34 | 812 | 23 | 2128.2712 | 0 | 0 | 2128.2712 | Heating | 1877.8864 | 8.5 | 1877.8864 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 375.5773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1916.2106 | 0 | 383.2421 | 3.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 21:00 | 2 | 3 | 21 | 34 | 813 | 19.04 | 2030.8168 | 0 | 0 | 2030.8168 | Heating | 1791.8972 | 8.5 | 1791.8972 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.3794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1828.4665 | 0 | 365.6933 | 3.657% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 22:00 | 2 | 3 | 22 | 34 | 814 | 21.02 | 1965.2883 | 0 | 0 | 1965.2883 | Heating | 1734.078 | 8.5 | 1734.078 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.8156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1769.4673 | 0 | 353.8935 | 3.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-03 23:00 | 2 | 3 | 23 | 34 | 815 | 21.02 | 2010.9728 | 0 | 0 | 2010.9728 | Heating | 1774.3877 | 8.5 | 1774.3877 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 354.8775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1810.5997 | 0 | 362.1199 | 3.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 | 2 | 4 | 0 | 35 | 816 | 21.92 | 2057.7055 | 0 | 0 | 2057.7055 | Heating | 1815.6225 | 8.5 | 1815.6225 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.1245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1852.676 | 0 | 370.5352 | 3.705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 01:00 | 2 | 4 | 1 | 35 | 817 | 21.92 | 2133.6685 | 0 | 0 | 2133.6685 | Heating | 1882.6487 | 8.5 | 1882.6487 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.5297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1921.0701 | 0 | 384.214 | 3.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 02:00 | 2 | 4 | 2 | 35 | 818 | 21.92 | 2240.5811 | 0 | 0 | 2240.5811 | Heating | 1976.9833 | 8.5 | 1976.9833 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 395.3967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2017.3299 | 0 | 403.466 | 4.035% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 03:00 | 2 | 4 | 3 | 35 | 819 | 21.92 | 2236.2402 | 0 | 0 | 2236.2402 | Heating | 1973.1531 | 8.5 | 1973.1531 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 394.6306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2013.4215 | 0 | 402.6843 | 4.027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 04:00 | 2 | 4 | 4 | 35 | 820 | 21.02 | 2235.0706 | 0 | 0 | 2235.0706 | Heating | 1972.1211 | 8.5 | 1972.1211 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 394.4242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2012.3685 | 0 | 402.4737 | 4.025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 05:00 | 2 | 4 | 5 | 35 | 821 | 21.02 | 2292.0132 | 0 | 0 | 2292.0132 | Heating | 2022.3646 | 8.5 | 2022.3646 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.4729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2063.6373 | 0 | 412.7275 | 4.127% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 06:00 | 2 | 4 | 6 | 35 | 822 | 19.94 | 2275.8189 | 0 | 0 | 2275.8189 | Heating | 2008.0755 | 8.5 | 2008.0755 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 401.6151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2049.0566 | 0 | 409.8113 | 4.098% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 07:00 | 2 | 4 | 7 | 35 | 823 | 19.04 | 12667.4131 | 0 | 0 | 12667.4131 | Heating | 11177.1292 | 8.5 | 11177.1292 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2235.4258 | 44.71% | 1 | 89.42% | 0% | 0% | 0% | 63.01 | 0 | 0 | 0 | 63.01 | 11405.2339 | 0 | 2281.0468 | 22.81% | 1 | 45.62% | 0% | 0% | 6.7018 | 0 | 0 | 6.7018 | 69.7118
2007-02-04 08:00 | 2 | 4 | 8 | 35 | 824 | 19.04 | 9826.992 | 0 | 0 | 9826.992 | Heating | 8670.8753 | 8.5 | 8670.8753 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1734.1751 | 34.68% | 1 | 69.37% | 0% | 0% | 0% | 35.1394 | 0 | 0 | 0 | 35.1394 | 8847.8319 | 0 | 1769.5664 | 17.7% | 1 | 35.39% | 0% | 0% | 3.7375 | 0 | 0 | 3.7375 | 38.8769
2007-02-04 09:00 | 2 | 4 | 9 | 35 | 825 | 21.02 | 8217.5937 | 0 | 0 | 8217.5937 | Heating | 7250.8179 | 8.5 | 7250.8179 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1450.1636 | 30% | 1 | 58.01% | 0% | 0% | 0% | 23.2884 | 0 | 0 | 0 | 23.2884 | 7398.7938 | 0 | 1479.7588 | 14.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.563
2007-02-04 10:00 | 2 | 4 | 10 | 35 | 826 | 21.2 | 6849.9038 | 0 | 0 | 6849.9038 | Heating | 6044.0328 | 8.5 | 6044.0328 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1208.8066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6167.3804 | 0 | 1233.4761 | 12.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 11:00 | 2 | 4 | 11 | 35 | 827 | 23 | 6036.3277 | 0 | 0 | 6036.3277 | Heating | 5326.1715 | 8.5 | 5326.1715 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1065.2343 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5434.8689 | 0 | 1086.9738 | 10.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 12:00 | 2 | 4 | 12 | 35 | 828 | 24.98 | 5394.1328 | 0 | 0 | 5394.1328 | Heating | 4759.5289 | 8.5 | 4759.5289 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 951.9058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4856.6622 | 0 | 971.3324 | 9.713% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 13:00 | 2 | 4 | 13 | 35 | 829 | 23 | 4991.632 | 0 | 0 | 4991.632 | Heating | 4404.3812 | 8.5 | 4404.3812 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 880.8762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4494.2665 | 0 | 898.8533 | 8.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 14:00 | 2 | 4 | 14 | 35 | 830 | 21.92 | 4725.0088 | 0 | 0 | 4725.0088 | Heating | 4169.1254 | 8.5 | 4169.1254 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 833.8251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4254.2096 | 0 | 850.8419 | 8.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 15:00 | 2 | 4 | 15 | 35 | 831 | 24.98 | 4553.1608 | 0 | 0 | 4553.1608 | Heating | 4017.4948 | 8.5 | 4017.4948 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 803.499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4099.4845 | 0 | 819.8969 | 8.199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 16:00 | 2 | 4 | 16 | 35 | 832 | 24.08 | 4453.7311 | 0 | 0 | 4453.7311 | Heating | 3929.7627 | 8.5 | 3929.7627 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 785.9525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4009.9619 | 0 | 801.9924 | 8.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 17:00 | 2 | 4 | 17 | 35 | 833 | 24.08 | 5077.6401 | 0 | 0 | 5077.6401 | Heating | 4480.2707 | 8.5 | 4480.2707 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 896.0541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4571.7048 | 0 | 914.341 | 9.143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 18:00 | 2 | 4 | 18 | 35 | 834 | 19.94 | 5891.5552 | 0 | 0 | 5891.5552 | Heating | 5198.4311 | 8.5 | 5198.4311 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1039.6862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5304.5215 | 0 | 1060.9043 | 10.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 19:00 | 2 | 4 | 19 | 35 | 835 | 17.96 | 6116.9172 | 0 | 0 | 6116.9172 | Heating | 5397.2799 | 8.5 | 5397.2799 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1079.456 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5507.4284 | 0 | 1101.4857 | 11.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 20:00 | 2 | 4 | 20 | 35 | 836 | 17.96 | 6346.9333 | 0 | 0 | 6346.9333 | Heating | 5600.2353 | 8.5 | 5600.2353 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1120.0471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5714.5258 | 0 | 1142.9052 | 11.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 21:00 | 2 | 4 | 21 | 35 | 837 | 15.08 | 6778.6411 | 0 | 0 | 6778.6411 | Heating | 5981.1539 | 8.5 | 5981.1539 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1196.2308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6103.2183 | 0 | 1220.6437 | 12.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 22:00 | 2 | 4 | 22 | 35 | 838 | 14 | 2156.5158 | 0 | 0 | 2156.5158 | Heating | 1902.808 | 8.5 | 1902.808 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.5616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1941.6408 | 0 | 388.3282 | 3.883% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-04 23:00 | 2 | 4 | 23 | 35 | 839 | 14 | 2329.2044 | 0 | 0 | 2329.2044 | Heating | 2055.1804 | 8.5 | 2055.1804 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.0361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2097.1228 | 0 | 419.4246 | 4.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 | 2 | 5 | 0 | 36 | 840 | 17.06 | 2685.2428 | 0 | 0 | 2685.2428 | Heating | 2369.3318 | 8.5 | 2369.3318 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 473.8664 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2417.6856 | 0 | 483.5371 | 4.835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 01:00 | 2 | 5 | 1 | 36 | 841 | 17.96 | 2934.7496 | 0 | 0 | 2934.7496 | Heating | 2589.4849 | 8.5 | 2589.4849 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2642.3315 | 0 | 528.4663 | 5.285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 02:00 | 2 | 5 | 2 | 36 | 842 | 17.96 | 3138.9027 | 0 | 0 | 3138.9027 | Heating | 2769.62 | 8.5 | 2769.62 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 553.924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2826.1429 | 0 | 565.2286 | 5.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 03:00 | 2 | 5 | 3 | 36 | 843 | 17.96 | 3281.8554 | 0 | 0 | 3281.8554 | Heating | 2895.7548 | 8.5 | 2895.7548 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 579.151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2954.8518 | 0 | 590.9704 | 5.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 04:00 | 2 | 5 | 4 | 36 | 844 | 17.96 | 3354.9169 | 0 | 0 | 3354.9169 | Heating | 2960.2208 | 8.5 | 2960.2208 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 592.0442 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3020.6334 | 0 | 604.1267 | 6.041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 05:00 | 2 | 5 | 5 | 36 | 845 | 17.96 | 3501.746 | 0 | 0 | 3501.746 | Heating | 3089.7759 | 8.5 | 3089.7759 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 617.9552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3152.8326 | 0 | 630.5665 | 6.306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 06:00 | 2 | 5 | 6 | 36 | 846 | 17.96 | 3617.4648 | 0 | 0 | 3617.4648 | Heating | 3191.8807 | 8.5 | 3191.8807 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 638.3761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3257.0212 | 0 | 651.4042 | 6.514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 07:00 | 2 | 5 | 7 | 36 | 847 | 17.96 | 15790.4714 | 0 | 0 | 15790.4714 | Heating | 13932.7688 | 8.5 | 13932.7688 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2786.5538 | 55.73% | 2 | 55.73% | 55.73% | 0% | 0% | 21.2406 | 21.2406 | 0 | 0 | 42.4812 | 14217.1111 | 0 | 2843.4222 | 28.43% | 1 | 56.87% | 0% | 0% | 11.1254 | 0 | 0 | 11.1254 | 53.6067
2007-02-05 08:00 | 2 | 5 | 8 | 36 | 848 | 17.96 | 13698.6437 | 0 | 0 | 13698.6437 | Heating | 12087.0386 | 8.5 | 12087.0386 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2417.4077 | 48.35% | 1 | 96.7% | 0% | 0% | 0% | 75.4372 | 0 | 0 | 0 | 75.4372 | 12333.7128 | 0 | 2466.7426 | 24.67% | 1 | 49.33% | 0% | 0% | 8.0236 | 0 | 0 | 8.0236 | 83.4608
2007-02-05 09:00 | 2 | 5 | 9 | 36 | 849 | 19.04 | 11633.6661 | 0 | 0 | 11633.6661 | Heating | 10264.9995 | 8.5 | 10264.9995 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2052.9999 | 41.06% | 1 | 82.12% | 0% | 0% | 0% | 51.8055 | 0 | 0 | 0 | 51.8055 | 10474.4893 | 0 | 2094.8979 | 20.95% | 1 | 41.9% | 0% | 0% | 5.5101 | 0 | 0 | 5.5101 | 57.3155
2007-02-05 10:00 | 2 | 5 | 10 | 36 | 850 | 21.92 | 9788.4115 | 0 | 0 | 9788.4115 | Heating | 8636.8337 | 8.5 | 8636.8337 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1727.3667 | 34.55% | 1 | 69.09% | 0% | 0% | 0% | 34.8229 | 0 | 0 | 0 | 34.8229 | 8813.0956 | 0 | 1762.6191 | 17.63% | 1 | 35.25% | 0% | 0% | 3.7038 | 0 | 0 | 3.7038 | 38.5267
2007-02-05 11:00 | 2 | 5 | 11 | 36 | 851 | 21.92 | 8577.7923 | 0 | 0 | 8577.7923 | Heating | 7568.6402 | 8.5 | 7568.6402 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1513.728 | 30.27% | 1 | 60.55% | 0% | 0% | 0% | 25.7034 | 0 | 0 | 0 | 25.7034 | 7723.1023 | 0 | 1544.6205 | 15.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.978
2007-02-05 12:00 | 2 | 5 | 12 | 36 | 852 | 23 | 7587.2712 | 0 | 0 | 7587.2712 | Heating | 6694.6511 | 8.5 | 6694.6511 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1338.9302 | 30% | 1 | 53.56% | 0% | 0% | 0% | 19.3831 | 0 | 0 | 0 | 19.3831 | 6831.2766 | 0 | 1366.2553 | 13.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.6577
2007-02-05 13:00 | 2 | 5 | 13 | 36 | 853 | 26.06 | 7101.5728 | 0 | 0 | 7101.5728 | Heating | 6266.0937 | 8.5 | 6266.0937 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1253.2187 | 30% | 1 | 50.13% | 0% | 0% | 0% | 16.6473 | 0 | 0 | 0 | 16.6473 | 6393.9732 | 0 | 1278.7946 | 12.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9218
2007-02-05 14:00 | 2 | 5 | 14 | 36 | 854 | 26.06 | 6776.7851 | 0 | 0 | 6776.7851 | Heating | 5979.5163 | 8.5 | 5979.5163 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1195.9033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6101.5473 | 0 | 1220.3095 | 12.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 15:00 | 2 | 5 | 15 | 36 | 855 | 28.04 | 6569.8711 | 0 | 0 | 6569.8711 | Heating | 5796.9451 | 8.5 | 5796.9451 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1159.389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5915.2501 | 0 | 1183.05 | 11.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 16:00 | 2 | 5 | 16 | 36 | 856 | 26.96 | 6484.323 | 0 | 0 | 6484.323 | Heating | 5721.4615 | 8.5 | 5721.4615 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1144.2923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5838.226 | 0 | 1167.6452 | 11.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 17:00 | 2 | 5 | 17 | 36 | 857 | 26.96 | 6684.8524 | 0 | 0 | 6684.8524 | Heating | 5898.3991 | 8.5 | 5898.3991 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1179.6798 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6018.7746 | 0 | 1203.7549 | 12.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 18:00 | 2 | 5 | 18 | 36 | 858 | 26.06 | 7565.7547 | 0 | 0 | 7565.7547 | Heating | 6675.666 | 8.5 | 6675.666 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1335.1332 | 30% | 1 | 53.41% | 0% | 0% | 0% | 19.257 | 0 | 0 | 0 | 19.257 | 6811.904 | 0 | 1362.3808 | 13.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.5315
2007-02-05 19:00 | 2 | 5 | 19 | 36 | 859 | 24.98 | 8184.0099 | 0 | 0 | 8184.0099 | Heating | 7221.1852 | 8.5 | 7221.1852 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1444.237 | 30% | 1 | 57.77% | 0% | 0% | 0% | 23.0701 | 0 | 0 | 0 | 23.0701 | 7368.5563 | 0 | 1473.7113 | 14.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.3446
2007-02-05 20:00 | 2 | 5 | 20 | 36 | 860 | 24.98 | 9284.3241 | 0 | 0 | 9284.3241 | Heating | 8192.0507 | 8.5 | 8192.0507 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1638.4101 | 32.77% | 1 | 65.54% | 0% | 0% | 0% | 30.8356 | 0 | 0 | 0 | 30.8356 | 8359.2354 | 0 | 1671.8471 | 16.72% | 1 | 33.44% | 0% | 0% | 3.2797 | 0 | 0 | 3.2797 | 34.1153
2007-02-05 21:00 | 2 | 5 | 21 | 36 | 861 | 24.98 | 9770.9356 | 0 | 0 | 9770.9356 | Heating | 8621.4137 | 8.5 | 8621.4137 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1724.2827 | 34.49% | 1 | 68.97% | 0% | 0% | 0% | 34.6801 | 0 | 0 | 0 | 34.6801 | 8797.3609 | 0 | 1759.4722 | 17.59% | 1 | 35.19% | 0% | 0% | 3.6886 | 0 | 0 | 3.6886 | 38.3687
2007-02-05 22:00 | 2 | 5 | 22 | 36 | 862 | 26.06 | 2923.7318 | 0 | 0 | 2923.7318 | Heating | 2579.7634 | 8.5 | 2579.7634 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 515.9527 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2632.4116 | 0 | 526.4823 | 5.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-05 23:00 | 2 | 5 | 23 | 36 | 863 | 26.06 | 3054.1304 | 0 | 0 | 3054.1304 | Heating | 2694.8209 | 8.5 | 2694.8209 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 538.9642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2749.8173 | 0 | 549.9635 | 5.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 | 2 | 6 | 0 | 37 | 864 | 26.96 | 3532.1643 | 0 | 0 | 3532.1643 | Heating | 3116.6155 | 8.5 | 3116.6155 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 623.3231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3180.2199 | 0 | 636.044 | 6.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 01:00 | 2 | 6 | 1 | 37 | 865 | 26.96 | 3831.7737 | 0 | 0 | 3831.7737 | Heating | 3380.9768 | 8.5 | 3380.9768 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 676.1954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3449.9764 | 0 | 689.9953 | 6.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 02:00 | 2 | 6 | 2 | 37 | 866 | 26.96 | 3713.7947 | 0 | 0 | 3713.7947 | Heating | 3276.8777 | 8.5 | 3276.8777 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 655.3755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3343.7527 | 0 | 668.7505 | 6.688% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 03:00 | 2 | 6 | 3 | 37 | 867 | 26.06 | 3834.747 | 0 | 0 | 3834.747 | Heating | 3383.6003 | 8.5 | 3383.6003 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 676.7201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3452.6534 | 0 | 690.5307 | 6.905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 04:00 | 2 | 6 | 4 | 37 | 868 | 24.98 | 3761.0241 | 0 | 0 | 3761.0241 | Heating | 3318.5507 | 8.5 | 3318.5507 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 663.7101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3386.2762 | 0 | 677.2552 | 6.773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 05:00 | 2 | 6 | 5 | 37 | 869 | 24.98 | 3539.8389 | 0 | 0 | 3539.8389 | Heating | 3123.3873 | 8.5 | 3123.3873 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 624.6775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3187.1299 | 0 | 637.426 | 6.374% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 06:00 | 2 | 6 | 6 | 37 | 870 | 26.06 | 3506.5083 | 0 | 0 | 3506.5083 | Heating | 3093.9779 | 8.5 | 3093.9779 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 618.7956 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3157.1203 | 0 | 631.4241 | 6.314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 07:00 | 2 | 6 | 7 | 37 | 871 | 26.06 | 16175.8339 | 0 | 0 | 16175.8339 | Heating | 14272.7946 | 8.5 | 14272.7946 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2854.5589 | 57.09% | 2 | 57.09% | 57.09% | 0% | 0% | 22.4518 | 22.4518 | 0 | 0 | 44.9037 | 14564.0761 | 0 | 2912.8152 | 29.13% | 1 | 58.26% | 0% | 0% | 11.7599 | 0 | 0 | 11.7599 | 56.6635
2007-02-06 08:00 | 2 | 6 | 8 | 37 | 872 | 26.06 | 13800.9973 | 0 | 0 | 13800.9973 | Heating | 12177.3505 | 8.5 | 12177.3505 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2435.4701 | 48.71% | 1 | 97.42% | 0% | 0% | 0% | 76.7399 | 0 | 0 | 0 | 76.7399 | 12425.8679 | 0 | 2485.1736 | 24.85% | 1 | 49.7% | 0% | 0% | 8.1621 | 0 | 0 | 8.1621 | 84.9021
2007-02-06 09:00 | 2 | 6 | 9 | 37 | 873 | 28.04 | 11440.0215 | 0 | 0 | 11440.0215 | Heating | 10094.1366 | 8.5 | 10094.1366 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2018.8273 | 40.38% | 1 | 80.75% | 0% | 0% | 0% | 49.8436 | 0 | 0 | 0 | 49.8436 | 10300.1394 | 0 | 2060.0279 | 20.6% | 1 | 41.2% | 0% | 0% | 5.3014 | 0 | 0 | 5.3014 | 55.145
2007-02-06 10:00 | 2 | 6 | 10 | 37 | 874 | 30.02 | 9518.3842 | 0 | 0 | 9518.3842 | Heating | 8398.5743 | 8.5 | 8398.5743 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1679.7149 | 33.59% | 1 | 67.19% | 0% | 0% | 0% | 32.653 | 0 | 0 | 0 | 32.653 | 8569.9737 | 0 | 1713.9947 | 17.14% | 1 | 34.28% | 0% | 0% | 3.473 | 0 | 0 | 3.473 | 36.126
2007-02-06 11:00 | 2 | 6 | 11 | 37 | 875 | 30.02 | 8411.2487 | 0 | 0 | 8411.2487 | Heating | 7421.69 | 8.5 | 7421.69 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1484.338 | 30% | 1 | 59.37% | 0% | 0% | 0% | 24.5701 | 0 | 0 | 0 | 24.5701 | 7573.1531 | 0 | 1514.6306 | 15.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.8446
2007-02-06 12:00 | 2 | 6 | 12 | 37 | 876 | 30.02 | 7494.9777 | 0 | 0 | 7494.9777 | Heating | 6613.2156 | 8.5 | 6613.2156 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1322.6431 | 30% | 1 | 52.91% | 0% | 0% | 0% | 18.8451 | 0 | 0 | 0 | 18.8451 | 6748.1792 | 0 | 1349.6358 | 13.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.1197
2007-02-06 13:00 | 2 | 6 | 13 | 37 | 877 | 33.08 | 6852.1701 | 0 | 0 | 6852.1701 | Heating | 6046.0325 | 8.5 | 6046.0325 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1209.2065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6169.4209 | 0 | 1233.8842 | 12.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 14:00 | 2 | 6 | 14 | 37 | 878 | 33.08 | 6379.614 | 0 | 0 | 6379.614 | Heating | 5629.0712 | 8.5 | 5629.0712 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1125.8142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5743.9502 | 0 | 1148.79 | 11.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 15:00 | 2 | 6 | 15 | 37 | 879 | 32 | 6245.3069 | 0 | 0 | 6245.3069 | Heating | 5510.5649 | 8.5 | 5510.5649 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1102.113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5623.0254 | 0 | 1124.6051 | 11.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 16:00 | 2 | 6 | 16 | 37 | 880 | 30.02 | 6348.9269 | 0 | 0 | 6348.9269 | Heating | 5601.9943 | 8.5 | 5601.9943 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1120.3989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5716.3207 | 0 | 1143.2641 | 11.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 17:00 | 2 | 6 | 17 | 37 | 881 | 30.02 | 6652.4896 | 0 | 0 | 6652.4896 | Heating | 5869.8438 | 8.5 | 5869.8438 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1173.9688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5989.6365 | 0 | 1197.9273 | 11.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 18:00 | 2 | 6 | 18 | 37 | 882 | 24.98 | 7076.5474 | 0 | 0 | 7076.5474 | Heating | 6244.0124 | 8.5 | 6244.0124 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1248.8025 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6371.4412 | 0 | 1274.2882 | 12.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 19:00 | 2 | 6 | 19 | 37 | 883 | 23 | 7284.3901 | 0 | 0 | 7284.3901 | Heating | 6427.403 | 8.5 | 6427.403 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1285.4806 | 30% | 1 | 51.42% | 0% | 0% | 0% | 17.6495 | 0 | 0 | 0 | 17.6495 | 6558.5745 | 0 | 1311.7149 | 13.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.924
2007-02-06 20:00 | 2 | 6 | 20 | 37 | 884 | 23 | 7795.0123 | 0 | 0 | 7795.0123 | Heating | 6877.952 | 8.5 | 6877.952 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1375.5904 | 30% | 1 | 55.02% | 0% | 0% | 0% | 20.6256 | 0 | 0 | 0 | 20.6256 | 7018.3184 | 0 | 1403.6637 | 14.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.9001
2007-02-06 21:00 | 2 | 6 | 21 | 37 | 885 | 21.02 | 8675.5644 | 0 | 0 | 8675.5644 | Heating | 7654.9098 | 8.5 | 7654.9098 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1530.982 | 30.62% | 1 | 61.24% | 0% | 0% | 0% | 26.3823 | 0 | 0 | 0 | 26.3823 | 7811.1324 | 0 | 1562.2265 | 15.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.6568
2007-02-06 22:00 | 2 | 6 | 22 | 37 | 886 | 19.94 | 2765.9058 | 0 | 0 | 2765.9058 | Heating | 2440.5051 | 8.5 | 2440.5051 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 488.101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2490.3113 | 0 | 498.0623 | 4.981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-06 23:00 | 2 | 6 | 23 | 37 | 887 | 19.94 | 3037.0975 | 0 | 0 | 3037.0975 | Heating | 2679.7919 | 8.5 | 2679.7919 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 535.9584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2734.4815 | 0 | 546.8963 | 5.469% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 | 2 | 7 | 0 | 38 | 888 | 17.96 | 3308.35 | 0 | 0 | 3308.35 | Heating | 2919.1323 | 8.5 | 2919.1323 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 583.8265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2978.7064 | 0 | 595.7413 | 5.957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 01:00 | 2 | 7 | 1 | 38 | 889 | 15.08 | 3485.9212 | 0 | 0 | 3485.9212 | Heating | 3075.8128 | 8.5 | 3075.8128 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 615.1626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3138.5845 | 0 | 627.7169 | 6.277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 02:00 | 2 | 7 | 2 | 38 | 890 | 15.08 | 3743.4275 | 0 | 0 | 3743.4275 | Heating | 3303.0243 | 8.5 | 3303.0243 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 660.6049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3370.4329 | 0 | 674.0866 | 6.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 03:00 | 2 | 7 | 3 | 38 | 891 | 15.08 | 3908.3508 | 0 | 0 | 3908.3508 | Heating | 3448.5448 | 8.5 | 3448.5448 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 689.709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3518.9233 | 0 | 703.7847 | 7.038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 04:00 | 2 | 7 | 4 | 38 | 892 | 14 | 3979.9279 | 0 | 0 | 3979.9279 | Heating | 3511.7011 | 8.5 | 3511.7011 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 702.3402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3583.3684 | 0 | 716.6737 | 7.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 05:00 | 2 | 7 | 5 | 38 | 893 | 14 | 4312.7143 | 0 | 0 | 4312.7143 | Heating | 3805.3361 | 8.5 | 3805.3361 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 761.0672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3882.996 | 0 | 776.5992 | 7.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 06:00 | 2 | 7 | 6 | 38 | 894 | 14 | 4376.1303 | 0 | 0 | 4376.1303 | Heating | 3861.2914 | 8.5 | 3861.2914 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 772.2583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3940.0933 | 0 | 788.0187 | 7.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 07:00 | 2 | 7 | 7 | 38 | 895 | 12.02 | 17882.5674 | 0 | 0 | 17882.5674 | Heating | 15778.7359 | 8.5 | 15778.7359 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3155.7472 | 63.11% | 2 | 63.11% | 63.11% | 0% | 0% | 28.2779 | 28.2779 | 0 | 0 | 56.5558 | 16100.7509 | 0 | 3220.1502 | 32.2% | 1 | 64.4% | 0% | 0% | 14.8114 | 0 | 0 | 14.8114 | 71.3672
2007-02-07 08:00 | 2 | 7 | 8 | 38 | 896 | 12.02 | 15335.1095 | 0 | 0 | 15335.1095 | Heating | 13530.9789 | 8.5 | 13530.9789 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2706.1958 | 54.12% | 2 | 54.12% | 54.12% | 0% | 0% | 19.8581 | 19.8581 | 0 | 0 | 39.7162 | 13807.1214 | 0 | 2761.4243 | 27.61% | 1 | 55.23% | 0% | 0% | 10.4013 | 0 | 0 | 10.4013 | 50.1176
2007-02-07 09:00 | 2 | 7 | 9 | 38 | 897 | 15.98 | 12784.6773 | 0 | 0 | 12784.6773 | Heating | 11280.5976 | 8.5 | 11280.5976 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2256.1195 | 45.12% | 1 | 90.24% | 0% | 0% | 0% | 64.3597 | 0 | 0 | 0 | 64.3597 | 11510.8139 | 0 | 2302.1628 | 23.02% | 1 | 46.04% | 0% | 0% | 6.8453 | 0 | 0 | 6.8453 | 71.205
2007-02-07 10:00 | 2 | 7 | 10 | 38 | 898 | 17.96 | 10495.2559 | 0 | 0 | 10495.2559 | Heating | 9260.5199 | 8.5 | 9260.5199 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1852.104 | 37.04% | 1 | 74.08% | 0% | 0% | 0% | 40.88 | 0 | 0 | 0 | 40.88 | 9449.5101 | 0 | 1889.902 | 18.9% | 1 | 37.8% | 0% | 0% | 4.348 | 0 | 0 | 4.348 | 45.2281
2007-02-07 11:00 | 2 | 7 | 11 | 38 | 899 | 17.96 | 9016.1043 | 0 | 0 | 9016.1043 | Heating | 7955.3861 | 8.5 | 7955.3861 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1591.0772 | 31.82% | 1 | 63.64% | 0% | 0% | 0% | 28.8251 | 0 | 0 | 0 | 28.8251 | 8117.7409 | 0 | 1623.5482 | 16.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.0997
2007-02-07 12:00 | 2 | 7 | 12 | 38 | 900 | 21.02 | 7963.1059 | 0 | 0 | 7963.1059 | Heating | 7026.2699 | 8.5 | 7026.2699 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1405.254 | 30% | 1 | 56.21% | 0% | 0% | 0% | 21.6629 | 0 | 0 | 0 | 21.6629 | 7169.6632 | 0 | 1433.9326 | 14.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.9375
2007-02-07 13:00 | 2 | 7 | 13 | 38 | 901 | 23 | 7379.7005 | 0 | 0 | 7379.7005 | Heating | 6511.5004 | 8.5 | 6511.5004 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1302.3001 | 30% | 1 | 52.09% | 0% | 0% | 0% | 18.1851 | 0 | 0 | 0 | 18.1851 | 6644.3882 | 0 | 1328.8776 | 13.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.4597
2007-02-07 14:00 | 2 | 7 | 14 | 38 | 902 | 23 | 7065.4368 | 0 | 0 | 7065.4368 | Heating | 6234.209 | 8.5 | 6234.209 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1246.8418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6361.4377 | 0 | 1272.2875 | 12.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 15:00 | 2 | 7 | 15 | 38 | 903 | 24.08 | 6637.88 | 0 | 0 | 6637.88 | Heating | 5856.9529 | 8.5 | 5856.9529 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1171.3906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5976.4826 | 0 | 1195.2965 | 11.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 16:00 | 2 | 7 | 16 | 38 | 904 | 24.08 | 6315.1512 | 0 | 0 | 6315.1512 | Heating | 5572.1922 | 8.5 | 5572.1922 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1114.4384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5685.9104 | 0 | 1137.1821 | 11.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 17:00 | 2 | 7 | 17 | 38 | 905 | 24.08 | 6396.5807 | 0 | 0 | 6396.5807 | Heating | 5644.0418 | 8.5 | 5644.0418 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1128.8084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5759.2263 | 0 | 1151.8453 | 11.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 18:00 | 2 | 7 | 18 | 38 | 906 | 23 | 6623.9004 | 0 | 0 | 6623.9004 | Heating | 5844.618 | 8.5 | 5844.618 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1168.9236 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5963.8959 | 0 | 1192.7792 | 11.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 19:00 | 2 | 7 | 19 | 38 | 907 | 21.92 | 6683.8342 | 0 | 0 | 6683.8342 | Heating | 5897.5008 | 8.5 | 5897.5008 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1179.5002 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6017.8579 | 0 | 1203.5716 | 12.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 20:00 | 2 | 7 | 20 | 38 | 908 | 21.92 | 6766.4075 | 0 | 0 | 6766.4075 | Heating | 5970.3596 | 8.5 | 5970.3596 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1194.0719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6092.2037 | 0 | 1218.4407 | 12.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 21:00 | 2 | 7 | 21 | 38 | 909 | 19.94 | 6984.0398 | 0 | 0 | 6984.0398 | Heating | 6162.388 | 8.5 | 6162.388 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1232.4776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6288.1511 | 0 | 1257.6302 | 12.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 22:00 | 2 | 7 | 22 | 38 | 910 | 19.04 | 2123.8993 | 0 | 0 | 2123.8993 | Heating | 1874.0288 | 8.5 | 1874.0288 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.8058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1912.2743 | 0 | 382.4549 | 3.825% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-07 23:00 | 2 | 7 | 23 | 38 | 911 | 19.04 | 2226.9403 | 0 | 0 | 2226.9403 | Heating | 1964.9473 | 8.5 | 1964.9473 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 392.9895 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2005.0483 | 0 | 401.0097 | 4.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 | 2 | 8 | 0 | 39 | 912 | 19.04 | 2387.1617 | 0 | 0 | 2387.1617 | Heating | 2106.3192 | 8.5 | 2106.3192 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.2638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2149.3053 | 0 | 429.8611 | 4.299% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 01:00 | 2 | 8 | 1 | 39 | 913 | 19.04 | 2468.2964 | 0 | 0 | 2468.2964 | Heating | 2177.9086 | 8.5 | 2177.9086 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 435.5817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2222.3557 | 0 | 444.4711 | 4.445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 02:00 | 2 | 8 | 2 | 39 | 914 | 19.04 | 2475.6565 | 0 | 0 | 2475.6565 | Heating | 2184.4028 | 8.5 | 2184.4028 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 436.8806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2228.9824 | 0 | 445.7965 | 4.458% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 03:00 | 2 | 8 | 3 | 39 | 915 | 19.04 | 2510.1311 | 0 | 0 | 2510.1311 | Heating | 2214.8216 | 8.5 | 2214.8216 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 442.9643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2260.022 | 0 | 452.0044 | 4.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 04:00 | 2 | 8 | 4 | 39 | 916 | 19.04 | 2557.3122 | 0 | 0 | 2557.3122 | Heating | 2256.452 | 8.5 | 2256.452 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 451.2904 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2302.502 | 0 | 460.5004 | 4.605% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 05:00 | 2 | 8 | 5 | 39 | 917 | 19.04 | 2544.0992 | 0 | 0 | 2544.0992 | Heating | 2244.7934 | 8.5 | 2244.7934 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 448.9587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2290.6056 | 0 | 458.1211 | 4.581% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 06:00 | 2 | 8 | 6 | 39 | 918 | 21.02 | 2565.6505 | 0 | 0 | 2565.6505 | Heating | 2263.8093 | 8.5 | 2263.8093 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 452.7619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2310.0095 | 0 | 462.0019 | 4.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 07:00 | 2 | 8 | 7 | 39 | 919 | 21.02 | 13615.7263 | 0 | 0 | 13615.7263 | Heating | 12013.8761 | 8.5 | 12013.8761 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2402.7752 | 48.06% | 1 | 96.11% | 0% | 0% | 0% | 74.3911 | 0 | 0 | 0 | 74.3911 | 12259.0573 | 0 | 2451.8115 | 24.52% | 1 | 49.04% | 0% | 0% | 7.9123 | 0 | 0 | 7.9123 | 82.3034
2007-02-08 08:00 | 2 | 8 | 8 | 39 | 920 | 21.02 | 10767.7917 | 0 | 0 | 10767.7917 | Heating | 9500.9927 | 8.5 | 9500.9927 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1900.1985 | 38% | 1 | 76.01% | 0% | 0% | 0% | 43.3629 | 0 | 0 | 0 | 43.3629 | 9694.8905 | 0 | 1938.9781 | 19.39% | 1 | 38.78% | 0% | 0% | 4.6121 | 0 | 0 | 4.6121 | 47.975
2007-02-08 09:00 | 2 | 8 | 9 | 39 | 921 | 19.4 | 8756.5624 | 0 | 0 | 8756.5624 | Heating | 7726.3786 | 8.5 | 7726.3786 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1545.2757 | 30.91% | 1 | 61.81% | 0% | 0% | 0% | 26.9522 | 0 | 0 | 0 | 26.9522 | 7884.0598 | 0 | 1576.812 | 15.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.2268
2007-02-08 10:00 | 2 | 8 | 10 | 39 | 922 | 19.4 | 6911.4061 | 0 | 0 | 6911.4061 | Heating | 6098.2995 | 8.5 | 6098.2995 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1219.6599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6222.7546 | 0 | 1244.5509 | 12.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 11:00 | 2 | 8 | 11 | 39 | 923 | 21.02 | 6135.0144 | 0 | 0 | 6135.0144 | Heating | 5413.248 | 8.5 | 5413.248 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1082.6496 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5523.7224 | 0 | 1104.7445 | 11.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 12:00 | 2 | 8 | 12 | 39 | 924 | 21.2 | 5553.0072 | 0 | 0 | 5553.0072 | Heating | 4899.7122 | 8.5 | 4899.7122 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 979.9424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4999.7063 | 0 | 999.9413 | 9.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 13:00 | 2 | 8 | 13 | 39 | 925 | 24.08 | 5201.4422 | 0 | 0 | 5201.4422 | Heating | 4589.5078 | 8.5 | 4589.5078 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 917.9016 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4683.1712 | 0 | 936.6342 | 9.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 14:00 | 2 | 8 | 14 | 39 | 926 | 24.08 | 5064.9625 | 0 | 0 | 5064.9625 | Heating | 4469.0846 | 8.5 | 4469.0846 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 893.8169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4560.2904 | 0 | 912.0581 | 9.121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 15:00 | 2 | 8 | 15 | 39 | 927 | 26.96 | 5069.9492 | 0 | 0 | 5069.9492 | Heating | 4473.4846 | 8.5 | 4473.4846 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 894.6969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4564.7802 | 0 | 912.956 | 9.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 16:00 | 2 | 8 | 16 | 39 | 928 | 28.04 | 5174.1875 | 0 | 0 | 5174.1875 | Heating | 4565.4596 | 8.5 | 4565.4596 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 913.0919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4658.6322 | 0 | 931.7264 | 9.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 17:00 | 2 | 8 | 17 | 39 | 929 | 28.04 | 5447.1774 | 0 | 0 | 5447.1774 | Heating | 4806.333 | 8.5 | 4806.333 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 961.2666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4904.4214 | 0 | 980.8843 | 9.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 18:00 | 2 | 8 | 18 | 39 | 930 | 28.4 | 5847.5159 | 0 | 0 | 5847.5159 | Heating | 5159.5729 | 8.5 | 5159.5729 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1031.9146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5264.8703 | 0 | 1052.9741 | 10.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 19:00 | 2 | 8 | 19 | 39 | 931 | 26.96 | 6028.7403 | 0 | 0 | 6028.7403 | Heating | 5319.4767 | 8.5 | 5319.4767 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1063.8953 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5428.0375 | 0 | 1085.6075 | 10.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 20:00 | 2 | 8 | 20 | 39 | 932 | 26.96 | 6339.0979 | 0 | 0 | 6339.0979 | Heating | 5593.3217 | 8.5 | 5593.3217 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1118.6643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5707.4711 | 0 | 1141.4942 | 11.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 21:00 | 2 | 8 | 21 | 39 | 933 | 24.8 | 6931.4033 | 0 | 0 | 6931.4033 | Heating | 6115.9441 | 8.5 | 6115.9441 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1223.1888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6240.7593 | 0 | 1248.1519 | 12.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 22:00 | 2 | 8 | 22 | 39 | 934 | 24.8 | 2048.4018 | 0 | 0 | 2048.4018 | Heating | 1807.4133 | 8.5 | 1807.4133 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.4827 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1844.2993 | 0 | 368.8599 | 3.689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-08 23:00 | 2 | 8 | 23 | 39 | 935 | 24.08 | 1943.7464 | 0 | 0 | 1943.7464 | Heating | 1715.0704 | 8.5 | 1715.0704 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.0141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1750.0718 | 0 | 350.0144 | 3.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 | 2 | 9 | 0 | 40 | 936 | 23 | 2293.065 | 0 | 0 | 2293.065 | Heating | 2023.2926 | 8.5 | 2023.2926 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.6585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2064.5843 | 0 | 412.9169 | 4.129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 01:00 | 2 | 9 | 1 | 40 | 937 | 23 | 2557.7058 | 0 | 0 | 2557.7058 | Heating | 2256.7992 | 8.5 | 2256.7992 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 451.3598 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2302.8563 | 0 | 460.5713 | 4.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 02:00 | 2 | 9 | 2 | 40 | 938 | 23 | 2709.615 | 0 | 0 | 2709.615 | Heating | 2390.8368 | 8.5 | 2390.8368 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 478.1674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2439.6294 | 0 | 487.9259 | 4.879% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 03:00 | 2 | 9 | 3 | 40 | 939 | 23 | 2883.5731 | 0 | 0 | 2883.5731 | Heating | 2544.3292 | 8.5 | 2544.3292 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 508.8658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2596.2543 | 0 | 519.2509 | 5.193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 04:00 | 2 | 9 | 4 | 40 | 940 | 21.2 | 3243.1617 | 0 | 0 | 3243.1617 | Heating | 2861.6132 | 8.5 | 2861.6132 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 572.3226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2920.0135 | 0 | 584.0027 | 5.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 05:00 | 2 | 9 | 5 | 40 | 941 | 21.92 | 3611.131 | 0 | 0 | 3611.131 | Heating | 3186.292 | 8.5 | 3186.292 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 637.2584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3251.3184 | 0 | 650.2637 | 6.503% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 06:00 | 2 | 9 | 6 | 40 | 942 | 19.04 | 3769.0847 | 0 | 0 | 3769.0847 | Heating | 3325.663 | 8.5 | 3325.663 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 665.1326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3393.5336 | 0 | 678.7067 | 6.787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 07:00 | 2 | 9 | 7 | 40 | 943 | 17.96 | 16575.5607 | 0 | 0 | 16575.5607 | Heating | 14625.4948 | 8.5 | 14625.4948 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2925.099 | 58.5% | 2 | 58.5% | 58.5% | 0% | 0% | 23.7485 | 23.7485 | 0 | 0 | 47.4969 | 14923.9743 | 0 | 2984.7949 | 29.85% | 1 | 59.7% | 0% | 0% | 12.439 | 0 | 0 | 12.439 | 59.9359
2007-02-09 08:00 | 2 | 9 | 8 | 40 | 944 | 17.96 | 13941.7555 | 0 | 0 | 13941.7555 | Heating | 12301.549 | 8.5 | 12301.549 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2460.3098 | 49.21% | 1 | 98.41% | 0% | 0% | 0% | 78.5521 | 0 | 0 | 0 | 78.5521 | 12552.601 | 0 | 2510.5202 | 25.11% | 1 | 50.21% | 0% | 0% | 8.3548 | 0 | 0 | 8.3548 | 86.9069
2007-02-09 09:00 | 2 | 9 | 9 | 40 | 945 | 15.8 | 11848.6113 | 0 | 0 | 11848.6113 | Heating | 10454.6571 | 8.5 | 10454.6571 | 0 | 2.8226 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2090.9314 | 41.82% | 1 | 83.64% | 0% | 0% | 0% | 54.0334 | 0 | 0 | 0 | 54.0334 | 10668.0174 | 0 | 2133.6035 | 21.34% | 1 | 42.67% | 0% | 0% | 5.747 | 0 | 0 | 5.747 | 59.7805
2007-02-09 10:00 | 2 | 9 | 10 | 40 | 946 | 15.98 | 9498.3403 | 0 | 0 | 9498.3403 | Heating | 8380.8885 | 8.5 | 8380.8885 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1676.1777 | 33.52% | 1 | 67.05% | 0% | 0% | 0% | 32.495 | 0 | 0 | 0 | 32.495 | 8551.927 | 0 | 1710.3854 | 17.1% | 1 | 34.21% | 0% | 0% | 3.4562 | 0 | 0 | 3.4562 | 35.9512
2007-02-09 11:00 | 2 | 9 | 11 | 40 | 947 | 17.6 | 7659.4214 | 0 | 0 | 7659.4214 | Heating | 6758.313 | 8.5 | 6758.313 | 0 | 2.8595 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1351.6626 | 30% | 1 | 54.07% | 0% | 0% | 0% | 19.8097 | 0 | 0 | 0 | 19.8097 | 6896.2378 | 0 | 1379.2476 | 13.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.0843
2007-02-09 12:00 | 2 | 9 | 12 | 40 | 948 | 21.92 | 6515.0799 | 0 | 0 | 6515.0799 | Heating | 5748.6 | 8.5 | 5748.6 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1149.72 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5865.9183 | 0 | 1173.1837 | 11.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 13:00 | 2 | 9 | 13 | 40 | 949 | 21.2 | 6044.152 | 0 | 0 | 6044.152 | Heating | 5333.0753 | 8.5 | 5333.0753 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1066.6151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5441.9136 | 0 | 1088.3827 | 10.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 14:00 | 2 | 9 | 14 | 40 | 950 | 24.08 | 5296.9404 | 0 | 0 | 5296.9404 | Heating | 4673.771 | 8.5 | 4673.771 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 934.7542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4769.154 | 0 | 953.8308 | 9.538% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 15:00 | 2 | 9 | 15 | 40 | 951 | 24.98 | 4729.2978 | 0 | 0 | 4729.2978 | Heating | 4172.9099 | 8.5 | 4172.9099 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 834.582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4258.0713 | 0 | 851.6143 | 8.516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 16:00 | 2 | 9 | 16 | 40 | 952 | 24.98 | 4603.8174 | 0 | 0 | 4603.8174 | Heating | 4062.1918 | 8.5 | 4062.1918 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 812.4384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4145.0937 | 0 | 829.0187 | 8.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 17:00 | 2 | 9 | 17 | 40 | 953 | 24.98 | 4569.7461 | 0 | 0 | 4569.7461 | Heating | 4032.1289 | 8.5 | 4032.1289 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 806.4258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4114.4173 | 0 | 822.8835 | 8.229% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 18:00 | 2 | 9 | 18 | 40 | 954 | 19.94 | 4707.8357 | 0 | 0 | 4707.8357 | Heating | 4153.9726 | 8.5 | 4153.9726 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 830.7945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4238.7476 | 0 | 847.7495 | 8.477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 19:00 | 2 | 9 | 19 | 40 | 955 | 15.98 | 4850.7865 | 0 | 0 | 4850.7865 | Heating | 4280.1057 | 8.5 | 4280.1057 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 856.0211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4367.4548 | 0 | 873.491 | 8.735% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 20:00 | 2 | 9 | 20 | 40 | 956 | 15.98 | 5301.6631 | 0 | 0 | 5301.6631 | Heating | 4677.938 | 8.5 | 4677.938 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 935.5876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4773.4061 | 0 | 954.6812 | 9.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 21:00 | 2 | 9 | 21 | 40 | 957 | 12.02 | 5565.8412 | 0 | 0 | 5565.8412 | Heating | 4911.0364 | 8.5 | 4911.0364 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 982.2073 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5011.2616 | 0 | 1002.2523 | 10.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 22:00 | 2 | 9 | 22 | 40 | 958 | 10.94 | 5983.5449 | 0 | 0 | 5983.5449 | Heating | 5279.5984 | 8.5 | 5279.5984 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1055.9197 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5387.3453 | 0 | 1077.4691 | 10.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-09 23:00 | 2 | 9 | 23 | 40 | 959 | 10.94 | 1742.2006 | 0 | 0 | 1742.2006 | Heating | 1537.2359 | 8.5 | 1537.2359 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 307.4472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1568.608 | 0 | 313.7216 | 3.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 | 2 | 10 | 0 | 41 | 960 | 5 | 1781.211 | 0 | 0 | 1781.211 | Heating | 1571.6568 | 8.5 | 1571.6568 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 314.3314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1603.7314 | 0 | 320.7463 | 3.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 01:00 | 2 | 10 | 1 | 41 | 961 | 3.02 | 1814.4899 | 0 | 0 | 1814.4899 | Heating | 1601.0205 | 8.5 | 1601.0205 | 0 | 2.6241 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.2041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1633.6944 | 0 | 326.7389 | 3.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 02:00 | 2 | 10 | 2 | 41 | 962 | 3.02 | 1830.3218 | 0 | 0 | 1830.3218 | Heating | 1614.9898 | 8.5 | 1614.9898 | 0 | 2.6241 | 0 | 0 | 0 | 0 | 8.5 | 0 | 322.998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1647.9488 | 0 | 329.5898 | 3.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 03:00 | 2 | 10 | 3 | 41 | 963 | 1.04 | 1850.3151 | 0 | 0 | 1850.3151 | Heating | 1632.6309 | 8.5 | 1632.6309 | 0 | 2.5975 | 0 | 0 | 0 | 0 | 8.5 | 0 | 326.5262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1665.9499 | 0 | 333.19 | 3.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 04:00 | 2 | 10 | 4 | 41 | 964 | -2.02 | 1892.2241 | 0 | 0 | 1892.2241 | Heating | 1669.6095 | 8.5 | 1669.6095 | 0 | 2.5555 | 0 | 0 | 0 | 0 | 8.5 | 0 | 333.9219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1703.6832 | 0 | 340.7366 | 3.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 05:00 | 2 | 10 | 5 | 41 | 965 | -2.02 | 2013.6068 | 0 | 0 | 2013.6068 | Heating | 1776.7119 | 8.5 | 1776.7119 | 0 | 2.5555 | 0 | 0 | 0 | 0 | 8.5 | 0 | 355.3424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1812.9713 | 0 | 362.5943 | 3.626% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 06:00 | 2 | 10 | 6 | 41 | 966 | -0.94 | 2110.5107 | 0 | 0 | 2110.5107 | Heating | 1862.2153 | 8.5 | 1862.2153 | 0 | 2.5706 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.4431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1900.2197 | 0 | 380.0439 | 3.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 07:00 | 2 | 10 | 7 | 41 | 967 | -2.02 | 2103.0012 | 0 | 0 | 2103.0012 | Heating | 1855.5893 | 8.5 | 1855.5893 | 0 | 2.5555 | 0 | 0 | 0 | 0 | 8.5 | 0 | 371.1179 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1893.4584 | 0 | 378.6917 | 3.787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 08:00 | 2 | 10 | 8 | 41 | 968 | -2.02 | 2165.5454 | 0 | 0 | 2165.5454 | Heating | 1910.7754 | 8.5 | 1910.7754 | 0 | 2.5555 | 0 | 0 | 0 | 0 | 8.5 | 0 | 382.1551 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1949.7708 | 0 | 389.9542 | 3.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 09:00 | 2 | 10 | 9 | 41 | 969 | 6.98 | 11132.0724 | 0 | 0 | 11132.0724 | Heating | 9822.4168 | 8.5 | 9822.4168 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1964.4834 | 39.29% | 1 | 78.58% | 0% | 0% | 0% | 46.8115 | 0 | 0 | 0 | 46.8115 | 10022.8743 | 0 | 2004.5749 | 20.05% | 1 | 40.09% | 0% | 0% | 4.9789 | 0 | 0 | 4.9789 | 51.7904
2007-02-10 10:00 | 2 | 10 | 10 | 41 | 970 | 15.08 | 8503.6186 | 0 | 0 | 8503.6186 | Heating | 7503.1929 | 8.5 | 7503.1929 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1500.6386 | 30.01% | 1 | 60.03% | 0% | 0% | 0% | 25.1951 | 0 | 0 | 0 | 25.1951 | 7656.3192 | 0 | 1531.2638 | 15.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.4696
2007-02-10 11:00 | 2 | 10 | 11 | 41 | 971 | 15.08 | 7234.1321 | 0 | 0 | 7234.1321 | Heating | 6383.0577 | 8.5 | 6383.0577 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1276.6115 | 30% | 1 | 51.06% | 0% | 0% | 0% | 17.3707 | 0 | 0 | 0 | 17.3707 | 6513.3242 | 0 | 1302.6648 | 13.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.6452
2007-02-10 12:00 | 2 | 10 | 12 | 41 | 972 | 19.04 | 6488.371 | 0 | 0 | 6488.371 | Heating | 5725.0332 | 8.5 | 5725.0332 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1145.0066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5841.8706 | 0 | 1168.3741 | 11.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 13:00 | 2 | 10 | 13 | 41 | 973 | 24.08 | 5729.5581 | 0 | 0 | 5729.5581 | Heating | 5055.4925 | 8.5 | 5055.4925 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1011.0985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5158.6658 | 0 | 1031.7332 | 10.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 14:00 | 2 | 10 | 14 | 41 | 974 | 24.08 | 5339.4674 | 0 | 0 | 5339.4674 | Heating | 4711.2948 | 8.5 | 4711.2948 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 942.259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4807.4437 | 0 | 961.4887 | 9.615% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 15:00 | 2 | 10 | 15 | 41 | 975 | 26.96 | 5077.2247 | 0 | 0 | 5077.2247 | Heating | 4479.9041 | 8.5 | 4479.9041 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 895.9808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4571.3308 | 0 | 914.2662 | 9.143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 16:00 | 2 | 10 | 16 | 41 | 976 | 26.06 | 5001.2339 | 0 | 0 | 5001.2339 | Heating | 4412.8535 | 8.5 | 4412.8535 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 882.5707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4502.9117 | 0 | 900.5823 | 9.006% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 17:00 | 2 | 10 | 17 | 41 | 977 | 26.06 | 5177.7743 | 0 | 0 | 5177.7743 | Heating | 4568.6244 | 8.5 | 4568.6244 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 913.7249 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4661.8616 | 0 | 932.3723 | 9.324% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 18:00 | 2 | 10 | 18 | 41 | 978 | 21.02 | 7513.706 | 0 | 0 | 7513.706 | Heating | 6629.7406 | 8.5 | 6629.7406 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1325.9481 | 30% | 1 | 53.04% | 0% | 0% | 0% | 18.9536 | 0 | 0 | 0 | 18.9536 | 6765.0414 | 0 | 1353.0083 | 13.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.2282
2007-02-10 19:00 | 2 | 10 | 19 | 41 | 979 | 17.06 | 8197.6052 | 0 | 0 | 8197.6052 | Heating | 7233.1811 | 8.5 | 7233.1811 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1446.6362 | 30% | 1 | 57.87% | 0% | 0% | 0% | 23.1583 | 0 | 0 | 0 | 23.1583 | 7380.797 | 0 | 1476.1594 | 14.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.4329
2007-02-10 20:00 | 2 | 10 | 20 | 41 | 980 | 17.06 | 2140.6252 | 0 | 0 | 2140.6252 | Heating | 1888.7869 | 8.5 | 1888.7869 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 377.7574 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1927.3336 | 0 | 385.4667 | 3.855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 21:00 | 2 | 10 | 21 | 41 | 981 | 12.92 | 2228.5271 | 0 | 0 | 2228.5271 | Heating | 1966.3474 | 8.5 | 1966.3474 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 393.2695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2006.477 | 0 | 401.2954 | 4.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 22:00 | 2 | 10 | 22 | 41 | 982 | 10.94 | 2390.094 | 0 | 0 | 2390.094 | Heating | 2108.9064 | 8.5 | 2108.9064 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.7813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2151.9453 | 0 | 430.3891 | 4.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-10 23:00 | 2 | 10 | 23 | 41 | 983 | 10.94 | 2723.2865 | 0 | 0 | 2723.2865 | Heating | 2402.8999 | 8.5 | 2402.8999 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 480.58 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2451.9387 | 0 | 490.3877 | 4.904% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 | 2 | 11 | 0 | 42 | 984 | 14 | 3032.3466 | 0 | 0 | 3032.3466 | Heating | 2675.5999 | 8.5 | 2675.5999 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 535.12 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2730.204 | 0 | 546.0408 | 5.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 01:00 | 2 | 11 | 1 | 42 | 985 | 15.08 | 3100.0753 | 0 | 0 | 3100.0753 | Heating | 2735.3606 | 8.5 | 2735.3606 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 547.0721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2791.1842 | 0 | 558.2368 | 5.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 02:00 | 2 | 11 | 2 | 42 | 986 | 15.08 | 3198.2022 | 0 | 0 | 3198.2022 | Heating | 2821.9431 | 8.5 | 2821.9431 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 564.3886 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2879.5338 | 0 | 575.9068 | 5.759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 03:00 | 2 | 11 | 3 | 42 | 987 | 17.06 | 3164.9321 | 0 | 0 | 3164.9321 | Heating | 2792.5871 | 8.5 | 2792.5871 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 558.5174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2849.5787 | 0 | 569.9157 | 5.699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 04:00 | 2 | 11 | 4 | 42 | 988 | 19.94 | 3211.2226 | 0 | 0 | 3211.2226 | Heating | 2833.4317 | 8.5 | 2833.4317 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 566.6863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2891.2569 | 0 | 578.2514 | 5.783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 05:00 | 2 | 11 | 5 | 42 | 989 | 19.94 | 3206.7495 | 0 | 0 | 3206.7495 | Heating | 2829.4849 | 8.5 | 2829.4849 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 565.897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2887.2295 | 0 | 577.4459 | 5.774% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 06:00 | 2 | 11 | 6 | 42 | 990 | 30.2 | 3121.2883 | 0 | 0 | 3121.2883 | Heating | 2754.0779 | 8.5 | 2754.0779 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.8156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2810.2836 | 0 | 562.0567 | 5.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 07:00 | 2 | 11 | 7 | 42 | 991 | 33.08 | 15123.4562 | 0 | 0 | 15123.4562 | Heating | 13344.2261 | 8.5 | 13344.2261 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2668.8452 | 53.38% | 2 | 53.38% | 53.38% | 0% | 0% | 19.2334 | 19.2334 | 0 | 0 | 38.4668 | 13616.5572 | 0 | 2723.3114 | 27.23% | 1 | 54.47% | 0% | 0% | 10.0741 | 0 | 0 | 10.0741 | 48.5409
2007-02-11 08:00 | 2 | 11 | 8 | 42 | 992 | 33.08 | 12694.8127 | 0 | 0 | 12694.8127 | Heating | 11201.3053 | 8.5 | 11201.3053 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2240.2611 | 44.81% | 1 | 89.61% | 0% | 0% | 0% | 63.3239 | 0 | 0 | 0 | 63.3239 | 11429.9034 | 0 | 2285.9807 | 22.86% | 1 | 45.72% | 0% | 0% | 6.7352 | 0 | 0 | 6.7352 | 70.0591
2007-02-11 09:00 | 2 | 11 | 9 | 42 | 993 | 32 | 10379.3509 | 0 | 0 | 10379.3509 | Heating | 9158.2508 | 8.5 | 9158.2508 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1831.6502 | 36.63% | 1 | 73.27% | 0% | 0% | 0% | 39.8491 | 0 | 0 | 0 | 39.8491 | 9345.1539 | 0 | 1869.0308 | 18.69% | 1 | 37.38% | 0% | 0% | 4.2384 | 0 | 0 | 4.2384 | 44.0875
2007-02-11 10:00 | 2 | 11 | 10 | 42 | 994 | 32 | 8102.4149 | 0 | 0 | 8102.4149 | Heating | 7149.1896 | 8.5 | 7149.1896 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1429.8379 | 30% | 1 | 57.19% | 0% | 0% | 0% | 22.5445 | 0 | 0 | 0 | 22.5445 | 7295.0914 | 0 | 1459.0183 | 14.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.819
2007-02-11 11:00 | 2 | 11 | 11 | 42 | 995 | 33.98 | 7096.3031 | 0 | 0 | 7096.3031 | Heating | 6261.4439 | 8.5 | 6261.4439 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1252.2888 | 30% | 1 | 50.09% | 0% | 0% | 0% | 16.6189 | 0 | 0 | 0 | 16.6189 | 6389.2285 | 0 | 1277.8457 | 12.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8934
2007-02-11 12:00 | 2 | 11 | 12 | 42 | 996 | 35.96 | 6385.3194 | 0 | 0 | 6385.3194 | Heating | 5634.1054 | 8.5 | 5634.1054 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1126.8211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5749.0871 | 0 | 1149.8174 | 11.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 13:00 | 2 | 11 | 13 | 42 | 997 | 37.04 | 5774.5931 | 0 | 0 | 5774.5931 | Heating | 5095.2292 | 8.5 | 5095.2292 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1019.0458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5199.2134 | 0 | 1039.8427 | 10.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 14:00 | 2 | 11 | 14 | 42 | 998 | 37.04 | 5409.4539 | 0 | 0 | 5409.4539 | Heating | 4773.0475 | 8.5 | 4773.0475 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 954.6095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4870.4567 | 0 | 974.0913 | 9.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 15:00 | 2 | 11 | 15 | 42 | 999 | 37.94 | 5232.9887 | 0 | 0 | 5232.9887 | Heating | 4617.343 | 8.5 | 4617.343 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 923.4686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4711.5745 | 0 | 942.3149 | 9.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 16:00 | 2 | 11 | 16 | 42 | 1000 | 37.94 | 5105.7567 | 0 | 0 | 5105.7567 | Heating | 4505.0795 | 8.5 | 4505.0795 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 901.0159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4597.0199 | 0 | 919.404 | 9.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 17:00 | 2 | 11 | 17 | 42 | 1001 | 37.94 | 5179.4936 | 0 | 0 | 5179.4936 | Heating | 4570.1414 | 8.5 | 4570.1414 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 914.0283 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4663.4096 | 0 | 932.6819 | 9.327% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 18:00 | 2 | 11 | 18 | 42 | 1002 | 37.94 | 5460.0161 | 0 | 0 | 5460.0161 | Heating | 4817.6613 | 8.5 | 4817.6613 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 963.5323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4915.9809 | 0 | 983.1962 | 9.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 19:00 | 2 | 11 | 19 | 42 | 1003 | 37.94 | 5585.7289 | 0 | 0 | 5585.7289 | Heating | 4928.5843 | 8.5 | 4928.5843 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 985.7169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5029.1677 | 0 | 1005.8335 | 10.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 20:00 | 2 | 11 | 20 | 42 | 1004 | 37.94 | 5853.3144 | 0 | 0 | 5853.3144 | Heating | 5164.6892 | 8.5 | 5164.6892 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1032.9378 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5270.091 | 0 | 1054.0182 | 10.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 21:00 | 2 | 11 | 21 | 42 | 1005 | 37.4 | 6158.5244 | 0 | 0 | 6158.5244 | Heating | 5433.9921 | 8.5 | 5433.9921 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1086.7984 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5544.8899 | 0 | 1108.978 | 11.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 22:00 | 2 | 11 | 22 | 42 | 1006 | 37.4 | 1848.2959 | 0 | 0 | 1848.2959 | Heating | 1630.8493 | 8.5 | 1630.8493 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 326.1699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1664.1319 | 0 | 332.8264 | 3.328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-11 23:00 | 2 | 11 | 23 | 42 | 1007 | 37.04 | 1763.8421 | 0 | 0 | 1763.8421 | Heating | 1556.3313 | 8.5 | 1556.3313 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.2663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1588.0931 | 0 | 317.6186 | 3.176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 | 2 | 12 | 0 | 43 | 1008 | 35.06 | 2028.4332 | 0 | 0 | 2028.4332 | Heating | 1789.794 | 8.5 | 1789.794 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 357.9588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1826.3204 | 0 | 365.2641 | 3.653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 01:00 | 2 | 12 | 1 | 43 | 1009 | 35.6 | 2141.83 | 0 | 0 | 2141.83 | Heating | 1889.85 | 8.5 | 1889.85 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 377.97 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1928.4183 | 0 | 385.6837 | 3.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 02:00 | 2 | 12 | 2 | 43 | 1010 | 37.04 | 2320.6169 | 0 | 0 | 2320.6169 | Heating | 2047.6032 | 8.5 | 2047.6032 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.5206 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2089.391 | 0 | 417.8782 | 4.179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 03:00 | 2 | 12 | 3 | 43 | 1011 | 35.06 | 2416.7074 | 0 | 0 | 2416.7074 | Heating | 2132.3889 | 8.5 | 2132.3889 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.4778 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2175.907 | 0 | 435.1814 | 4.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 04:00 | 2 | 12 | 4 | 43 | 1012 | 35.96 | 2384.2601 | 0 | 0 | 2384.2601 | Heating | 2103.7589 | 8.5 | 2103.7589 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 420.7518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2146.6928 | 0 | 429.3386 | 4.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 05:00 | 2 | 12 | 5 | 43 | 1013 | 35.96 | 2258.7097 | 0 | 0 | 2258.7097 | Heating | 1992.9791 | 8.5 | 1992.9791 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 398.5958 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2033.6522 | 0 | 406.7304 | 4.067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 06:00 | 2 | 12 | 6 | 43 | 1014 | 37.04 | 2188.6116 | 0 | 0 | 2188.6116 | Heating | 1931.1279 | 8.5 | 1931.1279 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 386.2256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1970.5386 | 0 | 394.1077 | 3.941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 07:00 | 2 | 12 | 7 | 43 | 1015 | 37.04 | 12461.9378 | 0 | 0 | 12461.9378 | Heating | 10995.8274 | 8.5 | 10995.8274 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2199.1655 | 43.98% | 1 | 87.97% | 0% | 0% | 0% | 60.684 | 0 | 0 | 0 | 60.684 | 11220.2321 | 0 | 2244.0464 | 22.44% | 1 | 44.88% | 0% | 0% | 6.4544 | 0 | 0 | 6.4544 | 67.1384
2007-02-12 08:00 | 2 | 12 | 8 | 43 | 1016 | 37.04 | 9335.1869 | 0 | 0 | 9335.1869 | Heating | 8236.9296 | 8.5 | 8236.9296 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1647.3859 | 32.95% | 1 | 65.9% | 0% | 0% | 0% | 31.2256 | 0 | 0 | 0 | 31.2256 | 8405.0302 | 0 | 1681.006 | 16.81% | 1 | 33.62% | 0% | 0% | 3.3212 | 0 | 0 | 3.3212 | 34.5467
2007-02-12 09:00 | 2 | 12 | 9 | 43 | 1017 | 37.04 | 7531.3295 | 0 | 0 | 7531.3295 | Heating | 6645.2908 | 8.5 | 6645.2908 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1329.0582 | 30% | 1 | 53.16% | 0% | 0% | 0% | 19.056 | 0 | 0 | 0 | 19.056 | 6780.9089 | 0 | 1356.1818 | 13.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.3306
2007-02-12 10:00 | 2 | 12 | 10 | 43 | 1018 | 37.04 | 6156.144 | 0 | 0 | 6156.144 | Heating | 5431.8918 | 8.5 | 5431.8918 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1086.3784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5542.7467 | 0 | 1108.5493 | 11.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 11:00 | 2 | 12 | 11 | 43 | 1019 | 37.04 | 5392.0037 | 0 | 0 | 5392.0037 | Heating | 4757.6503 | 8.5 | 4757.6503 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 951.5301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4854.7452 | 0 | 970.949 | 9.709% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 12:00 | 2 | 12 | 12 | 43 | 1020 | 37.4 | 4640.986 | 0 | 0 | 4640.986 | Heating | 4094.9876 | 8.5 | 4094.9876 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 818.9975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4178.5588 | 0 | 835.7118 | 8.357% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 13:00 | 2 | 12 | 13 | 43 | 1021 | 37.4 | 4114.9369 | 0 | 0 | 4114.9369 | Heating | 3630.8267 | 8.5 | 3630.8267 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 726.1653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3704.9252 | 0 | 740.985 | 7.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 14:00 | 2 | 12 | 14 | 43 | 1022 | 37.04 | 3684.7404 | 0 | 0 | 3684.7404 | Heating | 3251.2415 | 8.5 | 3251.2415 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 650.2483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3317.5934 | 0 | 663.5187 | 6.635% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 15:00 | 2 | 12 | 15 | 43 | 1023 | 37.4 | 3447.73 | 0 | 0 | 3447.73 | Heating | 3042.1147 | 8.5 | 3042.1147 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 608.4229 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3104.1987 | 0 | 620.8397 | 6.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 16:00 | 2 | 12 | 16 | 43 | 1024 | 35.6 | 3514.5177 | 0 | 0 | 3514.5177 | Heating | 3101.045 | 8.5 | 3101.045 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 620.209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3164.3316 | 0 | 632.8663 | 6.329% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 17:00 | 2 | 12 | 17 | 43 | 1025 | 35.96 | 3859.3191 | 0 | 0 | 3859.3191 | Heating | 3405.2816 | 8.5 | 3405.2816 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 681.0563 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3474.7771 | 0 | 694.9554 | 6.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 18:00 | 2 | 12 | 18 | 43 | 1026 | 35.06 | 4167.6906 | 0 | 0 | 4167.6906 | Heating | 3677.3741 | 8.5 | 3677.3741 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 735.4748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3752.4225 | 0 | 750.4845 | 7.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 19:00 | 2 | 12 | 19 | 43 | 1027 | 35.06 | 4252.5693 | 0 | 0 | 4252.5693 | Heating | 3752.2671 | 8.5 | 3752.2671 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.4534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3828.8439 | 0 | 765.7688 | 7.658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 20:00 | 2 | 12 | 20 | 43 | 1028 | 35.06 | 4377.1928 | 0 | 0 | 4377.1928 | Heating | 3862.229 | 8.5 | 3862.229 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 772.4458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3941.05 | 0 | 788.21 | 7.882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 21:00 | 2 | 12 | 21 | 43 | 1029 | 33.98 | 4616.4992 | 0 | 0 | 4616.4992 | Heating | 4073.3817 | 8.5 | 4073.3817 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 814.6763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4156.5119 | 0 | 831.3024 | 8.313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 22:00 | 2 | 12 | 22 | 43 | 1030 | 33.08 | 1521.1056 | 0 | 0 | 1521.1056 | Heating | 1342.152 | 8.5 | 1342.152 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.4304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1369.5428 | 0 | 273.9086 | 2.739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-12 23:00 | 2 | 12 | 23 | 43 | 1031 | 33.08 | 1682.9003 | 0 | 0 | 1682.9003 | Heating | 1484.9121 | 8.5 | 1484.9121 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.9824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1515.2164 | 0 | 303.0433 | 3.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 | 2 | 13 | 0 | 44 | 1032 | 33.08 | 2119.9615 | 0 | 0 | 2119.9615 | Heating | 1870.5542 | 8.5 | 1870.5542 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.1108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1908.7288 | 0 | 381.7458 | 3.817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 01:00 | 2 | 13 | 1 | 44 | 1033 | 32 | 2417.0521 | 0 | 0 | 2417.0521 | Heating | 2132.693 | 8.5 | 2132.693 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.5386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2176.2174 | 0 | 435.2435 | 4.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 02:00 | 2 | 13 | 2 | 44 | 1034 | 32 | 2571.6307 | 0 | 0 | 2571.6307 | Heating | 2269.0859 | 8.5 | 2269.0859 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 453.8172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2315.3938 | 0 | 463.0788 | 4.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 03:00 | 2 | 13 | 3 | 44 | 1035 | 32 | 2720.0259 | 0 | 0 | 2720.0259 | Heating | 2400.0228 | 8.5 | 2400.0228 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 480.0046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2449.0029 | 0 | 489.8006 | 4.898% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 04:00 | 2 | 13 | 4 | 44 | 1036 | 32 | 2770.9305 | 0 | 0 | 2770.9305 | Heating | 2444.9387 | 8.5 | 2444.9387 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 488.9877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2494.8354 | 0 | 498.9671 | 4.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 05:00 | 2 | 13 | 5 | 44 | 1037 | 32 | 2686.7567 | 0 | 0 | 2686.7567 | Heating | 2370.6676 | 8.5 | 2370.6676 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 474.1335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2419.0486 | 0 | 483.8097 | 4.838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 06:00 | 2 | 13 | 6 | 44 | 1038 | 32 | 2649.4557 | 0 | 0 | 2649.4557 | Heating | 2337.7551 | 8.5 | 2337.7551 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.551 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2385.4643 | 0 | 477.0929 | 4.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 07:00 | 2 | 13 | 7 | 44 | 1039 | 30.02 | 13384.1385 | 0 | 0 | 13384.1385 | Heating | 11809.5339 | 8.5 | 11809.5339 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2361.9068 | 47.24% | 1 | 94.48% | 0% | 0% | 0% | 71.5131 | 0 | 0 | 0 | 71.5131 | 12050.5448 | 0 | 2410.109 | 24.1% | 1 | 48.2% | 0% | 0% | 7.6062 | 0 | 0 | 7.6062 | 79.1192
2007-02-13 08:00 | 2 | 13 | 8 | 44 | 1040 | 30.02 | 10463.3673 | 0 | 0 | 10463.3673 | Heating | 9232.3829 | 8.5 | 9232.3829 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1846.4766 | 36.93% | 1 | 73.86% | 0% | 0% | 0% | 40.5949 | 0 | 0 | 0 | 40.5949 | 9420.7989 | 0 | 1884.1598 | 18.84% | 1 | 37.68% | 0% | 0% | 4.3177 | 0 | 0 | 4.3177 | 44.9126
2007-02-13 09:00 | 2 | 13 | 9 | 44 | 1041 | 33.08 | 8728.5892 | 0 | 0 | 8728.5892 | Heating | 7701.6964 | 8.5 | 7701.6964 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1540.3393 | 30.81% | 1 | 61.61% | 0% | 0% | 0% | 26.7546 | 0 | 0 | 0 | 26.7546 | 7858.8738 | 0 | 1571.7748 | 15.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.0292
2007-02-13 10:00 | 2 | 13 | 10 | 44 | 1042 | 33.98 | 7345.8717 | 0 | 0 | 7345.8717 | Heating | 6481.6515 | 8.5 | 6481.6515 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1296.3303 | 30% | 1 | 51.85% | 0% | 0% | 0% | 17.994 | 0 | 0 | 0 | 17.994 | 6613.9301 | 0 | 1322.786 | 13.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.2685
2007-02-13 11:00 | 2 | 13 | 11 | 44 | 1043 | 33.98 | 6615.6836 | 0 | 0 | 6615.6836 | Heating | 5837.3678 | 8.5 | 5837.3678 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1167.4736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5956.4978 | 0 | 1191.2996 | 11.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 12:00 | 2 | 13 | 12 | 44 | 1044 | 35.96 | 6158.0374 | 0 | 0 | 6158.0374 | Heating | 5433.5624 | 8.5 | 5433.5624 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1086.7125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5544.4514 | 0 | 1108.8903 | 11.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 13:00 | 2 | 13 | 13 | 44 | 1045 | 37.94 | 5903.2362 | 0 | 0 | 5903.2362 | Heating | 5208.7378 | 8.5 | 5208.7378 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1041.7476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5315.0386 | 0 | 1063.0077 | 10.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 14:00 | 2 | 13 | 14 | 44 | 1046 | 37.94 | 5646.5809 | 0 | 0 | 5646.5809 | Heating | 4982.2772 | 8.5 | 4982.2772 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 996.4554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5083.9564 | 0 | 1016.7913 | 10.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 15:00 | 2 | 13 | 15 | 44 | 1047 | 37.94 | 5598.5324 | 0 | 0 | 5598.5324 | Heating | 4939.8815 | 8.5 | 4939.8815 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 987.9763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5040.6954 | 0 | 1008.1391 | 10.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 16:00 | 2 | 13 | 16 | 44 | 1048 | 37.94 | 5556.971 | 0 | 0 | 5556.971 | Heating | 4903.2097 | 8.5 | 4903.2097 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 980.6419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5003.2752 | 0 | 1000.655 | 10.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 17:00 | 2 | 13 | 17 | 44 | 1049 | 37.94 | 5713.343 | 0 | 0 | 5713.343 | Heating | 5041.185 | 8.5 | 5041.185 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1008.237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5144.0663 | 0 | 1028.8133 | 10.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 18:00 | 2 | 13 | 18 | 44 | 1050 | 33.98 | 6101.1259 | 0 | 0 | 6101.1259 | Heating | 5383.3464 | 8.5 | 5383.3464 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1076.6693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5493.2106 | 0 | 1098.6421 | 10.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 19:00 | 2 | 13 | 19 | 44 | 1051 | 33.08 | 6239.4378 | 0 | 0 | 6239.4378 | Heating | 5505.3863 | 8.5 | 5505.3863 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1101.0773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5617.7411 | 0 | 1123.5482 | 11.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 20:00 | 2 | 13 | 20 | 44 | 1052 | 33.08 | 6418.8312 | 0 | 0 | 6418.8312 | Heating | 5663.6746 | 8.5 | 5663.6746 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1132.7349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5779.2598 | 0 | 1155.852 | 11.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 21:00 | 2 | 13 | 21 | 44 | 1053 | 32 | 6797.7287 | 0 | 0 | 6797.7287 | Heating | 5997.9959 | 8.5 | 5997.9959 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1199.5992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6120.404 | 0 | 1224.0808 | 12.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 22:00 | 2 | 13 | 22 | 44 | 1054 | 30.92 | 2158.016 | 0 | 0 | 2158.016 | Heating | 1904.1317 | 8.5 | 1904.1317 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.8263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1942.9916 | 0 | 388.5983 | 3.886% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-13 23:00 | 2 | 13 | 23 | 44 | 1055 | 30.92 | 2478.3242 | 0 | 0 | 2478.3242 | Heating | 2186.7566 | 8.5 | 2186.7566 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 437.3513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2231.3843 | 0 | 446.2769 | 4.463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 | 2 | 14 | 0 | 45 | 1056 | 30.02 | 2966.5476 | 0 | 0 | 2966.5476 | Heating | 2617.542 | 8.5 | 2617.542 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.5084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2670.9612 | 0 | 534.1922 | 5.342% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 01:00 | 2 | 14 | 1 | 45 | 1057 | 28.94 | 3001.2679 | 0 | 0 | 3001.2679 | Heating | 2648.1776 | 8.5 | 2648.1776 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 529.6355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2702.222 | 0 | 540.4444 | 5.404% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 02:00 | 2 | 14 | 2 | 45 | 1058 | 28.94 | 2942.4344 | 0 | 0 | 2942.4344 | Heating | 2596.2657 | 8.5 | 2596.2657 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 519.2531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2649.2507 | 0 | 529.8501 | 5.299% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 03:00 | 2 | 14 | 3 | 45 | 1059 | 28.04 | 2963.3672 | 0 | 0 | 2963.3672 | Heating | 2614.7358 | 8.5 | 2614.7358 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 522.9472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2668.0978 | 0 | 533.6196 | 5.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 04:00 | 2 | 14 | 4 | 45 | 1060 | 26.06 | 2899.9512 | 0 | 0 | 2899.9512 | Heating | 2558.7805 | 8.5 | 2558.7805 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 511.7561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2611.0005 | 0 | 522.2001 | 5.222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 05:00 | 2 | 14 | 5 | 45 | 1061 | 26.06 | 2885.992 | 0 | 0 | 2885.992 | Heating | 2546.4636 | 8.5 | 2546.4636 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 509.2927 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2598.4322 | 0 | 519.6864 | 5.197% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 06:00 | 2 | 14 | 6 | 45 | 1062 | 24.98 | 2961.1526 | 0 | 0 | 2961.1526 | Heating | 2612.7817 | 8.5 | 2612.7817 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 522.5563 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2666.1037 | 0 | 533.2207 | 5.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 07:00 | 2 | 14 | 7 | 45 | 1063 | 24.08 | 13972.319 | 0 | 0 | 13972.319 | Heating | 12328.5167 | 8.5 | 12328.5167 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2465.7033 | 49.31% | 1 | 98.63% | 0% | 0% | 0% | 78.9487 | 0 | 0 | 0 | 78.9487 | 12580.1191 | 0 | 2516.0238 | 25.16% | 1 | 50.32% | 0% | 0% | 8.397 | 0 | 0 | 8.397 | 87.3457
2007-02-14 08:00 | 2 | 14 | 8 | 45 | 1064 | 24.08 | 11350.7491 | 0 | 0 | 11350.7491 | Heating | 10015.3668 | 8.5 | 10015.3668 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2003.0734 | 40.06% | 1 | 80.12% | 0% | 0% | 0% | 48.9535 | 0 | 0 | 0 | 48.9535 | 10219.7621 | 0 | 2043.9524 | 20.44% | 1 | 40.88% | 0% | 0% | 5.2067 | 0 | 0 | 5.2067 | 54.1602
2007-02-14 09:00 | 2 | 14 | 9 | 45 | 1065 | 30.92 | 9328.9747 | 0 | 0 | 9328.9747 | Heating | 8231.4482 | 8.5 | 8231.4482 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1646.2896 | 32.93% | 1 | 65.85% | 0% | 0% | 0% | 31.1778 | 0 | 0 | 0 | 31.1778 | 8399.437 | 0 | 1679.8874 | 16.8% | 1 | 33.6% | 0% | 0% | 3.3161 | 0 | 0 | 3.3161 | 34.4939
2007-02-14 10:00 | 2 | 14 | 10 | 45 | 1066 | 35.06 | 7582.9789 | 0 | 0 | 7582.9789 | Heating | 6690.8637 | 8.5 | 6690.8637 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1338.1727 | 30% | 1 | 53.53% | 0% | 0% | 0% | 19.3579 | 0 | 0 | 0 | 19.3579 | 6827.4119 | 0 | 1365.4824 | 13.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.6325
2007-02-14 11:00 | 2 | 14 | 11 | 45 | 1067 | 35.06 | 6398.2884 | 0 | 0 | 6398.2884 | Heating | 5645.5486 | 8.5 | 5645.5486 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1129.1097 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5760.7639 | 0 | 1152.1528 | 11.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 12:00 | 2 | 14 | 12 | 45 | 1068 | 35.06 | 5409.7041 | 0 | 0 | 5409.7041 | Heating | 4773.2683 | 8.5 | 4773.2683 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 954.6537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4870.6819 | 0 | 974.1364 | 9.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 13:00 | 2 | 14 | 13 | 45 | 1069 | 35.96 | 4896.5451 | 0 | 0 | 4896.5451 | Heating | 4320.481 | 8.5 | 4320.481 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 864.0962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4408.654 | 0 | 881.7308 | 8.817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 14:00 | 2 | 14 | 14 | 45 | 1070 | 35.96 | 4440.4285 | 0 | 0 | 4440.4285 | Heating | 3918.0251 | 8.5 | 3918.0251 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 783.605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3997.9848 | 0 | 799.597 | 7.996% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 15:00 | 2 | 14 | 15 | 45 | 1071 | 39.02 | 4186.7199 | 0 | 0 | 4186.7199 | Heating | 3694.1646 | 8.5 | 3694.1646 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 738.8329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3769.5557 | 0 | 753.9111 | 7.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 16:00 | 2 | 14 | 16 | 45 | 1072 | 37.94 | 4110.8723 | 0 | 0 | 4110.8723 | Heating | 3627.2403 | 8.5 | 3627.2403 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 725.4481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3701.2656 | 0 | 740.2531 | 7.403% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 17:00 | 2 | 14 | 17 | 45 | 1073 | 37.94 | 4091.2743 | 0 | 0 | 4091.2743 | Heating | 3609.9479 | 8.5 | 3609.9479 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 721.9896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3683.6204 | 0 | 736.7241 | 7.367% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 18:00 | 2 | 14 | 18 | 45 | 1074 | 35.96 | 4543.5215 | 0 | 0 | 4543.5215 | Heating | 4008.9895 | 8.5 | 4008.9895 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 801.7979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4090.8056 | 0 | 818.1611 | 8.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 19:00 | 2 | 14 | 19 | 45 | 1075 | 32 | 5094.2994 | 0 | 0 | 5094.2994 | Heating | 4494.9701 | 8.5 | 4494.9701 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 898.994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4586.7042 | 0 | 917.3408 | 9.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 20:00 | 2 | 14 | 20 | 45 | 1076 | 32 | 6060.2266 | 0 | 0 | 6060.2266 | Heating | 5347.2588 | 8.5 | 5347.2588 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1069.4518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5456.3865 | 0 | 1091.2773 | 10.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 21:00 | 2 | 14 | 21 | 45 | 1077 | 32 | 6726.4037 | 0 | 0 | 6726.4037 | Heating | 5935.0621 | 8.5 | 5935.0621 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1187.0124 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6056.1858 | 0 | 1211.2372 | 12.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 22:00 | 2 | 14 | 22 | 45 | 1078 | 30.02 | 2021.3851 | 0 | 0 | 2021.3851 | Heating | 1783.5751 | 8.5 | 1783.5751 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 356.715 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1819.9746 | 0 | 363.9949 | 3.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-14 23:00 | 2 | 14 | 23 | 45 | 1079 | 30.02 | 1807.3577 | 0 | 0 | 1807.3577 | Heating | 1594.7274 | 8.5 | 1594.7274 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 318.9455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1627.2729 | 0 | 325.4546 | 3.255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 | 2 | 15 | 0 | 46 | 1080 | 33.98 | 1983.2644 | 0 | 0 | 1983.2644 | Heating | 1749.9392 | 8.5 | 1749.9392 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 349.9878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1785.6522 | 0 | 357.1304 | 3.571% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 01:00 | 2 | 15 | 1 | 46 | 1081 | 35.96 | 1952.9301 | 0 | 0 | 1952.9301 | Heating | 1723.1736 | 8.5 | 1723.1736 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.6347 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1758.3404 | 0 | 351.6681 | 3.517% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 02:00 | 2 | 15 | 2 | 46 | 1082 | 35.96 | 1918.0978 | 0 | 0 | 1918.0978 | Heating | 1692.4392 | 8.5 | 1692.4392 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 338.4878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1726.9788 | 0 | 345.3958 | 3.454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 03:00 | 2 | 15 | 3 | 46 | 1083 | 35.96 | 1997.1753 | 0 | 0 | 1997.1753 | Heating | 1762.2135 | 8.5 | 1762.2135 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 352.4427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1798.177 | 0 | 359.6354 | 3.596% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 04:00 | 2 | 15 | 4 | 46 | 1084 | 35.96 | 2055.4505 | 0 | 0 | 2055.4505 | Heating | 1813.6328 | 8.5 | 1813.6328 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.7266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1850.6457 | 0 | 370.1291 | 3.701% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 05:00 | 2 | 15 | 5 | 46 | 1085 | 35.96 | 2104.8544 | 0 | 0 | 2104.8544 | Heating | 1857.2245 | 8.5 | 1857.2245 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 371.4449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1895.127 | 0 | 379.0254 | 3.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 06:00 | 2 | 15 | 6 | 46 | 1086 | 35.96 | 2096.0812 | 0 | 0 | 2096.0812 | Heating | 1849.4834 | 8.5 | 1849.4834 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.8967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1887.2279 | 0 | 377.4456 | 3.774% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 07:00 | 2 | 15 | 7 | 46 | 1087 | 35.06 | 11734.3261 | 0 | 0 | 11734.3261 | Heating | 10353.8172 | 8.5 | 10353.8172 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2070.7634 | 41.42% | 1 | 82.83% | 0% | 0% | 0% | 52.8422 | 0 | 0 | 0 | 52.8422 | 10565.1196 | 0 | 2113.0239 | 21.13% | 1 | 42.26% | 0% | 0% | 5.6203 | 0 | 0 | 5.6203 | 58.4626
2007-02-15 08:00 | 2 | 15 | 8 | 46 | 1088 | 35.06 | 8707.7501 | 0 | 0 | 8707.7501 | Heating | 7683.3089 | 8.5 | 7683.3089 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1536.6618 | 30.73% | 1 | 61.47% | 0% | 0% | 0% | 26.6079 | 0 | 0 | 0 | 26.6079 | 7840.1112 | 0 | 1568.0222 | 15.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.8825
2007-02-15 09:00 | 2 | 15 | 9 | 46 | 1089 | 37.04 | 6952.1728 | 0 | 0 | 6952.1728 | Heating | 6134.2701 | 8.5 | 6134.2701 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1226.854 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6259.4593 | 0 | 1251.8919 | 12.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 10:00 | 2 | 15 | 10 | 46 | 1090 | 39.92 | 5384.1607 | 0 | 0 | 5384.1607 | Heating | 4750.73 | 8.5 | 4750.73 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 950.146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4847.6837 | 0 | 969.5367 | 9.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 11:00 | 2 | 15 | 11 | 46 | 1091 | 39.92 | 4476.9427 | 0 | 0 | 4476.9427 | Heating | 3950.2436 | 8.5 | 3950.2436 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 790.0487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4030.8608 | 0 | 806.1722 | 8.062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 12:00 | 2 | 15 | 12 | 46 | 1092 | 46.04 | 3855.1575 | 0 | 0 | 3855.1575 | Heating | 3401.6096 | 8.5 | 3401.6096 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 680.3219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3471.0302 | 0 | 694.206 | 6.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 13:00 | 2 | 15 | 13 | 46 | 1093 | 46.94 | 3590.5243 | 0 | 0 | 3590.5243 | Heating | 3168.1097 | 8.5 | 3168.1097 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 633.6219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3232.765 | 0 | 646.553 | 6.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 14:00 | 2 | 15 | 14 | 46 | 1094 | 46.94 | 3281.2694 | 0 | 0 | 3281.2694 | Heating | 2895.2377 | 8.5 | 2895.2377 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 579.0475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2954.3241 | 0 | 590.8648 | 5.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 15:00 | 2 | 15 | 15 | 46 | 1095 | 44.06 | 3088.2031 | 0 | 0 | 3088.2031 | Heating | 2724.8851 | 8.5 | 2724.8851 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 544.977 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2780.495 | 0 | 556.099 | 5.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 16:00 | 2 | 15 | 16 | 46 | 1096 | 44.06 | 3015.7196 | 0 | 0 | 3015.7196 | Heating | 2660.929 | 8.5 | 2660.929 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 532.1858 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2715.2337 | 0 | 543.0467 | 5.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 17:00 | 2 | 15 | 17 | 46 | 1097 | 44.06 | 2956.4094 | 0 | 0 | 2956.4094 | Heating | 2608.5965 | 8.5 | 2608.5965 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 521.7193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2661.8332 | 0 | 532.3666 | 5.324% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 18:00 | 2 | 15 | 18 | 46 | 1098 | 39.92 | 3034.2443 | 0 | 0 | 3034.2443 | Heating | 2677.2744 | 8.5 | 2677.2744 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 535.4549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2731.9126 | 0 | 546.3825 | 5.464% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 19:00 | 2 | 15 | 19 | 46 | 1099 | 39.02 | 3107.3402 | 0 | 0 | 3107.3402 | Heating | 2741.7708 | 8.5 | 2741.7708 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 548.3542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2797.7253 | 0 | 559.5451 | 5.595% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 20:00 | 2 | 15 | 20 | 46 | 1100 | 39.02 | 3221.5559 | 0 | 0 | 3221.5559 | Heating | 2842.5493 | 8.5 | 2842.5493 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 568.5099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2900.5605 | 0 | 580.1121 | 5.801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 21:00 | 2 | 15 | 21 | 46 | 1101 | 35.96 | 3391.8319 | 0 | 0 | 3391.8319 | Heating | 2992.7928 | 8.5 | 2992.7928 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 598.5586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3053.8703 | 0 | 610.7741 | 6.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 22:00 | 2 | 15 | 22 | 46 | 1102 | 35.96 | 952.9596 | 0 | 0 | 952.9596 | Heating | 840.8467 | 8.5 | 840.8467 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.1693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 858.0069 | 0 | 171.6014 | 1.716% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-15 23:00 | 2 | 15 | 23 | 46 | 1103 | 35.96 | 826.2335 | 0 | 0 | 826.2335 | Heating | 729.0296 | 8.5 | 729.0296 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.8059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 743.9077 | 0 | 148.7815 | 1.488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 | 2 | 16 | 0 | 47 | 1104 | 30.2 | 886.4532 | 0 | 0 | 886.4532 | Heating | 782.1646 | 8.5 | 782.1646 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.4329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 798.1271 | 0 | 159.6254 | 1.596% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 01:00 | 2 | 16 | 1 | 47 | 1105 | 30.2 | 923.4813 | 0 | 0 | 923.4813 | Heating | 814.8364 | 8.5 | 814.8364 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.9673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 831.4658 | 0 | 166.2932 | 1.663% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 02:00 | 2 | 16 | 2 | 47 | 1106 | 30.92 | 986.996 | 0 | 0 | 986.996 | Heating | 870.8788 | 8.5 | 870.8788 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.1758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 888.6518 | 0 | 177.7304 | 1.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 03:00 | 2 | 16 | 3 | 47 | 1107 | 30.02 | 1100.8907 | 0 | 0 | 1100.8907 | Heating | 971.3741 | 8.5 | 971.3741 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 194.2748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 991.1981 | 0 | 198.2396 | 1.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 04:00 | 2 | 16 | 4 | 47 | 1108 | 30.92 | 1214.4476 | 0 | 0 | 1214.4476 | Heating | 1071.5714 | 8.5 | 1071.5714 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 214.3143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1093.4402 | 0 | 218.688 | 2.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 05:00 | 2 | 16 | 5 | 47 | 1109 | 30.92 | 1261.3103 | 0 | 0 | 1261.3103 | Heating | 1112.9209 | 8.5 | 1112.9209 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.5842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1135.6336 | 0 | 227.1267 | 2.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 06:00 | 2 | 16 | 6 | 47 | 1110 | 26.96 | 1310.9346 | 0 | 0 | 1310.9346 | Heating | 1156.707 | 8.5 | 1156.707 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.3414 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1180.3133 | 0 | 236.0627 | 2.361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 07:00 | 2 | 16 | 7 | 47 | 1111 | 26.06 | 8611.5007 | 0 | 0 | 8611.5007 | Heating | 7598.383 | 8.5 | 7598.383 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1519.6766 | 30.39% | 1 | 60.79% | 0% | 0% | 0% | 25.9363 | 0 | 0 | 0 | 25.9363 | 7753.452 | 0 | 1550.6904 | 15.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.2109
2007-02-16 08:00 | 2 | 16 | 8 | 47 | 1112 | 26.06 | 6615.8303 | 0 | 0 | 6615.8303 | Heating | 5837.4973 | 8.5 | 5837.4973 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1167.4995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5956.6299 | 0 | 1191.326 | 11.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 09:00 | 2 | 16 | 9 | 47 | 1113 | 26.96 | 5948.2103 | 0 | 0 | 5948.2103 | Heating | 5248.4208 | 8.5 | 5248.4208 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1049.6842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5355.5315 | 0 | 1071.1063 | 10.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 10:00 | 2 | 16 | 10 | 47 | 1114 | 28.94 | 5083.8997 | 0 | 0 | 5083.8997 | Heating | 4485.7939 | 8.5 | 4485.7939 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 897.1588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4577.3407 | 0 | 915.4681 | 9.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 11:00 | 2 | 16 | 11 | 47 | 1115 | 28.94 | 4435.7839 | 0 | 0 | 4435.7839 | Heating | 3913.927 | 8.5 | 3913.927 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 782.7854 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3993.803 | 0 | 798.7606 | 7.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 12:00 | 2 | 16 | 12 | 47 | 1116 | 30.02 | 3977.6794 | 0 | 0 | 3977.6794 | Heating | 3509.7171 | 8.5 | 3509.7171 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 701.9434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3581.344 | 0 | 716.2688 | 7.163% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 13:00 | 2 | 16 | 13 | 47 | 1117 | 32 | 3807.828 | 0 | 0 | 3807.828 | Heating | 3359.8483 | 8.5 | 3359.8483 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 671.9697 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3428.4166 | 0 | 685.6833 | 6.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 14:00 | 2 | 16 | 14 | 47 | 1118 | 32 | 3691.5725 | 0 | 0 | 3691.5725 | Heating | 3257.2698 | 8.5 | 3257.2698 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 651.454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3323.7447 | 0 | 664.7489 | 6.647% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 15:00 | 2 | 16 | 15 | 47 | 1119 | 30.92 | 3595.5151 | 0 | 0 | 3595.5151 | Heating | 3172.5133 | 8.5 | 3172.5133 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 634.5027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3237.2585 | 0 | 647.4517 | 6.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 16:00 | 2 | 16 | 16 | 47 | 1120 | 30.92 | 3761.5495 | 0 | 0 | 3761.5495 | Heating | 3319.0142 | 8.5 | 3319.0142 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 663.8028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3386.7492 | 0 | 677.3498 | 6.773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 17:00 | 2 | 16 | 17 | 47 | 1121 | 30.92 | 4026.4376 | 0 | 0 | 4026.4376 | Heating | 3552.739 | 8.5 | 3552.739 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 710.5478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3625.2439 | 0 | 725.0488 | 7.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 18:00 | 2 | 16 | 18 | 47 | 1122 | 28.94 | 4482.385 | 0 | 0 | 4482.385 | Heating | 3955.0456 | 8.5 | 3955.0456 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 791.0091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4035.7608 | 0 | 807.1522 | 8.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 19:00 | 2 | 16 | 19 | 47 | 1123 | 28.94 | 5061.0237 | 0 | 0 | 5061.0237 | Heating | 4465.6092 | 8.5 | 4465.6092 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 893.1218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4556.7441 | 0 | 911.3488 | 9.113% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 20:00 | 2 | 16 | 20 | 47 | 1124 | 28.94 | 5744.4134 | 0 | 0 | 5744.4134 | Heating | 5068.6 | 8.5 | 5068.6 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1013.72 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5172.0408 | 0 | 1034.4082 | 10.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 21:00 | 2 | 16 | 21 | 47 | 1125 | 26.96 | 6098.5532 | 0 | 0 | 6098.5532 | Heating | 5381.0763 | 8.5 | 5381.0763 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1076.2153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5490.8942 | 0 | 1098.1788 | 10.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 22:00 | 2 | 16 | 22 | 47 | 1126 | 26.06 | 6623.9762 | 0 | 0 | 6623.9762 | Heating | 5844.6849 | 8.5 | 5844.6849 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1168.937 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5963.9642 | 0 | 1192.7928 | 11.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-16 23:00 | 2 | 16 | 23 | 47 | 1127 | 26.06 | 1968.9996 | 0 | 0 | 1968.9996 | Heating | 1737.3526 | 8.5 | 1737.3526 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 347.4705 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1772.8088 | 0 | 354.5618 | 3.546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 | 2 | 17 | 0 | 48 | 1128 | 23 | 2033.7032 | 0 | 0 | 2033.7032 | Heating | 1794.444 | 8.5 | 1794.444 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.8888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1831.0653 | 0 | 366.2131 | 3.662% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 01:00 | 2 | 17 | 1 | 48 | 1129 | 21.92 | 2054.6209 | 0 | 0 | 2054.6209 | Heating | 1812.9008 | 8.5 | 1812.9008 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.5802 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1849.8988 | 0 | 369.9798 | 3.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 02:00 | 2 | 17 | 2 | 48 | 1130 | 21.92 | 2125.2793 | 0 | 0 | 2125.2793 | Heating | 1875.2464 | 8.5 | 1875.2464 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 375.0493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1913.5168 | 0 | 382.7034 | 3.827% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 03:00 | 2 | 17 | 3 | 48 | 1131 | 21.92 | 2138.0988 | 0 | 0 | 2138.0988 | Heating | 1886.5577 | 8.5 | 1886.5577 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 377.3115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1925.0589 | 0 | 385.0118 | 3.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 04:00 | 2 | 17 | 4 | 48 | 1132 | 21.02 | 2133.7732 | 0 | 0 | 2133.7732 | Heating | 1882.741 | 8.5 | 1882.741 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.5482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1921.1643 | 0 | 384.2329 | 3.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 05:00 | 2 | 17 | 5 | 48 | 1133 | 21.02 | 2273.4319 | 0 | 0 | 2273.4319 | Heating | 2005.9693 | 8.5 | 2005.9693 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 401.1939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2046.9075 | 0 | 409.3815 | 4.094% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 06:00 | 2 | 17 | 6 | 48 | 1134 | 19.94 | 2414.2774 | 0 | 0 | 2414.2774 | Heating | 2130.2448 | 8.5 | 2130.2448 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2173.7191 | 0 | 434.7438 | 4.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 07:00 | 2 | 17 | 7 | 48 | 1135 | 17.96 | 2496.0501 | 0 | 0 | 2496.0501 | Heating | 2202.3972 | 8.5 | 2202.3972 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 440.4794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2247.344 | 0 | 449.4688 | 4.495% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 08:00 | 2 | 17 | 8 | 48 | 1136 | 17.96 | 2483.9371 | 0 | 0 | 2483.9371 | Heating | 2191.7092 | 8.5 | 2191.7092 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.3418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2236.438 | 0 | 447.2876 | 4.473% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 09:00 | 2 | 17 | 9 | 48 | 1137 | 19.04 | 11970.2726 | 0 | 0 | 11970.2726 | Heating | 10562.0052 | 8.5 | 10562.0052 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2112.401 | 42.25% | 1 | 84.5% | 0% | 0% | 0% | 55.318 | 0 | 0 | 0 | 55.318 | 10777.5564 | 0 | 2155.5113 | 21.56% | 1 | 43.11% | 0% | 0% | 5.8837 | 0 | 0 | 5.8837 | 61.2017
2007-02-17 10:00 | 2 | 17 | 10 | 48 | 1138 | 19.94 | 8579.8891 | 0 | 0 | 8579.8891 | Heating | 7570.4904 | 8.5 | 7570.4904 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1514.0981 | 30.28% | 1 | 60.56% | 0% | 0% | 0% | 25.7179 | 0 | 0 | 0 | 25.7179 | 7724.9902 | 0 | 1544.998 | 15.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.9924
2007-02-17 11:00 | 2 | 17 | 11 | 48 | 1139 | 19.94 | 6988.5379 | 0 | 0 | 6988.5379 | Heating | 6166.357 | 8.5 | 6166.357 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1233.2714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6292.201 | 0 | 1258.4402 | 12.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 12:00 | 2 | 17 | 12 | 48 | 1140 | 24.08 | 6077.1653 | 0 | 0 | 6077.1653 | Heating | 5362.2047 | 8.5 | 5362.2047 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1072.4409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5471.6375 | 0 | 1094.3275 | 10.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 13:00 | 2 | 17 | 13 | 48 | 1141 | 24.08 | 5179.1253 | 0 | 0 | 5179.1253 | Heating | 4569.8165 | 8.5 | 4569.8165 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 913.9633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4663.078 | 0 | 932.6156 | 9.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 14:00 | 2 | 17 | 14 | 48 | 1142 | 24.08 | 4738.4492 | 0 | 0 | 4738.4492 | Heating | 4180.9846 | 8.5 | 4180.9846 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 836.1969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4266.3108 | 0 | 853.2622 | 8.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 15:00 | 2 | 17 | 15 | 48 | 1143 | 24.08 | 4305.4163 | 0 | 0 | 4305.4163 | Heating | 3798.8967 | 8.5 | 3798.8967 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 759.7793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3876.4252 | 0 | 775.285 | 7.753% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 16:00 | 2 | 17 | 16 | 48 | 1144 | 21.92 | 3891.6819 | 0 | 0 | 3891.6819 | Heating | 3433.837 | 8.5 | 3433.837 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 686.7674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3503.9153 | 0 | 700.7831 | 7.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 17:00 | 2 | 17 | 17 | 48 | 1145 | 21.92 | 3690.9839 | 0 | 0 | 3690.9839 | Heating | 3256.7505 | 8.5 | 3256.7505 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 651.3501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3323.2148 | 0 | 664.643 | 6.646% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 18:00 | 2 | 17 | 18 | 48 | 1146 | 15.98 | 5354.1959 | 0 | 0 | 5354.1959 | Heating | 4724.2905 | 8.5 | 4724.2905 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 944.8581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4820.7046 | 0 | 964.1409 | 9.641% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 19:00 | 2 | 17 | 19 | 48 | 1147 | 15.08 | 5978.4271 | 0 | 0 | 5978.4271 | Heating | 5275.0827 | 8.5 | 5275.0827 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1055.0165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5382.7375 | 0 | 1076.5475 | 10.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 20:00 | 2 | 17 | 20 | 48 | 1148 | 15.08 | 1336.0828 | 0 | 0 | 1336.0828 | Heating | 1178.8966 | 8.5 | 1178.8966 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.7793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1202.9557 | 0 | 240.5911 | 2.406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 21:00 | 2 | 17 | 21 | 48 | 1149 | 14 | 1434.2795 | 0 | 0 | 1434.2795 | Heating | 1265.5408 | 8.5 | 1265.5408 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.1082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1291.3681 | 0 | 258.2736 | 2.583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 22:00 | 2 | 17 | 22 | 48 | 1150 | 12.92 | 1542.8396 | 0 | 0 | 1542.8396 | Heating | 1361.3291 | 8.5 | 1361.3291 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.2658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1389.1113 | 0 | 277.8223 | 2.778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-17 23:00 | 2 | 17 | 23 | 48 | 1151 | 12.92 | 1672.8476 | 0 | 0 | 1672.8476 | Heating | 1476.042 | 8.5 | 1476.042 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.2084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1506.1653 | 0 | 301.2331 | 3.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 | 2 | 18 | 0 | 49 | 1152 | 12.92 | 1726.8894 | 0 | 0 | 1726.8894 | Heating | 1523.726 | 8.5 | 1523.726 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 304.7452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1554.8224 | 0 | 310.9645 | 3.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 01:00 | 2 | 18 | 1 | 49 | 1153 | 12.02 | 1771.3055 | 0 | 0 | 1771.3055 | Heating | 1562.9166 | 8.5 | 1562.9166 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 312.5833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1594.8128 | 0 | 318.9626 | 3.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 02:00 | 2 | 18 | 2 | 49 | 1154 | 12.02 | 1791.2743 | 0 | 0 | 1791.2743 | Heating | 1580.5361 | 8.5 | 1580.5361 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 316.1072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1612.792 | 0 | 322.5584 | 3.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 03:00 | 2 | 18 | 3 | 49 | 1155 | 10.94 | 1753.8663 | 0 | 0 | 1753.8663 | Heating | 1547.5291 | 8.5 | 1547.5291 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 309.5058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1579.1114 | 0 | 315.8223 | 3.158% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 04:00 | 2 | 18 | 4 | 49 | 1156 | 10.04 | 1673.9605 | 0 | 0 | 1673.9605 | Heating | 1477.024 | 8.5 | 1477.024 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.4048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1507.1673 | 0 | 301.4335 | 3.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 05:00 | 2 | 18 | 5 | 49 | 1157 | 10.04 | 1647.6912 | 0 | 0 | 1647.6912 | Heating | 1453.8452 | 8.5 | 1453.8452 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1483.5155 | 0 | 296.7031 | 2.967% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 06:00 | 2 | 18 | 6 | 49 | 1158 | 8.06 | 1666.3913 | 0 | 0 | 1666.3913 | Heating | 1470.3453 | 8.5 | 1470.3453 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 294.0691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1500.3523 | 0 | 300.0705 | 3.001% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 07:00 | 2 | 18 | 7 | 49 | 1159 | 8.06 | 10453.0955 | 0 | 0 | 10453.0955 | Heating | 9223.3196 | 8.5 | 9223.3196 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1844.6639 | 36.89% | 1 | 73.79% | 0% | 0% | 0% | 40.5033 | 0 | 0 | 0 | 40.5033 | 9411.5506 | 0 | 1882.3101 | 18.82% | 1 | 37.65% | 0% | 0% | 4.308 | 0 | 0 | 4.308 | 44.8113
2007-02-18 08:00 | 2 | 18 | 8 | 49 | 1160 | 8.06 | 7903.1132 | 0 | 0 | 7903.1132 | Heating | 6973.3352 | 8.5 | 6973.3352 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1394.667 | 30% | 1 | 55.79% | 0% | 0% | 0% | 21.2894 | 0 | 0 | 0 | 21.2894 | 7115.6482 | 0 | 1423.1296 | 14.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.5639
2007-02-18 09:00 | 2 | 18 | 9 | 49 | 1161 | 12.92 | 6291.5509 | 0 | 0 | 6291.5509 | Heating | 5551.3684 | 8.5 | 5551.3684 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1110.2737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5664.6616 | 0 | 1132.9323 | 11.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 10:00 | 2 | 18 | 10 | 49 | 1162 | 15.98 | 4771.1398 | 0 | 0 | 4771.1398 | Heating | 4209.8293 | 8.5 | 4209.8293 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 841.9659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4295.7442 | 0 | 859.1488 | 8.591% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 11:00 | 2 | 18 | 11 | 49 | 1163 | 15.98 | 3934.2018 | 0 | 0 | 3934.2018 | Heating | 3471.3546 | 8.5 | 3471.3546 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 694.2709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3542.1985 | 0 | 708.4397 | 7.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 12:00 | 2 | 18 | 12 | 49 | 1164 | 21.02 | 3188.6426 | 0 | 0 | 3188.6426 | Heating | 2813.5082 | 8.5 | 2813.5082 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 562.7016 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2870.9267 | 0 | 574.1853 | 5.742% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 13:00 | 2 | 18 | 13 | 49 | 1165 | 21.92 | 2817.6771 | 5.6124 | 5.6124 | 2812.0647 | Heating | 2481.2335 | 8.5 | 2481.2335 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 496.2467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2531.871 | 0 | 506.3742 | 5.064% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 14:00 | 2 | 18 | 14 | 49 | 1166 | 21.92 | 2433.9141 | 46.1521 | 46.1521 | 2387.762 | Heating | 2106.8489 | 8.5 | 2106.8489 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.3698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2149.8458 | 0 | 429.9692 | 4.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 15:00 | 2 | 18 | 15 | 49 | 1167 | 26.96 | 2168.553 | 69.7866 | 69.7866 | 2098.7664 | Heating | 1851.8527 | 8.5 | 1851.8527 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 370.3705 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1889.6456 | 0 | 377.9291 | 3.779% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 16:00 | 2 | 18 | 16 | 49 | 1168 | 26.96 | 2084.0127 | 65.4893 | 65.4893 | 2018.5234 | Heating | 1781.05 | 8.5 | 1781.05 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 356.21 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1817.398 | 0 | 363.4796 | 3.635% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 17:00 | 2 | 18 | 17 | 49 | 1169 | 26.96 | 2096.9096 | 41.0781 | 41.0781 | 2055.8315 | Heating | 1813.969 | 8.5 | 1813.969 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.7938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1850.9888 | 0 | 370.1978 | 3.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 18:00 | 2 | 18 | 18 | 49 | 1170 | 24.08 | 2679.3797 | 9.4339 | 9.4339 | 2669.9458 | Heating | 2355.8346 | 8.5 | 2355.8346 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.1669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2403.9128 | 0 | 480.7826 | 4.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 19:00 | 2 | 18 | 19 | 49 | 1171 | 23 | 3227.0475 | 0 | 0 | 3227.0475 | Heating | 2847.3948 | 8.5 | 2847.3948 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 569.479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2905.5049 | 0 | 581.101 | 5.811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 20:00 | 2 | 18 | 20 | 49 | 1172 | 23 | 3539.6165 | 0 | 0 | 3539.6165 | Heating | 3123.1911 | 8.5 | 3123.1911 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 624.6382 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3186.9297 | 0 | 637.3859 | 6.374% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 21:00 | 2 | 18 | 21 | 49 | 1173 | 19.94 | 3954.1444 | 0 | 0 | 3954.1444 | Heating | 3488.9509 | 8.5 | 3488.9509 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 697.7902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3560.154 | 0 | 712.0308 | 7.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 22:00 | 2 | 18 | 22 | 49 | 1174 | 19.94 | 1169.518 | 0 | 0 | 1169.518 | Heating | 1031.9277 | 8.5 | 1031.9277 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.3855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1052.9874 | 0 | 210.5975 | 2.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-18 23:00 | 2 | 18 | 23 | 49 | 1175 | 19.94 | 1175.666 | 0 | 0 | 1175.666 | Heating | 1037.3524 | 8.5 | 1037.3524 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.4705 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1058.5228 | 0 | 211.7046 | 2.117% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 | 2 | 19 | 0 | 50 | 1176 | 19.94 | 1479.5466 | 0 | 0 | 1479.5466 | Heating | 1305.4823 | 8.5 | 1305.4823 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.0965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1332.1248 | 0 | 266.425 | 2.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 01:00 | 2 | 19 | 1 | 50 | 1177 | 19.04 | 1689.3431 | 0 | 0 | 1689.3431 | Heating | 1490.5969 | 8.5 | 1490.5969 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 298.1194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1521.0172 | 0 | 304.2034 | 3.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 02:00 | 2 | 19 | 2 | 50 | 1178 | 19.04 | 1908.9672 | 0 | 0 | 1908.9672 | Heating | 1684.3828 | 8.5 | 1684.3828 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.8766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1718.758 | 0 | 343.7516 | 3.438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 03:00 | 2 | 19 | 3 | 50 | 1179 | 21.92 | 2183.6157 | 0 | 0 | 2183.6157 | Heating | 1926.7198 | 8.5 | 1926.7198 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1966.0406 | 0 | 393.2081 | 3.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 04:00 | 2 | 19 | 4 | 50 | 1180 | 19.94 | 2352.2609 | 0 | 0 | 2352.2609 | Heating | 2075.5244 | 8.5 | 2075.5244 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 415.1049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2117.882 | 0 | 423.5764 | 4.236% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 05:00 | 2 | 19 | 5 | 50 | 1181 | 19.94 | 2429.3487 | 0 | 0 | 2429.3487 | Heating | 2143.543 | 8.5 | 2143.543 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 428.7086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2187.2888 | 0 | 437.4578 | 4.375% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 06:00 | 2 | 19 | 6 | 50 | 1182 | 17.96 | 2480.9478 | 0 | 0 | 2480.9478 | Heating | 2189.0716 | 8.5 | 2189.0716 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 437.8143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2233.7465 | 0 | 446.7493 | 4.467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 07:00 | 2 | 19 | 7 | 50 | 1183 | 17.96 | 13482.2921 | 0 | 0 | 13482.2921 | Heating | 11896.1401 | 8.5 | 11896.1401 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2379.228 | 47.58% | 1 | 95.17% | 0% | 0% | 0% | 72.725 | 0 | 0 | 0 | 72.725 | 12138.9184 | 0 | 2427.7837 | 24.28% | 1 | 48.56% | 0% | 0% | 7.7351 | 0 | 0 | 7.7351 | 80.4601
2007-02-19 08:00 | 2 | 19 | 8 | 50 | 1184 | 17.96 | 10798.5624 | 0 | 0 | 10798.5624 | Heating | 9528.1433 | 8.5 | 9528.1433 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1905.6287 | 38.11% | 1 | 76.23% | 0% | 0% | 0% | 43.6485 | 0 | 0 | 0 | 43.6485 | 9722.5952 | 0 | 1944.519 | 19.45% | 1 | 38.89% | 0% | 0% | 4.6425 | 0 | 0 | 4.6425 | 48.291
2007-02-19 09:00 | 2 | 19 | 9 | 50 | 1185 | 26.06 | 8392.3212 | 0 | 0 | 8392.3212 | Heating | 7404.9893 | 8.5 | 7404.9893 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1480.9979 | 30% | 1 | 59.24% | 0% | 0% | 0% | 24.4431 | 0 | 0 | 0 | 24.4431 | 7556.1115 | 0 | 1511.2223 | 15.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.7176
2007-02-19 10:00 | 2 | 19 | 10 | 50 | 1186 | 33.08 | 6073.0527 | 0 | 0 | 6073.0527 | Heating | 5358.5759 | 8.5 | 5358.5759 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1071.7152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5467.9346 | 0 | 1093.5869 | 10.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 11:00 | 2 | 19 | 11 | 50 | 1187 | 33.08 | 4597.5246 | 0 | 0 | 4597.5246 | Heating | 4056.6393 | 8.5 | 4056.6393 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 811.3279 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4139.4279 | 0 | 827.8856 | 8.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 12:00 | 2 | 19 | 12 | 50 | 1188 | 39.02 | 3442.6213 | 0 | 0 | 3442.6213 | Heating | 3037.607 | 8.5 | 3037.607 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 607.5214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3099.599 | 0 | 619.9198 | 6.199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 13:00 | 2 | 19 | 13 | 50 | 1189 | 41 | 2857.8644 | 0 | 0 | 2857.8644 | Heating | 2521.6451 | 8.5 | 2521.6451 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 504.329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2573.1072 | 0 | 514.6214 | 5.146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 14:00 | 2 | 19 | 14 | 50 | 1190 | 42.08 | 2629.5435 | 0 | 0 | 2629.5435 | Heating | 2320.1855 | 8.5 | 2320.1855 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 464.0371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2367.5362 | 0 | 473.5072 | 4.735% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 15:00 | 2 | 19 | 15 | 50 | 1191 | 37.94 | 2473.1876 | 0 | 0 | 2473.1876 | Heating | 2182.2243 | 8.5 | 2182.2243 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 436.4449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2226.7595 | 0 | 445.3519 | 4.454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 16:00 | 2 | 19 | 16 | 50 | 1192 | 37.04 | 2442.5512 | 0 | 0 | 2442.5512 | Heating | 2155.1922 | 8.5 | 2155.1922 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 431.0384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2199.1757 | 0 | 439.8351 | 4.398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 17:00 | 2 | 19 | 17 | 50 | 1193 | 37.04 | 2626.2182 | 0 | 0 | 2626.2182 | Heating | 2317.2513 | 8.5 | 2317.2513 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 463.4503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2364.5422 | 0 | 472.9084 | 4.729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 18:00 | 2 | 19 | 18 | 50 | 1194 | 37.4 | 2899.3142 | 0 | 0 | 2899.3142 | Heating | 2558.2184 | 8.5 | 2558.2184 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 511.6437 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2610.4269 | 0 | 522.0854 | 5.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 19:00 | 2 | 19 | 19 | 50 | 1195 | 35.6 | 2969.3538 | 0 | 0 | 2969.3538 | Heating | 2620.018 | 8.5 | 2620.018 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 524.0036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2673.4878 | 0 | 534.6976 | 5.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 20:00 | 2 | 19 | 20 | 50 | 1196 | 35.96 | 3151.1357 | 0 | 0 | 3151.1357 | Heating | 2780.4138 | 8.5 | 2780.4138 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 556.0828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2837.157 | 0 | 567.4314 | 5.674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 21:00 | 2 | 19 | 21 | 50 | 1197 | 35.6 | 3635.4842 | 0 | 0 | 3635.4842 | Heating | 3207.7802 | 8.5 | 3207.7802 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 641.556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3273.2451 | 0 | 654.649 | 6.546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 22:00 | 2 | 19 | 22 | 50 | 1198 | 35.06 | 1087.8725 | 0 | 0 | 1087.8725 | Heating | 959.8875 | 8.5 | 959.8875 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.9775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 979.477 | 0 | 195.8954 | 1.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-19 23:00 | 2 | 19 | 23 | 50 | 1199 | 35.06 | 945.1855 | 0 | 0 | 945.1855 | Heating | 833.9872 | 8.5 | 833.9872 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 166.7974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 851.0074 | 0 | 170.2015 | 1.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 | 2 | 20 | 0 | 51 | 1200 | 33.8 | 1018.7032 | 0 | 0 | 1018.7032 | Heating | 898.8557 | 8.5 | 898.8557 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 179.7711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 917.1997 | 0 | 183.4399 | 1.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 01:00 | 2 | 20 | 1 | 51 | 1201 | 32 | 1099.1653 | 0 | 0 | 1099.1653 | Heating | 969.8518 | 8.5 | 969.8518 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 193.9704 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 989.6447 | 0 | 197.9289 | 1.979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 02:00 | 2 | 20 | 2 | 51 | 1202 | 32 | 1162.6101 | 0 | 0 | 1162.6101 | Heating | 1025.8324 | 8.5 | 1025.8324 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 205.1665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1046.7678 | 0 | 209.3536 | 2.094% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 03:00 | 2 | 20 | 3 | 51 | 1203 | 30.2 | 1206.0399 | 0 | 0 | 1206.0399 | Heating | 1064.1528 | 8.5 | 1064.1528 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.8306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1085.8702 | 0 | 217.174 | 2.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 04:00 | 2 | 20 | 4 | 51 | 1204 | 28.94 | 1202.5388 | 0 | 0 | 1202.5388 | Heating | 1061.0637 | 8.5 | 1061.0637 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.2127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1082.718 | 0 | 216.5436 | 2.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 05:00 | 2 | 20 | 5 | 51 | 1205 | 28.94 | 1220.7245 | 0 | 0 | 1220.7245 | Heating | 1077.1099 | 8.5 | 1077.1099 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1099.0917 | 0 | 219.8183 | 2.198% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 06:00 | 2 | 20 | 6 | 51 | 1206 | 26.96 | 1231.5165 | 0 | 0 | 1231.5165 | Heating | 1086.6322 | 8.5 | 1086.6322 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.3264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1108.8084 | 0 | 221.7617 | 2.218% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 07:00 | 2 | 20 | 7 | 51 | 1207 | 26.96 | 9179.3131 | 0 | 0 | 9179.3131 | Heating | 8099.3939 | 8.5 | 8099.3939 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1619.8788 | 32.4% | 1 | 64.8% | 0% | 0% | 0% | 30.0394 | 0 | 0 | 0 | 30.0394 | 8264.6877 | 0 | 1652.9375 | 16.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.3139
2007-02-20 08:00 | 2 | 20 | 8 | 51 | 1208 | 26.96 | 6673.5791 | 0 | 0 | 6673.5791 | Heating | 5888.4522 | 8.5 | 5888.4522 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1177.6904 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6008.6246 | 0 | 1201.7249 | 12.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 09:00 | 2 | 20 | 9 | 51 | 1209 | 26.96 | 5313.5912 | 0 | 0 | 5313.5912 | Heating | 4688.4628 | 8.5 | 4688.4628 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 937.6926 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4784.1457 | 0 | 956.8291 | 9.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 10:00 | 2 | 20 | 10 | 51 | 1210 | 28.94 | 4154.6543 | 0 | 0 | 4154.6543 | Heating | 3665.8714 | 8.5 | 3665.8714 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 733.1743 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3740.6851 | 0 | 748.137 | 7.481% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 11:00 | 2 | 20 | 11 | 51 | 1211 | 28.94 | 3569.2242 | 0 | 0 | 3569.2242 | Heating | 3149.3155 | 8.5 | 3149.3155 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 629.8631 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3213.5872 | 0 | 642.7174 | 6.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 12:00 | 2 | 20 | 12 | 51 | 1212 | 28.94 | 3047.6203 | 0 | 0 | 3047.6203 | Heating | 2689.0767 | 8.5 | 2689.0767 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 537.8153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2743.9558 | 0 | 548.7912 | 5.488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 13:00 | 2 | 20 | 13 | 51 | 1213 | 28.94 | 2784.5241 | 0 | 0 | 2784.5241 | Heating | 2456.9331 | 8.5 | 2456.9331 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 491.3866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2507.0746 | 0 | 501.4149 | 5.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 14:00 | 2 | 20 | 14 | 51 | 1214 | 28.94 | 2711.5759 | 0 | 0 | 2711.5759 | Heating | 2392.5669 | 8.5 | 2392.5669 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 478.5134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2441.3948 | 0 | 488.279 | 4.883% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 15:00 | 2 | 20 | 15 | 51 | 1215 | 28.94 | 2119.5945 | 0 | 0 | 2119.5945 | Heating | 1870.2304 | 8.5 | 1870.2304 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.0461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1908.3984 | 0 | 381.6797 | 3.817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 16:00 | 2 | 20 | 16 | 51 | 1216 | 28.04 | 1827.9639 | 0 | 0 | 1827.9639 | Heating | 1612.9093 | 8.5 | 1612.9093 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 322.5819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1645.8258 | 0 | 329.1652 | 3.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 17:00 | 2 | 20 | 17 | 51 | 1217 | 26.96 | 2076.3038 | 0 | 0 | 2076.3038 | Heating | 1832.0327 | 8.5 | 1832.0327 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 366.4065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1869.4211 | 0 | 373.8842 | 3.739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 18:00 | 2 | 20 | 18 | 51 | 1218 | 26.06 | 2537.9681 | 0 | 0 | 2537.9681 | Heating | 2239.3836 | 8.5 | 2239.3836 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 447.8767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2285.0853 | 0 | 457.0171 | 4.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 19:00 | 2 | 20 | 19 | 51 | 1219 | 24.98 | 2825.063 | 0 | 0 | 2825.063 | Heating | 2492.7026 | 8.5 | 2492.7026 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 498.5405 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2543.5741 | 0 | 508.7148 | 5.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 20:00 | 2 | 20 | 20 | 51 | 1220 | 24.98 | 3214.1789 | 0 | 0 | 3214.1789 | Heating | 2836.0402 | 8.5 | 2836.0402 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 567.208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2893.9185 | 0 | 578.7837 | 5.788% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 21:00 | 2 | 20 | 21 | 51 | 1221 | 24.98 | 3580.5116 | 0 | 0 | 3580.5116 | Heating | 3159.2749 | 8.5 | 3159.2749 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 631.855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3223.7499 | 0 | 644.75 | 6.447% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 22:00 | 2 | 20 | 22 | 51 | 1222 | 24.8 | 994.4378 | 0 | 0 | 994.4378 | Heating | 877.4451 | 8.5 | 877.4451 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 895.3521 | 0 | 179.0704 | 1.791% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-20 23:00 | 2 | 20 | 23 | 51 | 1223 | 24.98 | 879.6135 | 0 | 0 | 879.6135 | Heating | 776.1296 | 8.5 | 776.1296 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.2259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 791.969 | 0 | 158.3938 | 1.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 | 2 | 21 | 0 | 52 | 1224 | 24.98 | 918.5894 | 0 | 0 | 918.5894 | Heating | 810.52 | 8.5 | 810.52 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 827.0613 | 0 | 165.4123 | 1.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 01:00 | 2 | 21 | 1 | 52 | 1225 | 24.08 | 1136.7246 | 0 | 0 | 1136.7246 | Heating | 1002.9923 | 8.5 | 1002.9923 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 200.5985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1023.4615 | 0 | 204.6923 | 2.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 02:00 | 2 | 21 | 2 | 52 | 1226 | 24.08 | 1444.3097 | 0 | 0 | 1444.3097 | Heating | 1274.3909 | 8.5 | 1274.3909 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.8782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1300.3989 | 0 | 260.0798 | 2.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 03:00 | 2 | 21 | 3 | 52 | 1227 | 24.08 | 1731.5404 | 0 | 0 | 1731.5404 | Heating | 1527.8298 | 8.5 | 1527.8298 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 305.566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1559.01 | 0 | 311.802 | 3.118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 04:00 | 2 | 21 | 4 | 52 | 1228 | 23 | 1985.7136 | 0 | 0 | 1985.7136 | Heating | 1752.1003 | 8.5 | 1752.1003 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 350.4201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1787.8574 | 0 | 357.5715 | 3.576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 05:00 | 2 | 21 | 5 | 52 | 1229 | 23 | 2193.7463 | 0 | 0 | 2193.7463 | Heating | 1935.6585 | 8.5 | 1935.6585 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.1317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1975.1618 | 0 | 395.0324 | 3.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 06:00 | 2 | 21 | 6 | 52 | 1230 | 21.92 | 2422.8841 | 0 | 0 | 2422.8841 | Heating | 2137.8389 | 8.5 | 2137.8389 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.5678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2181.4683 | 0 | 436.2937 | 4.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 07:00 | 2 | 21 | 7 | 52 | 1231 | 21.2 | 12691.6284 | 0 | 0 | 12691.6284 | Heating | 11198.4956 | 8.5 | 11198.4956 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2239.6991 | 44.79% | 1 | 89.59% | 0% | 0% | 0% | 63.2874 | 0 | 0 | 0 | 63.2874 | 11427.0363 | 0 | 2285.4073 | 22.85% | 1 | 45.71% | 0% | 0% | 6.7313 | 0 | 0 | 6.7313 | 70.0187
2007-02-21 08:00 | 2 | 21 | 8 | 52 | 1232 | 19.94 | 10161.3273 | 0 | 0 | 10161.3273 | Heating | 8965.877 | 8.5 | 8965.877 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1793.1754 | 35.86% | 1 | 71.73% | 0% | 0% | 0% | 37.9501 | 0 | 0 | 0 | 37.9501 | 9148.8541 | 0 | 1829.7708 | 18.3% | 1 | 36.6% | 0% | 0% | 4.0364 | 0 | 0 | 4.0364 | 41.9865
2007-02-21 09:00 | 2 | 21 | 9 | 52 | 1233 | 19.04 | 8865.8553 | 0 | 0 | 8865.8553 | Heating | 7822.8135 | 8.5 | 7822.8135 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1564.5627 | 31.29% | 1 | 62.58% | 0% | 0% | 0% | 27.7322 | 0 | 0 | 0 | 27.7322 | 7982.4628 | 0 | 1596.4926 | 15.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.0068
2007-02-21 10:00 | 2 | 21 | 10 | 52 | 1234 | 19.94 | 7854.5052 | 0 | 0 | 7854.5052 | Heating | 6930.4457 | 8.5 | 6930.4457 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1386.0891 | 30% | 1 | 55.44% | 0% | 0% | 0% | 20.9894 | 0 | 0 | 0 | 20.9894 | 7071.8834 | 0 | 1414.3767 | 14.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.264
2007-02-21 11:00 | 2 | 21 | 11 | 52 | 1235 | 19.94 | 7525.1747 | 0 | 0 | 7525.1747 | Heating | 6639.86 | 8.5 | 6639.86 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1327.972 | 30% | 1 | 53.12% | 0% | 0% | 0% | 19.0202 | 0 | 0 | 0 | 19.0202 | 6775.3674 | 0 | 1355.0735 | 13.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.2948
2007-02-21 12:00 | 2 | 21 | 12 | 52 | 1236 | 19.04 | 7153.3402 | 0 | 0 | 7153.3402 | Heating | 6311.7707 | 8.5 | 6311.7707 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1262.3541 | 30% | 1 | 50.49% | 0% | 0% | 0% | 16.9277 | 0 | 0 | 0 | 16.9277 | 6440.5824 | 0 | 1288.1165 | 12.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2022
2007-02-21 13:00 | 2 | 21 | 13 | 52 | 1237 | 21.02 | 6934.8358 | 0 | 0 | 6934.8358 | Heating | 6118.9728 | 8.5 | 6118.9728 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1223.7946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6243.8498 | 0 | 1248.77 | 12.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 14:00 | 2 | 21 | 14 | 52 | 1238 | 21.02 | 6740.5367 | 0 | 0 | 6740.5367 | Heating | 5947.5324 | 8.5 | 5947.5324 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1189.5065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6068.9106 | 0 | 1213.7821 | 12.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 15:00 | 2 | 21 | 15 | 52 | 1239 | 21.02 | 6659.8676 | 0 | 0 | 6659.8676 | Heating | 5876.3538 | 8.5 | 5876.3538 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1175.2708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5996.2794 | 0 | 1199.2559 | 11.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 16:00 | 2 | 21 | 16 | 52 | 1240 | 21.02 | 6533.7 | 0 | 0 | 6533.7 | Heating | 5765.0294 | 8.5 | 5765.0294 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1153.0059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5882.6831 | 0 | 1176.5366 | 11.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 17:00 | 2 | 21 | 17 | 52 | 1241 | 21.02 | 6640.5447 | 0 | 0 | 6640.5447 | Heating | 5859.3042 | 8.5 | 5859.3042 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1171.8608 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5978.8818 | 0 | 1195.7764 | 11.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 18:00 | 2 | 21 | 18 | 52 | 1242 | 19.04 | 7001.499 | 0 | 0 | 7001.499 | Heating | 6177.7932 | 8.5 | 6177.7932 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1235.5586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6303.8706 | 0 | 1260.7741 | 12.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 19:00 | 2 | 21 | 19 | 52 | 1243 | 19.04 | 7211.2033 | 0 | 0 | 7211.2033 | Heating | 6362.8264 | 8.5 | 6362.8264 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1272.5653 | 30% | 1 | 50.9% | 0% | 0% | 0% | 17.2443 | 0 | 0 | 0 | 17.2443 | 6492.68 | 0 | 1298.536 | 12.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.5188
2007-02-21 20:00 | 2 | 21 | 20 | 52 | 1244 | 19.04 | 7522.3139 | 0 | 0 | 7522.3139 | Heating | 6637.3358 | 8.5 | 6637.3358 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1327.4672 | 30% | 1 | 53.1% | 0% | 0% | 0% | 19.0036 | 0 | 0 | 0 | 19.0036 | 6772.7917 | 0 | 1354.5583 | 13.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.2781
2007-02-21 21:00 | 2 | 21 | 21 | 52 | 1245 | 19.04 | 8137.446 | 0 | 0 | 8137.446 | Heating | 7180.0994 | 8.5 | 7180.0994 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1436.0199 | 30% | 1 | 57.44% | 0% | 0% | 0% | 22.7693 | 0 | 0 | 0 | 22.7693 | 7326.632 | 0 | 1465.3264 | 14.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.0439
2007-02-21 22:00 | 2 | 21 | 22 | 52 | 1246 | 19.94 | 2571.7703 | 0 | 0 | 2571.7703 | Heating | 2269.2091 | 8.5 | 2269.2091 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 453.8418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2315.5195 | 0 | 463.1039 | 4.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-21 23:00 | 2 | 21 | 23 | 52 | 1247 | 19.94 | 2728.0171 | 0 | 0 | 2728.0171 | Heating | 2407.0739 | 8.5 | 2407.0739 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 481.4148 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2456.1979 | 0 | 491.2396 | 4.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 | 2 | 22 | 0 | 53 | 1248 | 21.92 | 3041.8659 | 0 | 0 | 3041.8659 | Heating | 2683.9993 | 8.5 | 2683.9993 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 536.7999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2738.7748 | 0 | 547.755 | 5.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 01:00 | 2 | 22 | 1 | 53 | 1249 | 21.92 | 3254.8878 | 0 | 0 | 3254.8878 | Heating | 2871.9599 | 8.5 | 2871.9599 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 574.392 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2930.5713 | 0 | 586.1143 | 5.861% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 02:00 | 2 | 22 | 2 | 53 | 1250 | 21.92 | 3372.1883 | 0 | 0 | 3372.1883 | Heating | 2975.4603 | 8.5 | 2975.4603 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 595.0921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3036.1839 | 0 | 607.2368 | 6.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 03:00 | 2 | 22 | 3 | 53 | 1251 | 21.2 | 3515.895 | 0 | 0 | 3515.895 | Heating | 3102.2603 | 8.5 | 3102.2603 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 620.4521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3165.5717 | 0 | 633.1143 | 6.331% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 04:00 | 2 | 22 | 4 | 53 | 1252 | 21.02 | 3472.0559 | 0 | 0 | 3472.0559 | Heating | 3063.5788 | 8.5 | 3063.5788 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 612.7158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3126.1008 | 0 | 625.2202 | 6.252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 05:00 | 2 | 22 | 5 | 53 | 1253 | 21.02 | 3436.1709 | 0 | 0 | 3436.1709 | Heating | 3031.9155 | 8.5 | 3031.9155 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 606.3831 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3093.7913 | 0 | 618.7583 | 6.188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 06:00 | 2 | 22 | 6 | 53 | 1254 | 19.94 | 3404.8302 | 0 | 0 | 3404.8302 | Heating | 3004.2619 | 8.5 | 3004.2619 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 600.8524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3065.5734 | 0 | 613.1147 | 6.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 07:00 | 2 | 22 | 7 | 53 | 1255 | 19.4 | 15229.5754 | 0 | 0 | 15229.5754 | Heating | 13437.8607 | 8.5 | 13437.8607 | 0 | 2.8998 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2687.5721 | 53.75% | 2 | 53.75% | 53.75% | 0% | 0% | 19.5452 | 19.5452 | 0 | 0 | 39.0904 | 13712.1027 | 0 | 2742.4205 | 27.42% | 1 | 54.85% | 0% | 0% | 10.2374 | 0 | 0 | 10.2374 | 49.3278
2007-02-22 08:00 | 2 | 22 | 8 | 53 | 1256 | 17.96 | 12269.3903 | 0 | 0 | 12269.3903 | Heating | 10825.9326 | 8.5 | 10825.9326 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2165.1865 | 43.3% | 1 | 86.61% | 0% | 0% | 0% | 58.5491 | 0 | 0 | 0 | 58.5491 | 11046.87 | 0 | 2209.374 | 22.09% | 1 | 44.19% | 0% | 0% | 6.2273 | 0 | 0 | 6.2273 | 64.7764
2007-02-22 09:00 | 2 | 22 | 9 | 53 | 1257 | 21.2 | 9919.6666 | 0 | 0 | 9919.6666 | Heating | 8752.647 | 8.5 | 8752.647 | 0 | 2.944 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1750.5294 | 35.01% | 1 | 70.02% | 0% | 0% | 0% | 35.9063 | 0 | 0 | 0 | 35.9063 | 8931.2724 | 0 | 1786.2545 | 17.86% | 1 | 35.73% | 0% | 0% | 3.819 | 0 | 0 | 3.819 | 39.7253
2007-02-22 10:00 | 2 | 22 | 10 | 53 | 1258 | 26.06 | 7644.8915 | 0 | 0 | 7644.8915 | Heating | 6745.4925 | 8.5 | 6745.4925 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1349.0985 | 30% | 1 | 53.96% | 0% | 0% | 0% | 19.7234 | 0 | 0 | 0 | 19.7234 | 6883.1556 | 0 | 1376.6311 | 13.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.9979
2007-02-22 11:00 | 2 | 22 | 11 | 53 | 1259 | 26.06 | 6319.4864 | 0 | 0 | 6319.4864 | Heating | 5576.0174 | 8.5 | 5576.0174 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1115.2035 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5689.8137 | 0 | 1137.9627 | 11.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 12:00 | 2 | 22 | 12 | 53 | 1260 | 30.02 | 5186.9818 | 0 | 0 | 5186.9818 | Heating | 4576.7487 | 8.5 | 4576.7487 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 915.3497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4670.1517 | 0 | 934.0303 | 9.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 13:00 | 2 | 22 | 13 | 53 | 1261 | 33.08 | 4484.6746 | 0 | 0 | 4484.6746 | Heating | 3957.0659 | 8.5 | 3957.0659 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 791.4132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4037.8223 | 0 | 807.5645 | 8.076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 14:00 | 2 | 22 | 14 | 53 | 1262 | 33.08 | 3918.3425 | 0 | 0 | 3918.3425 | Heating | 3457.361 | 8.5 | 3457.361 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 691.4722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3527.9194 | 0 | 705.5839 | 7.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 15:00 | 2 | 22 | 15 | 53 | 1263 | 35.06 | 3555.1079 | 0 | 0 | 3555.1079 | Heating | 3136.8599 | 8.5 | 3136.8599 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 627.372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3200.8774 | 0 | 640.1755 | 6.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 16:00 | 2 | 22 | 16 | 53 | 1264 | 35.06 | 3232.1168 | 0 | 0 | 3232.1168 | Heating | 2851.8678 | 8.5 | 2851.8678 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 570.3736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2910.0692 | 0 | 582.0138 | 5.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 17:00 | 2 | 22 | 17 | 53 | 1265 | 35.06 | 3070.7132 | 0 | 0 | 3070.7132 | Heating | 2709.4528 | 8.5 | 2709.4528 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 541.8906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2764.7478 | 0 | 552.9496 | 5.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 18:00 | 2 | 22 | 18 | 53 | 1266 | 33.98 | 3088.1112 | 0 | 0 | 3088.1112 | Heating | 2724.804 | 8.5 | 2724.804 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 544.9608 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2780.4123 | 0 | 556.0825 | 5.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 19:00 | 2 | 22 | 19 | 53 | 1267 | 33.08 | 3270.5343 | 0 | 0 | 3270.5343 | Heating | 2885.7655 | 8.5 | 2885.7655 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 577.1531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2944.6587 | 0 | 588.9317 | 5.889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 20:00 | 2 | 22 | 20 | 53 | 1268 | 33.08 | 3360.6627 | 0 | 0 | 3360.6627 | Heating | 2965.2906 | 8.5 | 2965.2906 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 593.0581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3025.8067 | 0 | 605.1613 | 6.052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 21:00 | 2 | 22 | 21 | 53 | 1269 | 33.08 | 3492.3207 | 0 | 0 | 3492.3207 | Heating | 3081.4595 | 8.5 | 3081.4595 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 616.2919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3144.3464 | 0 | 628.8693 | 6.289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 22:00 | 2 | 22 | 22 | 53 | 1270 | 33.98 | 1007.4861 | 0 | 0 | 1007.4861 | Heating | 888.9583 | 8.5 | 888.9583 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.7917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 907.1003 | 0 | 181.4201 | 1.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-22 23:00 | 2 | 22 | 23 | 53 | 1271 | 33.98 | 870.6016 | 0 | 0 | 870.6016 | Heating | 768.1778 | 8.5 | 768.1778 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 153.6356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 783.8549 | 0 | 156.771 | 1.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 | 2 | 23 | 0 | 54 | 1272 | 33.98 | 961.9287 | 0 | 0 | 961.9287 | Heating | 848.7606 | 8.5 | 848.7606 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.7521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 866.0822 | 0 | 173.2164 | 1.732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 01:00 | 2 | 23 | 1 | 54 | 1273 | 33.98 | 1041.1474 | 0 | 0 | 1041.1474 | Heating | 918.6595 | 8.5 | 918.6595 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.7319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 937.4077 | 0 | 187.4815 | 1.875% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 02:00 | 2 | 23 | 2 | 54 | 1274 | 33.98 | 1056.6028 | 0 | 0 | 1056.6028 | Heating | 932.2966 | 8.5 | 932.2966 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 186.4593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 951.323 | 0 | 190.2646 | 1.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 03:00 | 2 | 23 | 3 | 54 | 1275 | 33.8 | 1067.5955 | 0 | 0 | 1067.5955 | Heating | 941.996 | 8.5 | 941.996 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.3992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 961.2204 | 0 | 192.2441 | 1.922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 04:00 | 2 | 23 | 4 | 54 | 1276 | 33.08 | 1083.4722 | 0 | 0 | 1083.4722 | Heating | 956.0049 | 8.5 | 956.0049 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 975.5152 | 0 | 195.103 | 1.951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 05:00 | 2 | 23 | 5 | 54 | 1277 | 33.08 | 1081.0991 | 0 | 0 | 1081.0991 | Heating | 953.911 | 8.5 | 953.911 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.7822 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 973.3786 | 0 | 194.6757 | 1.947% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 06:00 | 2 | 23 | 6 | 54 | 1278 | 32 | 1081.1066 | 0 | 0 | 1081.1066 | Heating | 953.9176 | 8.5 | 953.9176 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.7835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 973.3853 | 0 | 194.6771 | 1.947% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 07:00 | 2 | 23 | 7 | 54 | 1279 | 33.08 | 7760.7272 | 0 | 0 | 7760.7272 | Heating | 6847.7004 | 8.5 | 6847.7004 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1369.5401 | 30% | 1 | 54.78% | 0% | 0% | 0% | 20.4175 | 0 | 0 | 0 | 20.4175 | 6987.4494 | 0 | 1397.4899 | 13.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.6921
2007-02-23 08:00 | 2 | 23 | 8 | 54 | 1280 | 33.08 | 5757.5683 | 0 | 0 | 5757.5683 | Heating | 5080.2073 | 8.5 | 5080.2073 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1016.0415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5183.885 | 0 | 1036.777 | 10.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 09:00 | 2 | 23 | 9 | 54 | 1281 | 33.98 | 4793.0431 | 0 | 0 | 4793.0431 | Heating | 4229.1557 | 8.5 | 4229.1557 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 845.8311 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4315.465 | 0 | 863.093 | 8.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 10:00 | 2 | 23 | 10 | 54 | 1282 | 33.98 | 3802.4663 | 0 | 0 | 3802.4663 | Heating | 3355.1173 | 8.5 | 3355.1173 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 671.0235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3423.5891 | 0 | 684.7178 | 6.847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 11:00 | 2 | 23 | 11 | 54 | 1283 | 33.98 | 3037.9384 | 0 | 0 | 3037.9384 | Heating | 2680.5339 | 8.5 | 2680.5339 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 536.1068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2735.2386 | 0 | 547.0477 | 5.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 12:00 | 2 | 23 | 12 | 54 | 1284 | 35.06 | 2845.1472 | 0 | 0 | 2845.1472 | Heating | 2510.424 | 8.5 | 2510.424 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 502.0848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2561.6572 | 0 | 512.3314 | 5.123% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 13:00 | 2 | 23 | 13 | 54 | 1285 | 33.8 | 2807.1521 | 0 | 0 | 2807.1521 | Heating | 2476.8989 | 8.5 | 2476.8989 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 495.3798 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2527.4479 | 0 | 505.4896 | 5.055% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 14:00 | 2 | 23 | 14 | 54 | 1286 | 33.98 | 2618.2831 | 0 | 0 | 2618.2831 | Heating | 2310.2498 | 8.5 | 2310.2498 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 462.05 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2357.3978 | 0 | 471.4796 | 4.715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 15:00 | 2 | 23 | 15 | 54 | 1287 | 35.6 | 2485.2366 | 0 | 0 | 2485.2366 | Heating | 2192.8558 | 8.5 | 2192.8558 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.5712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2237.608 | 0 | 447.5216 | 4.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 16:00 | 2 | 23 | 16 | 54 | 1288 | 35.6 | 2471.5969 | 0 | 0 | 2471.5969 | Heating | 2180.8208 | 8.5 | 2180.8208 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 436.1642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2225.3274 | 0 | 445.0655 | 4.451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 17:00 | 2 | 23 | 17 | 54 | 1289 | 35.96 | 2695.4714 | 0 | 0 | 2695.4714 | Heating | 2378.3571 | 8.5 | 2378.3571 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 475.6714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2426.895 | 0 | 485.379 | 4.854% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 18:00 | 2 | 23 | 18 | 54 | 1290 | 35.96 | 3009.7288 | 0 | 0 | 3009.7288 | Heating | 2655.643 | 8.5 | 2655.643 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 531.1286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2709.8398 | 0 | 541.968 | 5.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 19:00 | 2 | 23 | 19 | 54 | 1291 | 35.96 | 3394.1812 | 0 | 0 | 3394.1812 | Heating | 2994.8658 | 8.5 | 2994.8658 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 598.9732 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3055.9855 | 0 | 611.1971 | 6.112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 20:00 | 2 | 23 | 20 | 54 | 1292 | 35.96 | 4007.8665 | 0 | 0 | 4007.8665 | Heating | 3536.3528 | 8.5 | 3536.3528 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 707.2706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3608.5233 | 0 | 721.7047 | 7.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 21:00 | 2 | 23 | 21 | 54 | 1293 | 35.96 | 4551.1893 | 0 | 0 | 4551.1893 | Heating | 4015.7552 | 8.5 | 4015.7552 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 803.151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4097.7094 | 0 | 819.5419 | 8.195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 22:00 | 2 | 23 | 22 | 54 | 1294 | 35.96 | 5101.4791 | 0 | 0 | 5101.4791 | Heating | 4501.3051 | 8.5 | 4501.3051 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 900.261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4593.1684 | 0 | 918.6337 | 9.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-23 23:00 | 2 | 23 | 23 | 54 | 1295 | 35.96 | 1405.2211 | 0 | 0 | 1405.2211 | Heating | 1239.901 | 8.5 | 1239.901 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.9802 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1265.2051 | 0 | 253.041 | 2.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 | 2 | 24 | 0 | 55 | 1296 | 35.06 | 1549.2666 | 0 | 0 | 1549.2666 | Heating | 1367 | 8.5 | 1367 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 273.4 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1394.8979 | 0 | 278.9796 | 2.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 01:00 | 2 | 24 | 1 | 55 | 1297 | 33.98 | 1604.6018 | 0 | 0 | 1604.6018 | Heating | 1415.8251 | 8.5 | 1415.8251 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 283.165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1444.7195 | 0 | 288.9439 | 2.889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 02:00 | 2 | 24 | 2 | 55 | 1298 | 33.98 | 1648.2573 | 0 | 0 | 1648.2573 | Heating | 1454.3446 | 8.5 | 1454.3446 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.8689 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1484.0252 | 0 | 296.805 | 2.968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 03:00 | 2 | 24 | 3 | 55 | 1299 | 33.8 | 1839.7136 | 0 | 0 | 1839.7136 | Heating | 1623.2767 | 8.5 | 1623.2767 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.6553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1656.4048 | 0 | 331.281 | 3.313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 04:00 | 2 | 24 | 4 | 55 | 1300 | 33.8 | 1943.9152 | 0 | 0 | 1943.9152 | Heating | 1715.2193 | 8.5 | 1715.2193 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.0439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1750.2238 | 0 | 350.0448 | 3.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 05:00 | 2 | 24 | 5 | 55 | 1301 | 33.08 | 1962.5616 | 0 | 0 | 1962.5616 | Heating | 1731.672 | 8.5 | 1731.672 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.3344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1767.0123 | 0 | 353.4025 | 3.534% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 06:00 | 2 | 24 | 6 | 55 | 1302 | 32 | 2027.057 | 0 | 0 | 2027.057 | Heating | 1788.5797 | 8.5 | 1788.5797 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 357.7159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1825.0813 | 0 | 365.0163 | 3.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 07:00 | 2 | 24 | 7 | 55 | 1303 | 32 | 2150.6784 | 0 | 0 | 2150.6784 | Heating | 1897.6574 | 8.5 | 1897.6574 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.5315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1936.3851 | 0 | 387.277 | 3.873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 08:00 | 2 | 24 | 8 | 55 | 1304 | 33.08 | 2128.3578 | 0 | 0 | 2128.3578 | Heating | 1877.9627 | 8.5 | 1877.9627 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 375.5925 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1916.2885 | 0 | 383.2577 | 3.833% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 09:00 | 2 | 24 | 9 | 55 | 1305 | 33.8 | 10825.3495 | 0 | 0 | 10825.3495 | Heating | 9551.779 | 8.5 | 9551.779 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1910.3558 | 38.21% | 1 | 76.41% | 0% | 0% | 0% | 43.8979 | 0 | 0 | 0 | 43.8979 | 9746.7133 | 0 | 1949.3427 | 19.49% | 1 | 38.99% | 0% | 0% | 4.669 | 0 | 0 | 4.669 | 48.5669
2007-02-24 10:00 | 2 | 24 | 10 | 55 | 1306 | 35.6 | 8135.1006 | 0 | 0 | 8135.1006 | Heating | 7178.03 | 8.5 | 7178.03 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1435.606 | 30% | 1 | 57.42% | 0% | 0% | 0% | 22.7542 | 0 | 0 | 0 | 22.7542 | 7324.5204 | 0 | 1464.9041 | 14.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.0288
2007-02-24 11:00 | 2 | 24 | 11 | 55 | 1307 | 35.06 | 6902.8331 | 0 | 0 | 6902.8331 | Heating | 6090.7351 | 8.5 | 6090.7351 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1218.147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6215.0358 | 0 | 1243.0072 | 12.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 12:00 | 2 | 24 | 12 | 55 | 1308 | 37.04 | 6163.7678 | 0 | 0 | 6163.7678 | Heating | 5438.6186 | 8.5 | 5438.6186 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1087.7237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5549.6108 | 0 | 1109.9222 | 11.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 13:00 | 2 | 24 | 13 | 55 | 1309 | 37.94 | 5409.9292 | 0 | 0 | 5409.9292 | Heating | 4773.467 | 8.5 | 4773.467 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 954.6934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4870.8846 | 0 | 974.1769 | 9.742% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 14:00 | 2 | 24 | 14 | 55 | 1310 | 37.94 | 5055.1029 | 0 | 0 | 5055.1029 | Heating | 4460.3849 | 8.5 | 4460.3849 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 892.077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4551.4132 | 0 | 910.2826 | 9.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 15:00 | 2 | 24 | 15 | 55 | 1311 | 35.96 | 4806.5908 | 0 | 0 | 4806.5908 | Heating | 4241.1095 | 8.5 | 4241.1095 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 848.2219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4327.6628 | 0 | 865.5326 | 8.655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 16:00 | 2 | 24 | 16 | 55 | 1312 | 35.06 | 4779.6836 | 0 | 0 | 4779.6836 | Heating | 4217.3679 | 8.5 | 4217.3679 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 843.4736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4303.4366 | 0 | 860.6873 | 8.607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 17:00 | 2 | 24 | 17 | 55 | 1313 | 35.06 | 4847.4341 | 0 | 0 | 4847.4341 | Heating | 4277.1477 | 8.5 | 4277.1477 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 855.4295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4364.4364 | 0 | 872.8873 | 8.729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 18:00 | 2 | 24 | 18 | 55 | 1314 | 33.8 | 6927.614 | 0 | 0 | 6927.614 | Heating | 6112.6006 | 8.5 | 6112.6006 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1222.5201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6237.3475 | 0 | 1247.4695 | 12.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 19:00 | 2 | 24 | 19 | 55 | 1315 | 32 | 7670.3738 | 0 | 0 | 7670.3738 | Heating | 6767.9769 | 8.5 | 6767.9769 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1353.5954 | 30% | 1 | 54.14% | 0% | 0% | 0% | 19.8749 | 0 | 0 | 0 | 19.8749 | 6906.0989 | 0 | 1381.2198 | 13.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.1495
2007-02-24 20:00 | 2 | 24 | 20 | 55 | 1316 | 32 | 1968.0893 | 0 | 0 | 1968.0893 | Heating | 1736.5494 | 8.5 | 1736.5494 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 347.3099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1771.9892 | 0 | 354.3978 | 3.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 21:00 | 2 | 24 | 21 | 55 | 1317 | 32 | 2115.2578 | 0 | 0 | 2115.2578 | Heating | 1866.404 | 8.5 | 1866.404 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.2808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1904.4938 | 0 | 380.8988 | 3.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 22:00 | 2 | 24 | 22 | 55 | 1318 | 32 | 2209.6317 | 0 | 0 | 2209.6317 | Heating | 1949.6751 | 8.5 | 1949.6751 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 389.935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1989.4644 | 0 | 397.8929 | 3.979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-24 23:00 | 2 | 24 | 23 | 55 | 1319 | 32 | 2265.0147 | 0 | 0 | 2265.0147 | Heating | 1998.5423 | 8.5 | 1998.5423 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 399.7085 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2039.3289 | 0 | 407.8658 | 4.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 | 2 | 25 | 0 | 56 | 1320 | 32 | 2321.9431 | 0 | 0 | 2321.9431 | Heating | 2048.7733 | 8.5 | 2048.7733 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.7547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2090.585 | 0 | 418.117 | 4.181% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 01:00 | 2 | 25 | 1 | 56 | 1321 | 30.92 | 2440.6079 | 0 | 0 | 2440.6079 | Heating | 2153.4775 | 8.5 | 2153.4775 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 430.6955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2197.4261 | 0 | 439.4852 | 4.395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 02:00 | 2 | 25 | 2 | 56 | 1322 | 30.92 | 2514.4646 | 0 | 0 | 2514.4646 | Heating | 2218.6452 | 8.5 | 2218.6452 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 443.729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2263.9237 | 0 | 452.7847 | 4.528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 03:00 | 2 | 25 | 3 | 56 | 1323 | 28.04 | 2591.8247 | 0 | 0 | 2591.8247 | Heating | 2286.9042 | 8.5 | 2286.9042 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 457.3808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2333.5757 | 0 | 466.7151 | 4.667% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 04:00 | 2 | 25 | 4 | 56 | 1324 | 24.98 | 2760.0025 | 0 | 0 | 2760.0025 | Heating | 2435.2963 | 8.5 | 2435.2963 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 487.0593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2484.9962 | 0 | 496.9992 | 4.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 05:00 | 2 | 25 | 5 | 56 | 1325 | 24.98 | 2816.0696 | 0 | 0 | 2816.0696 | Heating | 2484.7673 | 8.5 | 2484.7673 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 496.9535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2535.4768 | 0 | 507.0954 | 5.071% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 06:00 | 2 | 25 | 6 | 56 | 1326 | 21.92 | 2929.4413 | 0 | 0 | 2929.4413 | Heating | 2584.8011 | 8.5 | 2584.8011 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 516.9602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2637.5522 | 0 | 527.5104 | 5.275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 07:00 | 2 | 25 | 7 | 56 | 1327 | 21.92 | 14310.5189 | 0 | 0 | 14310.5189 | Heating | 12626.9285 | 8.5 | 12626.9285 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2525.3857 | 50.51% | 2 | 50.51% | 50.51% | 0% | 0% | 16.9381 | 16.9381 | 0 | 0 | 33.8763 | 12884.6209 | 0 | 2576.9242 | 25.77% | 1 | 51.54% | 0% | 0% | 8.8719 | 0 | 0 | 8.8719 | 42.7482
2007-02-25 08:00 | 2 | 25 | 8 | 56 | 1328 | 21.92 | 11363.4479 | 0 | 0 | 11363.4479 | Heating | 10026.5717 | 8.5 | 10026.5717 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2005.3143 | 40.11% | 1 | 80.21% | 0% | 0% | 0% | 49.0796 | 0 | 0 | 0 | 49.0796 | 10231.1956 | 0 | 2046.2391 | 20.46% | 1 | 40.92% | 0% | 0% | 5.2201 | 0 | 0 | 5.2201 | 54.2997
2007-02-25 09:00 | 2 | 25 | 9 | 56 | 1329 | 33.08 | 9048.4686 | 0 | 0 | 9048.4686 | Heating | 7983.9429 | 8.5 | 7983.9429 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1596.7886 | 31.94% | 1 | 63.87% | 0% | 0% | 0% | 29.0636 | 0 | 0 | 0 | 29.0636 | 8146.8805 | 0 | 1629.3761 | 16.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.3382
2007-02-25 10:00 | 2 | 25 | 10 | 56 | 1330 | 37.04 | 7125.064 | 0 | 0 | 7125.064 | Heating | 6286.8212 | 8.5 | 6286.8212 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1257.3642 | 30% | 1 | 50.29% | 0% | 0% | 0% | 16.7742 | 0 | 0 | 0 | 16.7742 | 6415.1236 | 0 | 1283.0247 | 12.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.0487
2007-02-25 11:00 | 2 | 25 | 11 | 56 | 1331 | 37.04 | 5820.2966 | 0 | 0 | 5820.2966 | Heating | 5135.5558 | 8.5 | 5135.5558 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1027.1112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5240.363 | 0 | 1048.0726 | 10.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 12:00 | 2 | 25 | 12 | 56 | 1332 | 39.02 | 4942.0488 | 0 | 0 | 4942.0488 | Heating | 4360.6313 | 8.5 | 4360.6313 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 872.1263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4449.6238 | 0 | 889.9248 | 8.899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 13:00 | 2 | 25 | 13 | 56 | 1333 | 39.02 | 4539.9276 | 0 | 0 | 4539.9276 | Heating | 4005.8185 | 8.5 | 4005.8185 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 801.1637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4087.5699 | 0 | 817.514 | 8.175% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 14:00 | 2 | 25 | 14 | 56 | 1334 | 39.02 | 4376.2208 | 0 | 0 | 4376.2208 | Heating | 3861.3713 | 8.5 | 3861.3713 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 772.2743 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3940.1748 | 0 | 788.035 | 7.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 15:00 | 2 | 25 | 15 | 56 | 1335 | 39.92 | 4164.322 | 0 | 0 | 4164.322 | Heating | 3674.4018 | 8.5 | 3674.4018 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 734.8804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3749.3896 | 0 | 749.8779 | 7.499% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 16:00 | 2 | 25 | 16 | 56 | 1336 | 39.02 | 4081.312 | 0 | 0 | 4081.312 | Heating | 3601.1577 | 8.5 | 3601.1577 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 720.2315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3674.6507 | 0 | 734.9301 | 7.349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 17:00 | 2 | 25 | 17 | 56 | 1337 | 39.02 | 4319.1352 | 0 | 0 | 4319.1352 | Heating | 3811.0016 | 8.5 | 3811.0016 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 762.2003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3888.7772 | 0 | 777.7554 | 7.778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 18:00 | 2 | 25 | 18 | 56 | 1338 | 37.94 | 4704.9543 | 0 | 0 | 4704.9543 | Heating | 4151.4303 | 8.5 | 4151.4303 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 830.2861 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4236.1533 | 0 | 847.2307 | 8.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 19:00 | 2 | 25 | 19 | 56 | 1339 | 37.04 | 5074.9937 | 0 | 0 | 5074.9937 | Heating | 4477.9356 | 8.5 | 4477.9356 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 895.5871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4569.3221 | 0 | 913.8644 | 9.139% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 20:00 | 2 | 25 | 20 | 56 | 1340 | 37.04 | 5490.5866 | 0 | 0 | 5490.5866 | Heating | 4844.6353 | 8.5 | 4844.6353 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 968.9271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4943.5054 | 0 | 988.7011 | 9.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 21:00 | 2 | 25 | 21 | 56 | 1341 | 35.06 | 5986.836 | 0 | 0 | 5986.836 | Heating | 5282.5024 | 8.5 | 5282.5024 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1056.5005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5390.3085 | 0 | 1078.0617 | 10.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 22:00 | 2 | 25 | 22 | 56 | 1342 | 33.08 | 1855.4421 | 0 | 0 | 1855.4421 | Heating | 1637.1548 | 8.5 | 1637.1548 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 327.431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1670.5661 | 0 | 334.1132 | 3.341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-25 23:00 | 2 | 25 | 23 | 56 | 1343 | 33.08 | 1862.0095 | 0 | 0 | 1862.0095 | Heating | 1642.9496 | 8.5 | 1642.9496 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.5899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1676.4792 | 0 | 335.2958 | 3.353% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 | 2 | 26 | 0 | 57 | 1344 | 33.08 | 2275.3215 | 0 | 0 | 2275.3215 | Heating | 2007.6366 | 8.5 | 2007.6366 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 401.5273 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2048.6088 | 0 | 409.7218 | 4.097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 01:00 | 2 | 26 | 1 | 57 | 1345 | 32 | 2490.8704 | 0 | 0 | 2490.8704 | Heating | 2197.8268 | 8.5 | 2197.8268 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 439.5654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2242.6804 | 0 | 448.5361 | 4.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 02:00 | 2 | 26 | 2 | 57 | 1346 | 32 | 2688.9867 | 0 | 0 | 2688.9867 | Heating | 2372.6354 | 8.5 | 2372.6354 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 474.5271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2421.0565 | 0 | 484.2113 | 4.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 03:00 | 2 | 26 | 3 | 57 | 1347 | 30.02 | 2876.384 | 0 | 0 | 2876.384 | Heating | 2537.9859 | 8.5 | 2537.9859 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 507.5972 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2589.7816 | 0 | 517.9563 | 5.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 04:00 | 2 | 26 | 4 | 57 | 1348 | 28.04 | 2939.3091 | 0 | 0 | 2939.3091 | Heating | 2593.508 | 8.5 | 2593.508 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 518.7016 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2646.4368 | 0 | 529.2874 | 5.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 05:00 | 2 | 26 | 5 | 57 | 1349 | 28.04 | 2887.5495 | 0 | 0 | 2887.5495 | Heating | 2547.8378 | 8.5 | 2547.8378 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 509.5676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2599.8344 | 0 | 519.9669 | 5.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 06:00 | 2 | 26 | 6 | 57 | 1350 | 26.06 | 2867.5537 | 0 | 0 | 2867.5537 | Heating | 2530.1945 | 8.5 | 2530.1945 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 506.0389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2581.8311 | 0 | 516.3662 | 5.164% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 07:00 | 2 | 26 | 7 | 57 | 1351 | 24.98 | 14555.0251 | 0 | 0 | 14555.0251 | Heating | 12842.6692 | 8.5 | 12842.6692 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2568.5338 | 51.37% | 2 | 51.37% | 51.37% | 0% | 0% | 17.6112 | 17.6112 | 0 | 0 | 35.2223 | 13104.7645 | 0 | 2620.9529 | 26.21% | 1 | 52.42% | 0% | 0% | 9.2244 | 0 | 0 | 9.2244 | 44.4467
2007-02-26 08:00 | 2 | 26 | 8 | 57 | 1352 | 24.98 | 11946.7614 | 0 | 0 | 11946.7614 | Heating | 10541.2601 | 8.5 | 10541.2601 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2108.252 | 42.17% | 1 | 84.33% | 0% | 0% | 0% | 55.0684 | 0 | 0 | 0 | 55.0684 | 10756.3879 | 0 | 2151.2776 | 21.51% | 1 | 43.03% | 0% | 0% | 5.8571 | 0 | 0 | 5.8571 | 60.9256
2007-02-26 09:00 | 2 | 26 | 9 | 57 | 1353 | 32 | 9341.1414 | 0 | 0 | 9341.1414 | Heating | 8242.1836 | 8.5 | 8242.1836 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1648.4367 | 32.97% | 1 | 65.94% | 0% | 0% | 0% | 31.2714 | 0 | 0 | 0 | 31.2714 | 8410.3914 | 0 | 1682.0783 | 16.82% | 1 | 33.64% | 0% | 0% | 3.326 | 0 | 0 | 3.326 | 34.5974
2007-02-26 10:00 | 2 | 26 | 10 | 57 | 1354 | 35.96 | 7128.1624 | 0 | 0 | 7128.1624 | Heating | 6289.555 | 8.5 | 6289.555 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1257.911 | 30% | 1 | 50.32% | 0% | 0% | 0% | 16.791 | 0 | 0 | 0 | 16.791 | 6417.9133 | 0 | 1283.5827 | 12.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.0655
2007-02-26 11:00 | 2 | 26 | 11 | 57 | 1355 | 35.96 | 5733.347 | 0 | 0 | 5733.347 | Heating | 5058.8356 | 8.5 | 5058.8356 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1011.7671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5162.0771 | 0 | 1032.4154 | 10.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 12:00 | 2 | 26 | 12 | 57 | 1356 | 41 | 4614.8115 | 0 | 0 | 4614.8115 | Heating | 4071.8925 | 8.5 | 4071.8925 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 814.3785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4154.9924 | 0 | 830.9985 | 8.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 13:00 | 2 | 26 | 13 | 57 | 1357 | 44.06 | 4213.4078 | 0 | 0 | 4213.4078 | Heating | 3717.7127 | 8.5 | 3717.7127 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 743.5425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3793.5844 | 0 | 758.7169 | 7.587% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 14:00 | 2 | 26 | 14 | 57 | 1358 | 44.06 | 4047.2092 | 0 | 0 | 4047.2092 | Heating | 3571.067 | 8.5 | 3571.067 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 714.2134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3643.9459 | 0 | 728.7892 | 7.288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 15:00 | 2 | 26 | 15 | 57 | 1359 | 42.98 | 3806.676 | 3.4998 | 3.4998 | 3803.1761 | Heating | 3355.7437 | 8.5 | 3355.7437 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 671.1487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3424.2282 | 0 | 684.8456 | 6.848% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 16:00 | 2 | 26 | 16 | 57 | 1360 | 42.98 | 3777.2144 | 1.4395 | 1.4395 | 3775.775 | Heating | 3331.5661 | 8.5 | 3331.5661 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 666.3132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3399.5573 | 0 | 679.9115 | 6.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 17:00 | 2 | 26 | 17 | 57 | 1361 | 42.98 | 3915.1941 | 0 | 0 | 3915.1941 | Heating | 3454.583 | 8.5 | 3454.583 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 690.9166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3525.0847 | 0 | 705.0169 | 7.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 18:00 | 2 | 26 | 18 | 57 | 1362 | 39.02 | 4305.9615 | 0 | 0 | 4305.9615 | Heating | 3799.3778 | 8.5 | 3799.3778 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 759.8756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3876.9161 | 0 | 775.3832 | 7.754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 19:00 | 2 | 26 | 19 | 57 | 1363 | 39.02 | 4638.8992 | 0 | 0 | 4638.8992 | Heating | 4093.1464 | 8.5 | 4093.1464 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 818.6293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4176.68 | 0 | 835.336 | 8.353% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 20:00 | 2 | 26 | 20 | 57 | 1364 | 39.02 | 5080.2261 | 0 | 0 | 5080.2261 | Heating | 4482.5524 | 8.5 | 4482.5524 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 896.5105 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4574.0331 | 0 | 914.8066 | 9.148% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 21:00 | 2 | 26 | 21 | 57 | 1365 | 37.94 | 5364.6554 | 0 | 0 | 5364.6554 | Heating | 4733.5195 | 8.5 | 4733.5195 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 946.7039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4830.1219 | 0 | 966.0244 | 9.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 22:00 | 2 | 26 | 22 | 57 | 1366 | 37.94 | 1509.4923 | 0 | 0 | 1509.4923 | Heating | 1331.905 | 8.5 | 1331.905 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1359.0867 | 0 | 271.8173 | 2.718% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-26 23:00 | 2 | 26 | 23 | 57 | 1367 | 37.94 | 1302.0678 | 0 | 0 | 1302.0678 | Heating | 1148.8833 | 8.5 | 1148.8833 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.7767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1172.3299 | 0 | 234.466 | 2.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 | 2 | 27 | 0 | 58 | 1368 | 35.96 | 1505.6261 | 0 | 0 | 1505.6261 | Heating | 1328.4937 | 8.5 | 1328.4937 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 265.6987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1355.6058 | 0 | 271.1212 | 2.711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 01:00 | 2 | 27 | 1 | 58 | 1369 | 35.6 | 1681.6023 | 0 | 0 | 1681.6023 | Heating | 1483.7668 | 8.5 | 1483.7668 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.7534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1514.0477 | 0 | 302.8095 | 3.028% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 02:00 | 2 | 27 | 2 | 58 | 1370 | 35.06 | 1833.2935 | 0 | 0 | 1833.2935 | Heating | 1617.6119 | 8.5 | 1617.6119 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.5224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1650.6244 | 0 | 330.1249 | 3.301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 03:00 | 2 | 27 | 3 | 58 | 1371 | 32 | 1916.5602 | 0 | 0 | 1916.5602 | Heating | 1691.0825 | 8.5 | 1691.0825 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 338.2165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1725.5944 | 0 | 345.1189 | 3.451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 04:00 | 2 | 27 | 4 | 58 | 1372 | 32 | 2050.5006 | 0 | 0 | 2050.5006 | Heating | 1809.2652 | 8.5 | 1809.2652 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1846.189 | 0 | 369.2378 | 3.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 05:00 | 2 | 27 | 5 | 58 | 1373 | 32 | 2093.897 | 0 | 0 | 2093.897 | Heating | 1847.5561 | 8.5 | 1847.5561 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.5112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1885.2614 | 0 | 377.0523 | 3.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 06:00 | 2 | 27 | 6 | 58 | 1374 | 33.08 | 2099.9163 | 0 | 0 | 2099.9163 | Heating | 1852.8673 | 8.5 | 1852.8673 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 370.5735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1890.681 | 0 | 378.1362 | 3.781% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 07:00 | 2 | 27 | 7 | 58 | 1375 | 33.8 | 12444.3697 | 0 | 0 | 12444.3697 | Heating | 10980.3262 | 8.5 | 10980.3262 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2196.0652 | 43.92% | 1 | 87.84% | 0% | 0% | 0% | 60.4874 | 0 | 0 | 0 | 60.4874 | 11204.4145 | 0 | 2240.8829 | 22.41% | 1 | 44.82% | 0% | 0% | 6.4335 | 0 | 0 | 6.4335 | 66.9209
2007-02-27 08:00 | 2 | 27 | 8 | 58 | 1376 | 33.08 | 9658.7919 | 0 | 0 | 9658.7919 | Heating | 8522.4634 | 8.5 | 8522.4634 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1704.4927 | 34.09% | 1 | 68.18% | 0% | 0% | 0% | 33.7715 | 0 | 0 | 0 | 33.7715 | 8696.3913 | 0 | 1739.2783 | 17.39% | 1 | 34.79% | 0% | 0% | 3.592 | 0 | 0 | 3.592 | 37.3634
2007-02-27 09:00 | 2 | 27 | 9 | 58 | 1377 | 33.98 | 7960.0094 | 0 | 0 | 7960.0094 | Heating | 7023.5377 | 8.5 | 7023.5377 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1404.7075 | 30% | 1 | 56.19% | 0% | 0% | 0% | 21.6436 | 0 | 0 | 0 | 21.6436 | 7166.8752 | 0 | 1433.375 | 14.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.9181
2007-02-27 10:00 | 2 | 27 | 10 | 58 | 1378 | 35.06 | 6480.843 | 0 | 0 | 6480.843 | Heating | 5718.3909 | 8.5 | 5718.3909 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1143.6782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5835.0927 | 0 | 1167.0185 | 11.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 11:00 | 2 | 27 | 11 | 58 | 1379 | 35.06 | 5608.7691 | 0 | 0 | 5608.7691 | Heating | 4948.9139 | 8.5 | 4948.9139 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 989.7828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5049.9121 | 0 | 1009.9824 | 10.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 12:00 | 2 | 27 | 12 | 58 | 1380 | 41 | 4949.9509 | 0 | 0 | 4949.9509 | Heating | 4367.6038 | 8.5 | 4367.6038 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 873.5208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4456.7385 | 0 | 891.3477 | 8.913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 13:00 | 2 | 27 | 13 | 58 | 1381 | 41 | 4677.784 | 0 | 0 | 4677.784 | Heating | 4127.4565 | 8.5 | 4127.4565 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 825.4913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4211.6903 | 0 | 842.3381 | 8.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 14:00 | 2 | 27 | 14 | 58 | 1382 | 41 | 4479.2447 | 0 | 0 | 4479.2447 | Heating | 3952.2747 | 8.5 | 3952.2747 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 790.4549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4032.9334 | 0 | 806.5867 | 8.066% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 15:00 | 2 | 27 | 15 | 58 | 1383 | 39.02 | 4222.6655 | 0 | 0 | 4222.6655 | Heating | 3725.8813 | 8.5 | 3725.8813 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.1763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3801.9197 | 0 | 760.3839 | 7.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 16:00 | 2 | 27 | 16 | 58 | 1384 | 37.94 | 4219.0346 | 0 | 0 | 4219.0346 | Heating | 3722.6776 | 8.5 | 3722.6776 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 744.5355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3798.6506 | 0 | 759.7301 | 7.597% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 17:00 | 2 | 27 | 17 | 58 | 1385 | 37.94 | 4246.3819 | 0 | 0 | 4246.3819 | Heating | 3746.8075 | 8.5 | 3746.8075 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 749.3615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3823.273 | 0 | 764.6546 | 7.647% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 18:00 | 2 | 27 | 18 | 58 | 1386 | 39.92 | 4459.5902 | 0 | 0 | 4459.5902 | Heating | 3934.9325 | 8.5 | 3934.9325 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 786.9865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4015.2373 | 0 | 803.0475 | 8.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 19:00 | 2 | 27 | 19 | 58 | 1387 | 37.4 | 4688.3986 | 0 | 0 | 4688.3986 | Heating | 4136.8223 | 8.5 | 4136.8223 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 827.3645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4221.2472 | 0 | 844.2494 | 8.442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 20:00 | 2 | 27 | 20 | 58 | 1388 | 35.96 | 4861.8273 | 0 | 0 | 4861.8273 | Heating | 4289.8476 | 8.5 | 4289.8476 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 857.9695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4377.3955 | 0 | 875.4791 | 8.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 21:00 | 2 | 27 | 21 | 58 | 1389 | 35.96 | 5221.3503 | 0 | 0 | 5221.3503 | Heating | 4607.0738 | 8.5 | 4607.0738 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 921.4148 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4701.0957 | 0 | 940.2191 | 9.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 22:00 | 2 | 27 | 22 | 58 | 1390 | 35.6 | 1548.0194 | 0 | 0 | 1548.0194 | Heating | 1365.8995 | 8.5 | 1365.8995 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 273.1799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1393.775 | 0 | 278.755 | 2.788% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-27 23:00 | 2 | 27 | 23 | 58 | 1391 | 35.96 | 1412.4262 | 0 | 0 | 1412.4262 | Heating | 1246.2584 | 8.5 | 1246.2584 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.2517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1271.6923 | 0 | 254.3385 | 2.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 | 2 | 28 | 0 | 59 | 1392 | 35.6 | 1690.4162 | 0 | 0 | 1690.4162 | Heating | 1491.5437 | 8.5 | 1491.5437 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 298.3087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1521.9834 | 0 | 304.3967 | 3.044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 01:00 | 2 | 28 | 1 | 59 | 1393 | 35.06 | 1838.0132 | 0 | 0 | 1838.0132 | Heating | 1621.7763 | 8.5 | 1621.7763 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.3553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1654.8738 | 0 | 330.9748 | 3.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 02:00 | 2 | 28 | 2 | 59 | 1394 | 35.06 | 1949.7373 | 0 | 0 | 1949.7373 | Heating | 1720.3564 | 8.5 | 1720.3564 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.0713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1755.4658 | 0 | 351.0932 | 3.511% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 03:00 | 2 | 28 | 3 | 59 | 1395 | 33.8 | 2120.8585 | 0 | 0 | 2120.8585 | Heating | 1871.3457 | 8.5 | 1871.3457 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.2691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1909.5364 | 0 | 381.9073 | 3.819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 04:00 | 2 | 28 | 4 | 59 | 1396 | 33.8 | 2218.4503 | 0 | 0 | 2218.4503 | Heating | 1957.4561 | 8.5 | 1957.4561 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 391.4912 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1997.4042 | 0 | 399.4808 | 3.995% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 05:00 | 2 | 28 | 5 | 59 | 1397 | 33.98 | 2367.093 | 0 | 0 | 2367.093 | Heating | 2088.6115 | 8.5 | 2088.6115 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 417.7223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2131.2362 | 0 | 426.2472 | 4.262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 06:00 | 2 | 28 | 6 | 59 | 1398 | 35.06 | 2545.8776 | 0 | 0 | 2545.8776 | Heating | 2246.3626 | 8.5 | 2246.3626 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.2725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2292.2067 | 0 | 458.4413 | 4.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 07:00 | 2 | 28 | 7 | 59 | 1399 | 35.6 | 13759.6708 | 0 | 0 | 13759.6708 | Heating | 12140.886 | 8.5 | 12140.886 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2428.1772 | 48.56% | 1 | 97.13% | 0% | 0% | 0% | 76.2124 | 0 | 0 | 0 | 76.2124 | 12388.6592 | 0 | 2477.7318 | 24.78% | 1 | 49.55% | 0% | 0% | 8.106 | 0 | 0 | 8.106 | 84.3185
2007-02-28 08:00 | 2 | 28 | 8 | 59 | 1400 | 35.96 | 10464.7557 | 0 | 0 | 10464.7557 | Heating | 9233.6079 | 8.5 | 9233.6079 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1846.7216 | 36.93% | 1 | 73.87% | 0% | 0% | 0% | 40.6073 | 0 | 0 | 0 | 40.6073 | 9422.0489 | 0 | 1884.4098 | 18.84% | 1 | 37.69% | 0% | 0% | 4.319 | 0 | 0 | 4.319 | 44.9263
2007-02-28 09:00 | 2 | 28 | 9 | 59 | 1401 | 37.04 | 8112.4462 | 0 | 0 | 8112.4462 | Heating | 7158.0407 | 8.5 | 7158.0407 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1431.6081 | 30% | 1 | 57.26% | 0% | 0% | 0% | 22.6088 | 0 | 0 | 0 | 22.6088 | 7304.1232 | 0 | 1460.8246 | 14.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.8833
2007-02-28 10:00 | 2 | 28 | 10 | 59 | 1402 | 37.4 | 6060.2039 | 0 | 0 | 6060.2039 | Heating | 5347.2387 | 8.5 | 5347.2387 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1069.4477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5456.3661 | 0 | 1091.2732 | 10.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 11:00 | 2 | 28 | 11 | 59 | 1403 | 37.94 | 4924.5667 | 0 | 0 | 4924.5667 | Heating | 4345.2059 | 8.5 | 4345.2059 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 869.0412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4433.8836 | 0 | 886.7767 | 8.868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 12:00 | 2 | 28 | 12 | 59 | 1404 | 39.92 | 4169.0705 | 0 | 0 | 4169.0705 | Heating | 3678.5916 | 8.5 | 3678.5916 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 735.7183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3753.6649 | 0 | 750.733 | 7.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 13:00 | 2 | 28 | 13 | 59 | 1405 | 41 | 3546.3854 | 8.8784 | 8.8784 | 3537.507 | Heating | 3121.3297 | 8.5 | 3121.3297 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 624.2659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3185.0303 | 0 | 637.0061 | 6.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 14:00 | 2 | 28 | 14 | 59 | 1406 | 41 | 3159.8948 | 53.8481 | 53.8481 | 3106.0467 | Heating | 2740.6294 | 8.5 | 2740.6294 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 548.1259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2796.5607 | 0 | 559.3121 | 5.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 15:00 | 2 | 28 | 15 | 59 | 1407 | 42.8 | 2925.1039 | 63.2578 | 63.2578 | 2861.8461 | Heating | 2525.1583 | 8.5 | 2525.1583 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.0317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2576.6922 | 0 | 515.3384 | 5.153% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 16:00 | 2 | 28 | 16 | 59 | 1408 | 42.08 | 2703.4773 | 67.9281 | 67.9281 | 2635.5492 | Heating | 2325.4846 | 8.5 | 2325.4846 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 465.0969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2372.9434 | 0 | 474.5887 | 4.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 17:00 | 2 | 28 | 17 | 59 | 1409 | 42.08 | 2907.6395 | 41.3467 | 41.3467 | 2866.2928 | Heating | 2529.0819 | 8.5 | 2529.0819 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.8164 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2580.6958 | 0 | 516.1392 | 5.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 18:00 | 2 | 28 | 18 | 59 | 1410 | 39.2 | 3363.8136 | 11.8341 | 11.8341 | 3351.9796 | Heating | 2957.629 | 8.5 | 2957.629 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.5258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3017.9888 | 0 | 603.5978 | 6.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 19:00 | 2 | 28 | 19 | 59 | 1411 | 37.04 | 3784.8135 | 0 | 0 | 3784.8135 | Heating | 3339.5413 | 8.5 | 3339.5413 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 667.9083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3407.6952 | 0 | 681.539 | 6.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 20:00 | 2 | 28 | 20 | 59 | 1412 | 35.96 | 4657.0021 | 0 | 0 | 4657.0021 | Heating | 4109.1195 | 8.5 | 4109.1195 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 821.8239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4192.9791 | 0 | 838.5958 | 8.386% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 21:00 | 2 | 28 | 21 | 59 | 1413 | 35.42 | 5436.6105 | 0 | 0 | 5436.6105 | Heating | 4797.0093 | 8.5 | 4797.0093 | 0 | 3.477 | 0 | 0 | 0 | 0 | 8.5 | 0 | 959.4019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4894.9074 | 0 | 978.9815 | 9.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 22:00 | 2 | 28 | 22 | 59 | 1414 | 33.98 | 1434.9871 | 0 | 0 | 1434.9871 | Heating | 1266.1651 | 8.5 | 1266.1651 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1292.0052 | 0 | 258.401 | 2.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-02-28 23:00 | 2 | 28 | 23 | 59 | 1415 | 32.72 | 1197.4085 | 0 | 0 | 1197.4085 | Heating | 1056.5369 | 8.5 | 1056.5369 | 0 | 3.3458 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.3074 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1078.0989 | 0 | 215.6198 | 2.156% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 | 3 | 1 | 0 | 60 | 1416 | 31.1 | 1232.9262 | 0 | 0 | 1232.9262 | Heating | 1087.8761 | 8.5 | 1087.8761 | 0 | 3.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.5752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1110.0776 | 0 | 222.0155 | 2.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 01:00 | 3 | 1 | 1 | 60 | 1417 | 29.3 | 1218.7616 | 0 | 0 | 1218.7616 | Heating | 1075.3779 | 8.5 | 1075.3779 | 0 | 3.2018 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.0756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1097.3244 | 0 | 219.4649 | 2.195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 02:00 | 3 | 1 | 2 | 60 | 1418 | 28.76 | 1164.2235 | 0 | 0 | 1164.2235 | Heating | 1027.2561 | 8.5 | 1027.2561 | 0 | 3.1812 | 0 | 0 | 0 | 0 | 8.5 | 0 | 205.4512 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1048.2205 | 0 | 209.6441 | 2.096% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 03:00 | 3 | 1 | 3 | 60 | 1419 | 26.96 | 1087.0862 | 0 | 0 | 1087.0862 | Heating | 959.1937 | 8.5 | 959.1937 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.8387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 978.7691 | 0 | 195.7538 | 1.958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 04:00 | 3 | 1 | 4 | 60 | 1420 | 25.16 | 994.4072 | 0 | 0 | 994.4072 | Heating | 877.4181 | 8.5 | 877.4181 | 0 | 3.0569 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.4836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 895.3246 | 0 | 179.0649 | 1.791% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 05:00 | 3 | 1 | 5 | 60 | 1421 | 23.72 | 991.3152 | 0 | 0 | 991.3152 | Heating | 874.6898 | 8.5 | 874.6898 | 0 | 3.0132 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 892.5407 | 0 | 178.5081 | 1.785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 06:00 | 3 | 1 | 6 | 60 | 1422 | 22.46 | 1041.8635 | 0 | 0 | 1041.8635 | Heating | 919.2914 | 8.5 | 919.2914 | 0 | 2.9775 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.8583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 938.0524 | 0 | 187.6105 | 1.876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 07:00 | 3 | 1 | 7 | 60 | 1423 | 21.92 | 8542.5347 | 0 | 0 | 8542.5347 | Heating | 7537.5306 | 8.5 | 7537.5306 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1507.5061 | 30.15% | 1 | 60.3% | 0% | 0% | 0% | 25.4611 | 0 | 0 | 0 | 25.4611 | 7691.3577 | 0 | 1538.2715 | 15.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.7356
2007-03-01 08:00 | 3 | 1 | 8 | 60 | 1424 | 21.92 | 6332.8049 | 0 | 0 | 6332.8049 | Heating | 5587.7691 | 8.5 | 5587.7691 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1117.5538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5701.8052 | 0 | 1140.361 | 11.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 09:00 | 3 | 1 | 9 | 60 | 1425 | 23 | 5144.2525 | 0 | 0 | 5144.2525 | Heating | 4539.0463 | 8.5 | 4539.0463 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 907.8093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4631.6799 | 0 | 926.336 | 9.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 10:00 | 3 | 1 | 10 | 60 | 1426 | 24.08 | 4065.7887 | 0 | 0 | 4065.7887 | Heating | 3587.4606 | 8.5 | 3587.4606 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 717.4921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3660.6741 | 0 | 732.1348 | 7.321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 11:00 | 3 | 1 | 11 | 60 | 1427 | 24.08 | 3565.1609 | 0 | 0 | 3565.1609 | Heating | 3145.7302 | 8.5 | 3145.7302 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 629.146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3209.9287 | 0 | 641.9857 | 6.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 12:00 | 3 | 1 | 12 | 60 | 1428 | 28.04 | 3173.5449 | 0 | 0 | 3173.5449 | Heating | 2800.1867 | 8.5 | 2800.1867 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 560.0373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2857.3334 | 0 | 571.4667 | 5.715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 13:00 | 3 | 1 | 13 | 60 | 1429 | 30.02 | 3013.9594 | 0 | 0 | 3013.9594 | Heating | 2659.3759 | 8.5 | 2659.3759 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 531.8752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2713.6489 | 0 | 542.7298 | 5.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 14:00 | 3 | 1 | 14 | 60 | 1430 | 30.02 | 2911.9509 | 0 | 0 | 2911.9509 | Heating | 2569.3684 | 8.5 | 2569.3684 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 513.8737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2621.8045 | 0 | 524.3609 | 5.244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 15:00 | 3 | 1 | 15 | 60 | 1431 | 33.98 | 2871.8516 | 0 | 0 | 2871.8516 | Heating | 2533.9867 | 8.5 | 2533.9867 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 506.7973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2585.7007 | 0 | 517.1401 | 5.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 16:00 | 3 | 1 | 16 | 60 | 1432 | 35.06 | 2848.1652 | 0 | 0 | 2848.1652 | Heating | 2513.087 | 8.5 | 2513.087 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 502.6174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2564.3745 | 0 | 512.8749 | 5.129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 17:00 | 3 | 1 | 17 | 60 | 1433 | 35.06 | 3100.7272 | 0 | 0 | 3100.7272 | Heating | 2735.9358 | 8.5 | 2735.9358 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 547.1872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2791.7712 | 0 | 558.3542 | 5.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 18:00 | 3 | 1 | 18 | 60 | 1434 | 30.92 | 3565.3225 | 0 | 0 | 3565.3225 | Heating | 3145.8728 | 8.5 | 3145.8728 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 629.1746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3210.0742 | 0 | 642.0148 | 6.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 19:00 | 3 | 1 | 19 | 60 | 1435 | 26.06 | 3979.8635 | 0 | 0 | 3979.8635 | Heating | 3511.6442 | 8.5 | 3511.6442 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 702.3288 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3583.3105 | 0 | 716.6621 | 7.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 20:00 | 3 | 1 | 20 | 60 | 1436 | 26.06 | 4340.5763 | 0 | 0 | 4340.5763 | Heating | 3829.9203 | 8.5 | 3829.9203 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 765.9841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3908.0819 | 0 | 781.6164 | 7.816% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 21:00 | 3 | 1 | 21 | 60 | 1437 | 26.06 | 4735.6308 | 0 | 0 | 4735.6308 | Heating | 4178.4978 | 8.5 | 4178.4978 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 835.6996 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4263.7733 | 0 | 852.7547 | 8.528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 22:00 | 3 | 1 | 22 | 60 | 1438 | 21.92 | 1456.1364 | 0 | 0 | 1456.1364 | Heating | 1284.8263 | 8.5 | 1284.8263 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 256.9653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1311.0472 | 0 | 262.2094 | 2.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-01 23:00 | 3 | 1 | 23 | 60 | 1439 | 21.92 | 1380.9972 | 0 | 0 | 1380.9972 | Heating | 1218.527 | 8.5 | 1218.527 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 243.7054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1243.3949 | 0 | 248.679 | 2.487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 | 3 | 2 | 0 | 61 | 1440 | 24.98 | 1655.1816 | 0 | 0 | 1655.1816 | Heating | 1460.4544 | 8.5 | 1460.4544 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.0909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1490.2596 | 0 | 298.0519 | 2.981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 01:00 | 3 | 2 | 1 | 61 | 1441 | 26.06 | 1842.096 | 0 | 0 | 1842.096 | Heating | 1625.3788 | 8.5 | 1625.3788 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 325.0758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1658.5498 | 0 | 331.71 | 3.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 02:00 | 3 | 2 | 2 | 61 | 1442 | 26.06 | 2012.8014 | 0 | 0 | 2012.8014 | Heating | 1776.0013 | 8.5 | 1776.0013 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 355.2003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1812.2462 | 0 | 362.4492 | 3.624% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 03:00 | 3 | 2 | 3 | 61 | 1443 | 28.04 | 2197.8051 | 0 | 0 | 2197.8051 | Heating | 1939.2398 | 8.5 | 1939.2398 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1978.8161 | 0 | 395.7632 | 3.958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 04:00 | 3 | 2 | 4 | 61 | 1444 | 30.02 | 2372.3491 | 0 | 0 | 2372.3491 | Heating | 2093.2492 | 8.5 | 2093.2492 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 418.6498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2135.9685 | 0 | 427.1937 | 4.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 05:00 | 3 | 2 | 5 | 61 | 1445 | 30.02 | 2522.7305 | 0 | 0 | 2522.7305 | Heating | 2225.9387 | 8.5 | 2225.9387 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.1877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2271.366 | 0 | 454.2732 | 4.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 06:00 | 3 | 2 | 6 | 61 | 1446 | 30.02 | 2649.6643 | 0 | 0 | 2649.6643 | Heating | 2337.9391 | 8.5 | 2337.9391 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.5878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2385.6522 | 0 | 477.1304 | 4.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 07:00 | 3 | 2 | 7 | 61 | 1447 | 30.92 | 12837.5941 | 0 | 0 | 12837.5941 | Heating | 11327.2889 | 8.5 | 11327.2889 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2265.4578 | 45.31% | 1 | 90.62% | 0% | 0% | 0% | 64.974 | 0 | 0 | 0 | 64.974 | 11558.4581 | 0 | 2311.6916 | 23.12% | 1 | 46.23% | 0% | 0% | 6.9107 | 0 | 0 | 6.9107 | 71.8847
2007-03-02 08:00 | 3 | 2 | 8 | 61 | 1448 | 30.92 | 10152.8053 | 0 | 0 | 10152.8053 | Heating | 8958.3576 | 8.5 | 8958.3576 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1791.6715 | 35.83% | 1 | 71.67% | 0% | 0% | 0% | 37.877 | 0 | 0 | 0 | 37.877 | 9141.1813 | 0 | 1828.2363 | 18.28% | 1 | 36.56% | 0% | 0% | 4.0286 | 0 | 0 | 4.0286 | 41.9056
2007-03-02 09:00 | 3 | 2 | 9 | 61 | 1449 | 33.08 | 9093.6217 | 0 | 0 | 9093.6217 | Heating | 8023.7838 | 8.5 | 8023.7838 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1604.7568 | 32.1% | 1 | 64.19% | 0% | 0% | 0% | 29.3983 | 0 | 0 | 0 | 29.3983 | 8187.5345 | 0 | 1637.5069 | 16.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.6728
2007-03-02 10:00 | 3 | 2 | 10 | 61 | 1450 | 35.06 | 8105.0517 | 0 | 0 | 8105.0517 | Heating | 7151.5162 | 8.5 | 7151.5162 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1430.3032 | 30% | 1 | 57.21% | 0% | 0% | 0% | 22.5614 | 0 | 0 | 0 | 22.5614 | 7297.4655 | 0 | 1459.4931 | 14.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.8359
2007-03-02 11:00 | 3 | 2 | 11 | 61 | 1451 | 35.06 | 7261.7971 | 0 | 0 | 7261.7971 | Heating | 6407.468 | 8.5 | 6407.468 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1281.4936 | 30% | 1 | 51.26% | 0% | 0% | 0% | 17.5238 | 0 | 0 | 0 | 17.5238 | 6538.2326 | 0 | 1307.6465 | 13.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7984
2007-03-02 12:00 | 3 | 2 | 12 | 61 | 1452 | 37.94 | 6708.2401 | 0 | 0 | 6708.2401 | Heating | 5919.0354 | 8.5 | 5919.0354 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1183.8071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6039.832 | 0 | 1207.9664 | 12.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 13:00 | 3 | 2 | 13 | 61 | 1453 | 35.6 | 6426.7506 | 0 | 0 | 6426.7506 | Heating | 5670.6623 | 8.5 | 5670.6623 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1134.1325 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5786.3901 | 0 | 1157.278 | 11.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 14:00 | 3 | 2 | 14 | 61 | 1454 | 33.98 | 6349.5091 | 0 | 0 | 6349.5091 | Heating | 5602.5081 | 8.5 | 5602.5081 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1120.5016 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5716.845 | 0 | 1143.369 | 11.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 15:00 | 3 | 2 | 15 | 61 | 1455 | 33.08 | 6351.2717 | 0 | 0 | 6351.2717 | Heating | 5604.0633 | 8.5 | 5604.0633 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1120.8127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5718.4319 | 0 | 1143.6864 | 11.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 16:00 | 3 | 2 | 16 | 61 | 1456 | 30.92 | 6379.4863 | 0 | 0 | 6379.4863 | Heating | 5628.9585 | 8.5 | 5628.9585 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1125.7917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5743.8352 | 0 | 1148.767 | 11.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 17:00 | 3 | 2 | 17 | 61 | 1457 | 30.92 | 6427.3635 | 0 | 0 | 6427.3635 | Heating | 5671.2031 | 8.5 | 5671.2031 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1134.2406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5786.9419 | 0 | 1157.3884 | 11.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 18:00 | 3 | 2 | 18 | 61 | 1458 | 24.08 | 6614.3537 | 0 | 0 | 6614.3537 | Heating | 5836.1945 | 8.5 | 5836.1945 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1167.2389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5955.3005 | 0 | 1191.0601 | 11.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-02 19:00 | 3 | 2 | 19 | 61 | 1459 | 21.92 | 7105.0454 | 0 | 0 | 7105.0454 | Heating | 6269.1577 | 8.5 | 6269.1577 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1253.8315 | 30% | 1 | 50.15% | 0% | 0% | 0% | 16.666 | 0 | 0 | 0 | 16.666 | 6397.0997 | 0 | 1279.4199 | 12.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9405
2007-03-02 20:00 | 3 | 2 | 20 | 61 | 1460 | 21.92 | 7634.3163 | 0 | 0 | 7634.3163 | Heating | 6736.1614 | 8.5 | 6736.1614 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1347.2323 | 30% | 1 | 53.89% | 0% | 0% | 0% | 19.6607 | 0 | 0 | 0 | 19.6607 | 6873.6341 | 0 | 1374.7268 | 13.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.9352
2007-03-02 21:00 | 3 | 2 | 21 | 61 | 1461 | 19.94 | 7847.9462 | 0 | 0 | 7847.9462 | Heating | 6924.6584 | 8.5 | 6924.6584 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1384.9317 | 30% | 1 | 55.4% | 0% | 0% | 0% | 20.9491 | 0 | 0 | 0 | 20.9491 | 7065.978 | 0 | 1413.1956 | 14.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.2237
2007-03-02 22:00 | 3 | 2 | 22 | 61 | 1462 | 19.04 | 8220.3501 | 0 | 0 | 8220.3501 | Heating | 7253.2501 | 8.5 | 7253.2501 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1450.65 | 30% | 1 | 58.03% | 0% | 0% | 0% | 23.3064 | 0 | 0 | 0 | 23.3064 | 7401.2756 | 0 | 1480.2551 | 14.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.5809
2007-03-02 23:00 | 3 | 2 | 23 | 61 | 1463 | 19.04 | 2552.9814 | 0 | 0 | 2552.9814 | Heating | 2252.6306 | 8.5 | 2252.6306 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 450.5261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2298.6027 | 0 | 459.7205 | 4.597% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 | 3 | 3 | 0 | 62 | 1464 | 15.08 | 2646.367 | 0 | 0 | 2646.367 | Heating | 2335.0297 | 8.5 | 2335.0297 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.0059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2382.6834 | 0 | 476.5367 | 4.765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 01:00 | 3 | 3 | 1 | 62 | 1465 | 12.92 | 2735.6698 | 0 | 0 | 2735.6698 | Heating | 2413.8263 | 8.5 | 2413.8263 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 482.7653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2463.088 | 0 | 492.6176 | 4.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 02:00 | 3 | 3 | 2 | 62 | 1466 | 12.92 | 2802.8043 | 0 | 0 | 2802.8043 | Heating | 2473.0626 | 8.5 | 2473.0626 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.6125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2523.5333 | 0 | 504.7067 | 5.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 03:00 | 3 | 3 | 3 | 62 | 1467 | 10.04 | 2852.4761 | 0 | 0 | 2852.4761 | Heating | 2516.8907 | 8.5 | 2516.8907 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 503.3781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2568.2558 | 0 | 513.6512 | 5.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 04:00 | 3 | 3 | 4 | 62 | 1468 | 8.96 | 2899.6072 | 0 | 0 | 2899.6072 | Heating | 2558.4769 | 8.5 | 2558.4769 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 511.6954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2610.6907 | 0 | 522.1381 | 5.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 05:00 | 3 | 3 | 5 | 62 | 1469 | 8.96 | 2883.0535 | 0 | 0 | 2883.0535 | Heating | 2543.8707 | 8.5 | 2543.8707 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 508.7741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2595.7864 | 0 | 519.1573 | 5.192% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 06:00 | 3 | 3 | 6 | 62 | 1470 | 8.06 | 2821.0937 | 0 | 0 | 2821.0937 | Heating | 2489.2003 | 8.5 | 2489.2003 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 497.8401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2540.0003 | 0 | 508.0001 | 5.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 07:00 | 3 | 3 | 7 | 62 | 1471 | 5 | 2739.2171 | 0 | 0 | 2739.2171 | Heating | 2416.9563 | 8.5 | 2416.9563 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 483.3913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2466.2819 | 0 | 493.2564 | 4.933% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 08:00 | 3 | 3 | 8 | 62 | 1472 | 5 | 2602.7148 | 0 | 0 | 2602.7148 | Heating | 2296.513 | 8.5 | 2296.513 | 0 | 2.6507 | 0 | 0 | 0 | 0 | 8.5 | 0 | 459.3026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2343.3806 | 0 | 468.6761 | 4.687% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 09:00 | 3 | 3 | 9 | 62 | 1473 | 12.02 | 12611.257 | 0 | 0 | 12611.257 | Heating | 11127.5797 | 8.5 | 11127.5797 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2225.5159 | 44.51% | 1 | 89.02% | 0% | 0% | 0% | 62.3694 | 0 | 0 | 0 | 62.3694 | 11354.6732 | 0 | 2270.9346 | 22.71% | 1 | 45.42% | 0% | 0% | 6.6337 | 0 | 0 | 6.6337 | 69.0031
2007-03-03 10:00 | 3 | 3 | 10 | 62 | 1474 | 14 | 9629.6974 | 0 | 0 | 9629.6974 | Heating | 8496.7918 | 8.5 | 8496.7918 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1699.3584 | 33.99% | 1 | 67.97% | 0% | 0% | 0% | 33.5379 | 0 | 0 | 0 | 33.5379 | 8670.1958 | 0 | 1734.0392 | 17.34% | 1 | 34.68% | 0% | 0% | 3.5671 | 0 | 0 | 3.5671 | 37.1051
2007-03-03 11:00 | 3 | 3 | 11 | 62 | 1475 | 14 | 8030.6308 | 0 | 0 | 8030.6308 | Heating | 7085.8507 | 8.5 | 7085.8507 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1417.1701 | 30% | 1 | 56.69% | 0% | 0% | 0% | 22.0878 | 0 | 0 | 0 | 22.0878 | 7230.4599 | 0 | 1446.092 | 14.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.3623
2007-03-03 12:00 | 3 | 3 | 12 | 62 | 1476 | 17.06 | 7049.7769 | 0 | 0 | 7049.7769 | Heating | 6220.3914 | 8.5 | 6220.3914 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1244.0783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6347.3382 | 0 | 1269.4676 | 12.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 13:00 | 3 | 3 | 13 | 62 | 1477 | 19.04 | 6087.3066 | 0 | 0 | 6087.3066 | Heating | 5371.1528 | 8.5 | 5371.1528 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1074.2306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5480.7682 | 0 | 1096.1536 | 10.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 14:00 | 3 | 3 | 14 | 62 | 1478 | 19.04 | 5641.2898 | 0 | 0 | 5641.2898 | Heating | 4977.6086 | 8.5 | 4977.6086 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 995.5217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5079.1925 | 0 | 1015.8385 | 10.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 15:00 | 3 | 3 | 15 | 62 | 1479 | 24.08 | 5446.5239 | 0 | 0 | 5446.5239 | Heating | 4805.7564 | 8.5 | 4805.7564 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 961.1513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4903.8331 | 0 | 980.7666 | 9.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 16:00 | 3 | 3 | 16 | 62 | 1480 | 24.08 | 5382.3863 | 0 | 0 | 5382.3863 | Heating | 4749.1644 | 8.5 | 4749.1644 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 949.8329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4846.0861 | 0 | 969.2172 | 9.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 17:00 | 3 | 3 | 17 | 62 | 1481 | 24.08 | 5275.4532 | 0 | 0 | 5275.4532 | Heating | 4654.8116 | 8.5 | 4654.8116 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 930.9623 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4749.8078 | 0 | 949.9616 | 9.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 18:00 | 3 | 3 | 18 | 62 | 1482 | 21.02 | 6922.9808 | 0 | 0 | 6922.9808 | Heating | 6108.5125 | 8.5 | 6108.5125 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1221.7025 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6233.176 | 0 | 1246.6352 | 12.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 19:00 | 3 | 3 | 19 | 62 | 1483 | 21.02 | 7164.7488 | 0 | 0 | 7164.7488 | Heating | 6321.8372 | 8.5 | 6321.8372 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1264.3674 | 30% | 1 | 50.57% | 0% | 0% | 0% | 16.9899 | 0 | 0 | 0 | 16.9899 | 6450.8543 | 0 | 1290.1709 | 12.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2644
2007-03-03 20:00 | 3 | 3 | 20 | 62 | 1484 | 21.02 | 1708.2105 | 0 | 0 | 1708.2105 | Heating | 1507.2445 | 8.5 | 1507.2445 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.4489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1538.0046 | 0 | 307.6009 | 3.076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 21:00 | 3 | 3 | 21 | 62 | 1485 | 17.06 | 1703.7441 | 0 | 0 | 1703.7441 | Heating | 1503.3036 | 8.5 | 1503.3036 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.6607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1533.9833 | 0 | 306.7967 | 3.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 22:00 | 3 | 3 | 22 | 62 | 1486 | 15.08 | 1700.9185 | 0 | 0 | 1700.9185 | Heating | 1500.8105 | 8.5 | 1500.8105 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.1621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1531.4393 | 0 | 306.2879 | 3.063% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-03 23:00 | 3 | 3 | 23 | 62 | 1487 | 15.08 | 1731.2116 | 0 | 0 | 1731.2116 | Heating | 1527.5397 | 8.5 | 1527.5397 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 305.5079 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1558.714 | 0 | 311.7428 | 3.117% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 | 3 | 4 | 0 | 63 | 1488 | 12.02 | 1769.6802 | 0 | 0 | 1769.6802 | Heating | 1561.4825 | 8.5 | 1561.4825 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 312.2965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1593.3495 | 0 | 318.6699 | 3.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 01:00 | 3 | 4 | 1 | 63 | 1489 | 8.96 | 1798.5511 | 0 | 0 | 1798.5511 | Heating | 1586.9569 | 8.5 | 1586.9569 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.3914 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1619.3437 | 0 | 323.8687 | 3.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 02:00 | 3 | 4 | 2 | 63 | 1490 | 8.96 | 1798.0234 | 0 | 0 | 1798.0234 | Heating | 1586.4912 | 8.5 | 1586.4912 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.2982 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1618.8686 | 0 | 323.7737 | 3.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 03:00 | 3 | 4 | 3 | 63 | 1491 | 10.04 | 1784.651 | 0 | 0 | 1784.651 | Heating | 1574.692 | 8.5 | 1574.692 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 314.9384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1606.8286 | 0 | 321.3657 | 3.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 04:00 | 3 | 4 | 4 | 63 | 1492 | 10.04 | 1762.9972 | 0 | 0 | 1762.9972 | Heating | 1555.5858 | 8.5 | 1555.5858 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.1172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1587.3324 | 0 | 317.4665 | 3.175% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 05:00 | 3 | 4 | 5 | 63 | 1493 | 10.04 | 1741.6473 | 0 | 0 | 1741.6473 | Heating | 1536.7476 | 8.5 | 1536.7476 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 307.3495 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1568.1098 | 0 | 313.622 | 3.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 06:00 | 3 | 4 | 6 | 63 | 1494 | 10.04 | 1714.0937 | 0 | 0 | 1714.0937 | Heating | 1512.4356 | 8.5 | 1512.4356 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 302.4871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1543.3016 | 0 | 308.6603 | 3.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 07:00 | 3 | 4 | 7 | 63 | 1495 | 10.04 | 10256.8564 | 0 | 0 | 10256.8564 | Heating | 9050.1674 | 8.5 | 9050.1674 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1810.0335 | 36.2% | 1 | 72.4% | 0% | 0% | 0% | 38.7758 | 0 | 0 | 0 | 38.7758 | 9234.8647 | 0 | 1846.9729 | 18.47% | 1 | 36.94% | 0% | 0% | 4.1242 | 0 | 0 | 4.1242 | 42.9
2007-03-04 08:00 | 3 | 4 | 8 | 63 | 1496 | 10.04 | 7617.1127 | 0 | 0 | 7617.1127 | Heating | 6720.9818 | 8.5 | 6720.9818 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1344.1964 | 30% | 1 | 53.77% | 0% | 0% | 0% | 19.5589 | 0 | 0 | 0 | 19.5589 | 6858.1447 | 0 | 1371.6289 | 13.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.8335
2007-03-04 09:00 | 3 | 4 | 9 | 63 | 1497 | 17.06 | 6062.5069 | 0 | 0 | 6062.5069 | Heating | 5349.2708 | 8.5 | 5349.2708 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1069.8542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5458.4396 | 0 | 1091.6879 | 10.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 10:00 | 3 | 4 | 10 | 63 | 1498 | 23 | 4786.5982 | 0 | 0 | 4786.5982 | Heating | 4223.469 | 8.5 | 4223.469 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 844.6938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4309.6623 | 0 | 861.9325 | 8.619% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 11:00 | 3 | 4 | 11 | 63 | 1499 | 23 | 4093.1056 | 0 | 0 | 4093.1056 | Heating | 3611.5638 | 8.5 | 3611.5638 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 722.3128 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3685.2692 | 0 | 737.0538 | 7.371% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 12:00 | 3 | 4 | 12 | 63 | 1500 | 32 | 3546.5748 | 0 | 0 | 3546.5748 | Heating | 3129.3307 | 8.5 | 3129.3307 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 625.8661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3193.1946 | 0 | 638.6389 | 6.386% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 13:00 | 3 | 4 | 13 | 63 | 1501 | 33.08 | 3239.3348 | 0 | 0 | 3239.3348 | Heating | 2858.2366 | 8.5 | 2858.2366 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 571.6473 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2916.568 | 0 | 583.3136 | 5.833% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 14:00 | 3 | 4 | 14 | 63 | 1502 | 33.08 | 2949.3541 | 0 | 0 | 2949.3541 | Heating | 2602.3713 | 8.5 | 2602.3713 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 520.4743 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2655.4809 | 0 | 531.0962 | 5.311% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 15:00 | 3 | 4 | 15 | 63 | 1503 | 37.04 | 2743.3319 | 0 | 0 | 2743.3319 | Heating | 2420.587 | 8.5 | 2420.587 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 484.1174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2469.9867 | 0 | 493.9973 | 4.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 16:00 | 3 | 4 | 16 | 63 | 1504 | 37.04 | 2549.1533 | 0 | 0 | 2549.1533 | Heating | 2249.2529 | 8.5 | 2249.2529 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.8506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2295.156 | 0 | 459.0312 | 4.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 17:00 | 3 | 4 | 17 | 63 | 1505 | 37.04 | 2621.8355 | 0 | 0 | 2621.8355 | Heating | 2313.3843 | 8.5 | 2313.3843 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 462.6769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2360.5962 | 0 | 472.1192 | 4.721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 18:00 | 3 | 4 | 18 | 63 | 1506 | 35.96 | 2906.6193 | 0 | 0 | 2906.6193 | Heating | 2564.6641 | 8.5 | 2564.6641 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 512.9328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2617.0042 | 0 | 523.4008 | 5.234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 19:00 | 3 | 4 | 19 | 63 | 1507 | 35.06 | 3116.9366 | 0 | 0 | 3116.9366 | Heating | 2750.2381 | 8.5 | 2750.2381 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.0476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2806.3655 | 0 | 561.2731 | 5.613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 20:00 | 3 | 4 | 20 | 63 | 1508 | 35.06 | 3188.9522 | 0 | 0 | 3188.9522 | Heating | 2813.7813 | 8.5 | 2813.7813 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 562.7563 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2871.2055 | 0 | 574.2411 | 5.742% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 21:00 | 3 | 4 | 21 | 63 | 1509 | 33.98 | 3177.2013 | 0 | 0 | 3177.2013 | Heating | 2803.4129 | 8.5 | 2803.4129 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 560.6826 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2860.6254 | 0 | 572.1251 | 5.721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 22:00 | 3 | 4 | 22 | 63 | 1510 | 33.98 | 879.2517 | 0 | 0 | 879.2517 | Heating | 775.8103 | 8.5 | 775.8103 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.1621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 791.6432 | 0 | 158.3286 | 1.583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-04 23:00 | 3 | 4 | 23 | 63 | 1511 | 33.98 | 725.0516 | 0 | 0 | 725.0516 | Heating | 639.7514 | 8.5 | 639.7514 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.9503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 652.8075 | 0 | 130.5615 | 1.306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 | 3 | 5 | 0 | 64 | 1512 | 33.98 | 749.7898 | 0 | 0 | 749.7898 | Heating | 661.5792 | 8.5 | 661.5792 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.3158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 675.0808 | 0 | 135.0162 | 1.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 01:00 | 3 | 5 | 1 | 64 | 1513 | 33.98 | 783.7238 | 0 | 0 | 783.7238 | Heating | 691.521 | 8.5 | 691.521 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.3042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 705.6336 | 0 | 141.1267 | 1.411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 02:00 | 3 | 5 | 2 | 64 | 1514 | 33.98 | 815.0487 | 0 | 0 | 815.0487 | Heating | 719.1606 | 8.5 | 719.1606 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 143.8321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 733.8374 | 0 | 146.7675 | 1.468% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 03:00 | 3 | 5 | 3 | 64 | 1515 | 35.06 | 839.2634 | 0 | 0 | 839.2634 | Heating | 740.5265 | 8.5 | 740.5265 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.1053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 755.6393 | 0 | 151.1279 | 1.511% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 04:00 | 3 | 5 | 4 | 64 | 1516 | 35.06 | 856.0134 | 0 | 0 | 856.0134 | Heating | 755.306 | 8.5 | 755.306 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.0612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 770.7204 | 0 | 154.1441 | 1.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 05:00 | 3 | 5 | 5 | 64 | 1517 | 35.06 | 871.8687 | 0 | 0 | 871.8687 | Heating | 769.2959 | 8.5 | 769.2959 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 153.8592 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 784.9959 | 0 | 156.9992 | 1.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 06:00 | 3 | 5 | 6 | 64 | 1518 | 35.6 | 876.6518 | 0 | 0 | 876.6518 | Heating | 773.5163 | 8.5 | 773.5163 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.7033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 789.3023 | 0 | 157.8605 | 1.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 07:00 | 3 | 5 | 7 | 64 | 1519 | 37.04 | 7350.631 | 0 | 0 | 7350.631 | Heating | 6485.8509 | 8.5 | 6485.8509 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1297.1702 | 30% | 1 | 51.89% | 0% | 0% | 0% | 18.0208 | 0 | 0 | 0 | 18.0208 | 6618.2152 | 0 | 1323.643 | 13.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.2953
2007-03-05 08:00 | 3 | 5 | 8 | 64 | 1520 | 37.04 | 5196.2801 | 0 | 0 | 5196.2801 | Heating | 4584.9531 | 8.5 | 4584.9531 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 916.9906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4678.5235 | 0 | 935.7047 | 9.357% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 09:00 | 3 | 5 | 9 | 64 | 1521 | 39.02 | 3912.494 | 0 | 0 | 3912.494 | Heating | 3452.2006 | 8.5 | 3452.2006 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 690.4401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3522.6536 | 0 | 704.5307 | 7.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 10:00 | 3 | 5 | 10 | 64 | 1522 | 42.08 | 2733.4278 | 0 | 0 | 2733.4278 | Heating | 2411.8481 | 8.5 | 2411.8481 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 482.3696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2461.0695 | 0 | 492.2139 | 4.922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 11:00 | 3 | 5 | 11 | 64 | 1523 | 42.08 | 1728.358 | 0 | 0 | 1728.358 | Heating | 1525.0217 | 8.5 | 1525.0217 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 305.0043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1556.1446 | 0 | 311.2289 | 3.112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 12:00 | 3 | 5 | 12 | 64 | 1524 | 42.98 | 689.7337 | 5.1139 | 5.1139 | 684.6198 | Heating | 604.0763 | 8.5 | 604.0763 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.8153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 616.4044 | 0 | 123.2809 | 1.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 13:00 | 3 | 5 | 13 | 64 | 1525 | 44.06 | 209.3615 | 45.3058 | 45.3058 | 164.0557 | Heating | 144.755 | 8.5 | 144.755 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 147.7092 | 0 | 29.5418 | 0.2954% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 14:00 | 3 | 5 | 14 | 64 | 1526 | 44.06 | 121.9252 | 146.9366 | 146.9366 | -25.0114 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 179.5892 | 179.5892 | 0 | 8.5 | 0 | 29.9315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 175.9974 | 35.1995 | 0.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 15:00 | 3 | 5 | 15 | 64 | 1527 | 48.02 | 95.2526 | 205.5003 | 205.5003 | -110.2476 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 251.167 | 251.167 | 0 | 8.5 | 0 | 41.8612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 246.1436 | 49.2287 | 0.4923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 16:00 | 3 | 5 | 16 | 64 | 1528 | 48.02 | 79.5381 | 188.8867 | 188.8867 | -109.3486 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 230.8615 | 230.8615 | 0 | 8.5 | 0 | 38.4769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 226.2443 | 45.2489 | 0.4525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 17:00 | 3 | 5 | 17 | 64 | 1529 | 48.02 | 91.1188 | 155.4189 | 155.4189 | -64.3001 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 189.9564 | 189.9564 | 0 | 8.5 | 0 | 31.6594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 186.1573 | 37.2315 | 0.3723% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 18:00 | 3 | 5 | 18 | 64 | 1530 | 46.94 | 125.856 | 80.6044 | 80.6044 | 45.2516 | Heating | 39.9279 | 8.5 | 39.9279 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.9856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.7427 | 0 | 8.1485 | 0.08149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 19:00 | 3 | 5 | 19 | 64 | 1531 | 48.92 | 160.7808 | 21.6975 | 21.6975 | 139.0833 | Heating | 122.7205 | 8.5 | 122.7205 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.5441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 125.225 | 0 | 25.045 | 0.2505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 20:00 | 3 | 5 | 20 | 64 | 1532 | 48.92 | 494.5562 | 6.8545 | 6.8545 | 487.7017 | Heating | 430.3251 | 8.5 | 430.3251 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 86.065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 439.1072 | 0 | 87.8214 | 0.8782% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 21:00 | 3 | 5 | 21 | 64 | 1533 | 48.92 | 1027.0262 | 0 | 0 | 1027.0262 | Heating | 906.1996 | 8.5 | 906.1996 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 181.2399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 924.6935 | 0 | 184.9387 | 1.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 22:00 | 3 | 5 | 22 | 64 | 1534 | 48.92 | 362.4685 | 0 | 0 | 362.4685 | Heating | 319.8251 | 8.5 | 319.8251 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 326.3522 | 0 | 65.2704 | 0.6527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-05 23:00 | 3 | 5 | 23 | 64 | 1535 | 48.92 | 452.6636 | 0 | 0 | 452.6636 | Heating | 399.4091 | 8.5 | 399.4091 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.8818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 407.5603 | 0 | 81.5121 | 0.8151% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 | 3 | 6 | 0 | 65 | 1536 | 48.02 | 569.534 | 0 | 0 | 569.534 | Heating | 502.53 | 8.5 | 502.53 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 512.7857 | 0 | 102.5571 | 1.026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 01:00 | 3 | 6 | 1 | 65 | 1537 | 48.92 | 688.2002 | 0 | 0 | 688.2002 | Heating | 607.2355 | 8.5 | 607.2355 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.4471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 619.628 | 0 | 123.9256 | 1.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 02:00 | 3 | 6 | 2 | 65 | 1538 | 48.92 | 758.4743 | 0 | 0 | 758.4743 | Heating | 669.242 | 8.5 | 669.242 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.8484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 682.9 | 0 | 136.58 | 1.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 03:00 | 3 | 6 | 3 | 65 | 1539 | 48.92 | 799.2264 | 0 | 0 | 799.2264 | Heating | 705.1998 | 8.5 | 705.1998 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.04 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 719.5916 | 0 | 143.9183 | 1.439% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 04:00 | 3 | 6 | 4 | 65 | 1540 | 48.92 | 861.5093 | 0 | 0 | 861.5093 | Heating | 760.1552 | 8.5 | 760.1552 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 775.6686 | 0 | 155.1337 | 1.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 05:00 | 3 | 6 | 5 | 65 | 1541 | 48.92 | 957.2026 | 0 | 0 | 957.2026 | Heating | 844.5906 | 8.5 | 844.5906 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.9181 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 861.8271 | 0 | 172.3654 | 1.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 06:00 | 3 | 6 | 6 | 65 | 1542 | 48.92 | 1063.4177 | 0 | 0 | 1063.4177 | Heating | 938.3098 | 8.5 | 938.3098 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 187.662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 957.4589 | 0 | 191.4918 | 1.915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 07:00 | 3 | 6 | 7 | 65 | 1543 | 50 | 8448.0378 | 0 | 0 | 8448.0378 | Heating | 7454.151 | 8.5 | 7454.151 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1490.8302 | 30% | 1 | 59.63% | 0% | 0% | 0% | 24.8179 | 0 | 0 | 0 | 24.8179 | 7606.2765 | 0 | 1521.2553 | 15.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.0925
2007-03-06 08:00 | 3 | 6 | 8 | 65 | 1544 | 48.92 | 6280.8524 | 0 | 0 | 6280.8524 | Heating | 5541.9286 | 8.5 | 5541.9286 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1108.3857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5655.0292 | 0 | 1131.0058 | 11.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 09:00 | 3 | 6 | 9 | 65 | 1545 | 48.2 | 5064.7453 | 0 | 0 | 5064.7453 | Heating | 4468.8929 | 8.5 | 4468.8929 | 0 | 4.3513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 893.7786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4560.0948 | 0 | 912.019 | 9.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 10:00 | 3 | 6 | 10 | 65 | 1546 | 48.92 | 3932.2009 | 0 | 0 | 3932.2009 | Heating | 3469.589 | 8.5 | 3469.589 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 693.9178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3540.397 | 0 | 708.0794 | 7.081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 11:00 | 3 | 6 | 11 | 65 | 1547 | 48.92 | 3351.564 | 0 | 0 | 3351.564 | Heating | 2957.2623 | 8.5 | 2957.2623 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.4525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3017.6146 | 0 | 603.5229 | 6.035% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 12:00 | 3 | 6 | 12 | 65 | 1548 | 50 | 2813.9428 | 0 | 0 | 2813.9428 | Heating | 2482.8907 | 8.5 | 2482.8907 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 496.5781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2533.562 | 0 | 506.7124 | 5.067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 13:00 | 3 | 6 | 13 | 65 | 1549 | 50 | 2548.5639 | 0 | 0 | 2548.5639 | Heating | 2248.7329 | 8.5 | 2248.7329 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.7466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2294.6254 | 0 | 458.9251 | 4.589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 14:00 | 3 | 6 | 14 | 65 | 1550 | 50 | 2480.3424 | 0 | 0 | 2480.3424 | Heating | 2188.5374 | 8.5 | 2188.5374 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 437.7075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2233.2015 | 0 | 446.6403 | 4.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 15:00 | 3 | 6 | 15 | 65 | 1551 | 37.94 | 2549.109 | 0 | 0 | 2549.109 | Heating | 2249.2138 | 8.5 | 2249.2138 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.8428 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2295.1161 | 0 | 459.0232 | 4.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 16:00 | 3 | 6 | 16 | 65 | 1552 | 33.8 | 2622.5357 | 0 | 0 | 2622.5357 | Heating | 2314.0021 | 8.5 | 2314.0021 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 462.8004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2361.2267 | 0 | 472.2453 | 4.722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 17:00 | 3 | 6 | 17 | 65 | 1553 | 33.98 | 2927.2529 | 0 | 0 | 2927.2529 | Heating | 2582.8702 | 8.5 | 2582.8702 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 516.574 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2635.5819 | 0 | 527.1164 | 5.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 18:00 | 3 | 6 | 18 | 65 | 1554 | 32 | 3389.012 | 0 | 0 | 3389.012 | Heating | 2990.3047 | 8.5 | 2990.3047 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 598.0609 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3051.3313 | 0 | 610.2663 | 6.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 19:00 | 3 | 6 | 19 | 65 | 1555 | 32 | 3805.5259 | 0 | 0 | 3805.5259 | Heating | 3357.817 | 8.5 | 3357.817 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 671.5634 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3426.3439 | 0 | 685.2688 | 6.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 20:00 | 3 | 6 | 20 | 65 | 1556 | 30.92 | 4224.2392 | 0 | 0 | 4224.2392 | Heating | 3727.2698 | 8.5 | 3727.2698 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3803.3366 | 0 | 760.6673 | 7.607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 21:00 | 3 | 6 | 21 | 65 | 1557 | 30.02 | 4705.0415 | 0 | 0 | 4705.0415 | Heating | 4151.5072 | 8.5 | 4151.5072 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 830.3014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4236.2318 | 0 | 847.2464 | 8.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 22:00 | 3 | 6 | 22 | 65 | 1558 | 30.92 | 1396.7092 | 0 | 0 | 1396.7092 | Heating | 1232.3905 | 8.5 | 1232.3905 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 246.4781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1257.5413 | 0 | 251.5083 | 2.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-06 23:00 | 3 | 6 | 23 | 65 | 1559 | 30.92 | 1231.0063 | 0 | 0 | 1231.0063 | Heating | 1086.182 | 8.5 | 1086.182 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.2364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1108.349 | 0 | 221.6698 | 2.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 | 3 | 7 | 0 | 66 | 1560 | 30.2 | 1412.4103 | 0 | 0 | 1412.4103 | Heating | 1246.2444 | 8.5 | 1246.2444 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.2489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1271.6779 | 0 | 254.3356 | 2.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 01:00 | 3 | 7 | 1 | 66 | 1561 | 28.94 | 1552.9311 | 0 | 0 | 1552.9311 | Heating | 1370.2333 | 8.5 | 1370.2333 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.0467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1398.1972 | 0 | 279.6394 | 2.796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 02:00 | 3 | 7 | 2 | 66 | 1562 | 28.94 | 1631.8581 | 0 | 0 | 1631.8581 | Heating | 1439.8748 | 8.5 | 1439.8748 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 287.975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1469.26 | 0 | 293.852 | 2.939% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 03:00 | 3 | 7 | 3 | 66 | 1563 | 26.6 | 1678.5054 | 0 | 0 | 1678.5054 | Heating | 1481.0342 | 8.5 | 1481.0342 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.2068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1511.2594 | 0 | 302.2519 | 3.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 04:00 | 3 | 7 | 4 | 66 | 1564 | 24.8 | 1705.4765 | 0 | 0 | 1705.4765 | Heating | 1504.8322 | 8.5 | 1504.8322 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.9664 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1535.5431 | 0 | 307.1086 | 3.071% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 05:00 | 3 | 7 | 5 | 66 | 1565 | 24.98 | 1758.0375 | 0 | 0 | 1758.0375 | Heating | 1551.2095 | 8.5 | 1551.2095 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 310.2419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1582.8669 | 0 | 316.5734 | 3.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 06:00 | 3 | 7 | 6 | 66 | 1566 | 24.8 | 1816.8235 | 0 | 0 | 1816.8235 | Heating | 1603.0795 | 8.5 | 1603.0795 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.6159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1635.7955 | 0 | 327.1591 | 3.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 07:00 | 3 | 7 | 7 | 66 | 1567 | 24.8 | 11319.4631 | 0 | 0 | 11319.4631 | Heating | 9987.7615 | 8.5 | 9987.7615 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1997.5523 | 39.95% | 1 | 79.9% | 0% | 0% | 0% | 48.6437 | 0 | 0 | 0 | 48.6437 | 10191.5934 | 0 | 2038.3187 | 20.38% | 1 | 40.77% | 0% | 0% | 5.1738 | 0 | 0 | 5.1738 | 53.8175
2007-03-07 08:00 | 3 | 7 | 8 | 66 | 1568 | 23 | 8271.4156 | 0 | 0 | 8271.4156 | Heating | 7298.3078 | 8.5 | 7298.3078 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1459.6616 | 30% | 1 | 58.39% | 0% | 0% | 0% | 23.6407 | 0 | 0 | 0 | 23.6407 | 7447.2529 | 0 | 1489.4506 | 14.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.9153
2007-03-07 09:00 | 3 | 7 | 9 | 66 | 1569 | 24.8 | 6349.7673 | 0 | 0 | 6349.7673 | Heating | 5602.7358 | 8.5 | 5602.7358 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1120.5472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5717.0774 | 0 | 1143.4155 | 11.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 10:00 | 3 | 7 | 10 | 66 | 1570 | 24.8 | 4583.6561 | 0 | 0 | 4583.6561 | Heating | 4044.4024 | 8.5 | 4044.4024 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 808.8805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4126.9413 | 0 | 825.3883 | 8.254% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 11:00 | 3 | 7 | 11 | 66 | 1571 | 24.08 | 3799.7239 | 0 | 0 | 3799.7239 | Heating | 3352.6976 | 8.5 | 3352.6976 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 670.5395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3421.12 | 0 | 684.224 | 6.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 12:00 | 3 | 7 | 12 | 66 | 1572 | 24.8 | 3279.3856 | 0 | 0 | 3279.3856 | Heating | 2893.5755 | 8.5 | 2893.5755 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 578.7151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2952.6281 | 0 | 590.5256 | 5.905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 13:00 | 3 | 7 | 13 | 66 | 1573 | 24.8 | 3006.6523 | 0 | 0 | 3006.6523 | Heating | 2652.9285 | 8.5 | 2652.9285 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 530.5857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2707.0699 | 0 | 541.414 | 5.414% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 14:00 | 3 | 7 | 14 | 66 | 1574 | 26.96 | 2884.4456 | 0 | 0 | 2884.4456 | Heating | 2545.099 | 8.5 | 2545.099 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 509.0198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2597.0398 | 0 | 519.408 | 5.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 15:00 | 3 | 7 | 15 | 66 | 1575 | 28.94 | 2881.6896 | 0 | 0 | 2881.6896 | Heating | 2542.6673 | 8.5 | 2542.6673 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 508.5335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2594.5584 | 0 | 518.9117 | 5.189% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 16:00 | 3 | 7 | 16 | 66 | 1576 | 30.02 | 2938.7362 | 0 | 0 | 2938.7362 | Heating | 2593.0026 | 8.5 | 2593.0026 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 518.6005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2645.921 | 0 | 529.1842 | 5.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 17:00 | 3 | 7 | 17 | 66 | 1577 | 30.02 | 3239.5852 | 0 | 0 | 3239.5852 | Heating | 2858.4575 | 8.5 | 2858.4575 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 571.6915 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2916.7934 | 0 | 583.3587 | 5.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 18:00 | 3 | 7 | 18 | 66 | 1578 | 28.04 | 3721.9968 | 0 | 0 | 3721.9968 | Heating | 3284.1148 | 8.5 | 3284.1148 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 656.823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3351.1375 | 0 | 670.2275 | 6.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 19:00 | 3 | 7 | 19 | 66 | 1579 | 26.96 | 4172.7589 | 0 | 0 | 4172.7589 | Heating | 3681.846 | 8.5 | 3681.846 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 736.3692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3756.9858 | 0 | 751.3972 | 7.514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 20:00 | 3 | 7 | 20 | 66 | 1580 | 26.96 | 4546.1697 | 0 | 0 | 4546.1697 | Heating | 4011.3262 | 8.5 | 4011.3262 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 802.2652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4093.19 | 0 | 818.638 | 8.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 21:00 | 3 | 7 | 21 | 66 | 1581 | 24.98 | 4936.5592 | 0 | 0 | 4936.5592 | Heating | 4355.7876 | 8.5 | 4355.7876 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 871.1575 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4444.6812 | 0 | 888.9362 | 8.889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 22:00 | 3 | 7 | 22 | 66 | 1582 | 23 | 1468.8562 | 0 | 0 | 1468.8562 | Heating | 1296.0496 | 8.5 | 1296.0496 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 259.2099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1322.4996 | 0 | 264.4999 | 2.645% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-07 23:00 | 3 | 7 | 23 | 66 | 1583 | 23 | 1318.0155 | 0 | 0 | 1318.0155 | Heating | 1162.9549 | 8.5 | 1162.9549 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 232.591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1186.6886 | 0 | 237.3377 | 2.373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 | 3 | 8 | 0 | 67 | 1584 | 19.04 | 1529.8976 | 0 | 0 | 1529.8976 | Heating | 1349.9096 | 8.5 | 1349.9096 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 269.9819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1377.4588 | 0 | 275.4918 | 2.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 01:00 | 3 | 8 | 1 | 67 | 1585 | 14 | 1682.8945 | 0 | 0 | 1682.8945 | Heating | 1484.9069 | 8.5 | 1484.9069 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.9814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1515.2112 | 0 | 303.0422 | 3.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 02:00 | 3 | 8 | 2 | 67 | 1586 | 14 | 1846.9369 | 0 | 0 | 1846.9369 | Heating | 1629.6502 | 8.5 | 1629.6502 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 325.93 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1662.9084 | 0 | 332.5817 | 3.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 03:00 | 3 | 8 | 3 | 67 | 1587 | 12.92 | 2023.7721 | 0 | 0 | 2023.7721 | Heating | 1785.6813 | 8.5 | 1785.6813 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 357.1363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1822.1237 | 0 | 364.4247 | 3.644% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 04:00 | 3 | 8 | 4 | 67 | 1588 | 12.02 | 2194.0856 | 0 | 0 | 2194.0856 | Heating | 1935.9579 | 8.5 | 1935.9579 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.1916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1975.4673 | 0 | 395.0935 | 3.951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 05:00 | 3 | 8 | 5 | 67 | 1589 | 12.02 | 2294.0434 | 0 | 0 | 2294.0434 | Heating | 2024.156 | 8.5 | 2024.156 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.8312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2065.4653 | 0 | 413.0931 | 4.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 06:00 | 3 | 8 | 6 | 67 | 1590 | 12.02 | 2331.6064 | 0 | 0 | 2331.6064 | Heating | 2057.2998 | 8.5 | 2057.2998 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.46 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2099.2855 | 0 | 419.8571 | 4.199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 07:00 | 3 | 8 | 7 | 67 | 1591 | 14 | 12572.8095 | 0 | 0 | 12572.8095 | Heating | 11093.6554 | 8.5 | 11093.6554 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2218.7311 | 44.37% | 1 | 88.75% | 0% | 0% | 0% | 61.9329 | 0 | 0 | 0 | 61.9329 | 11320.0565 | 0 | 2264.0113 | 22.64% | 1 | 45.28% | 0% | 0% | 6.5872 | 0 | 0 | 6.5872 | 68.5202
2007-03-08 08:00 | 3 | 8 | 8 | 67 | 1592 | 14 | 9506.0336 | 0 | 0 | 9506.0336 | Heating | 8387.6767 | 8.5 | 8387.6767 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1677.5353 | 33.55% | 1 | 67.1% | 0% | 0% | 0% | 32.5556 | 0 | 0 | 0 | 32.5556 | 8558.8538 | 0 | 1711.7708 | 17.12% | 1 | 34.24% | 0% | 0% | 3.4626 | 0 | 0 | 3.4626 | 36.0183
2007-03-08 09:00 | 3 | 8 | 9 | 67 | 1593 | 19.04 | 7654.0034 | 0 | 0 | 7654.0034 | Heating | 6753.5324 | 8.5 | 6753.5324 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1350.7065 | 30% | 1 | 54.03% | 0% | 0% | 0% | 19.7775 | 0 | 0 | 0 | 19.7775 | 6891.3596 | 0 | 1378.2719 | 13.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.052
2007-03-08 10:00 | 3 | 8 | 10 | 67 | 1594 | 24.08 | 6045.0674 | 0 | 0 | 6045.0674 | Heating | 5333.883 | 8.5 | 5333.883 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1066.7766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5442.7378 | 0 | 1088.5476 | 10.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 11:00 | 3 | 8 | 11 | 67 | 1595 | 24.08 | 5191.1593 | 0 | 0 | 5191.1593 | Heating | 4580.4347 | 8.5 | 4580.4347 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 916.0869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4673.9129 | 0 | 934.7826 | 9.348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 12:00 | 3 | 8 | 12 | 67 | 1596 | 26.96 | 4604.5645 | 0 | 0 | 4604.5645 | Heating | 4062.851 | 8.5 | 4062.851 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 812.5702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4145.7663 | 0 | 829.1533 | 8.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 13:00 | 3 | 8 | 13 | 67 | 1597 | 28.94 | 4319.7963 | 0 | 0 | 4319.7963 | Heating | 3811.5849 | 8.5 | 3811.5849 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 762.317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3889.3724 | 0 | 777.8745 | 7.779% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 14:00 | 3 | 8 | 14 | 67 | 1598 | 28.94 | 4113.0854 | 0 | 0 | 4113.0854 | Heating | 3629.193 | 8.5 | 3629.193 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 725.8386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3703.2581 | 0 | 740.6516 | 7.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 15:00 | 3 | 8 | 15 | 67 | 1599 | 30.92 | 3987.2502 | 0 | 0 | 3987.2502 | Heating | 3518.1619 | 8.5 | 3518.1619 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 703.6324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3589.9612 | 0 | 717.9922 | 7.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 16:00 | 3 | 8 | 16 | 67 | 1600 | 30.92 | 3925.6278 | 0 | 0 | 3925.6278 | Heating | 3463.7892 | 8.5 | 3463.7892 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 692.7578 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3534.4788 | 0 | 706.8958 | 7.069% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 17:00 | 3 | 8 | 17 | 67 | 1601 | 30.92 | 4176.2555 | 0 | 0 | 4176.2555 | Heating | 3684.9314 | 8.5 | 3684.9314 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 736.9863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3760.134 | 0 | 752.0268 | 7.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 18:00 | 3 | 8 | 18 | 67 | 1602 | 28.94 | 4668.3074 | 0 | 0 | 4668.3074 | Heating | 4119.0947 | 8.5 | 4119.0947 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 823.8189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4203.1579 | 0 | 840.6316 | 8.406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 19:00 | 3 | 8 | 19 | 67 | 1603 | 24.98 | 5112.6018 | 0 | 0 | 5112.6018 | Heating | 4511.1192 | 8.5 | 4511.1192 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 902.2238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4603.1829 | 0 | 920.6366 | 9.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 20:00 | 3 | 8 | 20 | 67 | 1604 | 24.98 | 5559.3759 | 0 | 0 | 5559.3759 | Heating | 4905.3317 | 8.5 | 4905.3317 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 981.0663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5005.4405 | 0 | 1001.0881 | 10.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 21:00 | 3 | 8 | 21 | 67 | 1605 | 24.08 | 6146.2162 | 0 | 0 | 6146.2162 | Heating | 5423.1319 | 8.5 | 5423.1319 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1084.6264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5533.8081 | 0 | 1106.7616 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 22:00 | 3 | 8 | 22 | 67 | 1606 | 21.92 | 1900.8041 | 0 | 0 | 1900.8041 | Heating | 1677.1801 | 8.5 | 1677.1801 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 335.436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1711.4082 | 0 | 342.2816 | 3.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-08 23:00 | 3 | 8 | 23 | 67 | 1607 | 21.92 | 1905.8986 | 0 | 0 | 1905.8986 | Heating | 1681.6752 | 8.5 | 1681.6752 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1715.9951 | 0 | 343.199 | 3.432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 | 3 | 9 | 0 | 68 | 1608 | 19.94 | 2270.494 | 0 | 0 | 2270.494 | Heating | 2003.377 | 8.5 | 2003.377 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 400.6754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2044.2623 | 0 | 408.8525 | 4.089% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 01:00 | 3 | 9 | 1 | 68 | 1609 | 19.04 | 2528.7876 | 0 | 0 | 2528.7876 | Heating | 2231.2832 | 8.5 | 2231.2832 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 446.2566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2276.8196 | 0 | 455.3639 | 4.554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 02:00 | 3 | 9 | 2 | 68 | 1610 | 19.04 | 2659.2942 | 0 | 0 | 2659.2942 | Heating | 2346.436 | 8.5 | 2346.436 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 469.2872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2394.3225 | 0 | 478.8645 | 4.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 03:00 | 3 | 9 | 3 | 68 | 1611 | 17.06 | 2720.7158 | 0 | 0 | 2720.7158 | Heating | 2400.6316 | 8.5 | 2400.6316 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 480.1263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2449.624 | 0 | 489.9248 | 4.899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 04:00 | 3 | 9 | 4 | 68 | 1612 | 15.08 | 2765.1195 | 0 | 0 | 2765.1195 | Heating | 2439.8113 | 8.5 | 2439.8113 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 487.9623 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2489.6034 | 0 | 497.9207 | 4.979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 05:00 | 3 | 9 | 5 | 68 | 1613 | 15.08 | 2791.0694 | 0 | 0 | 2791.0694 | Heating | 2462.7083 | 8.5 | 2462.7083 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 492.5417 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2512.9676 | 0 | 502.5935 | 5.026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 06:00 | 3 | 9 | 6 | 68 | 1614 | 14 | 2801.8688 | 0 | 0 | 2801.8688 | Heating | 2472.2372 | 8.5 | 2472.2372 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.4474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2522.691 | 0 | 504.5382 | 5.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 07:00 | 3 | 9 | 7 | 68 | 1615 | 15.08 | 13455.5081 | 0 | 0 | 13455.5081 | Heating | 11872.5071 | 8.5 | 11872.5071 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2374.5014 | 47.49% | 1 | 94.98% | 0% | 0% | 0% | 72.3932 | 0 | 0 | 0 | 72.3932 | 12114.8032 | 0 | 2422.9606 | 24.23% | 1 | 48.46% | 0% | 0% | 7.6998 | 0 | 0 | 7.6998 | 80.093
2007-03-09 08:00 | 3 | 9 | 8 | 68 | 1616 | 15.08 | 10669.986 | 0 | 0 | 10669.986 | Heating | 9414.6935 | 8.5 | 9414.6935 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1882.9387 | 37.66% | 1 | 75.32% | 0% | 0% | 0% | 42.4624 | 0 | 0 | 0 | 42.4624 | 9606.8301 | 0 | 1921.366 | 19.21% | 1 | 38.43% | 0% | 0% | 4.5163 | 0 | 0 | 4.5163 | 46.9787
2007-03-09 09:00 | 3 | 9 | 9 | 68 | 1617 | 19.94 | 8800.028 | 0 | 0 | 8800.028 | Heating | 7764.7306 | 8.5 | 7764.7306 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1552.9461 | 31.06% | 1 | 62.12% | 0% | 0% | 0% | 27.2609 | 0 | 0 | 0 | 27.2609 | 7923.1945 | 0 | 1584.6389 | 15.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.5355
2007-03-09 10:00 | 3 | 9 | 10 | 68 | 1618 | 24.08 | 7146.011 | 0 | 0 | 7146.011 | Heating | 6305.3038 | 8.5 | 6305.3038 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1261.0608 | 30% | 1 | 50.44% | 0% | 0% | 0% | 16.8878 | 0 | 0 | 0 | 16.8878 | 6433.9835 | 0 | 1286.7967 | 12.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.1624
2007-03-09 11:00 | 3 | 9 | 11 | 68 | 1619 | 24.08 | 5853.3318 | 0 | 0 | 5853.3318 | Heating | 5164.7046 | 8.5 | 5164.7046 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1032.9409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5270.1067 | 0 | 1054.0213 | 10.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 12:00 | 3 | 9 | 12 | 68 | 1620 | 32 | 4903.8253 | 0 | 0 | 4903.8253 | Heating | 4326.9047 | 8.5 | 4326.9047 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 865.3809 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4415.2088 | 0 | 883.0418 | 8.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 13:00 | 3 | 9 | 13 | 68 | 1621 | 33.08 | 4253.802 | 0 | 0 | 4253.802 | Heating | 3753.3547 | 8.5 | 3753.3547 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.6709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3829.9538 | 0 | 765.9908 | 7.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 14:00 | 3 | 9 | 14 | 68 | 1622 | 33.08 | 4006.1407 | 0 | 0 | 4006.1407 | Heating | 3534.83 | 8.5 | 3534.83 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 706.966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3606.9694 | 0 | 721.3939 | 7.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 15:00 | 3 | 9 | 15 | 68 | 1623 | 35.06 | 4016.0215 | 0 | 0 | 4016.0215 | Heating | 3543.5483 | 8.5 | 3543.5483 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 708.7097 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3615.8657 | 0 | 723.1731 | 7.232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 16:00 | 3 | 9 | 16 | 68 | 1624 | 35.96 | 4022.4277 | 0 | 0 | 4022.4277 | Heating | 3549.2009 | 8.5 | 3549.2009 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 709.8402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3621.6336 | 0 | 724.3267 | 7.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 17:00 | 3 | 9 | 17 | 68 | 1625 | 35.96 | 4198.8898 | 0 | 0 | 4198.8898 | Heating | 3704.9027 | 8.5 | 3704.9027 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 740.9805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3780.513 | 0 | 756.1026 | 7.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 18:00 | 3 | 9 | 18 | 68 | 1626 | 37.04 | 4607.1163 | 0 | 0 | 4607.1163 | Heating | 4065.1026 | 8.5 | 4065.1026 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 813.0205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4148.0639 | 0 | 829.6128 | 8.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 19:00 | 3 | 9 | 19 | 68 | 1627 | 35.96 | 5189.6839 | 0 | 0 | 5189.6839 | Heating | 4579.1329 | 8.5 | 4579.1329 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 915.8266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4672.5846 | 0 | 934.5169 | 9.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 20:00 | 3 | 9 | 20 | 68 | 1628 | 35.96 | 5878.0526 | 0 | 0 | 5878.0526 | Heating | 5186.517 | 8.5 | 5186.517 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1037.3034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5292.3643 | 0 | 1058.4729 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 21:00 | 3 | 9 | 21 | 68 | 1629 | 35.06 | 6235.8393 | 0 | 0 | 6235.8393 | Heating | 5502.2112 | 8.5 | 5502.2112 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1100.4422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5614.5012 | 0 | 1122.9002 | 11.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 22:00 | 3 | 9 | 22 | 68 | 1630 | 35.06 | 6779.3416 | 0 | 0 | 6779.3416 | Heating | 5981.772 | 8.5 | 5981.772 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1196.3544 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6103.849 | 0 | 1220.7698 | 12.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-09 23:00 | 3 | 9 | 23 | 68 | 1631 | 35.06 | 2029.9433 | 0 | 0 | 2029.9433 | Heating | 1791.1265 | 8.5 | 1791.1265 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.2253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1827.6801 | 0 | 365.536 | 3.655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 | 3 | 10 | 0 | 69 | 1632 | 35.06 | 2058.642 | 0 | 0 | 2058.642 | Heating | 1816.4489 | 8.5 | 1816.4489 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.2898 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1853.5192 | 0 | 370.7038 | 3.707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 01:00 | 3 | 10 | 1 | 69 | 1633 | 33.98 | 2076.1962 | 0 | 0 | 2076.1962 | Heating | 1831.9378 | 8.5 | 1831.9378 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 366.3876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1869.3243 | 0 | 373.8649 | 3.739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 02:00 | 3 | 10 | 2 | 69 | 1634 | 33.98 | 2167.2783 | 0 | 0 | 2167.2783 | Heating | 1912.3043 | 8.5 | 1912.3043 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 382.4609 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1951.331 | 0 | 390.2662 | 3.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 03:00 | 3 | 10 | 3 | 69 | 1635 | 35.6 | 2302.3365 | 0 | 0 | 2302.3365 | Heating | 2031.4734 | 8.5 | 2031.4734 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 406.2947 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2072.932 | 0 | 414.5864 | 4.146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 04:00 | 3 | 10 | 4 | 69 | 1636 | 35.06 | 2444.4043 | 0 | 0 | 2444.4043 | Heating | 2156.8273 | 8.5 | 2156.8273 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 431.3655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2200.8442 | 0 | 440.1688 | 4.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 05:00 | 3 | 10 | 5 | 69 | 1637 | 35.06 | 2494.695 | 0 | 0 | 2494.695 | Heating | 2201.2015 | 8.5 | 2201.2015 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 440.2403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2246.124 | 0 | 449.2248 | 4.492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 06:00 | 3 | 10 | 6 | 69 | 1638 | 35.6 | 2472.2927 | 0 | 0 | 2472.2927 | Heating | 2181.4347 | 8.5 | 2181.4347 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 436.2869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2225.9538 | 0 | 445.1908 | 4.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 07:00 | 3 | 10 | 7 | 69 | 1639 | 35.06 | 2416.9847 | 0 | 0 | 2416.9847 | Heating | 2132.6335 | 8.5 | 2132.6335 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.5267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2176.1567 | 0 | 435.2313 | 4.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 08:00 | 3 | 10 | 8 | 69 | 1640 | 35.06 | 2172.1889 | 0 | 0 | 2172.1889 | Heating | 1916.6372 | 8.5 | 1916.6372 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 383.3274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1955.7523 | 0 | 391.1505 | 3.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 09:00 | 3 | 10 | 9 | 69 | 1641 | 35.6 | 10986.5189 | 0 | 0 | 10986.5189 | Heating | 9693.9873 | 8.5 | 9693.9873 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1938.7975 | 38.78% | 1 | 77.55% | 0% | 0% | 0% | 45.4157 | 0 | 0 | 0 | 45.4157 | 9891.8238 | 0 | 1978.3648 | 19.78% | 1 | 39.57% | 0% | 0% | 4.8304 | 0 | 0 | 4.8304 | 50.2461
2007-03-10 10:00 | 3 | 10 | 10 | 69 | 1642 | 35.6 | 7372.8595 | 0 | 0 | 7372.8595 | Heating | 6505.4643 | 8.5 | 6505.4643 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1301.0929 | 30% | 1 | 52.04% | 0% | 0% | 0% | 18.1464 | 0 | 0 | 0 | 18.1464 | 6638.2289 | 0 | 1327.6458 | 13.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.4209
2007-03-10 11:00 | 3 | 10 | 11 | 69 | 1643 | 35.06 | 5455.2876 | 0 | 0 | 5455.2876 | Heating | 4813.489 | 8.5 | 4813.489 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 962.6978 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4911.7235 | 0 | 982.3447 | 9.823% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 12:00 | 3 | 10 | 12 | 69 | 1644 | 37.94 | 4338.1103 | 0 | 0 | 4338.1103 | Heating | 3827.7444 | 8.5 | 3827.7444 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 765.5489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3905.8616 | 0 | 781.1723 | 7.812% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 13:00 | 3 | 10 | 13 | 69 | 1645 | 39.2 | 3292.8026 | 0 | 0 | 3292.8026 | Heating | 2905.4141 | 8.5 | 2905.4141 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 581.0828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2964.7082 | 0 | 592.9416 | 5.929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 14:00 | 3 | 10 | 14 | 69 | 1646 | 39.02 | 2952.856 | 0 | 0 | 2952.856 | Heating | 2605.4612 | 8.5 | 2605.4612 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 521.0922 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2658.6338 | 0 | 531.7268 | 5.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 15:00 | 3 | 10 | 15 | 69 | 1647 | 39.92 | 2916.1847 | 0 | 0 | 2916.1847 | Heating | 2573.1041 | 8.5 | 2573.1041 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 514.6208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2625.6164 | 0 | 525.1233 | 5.251% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 16:00 | 3 | 10 | 16 | 69 | 1648 | 41 | 2956.7034 | 0 | 0 | 2956.7034 | Heating | 2608.8559 | 8.5 | 2608.8559 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 521.7712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2662.0979 | 0 | 532.4196 | 5.324% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 17:00 | 3 | 10 | 17 | 69 | 1649 | 41 | 3148.6695 | 0 | 0 | 3148.6695 | Heating | 2778.2378 | 8.5 | 2778.2378 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 555.6476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2834.9365 | 0 | 566.9873 | 5.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 18:00 | 3 | 10 | 18 | 69 | 1650 | 37.4 | 4872.5563 | 0 | 0 | 4872.5563 | Heating | 4299.3144 | 8.5 | 4299.3144 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 859.8629 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4387.0555 | 0 | 877.4111 | 8.774% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 19:00 | 3 | 10 | 19 | 69 | 1651 | 42.98 | 5545.3553 | 0 | 0 | 5545.3553 | Heating | 4892.9606 | 8.5 | 4892.9606 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 978.5921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4992.8169 | 0 | 998.5634 | 9.986% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 20:00 | 3 | 10 | 20 | 69 | 1652 | 42.98 | 1308.9625 | 0 | 0 | 1308.9625 | Heating | 1154.9669 | 8.5 | 1154.9669 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.9934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1178.5376 | 0 | 235.7075 | 2.357% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 21:00 | 3 | 10 | 21 | 69 | 1653 | 42.8 | 1373.4526 | 0 | 0 | 1373.4526 | Heating | 1211.8699 | 8.5 | 1211.8699 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1236.602 | 0 | 247.3204 | 2.473% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 22:00 | 3 | 10 | 22 | 69 | 1654 | 42.8 | 1433.6085 | 0 | 0 | 1433.6085 | Heating | 1264.9487 | 8.5 | 1264.9487 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.9897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1290.764 | 0 | 258.1528 | 2.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-10 23:00 | 3 | 10 | 23 | 69 | 1655 | 42.98 | 1505.9816 | 0 | 0 | 1505.9816 | Heating | 1328.8073 | 8.5 | 1328.8073 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 265.7615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1355.9258 | 0 | 271.1852 | 2.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 | 3 | 11 | 0 | 70 | 1656 | 42.98 | 1568.838 | 0 | 0 | 1568.838 | Heating | 1384.2688 | 8.5 | 1384.2688 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 276.8538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1412.5192 | 0 | 282.5038 | 2.825% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 01:00 | 3 | 11 | 1 | 70 | 1657 | 46.04 | 1621.3719 | 0 | 0 | 1621.3719 | Heating | 1430.6223 | 8.5 | 1430.6223 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.1245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1459.8186 | 0 | 291.9637 | 2.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 02:00 | 3 | 11 | 2 | 70 | 1658 | 46.04 | 1659.2216 | 0 | 0 | 1659.2216 | Heating | 1464.0191 | 8.5 | 1464.0191 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.8038 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1493.897 | 0 | 298.7794 | 2.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 03:00 | 3 | 11 | 3 | 70 | 1659 | 46.04 | 1683.4981 | 0 | 0 | 1683.4981 | Heating | 1485.4395 | 8.5 | 1485.4395 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.0879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1515.7546 | 0 | 303.1509 | 3.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 04:00 | 3 | 11 | 4 | 70 | 1660 | 42.98 | 1704.1676 | 0 | 0 | 1704.1676 | Heating | 1503.6773 | 8.5 | 1503.6773 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.7355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1534.3646 | 0 | 306.8729 | 3.069% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 05:00 | 3 | 11 | 5 | 70 | 1661 | 42.98 | 1710.6618 | 0 | 0 | 1710.6618 | Heating | 1509.4075 | 8.5 | 1509.4075 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.8815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1540.2117 | 0 | 308.0423 | 3.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 06:00 | 3 | 11 | 6 | 70 | 1662 | 44.6 | 1694.6478 | 0 | 0 | 1694.6478 | Heating | 1495.2775 | 8.5 | 1495.2775 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 299.0555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1525.7934 | 0 | 305.1587 | 3.052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 07:00 | 3 | 11 | 7 | 70 | 1663 | 44.6 | 10255.5179 | 0 | 0 | 10255.5179 | Heating | 9048.9864 | 8.5 | 9048.9864 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1809.7973 | 36.2% | 1 | 72.39% | 0% | 0% | 0% | 38.7641 | 0 | 0 | 0 | 38.7641 | 9233.6596 | 0 | 1846.7319 | 18.47% | 1 | 36.93% | 0% | 0% | 4.123 | 0 | 0 | 4.123 | 42.8871
2007-03-11 08:00 | 3 | 11 | 8 | 70 | 1664 | 44.06 | 7665.1953 | 0 | 0 | 7665.1953 | Heating | 6763.4076 | 8.5 | 6763.4076 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1352.6815 | 30% | 1 | 54.11% | 0% | 0% | 0% | 19.8441 | 0 | 0 | 0 | 19.8441 | 6901.4363 | 0 | 1380.2873 | 13.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.1186
2007-03-11 09:00 | 3 | 11 | 9 | 70 | 1665 | 42.98 | 6156.309 | 0 | 0 | 6156.309 | Heating | 5432.0373 | 8.5 | 5432.0373 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1086.4075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5542.8953 | 0 | 1108.5791 | 11.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 10:00 | 3 | 11 | 10 | 70 | 1666 | 44.96 | 4750.078 | 0 | 0 | 4750.078 | Heating | 4191.2453 | 8.5 | 4191.2453 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 838.2491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4276.7809 | 0 | 855.3562 | 8.554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 11:00 | 3 | 11 | 11 | 70 | 1667 | 44.96 | 4025.6283 | 0 | 0 | 4025.6283 | Heating | 3552.025 | 8.5 | 3552.025 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 710.405 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3624.5153 | 0 | 724.9031 | 7.249% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 12:00 | 3 | 11 | 12 | 70 | 1668 | 50 | 3395.4222 | 0 | 0 | 3395.4222 | Heating | 2995.9607 | 8.5 | 2995.9607 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 599.1921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3057.1028 | 0 | 611.4206 | 6.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 13:00 | 3 | 11 | 13 | 70 | 1669 | 51.08 | 3019.4781 | 0 | 0 | 3019.4781 | Heating | 2664.2454 | 8.5 | 2664.2454 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 532.8491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2718.6178 | 0 | 543.7236 | 5.437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 14:00 | 3 | 11 | 14 | 70 | 1670 | 51.08 | 2809.2455 | 0 | 0 | 2809.2455 | Heating | 2478.746 | 8.5 | 2478.746 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 495.7492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2529.3327 | 0 | 505.8665 | 5.059% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 15:00 | 3 | 11 | 15 | 70 | 1671 | 53.06 | 2710.3889 | 0 | 0 | 2710.3889 | Heating | 2391.5196 | 8.5 | 2391.5196 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 478.3039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2440.3262 | 0 | 488.0652 | 4.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 16:00 | 3 | 11 | 16 | 70 | 1672 | 53.06 | 2707.8915 | 0 | 0 | 2707.8915 | Heating | 2389.316 | 8.5 | 2389.316 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 477.8632 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2438.0776 | 0 | 487.6155 | 4.876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 17:00 | 3 | 11 | 17 | 70 | 1673 | 53.06 | 3017.5191 | 0 | 0 | 3017.5191 | Heating | 2662.5168 | 8.5 | 2662.5168 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 532.5034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2716.8539 | 0 | 543.3708 | 5.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 18:00 | 3 | 11 | 18 | 70 | 1674 | 48.92 | 3532.1644 | 0 | 0 | 3532.1644 | Heating | 3116.6156 | 8.5 | 3116.6156 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 623.3231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3180.22 | 0 | 636.044 | 6.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 19:00 | 3 | 11 | 19 | 70 | 1675 | 42.98 | 3990.7333 | 0 | 0 | 3990.7333 | Heating | 3521.2353 | 8.5 | 3521.2353 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 704.2471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3593.0972 | 0 | 718.6194 | 7.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 20:00 | 3 | 11 | 20 | 70 | 1676 | 42.98 | 4511.9623 | 0 | 0 | 4511.9623 | Heating | 3981.1432 | 8.5 | 3981.1432 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 796.2286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4062.3911 | 0 | 812.4782 | 8.125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 21:00 | 3 | 11 | 21 | 70 | 1677 | 42.08 | 5025.0409 | 0 | 0 | 5025.0409 | Heating | 4433.8596 | 8.5 | 4433.8596 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 886.7719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4524.3465 | 0 | 904.8693 | 9.049% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 22:00 | 3 | 11 | 22 | 70 | 1678 | 39.92 | 1543.1895 | 0 | 0 | 1543.1895 | Heating | 1361.6378 | 8.5 | 1361.6378 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.3276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1389.4263 | 0 | 277.8853 | 2.779% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-11 23:00 | 3 | 11 | 23 | 70 | 1679 | 39.92 | 1509.4055 | 0 | 0 | 1509.4055 | Heating | 1331.8284 | 8.5 | 1331.8284 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.3657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1359.0085 | 0 | 271.8017 | 2.718% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 | 3 | 12 | 0 | 71 | 1680 | 37.94 | 1868.3866 | 0 | 0 | 1868.3866 | Heating | 1648.5764 | 8.5 | 1648.5764 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.7153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1682.2209 | 0 | 336.4442 | 3.364% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 01:00 | 3 | 12 | 1 | 71 | 1681 | 37.94 | 2120.3079 | 0 | 0 | 2120.3079 | Heating | 1870.8599 | 8.5 | 1870.8599 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1909.0407 | 0 | 381.8081 | 3.818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 02:00 | 3 | 12 | 2 | 71 | 1682 | 37.94 | 2288.0072 | 0 | 0 | 2288.0072 | Heating | 2018.8299 | 8.5 | 2018.8299 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 403.766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2060.0305 | 0 | 412.0061 | 4.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 03:00 | 3 | 12 | 3 | 71 | 1683 | 37.04 | 2418.6477 | 0 | 0 | 2418.6477 | Heating | 2134.1009 | 8.5 | 2134.1009 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.8202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2177.654 | 0 | 435.5308 | 4.355% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 04:00 | 3 | 12 | 4 | 71 | 1684 | 35.06 | 2527.5915 | 0 | 0 | 2527.5915 | Heating | 2230.2278 | 8.5 | 2230.2278 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 446.0456 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2275.7427 | 0 | 455.1485 | 4.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 05:00 | 3 | 12 | 5 | 71 | 1685 | 35.06 | 2586.4676 | 0 | 0 | 2586.4676 | Heating | 2282.1773 | 8.5 | 2282.1773 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 456.4355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2328.7523 | 0 | 465.7505 | 4.658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 06:00 | 3 | 12 | 6 | 71 | 1686 | 35.06 | 2606.9039 | 0 | 0 | 2606.9039 | Heating | 2300.2093 | 8.5 | 2300.2093 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 460.0419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2347.1524 | 0 | 469.4305 | 4.694% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 07:00 | 3 | 12 | 7 | 71 | 1687 | 35.06 | 13310.8284 | 0 | 0 | 13310.8284 | Heating | 11744.8486 | 8.5 | 11744.8486 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2348.9697 | 46.98% | 1 | 93.96% | 0% | 0% | 0% | 70.6153 | 0 | 0 | 0 | 70.6153 | 11984.5394 | 0 | 2396.9079 | 23.97% | 1 | 47.94% | 0% | 0% | 7.5107 | 0 | 0 | 7.5107 | 78.126
2007-03-12 08:00 | 3 | 12 | 8 | 71 | 1688 | 35.06 | 10487.3595 | 0 | 0 | 10487.3595 | Heating | 9253.5525 | 8.5 | 9253.5525 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1850.7105 | 37.01% | 1 | 74.03% | 0% | 0% | 0% | 40.8093 | 0 | 0 | 0 | 40.8093 | 9442.4005 | 0 | 1888.4801 | 18.88% | 1 | 37.77% | 0% | 0% | 4.3405 | 0 | 0 | 4.3405 | 45.1498
2007-03-12 09:00 | 3 | 12 | 9 | 71 | 1689 | 37.04 | 8194.0143 | 0 | 0 | 8194.0143 | Heating | 7230.0126 | 8.5 | 7230.0126 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1446.0025 | 30% | 1 | 57.84% | 0% | 0% | 0% | 23.135 | 0 | 0 | 0 | 23.135 | 7377.5639 | 0 | 1475.5128 | 14.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.4096
2007-03-12 10:00 | 3 | 12 | 10 | 71 | 1690 | 37.94 | 6228.6301 | 0 | 0 | 6228.6301 | Heating | 5495.8501 | 8.5 | 5495.8501 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1099.17 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5608.0103 | 0 | 1121.6021 | 11.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 11:00 | 3 | 12 | 11 | 71 | 1691 | 37.94 | 4997.1853 | 0 | 0 | 4997.1853 | Heating | 4409.2812 | 8.5 | 4409.2812 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 881.8562 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4499.2665 | 0 | 899.8533 | 8.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 12:00 | 3 | 12 | 12 | 71 | 1692 | 39.92 | 4076.2805 | 0 | 0 | 4076.2805 | Heating | 3596.7181 | 8.5 | 3596.7181 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 719.3436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3670.1205 | 0 | 734.0241 | 7.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 13:00 | 3 | 12 | 13 | 71 | 1693 | 41 | 3499.7891 | 0 | 0 | 3499.7891 | Heating | 3088.0492 | 8.5 | 3088.0492 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 617.6098 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3151.0706 | 0 | 630.2141 | 6.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 14:00 | 3 | 12 | 14 | 71 | 1694 | 41 | 3226.7501 | 0 | 0 | 3226.7501 | Heating | 2847.1324 | 8.5 | 2847.1324 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 569.4265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2905.2372 | 0 | 581.0474 | 5.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 15:00 | 3 | 12 | 15 | 71 | 1695 | 42.98 | 3177.8718 | 0 | 0 | 3177.8718 | Heating | 2804.0045 | 8.5 | 2804.0045 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 560.8009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2861.2291 | 0 | 572.2458 | 5.722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 16:00 | 3 | 12 | 16 | 71 | 1696 | 44.06 | 3135.6466 | 0 | 0 | 3135.6466 | Heating | 2766.747 | 8.5 | 2766.747 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 553.3494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2823.2112 | 0 | 564.6422 | 5.646% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 17:00 | 3 | 12 | 17 | 71 | 1697 | 44.06 | 3320.4706 | 0 | 0 | 3320.4706 | Heating | 2929.827 | 8.5 | 2929.827 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 585.9654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2989.6194 | 0 | 597.9239 | 5.979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 18:00 | 3 | 12 | 18 | 71 | 1698 | 42.98 | 3645.5417 | 0 | 0 | 3645.5417 | Heating | 3216.6544 | 8.5 | 3216.6544 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 643.3309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3282.3004 | 0 | 656.4601 | 6.565% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 19:00 | 3 | 12 | 19 | 71 | 1699 | 41 | 3916.2856 | 0 | 0 | 3916.2856 | Heating | 3455.5461 | 8.5 | 3455.5461 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 691.1092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3526.0674 | 0 | 705.2135 | 7.052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 20:00 | 3 | 12 | 20 | 71 | 1700 | 41 | 4262.1484 | 0 | 0 | 4262.1484 | Heating | 3760.7192 | 8.5 | 3760.7192 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 752.1438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3837.4686 | 0 | 767.4937 | 7.675% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 21:00 | 3 | 12 | 21 | 71 | 1701 | 39.02 | 4693.0344 | 0 | 0 | 4693.0344 | Heating | 4140.9127 | 8.5 | 4140.9127 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 828.1825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4225.4211 | 0 | 845.0842 | 8.451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 22:00 | 3 | 12 | 22 | 71 | 1702 | 37.94 | 1463.4964 | 0 | 0 | 1463.4964 | Heating | 1291.3204 | 8.5 | 1291.3204 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 258.2641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1317.6739 | 0 | 263.5348 | 2.635% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-12 23:00 | 3 | 12 | 23 | 71 | 1703 | 37.94 | 1353.215 | 0 | 0 | 1353.215 | Heating | 1194.0132 | 8.5 | 1194.0132 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.8026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1218.3808 | 0 | 243.6762 | 2.437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 | 3 | 13 | 0 | 72 | 1704 | 39.02 | 1497.8487 | 0 | 0 | 1497.8487 | Heating | 1321.6312 | 8.5 | 1321.6312 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.3262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1348.6032 | 0 | 269.7206 | 2.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 01:00 | 3 | 13 | 1 | 72 | 1705 | 39.92 | 1538.5218 | 0 | 0 | 1538.5218 | Heating | 1357.5192 | 8.5 | 1357.5192 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 271.5038 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1385.2237 | 0 | 277.0447 | 2.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 02:00 | 3 | 13 | 2 | 72 | 1706 | 39.92 | 1538.9507 | 0 | 0 | 1538.9507 | Heating | 1357.8976 | 8.5 | 1357.8976 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 271.5795 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1385.6098 | 0 | 277.122 | 2.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 03:00 | 3 | 13 | 3 | 72 | 1707 | 41 | 1513.674 | 0 | 0 | 1513.674 | Heating | 1335.5947 | 8.5 | 1335.5947 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.1189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1362.8517 | 0 | 272.5703 | 2.726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 04:00 | 3 | 13 | 4 | 72 | 1708 | 39.92 | 1476.4952 | 0 | 0 | 1476.4952 | Heating | 1302.7899 | 8.5 | 1302.7899 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 260.558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1329.3774 | 0 | 265.8755 | 2.659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 05:00 | 3 | 13 | 5 | 72 | 1709 | 39.92 | 1410.471 | 0 | 0 | 1410.471 | Heating | 1244.5332 | 8.5 | 1244.5332 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.9066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1269.9319 | 0 | 253.9864 | 2.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 06:00 | 3 | 13 | 6 | 72 | 1710 | 39.92 | 1305.5724 | 0 | 0 | 1305.5724 | Heating | 1151.9756 | 8.5 | 1151.9756 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.3951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1175.4853 | 0 | 235.0971 | 2.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 07:00 | 3 | 13 | 7 | 72 | 1711 | 39.02 | 8930.1937 | 0 | 0 | 8930.1937 | Heating | 7879.5827 | 8.5 | 7879.5827 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1575.9165 | 31.52% | 1 | 63.04% | 0% | 0% | 0% | 28.1973 | 0 | 0 | 0 | 28.1973 | 8040.3905 | 0 | 1608.0781 | 16.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.4718
2007-03-13 08:00 | 3 | 13 | 8 | 72 | 1712 | 39.02 | 6148.2195 | 0 | 0 | 6148.2195 | Heating | 5424.8996 | 8.5 | 5424.8996 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1084.9799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5535.6118 | 0 | 1107.1224 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 09:00 | 3 | 13 | 9 | 72 | 1713 | 39.02 | 4314.9067 | 0 | 0 | 4314.9067 | Heating | 3807.2706 | 8.5 | 3807.2706 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 761.4541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3884.9701 | 0 | 776.994 | 7.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 10:00 | 3 | 13 | 10 | 72 | 1714 | 39.92 | 2653.1095 | 0 | 0 | 2653.1095 | Heating | 2340.979 | 8.5 | 2340.979 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 468.1958 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2388.754 | 0 | 477.7508 | 4.778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 11:00 | 3 | 13 | 11 | 72 | 1715 | 39.92 | 1996.2869 | 0 | 0 | 1996.2869 | Heating | 1761.4296 | 8.5 | 1761.4296 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 352.2859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1797.3771 | 0 | 359.4754 | 3.595% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 12:00 | 3 | 13 | 12 | 72 | 1716 | 42.08 | 1684.5185 | 0 | 0 | 1684.5185 | Heating | 1486.3399 | 8.5 | 1486.3399 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1516.6733 | 0 | 303.3347 | 3.033% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 13:00 | 3 | 13 | 13 | 72 | 1717 | 41 | 1626.2558 | 0 | 0 | 1626.2558 | Heating | 1434.9316 | 8.5 | 1434.9316 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.9863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1464.2159 | 0 | 292.8432 | 2.928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 14:00 | 3 | 13 | 14 | 72 | 1718 | 41 | 1739.8214 | 0 | 0 | 1739.8214 | Heating | 1535.1365 | 8.5 | 1535.1365 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 307.0273 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1566.4658 | 0 | 313.2932 | 3.133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 15:00 | 3 | 13 | 15 | 72 | 1719 | 42.8 | 1984.8678 | 0 | 0 | 1984.8678 | Heating | 1751.3539 | 8.5 | 1751.3539 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 350.2708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1787.0959 | 0 | 357.4192 | 3.574% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 16:00 | 3 | 13 | 16 | 72 | 1720 | 42.08 | 2199.7079 | 0 | 0 | 2199.7079 | Heating | 1940.9187 | 8.5 | 1940.9187 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 388.1837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1980.5293 | 0 | 396.1059 | 3.961% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 17:00 | 3 | 13 | 17 | 72 | 1721 | 42.08 | 2495.3756 | 0 | 0 | 2495.3756 | Heating | 2201.802 | 8.5 | 2201.802 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 440.3604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2246.7367 | 0 | 449.3473 | 4.493% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 18:00 | 3 | 13 | 18 | 72 | 1722 | 39.02 | 2862.15 | 0 | 0 | 2862.15 | Heating | 2525.4265 | 8.5 | 2525.4265 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.0853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2576.9658 | 0 | 515.3932 | 5.154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 19:00 | 3 | 13 | 19 | 72 | 1723 | 37.94 | 3179.392 | 0 | 0 | 3179.392 | Heating | 2805.3458 | 8.5 | 2805.3458 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 561.0692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2862.5978 | 0 | 572.5196 | 5.725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 20:00 | 3 | 13 | 20 | 72 | 1724 | 37.94 | 3571.3937 | 0 | 0 | 3571.3937 | Heating | 3151.2297 | 8.5 | 3151.2297 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 630.2459 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3215.5405 | 0 | 643.1081 | 6.431% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 21:00 | 3 | 13 | 21 | 72 | 1725 | 37.04 | 4073.1385 | 0 | 0 | 4073.1385 | Heating | 3593.9457 | 8.5 | 3593.9457 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 718.7891 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3667.2916 | 0 | 733.4583 | 7.335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 22:00 | 3 | 13 | 22 | 72 | 1726 | 35.96 | 1272.8703 | 0 | 0 | 1272.8703 | Heating | 1123.1209 | 8.5 | 1123.1209 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.6242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1146.0417 | 0 | 229.2083 | 2.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-13 23:00 | 3 | 13 | 23 | 72 | 1727 | 35.96 | 1160.9718 | 0 | 0 | 1160.9718 | Heating | 1024.3869 | 8.5 | 1024.3869 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 204.8774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1045.2928 | 0 | 209.0586 | 2.091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 | 3 | 14 | 0 | 73 | 1728 | 35.06 | 1372.3088 | 0 | 0 | 1372.3088 | Heating | 1210.8607 | 8.5 | 1210.8607 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.1721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1235.5722 | 0 | 247.1144 | 2.471% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 01:00 | 3 | 14 | 1 | 73 | 1729 | 35.06 | 1512.5299 | 0 | 0 | 1512.5299 | Heating | 1334.5852 | 8.5 | 1334.5852 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1361.8217 | 0 | 272.3643 | 2.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 02:00 | 3 | 14 | 2 | 73 | 1730 | 35.06 | 1624.3292 | 0 | 0 | 1624.3292 | Heating | 1433.2317 | 8.5 | 1433.2317 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.6463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1462.4813 | 0 | 292.4963 | 2.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 03:00 | 3 | 14 | 3 | 73 | 1731 | 35.06 | 1725.5173 | 0 | 0 | 1725.5173 | Heating | 1522.5153 | 8.5 | 1522.5153 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 304.5031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1553.587 | 0 | 310.7174 | 3.107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 04:00 | 3 | 14 | 4 | 73 | 1732 | 35.06 | 1815.5532 | 0 | 0 | 1815.5532 | Heating | 1601.9587 | 8.5 | 1601.9587 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.3917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1634.6518 | 0 | 326.9304 | 3.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 05:00 | 3 | 14 | 5 | 73 | 1733 | 35.06 | 1893.5246 | 0 | 0 | 1893.5246 | Heating | 1670.757 | 8.5 | 1670.757 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 334.1514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1704.8541 | 0 | 340.9708 | 3.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 06:00 | 3 | 14 | 6 | 73 | 1734 | 33.98 | 1953.7608 | 0 | 0 | 1953.7608 | Heating | 1723.9066 | 8.5 | 1723.9066 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.7813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1759.0883 | 0 | 351.8177 | 3.518% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 07:00 | 3 | 14 | 7 | 73 | 1735 | 33.8 | 11170.6408 | 0 | 0 | 11170.6408 | Heating | 9856.4477 | 8.5 | 9856.4477 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1971.2895 | 39.43% | 1 | 78.85% | 0% | 0% | 0% | 47.1853 | 0 | 0 | 0 | 47.1853 | 10057.5997 | 0 | 2011.5199 | 20.12% | 1 | 40.23% | 0% | 0% | 5.0187 | 0 | 0 | 5.0187 | 52.204
2007-03-14 08:00 | 3 | 14 | 8 | 73 | 1736 | 33.98 | 8377.731 | 0 | 0 | 8377.731 | Heating | 7392.1156 | 8.5 | 7392.1156 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1478.4231 | 30% | 1 | 59.14% | 0% | 0% | 0% | 24.3455 | 0 | 0 | 0 | 24.3455 | 7542.9751 | 0 | 1508.595 | 15.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.62
2007-03-14 09:00 | 3 | 14 | 9 | 73 | 1737 | 33.8 | 6585.991 | 0 | 0 | 6585.991 | Heating | 5811.1685 | 8.5 | 5811.1685 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1162.2337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5929.7638 | 0 | 1185.9528 | 11.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 10:00 | 3 | 14 | 10 | 73 | 1738 | 32 | 5006.727 | 0 | 0 | 5006.727 | Heating | 4417.7003 | 8.5 | 4417.7003 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 883.5401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4507.8574 | 0 | 901.5715 | 9.016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 11:00 | 3 | 14 | 11 | 73 | 1739 | 32 | 4112.214 | 0 | 0 | 4112.214 | Heating | 3628.4242 | 8.5 | 3628.4242 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 725.6848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3702.4736 | 0 | 740.4947 | 7.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 12:00 | 3 | 14 | 12 | 73 | 1740 | 33.8 | 3399.1767 | 0 | 0 | 3399.1767 | Heating | 2999.2736 | 8.5 | 2999.2736 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 599.8547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3060.4833 | 0 | 612.0967 | 6.121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 13:00 | 3 | 14 | 13 | 73 | 1741 | 39.02 | 2958.3137 | 0 | 0 | 2958.3137 | Heating | 2610.2768 | 8.5 | 2610.2768 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 522.0554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2663.5477 | 0 | 532.7095 | 5.327% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 14:00 | 3 | 14 | 14 | 73 | 1742 | 39.02 | 2532.6404 | 8.067 | 8.067 | 2524.5734 | Heating | 2227.5648 | 8.5 | 2227.5648 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2273.0253 | 0 | 454.6051 | 4.546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 15:00 | 3 | 14 | 15 | 73 | 1743 | 39.02 | 2163.4784 | 20.9095 | 20.9095 | 2142.5689 | Heating | 1890.502 | 8.5 | 1890.502 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.1004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1929.0837 | 0 | 385.8167 | 3.858% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 16:00 | 3 | 14 | 16 | 73 | 1744 | 39.02 | 1859.2299 | 26.1367 | 26.1367 | 1833.0932 | Heating | 1617.4352 | 8.5 | 1617.4352 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1650.444 | 0 | 330.0888 | 3.301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 17:00 | 3 | 14 | 17 | 73 | 1745 | 39.02 | 2047.2957 | 17.1768 | 17.1768 | 2030.1189 | Heating | 1791.2814 | 8.5 | 1791.2814 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.2563 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1827.8382 | 0 | 365.5676 | 3.656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 18:00 | 3 | 14 | 18 | 73 | 1746 | 37.94 | 2520.1902 | 0.59613 | 0.59613 | 2519.594 | Heating | 2223.1712 | 8.5 | 2223.1712 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 444.6342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2268.5421 | 0 | 453.7084 | 4.537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 19:00 | 3 | 14 | 19 | 73 | 1747 | 37.04 | 3002.872 | 0 | 0 | 3002.872 | Heating | 2649.593 | 8.5 | 2649.593 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 529.9186 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2703.6663 | 0 | 540.7333 | 5.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 20:00 | 3 | 14 | 20 | 73 | 1748 | 37.04 | 3593.9127 | 0 | 0 | 3593.9127 | Heating | 3171.0995 | 8.5 | 3171.0995 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 634.2199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3235.8158 | 0 | 647.1632 | 6.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 21:00 | 3 | 14 | 21 | 73 | 1749 | 35.06 | 4223.9934 | 0 | 0 | 4223.9934 | Heating | 3727.053 | 8.5 | 3727.053 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.4106 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3803.1153 | 0 | 760.6231 | 7.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 22:00 | 3 | 14 | 22 | 73 | 1750 | 30.02 | 1271.5641 | 0 | 0 | 1271.5641 | Heating | 1121.9683 | 8.5 | 1121.9683 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.3937 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1144.8657 | 0 | 228.9731 | 2.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-14 23:00 | 3 | 14 | 23 | 73 | 1751 | 30.02 | 1148.8221 | 0 | 0 | 1148.8221 | Heating | 1013.6666 | 8.5 | 1013.6666 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.7333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1034.3536 | 0 | 206.8707 | 2.069% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 | 3 | 15 | 0 | 74 | 1752 | 28.94 | 1268.9567 | 0 | 0 | 1268.9567 | Heating | 1119.6677 | 8.5 | 1119.6677 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.9335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1142.518 | 0 | 228.5036 | 2.285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 01:00 | 3 | 15 | 1 | 74 | 1753 | 28.94 | 1369.1143 | 0 | 0 | 1369.1143 | Heating | 1208.042 | 8.5 | 1208.042 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 241.6084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1232.6959 | 0 | 246.5392 | 2.465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 02:00 | 3 | 15 | 2 | 74 | 1754 | 28.94 | 1344.4219 | 0 | 0 | 1344.4219 | Heating | 1186.2547 | 8.5 | 1186.2547 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.2509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1210.4639 | 0 | 242.0928 | 2.421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 03:00 | 3 | 15 | 3 | 74 | 1755 | 26.96 | 1234.4968 | 0 | 0 | 1234.4968 | Heating | 1089.2619 | 8.5 | 1089.2619 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.8524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1111.4917 | 0 | 222.2983 | 2.223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 04:00 | 3 | 15 | 4 | 74 | 1756 | 24.08 | 1105.6315 | 0 | 0 | 1105.6315 | Heating | 975.5572 | 8.5 | 975.5572 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.1114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 995.4666 | 0 | 199.0933 | 1.991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 05:00 | 3 | 15 | 5 | 74 | 1757 | 24.08 | 1088.2003 | 0 | 0 | 1088.2003 | Heating | 960.1768 | 8.5 | 960.1768 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 192.0354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 979.7722 | 0 | 195.9544 | 1.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 06:00 | 3 | 15 | 6 | 74 | 1758 | 21.92 | 1134.2375 | 0 | 0 | 1134.2375 | Heating | 1000.7978 | 8.5 | 1000.7978 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 200.1596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1021.2222 | 0 | 204.2444 | 2.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 07:00 | 3 | 15 | 7 | 74 | 1759 | 23 | 8812.5788 | 0 | 0 | 8812.5788 | Heating | 7775.8048 | 8.5 | 7775.8048 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1555.161 | 31.1% | 1 | 62.21% | 0% | 0% | 0% | 27.3504 | 0 | 0 | 0 | 27.3504 | 7934.4947 | 0 | 1586.8989 | 15.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.625
2007-03-15 08:00 | 3 | 15 | 8 | 74 | 1760 | 23 | 6429.3568 | 0 | 0 | 6429.3568 | Heating | 5672.9619 | 8.5 | 5672.9619 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1134.5924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5788.7366 | 0 | 1157.7473 | 11.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 09:00 | 3 | 15 | 9 | 74 | 1761 | 30.92 | 5134.8616 | 0 | 0 | 5134.8616 | Heating | 4530.7602 | 8.5 | 4530.7602 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 906.152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4623.2247 | 0 | 924.6449 | 9.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 10:00 | 3 | 15 | 10 | 74 | 1762 | 35.96 | 4005.2907 | 0 | 0 | 4005.2907 | Heating | 3534.08 | 8.5 | 3534.08 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 706.816 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3606.2041 | 0 | 721.2408 | 7.212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 11:00 | 3 | 15 | 11 | 74 | 1763 | 35.96 | 3381.4941 | 0 | 0 | 3381.4941 | Heating | 2983.6713 | 8.5 | 2983.6713 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 596.7343 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3044.5625 | 0 | 608.9125 | 6.089% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 12:00 | 3 | 15 | 12 | 74 | 1764 | 42.98 | 2794.708 | 0 | 0 | 2794.708 | Heating | 2465.9189 | 8.5 | 2465.9189 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 493.1838 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2516.2437 | 0 | 503.2487 | 5.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 13:00 | 3 | 15 | 13 | 74 | 1765 | 44.96 | 2375.9951 | 0 | 0 | 2375.9951 | Heating | 2096.4663 | 8.5 | 2096.4663 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 419.2933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2139.2513 | 0 | 427.8503 | 4.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 14:00 | 3 | 15 | 14 | 74 | 1766 | 44.96 | 2201.3558 | 0 | 0 | 2201.3558 | Heating | 1942.3727 | 8.5 | 1942.3727 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 388.4745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1982.013 | 0 | 396.4026 | 3.964% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 15:00 | 3 | 15 | 15 | 74 | 1767 | 46.94 | 2167.2553 | 1.0925 | 1.0925 | 2166.1628 | Heating | 1911.3201 | 8.5 | 1911.3201 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 382.264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1950.3266 | 0 | 390.0653 | 3.901% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 16:00 | 3 | 15 | 16 | 74 | 1768 | 46.94 | 2181.389 | 0.23588 | 0.23588 | 2181.1531 | Heating | 1924.5469 | 8.5 | 1924.5469 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.9094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1963.8234 | 0 | 392.7647 | 3.928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 17:00 | 3 | 15 | 17 | 74 | 1769 | 46.94 | 2487.4644 | 0 | 0 | 2487.4644 | Heating | 2194.8215 | 8.5 | 2194.8215 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.9643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2239.6138 | 0 | 447.9228 | 4.479% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 18:00 | 3 | 15 | 18 | 74 | 1770 | 42.98 | 2960.1412 | 0 | 0 | 2960.1412 | Heating | 2611.8893 | 8.5 | 2611.8893 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 522.3779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2665.1931 | 0 | 533.0386 | 5.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 19:00 | 3 | 15 | 19 | 74 | 1771 | 42.08 | 3401.3655 | 0 | 0 | 3401.3655 | Heating | 3001.2048 | 8.5 | 3001.2048 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 600.241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3062.4539 | 0 | 612.4908 | 6.125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 20:00 | 3 | 15 | 20 | 74 | 1772 | 42.08 | 3837.1536 | 0 | 0 | 3837.1536 | Heating | 3385.7238 | 8.5 | 3385.7238 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 677.1448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3454.8202 | 0 | 690.964 | 6.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 21:00 | 3 | 15 | 21 | 74 | 1773 | 39.02 | 4280.2708 | 0 | 0 | 4280.2708 | Heating | 3776.7095 | 8.5 | 3776.7095 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 755.3419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3853.7852 | 0 | 770.757 | 7.708% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 22:00 | 3 | 15 | 22 | 74 | 1774 | 39.02 | 1264.2323 | 0 | 0 | 1264.2323 | Heating | 1115.499 | 8.5 | 1115.499 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.0998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1138.2643 | 0 | 227.6529 | 2.277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-15 23:00 | 3 | 15 | 23 | 74 | 1775 | 39.02 | 1145.2042 | 0 | 0 | 1145.2042 | Heating | 1010.4743 | 8.5 | 1010.4743 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.0949 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1031.0962 | 0 | 206.2192 | 2.062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 | 3 | 16 | 0 | 75 | 1776 | 35.96 | 1324.6125 | 0 | 0 | 1324.6125 | Heating | 1168.7758 | 8.5 | 1168.7758 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.7552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1192.6283 | 0 | 238.5257 | 2.385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 01:00 | 3 | 16 | 1 | 75 | 1777 | 35.96 | 1491.8501 | 0 | 0 | 1491.8501 | Heating | 1316.3383 | 8.5 | 1316.3383 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 263.2677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1343.2024 | 0 | 268.6405 | 2.686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 02:00 | 3 | 16 | 2 | 75 | 1778 | 35.96 | 1624.2064 | 0 | 0 | 1624.2064 | Heating | 1433.1233 | 8.5 | 1433.1233 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.6247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1462.3707 | 0 | 292.4741 | 2.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 03:00 | 3 | 16 | 3 | 75 | 1779 | 35.6 | 1740.3865 | 0 | 0 | 1740.3865 | Heating | 1535.6351 | 8.5 | 1535.6351 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 307.127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1566.9746 | 0 | 313.3949 | 3.134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 04:00 | 3 | 16 | 4 | 75 | 1780 | 35.6 | 1839.4202 | 0 | 0 | 1839.4202 | Heating | 1623.0178 | 8.5 | 1623.0178 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.6036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1656.1406 | 0 | 331.2281 | 3.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 05:00 | 3 | 16 | 5 | 75 | 1781 | 35.96 | 1961.9909 | 0 | 0 | 1961.9909 | Heating | 1731.1684 | 8.5 | 1731.1684 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.2337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1766.4984 | 0 | 353.2997 | 3.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 06:00 | 3 | 16 | 6 | 75 | 1782 | 35.96 | 2103.0215 | 0 | 0 | 2103.0215 | Heating | 1855.6072 | 8.5 | 1855.6072 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 371.1214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1893.4767 | 0 | 378.6953 | 3.787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 07:00 | 3 | 16 | 7 | 75 | 1783 | 35.6 | 11826.736 | 0 | 0 | 11826.736 | Heating | 10435.3553 | 8.5 | 10435.3553 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2087.0711 | 41.74% | 1 | 83.48% | 0% | 0% | 0% | 53.8043 | 0 | 0 | 0 | 53.8043 | 10648.3217 | 0 | 2129.6643 | 21.3% | 1 | 42.59% | 0% | 0% | 5.7227 | 0 | 0 | 5.7227 | 59.5269
2007-03-16 08:00 | 3 | 16 | 8 | 75 | 1784 | 35.06 | 9326.4489 | 0 | 0 | 9326.4489 | Heating | 8229.2196 | 8.5 | 8229.2196 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1645.8439 | 32.92% | 1 | 65.83% | 0% | 0% | 0% | 31.1584 | 0 | 0 | 0 | 31.1584 | 8397.1628 | 0 | 1679.4326 | 16.79% | 1 | 33.59% | 0% | 0% | 3.314 | 0 | 0 | 3.314 | 34.4724
2007-03-16 09:00 | 3 | 16 | 9 | 75 | 1785 | 35.96 | 8373.8655 | 0 | 0 | 8373.8655 | Heating | 7388.7049 | 8.5 | 7388.7049 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1477.741 | 30% | 1 | 59.11% | 0% | 0% | 0% | 24.3196 | 0 | 0 | 0 | 24.3196 | 7539.4948 | 0 | 1507.899 | 15.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.5942
2007-03-16 10:00 | 3 | 16 | 10 | 75 | 1786 | 35.96 | 7443.2074 | 0 | 0 | 7443.2074 | Heating | 6567.536 | 8.5 | 6567.536 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1313.5072 | 30% | 1 | 52.54% | 0% | 0% | 0% | 18.5471 | 0 | 0 | 0 | 18.5471 | 6701.5673 | 0 | 1340.3135 | 13.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.8216
2007-03-16 11:00 | 3 | 16 | 11 | 75 | 1787 | 35.96 | 6548.1073 | 0 | 0 | 6548.1073 | Heating | 5777.7417 | 8.5 | 5777.7417 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1155.5483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5895.6548 | 0 | 1179.131 | 11.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 12:00 | 3 | 16 | 12 | 75 | 1788 | 37.4 | 5882.8376 | 0 | 0 | 5882.8376 | Heating | 5190.739 | 8.5 | 5190.739 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1038.1478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5296.6725 | 0 | 1059.3345 | 10.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 13:00 | 3 | 16 | 13 | 75 | 1789 | 42.98 | 5489.2642 | 0 | 0 | 5489.2642 | Heating | 4843.4684 | 8.5 | 4843.4684 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 968.6937 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4942.3147 | 0 | 988.4629 | 9.885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 14:00 | 3 | 16 | 14 | 75 | 1790 | 42.98 | 5337.7555 | 0 | 0 | 5337.7555 | Heating | 4709.7842 | 8.5 | 4709.7842 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 941.9568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4805.9023 | 0 | 961.1805 | 9.612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 15:00 | 3 | 16 | 15 | 75 | 1791 | 50 | 5313.0708 | 0 | 0 | 5313.0708 | Heating | 4688.0037 | 8.5 | 4688.0037 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 937.6007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4783.6772 | 0 | 956.7354 | 9.567% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 16:00 | 3 | 16 | 16 | 75 | 1792 | 48.92 | 5278.6935 | 0 | 0 | 5278.6935 | Heating | 4657.6708 | 8.5 | 4657.6708 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 931.5342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4752.7253 | 0 | 950.5451 | 9.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 17:00 | 3 | 16 | 17 | 75 | 1793 | 48.92 | 5255.0922 | 0 | 0 | 5255.0922 | Heating | 4636.8461 | 8.5 | 4636.8461 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 927.3692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4731.4756 | 0 | 946.2951 | 9.463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 18:00 | 3 | 16 | 18 | 75 | 1794 | 46.04 | 5363.1493 | 0 | 0 | 5363.1493 | Heating | 4732.1905 | 8.5 | 4732.1905 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 946.4381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4828.7658 | 0 | 965.7532 | 9.658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 19:00 | 3 | 16 | 19 | 75 | 1795 | 46.4 | 5695.5112 | 0 | 0 | 5695.5112 | Heating | 5025.451 | 8.5 | 5025.451 | 0 | 4.1996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1005.0902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5128.0113 | 0 | 1025.6023 | 10.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 20:00 | 3 | 16 | 20 | 75 | 1796 | 46.04 | 6364.2972 | 0 | 0 | 6364.2972 | Heating | 5615.5563 | 8.5 | 5615.5563 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1123.1113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5730.1595 | 0 | 1146.0319 | 11.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 21:00 | 3 | 16 | 21 | 75 | 1797 | 44.96 | 6865.5497 | 0 | 0 | 6865.5497 | Heating | 6057.838 | 8.5 | 6057.838 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1211.5676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6181.4673 | 0 | 1236.2935 | 12.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-16 22:00 | 3 | 16 | 22 | 75 | 1798 | 44.6 | 7559.2886 | 0 | 0 | 7559.2886 | Heating | 6669.9605 | 8.5 | 6669.9605 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1333.9921 | 30% | 1 | 53.36% | 0% | 0% | 0% | 19.2191 | 0 | 0 | 0 | 19.2191 | 6806.0821 | 0 | 1361.2164 | 13.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.4937
2007-03-16 23:00 | 3 | 16 | 23 | 75 | 1799 | 44.06 | 2414.5219 | 0 | 0 | 2414.5219 | Heating | 2130.4605 | 8.5 | 2130.4605 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.0921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2173.9393 | 0 | 434.7879 | 4.348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 | 3 | 17 | 0 | 76 | 1800 | 42.98 | 2436.5978 | 0 | 0 | 2436.5978 | Heating | 2149.9392 | 8.5 | 2149.9392 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 429.9878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2193.8155 | 0 | 438.7631 | 4.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 01:00 | 3 | 17 | 1 | 76 | 1801 | 42.08 | 2450.42 | 0 | 0 | 2450.42 | Heating | 2162.1353 | 8.5 | 2162.1353 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 432.4271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2206.2605 | 0 | 441.2521 | 4.413% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 02:00 | 3 | 17 | 2 | 76 | 1802 | 42.08 | 2573.0352 | 0 | 0 | 2573.0352 | Heating | 2270.3252 | 8.5 | 2270.3252 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 454.065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2316.6584 | 0 | 463.3317 | 4.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 03:00 | 3 | 17 | 3 | 76 | 1803 | 39.2 | 2781.0418 | 0 | 0 | 2781.0418 | Heating | 2453.8604 | 8.5 | 2453.8604 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 490.7721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2503.9392 | 0 | 500.7878 | 5.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 04:00 | 3 | 17 | 4 | 76 | 1804 | 39.02 | 2994.8087 | 0 | 0 | 2994.8087 | Heating | 2642.4782 | 8.5 | 2642.4782 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 528.4956 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2696.4064 | 0 | 539.2813 | 5.393% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 05:00 | 3 | 17 | 5 | 76 | 1805 | 39.02 | 3128.5724 | 0 | 0 | 3128.5724 | Heating | 2760.5051 | 8.5 | 2760.5051 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 552.101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2816.8419 | 0 | 563.3684 | 5.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 06:00 | 3 | 17 | 6 | 76 | 1806 | 33.98 | 3197.9115 | 0 | 0 | 3197.9115 | Heating | 2821.6866 | 8.5 | 2821.6866 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 564.3373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2879.2721 | 0 | 575.8544 | 5.759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 07:00 | 3 | 17 | 7 | 76 | 1807 | 33.98 | 3223.3236 | 0 | 0 | 3223.3236 | Heating | 2844.1091 | 8.5 | 2844.1091 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 568.8218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2902.1521 | 0 | 580.4304 | 5.804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 08:00 | 3 | 17 | 8 | 76 | 1808 | 33.98 | 3083.007 | 0 | 0 | 3083.007 | Heating | 2720.3003 | 8.5 | 2720.3003 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 544.0601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2775.8166 | 0 | 555.1633 | 5.552% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 09:00 | 3 | 17 | 9 | 76 | 1809 | 46.94 | 12889.3763 | 0 | 0 | 12889.3763 | Heating | 11372.9791 | 8.5 | 11372.9791 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2274.5958 | 45.49% | 1 | 90.98% | 0% | 0% | 0% | 65.5784 | 0 | 0 | 0 | 65.5784 | 11605.0807 | 0 | 2321.0161 | 23.21% | 1 | 46.42% | 0% | 0% | 6.975 | 0 | 0 | 6.975 | 72.5534
2007-03-17 10:00 | 3 | 17 | 10 | 76 | 1810 | 50 | 10020.8009 | 0 | 0 | 10020.8009 | Heating | 8841.8831 | 8.5 | 8841.8831 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1768.3766 | 35.37% | 1 | 70.74% | 0% | 0% | 0% | 36.7539 | 0 | 0 | 0 | 36.7539 | 9022.3297 | 0 | 1804.4659 | 18.04% | 1 | 36.09% | 0% | 0% | 3.9092 | 0 | 0 | 3.9092 | 40.663
2007-03-17 11:00 | 3 | 17 | 11 | 76 | 1811 | 50 | 8411.896 | 0 | 0 | 8411.896 | Heating | 7422.2611 | 8.5 | 7422.2611 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1484.4522 | 30% | 1 | 59.38% | 0% | 0% | 0% | 24.5744 | 0 | 0 | 0 | 24.5744 | 7573.7358 | 0 | 1514.7472 | 15.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.849
2007-03-17 12:00 | 3 | 17 | 12 | 76 | 1812 | 55.04 | 7564.1218 | 0 | 0 | 7564.1218 | Heating | 6674.2252 | 8.5 | 6674.2252 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1334.845 | 30% | 1 | 53.39% | 0% | 0% | 0% | 19.2474 | 0 | 0 | 0 | 19.2474 | 6810.4338 | 0 | 1362.0868 | 13.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.5219
2007-03-17 13:00 | 3 | 17 | 13 | 76 | 1813 | 57.92 | 6667.2578 | 0 | 0 | 6667.2578 | Heating | 5882.8746 | 8.5 | 5882.8746 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1176.5749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6002.9332 | 0 | 1200.5866 | 12.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 14:00 | 3 | 17 | 14 | 76 | 1814 | 59 | 6502.4893 | 0 | 0 | 6502.4893 | Heating | 5737.4905 | 8.5 | 5737.4905 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1147.4981 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5854.5822 | 0 | 1170.9164 | 11.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 15:00 | 3 | 17 | 15 | 76 | 1815 | 60.08 | 6574.1434 | 0 | 0 | 6574.1434 | Heating | 5800.7147 | 8.5 | 5800.7147 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1160.1429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5919.0967 | 0 | 1183.8193 | 11.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 16:00 | 3 | 17 | 16 | 76 | 1816 | 60.98 | 6716.5548 | 0 | 0 | 6716.5548 | Heating | 5926.3719 | 8.5 | 5926.3719 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1185.2744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6047.3182 | 0 | 1209.4636 | 12.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 17:00 | 3 | 17 | 17 | 76 | 1817 | 60.98 | 6958.2129 | 0 | 0 | 6958.2129 | Heating | 6139.5996 | 8.5 | 6139.5996 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1227.9199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6264.8975 | 0 | 1252.9795 | 12.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 18:00 | 3 | 17 | 18 | 76 | 1818 | 55.04 | 9398.219 | 0 | 0 | 9398.219 | Heating | 8292.5462 | 8.5 | 8292.5462 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1658.5092 | 33.17% | 1 | 66.34% | 0% | 0% | 0% | 31.7126 | 0 | 0 | 0 | 31.7126 | 8461.7818 | 0 | 1692.3564 | 16.92% | 1 | 33.85% | 0% | 0% | 3.373 | 0 | 0 | 3.373 | 35.0856
2007-03-17 19:00 | 3 | 17 | 19 | 76 | 1819 | 51.08 | 10100.5168 | 0 | 0 | 10100.5168 | Heating | 8912.2207 | 8.5 | 8912.2207 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1782.4441 | 35.65% | 1 | 71.3% | 0% | 0% | 0% | 37.4298 | 0 | 0 | 0 | 37.4298 | 9094.1028 | 0 | 1818.8206 | 18.19% | 1 | 36.38% | 0% | 0% | 3.9811 | 0 | 0 | 3.9811 | 41.4109
2007-03-17 20:00 | 3 | 17 | 20 | 76 | 1820 | 51.08 | 2866.6603 | 0 | 0 | 2866.6603 | Heating | 2529.4061 | 8.5 | 2529.4061 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.8812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2581.0267 | 0 | 516.2053 | 5.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 21:00 | 3 | 17 | 21 | 76 | 1821 | 51.98 | 2941.6368 | 0 | 0 | 2941.6368 | Heating | 2595.5619 | 8.5 | 2595.5619 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 519.1124 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2648.5325 | 0 | 529.7065 | 5.297% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 22:00 | 3 | 17 | 22 | 76 | 1822 | 50 | 3016.3301 | 0 | 0 | 3016.3301 | Heating | 2661.4678 | 8.5 | 2661.4678 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 532.2936 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2715.7834 | 0 | 543.1567 | 5.432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-17 23:00 | 3 | 17 | 23 | 76 | 1823 | 50 | 3108.8591 | 0 | 0 | 3108.8591 | Heating | 2743.1109 | 8.5 | 2743.1109 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 548.6222 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2799.0928 | 0 | 559.8186 | 5.598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 | 3 | 18 | 0 | 77 | 1824 | 50 | 3197.374 | 0 | 0 | 3197.374 | Heating | 2821.2124 | 8.5 | 2821.2124 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 564.2425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2878.7882 | 0 | 575.7576 | 5.758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 01:00 | 3 | 18 | 1 | 77 | 1825 | 51.98 | 3265.8478 | 0 | 0 | 3265.8478 | Heating | 2881.6304 | 8.5 | 2881.6304 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 576.3261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2940.4392 | 0 | 588.0878 | 5.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 02:00 | 3 | 18 | 2 | 77 | 1826 | 51.98 | 3326.124 | 0 | 0 | 3326.124 | Heating | 2934.8153 | 8.5 | 2934.8153 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 586.9631 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2994.7095 | 0 | 598.9419 | 5.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 03:00 | 3 | 18 | 3 | 77 | 1827 | 51.98 | 3371.0002 | 0 | 0 | 3371.0002 | Heating | 2974.4119 | 8.5 | 2974.4119 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 594.8824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3035.1142 | 0 | 607.0228 | 6.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 04:00 | 3 | 18 | 4 | 77 | 1828 | 50 | 3411.2226 | 0 | 0 | 3411.2226 | Heating | 3009.9023 | 8.5 | 3009.9023 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 601.9805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3071.3289 | 0 | 614.2658 | 6.143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 05:00 | 3 | 18 | 5 | 77 | 1829 | 50 | 3478.9464 | 0 | 0 | 3478.9464 | Heating | 3069.6586 | 8.5 | 3069.6586 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 613.9317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3132.3047 | 0 | 626.4609 | 6.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 06:00 | 3 | 18 | 6 | 77 | 1830 | 51.98 | 3541.0681 | 0 | 0 | 3541.0681 | Heating | 3124.4718 | 8.5 | 3124.4718 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 624.8944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3188.2365 | 0 | 637.6473 | 6.376% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 07:00 | 3 | 18 | 7 | 77 | 1831 | 51.98 | 15635.3609 | 0 | 0 | 15635.3609 | Heating | 13795.9066 | 8.5 | 13795.9066 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2759.1813 | 55.18% | 2 | 55.18% | 55.18% | 0% | 0% | 20.7638 | 20.7638 | 0 | 0 | 41.5276 | 14077.4558 | 0 | 2815.4912 | 28.15% | 1 | 56.31% | 0% | 0% | 10.8757 | 0 | 0 | 10.8757 | 52.4033
2007-03-18 08:00 | 3 | 18 | 8 | 77 | 1832 | 51.98 | 12827.5198 | 0 | 0 | 12827.5198 | Heating | 11318.3998 | 8.5 | 11318.3998 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2263.68 | 45.27% | 1 | 90.55% | 0% | 0% | 0% | 64.8568 | 0 | 0 | 0 | 64.8568 | 11549.3876 | 0 | 2309.8775 | 23.1% | 1 | 46.2% | 0% | 0% | 6.8982 | 0 | 0 | 6.8982 | 71.755
2007-03-18 09:00 | 3 | 18 | 9 | 77 | 1833 | 53.96 | 10485.0064 | 0 | 0 | 10485.0064 | Heating | 9251.4762 | 8.5 | 9251.4762 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1850.2952 | 37.01% | 1 | 74.01% | 0% | 0% | 0% | 40.7883 | 0 | 0 | 0 | 40.7883 | 9440.2819 | 0 | 1888.0564 | 18.88% | 1 | 37.76% | 0% | 0% | 4.3383 | 0 | 0 | 4.3383 | 45.1265
2007-03-18 10:00 | 3 | 18 | 10 | 77 | 1834 | 57.92 | 8330.4833 | 0 | 0 | 8330.4833 | Heating | 7350.4264 | 8.5 | 7350.4264 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1470.0853 | 30% | 1 | 58.8% | 0% | 0% | 0% | 24.0308 | 0 | 0 | 0 | 24.0308 | 7500.4351 | 0 | 1500.087 | 15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.3054
2007-03-18 11:00 | 3 | 18 | 11 | 77 | 1835 | 57.92 | 6951.5607 | 0 | 0 | 6951.5607 | Heating | 6133.73 | 8.5 | 6133.73 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1226.746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6258.9082 | 0 | 1251.7816 | 12.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 12:00 | 3 | 18 | 12 | 77 | 1836 | 60.08 | 5676.7596 | 0 | 0 | 5676.7596 | Heating | 5008.9055 | 8.5 | 5008.9055 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1001.7811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5111.1281 | 0 | 1022.2256 | 10.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 13:00 | 3 | 18 | 13 | 77 | 1837 | 60.98 | 4776.6171 | 0 | 0 | 4776.6171 | Heating | 4214.6622 | 8.5 | 4214.6622 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 842.9324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4300.6757 | 0 | 860.1351 | 8.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 14:00 | 3 | 18 | 14 | 77 | 1838 | 60.98 | 4170.8656 | 0 | 0 | 4170.8656 | Heating | 3680.1755 | 8.5 | 3680.1755 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 736.0351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3755.2812 | 0 | 751.0562 | 7.511% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 15:00 | 3 | 18 | 15 | 77 | 1839 | 60.08 | 3809.452 | 0 | 0 | 3809.452 | Heating | 3361.2812 | 8.5 | 3361.2812 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 672.2562 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3429.8788 | 0 | 685.9758 | 6.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 16:00 | 3 | 18 | 16 | 77 | 1840 | 57.92 | 3502.1901 | 0 | 0 | 3502.1901 | Heating | 3090.1677 | 8.5 | 3090.1677 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 618.0335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3153.2324 | 0 | 630.6465 | 6.306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 17:00 | 3 | 18 | 17 | 77 | 1841 | 57.92 | 3706.9072 | 0 | 0 | 3706.9072 | Heating | 3270.8005 | 8.5 | 3270.8005 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 654.1601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3337.5515 | 0 | 667.5103 | 6.675% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 18:00 | 3 | 18 | 18 | 77 | 1842 | 53.06 | 4235.6799 | 0 | 0 | 4235.6799 | Heating | 3737.3646 | 8.5 | 3737.3646 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 747.4729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3813.6374 | 0 | 762.7275 | 7.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 19:00 | 3 | 18 | 19 | 77 | 1843 | 51.08 | 4733.4501 | 0 | 0 | 4733.4501 | Heating | 4176.5736 | 8.5 | 4176.5736 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 835.3147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4261.8098 | 0 | 852.362 | 8.524% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 20:00 | 3 | 18 | 20 | 77 | 1844 | 51.08 | 5326.428 | 0 | 0 | 5326.428 | Heating | 4699.7894 | 8.5 | 4699.7894 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 939.9579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4795.7035 | 0 | 959.1407 | 9.591% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 21:00 | 3 | 18 | 21 | 77 | 1845 | 46.04 | 5957.1017 | 0 | 0 | 5957.1017 | Heating | 5256.2662 | 8.5 | 5256.2662 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1051.2532 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5363.5369 | 0 | 1072.7074 | 10.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 22:00 | 3 | 18 | 22 | 77 | 1846 | 44.96 | 1865.4476 | 0 | 0 | 1865.4476 | Heating | 1645.9832 | 8.5 | 1645.9832 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.1966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1679.5747 | 0 | 335.9149 | 3.359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-18 23:00 | 3 | 18 | 23 | 77 | 1847 | 44.96 | 1591.1031 | 0 | 0 | 1591.1031 | Heating | 1403.9145 | 8.5 | 1403.9145 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 280.7829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1432.5658 | 0 | 286.5132 | 2.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 | 3 | 19 | 0 | 78 | 1848 | 44.06 | 1700.1914 | 0 | 0 | 1700.1914 | Heating | 1500.1689 | 8.5 | 1500.1689 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.0338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1530.7845 | 0 | 306.1569 | 3.062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 01:00 | 3 | 19 | 1 | 78 | 1849 | 44.96 | 1683.5074 | 0 | 0 | 1683.5074 | Heating | 1485.4477 | 8.5 | 1485.4477 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.0895 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1515.763 | 0 | 303.1526 | 3.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 02:00 | 3 | 19 | 2 | 78 | 1850 | 44.96 | 1688.4498 | 0 | 0 | 1688.4498 | Heating | 1489.8086 | 8.5 | 1489.8086 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.9617 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1520.2129 | 0 | 304.0426 | 3.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 03:00 | 3 | 19 | 3 | 78 | 1851 | 42.08 | 1706.2443 | 0 | 0 | 1706.2443 | Heating | 1505.5097 | 8.5 | 1505.5097 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.1019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1536.2344 | 0 | 307.2469 | 3.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 04:00 | 3 | 19 | 4 | 78 | 1852 | 39.92 | 1706.8629 | 0 | 0 | 1706.8629 | Heating | 1506.0555 | 8.5 | 1506.0555 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.2111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1536.7913 | 0 | 307.3583 | 3.074% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 05:00 | 3 | 19 | 5 | 78 | 1853 | 39.92 | 1663.9561 | 0 | 0 | 1663.9561 | Heating | 1468.1966 | 8.5 | 1468.1966 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 293.6393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1498.1598 | 0 | 299.632 | 2.996% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 06:00 | 3 | 19 | 6 | 78 | 1854 | 39.02 | 1571.912 | 0 | 0 | 1571.912 | Heating | 1386.9812 | 8.5 | 1386.9812 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 277.3962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1415.2869 | 0 | 283.0574 | 2.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 07:00 | 3 | 19 | 7 | 78 | 1855 | 37.94 | 9863.4101 | 0 | 0 | 9863.4101 | Heating | 8703.0089 | 8.5 | 8703.0089 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1740.6018 | 34.81% | 1 | 69.62% | 0% | 0% | 0% | 35.4397 | 0 | 0 | 0 | 35.4397 | 8880.6213 | 0 | 1776.1243 | 17.76% | 1 | 35.52% | 0% | 0% | 3.7694 | 0 | 0 | 3.7694 | 39.2091
2007-03-19 08:00 | 3 | 19 | 8 | 78 | 1856 | 37.94 | 7163.2664 | 0 | 0 | 7163.2664 | Heating | 6320.5292 | 8.5 | 6320.5292 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1264.1058 | 30% | 1 | 50.56% | 0% | 0% | 0% | 16.9818 | 0 | 0 | 0 | 16.9818 | 6449.5196 | 0 | 1289.9039 | 12.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2563
2007-03-19 09:00 | 3 | 19 | 9 | 78 | 1857 | 37.4 | 5583.8354 | 0 | 0 | 5583.8354 | Heating | 4926.9135 | 8.5 | 4926.9135 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 985.3827 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5027.4628 | 0 | 1005.4926 | 10.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 10:00 | 3 | 19 | 10 | 78 | 1858 | 35.6 | 4274.6696 | 0 | 0 | 4274.6696 | Heating | 3771.7673 | 8.5 | 3771.7673 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 754.3535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3848.7421 | 0 | 769.7484 | 7.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 11:00 | 3 | 19 | 11 | 78 | 1859 | 35.96 | 3316.2791 | 0 | 0 | 3316.2791 | Heating | 2926.1287 | 8.5 | 2926.1287 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 585.2257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2985.8456 | 0 | 597.1691 | 5.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 12:00 | 3 | 19 | 12 | 78 | 1860 | 39.92 | 2347.7467 | 0 | 0 | 2347.7467 | Heating | 2071.5412 | 8.5 | 2071.5412 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 414.3082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2113.8176 | 0 | 422.7635 | 4.228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 13:00 | 3 | 19 | 13 | 78 | 1861 | 42.08 | 1652.5319 | 0 | 0 | 1652.5319 | Heating | 1458.1164 | 8.5 | 1458.1164 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 291.6233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1487.8739 | 0 | 297.5748 | 2.976% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 14:00 | 3 | 19 | 14 | 78 | 1862 | 42.08 | 1129.644 | 0 | 0 | 1129.644 | Heating | 996.7447 | 8.5 | 996.7447 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.3489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1017.0865 | 0 | 203.4173 | 2.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 15:00 | 3 | 19 | 15 | 78 | 1863 | 44.96 | 700.8483 | 10.6389 | 10.6389 | 690.2095 | Heating | 609.0084 | 8.5 | 609.0084 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.8017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 621.4371 | 0 | 124.2874 | 1.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 16:00 | 3 | 19 | 16 | 78 | 1864 | 44.06 | 346.8341 | 29.2017 | 29.2017 | 317.6324 | Heating | 280.2639 | 8.5 | 280.2639 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 56.0528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 285.9836 | 0 | 57.1967 | 0.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 17:00 | 3 | 19 | 17 | 78 | 1865 | 44.06 | 319.629 | 39.1063 | 39.1063 | 280.5228 | Heating | 247.5201 | 8.5 | 247.5201 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 252.5715 | 0 | 50.5143 | 0.5051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 18:00 | 3 | 19 | 18 | 78 | 1866 | 39.92 | 585.4385 | 11.75 | 11.75 | 573.6884 | Heating | 506.1957 | 8.5 | 506.1957 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.2391 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 516.5262 | 0 | 103.3052 | 1.033% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 19:00 | 3 | 19 | 19 | 78 | 1867 | 37.94 | 1007.1585 | 0 | 0 | 1007.1585 | Heating | 888.6692 | 8.5 | 888.6692 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.7338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 906.8053 | 0 | 181.3611 | 1.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 20:00 | 3 | 19 | 20 | 78 | 1868 | 37.94 | 1518.4034 | 0 | 0 | 1518.4034 | Heating | 1339.7677 | 8.5 | 1339.7677 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.9535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1367.1099 | 0 | 273.422 | 2.734% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 21:00 | 3 | 19 | 21 | 78 | 1869 | 32 | 2030.8369 | 0 | 0 | 2030.8369 | Heating | 1791.9149 | 8.5 | 1791.9149 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.383 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1828.4846 | 0 | 365.6969 | 3.657% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 22:00 | 3 | 19 | 22 | 78 | 1870 | 30.92 | 577.9616 | 0 | 0 | 577.9616 | Heating | 509.9661 | 8.5 | 509.9661 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.9932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 520.3736 | 0 | 104.0747 | 1.041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-19 23:00 | 3 | 19 | 23 | 78 | 1871 | 30.92 | 636.1837 | 0 | 0 | 636.1837 | Heating | 561.3386 | 8.5 | 561.3386 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.2677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 572.7945 | 0 | 114.5589 | 1.146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 | 3 | 20 | 0 | 79 | 1872 | 28.94 | 695.7375 | 0 | 0 | 695.7375 | Heating | 613.886 | 8.5 | 613.886 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.7772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 626.4143 | 0 | 125.2829 | 1.253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 01:00 | 3 | 20 | 1 | 79 | 1873 | 28.94 | 755.5632 | 0 | 0 | 755.5632 | Heating | 666.6734 | 8.5 | 666.6734 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.3347 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 680.279 | 0 | 136.0558 | 1.361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 02:00 | 3 | 20 | 2 | 79 | 1874 | 28.94 | 811.3782 | 0 | 0 | 811.3782 | Heating | 715.9219 | 8.5 | 715.9219 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 143.1844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 730.5326 | 0 | 146.1065 | 1.461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 03:00 | 3 | 20 | 3 | 79 | 1875 | 26.06 | 865.0367 | 0 | 0 | 865.0367 | Heating | 763.2677 | 8.5 | 763.2677 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.6535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 778.8446 | 0 | 155.7689 | 1.558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 04:00 | 3 | 20 | 4 | 79 | 1876 | 24.08 | 922.7256 | 0 | 0 | 922.7256 | Heating | 814.1696 | 8.5 | 814.1696 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.8339 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 830.7853 | 0 | 166.1571 | 1.662% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 05:00 | 3 | 20 | 5 | 79 | 1877 | 24.08 | 964.5681 | 0 | 0 | 964.5681 | Heating | 851.0895 | 8.5 | 851.0895 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.2179 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 868.4586 | 0 | 173.6917 | 1.737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 06:00 | 3 | 20 | 6 | 79 | 1878 | 21.92 | 975.0142 | 0 | 0 | 975.0142 | Heating | 860.3066 | 8.5 | 860.3066 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.0613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 877.8639 | 0 | 175.5728 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 07:00 | 3 | 20 | 7 | 79 | 1879 | 24.08 | 8302.0242 | 0 | 0 | 8302.0242 | Heating | 7325.3154 | 8.5 | 7325.3154 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1465.0631 | 30% | 1 | 58.6% | 0% | 0% | 0% | 23.8424 | 0 | 0 | 0 | 23.8424 | 7474.8117 | 0 | 1494.9623 | 14.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.117
2007-03-20 08:00 | 3 | 20 | 8 | 79 | 1880 | 24.08 | 5348.9755 | 0 | 0 | 5348.9755 | Heating | 4719.6842 | 8.5 | 4719.6842 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 943.9368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4816.0043 | 0 | 963.2009 | 9.632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 09:00 | 3 | 20 | 9 | 79 | 1881 | 33.08 | 3055.5768 | 0 | 0 | 3055.5768 | Heating | 2696.0972 | 8.5 | 2696.0972 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 539.2194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2751.1196 | 0 | 550.2239 | 5.502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 10:00 | 3 | 20 | 10 | 79 | 1882 | 37.04 | 1021.933 | 3.3237 | 3.3237 | 1018.6093 | Heating | 898.7729 | 8.5 | 898.7729 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 179.7546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 917.1152 | 0 | 183.423 | 1.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 11:00 | 3 | 20 | 11 | 79 | 1883 | 37.04 | 152.5602 | 60.3676 | 60.3676 | 92.1926 | Heating | 81.3464 | 8.5 | 81.3464 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.2693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.0065 | 0 | 16.6013 | 0.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 12:00 | 3 | 20 | 12 | 79 | 1884 | 39.02 | 59.0109 | 200.3819 | 200.3819 | -141.371 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 244.9112 | 244.9112 | 0 | 8.5 | 0 | 40.8185 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 240.013 | 48.0026 | 0.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 13:00 | 3 | 20 | 13 | 79 | 1885 | 39.92 | 15.9659 | 1019.0188 | 1019.0188 | -1003.0529 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1245.4674 | 1245.4674 | 0 | 8.5 | 0 | 207.5779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1220.558 | 244.1116 | 2.441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 14:00 | 3 | 20 | 14 | 79 | 1886 | 39.92 | 1.7452 | 2213.2302 | 2213.2302 | -2211.4851 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2705.0592 | 2705.0592 | 0 | 8.5 | 0 | 450.8432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2650.958 | 530.1916 | 5.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 15:00 | 3 | 20 | 15 | 79 | 1887 | 44.06 | 0.004391 | 3052.3069 | 3052.3069 | -3052.3025 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3730.5973 | 3730.5973 | 0 | 8.5 | 0 | 621.7662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3655.9854 | 731.1971 | 7.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 16:00 | 3 | 20 | 16 | 79 | 1888 | 44.96 | 0 | 3478.3561 | 3478.3561 | -3478.3561 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4251.3241 | 4251.3241 | 0 | 8.5 | 0 | 708.554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4166.2977 | 833.2595 | 8.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 17:00 | 3 | 20 | 17 | 79 | 1889 | 44.96 | 0 | 3198.1214 | 3198.1214 | -3198.1214 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3908.8151 | 3908.8151 | 0 | 8.5 | 0 | 651.4692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3830.6388 | 766.1278 | 7.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 18:00 | 3 | 20 | 18 | 79 | 1890 | 41 | 0 | 2156.6352 | 2156.6352 | -2156.6352 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2635.8874 | 2635.8874 | 0 | 8.5 | 0 | 439.3146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2583.1697 | 516.6339 | 5.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 19:00 | 3 | 20 | 19 | 79 | 1891 | 41 | 0 | 685.8365 | 685.8365 | -685.8365 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 838.2446 | 838.2446 | 0 | 8.5 | 0 | 139.7074 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 821.4797 | 164.2959 | 1.643% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 20:00 | 3 | 20 | 20 | 79 | 1892 | 41 | 0.13917 | 202.1137 | 202.1137 | -201.9745 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 247.0278 | 247.0278 | 0 | 8.5 | 0 | 41.1713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 242.0873 | 48.4175 | 0.4842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 21:00 | 3 | 20 | 21 | 79 | 1893 | 37.04 | 3.6747 | 109.5803 | 109.5803 | -105.9057 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 133.9315 | 133.9315 | 0 | 8.5 | 0 | 22.3219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 131.2529 | 26.2506 | 0.2625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 22:00 | 3 | 20 | 22 | 79 | 1894 | 37.04 | 12.2491 | 72.2074 | 72.2074 | -59.9583 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 88.2535 | 88.2535 | 0 | 8.5 | 0 | 14.7089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 86.4885 | 17.2977 | 0.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-20 23:00 | 3 | 20 | 23 | 79 | 1895 | 37.04 | 25.6731 | 0 | 0 | 25.6731 | Heating | 22.6527 | 8.5 | 22.6527 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5305 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.115 | 0 | 4.623 | 0.04623% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 | 3 | 21 | 0 | 80 | 1896 | 39.02 | 40.6803 | 0 | 0 | 40.6803 | Heating | 35.8944 | 8.5 | 35.8944 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.1789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 36.6269 | 0 | 7.3254 | 0.07325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 01:00 | 3 | 21 | 1 | 80 | 1897 | 39.92 | 54.6468 | 0 | 0 | 54.6468 | Heating | 48.2178 | 8.5 | 48.2178 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.6436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 49.2018 | 0 | 9.8404 | 0.0984% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 02:00 | 3 | 21 | 2 | 80 | 1898 | 39.92 | 70.486 | 0 | 0 | 70.486 | Heating | 62.1935 | 8.5 | 62.1935 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.4387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 63.4628 | 0 | 12.6926 | 0.1269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 03:00 | 3 | 21 | 3 | 80 | 1899 | 37.94 | 92.8493 | 0 | 0 | 92.8493 | Heating | 81.9259 | 8.5 | 81.9259 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.3852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.5978 | 0 | 16.7196 | 0.1672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 04:00 | 3 | 21 | 4 | 80 | 1900 | 39.02 | 115.9792 | 0 | 0 | 115.9792 | Heating | 102.3346 | 8.5 | 102.3346 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.4669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 104.4231 | 0 | 20.8846 | 0.2088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 05:00 | 3 | 21 | 5 | 80 | 1901 | 39.02 | 128.6022 | 0 | 0 | 128.6022 | Heating | 113.4725 | 8.5 | 113.4725 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.6945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 115.7883 | 0 | 23.1577 | 0.2316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 06:00 | 3 | 21 | 6 | 80 | 1902 | 37.94 | 129.0721 | 0 | 0 | 129.0721 | Heating | 113.8871 | 8.5 | 113.8871 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.7774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.2114 | 0 | 23.2423 | 0.2324% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 07:00 | 3 | 21 | 7 | 80 | 1903 | 35.6 | 1930.3351 | 81.1224 | 81.1224 | 1849.2127 | Heating | 1631.6583 | 8.5 | 1631.6583 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 326.3317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1664.9574 | 0 | 332.9915 | 3.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 08:00 | 3 | 21 | 8 | 80 | 1904 | 35.06 | 1390.0364 | 0 | 0 | 1390.0364 | Heating | 1226.5027 | 8.5 | 1226.5027 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.3005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1251.5334 | 0 | 250.3067 | 2.503% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 09:00 | 3 | 21 | 9 | 80 | 1905 | 33.08 | 763.4996 | 65.6838 | 65.6838 | 697.8158 | Heating | 615.7198 | 8.5 | 615.7198 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 628.2856 | 0 | 125.6571 | 1.257% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 10:00 | 3 | 21 | 10 | 80 | 1906 | 33.8 | 77.6824 | 173.0086 | 173.0086 | -95.3263 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 211.455 | 211.455 | 0 | 8.5 | 0 | 35.2425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 207.2259 | 41.4452 | 0.4145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 11:00 | 3 | 21 | 11 | 80 | 1907 | 33.98 | 46.9755 | 342.1707 | 342.1707 | -295.1952 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 418.2086 | 418.2086 | 0 | 8.5 | 0 | 69.7014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 409.8444 | 81.9689 | 0.8197% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 12:00 | 3 | 21 | 12 | 80 | 1908 | 35.6 | 34.675 | 504.1927 | 504.1927 | -469.5177 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 616.2355 | 616.2355 | 0 | 8.5 | 0 | 102.7059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 603.9108 | 120.7822 | 1.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 13:00 | 3 | 21 | 13 | 80 | 1909 | 35.96 | 28.5435 | 602.3941 | 602.3941 | -573.8506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 736.2595 | 736.2595 | 0 | 8.5 | 0 | 122.7099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 721.5343 | 144.3069 | 1.443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 14:00 | 3 | 21 | 14 | 80 | 1910 | 35.96 | 70.8937 | 670.0563 | 670.0563 | -599.1626 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 818.9577 | 818.9577 | 0 | 8.5 | 0 | 136.4929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 802.5785 | 160.5157 | 1.605% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 15:00 | 3 | 21 | 15 | 80 | 1911 | 37.4 | 177.5831 | 549.3504 | 549.3504 | -371.7673 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 671.4282 | 671.4282 | 0 | 8.5 | 0 | 111.9047 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 657.9997 | 131.5999 | 1.316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 16:00 | 3 | 21 | 16 | 80 | 1912 | 37.4 | 444.4767 | 223.5847 | 223.5847 | 220.892 | Heating | 194.9047 | 8.5 | 194.9047 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.9809 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 198.8823 | 0 | 39.7765 | 0.3978% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 17:00 | 3 | 21 | 17 | 80 | 1913 | 37.04 | 753.265 | 154.6033 | 154.6033 | 598.6617 | Heating | 528.2309 | 8.5 | 528.2309 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.6462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 539.0112 | 0 | 107.8022 | 1.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 18:00 | 3 | 21 | 18 | 80 | 1914 | 37.4 | 967.7536 | 68.1057 | 68.1057 | 899.6479 | Heating | 793.807 | 8.5 | 793.807 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.7614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 810.0071 | 0 | 162.0014 | 1.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 19:00 | 3 | 21 | 19 | 80 | 1915 | 37.4 | 1279.9614 | 1.455 | 1.455 | 1278.5064 | Heating | 1128.0939 | 8.5 | 1128.0939 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.6188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1151.1162 | 0 | 230.2232 | 2.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 20:00 | 3 | 21 | 20 | 80 | 1916 | 37.04 | 1674.316 | 0 | 0 | 1674.316 | Heating | 1477.3376 | 8.5 | 1477.3376 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.4675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1507.4874 | 0 | 301.4975 | 3.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 21:00 | 3 | 21 | 21 | 80 | 1917 | 37.4 | 2145.3706 | 0 | 0 | 2145.3706 | Heating | 1892.9741 | 8.5 | 1892.9741 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.5948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1931.6062 | 0 | 386.3212 | 3.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 22:00 | 3 | 21 | 22 | 80 | 1918 | 37.4 | 531.2143 | 0 | 0 | 531.2143 | Heating | 468.7185 | 8.5 | 468.7185 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.7437 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 478.2841 | 0 | 95.6568 | 0.9566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-21 23:00 | 3 | 21 | 23 | 80 | 1919 | 37.94 | 638.3324 | 0 | 0 | 638.3324 | Heating | 563.2345 | 8.5 | 563.2345 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.6469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 574.7291 | 0 | 114.9458 | 1.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 | 3 | 22 | 0 | 81 | 1920 | 41 | 758.9907 | 0 | 0 | 758.9907 | Heating | 669.6976 | 8.5 | 669.6976 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.9395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 683.3649 | 0 | 136.673 | 1.367% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 01:00 | 3 | 22 | 1 | 81 | 1921 | 41 | 899.1042 | 0 | 0 | 899.1042 | Heating | 793.3272 | 8.5 | 793.3272 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.6654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 809.5176 | 0 | 161.9035 | 1.619% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 02:00 | 3 | 22 | 2 | 81 | 1922 | 39.92 | 1124.6804 | 0 | 0 | 1124.6804 | Heating | 992.3651 | 8.5 | 992.3651 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 198.473 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1012.6174 | 0 | 202.5235 | 2.025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 03:00 | 3 | 22 | 3 | 81 | 1923 | 39.02 | 1393.5522 | 0 | 0 | 1393.5522 | Heating | 1229.6049 | 8.5 | 1229.6049 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1254.6989 | 0 | 250.9398 | 2.509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 04:00 | 3 | 22 | 4 | 81 | 1924 | 39.02 | 1690.9588 | 0 | 0 | 1690.9588 | Heating | 1492.0224 | 8.5 | 1492.0224 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 298.4045 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1522.4719 | 0 | 304.4944 | 3.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 05:00 | 3 | 22 | 5 | 81 | 1925 | 39.02 | 1924.6473 | 0 | 0 | 1924.6473 | Heating | 1698.2182 | 8.5 | 1698.2182 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.6436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1732.8757 | 0 | 346.5751 | 3.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 06:00 | 3 | 22 | 6 | 81 | 1926 | 37.94 | 2081.4172 | 0 | 0 | 2081.4172 | Heating | 1836.5445 | 8.5 | 1836.5445 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 367.3089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1874.0251 | 0 | 374.805 | 3.748% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 07:00 | 3 | 22 | 7 | 81 | 1927 | 37.04 | 11837.8775 | 0 | 0 | 11837.8775 | Heating | 10445.1861 | 8.5 | 10445.1861 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2089.0372 | 41.78% | 1 | 83.56% | 0% | 0% | 0% | 53.9209 | 0 | 0 | 0 | 53.9209 | 10658.3531 | 0 | 2131.6706 | 21.32% | 1 | 42.63% | 0% | 0% | 5.7351 | 0 | 0 | 5.7351 | 59.656
2007-03-22 08:00 | 3 | 22 | 8 | 81 | 1928 | 37.04 | 9056.0736 | 0 | 0 | 9056.0736 | Heating | 7990.6531 | 8.5 | 7990.6531 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1598.1306 | 31.96% | 1 | 63.93% | 0% | 0% | 0% | 29.1199 | 0 | 0 | 0 | 29.1199 | 8153.7277 | 0 | 1630.7455 | 16.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.3944
2007-03-22 09:00 | 3 | 22 | 9 | 81 | 1929 | 39.02 | 7357.6458 | 0 | 0 | 7357.6458 | Heating | 6492.0404 | 8.5 | 6492.0404 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1298.4081 | 30% | 1 | 51.94% | 0% | 0% | 0% | 18.0604 | 0 | 0 | 0 | 18.0604 | 6624.5311 | 0 | 1324.9062 | 13.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.3349
2007-03-22 10:00 | 3 | 22 | 10 | 81 | 1930 | 39.92 | 5860.6305 | 0 | 0 | 5860.6305 | Heating | 5171.1445 | 8.5 | 5171.1445 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1034.2289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5276.6781 | 0 | 1055.3356 | 10.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 11:00 | 3 | 22 | 11 | 81 | 1931 | 39.92 | 5010.974 | 0 | 0 | 5010.974 | Heating | 4421.4476 | 8.5 | 4421.4476 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 884.2895 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4511.6812 | 0 | 902.3362 | 9.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 12:00 | 3 | 22 | 12 | 81 | 1932 | 41 | 4314.6037 | 0 | 0 | 4314.6037 | Heating | 3807.0033 | 8.5 | 3807.0033 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 761.4007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3884.6972 | 0 | 776.9394 | 7.769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 13:00 | 3 | 22 | 13 | 81 | 1933 | 41 | 3907.5184 | 0 | 0 | 3907.5184 | Heating | 3447.8104 | 8.5 | 3447.8104 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 689.5621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3518.1739 | 0 | 703.6348 | 7.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 14:00 | 3 | 22 | 14 | 81 | 1934 | 41 | 3644.9543 | 0 | 0 | 3644.9543 | Heating | 3216.1361 | 8.5 | 3216.1361 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 643.2272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3281.7715 | 0 | 656.3543 | 6.564% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 15:00 | 3 | 22 | 15 | 81 | 1935 | 41 | 3501.0828 | 0 | 0 | 3501.0828 | Heating | 3089.1907 | 8.5 | 3089.1907 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 617.8381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3152.2354 | 0 | 630.4471 | 6.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 16:00 | 3 | 22 | 16 | 81 | 1936 | 41 | 3396.9855 | 0 | 0 | 3396.9855 | Heating | 2997.3401 | 8.5 | 2997.3401 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 599.468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3058.5103 | 0 | 611.7021 | 6.117% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 17:00 | 3 | 22 | 17 | 81 | 1937 | 41 | 3651.7174 | 0 | 0 | 3651.7174 | Heating | 3222.1036 | 8.5 | 3222.1036 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 644.4207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3287.8608 | 0 | 657.5722 | 6.576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 18:00 | 3 | 22 | 18 | 81 | 1938 | 39.02 | 4138.322 | 0 | 0 | 4138.322 | Heating | 3651.4606 | 8.5 | 3651.4606 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 730.2921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3725.9802 | 0 | 745.196 | 7.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 19:00 | 3 | 22 | 19 | 81 | 1939 | 35.96 | 4649.442 | 0 | 0 | 4649.442 | Heating | 4102.4489 | 8.5 | 4102.4489 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 820.4898 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4186.1723 | 0 | 837.2345 | 8.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 20:00 | 3 | 22 | 20 | 81 | 1940 | 35.96 | 5175.9076 | 0 | 0 | 5175.9076 | Heating | 4566.9773 | 8.5 | 4566.9773 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 913.3955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4660.1809 | 0 | 932.0362 | 9.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 21:00 | 3 | 22 | 21 | 81 | 1941 | 37.04 | 5699.4597 | 0 | 0 | 5699.4597 | Heating | 5028.935 | 8.5 | 5028.935 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1005.787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5131.5664 | 0 | 1026.3133 | 10.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 22:00 | 3 | 22 | 22 | 81 | 1942 | 33.98 | 1701.737 | 0 | 0 | 1701.737 | Heating | 1501.5327 | 8.5 | 1501.5327 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.3065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1532.1762 | 0 | 306.4352 | 3.064% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-22 23:00 | 3 | 22 | 23 | 81 | 1943 | 33.98 | 1563.301 | 0 | 0 | 1563.301 | Heating | 1379.3833 | 8.5 | 1379.3833 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 275.8767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1407.534 | 0 | 281.5068 | 2.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 | 3 | 23 | 0 | 82 | 1944 | 32 | 1861.1417 | 0 | 0 | 1861.1417 | Heating | 1642.1838 | 8.5 | 1642.1838 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.4368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1675.6978 | 0 | 335.1396 | 3.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 01:00 | 3 | 23 | 1 | 82 | 1945 | 30.92 | 2054.2154 | 0 | 0 | 2054.2154 | Heating | 1812.543 | 8.5 | 1812.543 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.5086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1849.5337 | 0 | 369.9067 | 3.699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 02:00 | 3 | 23 | 2 | 82 | 1946 | 30.92 | 2224.323 | 0 | 0 | 2224.323 | Heating | 1962.638 | 8.5 | 1962.638 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 392.5276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2002.6918 | 0 | 400.5384 | 4.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 03:00 | 3 | 23 | 3 | 82 | 1947 | 30.02 | 2351.2364 | 0 | 0 | 2351.2364 | Heating | 2074.6204 | 8.5 | 2074.6204 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 414.9241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2116.9595 | 0 | 423.3919 | 4.234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 04:00 | 3 | 23 | 4 | 82 | 1948 | 30.02 | 2459.7648 | 0 | 0 | 2459.7648 | Heating | 2170.3807 | 8.5 | 2170.3807 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 434.0761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2214.6742 | 0 | 442.9348 | 4.429% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 05:00 | 3 | 23 | 5 | 82 | 1949 | 30.02 | 2522.8621 | 0 | 0 | 2522.8621 | Heating | 2226.0548 | 8.5 | 2226.0548 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2271.4845 | 0 | 454.2969 | 4.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 06:00 | 3 | 23 | 6 | 82 | 1950 | 28.04 | 2536.9053 | 0 | 0 | 2536.9053 | Heating | 2238.4459 | 8.5 | 2238.4459 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 447.6892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2284.1285 | 0 | 456.8257 | 4.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 07:00 | 3 | 23 | 7 | 82 | 1951 | 26.96 | 12718.4435 | 0 | 0 | 12718.4435 | Heating | 11222.156 | 8.5 | 11222.156 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2244.4312 | 44.89% | 1 | 89.78% | 0% | 0% | 0% | 63.5954 | 0 | 0 | 0 | 63.5954 | 11451.1796 | 0 | 2290.2359 | 22.9% | 1 | 45.8% | 0% | 0% | 6.764 | 0 | 0 | 6.764 | 70.3594
2007-03-23 08:00 | 3 | 23 | 8 | 82 | 1952 | 26.96 | 9737.4897 | 0 | 0 | 9737.4897 | Heating | 8591.9027 | 8.5 | 8591.9027 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1718.3805 | 34.37% | 1 | 68.74% | 0% | 0% | 0% | 34.4077 | 0 | 0 | 0 | 34.4077 | 8767.2477 | 0 | 1753.4495 | 17.53% | 1 | 35.07% | 0% | 0% | 3.6596 | 0 | 0 | 3.6596 | 38.0673
2007-03-23 09:00 | 3 | 23 | 9 | 82 | 1953 | 28.04 | 7697.4879 | 0 | 0 | 7697.4879 | Heating | 6791.9011 | 8.5 | 6791.9011 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1358.3802 | 30% | 1 | 54.34% | 0% | 0% | 0% | 20.0369 | 0 | 0 | 0 | 20.0369 | 6930.5113 | 0 | 1386.1023 | 13.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.3114
2007-03-23 10:00 | 3 | 23 | 10 | 82 | 1954 | 28.04 | 5651.9277 | 0 | 0 | 5651.9277 | Heating | 4986.995 | 8.5 | 4986.995 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 997.399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5088.7704 | 0 | 1017.7541 | 10.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 11:00 | 3 | 23 | 11 | 82 | 1955 | 28.04 | 3941.108 | 0 | 0 | 3941.108 | Heating | 3477.4482 | 8.5 | 3477.4482 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 695.4896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3548.4166 | 0 | 709.6833 | 7.097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 12:00 | 3 | 23 | 12 | 82 | 1956 | 28.94 | 2679.0783 | 0 | 0 | 2679.0783 | Heating | 2363.8926 | 8.5 | 2363.8926 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 472.7785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2412.1353 | 0 | 482.4271 | 4.824% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 13:00 | 3 | 23 | 13 | 82 | 1957 | 30.02 | 1819.1388 | 0 | 0 | 1819.1388 | Heating | 1605.1225 | 8.5 | 1605.1225 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.0245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1637.8801 | 0 | 327.576 | 3.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 14:00 | 3 | 23 | 14 | 82 | 1958 | 30.02 | 1236.8749 | 0.02258 | 0.02258 | 1236.8524 | Heating | 1091.3403 | 8.5 | 1091.3403 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.2681 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1113.6126 | 0 | 222.7225 | 2.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 15:00 | 3 | 23 | 15 | 82 | 1959 | 30.92 | 836.9127 | 0 | 0 | 836.9127 | Heating | 738.4524 | 8.5 | 738.4524 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 147.6905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 753.5228 | 0 | 150.7046 | 1.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 16:00 | 3 | 23 | 16 | 82 | 1960 | 32 | 518.3046 | 0 | 0 | 518.3046 | Heating | 457.3276 | 8.5 | 457.3276 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.4655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 466.6608 | 0 | 93.3322 | 0.9333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 17:00 | 3 | 23 | 17 | 82 | 1961 | 32 | 616.0652 | 0 | 0 | 616.0652 | Heating | 543.5869 | 8.5 | 543.5869 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.7174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 554.6805 | 0 | 110.9361 | 1.109% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 18:00 | 3 | 23 | 18 | 82 | 1962 | 30.2 | 1152.2135 | 0 | 0 | 1152.2135 | Heating | 1016.659 | 8.5 | 1016.659 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 203.3318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1037.4071 | 0 | 207.4814 | 2.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 19:00 | 3 | 23 | 19 | 82 | 1963 | 30.02 | 2082.6734 | 0 | 0 | 2082.6734 | Heating | 1837.653 | 8.5 | 1837.653 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 367.5306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1875.1561 | 0 | 375.0312 | 3.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 20:00 | 3 | 23 | 20 | 82 | 1964 | 30.02 | 2879.5149 | 0 | 0 | 2879.5149 | Heating | 2540.7485 | 8.5 | 2540.7485 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 508.1497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2592.6005 | 0 | 518.5201 | 5.185% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 21:00 | 3 | 23 | 21 | 82 | 1965 | 28.94 | 3535.4371 | 0 | 0 | 3535.4371 | Heating | 3119.5033 | 8.5 | 3119.5033 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 623.9007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3183.1667 | 0 | 636.6333 | 6.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 22:00 | 3 | 23 | 22 | 82 | 1966 | 28.94 | 4449.9947 | 0 | 0 | 4449.9947 | Heating | 3926.4659 | 8.5 | 3926.4659 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 785.2932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4006.5979 | 0 | 801.3196 | 8.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-23 23:00 | 3 | 23 | 23 | 82 | 1967 | 28.94 | 1054.8794 | 0 | 0 | 1054.8794 | Heating | 930.776 | 8.5 | 930.776 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 186.1552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 949.7714 | 0 | 189.9543 | 1.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 | 3 | 24 | 0 | 83 | 1968 | 28.04 | 1088.1094 | 0 | 0 | 1088.1094 | Heating | 960.0965 | 8.5 | 960.0965 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 192.0193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 979.6903 | 0 | 195.9381 | 1.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 01:00 | 3 | 24 | 1 | 83 | 1969 | 28.04 | 1102.6968 | 0 | 0 | 1102.6968 | Heating | 972.9678 | 8.5 | 972.9678 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 194.5936 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 992.8243 | 0 | 198.5649 | 1.986% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 02:00 | 3 | 24 | 2 | 83 | 1970 | 28.04 | 1132.1102 | 0 | 0 | 1132.1102 | Heating | 998.9208 | 8.5 | 998.9208 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.7842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1019.3069 | 0 | 203.8614 | 2.039% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 03:00 | 3 | 24 | 3 | 83 | 1971 | 26.96 | 1177.5751 | 0 | 0 | 1177.5751 | Heating | 1039.0368 | 8.5 | 1039.0368 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.8074 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1060.2417 | 0 | 212.0483 | 2.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 04:00 | 3 | 24 | 4 | 83 | 1972 | 26.06 | 1218.5243 | 0 | 0 | 1218.5243 | Heating | 1075.1685 | 8.5 | 1075.1685 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.0337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1097.1107 | 0 | 219.4221 | 2.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 05:00 | 3 | 24 | 5 | 83 | 1973 | 26.06 | 1236.064 | 0 | 0 | 1236.064 | Heating | 1090.6447 | 8.5 | 1090.6447 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.1289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1112.9028 | 0 | 222.5806 | 2.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 06:00 | 3 | 24 | 6 | 83 | 1974 | 24.8 | 1234.6546 | 0 | 0 | 1234.6546 | Heating | 1089.4011 | 8.5 | 1089.4011 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.8802 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1111.6338 | 0 | 222.3268 | 2.223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 07:00 | 3 | 24 | 7 | 83 | 1975 | 24.98 | 1174.0065 | 0 | 0 | 1174.0065 | Heating | 1035.8881 | 8.5 | 1035.8881 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.1776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1057.0287 | 0 | 211.4057 | 2.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 08:00 | 3 | 24 | 8 | 83 | 1976 | 24.98 | 971.7511 | 0 | 0 | 971.7511 | Heating | 857.4275 | 8.5 | 857.4275 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.4855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 874.926 | 0 | 174.9852 | 1.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 09:00 | 3 | 24 | 9 | 83 | 1977 | 30.02 | 6345.6013 | 0 | 0 | 6345.6013 | Heating | 5599.06 | 8.5 | 5599.06 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1119.812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5713.3265 | 0 | 1142.6653 | 11.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 10:00 | 3 | 24 | 10 | 83 | 1978 | 32 | 3702.3879 | 0 | 0 | 3702.3879 | Heating | 3266.8128 | 8.5 | 3266.8128 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 653.3626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3333.4825 | 0 | 666.6965 | 6.667% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 11:00 | 3 | 24 | 11 | 83 | 1979 | 32 | 2169.2604 | 0 | 0 | 2169.2604 | Heating | 1914.0533 | 8.5 | 1914.0533 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 382.8107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1953.1156 | 0 | 390.6231 | 3.906% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 12:00 | 3 | 24 | 12 | 83 | 1980 | 37.94 | 1149.2731 | 0 | 0 | 1149.2731 | Heating | 1014.0645 | 8.5 | 1014.0645 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.8129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1034.7597 | 0 | 206.9519 | 2.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 13:00 | 3 | 24 | 13 | 83 | 1981 | 37.04 | 181.124 | 0 | 0 | 181.124 | Heating | 159.8153 | 8.5 | 159.8153 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.9631 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 163.0768 | 0 | 32.6154 | 0.3262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 14:00 | 3 | 24 | 14 | 83 | 1982 | 37.04 | 50.7459 | 0 | 0 | 50.7459 | Heating | 44.7758 | 8.5 | 44.7758 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.9552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 45.6896 | 0 | 9.1379 | 0.09138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 15:00 | 3 | 24 | 15 | 83 | 1983 | 42.08 | 24.763 | 0 | 0 | 24.763 | Heating | 21.8497 | 8.5 | 21.8497 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.3699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.2956 | 0 | 4.4591 | 0.04459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 16:00 | 3 | 24 | 16 | 83 | 1984 | 39.92 | 8.0268 | 0 | 0 | 8.0268 | Heating | 7.0824 | 8.5 | 7.0824 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.227 | 0 | 1.4454 | 0.01445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 17:00 | 3 | 24 | 17 | 83 | 1985 | 39.92 | 6.2711 | 0 | 0 | 6.2711 | Heating | 5.5334 | 8.5 | 5.5334 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1067 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.6463 | 0 | 1.1293 | 0.01129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 18:00 | 3 | 24 | 18 | 83 | 1986 | 37.04 | 12.3567 | 0 | 0 | 12.3567 | Heating | 10.903 | 8.5 | 10.903 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.1255 | 0 | 2.2251 | 0.02225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 19:00 | 3 | 24 | 19 | 83 | 1987 | 35.06 | 488.782 | 0 | 0 | 488.782 | Heating | 431.2783 | 8.5 | 431.2783 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 86.2557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 440.0799 | 0 | 88.016 | 0.8802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 20:00 | 3 | 24 | 20 | 83 | 1988 | 35.06 | 66.9915 | 0 | 0 | 66.9915 | Heating | 59.1101 | 8.5 | 59.1101 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.822 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 60.3164 | 0 | 12.0633 | 0.1206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 21:00 | 3 | 24 | 21 | 83 | 1989 | 32 | 125.073 | 0 | 0 | 125.073 | Heating | 110.3586 | 8.5 | 110.3586 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.0717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 112.6108 | 0 | 22.5222 | 0.2252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 22:00 | 3 | 24 | 22 | 83 | 1990 | 30.02 | 194.782 | 0 | 0 | 194.782 | Heating | 171.8665 | 8.5 | 171.8665 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.3733 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 175.374 | 0 | 35.0748 | 0.3507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-24 23:00 | 3 | 24 | 23 | 83 | 1991 | 30.02 | 279.6767 | 0 | 0 | 279.6767 | Heating | 246.7736 | 8.5 | 246.7736 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.3547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 251.8098 | 0 | 50.362 | 0.5036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 | 3 | 25 | 0 | 84 | 1992 | 28.94 | 357.5831 | 0 | 0 | 357.5831 | Heating | 315.5145 | 8.5 | 315.5145 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.1029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 321.9536 | 0 | 64.3907 | 0.6439% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 01:00 | 3 | 25 | 1 | 84 | 1993 | 28.04 | 433.237 | 0 | 0 | 433.237 | Heating | 382.2679 | 8.5 | 382.2679 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.4536 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 390.0693 | 0 | 78.0139 | 0.7801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 02:00 | 3 | 25 | 2 | 84 | 1994 | 28.04 | 486.532 | 0 | 0 | 486.532 | Heating | 429.293 | 8.5 | 429.293 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.8586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 438.054 | 0 | 87.6108 | 0.8761% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 03:00 | 3 | 25 | 3 | 84 | 1995 | 26.96 | 529.3181 | 0 | 0 | 529.3181 | Heating | 467.0454 | 8.5 | 467.0454 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.4091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 476.5769 | 0 | 95.3154 | 0.9532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 04:00 | 3 | 25 | 4 | 84 | 1996 | 26.06 | 578.4552 | 0 | 0 | 578.4552 | Heating | 510.4017 | 8.5 | 510.4017 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.0803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 520.818 | 0 | 104.1636 | 1.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 05:00 | 3 | 25 | 5 | 84 | 1997 | 26.06 | 604.1378 | 0 | 0 | 604.1378 | Heating | 533.0628 | 8.5 | 533.0628 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.6126 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 543.9416 | 0 | 108.7883 | 1.088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 06:00 | 3 | 25 | 6 | 84 | 1998 | 24.98 | 600.5792 | 0 | 0 | 600.5792 | Heating | 529.9228 | 8.5 | 529.9228 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.9846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 540.7376 | 0 | 108.1475 | 1.081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 07:00 | 3 | 25 | 7 | 84 | 1999 | 26.96 | 6221.1354 | 0 | 0 | 6221.1354 | Heating | 5489.2371 | 8.5 | 5489.2371 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1097.8474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5601.2624 | 0 | 1120.2525 | 11.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 08:00 | 3 | 25 | 8 | 84 | 2000 | 26.96 | 4156.4148 | 0 | 0 | 4156.4148 | Heating | 3667.4248 | 8.5 | 3667.4248 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 733.485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3742.2702 | 0 | 748.454 | 7.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 09:00 | 3 | 25 | 9 | 84 | 2001 | 33.08 | 2855.499 | 0 | 0 | 2855.499 | Heating | 2519.558 | 8.5 | 2519.558 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 503.9116 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2570.9775 | 0 | 514.1955 | 5.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 10:00 | 3 | 25 | 10 | 84 | 2002 | 33.98 | 1672.8285 | 0 | 0 | 1672.8285 | Heating | 1476.0252 | 8.5 | 1476.0252 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1506.1481 | 0 | 301.2296 | 3.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 11:00 | 3 | 25 | 11 | 84 | 2003 | 33.98 | 976.161 | 0 | 0 | 976.161 | Heating | 861.3185 | 8.5 | 861.3185 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.2637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 878.8964 | 0 | 175.7793 | 1.758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 12:00 | 3 | 25 | 12 | 84 | 2004 | 35.96 | 354.4948 | 0 | 0 | 354.4948 | Heating | 312.7895 | 8.5 | 312.7895 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.5579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 319.173 | 0 | 63.8346 | 0.6383% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 13:00 | 3 | 25 | 13 | 84 | 2005 | 37.04 | 177.8443 | 0 | 0 | 177.8443 | Heating | 156.9214 | 8.5 | 156.9214 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.3843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 160.1239 | 0 | 32.0248 | 0.3202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 14:00 | 3 | 25 | 14 | 84 | 2006 | 37.04 | 150.1637 | 18.5248 | 18.5248 | 131.6389 | Heating | 116.152 | 8.5 | 116.152 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.2304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 118.5224 | 0 | 23.7045 | 0.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 15:00 | 3 | 25 | 15 | 84 | 2007 | 35.96 | 170.8011 | 40.2047 | 40.2047 | 130.5965 | Heating | 115.2322 | 8.5 | 115.2322 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.0464 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 117.5838 | 0 | 23.5168 | 0.2352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 16:00 | 3 | 25 | 16 | 84 | 2008 | 35.06 | 197.8224 | 48.4432 | 48.4432 | 149.3792 | Heating | 131.8052 | 8.5 | 131.8052 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 134.4951 | 0 | 26.899 | 0.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 17:00 | 3 | 25 | 17 | 84 | 2009 | 35.06 | 208.333 | 60.0689 | 60.0689 | 148.264 | Heating | 130.8212 | 8.5 | 130.8212 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.1642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 133.491 | 0 | 26.6982 | 0.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 18:00 | 3 | 25 | 18 | 84 | 2010 | 30.02 | 220.2331 | 26.5346 | 26.5346 | 193.6985 | Heating | 170.9105 | 8.5 | 170.9105 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.1821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 174.3984 | 0 | 34.8797 | 0.3488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 19:00 | 3 | 25 | 19 | 84 | 2011 | 28.94 | 325.6904 | 0.29953 | 0.29953 | 325.3909 | Heating | 287.1096 | 8.5 | 287.1096 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.4219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 292.969 | 0 | 58.5938 | 0.5859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 20:00 | 3 | 25 | 20 | 84 | 2012 | 28.94 | 881.611 | 0 | 0 | 881.611 | Heating | 777.8921 | 8.5 | 777.8921 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.5784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 793.7674 | 0 | 158.7535 | 1.588% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 21:00 | 3 | 25 | 21 | 84 | 2013 | 26.06 | 1516.7623 | 0 | 0 | 1516.7623 | Heating | 1338.3196 | 8.5 | 1338.3196 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.6639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1365.6323 | 0 | 273.1265 | 2.731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 22:00 | 3 | 25 | 22 | 84 | 2014 | 24.98 | 467.1884 | 0 | 0 | 467.1884 | Heating | 412.2251 | 8.5 | 412.2251 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 420.6378 | 0 | 84.1276 | 0.8413% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-25 23:00 | 3 | 25 | 23 | 84 | 2015 | 24.98 | 542.3986 | 0 | 0 | 542.3986 | Heating | 478.587 | 8.5 | 478.587 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.7174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 488.3541 | 0 | 97.6708 | 0.9767% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 | 3 | 26 | 0 | 85 | 2016 | 23 | 595.0999 | 0 | 0 | 595.0999 | Heating | 525.0882 | 8.5 | 525.0882 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.0176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 535.8042 | 0 | 107.1608 | 1.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 01:00 | 3 | 26 | 1 | 85 | 2017 | 21.92 | 642.4565 | 0 | 0 | 642.4565 | Heating | 566.8734 | 8.5 | 566.8734 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.3747 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 578.4422 | 0 | 115.6884 | 1.157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 02:00 | 3 | 26 | 2 | 85 | 2018 | 21.92 | 671.667 | 0 | 0 | 671.667 | Heating | 592.6474 | 8.5 | 592.6474 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.5295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 604.7422 | 0 | 120.9484 | 1.209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 03:00 | 3 | 26 | 3 | 85 | 2019 | 21.02 | 692.6904 | 0 | 0 | 692.6904 | Heating | 611.1974 | 8.5 | 611.1974 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.2395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 623.6708 | 0 | 124.7342 | 1.247% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 04:00 | 3 | 26 | 4 | 85 | 2020 | 19.04 | 711.3459 | 0 | 0 | 711.3459 | Heating | 627.6581 | 8.5 | 627.6581 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.5316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 640.4675 | 0 | 128.0935 | 1.281% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 05:00 | 3 | 26 | 5 | 85 | 2021 | 19.04 | 739.3534 | 0 | 0 | 739.3534 | Heating | 652.3706 | 8.5 | 652.3706 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.4741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 665.6843 | 0 | 133.1369 | 1.331% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 06:00 | 3 | 26 | 6 | 85 | 2022 | 19.04 | 778.9394 | 0 | 0 | 778.9394 | Heating | 687.2995 | 8.5 | 687.2995 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.4599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 701.326 | 0 | 140.2652 | 1.403% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 07:00 | 3 | 26 | 7 | 85 | 2023 | 21.02 | 7418.521 | 0 | 0 | 7418.521 | Heating | 6545.7538 | 8.5 | 6545.7538 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1309.1508 | 30% | 1 | 52.37% | 0% | 0% | 0% | 18.4059 | 0 | 0 | 0 | 18.4059 | 6679.3406 | 0 | 1335.8681 | 13.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.6805
2007-03-26 08:00 | 3 | 26 | 8 | 85 | 2024 | 21.02 | 5003.3421 | 0 | 0 | 5003.3421 | Heating | 4414.7136 | 8.5 | 4414.7136 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 882.9427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4504.8098 | 0 | 900.962 | 9.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 09:00 | 3 | 26 | 9 | 85 | 2025 | 26.96 | 3313.0602 | 0 | 0 | 3313.0602 | Heating | 2923.2884 | 8.5 | 2923.2884 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 584.6577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2982.9474 | 0 | 596.5895 | 5.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 10:00 | 3 | 26 | 10 | 85 | 2026 | 28.94 | 1720.9188 | 5.3597 | 5.3597 | 1715.5592 | Heating | 1513.7287 | 8.5 | 1513.7287 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 302.7457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1544.6211 | 0 | 308.9242 | 3.089% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 11:00 | 3 | 26 | 11 | 85 | 2027 | 28.94 | 921.6753 | 22.9343 | 22.9343 | 898.741 | Heating | 793.0068 | 8.5 | 793.0068 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.6014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 809.1906 | 0 | 161.8381 | 1.618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 12:00 | 3 | 26 | 12 | 85 | 2028 | 33.08 | 323.7464 | 98.9258 | 98.9258 | 224.8206 | Heating | 198.3711 | 8.5 | 198.3711 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.6742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 202.4195 | 0 | 40.4839 | 0.4048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 13:00 | 3 | 26 | 13 | 85 | 2029 | 35.06 | 157.253 | 241.3748 | 241.3748 | -84.1218 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 295.0136 | 295.0136 | 0 | 8.5 | 0 | 49.1689 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 289.1134 | 57.8227 | 0.5782% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 14:00 | 3 | 26 | 14 | 85 | 2030 | 35.06 | 106.1782 | 416.6799 | 416.6799 | -310.5017 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 509.2755 | 509.2755 | 0 | 8.5 | 0 | 84.8792 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 499.09 | 99.818 | 0.9982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 15:00 | 3 | 26 | 15 | 85 | 2031 | 35.96 | 70.6516 | 568.5861 | 568.5861 | -497.9345 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 694.9386 | 694.9386 | 0 | 8.5 | 0 | 115.8231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 681.0398 | 136.208 | 1.362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 16:00 | 3 | 26 | 16 | 85 | 2032 | 35.06 | 40.0968 | 658.2533 | 658.2533 | -618.1565 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 804.5319 | 804.5319 | 0 | 8.5 | 0 | 134.0886 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 788.4412 | 157.6882 | 1.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 17:00 | 3 | 26 | 17 | 85 | 2033 | 35.06 | 40.0399 | 492.4459 | 492.4459 | -452.406 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 601.8783 | 601.8783 | 0 | 8.5 | 0 | 100.313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 589.8407 | 117.9681 | 1.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 18:00 | 3 | 26 | 18 | 85 | 2034 | 30.92 | 77.1121 | 289.8294 | 289.8294 | -212.7173 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 354.2359 | 354.2359 | 0 | 8.5 | 0 | 59.0393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 347.1512 | 69.4302 | 0.6943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 19:00 | 3 | 26 | 19 | 85 | 2035 | 28.94 | 131.8118 | 122.3659 | 122.3659 | 9.4459 | Heating | 8.3346 | 8.5 | 8.3346 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.5047 | 0 | 1.7009 | 0.01701% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 20:00 | 3 | 26 | 20 | 85 | 2036 | 28.94 | 607.8547 | 73.3329 | 73.3329 | 534.5218 | Heating | 471.6369 | 8.5 | 471.6369 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.3274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 481.2621 | 0 | 96.2524 | 0.9625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 21:00 | 3 | 26 | 21 | 85 | 2037 | 26.96 | 1414.128 | 15.495 | 15.495 | 1398.633 | Heating | 1234.088 | 8.5 | 1234.088 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 246.8176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1259.2734 | 0 | 251.8547 | 2.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 22:00 | 3 | 26 | 22 | 85 | 2038 | 26.06 | 432.0914 | 0.23293 | 0.23293 | 431.8585 | Heating | 381.0516 | 8.5 | 381.0516 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.2103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 388.8281 | 0 | 77.7656 | 0.7777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-26 23:00 | 3 | 26 | 23 | 85 | 2039 | 26.06 | 476.7601 | 0 | 0 | 476.7601 | Heating | 420.6706 | 8.5 | 420.6706 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.1341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 429.2558 | 0 | 85.8512 | 0.8585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 | 3 | 27 | 0 | 86 | 2040 | 24.98 | 458.0697 | 0 | 0 | 458.0697 | Heating | 404.1791 | 8.5 | 404.1791 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.8358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 412.4277 | 0 | 82.4855 | 0.8249% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 01:00 | 3 | 27 | 1 | 86 | 2041 | 24.08 | 422.6858 | 0 | 0 | 422.6858 | Heating | 372.9581 | 8.5 | 372.9581 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.5916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 380.5695 | 0 | 76.1139 | 0.7611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 02:00 | 3 | 27 | 2 | 86 | 2042 | 24.08 | 416.2665 | 0 | 0 | 416.2665 | Heating | 367.294 | 8.5 | 367.294 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.4588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 374.7898 | 0 | 74.958 | 0.7496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 03:00 | 3 | 27 | 3 | 86 | 2043 | 21.92 | 442.1682 | 0 | 0 | 442.1682 | Heating | 390.1484 | 8.5 | 390.1484 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.0297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 398.1106 | 0 | 79.6221 | 0.7962% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 04:00 | 3 | 27 | 4 | 86 | 2044 | 21.02 | 469.2893 | 0 | 0 | 469.2893 | Heating | 414.0788 | 8.5 | 414.0788 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.8158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 422.5294 | 0 | 84.5059 | 0.8451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 05:00 | 3 | 27 | 5 | 86 | 2045 | 21.02 | 473.7345 | 0 | 0 | 473.7345 | Heating | 418.001 | 8.5 | 418.001 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.6002 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 426.5317 | 0 | 85.3063 | 0.8531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 06:00 | 3 | 27 | 6 | 86 | 2046 | 21.02 | 453.6193 | 0 | 0 | 453.6193 | Heating | 400.2523 | 8.5 | 400.2523 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.0505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 408.4207 | 0 | 81.6841 | 0.8168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 07:00 | 3 | 27 | 7 | 86 | 2047 | 23 | 4763.743 | 34.2358 | 34.2358 | 4729.5072 | Heating | 4173.0946 | 8.5 | 4173.0946 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 834.6189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4258.2598 | 0 | 851.652 | 8.517% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 08:00 | 3 | 27 | 8 | 86 | 2048 | 23 | 2818.8051 | 0 | 0 | 2818.8051 | Heating | 2487.181 | 8.5 | 2487.181 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 497.4362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2537.9398 | 0 | 507.588 | 5.076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 09:00 | 3 | 27 | 9 | 86 | 2049 | 26.96 | 1681.0982 | 0 | 0 | 1681.0982 | Heating | 1483.322 | 8.5 | 1483.322 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.6644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1513.5938 | 0 | 302.7188 | 3.027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 10:00 | 3 | 27 | 10 | 86 | 2050 | 30.92 | 461.3745 | 20.2169 | 20.2169 | 441.1576 | Heating | 389.2567 | 8.5 | 389.2567 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.8513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 397.2008 | 0 | 79.4402 | 0.7944% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 11:00 | 3 | 27 | 11 | 86 | 2051 | 30.92 | 115.1371 | 87.7713 | 87.7713 | 27.3659 | Heating | 24.1464 | 8.5 | 24.1464 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.8293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.6392 | 0 | 4.9278 | 0.04928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 12:00 | 3 | 27 | 12 | 86 | 2052 | 33.98 | 49.2519 | 270.571 | 270.571 | -221.3191 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 330.6979 | 330.6979 | 0 | 8.5 | 0 | 55.1163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 324.0839 | 64.8168 | 0.6482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 13:00 | 3 | 27 | 13 | 86 | 2053 | 35.96 | 14.2531 | 585.2788 | 585.2788 | -571.0257 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 715.3408 | 715.3408 | 0 | 8.5 | 0 | 119.2235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 701.034 | 140.2068 | 1.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 14:00 | 3 | 27 | 14 | 86 | 2054 | 35.96 | 3.9306 | 1410.3212 | 1410.3212 | -1406.3906 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1723.7259 | 1723.7259 | 0 | 8.5 | 0 | 287.2876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1689.2514 | 337.8503 | 3.379% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 15:00 | 3 | 27 | 15 | 86 | 2055 | 37.04 | 0.66351 | 2003.5023 | 2003.5023 | -2002.8388 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2448.725 | 2448.725 | 0 | 8.5 | 0 | 408.1208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2399.7505 | 479.9501 | 4.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 16:00 | 3 | 27 | 16 | 86 | 2056 | 35.96 | 0 | 2334.6578 | 2334.6578 | -2334.6578 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2853.4706 | 2853.4706 | 0 | 8.5 | 0 | 475.5784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2796.4012 | 559.2802 | 5.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 17:00 | 3 | 27 | 17 | 86 | 2057 | 35.96 | 0 | 1989.5473 | 1989.5473 | -1989.5473 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2431.6689 | 2431.6689 | 0 | 8.5 | 0 | 405.2782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2383.0355 | 476.6071 | 4.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 18:00 | 3 | 27 | 18 | 86 | 2058 | 32 | 1.3255 | 912.3345 | 912.3345 | -911.0091 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1115.0755 | 1115.0755 | 0 | 8.5 | 0 | 185.8459 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1092.774 | 218.5548 | 2.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 19:00 | 3 | 27 | 19 | 86 | 2059 | 28.94 | 7.943 | 218.6124 | 218.6124 | -210.6694 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 267.1929 | 267.1929 | 0 | 8.5 | 0 | 44.5322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 261.849 | 52.3698 | 0.5237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 20:00 | 3 | 27 | 20 | 86 | 2060 | 28.94 | 24.365 | 174.57 | 174.57 | -150.205 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 213.3633 | 213.3633 | 0 | 8.5 | 0 | 35.5605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 209.096 | 41.8192 | 0.4182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 21:00 | 3 | 27 | 21 | 86 | 2061 | 26.96 | 46.1316 | 85.8524 | 85.8524 | -39.7208 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 104.9307 | 104.9307 | 0 | 8.5 | 0 | 17.4885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 102.8321 | 20.5664 | 0.2057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 22:00 | 3 | 27 | 22 | 86 | 2062 | 26.06 | 68.2557 | 54.1429 | 54.1429 | 14.1128 | Heating | 12.4525 | 8.5 | 12.4525 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.7066 | 0 | 2.5413 | 0.02541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-27 23:00 | 3 | 27 | 23 | 86 | 2063 | 26.06 | 112.6651 | 0 | 0 | 112.6651 | Heating | 99.4104 | 8.5 | 99.4104 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.8821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 101.4392 | 0 | 20.2878 | 0.2029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 | 3 | 28 | 0 | 87 | 2064 | 26.96 | 153.9325 | 0 | 0 | 153.9325 | Heating | 135.8228 | 8.5 | 135.8228 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.1646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 138.5947 | 0 | 27.7189 | 0.2772% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 01:00 | 3 | 28 | 1 | 87 | 2065 | 26.96 | 198.572 | 0 | 0 | 198.572 | Heating | 175.2106 | 8.5 | 175.2106 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.0421 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 178.7863 | 0 | 35.7573 | 0.3576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 02:00 | 3 | 28 | 2 | 87 | 2066 | 26.96 | 261.9549 | 0 | 0 | 261.9549 | Heating | 231.1367 | 8.5 | 231.1367 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 46.2273 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 235.8537 | 0 | 47.1707 | 0.4717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 03:00 | 3 | 28 | 3 | 87 | 2067 | 24.98 | 343.3945 | 0 | 0 | 343.3945 | Heating | 302.9951 | 8.5 | 302.9951 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 309.1787 | 0 | 61.8357 | 0.6184% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 04:00 | 3 | 28 | 4 | 87 | 2068 | 24.98 | 428.3387 | 0 | 0 | 428.3387 | Heating | 377.9459 | 8.5 | 377.9459 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.5892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 385.6591 | 0 | 77.1318 | 0.7713% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 05:00 | 3 | 28 | 5 | 87 | 2069 | 24.98 | 489.7777 | 0 | 0 | 489.7777 | Heating | 432.1568 | 8.5 | 432.1568 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 86.4314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 440.9763 | 0 | 88.1953 | 0.882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 06:00 | 3 | 28 | 6 | 87 | 2070 | 24.08 | 523.0506 | 0 | 0 | 523.0506 | Heating | 461.5152 | 8.5 | 461.5152 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 470.9339 | 0 | 94.1868 | 0.9419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 07:00 | 3 | 28 | 7 | 87 | 2071 | 24.98 | 5573.2778 | 0 | 0 | 5573.2778 | Heating | 4917.5981 | 8.5 | 4917.5981 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 983.5196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5017.9572 | 0 | 1003.5914 | 10.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 08:00 | 3 | 28 | 8 | 87 | 2072 | 24.98 | 4178.6668 | 0 | 0 | 4178.6668 | Heating | 3687.0589 | 8.5 | 3687.0589 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 737.4118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3762.305 | 0 | 752.461 | 7.525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 09:00 | 3 | 28 | 9 | 87 | 2073 | 30.92 | 3643.3434 | 0 | 0 | 3643.3434 | Heating | 3214.7148 | 8.5 | 3214.7148 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 642.943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3280.3212 | 0 | 656.0642 | 6.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 10:00 | 3 | 28 | 10 | 87 | 2074 | 33.08 | 3076.2037 | 0 | 0 | 3076.2037 | Heating | 2714.2974 | 8.5 | 2714.2974 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 542.8595 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2769.6912 | 0 | 553.9382 | 5.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 11:00 | 3 | 28 | 11 | 87 | 2075 | 33.08 | 2742.7811 | 0 | 0 | 2742.7811 | Heating | 2420.101 | 8.5 | 2420.101 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 484.0202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2469.4908 | 0 | 493.8982 | 4.939% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 12:00 | 3 | 28 | 12 | 87 | 2076 | 37.94 | 2282.5017 | 0 | 0 | 2282.5017 | Heating | 2013.9721 | 8.5 | 2013.9721 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.7944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2055.0736 | 0 | 411.0147 | 4.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 13:00 | 3 | 28 | 13 | 87 | 2077 | 39.92 | 1950.2572 | 0 | 0 | 1950.2572 | Heating | 1720.8152 | 8.5 | 1720.8152 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1755.9339 | 0 | 351.1868 | 3.512% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 14:00 | 3 | 28 | 14 | 87 | 2078 | 39.92 | 1822.9352 | 7.4727 | 7.4727 | 1815.4626 | Heating | 1601.8788 | 8.5 | 1601.8788 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.3758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1634.5702 | 0 | 326.914 | 3.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 15:00 | 3 | 28 | 15 | 87 | 2079 | 42.08 | 1828.8683 | 7.4856 | 7.4856 | 1821.3827 | Heating | 1607.1024 | 8.5 | 1607.1024 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.4205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1639.9004 | 0 | 327.9801 | 3.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 16:00 | 3 | 28 | 16 | 87 | 2080 | 41 | 1902.4817 | 5.5372 | 5.5372 | 1896.9444 | Heating | 1673.7745 | 8.5 | 1673.7745 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 334.7549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1707.9332 | 0 | 341.5866 | 3.416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 17:00 | 3 | 28 | 17 | 87 | 2081 | 41 | 2070.364 | 15.5476 | 15.5476 | 2054.8164 | Heating | 1813.0733 | 8.5 | 1813.0733 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.6147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1850.0748 | 0 | 370.015 | 3.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 18:00 | 3 | 28 | 18 | 87 | 2082 | 35.96 | 2346.5813 | 9.8031 | 9.8031 | 2336.7782 | Heating | 2061.8632 | 8.5 | 2061.8632 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.3726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2103.942 | 0 | 420.7884 | 4.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 19:00 | 3 | 28 | 19 | 87 | 2083 | 35.06 | 2655.956 | 0 | 0 | 2655.956 | Heating | 2343.4906 | 8.5 | 2343.4906 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 468.6981 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2391.3169 | 0 | 478.2634 | 4.783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 20:00 | 3 | 28 | 20 | 87 | 2084 | 35.06 | 2898.9915 | 0 | 0 | 2898.9915 | Heating | 2557.9337 | 8.5 | 2557.9337 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 511.5867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2610.1364 | 0 | 522.0273 | 5.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 21:00 | 3 | 28 | 21 | 87 | 2085 | 33.08 | 3113.4099 | 0 | 0 | 3113.4099 | Heating | 2747.1264 | 8.5 | 2747.1264 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 549.4253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2803.1902 | 0 | 560.638 | 5.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 22:00 | 3 | 28 | 22 | 87 | 2086 | 32 | 778.6228 | 0 | 0 | 778.6228 | Heating | 687.0201 | 8.5 | 687.0201 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 701.0409 | 0 | 140.2082 | 1.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-28 23:00 | 3 | 28 | 23 | 87 | 2087 | 32 | 776.6101 | 0 | 0 | 776.6101 | Heating | 685.2442 | 8.5 | 685.2442 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.0488 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 699.2288 | 0 | 139.8458 | 1.398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 | 3 | 29 | 0 | 88 | 2088 | 30.92 | 843.596 | 0 | 0 | 843.596 | Heating | 744.3494 | 8.5 | 744.3494 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.8699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 759.5402 | 0 | 151.908 | 1.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 01:00 | 3 | 29 | 1 | 88 | 2089 | 30.02 | 918.4051 | 0 | 0 | 918.4051 | Heating | 810.3574 | 8.5 | 810.3574 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.0715 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 826.8953 | 0 | 165.3791 | 1.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 02:00 | 3 | 29 | 2 | 88 | 2090 | 30.02 | 1009.9811 | 0 | 0 | 1009.9811 | Heating | 891.1598 | 8.5 | 891.1598 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 178.232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 909.3468 | 0 | 181.8694 | 1.819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 03:00 | 3 | 29 | 3 | 88 | 2091 | 28.94 | 1129.6362 | 0 | 0 | 1129.6362 | Heating | 996.7378 | 8.5 | 996.7378 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.3476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1017.0794 | 0 | 203.4159 | 2.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 04:00 | 3 | 29 | 4 | 88 | 2092 | 28.04 | 1265.3401 | 0 | 0 | 1265.3401 | Heating | 1116.4766 | 8.5 | 1116.4766 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.2953 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1139.2618 | 0 | 227.8524 | 2.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 05:00 | 3 | 29 | 5 | 88 | 2093 | 28.04 | 1345.1579 | 0 | 0 | 1345.1579 | Heating | 1186.904 | 8.5 | 1186.904 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.3808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1211.1265 | 0 | 242.2253 | 2.422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 06:00 | 3 | 29 | 6 | 88 | 2094 | 28.04 | 1355.1532 | 0 | 0 | 1355.1532 | Heating | 1195.7234 | 8.5 | 1195.7234 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 239.1447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1220.1259 | 0 | 244.0252 | 2.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 07:00 | 3 | 29 | 7 | 88 | 2095 | 30.02 | 9718.3175 | 0 | 0 | 9718.3175 | Heating | 8574.986 | 8.5 | 8574.986 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1714.9972 | 34.3% | 1 | 68.6% | 0% | 0% | 0% | 34.2521 | 0 | 0 | 0 | 34.2521 | 8749.9858 | 0 | 1749.9972 | 17.5% | 1 | 35% | 0% | 0% | 3.6431 | 0 | 0 | 3.6431 | 37.8951
2007-03-29 08:00 | 3 | 29 | 8 | 88 | 2096 | 30.02 | 6994.2046 | 0 | 0 | 6994.2046 | Heating | 6171.357 | 8.5 | 6171.357 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1234.2714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6297.303 | 0 | 1259.4606 | 12.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 09:00 | 3 | 29 | 9 | 88 | 2097 | 33.98 | 5285.9339 | 0 | 0 | 5285.9339 | Heating | 4664.0593 | 8.5 | 4664.0593 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 932.8119 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4759.2442 | 0 | 951.8488 | 9.518% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 10:00 | 3 | 29 | 10 | 88 | 2098 | 35.06 | 3710.3643 | 0 | 0 | 3710.3643 | Heating | 3273.8509 | 8.5 | 3273.8509 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 654.7702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3340.6641 | 0 | 668.1328 | 6.681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 11:00 | 3 | 29 | 11 | 88 | 2099 | 35.06 | 2631.344 | 0 | 0 | 2631.344 | Heating | 2321.7741 | 8.5 | 2321.7741 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 464.3548 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2369.1573 | 0 | 473.8315 | 4.738% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 12:00 | 3 | 29 | 12 | 88 | 2100 | 37.04 | 1642.9356 | 16.4268 | 16.4268 | 1626.5088 | Heating | 1435.1548 | 8.5 | 1435.1548 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 287.031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1464.4437 | 0 | 292.8887 | 2.929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 13:00 | 3 | 29 | 13 | 88 | 2101 | 41 | 842.8215 | 64.3813 | 64.3813 | 778.4402 | Heating | 686.859 | 8.5 | 686.859 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.3718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 700.8765 | 0 | 140.1753 | 1.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 14:00 | 3 | 29 | 14 | 88 | 2102 | 41 | 446.5227 | 173.9045 | 173.9045 | 272.6182 | Heating | 240.5455 | 8.5 | 240.5455 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.1091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 245.4546 | 0 | 49.0909 | 0.4909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 15:00 | 3 | 29 | 15 | 88 | 2103 | 42.08 | 364.6797 | 210.6993 | 210.6993 | 153.9803 | Heating | 135.865 | 8.5 | 135.865 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.173 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 138.6378 | 0 | 27.7276 | 0.2773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 16:00 | 3 | 29 | 16 | 88 | 2104 | 44.06 | 302.3968 | 156.4911 | 156.4911 | 145.9057 | Heating | 128.7403 | 8.5 | 128.7403 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.7481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 131.3677 | 0 | 26.2735 | 0.2627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 17:00 | 3 | 29 | 17 | 88 | 2105 | 44.06 | 364.8105 | 121.2891 | 121.2891 | 243.5213 | Heating | 214.8718 | 8.5 | 214.8718 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 42.9744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 219.2569 | 0 | 43.8514 | 0.4385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 18:00 | 3 | 29 | 18 | 88 | 2106 | 42.08 | 652.2648 | 61.8244 | 61.8244 | 590.4404 | Heating | 520.9768 | 8.5 | 520.9768 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 104.1954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 531.609 | 0 | 106.3218 | 1.063% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 19:00 | 3 | 29 | 19 | 88 | 2107 | 39.02 | 1203.6037 | 10.7606 | 10.7606 | 1192.843 | Heating | 1052.5086 | 8.5 | 1052.5086 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 210.5017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1073.9883 | 0 | 214.7977 | 2.148% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 20:00 | 3 | 29 | 20 | 88 | 2108 | 39.02 | 1726.7568 | 0.53507 | 0.53507 | 1726.2217 | Heating | 1523.1368 | 8.5 | 1523.1368 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 304.6274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1554.2212 | 0 | 310.8442 | 3.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 21:00 | 3 | 29 | 21 | 88 | 2109 | 33.98 | 2210.41 | 0 | 0 | 2210.41 | Heating | 1950.3618 | 8.5 | 1950.3618 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.0724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1990.1651 | 0 | 398.033 | 3.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 22:00 | 3 | 29 | 22 | 88 | 2110 | 33.98 | 610.1889 | 0 | 0 | 610.1889 | Heating | 538.402 | 8.5 | 538.402 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.6804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 549.3898 | 0 | 109.878 | 1.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-29 23:00 | 3 | 29 | 23 | 88 | 2111 | 33.98 | 670.2495 | 0 | 0 | 670.2495 | Heating | 591.3966 | 8.5 | 591.3966 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.2793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 603.4659 | 0 | 120.6932 | 1.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 | 3 | 30 | 0 | 89 | 2112 | 33.08 | 737.2743 | 0 | 0 | 737.2743 | Heating | 650.5362 | 8.5 | 650.5362 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.1072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 663.8124 | 0 | 132.7625 | 1.328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 01:00 | 3 | 30 | 1 | 89 | 2113 | 33.98 | 802.6648 | 0 | 0 | 802.6648 | Heating | 708.2337 | 8.5 | 708.2337 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.6467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 722.6874 | 0 | 144.5375 | 1.445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 02:00 | 3 | 30 | 2 | 89 | 2114 | 33.98 | 866.0999 | 0 | 0 | 866.0999 | Heating | 764.2058 | 8.5 | 764.2058 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.8412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 779.8018 | 0 | 155.9604 | 1.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 03:00 | 3 | 30 | 3 | 89 | 2115 | 32 | 947.5998 | 0 | 0 | 947.5998 | Heating | 836.1175 | 8.5 | 836.1175 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 167.2235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 853.1811 | 0 | 170.6362 | 1.706% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 04:00 | 3 | 30 | 4 | 89 | 2116 | 32 | 1058.9183 | 0 | 0 | 1058.9183 | Heating | 934.3397 | 8.5 | 934.3397 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 186.8679 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 953.4078 | 0 | 190.6816 | 1.907% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 05:00 | 3 | 30 | 5 | 89 | 2117 | 32 | 1129.6885 | 0 | 0 | 1129.6885 | Heating | 996.784 | 8.5 | 996.784 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.3568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1017.1265 | 0 | 203.4253 | 2.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 06:00 | 3 | 30 | 6 | 89 | 2118 | 30.92 | 1148.1837 | 0 | 0 | 1148.1837 | Heating | 1013.1033 | 8.5 | 1013.1033 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.6207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1033.7789 | 0 | 206.7558 | 2.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 07:00 | 3 | 30 | 7 | 89 | 2119 | 33.98 | 8776.1824 | 0 | 0 | 8776.1824 | Heating | 7743.6903 | 8.5 | 7743.6903 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1548.7381 | 30.97% | 1 | 61.95% | 0% | 0% | 0% | 27.0913 | 0 | 0 | 0 | 27.0913 | 7901.7248 | 0 | 1580.345 | 15.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.3659
2007-03-30 08:00 | 3 | 30 | 8 | 89 | 2120 | 33.98 | 6058.756 | 0 | 0 | 6058.756 | Heating | 5345.9612 | 8.5 | 5345.9612 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1069.1922 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5455.0624 | 0 | 1091.0125 | 10.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 09:00 | 3 | 30 | 9 | 89 | 2121 | 41 | 4413.9414 | 0 | 0 | 4413.9414 | Heating | 3894.6542 | 8.5 | 3894.6542 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 778.9308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3974.1369 | 0 | 794.8274 | 7.948% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 10:00 | 3 | 30 | 10 | 89 | 2122 | 44.06 | 2592.1644 | 0 | 0 | 2592.1644 | Heating | 2287.2039 | 8.5 | 2287.2039 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 457.4408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2333.8816 | 0 | 466.7763 | 4.668% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 11:00 | 3 | 30 | 11 | 89 | 2123 | 44.06 | 1173.857 | 0 | 0 | 1173.857 | Heating | 1035.7562 | 8.5 | 1035.7562 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.1512 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1056.8941 | 0 | 211.3788 | 2.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 12:00 | 3 | 30 | 12 | 89 | 2124 | 48.02 | 317.9375 | 23.2015 | 23.2015 | 294.736 | Heating | 260.0612 | 8.5 | 260.0612 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.0122 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 265.3686 | 0 | 53.0737 | 0.5307% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 13:00 | 3 | 30 | 13 | 89 | 2125 | 50 | 128.7654 | 67.3877 | 67.3877 | 61.3776 | Heating | 54.1567 | 8.5 | 54.1567 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.8313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 55.262 | 0 | 11.0524 | 0.1105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 14:00 | 3 | 30 | 14 | 89 | 2126 | 50 | 86.9699 | 91.3202 | 91.3202 | -4.3503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 111.6136 | 111.6136 | 0 | 8.5 | 0 | 18.6023 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 109.3813 | 21.8763 | 0.2188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 15:00 | 3 | 30 | 15 | 89 | 2127 | 53.06 | 78.012 | 52.4423 | 52.4423 | 25.5698 | Heating | 22.5616 | 8.5 | 22.5616 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.022 | 0 | 4.6044 | 0.04604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 16:00 | 3 | 30 | 16 | 89 | 2128 | 53.06 | 72.226 | 48.9358 | 48.9358 | 23.2902 | Heating | 20.5502 | 8.5 | 20.5502 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.11 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.9696 | 0 | 4.1939 | 0.04194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 17:00 | 3 | 30 | 17 | 89 | 2129 | 53.06 | 70.3402 | 44.0997 | 44.0997 | 26.2405 | Heating | 23.1534 | 8.5 | 23.1534 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.6259 | 0 | 4.7252 | 0.04725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 18:00 | 3 | 30 | 18 | 89 | 2130 | 50 | 67.8495 | 20.5403 | 20.5403 | 47.3092 | Heating | 41.7434 | 8.5 | 41.7434 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.3487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.5953 | 0 | 8.5191 | 0.08519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 19:00 | 3 | 30 | 19 | 89 | 2131 | 48.92 | 91.7599 | 0 | 0 | 91.7599 | Heating | 80.9646 | 8.5 | 80.9646 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.1929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 82.617 | 0 | 16.5234 | 0.1652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 20:00 | 3 | 30 | 20 | 89 | 2132 | 48.92 | 389.4251 | 0 | 0 | 389.4251 | Heating | 343.6104 | 8.5 | 343.6104 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.7221 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 350.6228 | 0 | 70.1246 | 0.7012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 21:00 | 3 | 30 | 21 | 89 | 2133 | 44.06 | 854.391 | 0 | 0 | 854.391 | Heating | 753.8744 | 8.5 | 753.8744 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.7749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 769.2596 | 0 | 153.8519 | 1.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 22:00 | 3 | 30 | 22 | 89 | 2134 | 42.98 | 1406.3847 | 0 | 0 | 1406.3847 | Heating | 1240.9277 | 8.5 | 1240.9277 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.1855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1266.2527 | 0 | 253.2505 | 2.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-30 23:00 | 3 | 30 | 23 | 89 | 2135 | 42.98 | 298.3762 | 0 | 0 | 298.3762 | Heating | 263.2731 | 8.5 | 263.2731 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.6546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 268.6461 | 0 | 53.7292 | 0.5373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 | 3 | 31 | 0 | 90 | 2136 | 41 | 388.5388 | 0 | 0 | 388.5388 | Heating | 342.8284 | 8.5 | 342.8284 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.5657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 349.8249 | 0 | 69.965 | 0.6996% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 01:00 | 3 | 31 | 1 | 90 | 2137 | 39.92 | 480.2326 | 0 | 0 | 480.2326 | Heating | 423.7346 | 8.5 | 423.7346 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.7469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 432.3823 | 0 | 86.4765 | 0.8648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 02:00 | 3 | 31 | 2 | 90 | 2138 | 39.92 | 542.8054 | 0 | 0 | 542.8054 | Heating | 478.9459 | 8.5 | 478.9459 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.7892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 488.7203 | 0 | 97.7441 | 0.9774% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 03:00 | 3 | 31 | 3 | 90 | 2139 | 39.02 | 590.0779 | 0 | 0 | 590.0779 | Heating | 520.657 | 8.5 | 520.657 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 104.1314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 531.2826 | 0 | 106.2565 | 1.063% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 04:00 | 3 | 31 | 4 | 90 | 2140 | 39.02 | 633.8342 | 0 | 0 | 633.8342 | Heating | 559.2654 | 8.5 | 559.2654 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.8531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 570.679 | 0 | 114.1358 | 1.141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 05:00 | 3 | 31 | 5 | 90 | 2141 | 39.02 | 656.3643 | 0 | 0 | 656.3643 | Heating | 579.145 | 8.5 | 579.145 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 590.9642 | 0 | 118.1928 | 1.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 06:00 | 3 | 31 | 6 | 90 | 2142 | 37.94 | 662.5148 | 0 | 0 | 662.5148 | Heating | 584.5719 | 8.5 | 584.5719 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.9144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 596.5019 | 0 | 119.3004 | 1.193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 07:00 | 3 | 31 | 7 | 90 | 2143 | 37.94 | 656.5908 | 0 | 0 | 656.5908 | Heating | 579.3448 | 8.5 | 579.3448 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 591.1682 | 0 | 118.2336 | 1.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 08:00 | 3 | 31 | 8 | 90 | 2144 | 37.94 | 630.5947 | 0 | 0 | 630.5947 | Heating | 556.4071 | 8.5 | 556.4071 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.2814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 567.7623 | 0 | 113.5525 | 1.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 09:00 | 3 | 31 | 9 | 90 | 2145 | 42.08 | 5659.1408 | 0 | 0 | 5659.1408 | Heating | 4993.3595 | 8.5 | 4993.3595 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 998.6719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5095.2648 | 0 | 1019.053 | 10.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 10:00 | 3 | 31 | 10 | 90 | 2146 | 44.96 | 3914.123 | 0 | 0 | 3914.123 | Heating | 3453.6379 | 8.5 | 3453.6379 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 690.7276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3524.1203 | 0 | 704.8241 | 7.048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 11:00 | 3 | 31 | 11 | 90 | 2147 | 44.96 | 2892.9679 | 0 | 0 | 2892.9679 | Heating | 2552.6187 | 8.5 | 2552.6187 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 510.5237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2604.713 | 0 | 520.9426 | 5.209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 12:00 | 3 | 31 | 12 | 90 | 2148 | 48.02 | 2091.146 | 0 | 0 | 2091.146 | Heating | 1845.1288 | 8.5 | 1845.1288 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.0258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1882.7845 | 0 | 376.5569 | 3.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 13:00 | 3 | 31 | 13 | 90 | 2149 | 48.92 | 1200.254 | 0 | 0 | 1200.254 | Heating | 1059.0477 | 8.5 | 1059.0477 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.8095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1080.6609 | 0 | 216.1322 | 2.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 14:00 | 3 | 31 | 14 | 90 | 2150 | 48.92 | 956.1315 | 0 | 0 | 956.1315 | Heating | 843.6454 | 8.5 | 843.6454 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.7291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 860.8627 | 0 | 172.1725 | 1.722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 15:00 | 3 | 31 | 15 | 90 | 2151 | 48.02 | 1025.1602 | 0 | 0 | 1025.1602 | Heating | 904.5531 | 8.5 | 904.5531 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 180.9106 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 923.0134 | 0 | 184.6027 | 1.846% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 16:00 | 3 | 31 | 16 | 90 | 2152 | 46.04 | 1118.6049 | 0 | 0 | 1118.6049 | Heating | 987.0043 | 8.5 | 987.0043 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 197.4009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1007.1473 | 0 | 201.4295 | 2.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 17:00 | 3 | 31 | 17 | 90 | 2153 | 46.04 | 1223.3106 | 0 | 0 | 1223.3106 | Heating | 1079.3917 | 8.5 | 1079.3917 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.8783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1101.4201 | 0 | 220.284 | 2.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 18:00 | 3 | 31 | 18 | 90 | 2154 | 44.06 | 2315.9774 | 0 | 0 | 2315.9774 | Heating | 2043.5094 | 8.5 | 2043.5094 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 408.7019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2085.2137 | 0 | 417.0427 | 4.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 19:00 | 3 | 31 | 19 | 90 | 2155 | 43.16 | 2773.2603 | 0 | 0 | 2773.2603 | Heating | 2446.9944 | 8.5 | 2446.9944 | 0 | 3.9517 | 0 | 0 | 0 | 0 | 8.5 | 0 | 489.3989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2496.9331 | 0 | 499.3866 | 4.994% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 20:00 | 3 | 31 | 20 | 90 | 2156 | 42.62 | 393.0292 | 0 | 0 | 393.0292 | Heating | 346.7905 | 8.5 | 346.7905 | 0 | 3.9134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 69.3581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 353.8679 | 0 | 70.7736 | 0.7077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 21:00 | 3 | 31 | 21 | 90 | 2157 | 41.54 | 413.461 | 0 | 0 | 413.461 | Heating | 364.8185 | 8.5 | 364.8185 | 0 | 3.8392 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.9637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 372.2638 | 0 | 74.4528 | 0.7445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 22:00 | 3 | 31 | 22 | 90 | 2158 | 38.48 | 464.0584 | 0 | 0 | 464.0584 | Heating | 409.4633 | 8.5 | 409.4633 | 0 | 3.6462 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.8927 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 417.8197 | 0 | 83.5639 | 0.8356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-03-31 23:00 | 3 | 31 | 23 | 90 | 2159 | 35.42 | 575.451 | 0 | 0 | 575.451 | Heating | 507.7509 | 8.5 | 507.7509 | 0 | 3.477 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.5502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 518.1132 | 0 | 103.6226 | 1.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 | 4 | 1 | 0 | 91 | 2160 | 33.08 | 721.3784 | 0 | 0 | 721.3784 | Heating | 636.5104 | 8.5 | 636.5104 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.3021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 649.5004 | 0 | 129.9001 | 1.299% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 01:00 | 4 | 1 | 1 | 91 | 2161 | 30.74 | 889.5648 | 0 | 0 | 889.5648 | Heating | 784.9101 | 8.5 | 784.9101 | 0 | 3.2596 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.982 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 800.9287 | 0 | 160.1857 | 1.602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 02:00 | 4 | 1 | 2 | 91 | 2162 | 30.92 | 1069.1522 | 0 | 0 | 1069.1522 | Heating | 943.3696 | 8.5 | 943.3696 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.6739 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 962.6221 | 0 | 192.5244 | 1.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 03:00 | 4 | 1 | 3 | 91 | 2163 | 30.92 | 1236.095 | 0 | 0 | 1236.095 | Heating | 1090.6721 | 8.5 | 1090.6721 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.1344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1112.9307 | 0 | 222.5861 | 2.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 04:00 | 4 | 1 | 4 | 91 | 2164 | 31.46 | 1411.963 | 0 | 0 | 1411.963 | Heating | 1245.8497 | 8.5 | 1245.8497 | 0 | 3.29 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.1699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1271.2753 | 0 | 254.2551 | 2.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 05:00 | 4 | 1 | 5 | 91 | 2165 | 32.18 | 1582.3884 | 0 | 0 | 1582.3884 | Heating | 1396.2251 | 8.5 | 1396.2251 | 0 | 3.3215 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1424.7195 | 0 | 284.9439 | 2.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 06:00 | 4 | 1 | 6 | 91 | 2166 | 34.16 | 1738.2037 | 0 | 0 | 1738.2037 | Heating | 1533.7091 | 8.5 | 1533.7091 | 0 | 3.4137 | 0 | 0 | 0 | 0 | 8.5 | 0 | 306.7418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1565.0093 | 0 | 313.0019 | 3.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 07:00 | 4 | 1 | 7 | 91 | 2167 | 33.98 | 10347.4273 | 0 | 0 | 10347.4273 | Heating | 9130.0829 | 8.5 | 9130.0829 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1826.0166 | 36.52% | 1 | 73.04% | 0% | 0% | 0% | 39.5678 | 0 | 0 | 0 | 39.5678 | 9316.4112 | 0 | 1863.2822 | 18.63% | 1 | 37.27% | 0% | 0% | 4.2085 | 0 | 0 | 4.2085 | 43.7763
2007-04-01 08:00 | 4 | 1 | 8 | 91 | 2168 | 33.98 | 6731.7947 | 0 | 0 | 6731.7947 | Heating | 5939.8189 | 8.5 | 5939.8189 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1187.9638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6061.0397 | 0 | 1212.2079 | 12.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 09:00 | 4 | 1 | 9 | 91 | 2169 | 39.02 | 4384.8011 | 0 | 0 | 4384.8011 | Heating | 3868.9421 | 8.5 | 3868.9421 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 773.7884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3947.9002 | 0 | 789.58 | 7.896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 10:00 | 4 | 1 | 10 | 91 | 2170 | 42.08 | 2634.1165 | 0 | 0 | 2634.1165 | Heating | 2324.2205 | 8.5 | 2324.2205 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 464.8441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2371.6535 | 0 | 474.3307 | 4.743% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 11:00 | 4 | 1 | 11 | 91 | 2171 | 42.08 | 1628.4777 | 0 | 0 | 1628.4777 | Heating | 1436.8921 | 8.5 | 1436.8921 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 287.3784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1466.2164 | 0 | 293.2433 | 2.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 12:00 | 4 | 1 | 12 | 91 | 2172 | 48.02 | 858.902 | 10.1444 | 10.1444 | 848.7576 | Heating | 748.9037 | 8.5 | 748.9037 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.7807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 764.1875 | 0 | 152.8375 | 1.528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 13:00 | 4 | 1 | 13 | 91 | 2173 | 50 | 485.7437 | 37.2792 | 37.2792 | 448.4645 | Heating | 395.704 | 8.5 | 395.704 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.1408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 403.7796 | 0 | 80.7559 | 0.8076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 14:00 | 4 | 1 | 14 | 91 | 2174 | 50 | 327.4361 | 117.3149 | 117.3149 | 210.1212 | Heating | 185.4011 | 8.5 | 185.4011 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 37.0802 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 189.1848 | 0 | 37.837 | 0.3784% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 15:00 | 4 | 1 | 15 | 91 | 2175 | 51.08 | 230.7803 | 178.9575 | 178.9575 | 51.8227 | Heating | 45.7259 | 8.5 | 45.7259 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.1452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 46.6591 | 0 | 9.3318 | 0.09332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 16:00 | 4 | 1 | 16 | 91 | 2176 | 50 | 215.7945 | 165.5933 | 165.5933 | 50.2012 | Heating | 44.2952 | 8.5 | 44.2952 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 45.1992 | 0 | 9.0398 | 0.0904% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 17:00 | 4 | 1 | 17 | 91 | 2177 | 50 | 245.2691 | 128.9372 | 128.9372 | 116.332 | Heating | 102.6459 | 8.5 | 102.6459 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.5292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 104.7407 | 0 | 20.9481 | 0.2095% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 18:00 | 4 | 1 | 18 | 91 | 2178 | 48.02 | 379.3842 | 78.2016 | 78.2016 | 301.1826 | Heating | 265.7493 | 8.5 | 265.7493 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.1499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 271.1728 | 0 | 54.2346 | 0.5423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 19:00 | 4 | 1 | 19 | 91 | 2179 | 46.04 | 1503.9893 | 7.3361 | 7.3361 | 1496.6532 | Heating | 1320.5763 | 8.5 | 1320.5763 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.1153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1347.5269 | 0 | 269.5054 | 2.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 20:00 | 4 | 1 | 20 | 91 | 2180 | 46.04 | 2684.968 | 0 | 0 | 2684.968 | Heating | 2369.0894 | 8.5 | 2369.0894 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 473.8179 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2417.4382 | 0 | 483.4876 | 4.835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 21:00 | 4 | 1 | 21 | 91 | 2181 | 39.02 | 3330.183 | 0 | 0 | 3330.183 | Heating | 2938.3968 | 8.5 | 2938.3968 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 587.6794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2998.3641 | 0 | 599.6728 | 5.997% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 22:00 | 4 | 1 | 22 | 91 | 2182 | 37.94 | 928.9518 | 0 | 0 | 928.9518 | Heating | 819.6633 | 8.5 | 819.6633 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.9327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 836.3911 | 0 | 167.2782 | 1.673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-01 23:00 | 4 | 1 | 23 | 91 | 2183 | 37.94 | 901.1142 | 0 | 0 | 901.1142 | Heating | 795.1007 | 8.5 | 795.1007 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 159.0201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 811.3273 | 0 | 162.2655 | 1.623% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 | 4 | 2 | 0 | 92 | 2184 | 33.08 | 1009.003 | 0 | 0 | 1009.003 | Heating | 890.2968 | 8.5 | 890.2968 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 178.0594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 908.4661 | 0 | 181.6932 | 1.817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 01:00 | 4 | 2 | 1 | 92 | 2185 | 30.92 | 1141.882 | 0 | 0 | 1141.882 | Heating | 1007.543 | 8.5 | 1007.543 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 201.5086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1028.1051 | 0 | 205.621 | 2.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 02:00 | 4 | 2 | 2 | 92 | 2186 | 30.92 | 1350.4244 | 0 | 0 | 1350.4244 | Heating | 1191.5509 | 8.5 | 1191.5509 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.3102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1215.8683 | 0 | 243.1737 | 2.432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 03:00 | 4 | 2 | 3 | 92 | 2187 | 30.92 | 1541.6811 | 0 | 0 | 1541.6811 | Heating | 1360.3068 | 8.5 | 1360.3068 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.0614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1388.0682 | 0 | 277.6136 | 2.776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 04:00 | 4 | 2 | 4 | 92 | 2188 | 30.92 | 1639.3552 | 0 | 0 | 1639.3552 | Heating | 1446.4899 | 8.5 | 1446.4899 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 289.298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1476.0101 | 0 | 295.202 | 2.952% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 05:00 | 4 | 2 | 5 | 92 | 2189 | 30.92 | 1615.665 | 0 | 0 | 1615.665 | Heating | 1425.5868 | 8.5 | 1425.5868 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 285.1174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1454.6804 | 0 | 290.9361 | 2.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 06:00 | 4 | 2 | 6 | 92 | 2190 | 39.02 | 9687.8874 | 0 | 0 | 9687.8874 | Heating | 8548.1359 | 8.5 | 8548.1359 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1709.6272 | 34.19% | 1 | 68.39% | 0% | 0% | 0% | 34.0059 | 0 | 0 | 0 | 34.0059 | 8722.5877 | 0 | 1744.5175 | 17.45% | 1 | 34.89% | 0% | 0% | 3.6169 | 0 | 0 | 3.6169 | 37.6228
2007-04-02 07:00 | 4 | 2 | 7 | 92 | 2191 | 39.92 | 7905.0303 | 0 | 0 | 7905.0303 | Heating | 6975.0267 | 8.5 | 6975.0267 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1395.0053 | 30% | 1 | 55.8% | 0% | 0% | 0% | 21.3013 | 0 | 0 | 0 | 21.3013 | 7117.3742 | 0 | 1423.4748 | 14.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.5758
2007-04-02 08:00 | 4 | 2 | 8 | 92 | 2192 | 39.92 | 6539.1123 | 0 | 0 | 6539.1123 | Heating | 5769.805 | 8.5 | 5769.805 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1153.961 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5887.5561 | 0 | 1177.5112 | 11.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 09:00 | 4 | 2 | 9 | 92 | 2193 | 42.08 | 4918.4493 | 0 | 0 | 4918.4493 | Heating | 4339.8082 | 8.5 | 4339.8082 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 867.9616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4428.3757 | 0 | 885.6751 | 8.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 10:00 | 4 | 2 | 10 | 92 | 2194 | 46.94 | 3614.5036 | 0 | 0 | 3614.5036 | Heating | 3189.2679 | 8.5 | 3189.2679 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 637.8536 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3254.355 | 0 | 650.871 | 6.509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 11:00 | 4 | 2 | 11 | 92 | 2195 | 46.94 | 2501.2957 | 0 | 0 | 2501.2957 | Heating | 2207.0256 | 8.5 | 2207.0256 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 441.4051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2252.0669 | 0 | 450.4134 | 4.504% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 12:00 | 4 | 2 | 12 | 92 | 2196 | 50 | 1614.3485 | 0 | 0 | 1614.3485 | Heating | 1424.4252 | 8.5 | 1424.4252 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 284.885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1453.4951 | 0 | 290.699 | 2.907% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 13:00 | 4 | 2 | 13 | 92 | 2197 | 53.06 | 1022.7288 | 0 | 0 | 1022.7288 | Heating | 902.4078 | 8.5 | 902.4078 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 180.4816 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 920.8243 | 0 | 184.1649 | 1.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 14:00 | 4 | 2 | 14 | 92 | 2198 | 53.06 | 654.0519 | 0 | 0 | 654.0519 | Heating | 577.1046 | 8.5 | 577.1046 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.4209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 588.8822 | 0 | 117.7764 | 1.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 15:00 | 4 | 2 | 15 | 92 | 2199 | 59 | 418.2408 | 0 | 0 | 418.2408 | Heating | 369.036 | 8.5 | 369.036 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.8072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 376.5673 | 0 | 75.3135 | 0.7531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 16:00 | 4 | 2 | 16 | 92 | 2200 | 59 | 346.5074 | 0 | 0 | 346.5074 | Heating | 305.7418 | 8.5 | 305.7418 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.1484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 311.9814 | 0 | 62.3963 | 0.624% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 17:00 | 4 | 2 | 17 | 92 | 2201 | 59 | 354.1241 | 0 | 0 | 354.1241 | Heating | 312.4624 | 8.5 | 312.4624 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.4925 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 318.8392 | 0 | 63.7678 | 0.6377% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 18:00 | 4 | 2 | 18 | 92 | 2202 | 53.06 | 827.1635 | 0 | 0 | 827.1635 | Heating | 729.8501 | 8.5 | 729.8501 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.97 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 744.745 | 0 | 148.949 | 1.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 19:00 | 4 | 2 | 19 | 92 | 2203 | 48.92 | 1361.4243 | 0 | 0 | 1361.4243 | Heating | 1201.2567 | 8.5 | 1201.2567 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 240.2513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1225.7722 | 0 | 245.1544 | 2.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 20:00 | 4 | 2 | 20 | 92 | 2204 | 48.92 | 1866.776 | 0 | 0 | 1866.776 | Heating | 1647.1553 | 8.5 | 1647.1553 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.4311 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1680.7707 | 0 | 336.1541 | 3.362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 21:00 | 4 | 2 | 21 | 92 | 2205 | 44.06 | 619.1237 | 0 | 0 | 619.1237 | Heating | 546.2856 | 8.5 | 546.2856 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.2571 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 557.4343 | 0 | 111.4869 | 1.115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 22:00 | 4 | 2 | 22 | 92 | 2206 | 41 | 808.8199 | 0 | 0 | 808.8199 | Heating | 713.6646 | 8.5 | 713.6646 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 142.7329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 728.2292 | 0 | 145.6458 | 1.456% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-02 23:00 | 4 | 2 | 23 | 92 | 2207 | 41 | 897.3762 | 0 | 0 | 897.3762 | Heating | 791.8026 | 8.5 | 791.8026 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.3605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 807.9618 | 0 | 161.5924 | 1.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 | 4 | 3 | 0 | 93 | 2208 | 39.92 | 946.9521 | 0 | 0 | 946.9521 | Heating | 835.5459 | 8.5 | 835.5459 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 167.1092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 852.5979 | 0 | 170.5196 | 1.705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 01:00 | 4 | 3 | 1 | 93 | 2209 | 37.94 | 991.7454 | 0 | 0 | 991.7454 | Heating | 875.0695 | 8.5 | 875.0695 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.0139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 892.928 | 0 | 178.5856 | 1.786% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 02:00 | 4 | 3 | 2 | 93 | 2210 | 37.94 | 1009.1745 | 0 | 0 | 1009.1745 | Heating | 890.4481 | 8.5 | 890.4481 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 178.0896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 908.6205 | 0 | 181.7241 | 1.817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 03:00 | 4 | 3 | 3 | 93 | 2211 | 35.96 | 996.514 | 0 | 0 | 996.514 | Heating | 879.277 | 8.5 | 879.277 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.8554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 897.2215 | 0 | 179.4443 | 1.794% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 04:00 | 4 | 3 | 4 | 93 | 2212 | 35.06 | 959.2745 | 0 | 0 | 959.2745 | Heating | 846.4186 | 8.5 | 846.4186 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.2837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 863.6925 | 0 | 172.7385 | 1.727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 05:00 | 4 | 3 | 5 | 93 | 2213 | 35.06 | 890.8472 | 0 | 0 | 890.8472 | Heating | 786.0417 | 8.5 | 786.0417 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.2083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 802.0834 | 0 | 160.4167 | 1.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 06:00 | 4 | 3 | 6 | 93 | 2214 | 32 | 6701.0412 | 0 | 0 | 6701.0412 | Heating | 5912.6834 | 8.5 | 5912.6834 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1182.5367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6033.3504 | 0 | 1206.6701 | 12.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 07:00 | 4 | 3 | 7 | 93 | 2215 | 35.06 | 5004.9232 | 0 | 0 | 5004.9232 | Heating | 4416.1087 | 8.5 | 4416.1087 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 883.2217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4506.2334 | 0 | 901.2467 | 9.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 08:00 | 4 | 3 | 8 | 93 | 2216 | 35.06 | 3688.6261 | 0 | 0 | 3688.6261 | Heating | 3254.6701 | 8.5 | 3254.6701 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 650.934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3321.0919 | 0 | 664.2184 | 6.642% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 09:00 | 4 | 3 | 9 | 93 | 2217 | 39.92 | 2452.0914 | 0 | 0 | 2452.0914 | Heating | 2163.6101 | 8.5 | 2163.6101 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 432.722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2207.7654 | 0 | 441.5531 | 4.416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 10:00 | 4 | 3 | 10 | 93 | 2218 | 42.98 | 1767.2281 | 0 | 0 | 1767.2281 | Heating | 1559.3189 | 8.5 | 1559.3189 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.8638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1591.1418 | 0 | 318.2284 | 3.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 11:00 | 4 | 3 | 11 | 93 | 2219 | 42.98 | 1170.1562 | 0 | 0 | 1170.1562 | Heating | 1032.4907 | 8.5 | 1032.4907 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.4981 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1053.562 | 0 | 210.7124 | 2.107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 12:00 | 4 | 3 | 12 | 93 | 2220 | 46.04 | 799.2194 | 0 | 0 | 799.2194 | Heating | 705.1936 | 8.5 | 705.1936 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.0387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 719.5853 | 0 | 143.9171 | 1.439% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 13:00 | 4 | 3 | 13 | 93 | 2221 | 48.02 | 354.7054 | 0 | 0 | 354.7054 | Heating | 312.9753 | 8.5 | 312.9753 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.5951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 319.3626 | 0 | 63.8725 | 0.6387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 14:00 | 4 | 3 | 14 | 93 | 2222 | 48.02 | 253.6926 | 0 | 0 | 253.6926 | Heating | 223.8464 | 8.5 | 223.8464 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.7693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 228.4147 | 0 | 45.6829 | 0.4568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 15:00 | 4 | 3 | 15 | 93 | 2223 | 51.98 | 346.5702 | 0 | 0 | 346.5702 | Heating | 305.7972 | 8.5 | 305.7972 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.1594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 312.038 | 0 | 62.4076 | 0.6241% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 16:00 | 4 | 3 | 16 | 93 | 2224 | 50 | 1049.1055 | 0 | 0 | 1049.1055 | Heating | 925.6814 | 8.5 | 925.6814 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 185.1363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 944.5728 | 0 | 188.9146 | 1.889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 17:00 | 4 | 3 | 17 | 93 | 2225 | 50 | 1765.3944 | 0 | 0 | 1765.3944 | Heating | 1557.701 | 8.5 | 1557.701 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.5402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1589.4908 | 0 | 317.8982 | 3.179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 18:00 | 4 | 3 | 18 | 93 | 2226 | 48.02 | 2389.8034 | 0 | 0 | 2389.8034 | Heating | 2108.65 | 8.5 | 2108.65 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.73 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2151.6837 | 0 | 430.3367 | 4.303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 19:00 | 4 | 3 | 19 | 93 | 2227 | 44.96 | 2646.5831 | 0 | 0 | 2646.5831 | Heating | 2335.2204 | 8.5 | 2335.2204 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.0441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2382.8779 | 0 | 476.5756 | 4.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 20:00 | 4 | 3 | 20 | 93 | 2228 | 44.96 | 3081.2306 | 0 | 0 | 3081.2306 | Heating | 2718.7329 | 8.5 | 2718.7329 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 543.7466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2774.2172 | 0 | 554.8434 | 5.548% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 21:00 | 4 | 3 | 21 | 93 | 2229 | 41 | 882.945 | 0 | 0 | 882.945 | Heating | 779.0691 | 8.5 | 779.0691 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.8138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 794.9685 | 0 | 158.9937 | 1.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 22:00 | 4 | 3 | 22 | 93 | 2230 | 37.94 | 820.3468 | 0 | 0 | 820.3468 | Heating | 723.8354 | 8.5 | 723.8354 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 144.7671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 738.6075 | 0 | 147.7215 | 1.477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-03 23:00 | 4 | 3 | 23 | 93 | 2231 | 37.94 | 924.1412 | 0 | 0 | 924.1412 | Heating | 815.4187 | 8.5 | 815.4187 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.0837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 832.0599 | 0 | 166.412 | 1.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 | 4 | 4 | 0 | 94 | 2232 | 37.04 | 1106.8104 | 0 | 0 | 1106.8104 | Heating | 976.5974 | 8.5 | 976.5974 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.3195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 996.5279 | 0 | 199.3056 | 1.993% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 01:00 | 4 | 4 | 1 | 94 | 2233 | 35.96 | 1192.2984 | 0 | 0 | 1192.2984 | Heating | 1052.028 | 8.5 | 1052.028 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 210.4056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1073.498 | 0 | 214.6996 | 2.147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 02:00 | 4 | 4 | 2 | 94 | 2234 | 35.96 | 1250.58 | 0 | 0 | 1250.58 | Heating | 1103.4529 | 8.5 | 1103.4529 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 220.6906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1125.9724 | 0 | 225.1945 | 2.252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 03:00 | 4 | 4 | 3 | 94 | 2235 | 35.06 | 1266.0794 | 0 | 0 | 1266.0794 | Heating | 1117.1289 | 8.5 | 1117.1289 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.4258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1139.9274 | 0 | 227.9855 | 2.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 04:00 | 4 | 4 | 4 | 94 | 2236 | 35.06 | 1277.1235 | 0 | 0 | 1277.1235 | Heating | 1126.8737 | 8.5 | 1126.8737 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.3747 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1149.8711 | 0 | 229.9742 | 2.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 05:00 | 4 | 4 | 5 | 94 | 2237 | 35.06 | 1289.0331 | 0 | 0 | 1289.0331 | Heating | 1137.3822 | 8.5 | 1137.3822 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 227.4764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1160.5941 | 0 | 232.1188 | 2.321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 06:00 | 4 | 4 | 6 | 94 | 2238 | 33.98 | 8865.2316 | 0 | 0 | 8865.2316 | Heating | 7822.2632 | 8.5 | 7822.2632 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1564.4526 | 31.29% | 1 | 62.58% | 0% | 0% | 0% | 27.7277 | 0 | 0 | 0 | 27.7277 | 7981.9012 | 0 | 1596.3802 | 15.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.0023
2007-04-04 07:00 | 4 | 4 | 7 | 94 | 2239 | 35.96 | 7165.8865 | 0 | 0 | 7165.8865 | Heating | 6322.8411 | 8.5 | 6322.8411 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1264.5682 | 30% | 1 | 50.58% | 0% | 0% | 0% | 16.9961 | 0 | 0 | 0 | 16.9961 | 6451.8786 | 0 | 1290.3757 | 12.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2706
2007-04-04 08:00 | 4 | 4 | 8 | 94 | 2240 | 35.96 | 5648.466 | 0 | 0 | 5648.466 | Heating | 4983.9406 | 8.5 | 4983.9406 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 996.7881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5085.6537 | 0 | 1017.1307 | 10.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 09:00 | 4 | 4 | 9 | 94 | 2241 | 44.06 | 4367.9553 | 0 | 0 | 4367.9553 | Heating | 3854.0782 | 8.5 | 3854.0782 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 770.8156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3932.7328 | 0 | 786.5466 | 7.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 10:00 | 4 | 4 | 10 | 94 | 2242 | 48.02 | 3668.9366 | 0 | 0 | 3668.9366 | Heating | 3237.297 | 8.5 | 3237.297 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 647.4594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3303.3643 | 0 | 660.6729 | 6.607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 11:00 | 4 | 4 | 11 | 94 | 2243 | 48.02 | 2850.8432 | 0 | 0 | 2850.8432 | Heating | 2515.4499 | 8.5 | 2515.4499 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 503.09 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2566.7856 | 0 | 513.3571 | 5.134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 12:00 | 4 | 4 | 12 | 94 | 2244 | 48.92 | 2183.8607 | 0 | 0 | 2183.8607 | Heating | 1926.936 | 8.5 | 1926.936 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.3872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1966.2612 | 0 | 393.2522 | 3.933% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 13:00 | 4 | 4 | 13 | 94 | 2245 | 50 | 1731.6372 | 10.5537 | 10.5537 | 1721.0835 | Heating | 1518.6031 | 8.5 | 1518.6031 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 303.7206 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1549.595 | 0 | 309.919 | 3.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 14:00 | 4 | 4 | 14 | 94 | 2246 | 50 | 1338.9816 | 38.297 | 38.297 | 1300.6846 | Heating | 1147.6629 | 8.5 | 1147.6629 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.5326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1171.0846 | 0 | 234.2169 | 2.342% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 15:00 | 4 | 4 | 15 | 94 | 2247 | 48.92 | 882.925 | 83.6862 | 83.6862 | 799.2388 | Heating | 705.2107 | 8.5 | 705.2107 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.0421 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 719.6028 | 0 | 143.9206 | 1.439% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 16:00 | 4 | 4 | 16 | 94 | 2248 | 48.02 | 767.143 | 85.5265 | 85.5265 | 681.6165 | Heating | 601.4263 | 8.5 | 601.4263 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.2853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 613.7003 | 0 | 122.7401 | 1.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 17:00 | 4 | 4 | 17 | 94 | 2249 | 48.02 | 807.7763 | 85.0435 | 85.0435 | 722.7328 | Heating | 637.7054 | 8.5 | 637.7054 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.5411 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 650.7198 | 0 | 130.144 | 1.301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 18:00 | 4 | 4 | 18 | 94 | 2250 | 44.06 | 1221.5224 | 46.3372 | 46.3372 | 1175.1853 | Heating | 1036.9282 | 8.5 | 1036.9282 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.3856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1058.09 | 0 | 211.618 | 2.116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 19:00 | 4 | 4 | 19 | 94 | 2251 | 41 | 1822.9701 | 6.5213 | 6.5213 | 1816.4488 | Heating | 1602.7489 | 8.5 | 1602.7489 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.5498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1635.4581 | 0 | 327.0916 | 3.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 20:00 | 4 | 4 | 20 | 94 | 2252 | 41 | 2519.7852 | 0 | 0 | 2519.7852 | Heating | 2223.3399 | 8.5 | 2223.3399 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 444.668 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2268.7142 | 0 | 453.7428 | 4.537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 21:00 | 4 | 4 | 21 | 94 | 2253 | 37.94 | 715.5001 | 0 | 0 | 715.5001 | Heating | 631.3237 | 8.5 | 631.3237 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.2647 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 644.2078 | 0 | 128.8416 | 1.288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 22:00 | 4 | 4 | 22 | 94 | 2254 | 37.94 | 738.3318 | 0 | 0 | 738.3318 | Heating | 651.4693 | 8.5 | 651.4693 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.2939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 664.7646 | 0 | 132.9529 | 1.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-04 23:00 | 4 | 4 | 23 | 94 | 2255 | 37.94 | 847.8991 | 0 | 0 | 847.8991 | Heating | 748.1463 | 8.5 | 748.1463 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.6293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 763.4146 | 0 | 152.6829 | 1.527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 | 4 | 5 | 0 | 95 | 2256 | 37.04 | 980.5029 | 0 | 0 | 980.5029 | Heating | 865.1496 | 8.5 | 865.1496 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 173.0299 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 882.8057 | 0 | 176.5611 | 1.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 01:00 | 4 | 5 | 1 | 95 | 2257 | 37.4 | 1140.5245 | 0 | 0 | 1140.5245 | Heating | 1006.3451 | 8.5 | 1006.3451 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 201.269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1026.8828 | 0 | 205.3766 | 2.054% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 02:00 | 4 | 5 | 2 | 95 | 2258 | 37.04 | 1300.6617 | 0 | 0 | 1300.6617 | Heating | 1147.6427 | 8.5 | 1147.6427 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.5285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1171.0639 | 0 | 234.2128 | 2.342% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 03:00 | 4 | 5 | 3 | 95 | 2259 | 37.94 | 1390.2206 | 0 | 0 | 1390.2206 | Heating | 1226.6653 | 8.5 | 1226.6653 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.3331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1251.6992 | 0 | 250.3398 | 2.503% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 04:00 | 4 | 5 | 4 | 95 | 2260 | 37.94 | 1486.0883 | 0 | 0 | 1486.0883 | Heating | 1311.2544 | 8.5 | 1311.2544 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 262.2509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1338.0147 | 0 | 267.6029 | 2.676% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 05:00 | 4 | 5 | 5 | 95 | 2261 | 37.94 | 1656.4006 | 0 | 0 | 1656.4006 | Heating | 1461.53 | 8.5 | 1461.53 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1491.3571 | 0 | 298.2714 | 2.983% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 06:00 | 4 | 5 | 6 | 95 | 2262 | 37.94 | 10595.056 | 0 | 0 | 10595.056 | Heating | 9348.5788 | 8.5 | 9348.5788 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1869.7158 | 37.39% | 1 | 74.79% | 0% | 0% | 0% | 41.7797 | 0 | 0 | 0 | 41.7797 | 9539.3661 | 0 | 1907.8732 | 19.08% | 1 | 38.16% | 0% | 0% | 4.4437 | 0 | 0 | 4.4437 | 46.2234
2007-04-05 07:00 | 4 | 5 | 7 | 95 | 2263 | 37.94 | 8158.734 | 0 | 0 | 8158.734 | Heating | 7198.8829 | 8.5 | 7198.8829 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1439.7766 | 30% | 1 | 57.59% | 0% | 0% | 0% | 22.9066 | 0 | 0 | 0 | 22.9066 | 7345.7989 | 0 | 1469.1598 | 14.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.1811
2007-04-05 08:00 | 4 | 5 | 8 | 95 | 2264 | 39.02 | 5701.3267 | 0 | 0 | 5701.3267 | Heating | 5030.5824 | 8.5 | 5030.5824 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1006.1165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5133.2473 | 0 | 1026.6495 | 10.27% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 09:00 | 4 | 5 | 9 | 95 | 2265 | 44.06 | 3521.3478 | 0 | 0 | 3521.3478 | Heating | 3107.0716 | 8.5 | 3107.0716 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 621.4143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3170.4812 | 0 | 634.0962 | 6.341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 10:00 | 4 | 5 | 10 | 95 | 2266 | 46.04 | 2389.6768 | 0 | 0 | 2389.6768 | Heating | 2108.5383 | 8.5 | 2108.5383 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.7077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2151.5697 | 0 | 430.3139 | 4.303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 11:00 | 4 | 5 | 11 | 95 | 2267 | 46.04 | 1355.9113 | 0 | 0 | 1355.9113 | Heating | 1196.3923 | 8.5 | 1196.3923 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 239.2785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1220.8085 | 0 | 244.1617 | 2.442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 12:00 | 4 | 5 | 12 | 95 | 2268 | 44.96 | 803.3397 | 6.7758 | 6.7758 | 796.5639 | Heating | 702.8505 | 8.5 | 702.8505 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 140.5701 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 717.1944 | 0 | 143.4389 | 1.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 13:00 | 4 | 5 | 13 | 95 | 2269 | 44.96 | 414.8851 | 50.441 | 50.441 | 364.444 | Heating | 321.5683 | 8.5 | 321.5683 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.3137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 328.1309 | 0 | 65.6262 | 0.6563% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 14:00 | 4 | 5 | 14 | 95 | 2270 | 44.96 | 215.9214 | 132.4138 | 132.4138 | 83.5075 | Heating | 73.6831 | 8.5 | 73.6831 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.7366 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 75.1869 | 0 | 15.0374 | 0.1504% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 15:00 | 4 | 5 | 15 | 95 | 2271 | 42.08 | 102.3612 | 280.5819 | 280.5819 | -178.2207 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 342.9335 | 342.9335 | 0 | 8.5 | 0 | 57.1556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 336.0748 | 67.215 | 0.6721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 16:00 | 4 | 5 | 16 | 95 | 2272 | 42.08 | 47.7787 | 275.4571 | 275.4571 | -227.6784 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 336.6698 | 336.6698 | 0 | 8.5 | 0 | 56.1116 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 329.9364 | 65.9873 | 0.6599% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 17:00 | 4 | 5 | 17 | 95 | 2273 | 42.08 | 29.6229 | 188.5553 | 188.5553 | -158.9324 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 230.4565 | 230.4565 | 0 | 8.5 | 0 | 38.4094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 225.8474 | 45.1695 | 0.4517% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 18:00 | 4 | 5 | 18 | 95 | 2274 | 39.02 | 24.1304 | 108.9245 | 108.9245 | -84.794 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 133.1299 | 133.1299 | 0 | 8.5 | 0 | 22.1883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 130.4673 | 26.0935 | 0.2609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 19:00 | 4 | 5 | 19 | 95 | 2275 | 37.04 | 47.3327 | 87.0362 | 87.0362 | -39.7035 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 106.3776 | 106.3776 | 0 | 8.5 | 0 | 17.7296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 104.2501 | 20.85 | 0.2085% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 20:00 | 4 | 5 | 20 | 95 | 2276 | 37.04 | 105.3501 | 24.9441 | 24.9441 | 80.406 | Heating | 70.9465 | 8.5 | 70.9465 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.1893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 72.3944 | 0 | 14.4789 | 0.1448% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 21:00 | 4 | 5 | 21 | 95 | 2277 | 37.04 | 125.9439 | 9.7962 | 9.7962 | 116.1477 | Heating | 102.4833 | 8.5 | 102.4833 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.4967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 104.5747 | 0 | 20.9149 | 0.2091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 22:00 | 4 | 5 | 22 | 95 | 2278 | 37.04 | 187.8664 | 0 | 0 | 187.8664 | Heating | 165.7645 | 8.5 | 165.7645 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.1529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 169.1474 | 0 | 33.8295 | 0.3383% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-05 23:00 | 4 | 5 | 23 | 95 | 2279 | 37.04 | 284.9584 | 0 | 0 | 284.9584 | Heating | 251.4339 | 8.5 | 251.4339 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.2868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 256.5652 | 0 | 51.313 | 0.5131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 | 4 | 6 | 0 | 96 | 2280 | 37.04 | 351.2847 | 0 | 0 | 351.2847 | Heating | 309.9571 | 8.5 | 309.9571 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.9914 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 316.2827 | 0 | 63.2565 | 0.6326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 01:00 | 4 | 6 | 1 | 96 | 2281 | 35.96 | 386.5276 | 0 | 0 | 386.5276 | Heating | 341.0537 | 8.5 | 341.0537 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.2107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 348.014 | 0 | 69.6028 | 0.696% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 02:00 | 4 | 6 | 2 | 96 | 2282 | 35.96 | 413.3624 | 0 | 0 | 413.3624 | Heating | 364.7315 | 8.5 | 364.7315 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.9463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 372.175 | 0 | 74.435 | 0.7443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 03:00 | 4 | 6 | 3 | 96 | 2283 | 33.98 | 441.9258 | 0 | 0 | 441.9258 | Heating | 389.9346 | 8.5 | 389.9346 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.9869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 397.8924 | 0 | 79.5785 | 0.7958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 04:00 | 4 | 6 | 4 | 96 | 2284 | 33.98 | 461.0831 | 0 | 0 | 461.0831 | Heating | 406.838 | 8.5 | 406.838 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.3676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 415.1408 | 0 | 83.0282 | 0.8303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 05:00 | 4 | 6 | 5 | 96 | 2285 | 33.98 | 471.574 | 0 | 0 | 471.574 | Heating | 416.0947 | 8.5 | 416.0947 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.2189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 424.5865 | 0 | 84.9173 | 0.8492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 06:00 | 4 | 6 | 6 | 96 | 2286 | 28.94 | 4883.1354 | 14.226 | 14.226 | 4868.9093 | Heating | 4296.0965 | 8.5 | 4296.0965 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 859.2193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4383.7719 | 0 | 876.7544 | 8.768% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 07:00 | 4 | 6 | 7 | 96 | 2287 | 33.98 | 3548.208 | 0 | 0 | 3548.208 | Heating | 3130.7718 | 8.5 | 3130.7718 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 626.1544 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3194.6651 | 0 | 638.933 | 6.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 08:00 | 4 | 6 | 8 | 96 | 2288 | 33.98 | 2967.8725 | 0 | 0 | 2967.8725 | Heating | 2618.711 | 8.5 | 2618.711 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.7422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2672.1541 | 0 | 534.4308 | 5.344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 09:00 | 4 | 6 | 9 | 96 | 2289 | 37.94 | 2319.6872 | 0 | 0 | 2319.6872 | Heating | 2046.7828 | 8.5 | 2046.7828 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.3566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2088.5539 | 0 | 417.7108 | 4.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 10:00 | 4 | 6 | 10 | 96 | 2290 | 41 | 1887.7422 | 0 | 0 | 1887.7422 | Heating | 1665.6549 | 8.5 | 1665.6549 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 333.131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1699.6479 | 0 | 339.9296 | 3.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 11:00 | 4 | 6 | 11 | 96 | 2291 | 41 | 1603.3701 | 0 | 0 | 1603.3701 | Heating | 1414.7383 | 8.5 | 1414.7383 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 282.9477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1443.6105 | 0 | 288.7221 | 2.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 12:00 | 4 | 6 | 12 | 96 | 2292 | 46.94 | 1478.5327 | 0 | 0 | 1478.5327 | Heating | 1304.5877 | 8.5 | 1304.5877 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 260.9175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1331.212 | 0 | 266.2424 | 2.662% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 13:00 | 4 | 6 | 13 | 96 | 2293 | 50 | 1531.0876 | 0 | 0 | 1531.0876 | Heating | 1350.9597 | 8.5 | 1350.9597 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 270.1919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1378.5303 | 0 | 275.7061 | 2.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 14:00 | 4 | 6 | 14 | 96 | 2294 | 50 | 1757.4292 | 0 | 0 | 1757.4292 | Heating | 1550.6728 | 8.5 | 1550.6728 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 310.1346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1582.3192 | 0 | 316.4638 | 3.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 15:00 | 4 | 6 | 15 | 96 | 2295 | 53.96 | 1839.106 | 0 | 0 | 1839.106 | Heating | 1622.7406 | 8.5 | 1622.7406 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.5481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1655.8577 | 0 | 331.1715 | 3.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 16:00 | 4 | 6 | 16 | 96 | 2296 | 55.04 | 2010.7903 | 0 | 0 | 2010.7903 | Heating | 1774.2267 | 8.5 | 1774.2267 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 354.8453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1810.4354 | 0 | 362.0871 | 3.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 17:00 | 4 | 6 | 17 | 96 | 2297 | 55.04 | 2240.2584 | 0 | 0 | 2240.2584 | Heating | 1976.6985 | 8.5 | 1976.6985 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 395.3397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2017.0393 | 0 | 403.4079 | 4.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 18:00 | 4 | 6 | 18 | 96 | 2298 | 51.08 | 2797.0262 | 0 | 0 | 2797.0262 | Heating | 2467.9643 | 8.5 | 2467.9643 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 493.5929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2518.3309 | 0 | 503.6662 | 5.037% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 19:00 | 4 | 6 | 19 | 96 | 2299 | 46.94 | 3272.1191 | 0 | 0 | 3272.1191 | Heating | 2887.1639 | 8.5 | 2887.1639 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 577.4328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2946.0856 | 0 | 589.2171 | 5.892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 20:00 | 4 | 6 | 20 | 96 | 2300 | 46.94 | 3493.4376 | 0 | 0 | 3493.4376 | Heating | 3082.4449 | 8.5 | 3082.4449 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 616.489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3145.352 | 0 | 629.0704 | 6.291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 21:00 | 4 | 6 | 21 | 96 | 2301 | 44.06 | 3979.4968 | 0 | 0 | 3979.4968 | Heating | 3511.3207 | 8.5 | 3511.3207 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 702.2641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3582.9803 | 0 | 716.5961 | 7.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 22:00 | 4 | 6 | 22 | 96 | 2302 | 37.04 | 969.5612 | 0 | 0 | 969.5612 | Heating | 855.4952 | 8.5 | 855.4952 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 872.9543 | 0 | 174.5909 | 1.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-06 23:00 | 4 | 6 | 23 | 96 | 2303 | 37.04 | 1067.6986 | 0 | 0 | 1067.6986 | Heating | 942.087 | 8.5 | 942.087 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.4174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 961.3132 | 0 | 192.2626 | 1.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 | 4 | 7 | 0 | 97 | 2304 | 35.06 | 1178.4329 | 0 | 0 | 1178.4329 | Heating | 1039.7938 | 8.5 | 1039.7938 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.9588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1061.014 | 0 | 212.2028 | 2.122% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 01:00 | 4 | 7 | 1 | 97 | 2305 | 35.06 | 1271.702 | 0 | 0 | 1271.702 | Heating | 1122.09 | 8.5 | 1122.09 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1144.9898 | 0 | 228.998 | 2.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 02:00 | 4 | 7 | 2 | 97 | 2306 | 35.06 | 1383.0748 | 0 | 0 | 1383.0748 | Heating | 1220.3601 | 8.5 | 1220.3601 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 244.072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1245.2654 | 0 | 249.0531 | 2.491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 03:00 | 4 | 7 | 3 | 97 | 2307 | 32 | 1436.8893 | 0 | 0 | 1436.8893 | Heating | 1267.8435 | 8.5 | 1267.8435 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.5687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1293.7178 | 0 | 258.7436 | 2.587% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 04:00 | 4 | 7 | 4 | 97 | 2308 | 30.92 | 1445.4681 | 0 | 0 | 1445.4681 | Heating | 1275.413 | 8.5 | 1275.413 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 255.0826 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1301.4419 | 0 | 260.2884 | 2.603% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 05:00 | 4 | 7 | 5 | 97 | 2309 | 30.92 | 1447.6564 | 0 | 0 | 1447.6564 | Heating | 1277.3439 | 8.5 | 1277.3439 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 255.4688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1303.4121 | 0 | 260.6824 | 2.607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 06:00 | 4 | 7 | 6 | 97 | 2310 | 30.02 | 1431.2172 | 0 | 0 | 1431.2172 | Heating | 1262.8387 | 8.5 | 1262.8387 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.5677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1288.6109 | 0 | 257.7222 | 2.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 07:00 | 4 | 7 | 7 | 97 | 2311 | 35.06 | 1429.3838 | 0 | 0 | 1429.3838 | Heating | 1261.221 | 8.5 | 1261.221 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.2442 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1286.9602 | 0 | 257.392 | 2.574% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 08:00 | 4 | 7 | 8 | 97 | 2312 | 35.06 | 8613.9587 | 0 | 0 | 8613.9587 | Heating | 7600.5518 | 8.5 | 7600.5518 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1520.1104 | 30.4% | 1 | 60.8% | 0% | 0% | 0% | 25.9534 | 0 | 0 | 0 | 25.9534 | 7755.6651 | 0 | 1551.133 | 15.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.2279
2007-04-07 09:00 | 4 | 7 | 9 | 97 | 2313 | 44.06 | 6450.2669 | 0 | 0 | 6450.2669 | Heating | 5691.412 | 8.5 | 5691.412 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1138.2824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5807.5633 | 0 | 1161.5127 | 11.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 10:00 | 4 | 7 | 10 | 97 | 2314 | 48.92 | 5396.6616 | 0 | 0 | 5396.6616 | Heating | 4761.7602 | 8.5 | 4761.7602 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 952.352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4858.939 | 0 | 971.7878 | 9.718% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 11:00 | 4 | 7 | 11 | 97 | 2315 | 48.92 | 4918.8142 | 0 | 0 | 4918.8142 | Heating | 4340.1302 | 8.5 | 4340.1302 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 868.026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4428.7043 | 0 | 885.7409 | 8.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 12:00 | 4 | 7 | 12 | 97 | 2316 | 53.96 | 4383.3803 | 0 | 0 | 4383.3803 | Heating | 3867.6885 | 8.5 | 3867.6885 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 773.5377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3946.6209 | 0 | 789.3242 | 7.893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 13:00 | 4 | 7 | 13 | 97 | 2317 | 55.04 | 4081.9014 | 0 | 0 | 4081.9014 | Heating | 3601.6777 | 8.5 | 3601.6777 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 720.3355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3675.1813 | 0 | 735.0363 | 7.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 14:00 | 4 | 7 | 14 | 97 | 2318 | 55.04 | 3907.6404 | 0 | 0 | 3907.6404 | Heating | 3447.918 | 8.5 | 3447.918 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 689.5836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3518.2837 | 0 | 703.6567 | 7.037% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 15:00 | 4 | 7 | 15 | 97 | 2319 | 53.96 | 3740.5782 | 0 | 0 | 3740.5782 | Heating | 3300.5101 | 8.5 | 3300.5101 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 660.102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3367.8675 | 0 | 673.5735 | 6.736% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 16:00 | 4 | 7 | 16 | 97 | 2320 | 53.96 | 3638.7603 | 0 | 0 | 3638.7603 | Heating | 3210.6708 | 8.5 | 3210.6708 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 642.1342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3276.1947 | 0 | 655.2389 | 6.552% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 17:00 | 4 | 7 | 17 | 97 | 2321 | 53.96 | 4956.9204 | 0 | 0 | 4956.9204 | Heating | 4373.7533 | 8.5 | 4373.7533 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 874.7507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4463.0136 | 0 | 892.6027 | 8.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 18:00 | 4 | 7 | 18 | 97 | 2322 | 53.06 | 5343.212 | 0 | 0 | 5343.212 | Heating | 4714.5988 | 8.5 | 4714.5988 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 942.9198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4810.8151 | 0 | 962.163 | 9.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 19:00 | 4 | 7 | 19 | 97 | 2323 | 50 | 1238.7072 | 0 | 0 | 1238.7072 | Heating | 1092.977 | 8.5 | 1092.977 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.5954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1115.2826 | 0 | 223.0565 | 2.231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 20:00 | 4 | 7 | 20 | 97 | 2324 | 50 | 1299.1618 | 0 | 0 | 1299.1618 | Heating | 1146.3192 | 8.5 | 1146.3192 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.2638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1169.7135 | 0 | 233.9427 | 2.339% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 21:00 | 4 | 7 | 21 | 97 | 2325 | 46.94 | 1358.4059 | 0 | 0 | 1358.4059 | Heating | 1198.5934 | 8.5 | 1198.5934 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 239.7187 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1223.0545 | 0 | 244.6109 | 2.446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 22:00 | 4 | 7 | 22 | 97 | 2326 | 44.96 | 1424.2218 | 0 | 0 | 1424.2218 | Heating | 1256.6663 | 8.5 | 1256.6663 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.3333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1282.3126 | 0 | 256.4625 | 2.565% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-07 23:00 | 4 | 7 | 23 | 97 | 2327 | 44.06 | 1522.2123 | 0 | 0 | 1522.2123 | Heating | 1343.1285 | 8.5 | 1343.1285 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.6257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1370.5393 | 0 | 274.1079 | 2.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 | 4 | 8 | 0 | 98 | 2328 | 42.08 | 1606.1786 | 0 | 0 | 1606.1786 | Heating | 1417.2164 | 8.5 | 1417.2164 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 283.4433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1446.1392 | 0 | 289.2278 | 2.892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 01:00 | 4 | 8 | 1 | 98 | 2329 | 42.08 | 1668.4567 | 0 | 0 | 1668.4567 | Heating | 1472.1677 | 8.5 | 1472.1677 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 294.4335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1502.212 | 0 | 300.4424 | 3.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 02:00 | 4 | 8 | 2 | 98 | 2330 | 42.08 | 1756.1576 | 0 | 0 | 1756.1576 | Heating | 1549.5509 | 8.5 | 1549.5509 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 309.9102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1581.1743 | 0 | 316.2349 | 3.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 03:00 | 4 | 8 | 3 | 98 | 2331 | 46.04 | 1819.3817 | 0 | 0 | 1819.3817 | Heating | 1605.3368 | 8.5 | 1605.3368 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.0674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1638.0988 | 0 | 327.6198 | 3.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 04:00 | 4 | 8 | 4 | 98 | 2332 | 46.4 | 1860.2784 | 0 | 0 | 1860.2784 | Heating | 1641.4222 | 8.5 | 1641.4222 | 0 | 4.1996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.2844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1674.9206 | 0 | 334.9841 | 3.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 05:00 | 4 | 8 | 5 | 98 | 2333 | 46.94 | 1905.5485 | 0 | 0 | 1905.5485 | Heating | 1681.3664 | 8.5 | 1681.3664 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.2733 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1715.68 | 0 | 343.136 | 3.431% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 06:00 | 4 | 8 | 6 | 98 | 2334 | 46.94 | 10247.9329 | 0 | 0 | 10247.9329 | Heating | 9042.2937 | 8.5 | 9042.2937 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1808.4587 | 36.17% | 1 | 72.34% | 0% | 0% | 0% | 38.6982 | 0 | 0 | 0 | 38.6982 | 9226.8303 | 0 | 1845.3661 | 18.45% | 1 | 36.91% | 0% | 0% | 4.116 | 0 | 0 | 4.116 | 42.8142
2007-04-08 07:00 | 4 | 8 | 7 | 98 | 2335 | 48.02 | 7566.0506 | 0 | 0 | 7566.0506 | Heating | 6675.927 | 8.5 | 6675.927 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1335.1854 | 30% | 1 | 53.41% | 0% | 0% | 0% | 19.2587 | 0 | 0 | 0 | 19.2587 | 6812.1704 | 0 | 1362.4341 | 13.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.5332
2007-04-08 08:00 | 4 | 8 | 8 | 98 | 2336 | 48.02 | 5875.4838 | 0 | 0 | 5875.4838 | Heating | 5184.2504 | 8.5 | 5184.2504 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1036.8501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5290.0514 | 0 | 1058.0103 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 09:00 | 4 | 8 | 9 | 98 | 2337 | 51.08 | 4251.4459 | 0 | 0 | 4251.4459 | Heating | 3751.2758 | 8.5 | 3751.2758 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.2552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3827.8324 | 0 | 765.5665 | 7.656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 10:00 | 4 | 8 | 10 | 98 | 2338 | 55.04 | 3115.2136 | 0 | 0 | 3115.2136 | Heating | 2748.7179 | 8.5 | 2748.7179 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 549.7436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2804.8142 | 0 | 560.9628 | 5.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 11:00 | 4 | 8 | 11 | 98 | 2339 | 55.94 | 2304.1705 | 0 | 0 | 2304.1705 | Heating | 2033.0916 | 8.5 | 2033.0916 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 406.6183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2074.5833 | 0 | 414.9167 | 4.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 12:00 | 4 | 8 | 12 | 98 | 2340 | 59 | 1714.3543 | 0 | 0 | 1714.3543 | Heating | 1512.6656 | 8.5 | 1512.6656 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 302.5331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1543.5363 | 0 | 308.7073 | 3.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 13:00 | 4 | 8 | 13 | 98 | 2341 | 60.08 | 1206.4924 | 19.8373 | 19.8373 | 1186.6551 | Heating | 1047.0486 | 8.5 | 1047.0486 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.4097 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1068.417 | 0 | 213.6834 | 2.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 14:00 | 4 | 8 | 14 | 98 | 2342 | 60.08 | 800.2651 | 49.6875 | 49.6875 | 750.5775 | Heating | 662.2743 | 8.5 | 662.2743 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.4549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 675.7901 | 0 | 135.158 | 1.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 15:00 | 4 | 8 | 15 | 98 | 2343 | 51.98 | 523.8555 | 57.0591 | 57.0591 | 466.7964 | Heating | 411.8791 | 8.5 | 411.8791 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.3758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 420.2848 | 0 | 84.057 | 0.8406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 16:00 | 4 | 8 | 16 | 98 | 2344 | 51.98 | 527.8001 | 75.8961 | 75.8961 | 451.904 | Heating | 398.7389 | 8.5 | 398.7389 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.7478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 406.8764 | 0 | 81.3753 | 0.8138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 17:00 | 4 | 8 | 17 | 98 | 2345 | 51.98 | 562.301 | 86.0322 | 86.0322 | 476.2688 | Heating | 420.2371 | 8.5 | 420.2371 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.0474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 428.8134 | 0 | 85.7627 | 0.8576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 18:00 | 4 | 8 | 18 | 98 | 2346 | 46.94 | 914.7083 | 55.334 | 55.334 | 859.3743 | Heating | 758.2714 | 8.5 | 758.2714 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.6543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 773.7463 | 0 | 154.7493 | 1.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 19:00 | 4 | 8 | 19 | 98 | 2347 | 42.98 | 1500.8039 | 17.5763 | 17.5763 | 1483.2276 | Heating | 1308.7303 | 8.5 | 1308.7303 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.7461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1335.439 | 0 | 267.0878 | 2.671% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 20:00 | 4 | 8 | 20 | 98 | 2348 | 42.98 | 2336.4418 | 0.033397 | 0.033397 | 2336.4084 | Heating | 2061.5368 | 8.5 | 2061.5368 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.3074 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2103.609 | 0 | 420.7218 | 4.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 21:00 | 4 | 8 | 21 | 98 | 2349 | 42.98 | 730.065 | 0 | 0 | 730.065 | Heating | 644.175 | 8.5 | 644.175 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 657.3215 | 0 | 131.4643 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 22:00 | 4 | 8 | 22 | 98 | 2350 | 42.98 | 837.4115 | 0 | 0 | 837.4115 | Heating | 738.8925 | 8.5 | 738.8925 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 147.7785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 753.972 | 0 | 150.7944 | 1.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-08 23:00 | 4 | 8 | 23 | 98 | 2351 | 42.98 | 964.6776 | 0 | 0 | 964.6776 | Heating | 851.1861 | 8.5 | 851.1861 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.2372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 868.5573 | 0 | 173.7115 | 1.737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 | 4 | 9 | 0 | 99 | 2352 | 42.98 | 1071.2399 | 0 | 0 | 1071.2399 | Heating | 945.2117 | 8.5 | 945.2117 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 189.0423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 964.5017 | 0 | 192.9003 | 1.929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 01:00 | 4 | 9 | 1 | 99 | 2353 | 42.98 | 1186.1079 | 0 | 0 | 1186.1079 | Heating | 1046.5658 | 8.5 | 1046.5658 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.3132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1067.9243 | 0 | 213.5849 | 2.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 02:00 | 4 | 9 | 2 | 99 | 2354 | 42.98 | 1277.3011 | 0 | 0 | 1277.3011 | Heating | 1127.0303 | 8.5 | 1127.0303 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.4061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1150.031 | 0 | 230.0062 | 2.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 03:00 | 4 | 9 | 3 | 99 | 2355 | 41 | 1291.1076 | 0 | 0 | 1291.1076 | Heating | 1139.2126 | 8.5 | 1139.2126 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 227.8425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1162.4618 | 0 | 232.4924 | 2.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 04:00 | 4 | 9 | 4 | 99 | 2356 | 39.92 | 1311.6702 | 0 | 0 | 1311.6702 | Heating | 1157.3561 | 8.5 | 1157.3561 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.4712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1180.9756 | 0 | 236.1951 | 2.362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 05:00 | 4 | 9 | 5 | 99 | 2357 | 39.92 | 1382.0956 | 0 | 0 | 1382.0956 | Heating | 1219.4961 | 8.5 | 1219.4961 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 243.8992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1244.3838 | 0 | 248.8768 | 2.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 06:00 | 4 | 9 | 6 | 99 | 2358 | 37.04 | 10119.2715 | 0 | 0 | 10119.2715 | Heating | 8928.769 | 8.5 | 8928.769 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1785.7538 | 35.72% | 1 | 71.43% | 0% | 0% | 0% | 37.5899 | 0 | 0 | 0 | 37.5899 | 9110.9887 | 0 | 1822.1977 | 18.22% | 1 | 36.44% | 0% | 0% | 3.9981 | 0 | 0 | 3.9981 | 41.5879
2007-04-09 07:00 | 4 | 9 | 7 | 99 | 2359 | 42.08 | 7244.6812 | 0 | 0 | 7244.6812 | Heating | 6392.3657 | 8.5 | 6392.3657 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1278.4731 | 30% | 1 | 51.14% | 0% | 0% | 0% | 17.429 | 0 | 0 | 0 | 17.429 | 6522.8222 | 0 | 1304.5644 | 13.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7035
2007-04-09 08:00 | 4 | 9 | 8 | 99 | 2360 | 42.08 | 5105.6313 | 0 | 0 | 5105.6313 | Heating | 4504.9688 | 8.5 | 4504.9688 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 900.9938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4596.9069 | 0 | 919.3814 | 9.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 09:00 | 4 | 9 | 9 | 99 | 2361 | 46.94 | 3038.8355 | 0 | 0 | 3038.8355 | Heating | 2681.3255 | 8.5 | 2681.3255 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 536.2651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2736.0464 | 0 | 547.2093 | 5.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 10:00 | 4 | 9 | 10 | 99 | 2362 | 48.92 | 1812.0012 | 0 | 0 | 1812.0012 | Heating | 1598.8246 | 8.5 | 1598.8246 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 319.7649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1631.4537 | 0 | 326.2907 | 3.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 11:00 | 4 | 9 | 11 | 99 | 2363 | 48.92 | 1112.9545 | 0 | 0 | 1112.9545 | Heating | 982.0187 | 8.5 | 982.0187 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.4037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1002.0599 | 0 | 200.412 | 2.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 12:00 | 4 | 9 | 12 | 99 | 2364 | 51.98 | 747.3537 | 5.4295 | 5.4295 | 741.9242 | Heating | 654.639 | 8.5 | 654.639 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.9278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 667.999 | 0 | 133.5998 | 1.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 13:00 | 4 | 9 | 13 | 99 | 2365 | 53.06 | 409.6393 | 50.4976 | 50.4976 | 359.1416 | Heating | 316.8897 | 8.5 | 316.8897 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.3779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 323.3568 | 0 | 64.6714 | 0.6467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 14:00 | 4 | 9 | 14 | 99 | 2366 | 53.06 | 267.8045 | 77.7911 | 77.7911 | 190.0134 | Heating | 167.6589 | 8.5 | 167.6589 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.5318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 171.0805 | 0 | 34.2161 | 0.3422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 15:00 | 4 | 9 | 15 | 99 | 2367 | 51.08 | 224.7085 | 117.3906 | 117.3906 | 107.3179 | Heating | 94.6922 | 8.5 | 94.6922 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.9384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 96.6247 | 0 | 19.3249 | 0.1932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 16:00 | 4 | 9 | 16 | 99 | 2368 | 50 | 179.6741 | 155.4804 | 155.4804 | 24.1938 | Heating | 21.3474 | 8.5 | 21.3474 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.2695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.7831 | 0 | 4.3566 | 0.04357% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 17:00 | 4 | 9 | 17 | 99 | 2369 | 50 | 174.0397 | 115.7011 | 115.7011 | 58.3386 | Heating | 51.4752 | 8.5 | 51.4752 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 52.5257 | 0 | 10.5051 | 0.1051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 18:00 | 4 | 9 | 18 | 99 | 2370 | 46.94 | 176.5761 | 47.6822 | 47.6822 | 128.8939 | Heating | 113.7299 | 8.5 | 113.7299 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.0509 | 0 | 23.2102 | 0.2321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 19:00 | 4 | 9 | 19 | 99 | 2371 | 42.98 | 499.6761 | 21.2956 | 21.2956 | 478.3805 | Heating | 422.1005 | 8.5 | 422.1005 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.4201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 430.7148 | 0 | 86.143 | 0.8614% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 20:00 | 4 | 9 | 20 | 99 | 2372 | 42.98 | 997.8126 | 0 | 0 | 997.8126 | Heating | 880.4229 | 8.5 | 880.4229 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 176.0846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 898.3907 | 0 | 179.6781 | 1.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 21:00 | 4 | 9 | 21 | 99 | 2373 | 39.92 | 314.3336 | 0 | 0 | 314.3336 | Heating | 277.3531 | 8.5 | 277.3531 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.4706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 283.0134 | 0 | 56.6027 | 0.566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 22:00 | 4 | 9 | 22 | 99 | 2374 | 37.94 | 343.5688 | 0 | 0 | 343.5688 | Heating | 303.1489 | 8.5 | 303.1489 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.6298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 309.3356 | 0 | 61.8671 | 0.6187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-09 23:00 | 4 | 9 | 23 | 99 | 2375 | 37.94 | 364.3706 | 0 | 0 | 364.3706 | Heating | 321.5035 | 8.5 | 321.5035 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.3007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 328.0648 | 0 | 65.613 | 0.6561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 | 4 | 10 | 0 | 100 | 2376 | 35.96 | 390.804 | 0 | 0 | 390.804 | Heating | 344.8271 | 8.5 | 344.8271 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.9654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 351.8644 | 0 | 70.3729 | 0.7037% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 01:00 | 4 | 10 | 1 | 100 | 2377 | 28.94 | 405.7525 | 0 | 0 | 405.7525 | Heating | 358.0169 | 8.5 | 358.0169 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.6034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 365.3234 | 0 | 73.0647 | 0.7306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 02:00 | 4 | 10 | 2 | 100 | 2378 | 28.94 | 405.6409 | 0 | 0 | 405.6409 | Heating | 357.9184 | 8.5 | 357.9184 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.5837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 365.2229 | 0 | 73.0446 | 0.7304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 03:00 | 4 | 10 | 3 | 100 | 2379 | 26.96 | 406.4807 | 0 | 0 | 406.4807 | Heating | 358.6594 | 8.5 | 358.6594 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.7319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 365.979 | 0 | 73.1958 | 0.732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 04:00 | 4 | 10 | 4 | 100 | 2380 | 26.96 | 409.233 | 0 | 0 | 409.233 | Heating | 361.088 | 8.5 | 361.088 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.2176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 368.4571 | 0 | 73.6914 | 0.7369% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 05:00 | 4 | 10 | 5 | 100 | 2381 | 26.96 | 414.0427 | 0 | 0 | 414.0427 | Heating | 365.3318 | 8.5 | 365.3318 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.0664 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 372.7876 | 0 | 74.5575 | 0.7456% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 06:00 | 4 | 10 | 6 | 100 | 2382 | 30.92 | 4497.4539 | 0 | 0 | 4497.4539 | Heating | 3968.3417 | 8.5 | 3968.3417 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 793.6683 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4049.3282 | 0 | 809.8656 | 8.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 07:00 | 4 | 10 | 7 | 100 | 2383 | 37.04 | 3124.4265 | 0 | 0 | 3124.4265 | Heating | 2756.8469 | 8.5 | 2756.8469 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 551.3694 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2813.1091 | 0 | 562.6218 | 5.626% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 08:00 | 4 | 10 | 8 | 100 | 2384 | 37.04 | 2463.6326 | 0 | 0 | 2463.6326 | Heating | 2173.7935 | 8.5 | 2173.7935 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 434.7587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2218.1566 | 0 | 443.6313 | 4.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 09:00 | 4 | 10 | 9 | 100 | 2385 | 44.96 | 1694.442 | 0 | 0 | 1694.442 | Heating | 1495.0959 | 8.5 | 1495.0959 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 299.0192 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1525.6081 | 0 | 305.1216 | 3.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 10:00 | 4 | 10 | 10 | 100 | 2386 | 50 | 1348.4269 | 0 | 0 | 1348.4269 | Heating | 1189.7884 | 8.5 | 1189.7884 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.9577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1214.0698 | 0 | 242.814 | 2.428% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 11:00 | 4 | 10 | 11 | 100 | 2387 | 50 | 1044.6289 | 0 | 0 | 1044.6289 | Heating | 921.7314 | 8.5 | 921.7314 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.3463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 940.5422 | 0 | 188.1084 | 1.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 12:00 | 4 | 10 | 12 | 100 | 2388 | 60.08 | 918.6958 | 0 | 0 | 918.6958 | Heating | 810.6139 | 8.5 | 810.6139 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.1228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 827.1571 | 0 | 165.4314 | 1.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 13:00 | 4 | 10 | 13 | 100 | 2389 | 60.98 | 1037.1749 | 0 | 0 | 1037.1749 | Heating | 915.1543 | 8.5 | 915.1543 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.0309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 933.8309 | 0 | 186.7662 | 1.868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 14:00 | 4 | 10 | 14 | 100 | 2390 | 60.98 | 862.1756 | 0 | 0 | 862.1756 | Heating | 760.7432 | 8.5 | 760.7432 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.1486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 776.2685 | 0 | 155.2537 | 1.553% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 15:00 | 4 | 10 | 15 | 100 | 2391 | 66.02 | 597.0458 | 0 | 0 | 597.0458 | Heating | 526.8051 | 8.5 | 526.8051 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 537.5562 | 0 | 107.5112 | 1.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 16:00 | 4 | 10 | 16 | 100 | 2392 | 64.94 | 521.4184 | 0 | 0 | 521.4184 | Heating | 460.075 | 8.5 | 460.075 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 469.4643 | 0 | 93.8929 | 0.9389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 17:00 | 4 | 10 | 17 | 100 | 2393 | 64.94 | 603.0222 | 0 | 0 | 603.0222 | Heating | 532.0784 | 8.5 | 532.0784 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.4157 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.9372 | 0 | 108.5874 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 18:00 | 4 | 10 | 18 | 100 | 2394 | 62.06 | 931.1129 | 0 | 0 | 931.1129 | Heating | 821.5702 | 8.5 | 821.5702 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 164.314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 838.3369 | 0 | 167.6674 | 1.677% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 19:00 | 4 | 10 | 19 | 100 | 2395 | 59 | 1297.8756 | 0 | 0 | 1297.8756 | Heating | 1145.1843 | 8.5 | 1145.1843 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.0369 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1168.5555 | 0 | 233.7111 | 2.337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 20:00 | 4 | 10 | 20 | 100 | 2396 | 59 | 1664.567 | 0 | 0 | 1664.567 | Heating | 1468.7356 | 8.5 | 1468.7356 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 293.7471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1498.7098 | 0 | 299.742 | 2.997% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 21:00 | 4 | 10 | 21 | 100 | 2397 | 55.94 | 481.2312 | 0 | 0 | 481.2312 | Heating | 424.6158 | 8.5 | 424.6158 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.9232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 433.2814 | 0 | 86.6563 | 0.8666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 22:00 | 4 | 10 | 22 | 100 | 2398 | 55.94 | 538.9354 | 0 | 0 | 538.9354 | Heating | 475.5313 | 8.5 | 475.5313 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.1063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 485.236 | 0 | 97.0472 | 0.9705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-10 23:00 | 4 | 10 | 23 | 100 | 2399 | 55.94 | 596.9458 | 0 | 0 | 596.9458 | Heating | 526.7169 | 8.5 | 526.7169 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.3434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 537.4662 | 0 | 107.4932 | 1.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 | 4 | 11 | 0 | 101 | 2400 | 55.94 | 665.0611 | 0 | 0 | 665.0611 | Heating | 586.8186 | 8.5 | 586.8186 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 117.3637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 598.7945 | 0 | 119.7589 | 1.198% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 01:00 | 4 | 11 | 1 | 101 | 2401 | 55.94 | 742.6902 | 0 | 0 | 742.6902 | Heating | 655.3149 | 8.5 | 655.3149 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 668.6886 | 0 | 133.7377 | 1.337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 02:00 | 4 | 11 | 2 | 101 | 2402 | 55.94 | 848.8855 | 0 | 0 | 848.8855 | Heating | 749.0166 | 8.5 | 749.0166 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.8033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 764.3026 | 0 | 152.8605 | 1.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 03:00 | 4 | 11 | 3 | 101 | 2403 | 55.94 | 936.4597 | 0 | 0 | 936.4597 | Heating | 826.288 | 8.5 | 826.288 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.2576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 843.151 | 0 | 168.6302 | 1.686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 04:00 | 4 | 11 | 4 | 101 | 2404 | 53.96 | 1078.5672 | 0 | 0 | 1078.5672 | Heating | 951.677 | 8.5 | 951.677 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.3354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 971.099 | 0 | 194.2198 | 1.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 05:00 | 4 | 11 | 5 | 101 | 2405 | 53.96 | 1184.6537 | 0 | 0 | 1184.6537 | Heating | 1045.2827 | 8.5 | 1045.2827 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.0565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1066.615 | 0 | 213.323 | 2.133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 06:00 | 4 | 11 | 6 | 101 | 2406 | 51.08 | 8424.1885 | 0 | 0 | 8424.1885 | Heating | 7433.1075 | 8.5 | 7433.1075 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1486.6215 | 30% | 1 | 59.46% | 0% | 0% | 0% | 24.6571 | 0 | 0 | 0 | 24.6571 | 7584.8036 | 0 | 1516.9607 | 15.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.9316
2007-04-11 07:00 | 4 | 11 | 7 | 101 | 2407 | 53.96 | 5864.4622 | 0 | 0 | 5864.4622 | Heating | 5174.5255 | 8.5 | 5174.5255 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1034.9051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5280.128 | 0 | 1056.0256 | 10.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 08:00 | 4 | 11 | 8 | 101 | 2408 | 53.96 | 4289.3318 | 0 | 0 | 4289.3318 | Heating | 3784.7045 | 8.5 | 3784.7045 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 756.9409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3861.9434 | 0 | 772.3887 | 7.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 09:00 | 4 | 11 | 9 | 101 | 2409 | 59 | 2919.9262 | 0 | 0 | 2919.9262 | Heating | 2576.4054 | 8.5 | 2576.4054 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 515.2811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2628.9852 | 0 | 525.797 | 5.258% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 10:00 | 4 | 11 | 10 | 101 | 2410 | 60.08 | 2118.8353 | 0 | 0 | 2118.8353 | Heating | 1869.5605 | 8.5 | 1869.5605 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.9121 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1907.7148 | 0 | 381.543 | 3.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 11:00 | 4 | 11 | 11 | 101 | 2411 | 60.08 | 1344.3381 | 0 | 0 | 1344.3381 | Heating | 1186.1807 | 8.5 | 1186.1807 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.2361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1210.3884 | 0 | 242.0777 | 2.421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 12:00 | 4 | 11 | 12 | 101 | 2412 | 64.94 | 807.6696 | 1.147 | 1.147 | 806.5226 | Heating | 711.6376 | 8.5 | 711.6376 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 142.3275 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 726.1608 | 0 | 145.2322 | 1.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 13:00 | 4 | 11 | 13 | 101 | 2413 | 64.04 | 462.767 | 27.2992 | 27.2992 | 435.4678 | Heating | 384.2363 | 8.5 | 384.2363 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.8473 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 392.0779 | 0 | 78.4156 | 0.7842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 14:00 | 4 | 11 | 14 | 101 | 2414 | 64.04 | 330.8517 | 103.2236 | 103.2236 | 227.6281 | Heating | 200.8483 | 8.5 | 200.8483 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.1697 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 204.9473 | 0 | 40.9895 | 0.4099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 15:00 | 4 | 11 | 15 | 101 | 2415 | 57.02 | 256.7492 | 110.7311 | 110.7311 | 146.018 | Heating | 128.8394 | 8.5 | 128.8394 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.7679 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 131.4688 | 0 | 26.2938 | 0.2629% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 16:00 | 4 | 11 | 16 | 101 | 2416 | 53.96 | 216.0236 | 114.8196 | 114.8196 | 101.204 | Heating | 89.2976 | 8.5 | 89.2976 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.8595 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 91.12 | 0 | 18.224 | 0.1822% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 17:00 | 4 | 11 | 17 | 101 | 2417 | 53.96 | 245.0689 | 68.5704 | 68.5704 | 176.4985 | Heating | 155.734 | 8.5 | 155.734 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.1468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 158.9122 | 0 | 31.7824 | 0.3178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 18:00 | 4 | 11 | 18 | 101 | 2418 | 48.02 | 493.3315 | 18.0523 | 18.0523 | 475.2792 | Heating | 419.364 | 8.5 | 419.364 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.8728 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 427.9224 | 0 | 85.5845 | 0.8558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 19:00 | 4 | 11 | 19 | 101 | 2419 | 48.02 | 1034.5258 | 2.2209 | 2.2209 | 1032.305 | Heating | 910.8573 | 8.5 | 910.8573 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.1715 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 929.4463 | 0 | 185.8893 | 1.859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 20:00 | 4 | 11 | 20 | 101 | 2420 | 48.02 | 1422.6183 | 0 | 0 | 1422.6183 | Heating | 1255.2514 | 8.5 | 1255.2514 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.0503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1280.8688 | 0 | 256.1738 | 2.562% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 21:00 | 4 | 11 | 21 | 101 | 2421 | 46.94 | 407.645 | 0 | 0 | 407.645 | Heating | 359.6868 | 8.5 | 359.6868 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.9374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 367.0274 | 0 | 73.4055 | 0.7341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 22:00 | 4 | 11 | 22 | 101 | 2422 | 46.04 | 473.3342 | 0 | 0 | 473.3342 | Heating | 417.6479 | 8.5 | 417.6479 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.5296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 426.1713 | 0 | 85.2343 | 0.8523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-11 23:00 | 4 | 11 | 23 | 101 | 2423 | 46.04 | 532.1812 | 0 | 0 | 532.1812 | Heating | 469.5717 | 8.5 | 469.5717 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.9143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 479.1548 | 0 | 95.831 | 0.9583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 | 4 | 12 | 0 | 102 | 2424 | 41 | 594.2015 | 0 | 0 | 594.2015 | Heating | 524.2955 | 8.5 | 524.2955 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 104.8591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 534.9954 | 0 | 106.9991 | 1.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 01:00 | 4 | 12 | 1 | 102 | 2425 | 37.94 | 698.9733 | 0 | 0 | 698.9733 | Heating | 616.7412 | 8.5 | 616.7412 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.3482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 629.3277 | 0 | 125.8655 | 1.259% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 02:00 | 4 | 12 | 2 | 102 | 2426 | 39.02 | 825.1496 | 0 | 0 | 825.1496 | Heating | 728.0732 | 8.5 | 728.0732 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.6146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 742.9318 | 0 | 148.5864 | 1.486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 03:00 | 4 | 12 | 3 | 102 | 2427 | 35.06 | 910.4415 | 0 | 0 | 910.4415 | Heating | 803.3307 | 8.5 | 803.3307 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.6661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 819.7252 | 0 | 163.945 | 1.639% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 04:00 | 4 | 12 | 4 | 102 | 2428 | 37.04 | 991.1796 | 0 | 0 | 991.1796 | Heating | 874.5702 | 8.5 | 874.5702 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.914 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 892.4186 | 0 | 178.4837 | 1.785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 05:00 | 4 | 12 | 5 | 102 | 2429 | 37.04 | 1071.5683 | 0 | 0 | 1071.5683 | Heating | 945.5015 | 8.5 | 945.5015 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 189.1003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 964.7974 | 0 | 192.9595 | 1.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 06:00 | 4 | 12 | 6 | 102 | 2430 | 33.98 | 8885.8408 | 0 | 0 | 8885.8408 | Heating | 7840.4477 | 8.5 | 7840.4477 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1568.0895 | 31.36% | 1 | 62.72% | 0% | 0% | 0% | 27.8762 | 0 | 0 | 0 | 27.8762 | 8000.4569 | 0 | 1600.0914 | 16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.1508
2007-04-12 07:00 | 4 | 12 | 7 | 102 | 2431 | 35.96 | 6226.8364 | 0 | 0 | 6226.8364 | Heating | 5494.2674 | 8.5 | 5494.2674 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1098.8535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5606.3953 | 0 | 1121.2791 | 11.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 08:00 | 4 | 12 | 8 | 102 | 2432 | 35.96 | 4672.2024 | 0 | 0 | 4672.2024 | Heating | 4122.5316 | 8.5 | 4122.5316 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 824.5063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4206.6649 | 0 | 841.333 | 8.413% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 09:00 | 4 | 12 | 9 | 102 | 2433 | 41 | 3271.5164 | 0 | 0 | 3271.5164 | Heating | 2886.6321 | 8.5 | 2886.6321 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 577.3264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2945.543 | 0 | 589.1086 | 5.891% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 10:00 | 4 | 12 | 10 | 102 | 2434 | 51.08 | 2378.5332 | 0 | 0 | 2378.5332 | Heating | 2098.7058 | 8.5 | 2098.7058 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 419.7412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2141.5365 | 0 | 428.3073 | 4.283% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 11:00 | 4 | 12 | 11 | 102 | 2435 | 51.08 | 1622.6423 | 0 | 0 | 1622.6423 | Heating | 1431.7432 | 8.5 | 1431.7432 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.3486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1460.9625 | 0 | 292.1925 | 2.922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 12:00 | 4 | 12 | 12 | 102 | 2436 | 60.98 | 1087.4115 | 0 | 0 | 1087.4115 | Heating | 959.4807 | 8.5 | 959.4807 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.8961 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 979.062 | 0 | 195.8124 | 1.958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 13:00 | 4 | 12 | 13 | 102 | 2437 | 62.96 | 897.0168 | 1.5032 | 1.5032 | 895.5136 | Heating | 790.159 | 8.5 | 790.159 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.0318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 806.2847 | 0 | 161.2569 | 1.613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 14:00 | 4 | 12 | 14 | 102 | 2438 | 62.96 | 722.2465 | 11.7493 | 11.7493 | 710.4972 | Heating | 626.9093 | 8.5 | 626.9093 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.3819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 639.7034 | 0 | 127.9407 | 1.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 15:00 | 4 | 12 | 15 | 102 | 2439 | 68 | 668.3582 | 17.0037 | 17.0037 | 651.3546 | Heating | 574.7246 | 8.5 | 574.7246 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.9449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 586.4537 | 0 | 117.2907 | 1.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 16:00 | 4 | 12 | 16 | 102 | 2440 | 69.08 | 944.5725 | 12.128 | 12.128 | 932.4446 | Heating | 822.7452 | 8.5 | 822.7452 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 164.549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 839.5359 | 0 | 167.9072 | 1.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 17:00 | 4 | 12 | 17 | 102 | 2441 | 69.08 | 1406.2336 | 0 | 0 | 1406.2336 | Heating | 1240.7943 | 8.5 | 1240.7943 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.1589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1266.1167 | 0 | 253.2233 | 2.532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 18:00 | 4 | 12 | 18 | 102 | 2442 | 64.04 | 1722.9449 | 0 | 0 | 1722.9449 | Heating | 1520.2455 | 8.5 | 1520.2455 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 304.0491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1551.2709 | 0 | 310.2542 | 3.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 19:00 | 4 | 12 | 19 | 102 | 2443 | 60.08 | 1977.0554 | 0 | 0 | 1977.0554 | Heating | 1744.4606 | 8.5 | 1744.4606 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 348.8921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1780.0619 | 0 | 356.0124 | 3.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 20:00 | 4 | 12 | 20 | 102 | 2444 | 60.08 | 2196.4589 | 0 | 0 | 2196.4589 | Heating | 1938.0519 | 8.5 | 1938.0519 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.6104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1977.604 | 0 | 395.5208 | 3.955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 21:00 | 4 | 12 | 21 | 102 | 2445 | 51.98 | 549.4328 | 0 | 0 | 549.4328 | Heating | 484.7937 | 8.5 | 484.7937 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.9587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 494.6874 | 0 | 98.9375 | 0.9894% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 22:00 | 4 | 12 | 22 | 102 | 2446 | 50 | 588.4545 | 0 | 0 | 588.4545 | Heating | 519.2246 | 8.5 | 519.2246 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 103.8449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 529.821 | 0 | 105.9642 | 1.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-12 23:00 | 4 | 12 | 23 | 102 | 2447 | 50 | 632.017 | 0 | 0 | 632.017 | Heating | 557.6621 | 8.5 | 557.6621 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.5324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 569.043 | 0 | 113.8086 | 1.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 | 4 | 13 | 0 | 103 | 2448 | 48.92 | 664.254 | 0 | 0 | 664.254 | Heating | 586.1065 | 8.5 | 586.1065 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 117.2213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 598.0678 | 0 | 119.6136 | 1.196% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 01:00 | 4 | 13 | 1 | 103 | 2449 | 48.02 | 683.5529 | 0 | 0 | 683.5529 | Heating | 603.1349 | 8.5 | 603.1349 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 615.4438 | 0 | 123.0888 | 1.231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 02:00 | 4 | 13 | 2 | 103 | 2450 | 48.02 | 699.7479 | 0 | 0 | 699.7479 | Heating | 617.4246 | 8.5 | 617.4246 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.4849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 630.0251 | 0 | 126.005 | 1.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 03:00 | 4 | 13 | 3 | 103 | 2451 | 44.96 | 712.925 | 0 | 0 | 712.925 | Heating | 629.0515 | 8.5 | 629.0515 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.8103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 641.8893 | 0 | 128.3779 | 1.284% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 04:00 | 4 | 13 | 4 | 103 | 2452 | 44.96 | 718.8742 | 0 | 0 | 718.8742 | Heating | 634.3008 | 8.5 | 634.3008 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.8602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 647.2457 | 0 | 129.4491 | 1.294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 05:00 | 4 | 13 | 5 | 103 | 2453 | 44.96 | 713.62 | 0 | 0 | 713.62 | Heating | 629.6647 | 8.5 | 629.6647 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.9329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 642.515 | 0 | 128.503 | 1.285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 06:00 | 4 | 13 | 6 | 103 | 2454 | 46.94 | 6555.1865 | 0 | 0 | 6555.1865 | Heating | 5783.988 | 8.5 | 5783.988 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1156.7976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5902.0286 | 0 | 1180.4057 | 11.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 07:00 | 4 | 13 | 7 | 103 | 2455 | 48.02 | 4757.2457 | 0 | 0 | 4757.2457 | Heating | 4197.5698 | 8.5 | 4197.5698 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 839.514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4283.2345 | 0 | 856.6469 | 8.566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 08:00 | 4 | 13 | 8 | 103 | 2456 | 48.02 | 4022.7034 | 0 | 0 | 4022.7034 | Heating | 3549.4442 | 8.5 | 3549.4442 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 709.8888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3621.8818 | 0 | 724.3764 | 7.244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 09:00 | 4 | 13 | 9 | 103 | 2457 | 59 | 3136.3013 | 0 | 0 | 3136.3013 | Heating | 2767.3247 | 8.5 | 2767.3247 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 553.4649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2823.8007 | 0 | 564.7601 | 5.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 10:00 | 4 | 13 | 10 | 103 | 2458 | 62.96 | 2384.7392 | 0 | 0 | 2384.7392 | Heating | 2104.1816 | 8.5 | 2104.1816 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 420.8363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2147.1241 | 0 | 429.4248 | 4.294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 11:00 | 4 | 13 | 11 | 103 | 2459 | 62.96 | 1929.9303 | 0 | 0 | 1929.9303 | Heating | 1702.8797 | 8.5 | 1702.8797 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.5759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1737.6324 | 0 | 347.5265 | 3.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 12:00 | 4 | 13 | 12 | 103 | 2460 | 69.08 | 1756.5413 | 0 | 0 | 1756.5413 | Heating | 1549.8894 | 8.5 | 1549.8894 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 309.9779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1581.5198 | 0 | 316.304 | 3.163% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 13:00 | 4 | 13 | 13 | 103 | 2461 | 71.06 | 1652.6421 | 0 | 0 | 1652.6421 | Heating | 1458.2136 | 8.5 | 1458.2136 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 291.6427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1487.9731 | 0 | 297.5946 | 2.976% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 14:00 | 4 | 13 | 14 | 103 | 2462 | 71.06 | 1553.1161 | 0 | 0 | 1553.1161 | Heating | 1370.3966 | 8.5 | 1370.3966 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.0793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1398.3639 | 0 | 279.6728 | 2.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 15:00 | 4 | 13 | 15 | 103 | 2463 | 75.92 | 1332.5313 | 0 | 0 | 1332.5313 | Heating | 1175.7629 | 8.5 | 1175.7629 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.1526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1199.7581 | 0 | 239.9516 | 2.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 16:00 | 4 | 13 | 16 | 103 | 2464 | 77 | 1148.7335 | 0 | 0 | 1148.7335 | Heating | 1013.5884 | 8.5 | 1013.5884 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.7177 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1034.2739 | 0 | 206.8548 | 2.069% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 17:00 | 4 | 13 | 17 | 103 | 2465 | 77 | 1170.8187 | 0 | 0 | 1170.8187 | Heating | 1033.0753 | 8.5 | 1033.0753 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.6151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1054.1585 | 0 | 210.8317 | 2.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 18:00 | 4 | 13 | 18 | 103 | 2466 | 77 | 1562.262 | 0 | 0 | 1562.262 | Heating | 1378.4664 | 8.5 | 1378.4664 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 275.6933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1406.5984 | 0 | 281.3197 | 2.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 19:00 | 4 | 13 | 19 | 103 | 2467 | 75.02 | 1756.1523 | 0 | 0 | 1756.1523 | Heating | 1549.5462 | 8.5 | 1549.5462 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 309.9092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1581.1695 | 0 | 316.2339 | 3.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 20:00 | 4 | 13 | 20 | 103 | 2468 | 75.02 | 1837.9317 | 0 | 0 | 1837.9317 | Heating | 1621.7044 | 8.5 | 1621.7044 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.3409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1654.8004 | 0 | 330.9601 | 3.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 21:00 | 4 | 13 | 21 | 103 | 2469 | 71.96 | 2137.2744 | 0 | 0 | 2137.2744 | Heating | 1885.8304 | 8.5 | 1885.8304 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 377.1661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1924.3167 | 0 | 384.8633 | 3.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 22:00 | 4 | 13 | 22 | 103 | 2470 | 69.98 | 419.6952 | 0 | 0 | 419.6952 | Heating | 370.3193 | 8.5 | 370.3193 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.0639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 377.8768 | 0 | 75.5754 | 0.7558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-13 23:00 | 4 | 13 | 23 | 103 | 2471 | 69.98 | 464.6814 | 0 | 0 | 464.6814 | Heating | 410.013 | 8.5 | 410.013 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.0026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 418.3806 | 0 | 83.6761 | 0.8368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 | 4 | 14 | 0 | 104 | 2472 | 69.08 | 545.8045 | 0 | 0 | 545.8045 | Heating | 481.5922 | 8.5 | 481.5922 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.3184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 491.4206 | 0 | 98.2841 | 0.9828% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 01:00 | 4 | 14 | 1 | 104 | 2473 | 69.08 | 646.0792 | 0 | 0 | 646.0792 | Heating | 570.0699 | 8.5 | 570.0699 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 581.7039 | 0 | 116.3408 | 1.163% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 02:00 | 4 | 14 | 2 | 104 | 2474 | 69.08 | 693.9317 | 0 | 0 | 693.9317 | Heating | 612.2927 | 8.5 | 612.2927 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.4585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 624.7885 | 0 | 124.9577 | 1.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 03:00 | 4 | 14 | 3 | 104 | 2475 | 66.02 | 727.6635 | 0 | 0 | 727.6635 | Heating | 642.0561 | 8.5 | 642.0561 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.4112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 655.1592 | 0 | 131.0318 | 1.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 04:00 | 4 | 14 | 4 | 104 | 2476 | 64.94 | 738.9757 | 0 | 0 | 738.9757 | Heating | 652.0373 | 8.5 | 652.0373 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.4075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 665.3442 | 0 | 133.0688 | 1.331% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 05:00 | 4 | 14 | 5 | 104 | 2477 | 64.94 | 737.2355 | 0 | 0 | 737.2355 | Heating | 650.5019 | 8.5 | 650.5019 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.1004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 663.7775 | 0 | 132.7555 | 1.328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 06:00 | 4 | 14 | 6 | 104 | 2478 | 62.96 | 679.7368 | 0 | 0 | 679.7368 | Heating | 599.7678 | 8.5 | 599.7678 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.9536 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 612.0079 | 0 | 122.4016 | 1.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 07:00 | 4 | 14 | 7 | 104 | 2479 | 64.94 | 621.1942 | 0 | 0 | 621.1942 | Heating | 548.1126 | 8.5 | 548.1126 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.6225 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 559.2985 | 0 | 111.8597 | 1.119% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 08:00 | 4 | 14 | 8 | 104 | 2480 | 64.94 | 5252.6125 | 0 | 0 | 5252.6125 | Heating | 4634.658 | 8.5 | 4634.658 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 926.9316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4729.2429 | 0 | 945.8486 | 9.458% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 09:00 | 4 | 14 | 9 | 104 | 2481 | 69.98 | 3495.4954 | 0 | 0 | 3495.4954 | Heating | 3084.2606 | 8.5 | 3084.2606 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 616.8521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3147.2047 | 0 | 629.4409 | 6.294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 10:00 | 4 | 14 | 10 | 104 | 2482 | 71.96 | 2546.7631 | 0 | 0 | 2546.7631 | Heating | 2247.1439 | 8.5 | 2247.1439 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.4288 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2293.004 | 0 | 458.6008 | 4.586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 11:00 | 4 | 14 | 11 | 104 | 2483 | 71.96 | 1857.5517 | 0 | 0 | 1857.5517 | Heating | 1639.0162 | 8.5 | 1639.0162 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 327.8032 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1672.4656 | 0 | 334.4931 | 3.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 12:00 | 4 | 14 | 12 | 104 | 2484 | 73.94 | 1114.6302 | 0 | 0 | 1114.6302 | Heating | 983.4972 | 8.5 | 983.4972 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.6994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1003.5686 | 0 | 200.7137 | 2.007% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 13:00 | 4 | 14 | 13 | 104 | 2485 | 75.92 | 774.8372 | 0 | 0 | 774.8372 | Heating | 683.6799 | 8.5 | 683.6799 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 697.6325 | 0 | 139.5265 | 1.395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 14:00 | 4 | 14 | 14 | 104 | 2486 | 75.92 | 612.386 | 0 | 0 | 612.386 | Heating | 540.3405 | 8.5 | 540.3405 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.0681 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 551.3679 | 0 | 110.2736 | 1.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 15:00 | 4 | 14 | 15 | 104 | 2487 | 78.08 | 374.01 | 0 | 0 | 374.01 | Heating | 330.0089 | 8.5 | 330.0089 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 66.0018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 336.7437 | 0 | 67.3487 | 0.6735% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 16:00 | 4 | 14 | 16 | 104 | 2488 | 77 | 147.6873 | 0 | 0 | 147.6873 | Heating | 130.3123 | 8.5 | 130.3123 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.0625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 132.9717 | 0 | 26.5943 | 0.2659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 17:00 | 4 | 14 | 17 | 104 | 2489 | 77 | 339.208 | 0 | 0 | 339.208 | Heating | 299.3012 | 8.5 | 299.3012 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.8602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 305.4094 | 0 | 61.0819 | 0.6108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 18:00 | 4 | 14 | 18 | 104 | 2490 | 73.94 | 616.9243 | 0 | 0 | 616.9243 | Heating | 544.345 | 8.5 | 544.345 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 555.454 | 0 | 111.0908 | 1.111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 19:00 | 4 | 14 | 19 | 104 | 2491 | 71.96 | 107.9824 | 0 | 0 | 107.9824 | Heating | 95.2786 | 8.5 | 95.2786 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.0557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 97.223 | 0 | 19.4446 | 0.1944% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 20:00 | 4 | 14 | 20 | 104 | 2492 | 71.96 | 216.6064 | 0 | 0 | 216.6064 | Heating | 191.1233 | 8.5 | 191.1233 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.2247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 195.0238 | 0 | 39.0048 | 0.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 21:00 | 4 | 14 | 21 | 104 | 2493 | 68 | 328.5447 | 0 | 0 | 328.5447 | Heating | 289.8924 | 8.5 | 289.8924 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.9785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 295.8085 | 0 | 59.1617 | 0.5916% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 22:00 | 4 | 14 | 22 | 104 | 2494 | 66.92 | 443.0621 | 0 | 0 | 443.0621 | Heating | 390.9372 | 8.5 | 390.9372 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.1874 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 398.9155 | 0 | 79.7831 | 0.7978% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-14 23:00 | 4 | 14 | 23 | 104 | 2495 | 66.92 | 557.1537 | 0 | 0 | 557.1537 | Heating | 491.6062 | 8.5 | 491.6062 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.3212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 501.639 | 0 | 100.3278 | 1.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 | 4 | 15 | 0 | 105 | 2496 | 66.02 | 674.1424 | 0 | 0 | 674.1424 | Heating | 594.8315 | 8.5 | 594.8315 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.9663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 606.9709 | 0 | 121.3942 | 1.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 01:00 | 4 | 15 | 1 | 105 | 2497 | 64.94 | 779.75 | 0 | 0 | 779.75 | Heating | 688.0147 | 8.5 | 688.0147 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.6029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 702.0558 | 0 | 140.4112 | 1.404% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 02:00 | 4 | 15 | 2 | 105 | 2498 | 64.94 | 858.0508 | 0 | 0 | 858.0508 | Heating | 757.1037 | 8.5 | 757.1037 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.4207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 772.5548 | 0 | 154.511 | 1.545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 03:00 | 4 | 15 | 3 | 105 | 2499 | 64.04 | 939.0537 | 0 | 0 | 939.0537 | Heating | 828.5768 | 8.5 | 828.5768 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.7154 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 845.4865 | 0 | 169.0973 | 1.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 04:00 | 4 | 15 | 4 | 105 | 2500 | 64.04 | 979.6671 | 0 | 0 | 979.6671 | Heating | 864.4121 | 8.5 | 864.4121 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.8824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 882.0532 | 0 | 176.4106 | 1.764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 05:00 | 4 | 15 | 5 | 105 | 2501 | 64.04 | 1049.707 | 0 | 0 | 1049.707 | Heating | 926.2121 | 8.5 | 926.2121 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 185.2424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 945.1144 | 0 | 189.0229 | 1.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 06:00 | 4 | 15 | 6 | 105 | 2502 | 64.04 | 8677.4208 | 0 | 0 | 8677.4208 | Heating | 7656.5477 | 8.5 | 7656.5477 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1531.3095 | 30.63% | 1 | 61.25% | 0% | 0% | 0% | 26.3953 | 0 | 0 | 0 | 26.3953 | 7812.8038 | 0 | 1562.5608 | 15.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.6698
2007-04-15 07:00 | 4 | 15 | 7 | 105 | 2503 | 64.04 | 5971.8752 | 0 | 0 | 5971.8752 | Heating | 5269.3016 | 8.5 | 5269.3016 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1053.8603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5376.8384 | 0 | 1075.3677 | 10.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 08:00 | 4 | 15 | 8 | 105 | 2504 | 62.96 | 3921.5962 | 0 | 0 | 3921.5962 | Heating | 3460.232 | 8.5 | 3460.232 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 692.0464 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3530.8489 | 0 | 706.1698 | 7.062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 09:00 | 4 | 15 | 9 | 105 | 2505 | 62.96 | 1887.0163 | 0 | 0 | 1887.0163 | Heating | 1665.0144 | 8.5 | 1665.0144 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 333.0029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1698.9943 | 0 | 339.7989 | 3.398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 10:00 | 4 | 15 | 10 | 105 | 2506 | 64.94 | 508.5777 | 10.9113 | 10.9113 | 497.6664 | Heating | 439.1174 | 8.5 | 439.1174 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.8235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 448.079 | 0 | 89.6158 | 0.8962% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 11:00 | 4 | 15 | 11 | 105 | 2507 | 64.94 | 68.7412 | 52.1221 | 52.1221 | 16.6191 | Heating | 14.6639 | 8.5 | 14.6639 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.9328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.9632 | 0 | 2.9926 | 0.02993% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 12:00 | 4 | 15 | 12 | 105 | 2508 | 64.04 | 7.0344 | 924.9303 | 924.9303 | -917.8959 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1130.4704 | 1130.4704 | 0 | 8.5 | 0 | 188.4117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1107.8609 | 221.5722 | 2.216% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 13:00 | 4 | 15 | 13 | 105 | 2509 | 62.96 | 0 | 2354.6805 | 2354.6805 | -2354.6805 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2877.9428 | 2877.9428 | 0 | 8.5 | 0 | 479.6571 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2820.3839 | 564.0768 | 5.641% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 14:00 | 4 | 15 | 14 | 105 | 2510 | 57.02 | 0 | 3706.2001 | 3706.2001 | -3706.2001 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4529.8001 | 4529.8001 | 0 | 8.5 | 0 | 754.9667 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4439.2041 | 887.8408 | 8.878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 15:00 | 4 | 15 | 15 | 105 | 2511 | 42.98 | 0 | 4872.3198 | 4872.3198 | -4872.3198 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5955.0575 | 5955.0575 | 0 | 8.5 | 0 | 992.5096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5835.9564 | 1167.1913 | 11.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 16:00 | 4 | 15 | 16 | 105 | 2512 | 41 | 0 | 5356.6016 | 5356.6016 | -5356.6016 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6546.9575 | 6546.9575 | 0 | 8.5 | 0 | 1091.1596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6416.0184 | 1283.2037 | 12.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 17:00 | 4 | 15 | 17 | 105 | 2513 | 41 | 0 | 5349.8087 | 5349.8087 | -5349.8087 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6538.6551 | 6538.6551 | 0 | 8.5 | 0 | 1089.7758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6407.882 | 1281.5764 | 12.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 18:00 | 4 | 15 | 18 | 105 | 2514 | 35.96 | 0 | 3659.4704 | 3659.4704 | -3659.4704 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4472.686 | 4472.686 | 0 | 8.5 | 0 | 745.4477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4383.2323 | 876.6465 | 8.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 19:00 | 4 | 15 | 19 | 105 | 2515 | 33.98 | 0 | 2677.7349 | 2677.7349 | -2677.7349 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3272.7871 | 3272.7871 | 0 | 8.5 | 0 | 545.4645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3207.3314 | 641.4663 | 6.415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 20:00 | 4 | 15 | 20 | 105 | 2516 | 33.08 | 0 | 1754.2483 | 1754.2483 | -1754.2483 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2144.0813 | 2144.0813 | 0 | 8.5 | 0 | 357.3469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2101.1997 | 420.2399 | 4.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 21:00 | 4 | 15 | 21 | 105 | 2517 | 32 | 0 | 461.204 | 461.204 | -461.204 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 563.6937 | 563.6937 | 0 | 8.5 | 0 | 93.949 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 552.4199 | 110.484 | 1.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 22:00 | 4 | 15 | 22 | 105 | 2518 | 30.02 | 0 | 2.813 | 2.813 | -2.813 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3.4381 | 3.4381 | 0 | 8.5 | 0 | 0.57301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3.3693 | 0.67386 | 0.006739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-15 23:00 | 4 | 15 | 23 | 105 | 2519 | 28.94 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-04-16 | 4 | 16 | 0 | 106 | 2520 | 30.02 | 0.15932 | 0 | 0 | 0.15932 | Heating | 0.14058 | 8.5 | 0.14058 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.028115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.14345 | 0 | 0.028689 | 0.0002869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 01:00 | 4 | 16 | 1 | 106 | 2521 | 30.02 | 2.3543 | 0 | 0 | 2.3543 | Heating | 2.0773 | 8.5 | 2.0773 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.41546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.1197 | 0 | 0.42394 | 0.004239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 02:00 | 4 | 16 | 2 | 106 | 2522 | 30.02 | 7.8801 | 0 | 0 | 7.8801 | Heating | 6.953 | 8.5 | 6.953 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.0949 | 0 | 1.419 | 0.01419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 03:00 | 4 | 16 | 3 | 106 | 2523 | 28.94 | 11.7746 | 0 | 0 | 11.7746 | Heating | 10.3894 | 8.5 | 10.3894 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.6014 | 0 | 2.1203 | 0.0212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 04:00 | 4 | 16 | 4 | 106 | 2524 | 28.94 | 15.9156 | 0 | 0 | 15.9156 | Heating | 14.0432 | 8.5 | 14.0432 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.8086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.3298 | 0 | 2.866 | 0.02866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 05:00 | 4 | 16 | 5 | 106 | 2525 | 28.94 | 14.6578 | 0 | 0 | 14.6578 | Heating | 12.9334 | 8.5 | 12.9334 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.1973 | 0 | 2.6395 | 0.02639% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 06:00 | 4 | 16 | 6 | 106 | 2526 | 26.96 | 1028.092 | 117.4784 | 117.4784 | 910.6137 | Heating | 803.4826 | 8.5 | 803.4826 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.6965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 819.8803 | 0 | 163.9761 | 1.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 07:00 | 4 | 16 | 7 | 106 | 2527 | 26.96 | 654.1987 | 0 | 0 | 654.1987 | Heating | 577.2342 | 8.5 | 577.2342 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.4468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 589.0144 | 0 | 117.8029 | 1.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 08:00 | 4 | 16 | 8 | 106 | 2528 | 26.96 | 421.9497 | 133.6853 | 133.6853 | 288.2645 | Heating | 254.351 | 8.5 | 254.351 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.8702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 259.5419 | 0 | 51.9084 | 0.5191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 09:00 | 4 | 16 | 9 | 106 | 2529 | 30.02 | 628.709 | 107.1615 | 107.1615 | 521.5475 | Heating | 460.189 | 8.5 | 460.189 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.0378 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 469.5806 | 0 | 93.9161 | 0.9392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 10:00 | 4 | 16 | 10 | 106 | 2530 | 30.92 | 951.2372 | 96.2286 | 96.2286 | 855.0086 | Heating | 754.4194 | 8.5 | 754.4194 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.8839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 769.8157 | 0 | 153.9631 | 1.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 11:00 | 4 | 16 | 11 | 106 | 2531 | 30.92 | 834.4176 | 167.3943 | 167.3943 | 667.0233 | Heating | 588.5499 | 8.5 | 588.5499 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 117.71 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 600.5612 | 0 | 120.1122 | 1.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 12:00 | 4 | 16 | 12 | 106 | 2532 | 33.98 | 723.773 | 224.7789 | 224.7789 | 498.9942 | Heating | 440.289 | 8.5 | 440.289 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.0578 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 449.2745 | 0 | 89.8549 | 0.8985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 13:00 | 4 | 16 | 13 | 106 | 2533 | 37.04 | 383.3724 | 462.4699 | 462.4699 | -79.0974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 565.241 | 565.241 | 0 | 8.5 | 0 | 94.2068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 553.9361 | 110.7872 | 1.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 14:00 | 4 | 16 | 14 | 106 | 2534 | 37.04 | 136.5191 | 749.0692 | 749.0692 | -612.55 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 915.529 | 915.529 | 0 | 8.5 | 0 | 152.5882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 897.2184 | 179.4437 | 1.794% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 15:00 | 4 | 16 | 15 | 106 | 2535 | 41 | 59.0058 | 707.8627 | 707.8627 | -648.8569 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 865.1655 | 865.1655 | 0 | 8.5 | 0 | 144.1942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 847.8622 | 169.5724 | 1.696% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 16:00 | 4 | 16 | 16 | 106 | 2536 | 41 | 62.3527 | 483.0391 | 483.0391 | -420.6864 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 590.3811 | 590.3811 | 0 | 8.5 | 0 | 98.3968 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 578.5734 | 115.7147 | 1.157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 17:00 | 4 | 16 | 17 | 106 | 2537 | 41 | 83.0304 | 365.5095 | 365.5095 | -282.4791 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 446.7338 | 446.7338 | 0 | 8.5 | 0 | 74.4556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 437.7991 | 87.5598 | 0.8756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 18:00 | 4 | 16 | 18 | 106 | 2538 | 39.02 | 125.6333 | 206.2153 | 206.2153 | -80.582 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 252.0409 | 252.0409 | 0 | 8.5 | 0 | 42.0068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 247.0001 | 49.4 | 0.494% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 19:00 | 4 | 16 | 19 | 106 | 2539 | 35.96 | 432.0637 | 151.264 | 151.264 | 280.7997 | Heating | 247.7644 | 8.5 | 247.7644 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.5529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 252.8209 | 0 | 50.5642 | 0.5056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 20:00 | 4 | 16 | 20 | 106 | 2540 | 35.96 | 980.0397 | 39.6332 | 39.6332 | 940.4064 | Heating | 829.7704 | 8.5 | 829.7704 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.9541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 846.7045 | 0 | 169.3409 | 1.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 21:00 | 4 | 16 | 21 | 106 | 2541 | 33.08 | 208.0256 | 12.6038 | 12.6038 | 195.4218 | Heating | 172.431 | 8.5 | 172.431 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.4862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 175.95 | 0 | 35.19 | 0.3519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 22:00 | 4 | 16 | 22 | 106 | 2542 | 30.92 | 306.4868 | 0 | 0 | 306.4868 | Heating | 270.4295 | 8.5 | 270.4295 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.0859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 275.9485 | 0 | 55.1897 | 0.5519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-16 23:00 | 4 | 16 | 23 | 106 | 2543 | 30.92 | 400.4235 | 0 | 0 | 400.4235 | Heating | 353.3148 | 8.5 | 353.3148 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 360.5253 | 0 | 72.1051 | 0.7211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 | 4 | 17 | 0 | 107 | 2544 | 30.02 | 433.7504 | 0 | 0 | 433.7504 | Heating | 382.721 | 8.5 | 382.721 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.5442 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 390.5316 | 0 | 78.1063 | 0.7811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 01:00 | 4 | 17 | 1 | 107 | 2545 | 28.94 | 521.5356 | 0 | 0 | 521.5356 | Heating | 460.1785 | 8.5 | 460.1785 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.0357 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 469.5699 | 0 | 93.914 | 0.9391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 02:00 | 4 | 17 | 2 | 107 | 2546 | 28.94 | 611.2673 | 0 | 0 | 611.2673 | Heating | 539.3535 | 8.5 | 539.3535 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.8707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 550.3607 | 0 | 110.0721 | 1.101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 03:00 | 4 | 17 | 3 | 107 | 2547 | 28.04 | 678.4022 | 0 | 0 | 678.4022 | Heating | 598.5902 | 8.5 | 598.5902 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 610.8063 | 0 | 122.1613 | 1.222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 04:00 | 4 | 17 | 4 | 107 | 2548 | 26.96 | 681.8747 | 0 | 0 | 681.8747 | Heating | 601.6541 | 8.5 | 601.6541 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.3308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 613.9328 | 0 | 122.7866 | 1.228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 05:00 | 4 | 17 | 5 | 107 | 2549 | 26.96 | 677.043 | 0 | 0 | 677.043 | Heating | 597.3909 | 8.5 | 597.3909 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.4782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 609.5826 | 0 | 121.9165 | 1.219% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 06:00 | 4 | 17 | 6 | 107 | 2550 | 26.06 | 6772.5018 | 0 | 0 | 6772.5018 | Heating | 5975.7369 | 8.5 | 5975.7369 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1195.1474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6097.6907 | 0 | 1219.5381 | 12.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 07:00 | 4 | 17 | 7 | 107 | 2551 | 30.02 | 4564.5861 | 0 | 0 | 4564.5861 | Heating | 4027.5759 | 8.5 | 4027.5759 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 805.5152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4109.7714 | 0 | 821.9543 | 8.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 08:00 | 4 | 17 | 8 | 107 | 2552 | 30.02 | 3279.6616 | 0 | 0 | 3279.6616 | Heating | 2893.819 | 8.5 | 2893.819 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 578.7638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2952.8766 | 0 | 590.5753 | 5.906% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 09:00 | 4 | 17 | 9 | 107 | 2553 | 37.04 | 2213.4853 | 0.26234 | 0.26234 | 2213.223 | Heating | 1952.8438 | 8.5 | 1952.8438 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.5688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1992.6977 | 0 | 398.5395 | 3.985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 10:00 | 4 | 17 | 10 | 107 | 2554 | 39.02 | 1942.3952 | 0.85514 | 0.85514 | 1941.54 | Heating | 1713.1236 | 8.5 | 1713.1236 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 342.6247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1748.0853 | 0 | 349.6171 | 3.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 11:00 | 4 | 17 | 11 | 107 | 2555 | 39.02 | 1925.3392 | 0 | 0 | 1925.3392 | Heating | 1698.8287 | 8.5 | 1698.8287 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.7657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1733.4987 | 0 | 346.6997 | 3.467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 12:00 | 4 | 17 | 12 | 107 | 2556 | 44.96 | 1632.8627 | 0 | 0 | 1632.8627 | Heating | 1440.7612 | 8.5 | 1440.7612 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 288.1522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1470.1645 | 0 | 294.0329 | 2.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 13:00 | 4 | 17 | 13 | 107 | 2557 | 46.94 | 992.4407 | 17.5303 | 17.5303 | 974.9104 | Heating | 860.215 | 8.5 | 860.215 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 877.7705 | 0 | 175.5541 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 14:00 | 4 | 17 | 14 | 107 | 2558 | 46.94 | 811.5115 | 61.7289 | 61.7289 | 749.7826 | Heating | 661.5729 | 8.5 | 661.5729 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.3146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 675.0744 | 0 | 135.0149 | 1.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 15:00 | 4 | 17 | 15 | 107 | 2559 | 51.98 | 614.0556 | 94.3698 | 94.3698 | 519.6858 | Heating | 458.5463 | 8.5 | 458.5463 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.7093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 467.9044 | 0 | 93.5809 | 0.9358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 16:00 | 4 | 17 | 16 | 107 | 2560 | 53.06 | 598.0586 | 99.3047 | 99.3047 | 498.7539 | Heating | 440.077 | 8.5 | 440.077 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.0154 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 449.0581 | 0 | 89.8116 | 0.8981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 17:00 | 4 | 17 | 17 | 107 | 2561 | 53.06 | 883.54 | 58.996 | 58.996 | 824.544 | Heating | 727.5388 | 8.5 | 727.5388 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.5078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 742.3865 | 0 | 148.4773 | 1.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 18:00 | 4 | 17 | 18 | 107 | 2562 | 50 | 1121.9997 | 12.1597 | 12.1597 | 1109.8401 | Heating | 979.2706 | 8.5 | 979.2706 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.8541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 999.2558 | 0 | 199.8512 | 1.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 19:00 | 4 | 17 | 19 | 107 | 2563 | 48.02 | 1598.7605 | 1.9847 | 1.9847 | 1596.7758 | Heating | 1408.9199 | 8.5 | 1408.9199 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 281.784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1437.6733 | 0 | 287.5347 | 2.875% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 20:00 | 4 | 17 | 20 | 107 | 2564 | 48.02 | 1961.5358 | 0 | 0 | 1961.5358 | Heating | 1730.7669 | 8.5 | 1730.7669 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.1534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1766.0886 | 0 | 353.2177 | 3.532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 21:00 | 4 | 17 | 21 | 107 | 2565 | 44.06 | 498.1788 | 0 | 0 | 498.1788 | Heating | 439.5695 | 8.5 | 439.5695 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.9139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 448.5404 | 0 | 89.7081 | 0.8971% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 22:00 | 4 | 17 | 22 | 107 | 2566 | 42.08 | 580.0858 | 0 | 0 | 580.0858 | Heating | 511.8404 | 8.5 | 511.8404 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.3681 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 522.2862 | 0 | 104.4572 | 1.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-17 23:00 | 4 | 17 | 23 | 107 | 2567 | 42.08 | 669.8999 | 0 | 0 | 669.8999 | Heating | 591.0882 | 8.5 | 591.0882 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.2176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 603.1512 | 0 | 120.6302 | 1.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 | 4 | 18 | 0 | 108 | 2568 | 37.94 | 745.8375 | 0 | 0 | 745.8375 | Heating | 658.0919 | 8.5 | 658.0919 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.6184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 671.5223 | 0 | 134.3045 | 1.343% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 01:00 | 4 | 18 | 1 | 108 | 2569 | 35.96 | 770.8671 | 0 | 0 | 770.8671 | Heating | 680.1769 | 8.5 | 680.1769 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.0354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 694.0581 | 0 | 138.8116 | 1.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 02:00 | 4 | 18 | 2 | 108 | 2570 | 35.96 | 801.1628 | 0 | 0 | 801.1628 | Heating | 706.9084 | 8.5 | 706.9084 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.3817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 721.3351 | 0 | 144.267 | 1.443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 03:00 | 4 | 18 | 3 | 108 | 2571 | 33.08 | 845.3757 | 0 | 0 | 845.3757 | Heating | 745.9197 | 8.5 | 745.9197 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.1839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 761.1426 | 0 | 152.2285 | 1.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 04:00 | 4 | 18 | 4 | 108 | 2572 | 30.92 | 874.1647 | 0 | 0 | 874.1647 | Heating | 771.3218 | 8.5 | 771.3218 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.2644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 787.0631 | 0 | 157.4126 | 1.574% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 05:00 | 4 | 18 | 5 | 108 | 2573 | 30.92 | 907.446 | 0 | 0 | 907.446 | Heating | 800.6877 | 8.5 | 800.6877 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.1375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 817.0282 | 0 | 163.4056 | 1.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 06:00 | 4 | 18 | 6 | 108 | 2574 | 30.02 | 8111.2284 | 0 | 0 | 8111.2284 | Heating | 7156.9662 | 8.5 | 7156.9662 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1431.3932 | 30% | 1 | 57.26% | 0% | 0% | 0% | 22.6009 | 0 | 0 | 0 | 22.6009 | 7303.0268 | 0 | 1460.6054 | 14.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.8755
2007-04-18 07:00 | 4 | 18 | 7 | 108 | 2575 | 33.98 | 5872.7099 | 0 | 0 | 5872.7099 | Heating | 5181.8028 | 8.5 | 5181.8028 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1036.3606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5287.5539 | 0 | 1057.5108 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 08:00 | 4 | 18 | 8 | 108 | 2576 | 33.98 | 4172.7606 | 0 | 0 | 4172.7606 | Heating | 3681.8475 | 8.5 | 3681.8475 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 736.3695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3756.9873 | 0 | 751.3975 | 7.514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 09:00 | 4 | 18 | 9 | 108 | 2577 | 41 | 2620.135 | 1.9074 | 1.9074 | 2618.2277 | Heating | 2310.2009 | 8.5 | 2310.2009 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 462.0402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2357.3479 | 0 | 471.4696 | 4.715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 10:00 | 4 | 18 | 10 | 108 | 2578 | 42.98 | 1883.3535 | 6.2968 | 6.2968 | 1877.0567 | Heating | 1656.2265 | 8.5 | 1656.2265 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 331.2453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1690.027 | 0 | 338.0054 | 3.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 11:00 | 4 | 18 | 11 | 108 | 2579 | 42.98 | 1294.2314 | 5.4542 | 5.4542 | 1288.7773 | Heating | 1137.1564 | 8.5 | 1137.1564 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 227.4313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1160.3637 | 0 | 232.0727 | 2.321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 12:00 | 4 | 18 | 12 | 108 | 2580 | 46.94 | 990.8401 | 13.7133 | 13.7133 | 977.1267 | Heating | 862.1707 | 8.5 | 862.1707 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.4341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 879.766 | 0 | 175.9532 | 1.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 13:00 | 4 | 18 | 13 | 108 | 2581 | 48.02 | 541.05 | 69.8644 | 69.8644 | 471.1856 | Heating | 415.752 | 8.5 | 415.752 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.1504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 424.2367 | 0 | 84.8473 | 0.8485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 14:00 | 4 | 18 | 14 | 108 | 2582 | 48.02 | 296.2548 | 158.8721 | 158.8721 | 137.3827 | Heating | 121.22 | 8.5 | 121.22 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 123.6939 | 0 | 24.7388 | 0.2474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 15:00 | 4 | 18 | 15 | 108 | 2583 | 50 | 240.9549 | 181.0085 | 181.0085 | 59.9464 | Heating | 52.8939 | 8.5 | 52.8939 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.5788 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 53.9733 | 0 | 10.7947 | 0.1079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 16:00 | 4 | 18 | 16 | 108 | 2584 | 50 | 198.5117 | 207.9172 | 207.9172 | -9.4055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 254.121 | 254.121 | 0 | 8.5 | 0 | 42.3535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 249.0386 | 49.8077 | 0.4981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 17:00 | 4 | 18 | 17 | 108 | 2585 | 50 | 172.4781 | 189.4274 | 189.4274 | -16.9493 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 231.5224 | 231.5224 | 0 | 8.5 | 0 | 38.5871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 226.8919 | 45.3784 | 0.4538% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 18:00 | 4 | 18 | 18 | 108 | 2586 | 48.92 | 177.852 | 127.1514 | 127.1514 | 50.7006 | Heating | 44.7358 | 8.5 | 44.7358 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.9472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 45.6488 | 0 | 9.1298 | 0.0913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 19:00 | 4 | 18 | 19 | 108 | 2587 | 48.02 | 701.7594 | 78.0806 | 78.0806 | 623.6788 | Heating | 550.3048 | 8.5 | 550.3048 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 561.5355 | 0 | 112.3071 | 1.123% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 20:00 | 4 | 18 | 20 | 108 | 2588 | 48.02 | 1535.7529 | 13.9037 | 13.9037 | 1521.8492 | Heating | 1342.8081 | 8.5 | 1342.8081 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.5616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1370.2123 | 0 | 274.0425 | 2.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 21:00 | 4 | 18 | 21 | 108 | 2589 | 44.96 | 449.9401 | 3.2196 | 3.2196 | 446.7205 | Heating | 394.1652 | 8.5 | 394.1652 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 402.2094 | 0 | 80.4419 | 0.8044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 22:00 | 4 | 18 | 22 | 108 | 2590 | 44.06 | 532.6091 | 0 | 0 | 532.6091 | Heating | 469.9492 | 8.5 | 469.9492 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.9898 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 479.54 | 0 | 95.908 | 0.9591% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-18 23:00 | 4 | 18 | 23 | 108 | 2591 | 44.06 | 616.448 | 0 | 0 | 616.448 | Heating | 543.9247 | 8.5 | 543.9247 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.7849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 555.0252 | 0 | 111.005 | 1.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 | 4 | 19 | 0 | 109 | 2592 | 41 | 677.1933 | 0 | 0 | 677.1933 | Heating | 597.5235 | 8.5 | 597.5235 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.5047 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 609.7178 | 0 | 121.9436 | 1.219% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 01:00 | 4 | 19 | 1 | 109 | 2593 | 42.98 | 620.2518 | 0 | 0 | 620.2518 | Heating | 547.281 | 8.5 | 547.281 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.4562 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 558.45 | 0 | 111.69 | 1.117% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 02:00 | 4 | 19 | 2 | 109 | 2594 | 42.98 | 533.6341 | 0 | 0 | 533.6341 | Heating | 470.8536 | 8.5 | 470.8536 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.1707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 480.4629 | 0 | 96.0926 | 0.9609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 03:00 | 4 | 19 | 3 | 109 | 2595 | 37.4 | 545.1116 | 0 | 0 | 545.1116 | Heating | 480.9808 | 8.5 | 480.9808 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.1962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 490.7967 | 0 | 98.1593 | 0.9816% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 04:00 | 4 | 19 | 4 | 109 | 2596 | 39.02 | 569.6687 | 0 | 0 | 569.6687 | Heating | 502.6489 | 8.5 | 502.6489 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.5298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 512.907 | 0 | 102.5814 | 1.026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 05:00 | 4 | 19 | 5 | 109 | 2597 | 35.96 | 536.8663 | 0 | 0 | 536.8663 | Heating | 473.7056 | 8.5 | 473.7056 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.7411 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 483.373 | 0 | 96.6746 | 0.9667% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 06:00 | 4 | 19 | 6 | 109 | 2598 | 42.98 | 5222.3628 | 31.9927 | 31.9927 | 5190.3702 | Heating | 4579.7384 | 8.5 | 4579.7384 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 915.9477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4673.2024 | 0 | 934.6405 | 9.346% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 07:00 | 4 | 19 | 7 | 109 | 2599 | 44.96 | 3257.946 | 0 | 0 | 3257.946 | Heating | 2874.6582 | 8.5 | 2874.6582 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 574.9316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2933.3247 | 0 | 586.6649 | 5.867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 08:00 | 4 | 19 | 8 | 109 | 2600 | 44.96 | 2200.4153 | 1.9288 | 1.9288 | 2198.4864 | Heating | 1939.841 | 8.5 | 1939.841 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.9682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1979.4295 | 0 | 395.8859 | 3.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 09:00 | 4 | 19 | 9 | 109 | 2601 | 50 | 947.2426 | 24.994 | 24.994 | 922.2486 | Heating | 813.7487 | 8.5 | 813.7487 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.7497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 830.3558 | 0 | 166.0712 | 1.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 10:00 | 4 | 19 | 10 | 109 | 2602 | 51.98 | 553.5929 | 43.8572 | 43.8572 | 509.7357 | Heating | 449.7668 | 8.5 | 449.7668 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 89.9534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 458.9457 | 0 | 91.7891 | 0.9179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 11:00 | 4 | 19 | 11 | 109 | 2603 | 51.98 | 165.1119 | 156.8401 | 156.8401 | 8.2717 | Heating | 7.2986 | 8.5 | 7.2986 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.4475 | 0 | 1.4895 | 0.0149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 12:00 | 4 | 19 | 12 | 109 | 2604 | 55.94 | 59.0053 | 370.7296 | 370.7296 | -311.7243 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 453.114 | 453.114 | 0 | 8.5 | 0 | 75.519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 444.0517 | 88.8103 | 0.8881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 13:00 | 4 | 19 | 13 | 109 | 2605 | 57.02 | 20.016 | 928.1391 | 928.1391 | -908.1231 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1134.3922 | 1134.3922 | 0 | 8.5 | 0 | 189.0654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1111.7043 | 222.3409 | 2.223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 14:00 | 4 | 19 | 14 | 109 | 2606 | 57.02 | 40.273 | 737.2062 | 737.2062 | -696.9332 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 901.0297 | 901.0297 | 0 | 8.5 | 0 | 150.1716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 883.0092 | 176.6018 | 1.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 15:00 | 4 | 19 | 15 | 109 | 2607 | 60.08 | 47.1794 | 551.7551 | 551.7551 | -504.5757 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 674.3674 | 674.3674 | 0 | 8.5 | 0 | 112.3946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 660.88 | 132.176 | 1.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 16:00 | 4 | 19 | 16 | 109 | 2608 | 60.08 | 36.4557 | 399.5495 | 399.5495 | -363.0938 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 488.3383 | 488.3383 | 0 | 8.5 | 0 | 81.3897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 478.5716 | 95.7143 | 0.9571% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 17:00 | 4 | 19 | 17 | 109 | 2609 | 60.08 | 43.4624 | 281.189 | 281.189 | -237.7266 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 343.6754 | 343.6754 | 0 | 8.5 | 0 | 57.2792 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 336.8019 | 67.3604 | 0.6736% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 18:00 | 4 | 19 | 18 | 109 | 2610 | 55.94 | 26.7284 | 182.3427 | 182.3427 | -155.6143 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 222.8633 | 222.8633 | 0 | 8.5 | 0 | 37.1439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 218.406 | 43.6812 | 0.4368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 19:00 | 4 | 19 | 19 | 109 | 2611 | 51.08 | 38.4248 | 148.5042 | 148.5042 | -110.0794 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 181.5052 | 181.5052 | 0 | 8.5 | 0 | 30.2509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 177.8751 | 35.575 | 0.3558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 20:00 | 4 | 19 | 20 | 109 | 2612 | 51.08 | 137.5876 | 48.0854 | 48.0854 | 89.5022 | Heating | 78.9726 | 8.5 | 78.9726 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.7945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 80.5842 | 0 | 16.1168 | 0.1612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 21:00 | 4 | 19 | 21 | 109 | 2613 | 46.04 | 155.3466 | 10.8518 | 10.8518 | 144.4948 | Heating | 127.4954 | 8.5 | 127.4954 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.4991 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 130.0974 | 0 | 26.0195 | 0.2602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 22:00 | 4 | 19 | 22 | 109 | 2614 | 44.96 | 234.9703 | 0 | 0 | 234.9703 | Heating | 207.3268 | 8.5 | 207.3268 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.4654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 211.5579 | 0 | 42.3116 | 0.4231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-19 23:00 | 4 | 19 | 23 | 109 | 2615 | 44.96 | 302.1112 | 0 | 0 | 302.1112 | Heating | 266.5687 | 8.5 | 266.5687 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.3137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 272.0089 | 0 | 54.4018 | 0.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 | 4 | 20 | 0 | 110 | 2616 | 42.08 | 374.076 | 0 | 0 | 374.076 | Heating | 330.067 | 8.5 | 330.067 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 66.0134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 336.8031 | 0 | 67.3606 | 0.6736% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 01:00 | 4 | 20 | 1 | 110 | 2617 | 41 | 443.7461 | 0 | 0 | 443.7461 | Heating | 391.5407 | 8.5 | 391.5407 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.3081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 399.5313 | 0 | 79.9063 | 0.7991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 02:00 | 4 | 20 | 2 | 110 | 2618 | 41 | 497.1193 | 0 | 0 | 497.1193 | Heating | 438.6347 | 8.5 | 438.6347 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.7269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 447.5864 | 0 | 89.5173 | 0.8952% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 03:00 | 4 | 20 | 3 | 110 | 2619 | 33.08 | 606.7373 | 0 | 0 | 606.7373 | Heating | 535.3564 | 8.5 | 535.3564 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.0713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 546.2821 | 0 | 109.2564 | 1.093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 04:00 | 4 | 20 | 4 | 110 | 2620 | 33.08 | 647.1103 | 0 | 0 | 647.1103 | Heating | 570.9797 | 8.5 | 570.9797 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.1959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 582.6323 | 0 | 116.5265 | 1.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 05:00 | 4 | 20 | 5 | 110 | 2621 | 33.08 | 618.4969 | 0 | 0 | 618.4969 | Heating | 545.7325 | 8.5 | 545.7325 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.1465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 556.8699 | 0 | 111.374 | 1.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 06:00 | 4 | 20 | 6 | 110 | 2622 | 30.92 | 5885.7924 | 0 | 0 | 5885.7924 | Heating | 5193.3462 | 8.5 | 5193.3462 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1038.6692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5299.3329 | 0 | 1059.8666 | 10.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 07:00 | 4 | 20 | 7 | 110 | 2623 | 39.92 | 4169.1032 | 0 | 0 | 4169.1032 | Heating | 3678.6204 | 8.5 | 3678.6204 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 735.7241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3753.6943 | 0 | 750.7389 | 7.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 08:00 | 4 | 20 | 8 | 110 | 2624 | 39.92 | 3567.1241 | 0 | 0 | 3567.1241 | Heating | 3147.4624 | 8.5 | 3147.4624 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 629.4925 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3211.6964 | 0 | 642.3393 | 6.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 09:00 | 4 | 20 | 9 | 110 | 2625 | 48.92 | 2635.9228 | 0.22311 | 0.22311 | 2635.6997 | Heating | 2325.6174 | 8.5 | 2325.6174 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 465.1235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2373.079 | 0 | 474.6158 | 4.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 10:00 | 4 | 20 | 10 | 110 | 2626 | 50 | 1778.761 | 2.4718 | 2.4718 | 1776.2892 | Heating | 1567.314 | 8.5 | 1567.314 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.4628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1599.3 | 0 | 319.86 | 3.199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 11:00 | 4 | 20 | 11 | 110 | 2627 | 50 | 1253.4103 | 0.44543 | 0.44543 | 1252.9649 | Heating | 1105.5573 | 8.5 | 1105.5573 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.1115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1128.1197 | 0 | 225.6239 | 2.256% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 12:00 | 4 | 20 | 12 | 110 | 2628 | 55.94 | 910.7995 | 3.817 | 3.817 | 906.9825 | Heating | 800.2787 | 8.5 | 800.2787 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.0557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 816.6109 | 0 | 163.3222 | 1.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 13:00 | 4 | 20 | 13 | 110 | 2629 | 57.92 | 676.17 | 3.2871 | 3.2871 | 672.8829 | Heating | 593.7202 | 8.5 | 593.7202 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 605.837 | 0 | 121.1674 | 1.212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 14:00 | 4 | 20 | 14 | 110 | 2630 | 57.92 | 549.7808 | 0 | 0 | 549.7808 | Heating | 485.1007 | 8.5 | 485.1007 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 97.0201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 495.0007 | 0 | 99.0001 | 0.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 15:00 | 4 | 20 | 15 | 110 | 2631 | 62.06 | 486.4015 | 0 | 0 | 486.4015 | Heating | 429.1778 | 8.5 | 429.1778 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.8356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 437.9365 | 0 | 87.5873 | 0.8759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 16:00 | 4 | 20 | 16 | 110 | 2632 | 62.06 | 525.9501 | 0 | 0 | 525.9501 | Heating | 464.0737 | 8.5 | 464.0737 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.8147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 473.5445 | 0 | 94.7089 | 0.9471% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 17:00 | 4 | 20 | 17 | 110 | 2633 | 62.06 | 661.0097 | 2.097 | 2.097 | 658.9127 | Heating | 581.3935 | 8.5 | 581.3935 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.2787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 593.2587 | 0 | 118.6517 | 1.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 18:00 | 4 | 20 | 18 | 110 | 2634 | 62.06 | 1352.8901 | 0 | 0 | 1352.8901 | Heating | 1193.7265 | 8.5 | 1193.7265 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.7453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1218.0883 | 0 | 243.6177 | 2.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 19:00 | 4 | 20 | 19 | 110 | 2635 | 59 | 1948.1649 | 0 | 0 | 1948.1649 | Heating | 1718.9691 | 8.5 | 1718.9691 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.7938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1754.0501 | 0 | 350.81 | 3.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 20:00 | 4 | 20 | 20 | 110 | 2636 | 59 | 2369.7517 | 0 | 0 | 2369.7517 | Heating | 2090.9574 | 8.5 | 2090.9574 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 418.1915 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2133.63 | 0 | 426.726 | 4.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 21:00 | 4 | 20 | 21 | 110 | 2637 | 55.94 | 2947.5806 | 0 | 0 | 2947.5806 | Heating | 2600.8064 | 8.5 | 2600.8064 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 520.1613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2653.8841 | 0 | 530.7768 | 5.308% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 22:00 | 4 | 20 | 22 | 110 | 2638 | 53.06 | 637.7336 | 0 | 0 | 637.7336 | Heating | 562.7062 | 8.5 | 562.7062 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.5412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 574.19 | 0 | 114.838 | 1.148% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-20 23:00 | 4 | 20 | 23 | 110 | 2639 | 53.06 | 743.4437 | 0 | 0 | 743.4437 | Heating | 655.9798 | 8.5 | 655.9798 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 669.3671 | 0 | 133.8734 | 1.339% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 | 4 | 21 | 0 | 111 | 2640 | 48.02 | 891.7306 | 0 | 0 | 891.7306 | Heating | 786.8212 | 8.5 | 786.8212 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.3642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 802.8787 | 0 | 160.5757 | 1.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 01:00 | 4 | 21 | 1 | 111 | 2641 | 46.04 | 1067.8919 | 0 | 0 | 1067.8919 | Heating | 942.2575 | 8.5 | 942.2575 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.4515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 961.4873 | 0 | 192.2975 | 1.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 02:00 | 4 | 21 | 2 | 111 | 2642 | 46.04 | 1130.7997 | 0 | 0 | 1130.7997 | Heating | 997.7645 | 8.5 | 997.7645 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.5529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1018.127 | 0 | 203.6254 | 2.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 03:00 | 4 | 21 | 3 | 111 | 2643 | 44.06 | 1147.8424 | 0 | 0 | 1147.8424 | Heating | 1012.8022 | 8.5 | 1012.8022 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.5604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1033.4716 | 0 | 206.6943 | 2.067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 04:00 | 4 | 21 | 4 | 111 | 2644 | 42.98 | 1118.7006 | 0 | 0 | 1118.7006 | Heating | 987.0888 | 8.5 | 987.0888 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 197.4178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1007.2334 | 0 | 201.4467 | 2.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 05:00 | 4 | 21 | 5 | 111 | 2645 | 42.98 | 1123.8293 | 0 | 0 | 1123.8293 | Heating | 991.6141 | 8.5 | 991.6141 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 198.3228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1011.8511 | 0 | 202.3702 | 2.024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 06:00 | 4 | 21 | 6 | 111 | 2646 | 41 | 1117.6403 | 0 | 0 | 1117.6403 | Heating | 986.1532 | 8.5 | 986.1532 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 197.2306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1006.2788 | 0 | 201.2558 | 2.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 07:00 | 4 | 21 | 7 | 111 | 2647 | 44.96 | 1015.6317 | 0 | 0 | 1015.6317 | Heating | 896.1456 | 8.5 | 896.1456 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 179.2291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 914.4343 | 0 | 182.8869 | 1.829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 08:00 | 4 | 21 | 8 | 111 | 2648 | 44.96 | 7295.1091 | 0 | 0 | 7295.1091 | Heating | 6436.861 | 8.5 | 6436.861 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1287.3722 | 30% | 1 | 51.49% | 0% | 0% | 0% | 17.7093 | 0 | 0 | 0 | 17.7093 | 6568.2255 | 0 | 1313.6451 | 13.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.9838
2007-04-21 09:00 | 4 | 21 | 9 | 111 | 2649 | 50 | 4948.3311 | 0 | 0 | 4948.3311 | Heating | 4366.1745 | 8.5 | 4366.1745 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 873.2349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4455.2801 | 0 | 891.056 | 8.911% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 10:00 | 4 | 21 | 10 | 111 | 2650 | 55.04 | 3539.1919 | 0 | 0 | 3539.1919 | Heating | 3122.8164 | 8.5 | 3122.8164 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 624.5633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3186.5474 | 0 | 637.3095 | 6.373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 11:00 | 4 | 21 | 11 | 111 | 2651 | 55.04 | 2661.976 | 0 | 0 | 2661.976 | Heating | 2348.8023 | 8.5 | 2348.8023 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 469.7605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2396.7371 | 0 | 479.3474 | 4.793% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 12:00 | 4 | 21 | 12 | 111 | 2652 | 62.96 | 1908.7436 | 0 | 0 | 1908.7436 | Heating | 1684.1855 | 8.5 | 1684.1855 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.8371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1718.5567 | 0 | 343.7113 | 3.437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 13:00 | 4 | 21 | 13 | 111 | 2653 | 66.92 | 1508.2351 | 0 | 0 | 1508.2351 | Heating | 1330.7957 | 8.5 | 1330.7957 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.1591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1357.9548 | 0 | 271.591 | 2.716% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 14:00 | 4 | 21 | 14 | 111 | 2654 | 66.92 | 1369.5953 | 0 | 0 | 1369.5953 | Heating | 1208.4664 | 8.5 | 1208.4664 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 241.6933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1233.129 | 0 | 246.6258 | 2.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 15:00 | 4 | 21 | 15 | 111 | 2655 | 71.06 | 1427.4319 | 0 | 0 | 1427.4319 | Heating | 1259.4987 | 8.5 | 1259.4987 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.8997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1285.2028 | 0 | 257.0406 | 2.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 16:00 | 4 | 21 | 16 | 111 | 2656 | 71.96 | 1426.0647 | 0 | 0 | 1426.0647 | Heating | 1258.2924 | 8.5 | 1258.2924 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.6585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1283.9718 | 0 | 256.7944 | 2.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 17:00 | 4 | 21 | 17 | 111 | 2657 | 71.96 | 2472.6573 | 0 | 0 | 2472.6573 | Heating | 2181.7564 | 8.5 | 2181.7564 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 436.3513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2226.2821 | 0 | 445.2564 | 4.453% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 18:00 | 4 | 21 | 18 | 111 | 2658 | 69.08 | 2776.4501 | 0 | 0 | 2776.4501 | Heating | 2449.8089 | 8.5 | 2449.8089 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 489.9618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2499.805 | 0 | 499.961 | 5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 19:00 | 4 | 21 | 19 | 111 | 2659 | 66.92 | 429.3928 | 0 | 0 | 429.3928 | Heating | 378.876 | 8.5 | 378.876 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.7752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 386.6081 | 0 | 77.3216 | 0.7732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 20:00 | 4 | 21 | 20 | 111 | 2660 | 66.92 | 530.7911 | 0 | 0 | 530.7911 | Heating | 468.3451 | 8.5 | 468.3451 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 477.9031 | 0 | 95.5806 | 0.9558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 21:00 | 4 | 21 | 21 | 111 | 2661 | 64.94 | 605.8637 | 0 | 0 | 605.8637 | Heating | 534.5856 | 8.5 | 534.5856 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.9171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 545.4955 | 0 | 109.0991 | 1.091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 22:00 | 4 | 21 | 22 | 111 | 2662 | 62.06 | 728.092 | 0 | 0 | 728.092 | Heating | 642.4341 | 8.5 | 642.4341 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.4868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 655.545 | 0 | 131.109 | 1.311% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-21 23:00 | 4 | 21 | 23 | 111 | 2663 | 62.06 | 885.3022 | 0 | 0 | 885.3022 | Heating | 781.149 | 8.5 | 781.149 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.2298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 797.0908 | 0 | 159.4182 | 1.594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 | 4 | 22 | 0 | 112 | 2664 | 60.08 | 1068.1191 | 0 | 0 | 1068.1191 | Heating | 942.458 | 8.5 | 942.458 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.4916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 961.6918 | 0 | 192.3384 | 1.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 01:00 | 4 | 22 | 1 | 112 | 2665 | 57.92 | 1294.7405 | 0 | 0 | 1294.7405 | Heating | 1142.4181 | 8.5 | 1142.4181 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 228.4836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1165.7328 | 0 | 233.1466 | 2.331% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 02:00 | 4 | 22 | 2 | 112 | 2666 | 57.92 | 1355.2255 | 0 | 0 | 1355.2255 | Heating | 1195.7872 | 8.5 | 1195.7872 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 239.1574 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1220.1911 | 0 | 244.0382 | 2.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 03:00 | 4 | 22 | 3 | 112 | 2667 | 55.04 | 1353.9153 | 0 | 0 | 1353.9153 | Heating | 1194.6312 | 8.5 | 1194.6312 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.9262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1219.0114 | 0 | 243.8023 | 2.438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 04:00 | 4 | 22 | 4 | 112 | 2668 | 53.06 | 1410.4275 | 0 | 0 | 1410.4275 | Heating | 1244.4949 | 8.5 | 1244.4949 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1269.8927 | 0 | 253.9785 | 2.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 05:00 | 4 | 22 | 5 | 112 | 2669 | 53.06 | 1440.6814 | 0 | 0 | 1440.6814 | Heating | 1271.1894 | 8.5 | 1271.1894 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.2379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1297.1321 | 0 | 259.4264 | 2.594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 06:00 | 4 | 22 | 6 | 112 | 2670 | 51.98 | 9493.1625 | 0 | 0 | 9493.1625 | Heating | 8376.3199 | 8.5 | 8376.3199 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1675.264 | 33.51% | 1 | 67.01% | 0% | 0% | 0% | 32.4543 | 0 | 0 | 0 | 32.4543 | 8547.2652 | 0 | 1709.453 | 17.09% | 1 | 34.19% | 0% | 0% | 3.4519 | 0 | 0 | 3.4519 | 35.9062
2007-04-22 07:00 | 4 | 22 | 7 | 112 | 2671 | 53.96 | 6682.7125 | 0 | 0 | 6682.7125 | Heating | 5896.511 | 8.5 | 5896.511 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1179.3022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6016.848 | 0 | 1203.3696 | 12.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 08:00 | 4 | 22 | 8 | 112 | 2672 | 53.96 | 4910.3003 | 0 | 0 | 4910.3003 | Heating | 4332.6179 | 8.5 | 4332.6179 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 866.5236 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4421.0387 | 0 | 884.2077 | 8.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 09:00 | 4 | 22 | 9 | 112 | 2673 | 55.94 | 3333.6585 | 0 | 0 | 3333.6585 | Heating | 2941.4633 | 8.5 | 2941.4633 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 588.2927 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3001.4932 | 0 | 600.2986 | 6.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 10:00 | 4 | 22 | 10 | 112 | 2674 | 59 | 2501.3356 | 0 | 0 | 2501.3356 | Heating | 2207.0608 | 8.5 | 2207.0608 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 441.4122 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2252.1029 | 0 | 450.4206 | 4.504% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 11:00 | 4 | 22 | 11 | 112 | 2675 | 59 | 1955.1599 | 0 | 0 | 1955.1599 | Heating | 1725.1411 | 8.5 | 1725.1411 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 345.0282 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1760.348 | 0 | 352.0696 | 3.521% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 12:00 | 4 | 22 | 12 | 112 | 2676 | 66.92 | 1382.4657 | 0.53805 | 0.53805 | 1381.9277 | Heating | 1219.348 | 8.5 | 1219.348 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 243.8696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1244.2326 | 0 | 248.8465 | 2.488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 13:00 | 4 | 22 | 13 | 112 | 2677 | 69.08 | 977.8822 | 7.6586 | 7.6586 | 970.2236 | Heating | 856.0796 | 8.5 | 856.0796 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.2159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 873.5506 | 0 | 174.7101 | 1.747% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 14:00 | 4 | 22 | 14 | 112 | 2678 | 69.08 | 727.8 | 20.9026 | 20.9026 | 706.8974 | Heating | 623.733 | 8.5 | 623.733 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.7466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 636.4622 | 0 | 127.2924 | 1.273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 15:00 | 4 | 22 | 15 | 112 | 2679 | 62.96 | 548.3925 | 24.8645 | 24.8645 | 523.528 | Heating | 461.9365 | 8.5 | 461.9365 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.3873 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 471.3638 | 0 | 94.2728 | 0.9427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 16:00 | 4 | 22 | 16 | 112 | 2680 | 62.96 | 571.9324 | 43.7226 | 43.7226 | 528.2098 | Heating | 466.0675 | 8.5 | 466.0675 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.2135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 475.5791 | 0 | 95.1158 | 0.9512% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 17:00 | 4 | 22 | 17 | 112 | 2681 | 62.96 | 775.914 | 21.4609 | 21.4609 | 754.4531 | Heating | 665.6939 | 8.5 | 665.6939 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.1388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 679.2795 | 0 | 135.8559 | 1.359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 18:00 | 4 | 22 | 18 | 112 | 2682 | 59 | 1156.6442 | 9.6071 | 9.6071 | 1147.0371 | Heating | 1012.0916 | 8.5 | 1012.0916 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.4183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1032.7465 | 0 | 206.5493 | 2.065% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 19:00 | 4 | 22 | 19 | 112 | 2683 | 57.92 | 1560.0841 | 2.9908 | 2.9908 | 1557.0932 | Heating | 1373.9058 | 8.5 | 1373.9058 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.7812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1401.9447 | 0 | 280.3889 | 2.804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 20:00 | 4 | 22 | 20 | 112 | 2684 | 57.92 | 1965.0601 | 0 | 0 | 1965.0601 | Heating | 1733.8766 | 8.5 | 1733.8766 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.7753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1769.2618 | 0 | 353.8524 | 3.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 21:00 | 4 | 22 | 21 | 112 | 2685 | 55.94 | 564.6138 | 0 | 0 | 564.6138 | Heating | 498.1887 | 8.5 | 498.1887 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.6377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 508.3558 | 0 | 101.6712 | 1.017% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 22:00 | 4 | 22 | 22 | 112 | 2686 | 55.94 | 641.6356 | 0 | 0 | 641.6356 | Heating | 566.1491 | 8.5 | 566.1491 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.2298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 577.7032 | 0 | 115.5406 | 1.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-22 23:00 | 4 | 22 | 23 | 112 | 2687 | 55.94 | 708.2964 | 0 | 0 | 708.2964 | Heating | 624.9674 | 8.5 | 624.9674 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.9935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 637.7218 | 0 | 127.5444 | 1.275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 | 4 | 23 | 0 | 113 | 2688 | 51.08 | 793.6207 | 0 | 0 | 793.6207 | Heating | 700.2535 | 8.5 | 700.2535 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 140.0507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 714.5444 | 0 | 142.9089 | 1.429% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 01:00 | 4 | 23 | 1 | 113 | 2689 | 48.92 | 845.776 | 0 | 0 | 845.776 | Heating | 746.2729 | 8.5 | 746.2729 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.2546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 761.503 | 0 | 152.3006 | 1.523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 02:00 | 4 | 23 | 2 | 113 | 2690 | 48.02 | 911.8416 | 0 | 0 | 911.8416 | Heating | 804.5661 | 8.5 | 804.5661 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.9132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 820.9858 | 0 | 164.1972 | 1.642% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 03:00 | 4 | 23 | 3 | 113 | 2691 | 46.04 | 1005.7088 | 0 | 0 | 1005.7088 | Heating | 887.3901 | 8.5 | 887.3901 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 905.5001 | 0 | 181.1 | 1.811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 04:00 | 4 | 23 | 4 | 113 | 2692 | 46.04 | 1160.5843 | 0 | 0 | 1160.5843 | Heating | 1024.045 | 8.5 | 1024.045 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 204.809 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1044.9439 | 0 | 208.9888 | 2.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 05:00 | 4 | 23 | 5 | 113 | 2693 | 44.96 | 1216.4575 | 0 | 0 | 1216.4575 | Heating | 1073.3448 | 8.5 | 1073.3448 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 214.669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1095.2498 | 0 | 219.05 | 2.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 06:00 | 4 | 23 | 6 | 113 | 2694 | 44.96 | 9003.8033 | 0 | 0 | 9003.8033 | Heating | 7944.5323 | 8.5 | 7944.5323 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1588.9065 | 31.78% | 1 | 63.56% | 0% | 0% | 0% | 28.7347 | 0 | 0 | 0 | 28.7347 | 8106.6656 | 0 | 1621.3331 | 16.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.0093
2007-04-23 07:00 | 4 | 23 | 7 | 113 | 2695 | 44.96 | 6111.4236 | 0 | 0 | 6111.4236 | Heating | 5392.4326 | 8.5 | 5392.4326 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1078.4865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5502.4823 | 0 | 1100.4965 | 11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 08:00 | 4 | 23 | 8 | 113 | 2696 | 42.98 | 4261.034 | 0 | 0 | 4261.034 | Heating | 3759.7359 | 8.5 | 3759.7359 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 751.9472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3836.4652 | 0 | 767.293 | 7.673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 09:00 | 4 | 23 | 9 | 113 | 2697 | 44.06 | 2602.6951 | 13.9974 | 13.9974 | 2588.6976 | Heating | 2284.145 | 8.5 | 2284.145 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 456.829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2330.7602 | 0 | 466.152 | 4.662% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 10:00 | 4 | 23 | 10 | 113 | 2698 | 44.96 | 1499.8844 | 38.9434 | 38.9434 | 1460.941 | Heating | 1289.0656 | 8.5 | 1289.0656 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 257.8131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1315.3731 | 0 | 263.0746 | 2.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 11:00 | 4 | 23 | 11 | 113 | 2699 | 44.96 | 658.1587 | 52.8925 | 52.8925 | 605.2661 | Heating | 534.0584 | 8.5 | 534.0584 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.8117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 544.9575 | 0 | 108.9915 | 1.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 12:00 | 4 | 23 | 12 | 113 | 2700 | 48.02 | 271.8958 | 82.2367 | 82.2367 | 189.6592 | Heating | 167.3463 | 8.5 | 167.3463 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.4693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 170.7616 | 0 | 34.1523 | 0.3415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 13:00 | 4 | 23 | 13 | 113 | 2701 | 53.06 | 204.0025 | 162.3513 | 162.3513 | 41.6513 | Heating | 36.7511 | 8.5 | 36.7511 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.3502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 37.5011 | 0 | 7.5002 | 0.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 14:00 | 4 | 23 | 14 | 113 | 2702 | 53.06 | 168.5956 | 254.9547 | 254.9547 | -86.3591 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 311.6113 | 311.6113 | 0 | 8.5 | 0 | 51.9352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 305.3791 | 61.0758 | 0.6108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 15:00 | 4 | 23 | 15 | 113 | 2703 | 50 | 114.4486 | 289.0753 | 289.0753 | -174.6267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 353.3143 | 353.3143 | 0 | 8.5 | 0 | 58.8857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 346.248 | 69.2496 | 0.6925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 16:00 | 4 | 23 | 16 | 113 | 2704 | 48.92 | 64.901 | 304.4384 | 304.4384 | -239.5374 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 372.0914 | 372.0914 | 0 | 8.5 | 0 | 62.0152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 364.6495 | 72.9299 | 0.7293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 17:00 | 4 | 23 | 17 | 113 | 2705 | 48.92 | 40.13 | 252.5157 | 252.5157 | -212.3857 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 308.6303 | 308.6303 | 0 | 8.5 | 0 | 51.4384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 302.4577 | 60.4915 | 0.6049% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 18:00 | 4 | 23 | 18 | 113 | 2706 | 46.04 | 37.1097 | 153.5759 | 153.5759 | -116.4662 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 187.7039 | 187.7039 | 0 | 8.5 | 0 | 31.284 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 183.9498 | 36.79 | 0.3679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 19:00 | 4 | 23 | 19 | 113 | 2707 | 44.06 | 72.9006 | 112.144 | 112.144 | -39.2434 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 137.0649 | 137.0649 | 0 | 8.5 | 0 | 22.8441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 134.3236 | 26.8647 | 0.2686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 20:00 | 4 | 23 | 20 | 113 | 2708 | 44.06 | 237.7028 | 41.8071 | 41.8071 | 195.8957 | Heating | 172.8491 | 8.5 | 172.8491 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.5698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 176.3767 | 0 | 35.2753 | 0.3528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 21:00 | 4 | 23 | 21 | 113 | 2709 | 42.98 | 208.7898 | 13.4389 | 13.4389 | 195.351 | Heating | 172.3685 | 8.5 | 172.3685 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.4737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 175.8862 | 0 | 35.1772 | 0.3518% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 22:00 | 4 | 23 | 22 | 113 | 2710 | 42.98 | 361.8147 | 0 | 0 | 361.8147 | Heating | 319.2482 | 8.5 | 319.2482 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.8496 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 325.7635 | 0 | 65.1527 | 0.6515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-23 23:00 | 4 | 23 | 23 | 113 | 2711 | 42.98 | 448.5786 | 0 | 0 | 448.5786 | Heating | 395.8046 | 8.5 | 395.8046 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.1609 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 403.8823 | 0 | 80.7765 | 0.8078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 | 4 | 24 | 0 | 114 | 2712 | 39.92 | 481.6067 | 0 | 0 | 481.6067 | Heating | 424.9471 | 8.5 | 424.9471 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.9894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 433.6195 | 0 | 86.7239 | 0.8672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 01:00 | 4 | 24 | 1 | 114 | 2713 | 39.02 | 524.0452 | 0 | 0 | 524.0452 | Heating | 462.3928 | 8.5 | 462.3928 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.4786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 471.8294 | 0 | 94.3659 | 0.9437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 02:00 | 4 | 24 | 2 | 114 | 2714 | 39.02 | 529.8052 | 0 | 0 | 529.8052 | Heating | 467.4752 | 8.5 | 467.4752 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.495 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 477.0155 | 0 | 95.4031 | 0.954% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 03:00 | 4 | 24 | 3 | 114 | 2715 | 37.94 | 552.0363 | 0 | 0 | 552.0363 | Heating | 487.0908 | 8.5 | 487.0908 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 97.4182 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 497.0315 | 0 | 99.4063 | 0.9941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 04:00 | 4 | 24 | 4 | 114 | 2716 | 37.04 | 567.3548 | 0 | 0 | 567.3548 | Heating | 500.6072 | 8.5 | 500.6072 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.1214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 510.8237 | 0 | 102.1647 | 1.022% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 05:00 | 4 | 24 | 5 | 114 | 2717 | 37.04 | 573.4063 | 0 | 0 | 573.4063 | Heating | 505.9468 | 8.5 | 505.9468 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.1894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 516.2722 | 0 | 103.2544 | 1.033% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 06:00 | 4 | 24 | 6 | 114 | 2718 | 37.94 | 5660.3673 | 11.6677 | 11.6677 | 5648.6995 | Heating | 4984.1467 | 8.5 | 4984.1467 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 996.8293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5085.8639 | 0 | 1017.1728 | 10.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 07:00 | 4 | 24 | 7 | 114 | 2719 | 39.92 | 3487.05 | 0 | 0 | 3487.05 | Heating | 3076.8088 | 8.5 | 3076.8088 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 615.3618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3139.6008 | 0 | 627.9202 | 6.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 08:00 | 4 | 24 | 8 | 114 | 2720 | 39.92 | 2093.1592 | 33.0318 | 33.0318 | 2060.1274 | Heating | 1817.7595 | 8.5 | 1817.7595 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.5519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1854.8566 | 0 | 370.9713 | 3.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 09:00 | 4 | 24 | 9 | 114 | 2721 | 44.96 | 553.2714 | 93.2918 | 93.2918 | 459.9795 | Heating | 405.8643 | 8.5 | 405.8643 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.1729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 414.1472 | 0 | 82.8294 | 0.8283% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 10:00 | 4 | 24 | 10 | 114 | 2722 | 48.92 | 54.3558 | 401.1099 | 401.1099 | -346.754 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 490.2454 | 490.2454 | 0 | 8.5 | 0 | 81.7076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 480.4405 | 96.0881 | 0.9609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 11:00 | 4 | 24 | 11 | 114 | 2723 | 48.92 | 2.4862 | 1274.2937 | 1274.2937 | -1271.8075 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1557.4701 | 1557.4701 | 0 | 8.5 | 0 | 259.5784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1526.3207 | 305.2641 | 3.053% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 12:00 | 4 | 24 | 12 | 114 | 2724 | 53.96 | 0 | 2494.004 | 2494.004 | -2494.004 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3048.2271 | 3048.2271 | 0 | 8.5 | 0 | 508.0379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2987.2626 | 597.4525 | 5.975% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 13:00 | 4 | 24 | 13 | 114 | 2725 | 57.02 | 0 | 3659.6061 | 3659.6061 | -3659.6061 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4472.8519 | 4472.8519 | 0 | 8.5 | 0 | 745.4753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4383.3948 | 876.679 | 8.767% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 14:00 | 4 | 24 | 14 | 114 | 2726 | 57.02 | 0 | 4616.1764 | 4616.1764 | -4616.1764 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5641.9933 | 5641.9933 | 0 | 8.5 | 0 | 940.3322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5529.1535 | 1105.8307 | 11.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 15:00 | 4 | 24 | 15 | 114 | 2727 | 57.02 | 0 | 4747.8187 | 4747.8187 | -4747.8187 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5802.8895 | 5802.8895 | 0 | 8.5 | 0 | 967.1482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5686.8317 | 1137.3663 | 11.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 16:00 | 4 | 24 | 16 | 114 | 2728 | 57.92 | 0 | 4506.6345 | 4506.6345 | -4506.6345 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5508.1088 | 5508.1088 | 0 | 8.5 | 0 | 918.0181 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5397.9466 | 1079.5893 | 10.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 17:00 | 4 | 24 | 17 | 114 | 2729 | 57.92 | 0 | 4329.515 | 4329.515 | -4329.515 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5291.6295 | 5291.6295 | 0 | 8.5 | 0 | 881.9382 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5185.7969 | 1037.1594 | 10.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 18:00 | 4 | 24 | 18 | 114 | 2730 | 55.04 | 0 | 3064.1482 | 3064.1482 | -3064.1482 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3745.0701 | 3745.0701 | 0 | 8.5 | 0 | 624.1783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3670.1687 | 734.0337 | 7.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 19:00 | 4 | 24 | 19 | 114 | 2731 | 51.98 | 0 | 2370.2095 | 2370.2095 | -2370.2095 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2896.9227 | 2896.9227 | 0 | 8.5 | 0 | 482.8204 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2838.9842 | 567.7968 | 5.678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 20:00 | 4 | 24 | 20 | 114 | 2732 | 51.98 | 0 | 1689.7745 | 1689.7745 | -1689.7745 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2065.28 | 2065.28 | 0 | 8.5 | 0 | 344.2133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2023.9744 | 404.7949 | 4.048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 21:00 | 4 | 24 | 21 | 114 | 2733 | 46.94 | 0 | 765.662 | 765.662 | -765.662 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 935.8091 | 935.8091 | 0 | 8.5 | 0 | 155.9682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 917.0929 | 183.4186 | 1.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 22:00 | 4 | 24 | 22 | 114 | 2734 | 44.96 | 0 | 6.9693 | 6.9693 | -6.9693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8.518 | 8.518 | 0 | 8.5 | 0 | 1.4197 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 8.3477 | 1.6695 | 0.0167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-24 23:00 | 4 | 24 | 23 | 114 | 2735 | 44.96 | 0 | 2.3504 | 2.3504 | -2.3504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.8727 | 2.8727 | 0 | 8.5 | 0 | 0.47878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.8152 | 0.56304 | 0.00563% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 | 4 | 25 | 0 | 115 | 2736 | 41 | 0 | 0.058398 | 0.058398 | -0.058398 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.071375 | 0.071375 | 0 | 8.5 | 0 | 0.011896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.069948 | 0.01399 | 0.0001399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 01:00 | 4 | 25 | 1 | 115 | 2737 | 39.92 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-04-25 02:00 | 4 | 25 | 2 | 115 | 2738 | 39.92 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-04-25 03:00 | 4 | 25 | 3 | 115 | 2739 | 33.98 | 1.1611 | 0 | 0 | 1.1611 | Heating | 1.0245 | 8.5 | 1.0245 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.2049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.0454 | 0 | 0.20908 | 0.002091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 04:00 | 4 | 25 | 4 | 115 | 2740 | 32 | 6.5322 | 0 | 0 | 6.5322 | Heating | 5.7637 | 8.5 | 5.7637 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1527 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.8813 | 0 | 1.1763 | 0.01176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 05:00 | 4 | 25 | 5 | 115 | 2741 | 32 | 10.1243 | 0 | 0 | 10.1243 | Heating | 8.9332 | 8.5 | 8.9332 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.7866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.1155 | 0 | 1.8231 | 0.01823% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 06:00 | 4 | 25 | 6 | 115 | 2742 | 33.98 | 955.6046 | 181.0328 | 181.0328 | 774.5719 | Heating | 683.4458 | 8.5 | 683.4458 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.6892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 697.3937 | 0 | 139.4787 | 1.395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 07:00 | 4 | 25 | 7 | 115 | 2743 | 42.08 | 611.4753 | 54.4115 | 54.4115 | 557.0638 | Heating | 491.5269 | 8.5 | 491.5269 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.3054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 501.558 | 0 | 100.3116 | 1.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 08:00 | 4 | 25 | 8 | 115 | 2744 | 42.08 | 148.9825 | 660.3675 | 660.3675 | -511.385 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 807.1159 | 807.1159 | 0 | 8.5 | 0 | 134.5193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 790.9736 | 158.1947 | 1.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 09:00 | 4 | 25 | 9 | 115 | 2745 | 46.94 | 21.179 | 714.7053 | 714.7053 | -693.5264 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 873.5287 | 873.5287 | 0 | 8.5 | 0 | 145.5881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 856.0582 | 171.2116 | 1.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 10:00 | 4 | 25 | 10 | 115 | 2746 | 51.08 | 31.2616 | 798.9772 | 798.9772 | -767.7156 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 976.5277 | 976.5277 | 0 | 8.5 | 0 | 162.7546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 956.9971 | 191.3994 | 1.914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 11:00 | 4 | 25 | 11 | 115 | 2747 | 51.08 | 30.4844 | 863.3676 | 863.3676 | -832.8832 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1055.2271 | 1055.2271 | 0 | 8.5 | 0 | 175.8712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1034.1225 | 206.8245 | 2.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 12:00 | 4 | 25 | 12 | 115 | 2748 | 57.02 | 11.0796 | 1251.6929 | 1251.6929 | -1240.6132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1529.8468 | 1529.8468 | 0 | 8.5 | 0 | 254.9745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1499.2499 | 299.85 | 2.998% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 13:00 | 4 | 25 | 13 | 115 | 2749 | 59 | 0.16521 | 2822.7802 | 2822.7802 | -2822.615 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3450.0647 | 3450.0647 | 0 | 8.5 | 0 | 575.0108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3381.0634 | 676.2127 | 6.762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 14:00 | 4 | 25 | 14 | 115 | 2750 | 59 | 0 | 3076.0466 | 3076.0466 | -3076.0466 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3759.6125 | 3759.6125 | 0 | 8.5 | 0 | 626.6021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3684.4203 | 736.8841 | 7.369% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 15:00 | 4 | 25 | 15 | 115 | 2751 | 62.06 | 0.17531 | 2119.8635 | 2119.8635 | -2119.6882 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2590.9442 | 2590.9442 | 0 | 8.5 | 0 | 431.824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2539.1254 | 507.8251 | 5.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 16:00 | 4 | 25 | 16 | 115 | 2752 | 62.96 | 4.0796 | 1118.744 | 1118.744 | -1114.6645 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1367.3538 | 1367.3538 | 0 | 8.5 | 0 | 227.8923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1340.0067 | 268.0013 | 2.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 17:00 | 4 | 25 | 17 | 115 | 2753 | 62.96 | 5.415 | 667.059 | 667.059 | -661.644 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 815.2944 | 815.2944 | 0 | 8.5 | 0 | 135.8824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 798.9885 | 159.7977 | 1.598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 18:00 | 4 | 25 | 18 | 115 | 2754 | 62.06 | 5.0617 | 305.9736 | 305.9736 | -300.912 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 373.9678 | 373.9678 | 0 | 8.5 | 0 | 62.328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 366.4884 | 73.2977 | 0.733% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 19:00 | 4 | 25 | 19 | 115 | 2755 | 62.06 | 13.4959 | 244.7324 | 244.7324 | -231.2365 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 299.1174 | 299.1174 | 0 | 8.5 | 0 | 49.8529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 293.135 | 58.627 | 0.5863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 20:00 | 4 | 25 | 20 | 115 | 2756 | 62.06 | 59.4551 | 137.8872 | 137.8872 | -78.4322 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 168.5289 | 168.5289 | 0 | 8.5 | 0 | 28.0881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 165.1583 | 33.0317 | 0.3303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 21:00 | 4 | 25 | 21 | 115 | 2757 | 57.92 | 23.7197 | 112.6051 | 112.6051 | -88.8854 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 137.6284 | 137.6284 | 0 | 8.5 | 0 | 22.9381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 134.8758 | 26.9752 | 0.2698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 22:00 | 4 | 25 | 22 | 115 | 2758 | 51.98 | 39.0235 | 0 | 0 | 39.0235 | Heating | 34.4325 | 8.5 | 34.4325 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.8865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.1352 | 0 | 7.027 | 0.07027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-25 23:00 | 4 | 25 | 23 | 115 | 2759 | 51.98 | 91.2297 | 0 | 0 | 91.2297 | Heating | 80.4968 | 8.5 | 80.4968 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.0994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 82.1396 | 0 | 16.4279 | 0.1643% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 | 4 | 26 | 0 | 116 | 2760 | 44.96 | 158.6291 | 0 | 0 | 158.6291 | Heating | 139.9669 | 8.5 | 139.9669 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.9934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 142.8234 | 0 | 28.5647 | 0.2856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 01:00 | 4 | 26 | 1 | 116 | 2761 | 44.06 | 216.3396 | 0 | 0 | 216.3396 | Heating | 190.8879 | 8.5 | 190.8879 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.1776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 194.7835 | 0 | 38.9567 | 0.3896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 02:00 | 4 | 26 | 2 | 116 | 2762 | 44.06 | 271.135 | 0 | 0 | 271.135 | Heating | 239.2368 | 8.5 | 239.2368 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.8474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 244.1191 | 0 | 48.8238 | 0.4882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 03:00 | 4 | 26 | 3 | 116 | 2763 | 44.06 | 311.4562 | 0 | 0 | 311.4562 | Heating | 274.8143 | 8.5 | 274.8143 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.9629 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 280.4228 | 0 | 56.0846 | 0.5608% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 04:00 | 4 | 26 | 4 | 116 | 2764 | 42.98 | 347.8534 | 0 | 0 | 347.8534 | Heating | 306.9295 | 8.5 | 306.9295 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.3859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 313.1934 | 0 | 62.6387 | 0.6264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 05:00 | 4 | 26 | 5 | 116 | 2765 | 42.98 | 369.3455 | 0 | 0 | 369.3455 | Heating | 325.8931 | 8.5 | 325.8931 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.1786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 332.5439 | 0 | 66.5088 | 0.6651% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 06:00 | 4 | 26 | 6 | 116 | 2766 | 42.98 | 4657.5927 | 36.2298 | 36.2298 | 4621.363 | Heating | 4077.6732 | 8.5 | 4077.6732 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 815.5346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4160.891 | 0 | 832.1782 | 8.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 07:00 | 4 | 26 | 7 | 116 | 2767 | 42.98 | 3229.8567 | 0 | 0 | 3229.8567 | Heating | 2849.8735 | 8.5 | 2849.8735 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 569.9747 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2908.0342 | 0 | 581.6068 | 5.816% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 08:00 | 4 | 26 | 8 | 116 | 2768 | 42.98 | 2494.3222 | 0 | 0 | 2494.3222 | Heating | 2200.8726 | 8.5 | 2200.8726 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 440.1745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2245.7883 | 0 | 449.1577 | 4.492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 09:00 | 4 | 26 | 9 | 116 | 2769 | 44.96 | 1647.5263 | 0.080255 | 0.080255 | 1647.4461 | Heating | 1453.6289 | 8.5 | 1453.6289 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.7258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1483.2948 | 0 | 296.659 | 2.967% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 10:00 | 4 | 26 | 10 | 116 | 2770 | 44.96 | 1256.5985 | 8.0999 | 8.0999 | 1248.4986 | Heating | 1101.6164 | 8.5 | 1101.6164 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 220.3233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1124.0984 | 0 | 224.8197 | 2.248% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 11:00 | 4 | 26 | 11 | 116 | 2771 | 44.96 | 707.8218 | 62.9302 | 62.9302 | 644.8916 | Heating | 569.022 | 8.5 | 569.022 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.8044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 580.6347 | 0 | 116.1269 | 1.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 12:00 | 4 | 26 | 12 | 116 | 2772 | 48.92 | 203.0788 | 278.7632 | 278.7632 | -75.6843 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 340.7105 | 340.7105 | 0 | 8.5 | 0 | 56.7851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 333.8963 | 66.7793 | 0.6678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 13:00 | 4 | 26 | 13 | 116 | 2773 | 53.96 | 86.5635 | 618.3027 | 618.3027 | -531.7392 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 755.7033 | 755.7033 | 0 | 8.5 | 0 | 125.9506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 740.5892 | 148.1178 | 1.481% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 14:00 | 4 | 26 | 14 | 116 | 2774 | 53.96 | 29.2289 | 1073.3294 | 1073.3294 | -1044.1006 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1311.8471 | 1311.8471 | 0 | 8.5 | 0 | 218.6412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1285.6101 | 257.122 | 2.571% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 15:00 | 4 | 26 | 15 | 116 | 2775 | 57.02 | 5.7441 | 1702.2805 | 1702.2805 | -1696.5364 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2080.565 | 2080.565 | 0 | 8.5 | 0 | 346.7608 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2038.9537 | 407.7907 | 4.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 16:00 | 4 | 26 | 16 | 116 | 2776 | 55.94 | 0.10267 | 2374.8575 | 2374.8575 | -2374.7548 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2902.6036 | 2902.6036 | 0 | 8.5 | 0 | 483.7673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2844.5515 | 568.9103 | 5.689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 17:00 | 4 | 26 | 17 | 116 | 2777 | 55.94 | 0 | 2427.4867 | 2427.4867 | -2427.4867 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2966.9282 | 2966.9282 | 0 | 8.5 | 0 | 494.488 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2907.5897 | 581.5179 | 5.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 18:00 | 4 | 26 | 18 | 116 | 2778 | 50 | 0 | 1086.0023 | 1086.0023 | -1086.0023 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1327.3361 | 1327.3361 | 0 | 8.5 | 0 | 221.2227 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1300.7894 | 260.1579 | 2.602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 19:00 | 4 | 26 | 19 | 116 | 2779 | 46.94 | 0.71837 | 312.7473 | 312.7473 | -312.0289 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 382.2467 | 382.2467 | 0 | 8.5 | 0 | 63.7078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 374.6018 | 74.9204 | 0.7492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 20:00 | 4 | 26 | 20 | 116 | 2780 | 46.04 | 9.4304 | 180.4981 | 180.4981 | -171.0678 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 220.6088 | 220.6088 | 0 | 8.5 | 0 | 36.7681 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 216.1967 | 43.2393 | 0.4324% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 21:00 | 4 | 26 | 21 | 116 | 2781 | 46.94 | 25.7322 | 123.8747 | 123.8747 | -98.1425 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 151.4024 | 151.4024 | 0 | 8.5 | 0 | 25.2337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 148.3743 | 29.6749 | 0.2967% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 22:00 | 4 | 26 | 22 | 116 | 2782 | 44.96 | 49.9208 | 0 | 0 | 49.9208 | Heating | 44.0478 | 8.5 | 44.0478 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.8096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.9467 | 0 | 8.9893 | 0.08989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-26 23:00 | 4 | 26 | 23 | 116 | 2783 | 44.96 | 78.7053 | 0 | 0 | 78.7053 | Heating | 69.4459 | 8.5 | 69.4459 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.8892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 70.8631 | 0 | 14.1726 | 0.1417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 | 4 | 27 | 0 | 117 | 2784 | 44.06 | 106.0286 | 0 | 0 | 106.0286 | Heating | 93.5547 | 8.5 | 93.5547 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.7109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 95.464 | 0 | 19.0928 | 0.1909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 01:00 | 4 | 27 | 1 | 117 | 2785 | 44.06 | 137.9471 | 0 | 0 | 137.9471 | Heating | 121.718 | 8.5 | 121.718 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.3436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 124.2021 | 0 | 24.8404 | 0.2484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 02:00 | 4 | 27 | 2 | 117 | 2786 | 44.06 | 164.3776 | 0 | 0 | 164.3776 | Heating | 145.039 | 8.5 | 145.039 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.0078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 147.999 | 0 | 29.5998 | 0.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 03:00 | 4 | 27 | 3 | 117 | 2787 | 41 | 180.7075 | 0 | 0 | 180.7075 | Heating | 159.4478 | 8.5 | 159.4478 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.8896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 162.7019 | 0 | 32.5404 | 0.3254% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 04:00 | 4 | 27 | 4 | 117 | 2788 | 42.98 | 191.1233 | 0 | 0 | 191.1233 | Heating | 168.6382 | 8.5 | 168.6382 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.7276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 172.0798 | 0 | 34.416 | 0.3442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 05:00 | 4 | 27 | 5 | 117 | 2789 | 42.98 | 203.2189 | 0 | 0 | 203.2189 | Heating | 179.3108 | 8.5 | 179.3108 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.8622 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 182.9702 | 0 | 36.594 | 0.3659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 06:00 | 4 | 27 | 6 | 117 | 2790 | 42.98 | 2947.612 | 81.1224 | 81.1224 | 2866.4896 | Heating | 2529.2556 | 8.5 | 2529.2556 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.8511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2580.873 | 0 | 516.1746 | 5.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 07:00 | 4 | 27 | 7 | 117 | 2791 | 44.06 | 1921.85 | 0 | 0 | 1921.85 | Heating | 1695.75 | 8.5 | 1695.75 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.15 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1730.3571 | 0 | 346.0714 | 3.461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 08:00 | 4 | 27 | 8 | 117 | 2792 | 44.06 | 1225.1103 | 20.8768 | 20.8768 | 1204.2335 | Heating | 1062.5589 | 8.5 | 1062.5589 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.5118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1084.2438 | 0 | 216.8488 | 2.168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 09:00 | 4 | 27 | 9 | 117 | 2793 | 48.02 | 203.7283 | 80.7027 | 80.7027 | 123.0256 | Heating | 108.552 | 8.5 | 108.552 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.7104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 110.7673 | 0 | 22.1535 | 0.2215% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 10:00 | 4 | 27 | 10 | 117 | 2794 | 48.92 | 4.1957 | 476.0063 | 476.0063 | -471.8106 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 581.7855 | 581.7855 | 0 | 8.5 | 0 | 96.9643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 570.1498 | 114.03 | 1.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 11:00 | 4 | 27 | 11 | 117 | 2795 | 48.92 | 0 | 1766.6185 | 1766.6185 | -1766.6185 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2159.2004 | 2159.2004 | 0 | 8.5 | 0 | 359.8667 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2116.0164 | 423.2033 | 4.232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 12:00 | 4 | 27 | 12 | 117 | 2796 | 50 | 0 | 3349.4708 | 3349.4708 | -3349.4708 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4093.7976 | 4093.7976 | 0 | 8.5 | 0 | 682.2996 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4011.9216 | 802.3843 | 8.024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 13:00 | 4 | 27 | 13 | 117 | 2797 | 51.08 | 0 | 4828.9097 | 4828.9097 | -4828.9097 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5902.0007 | 5902.0007 | 0 | 8.5 | 0 | 983.6668 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5783.9607 | 1156.7921 | 11.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 14:00 | 4 | 27 | 14 | 117 | 2798 | 51.08 | 0 | 5795.8126 | 5795.8126 | -5795.8126 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7083.771 | 7083.771 | 0 | 8.5 | 0 | 1180.6285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6942.0956 | 1388.4191 | 13.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 15:00 | 4 | 27 | 15 | 117 | 2799 | 51.98 | 0 | 4516.864 | 4516.864 | -4516.864 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5520.6115 | 5520.6115 | 0 | 8.5 | 0 | 920.1019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5410.1993 | 1082.0399 | 10.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 16:00 | 4 | 27 | 16 | 117 | 2800 | 51.98 | 0 | 4216.0054 | 4216.0054 | -4216.0054 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5152.8955 | 5152.8955 | 0 | 8.5 | 0 | 858.8159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5049.8376 | 1009.9675 | 10.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 17:00 | 4 | 27 | 17 | 117 | 2801 | 51.98 | 0 | 4921.6721 | 4921.6721 | -4921.6721 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6015.377 | 6015.377 | 0 | 8.5 | 0 | 1002.5628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5895.0695 | 1179.0139 | 11.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 18:00 | 4 | 27 | 18 | 117 | 2802 | 50 | 0 | 2819.3172 | 2819.3172 | -2819.3172 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3445.8322 | 3445.8322 | 0 | 8.5 | 0 | 574.3054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3376.9155 | 675.3831 | 6.754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 19:00 | 4 | 27 | 19 | 117 | 2803 | 48.02 | 0 | 1486.1367 | 1486.1367 | -1486.1367 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1816.3893 | 1816.3893 | 0 | 8.5 | 0 | 302.7316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1780.0616 | 356.0123 | 3.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 20:00 | 4 | 27 | 20 | 117 | 2804 | 48.02 | 0 | 929.7813 | 929.7813 | -929.7813 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1136.3994 | 1136.3994 | 0 | 8.5 | 0 | 189.3999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1113.6714 | 222.7343 | 2.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 21:00 | 4 | 27 | 21 | 117 | 2805 | 46.04 | 0 | 211.1293 | 211.1293 | -211.1293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 258.0469 | 258.0469 | 0 | 8.5 | 0 | 43.0078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 252.8859 | 50.5772 | 0.5058% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 22:00 | 4 | 27 | 22 | 117 | 2806 | 44.96 | 0 | 40.2532 | 40.2532 | -40.2532 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 49.1983 | 49.1983 | 0 | 8.5 | 0 | 8.1997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 48.2143 | 9.6429 | 0.09643% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-27 23:00 | 4 | 27 | 23 | 117 | 2807 | 44.96 | 0 | 2.2337 | 2.2337 | -2.2337 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.7301 | 2.7301 | 0 | 8.5 | 0 | 0.45502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.6755 | 0.5351 | 0.005351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 | 4 | 28 | 0 | 118 | 2808 | 44.96 | 1.4385 | 0 | 0 | 1.4385 | Heating | 1.2693 | 8.5 | 1.2693 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.25385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.2952 | 0 | 0.25903 | 0.00259% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 01:00 | 4 | 28 | 1 | 118 | 2809 | 44.96 | 14.9204 | 0 | 0 | 14.9204 | Heating | 13.1651 | 8.5 | 13.1651 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.4337 | 0 | 2.6867 | 0.02687% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 02:00 | 4 | 28 | 2 | 118 | 2810 | 44.96 | 46.6486 | 0 | 0 | 46.6486 | Heating | 41.1605 | 8.5 | 41.1605 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.2321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.0005 | 0 | 8.4001 | 0.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 03:00 | 4 | 28 | 3 | 118 | 2811 | 42.08 | 89.3852 | 0 | 0 | 89.3852 | Heating | 78.8693 | 8.5 | 78.8693 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.7739 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 80.4789 | 0 | 16.0958 | 0.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 04:00 | 4 | 28 | 4 | 118 | 2812 | 39.02 | 135.1877 | 0 | 0 | 135.1877 | Heating | 119.2833 | 8.5 | 119.2833 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.8567 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 121.7176 | 0 | 24.3435 | 0.2434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 05:00 | 4 | 28 | 5 | 118 | 2813 | 39.02 | 176.3321 | 0 | 0 | 176.3321 | Heating | 155.5872 | 8.5 | 155.5872 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.1174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 158.7624 | 0 | 31.7525 | 0.3175% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 06:00 | 4 | 28 | 6 | 118 | 2814 | 41 | 199.1311 | 0 | 0 | 199.1311 | Heating | 175.704 | 8.5 | 175.704 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.1408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 179.2898 | 0 | 35.858 | 0.3586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 07:00 | 4 | 28 | 7 | 118 | 2815 | 46.04 | 202.3044 | 0 | 0 | 202.3044 | Heating | 178.5039 | 8.5 | 178.5039 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.7008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 182.1468 | 0 | 36.4294 | 0.3643% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 08:00 | 4 | 28 | 8 | 118 | 2816 | 46.04 | 3855.0492 | 0 | 0 | 3855.0492 | Heating | 3401.514 | 8.5 | 3401.514 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 680.3028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3470.9326 | 0 | 694.1865 | 6.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 09:00 | 4 | 28 | 9 | 118 | 2817 | 51.08 | 2729.2229 | 0 | 0 | 2729.2229 | Heating | 2408.1379 | 8.5 | 2408.1379 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 481.6276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2457.2835 | 0 | 491.4567 | 4.915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 10:00 | 4 | 28 | 10 | 118 | 2818 | 53.96 | 2160.0479 | 0 | 0 | 2160.0479 | Heating | 1905.9247 | 8.5 | 1905.9247 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 381.1849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1944.8211 | 0 | 388.9642 | 3.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 11:00 | 4 | 28 | 11 | 118 | 2819 | 53.96 | 1787.0035 | 0 | 0 | 1787.0035 | Heating | 1576.7678 | 8.5 | 1576.7678 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 315.3536 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1608.9468 | 0 | 321.7894 | 3.218% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 12:00 | 4 | 28 | 12 | 118 | 2820 | 57.92 | 1162.1742 | 0 | 0 | 1162.1742 | Heating | 1025.4478 | 8.5 | 1025.4478 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 205.0896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1046.3753 | 0 | 209.2751 | 2.093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 13:00 | 4 | 28 | 13 | 118 | 2821 | 60.08 | 706.6165 | 0 | 0 | 706.6165 | Heating | 623.4851 | 8.5 | 623.4851 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.697 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 636.2093 | 0 | 127.2419 | 1.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 14:00 | 4 | 28 | 14 | 118 | 2822 | 60.08 | 523.8162 | 0 | 0 | 523.8162 | Heating | 462.1907 | 8.5 | 462.1907 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.4381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 471.6232 | 0 | 94.3246 | 0.9432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 15:00 | 4 | 28 | 15 | 118 | 2823 | 60.98 | 279.4789 | 0 | 0 | 279.4789 | Heating | 246.599 | 8.5 | 246.599 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.3198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 251.6317 | 0 | 50.3263 | 0.5033% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 16:00 | 4 | 28 | 16 | 118 | 2824 | 60.98 | 112.4198 | 0 | 0 | 112.4198 | Heating | 99.194 | 8.5 | 99.194 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.8388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 101.2183 | 0 | 20.2437 | 0.2024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 17:00 | 4 | 28 | 17 | 118 | 2825 | 60.98 | 865.0218 | 0 | 0 | 865.0218 | Heating | 763.2546 | 8.5 | 763.2546 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.6509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 778.8312 | 0 | 155.7662 | 1.558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 18:00 | 4 | 28 | 18 | 118 | 2826 | 59 | 1301.336 | 0 | 0 | 1301.336 | Heating | 1148.2376 | 8.5 | 1148.2376 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.6475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1171.671 | 0 | 234.3342 | 2.343% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 19:00 | 4 | 28 | 19 | 118 | 2827 | 55.94 | 82.5157 | 0 | 0 | 82.5157 | Heating | 72.8079 | 8.5 | 72.8079 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.5616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 74.2938 | 0 | 14.8588 | 0.1486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 20:00 | 4 | 28 | 20 | 118 | 2828 | 55.94 | 147.532 | 0 | 0 | 147.532 | Heating | 130.1753 | 8.5 | 130.1753 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.0351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 132.832 | 0 | 26.5664 | 0.2657% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 21:00 | 4 | 28 | 21 | 118 | 2829 | 51.98 | 204.9074 | 0 | 0 | 204.9074 | Heating | 180.8007 | 8.5 | 180.8007 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.1601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 184.4905 | 0 | 36.8981 | 0.369% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 22:00 | 4 | 28 | 22 | 118 | 2830 | 51.08 | 273.3268 | 0 | 0 | 273.3268 | Heating | 241.1707 | 8.5 | 241.1707 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.2341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 246.0926 | 0 | 49.2185 | 0.4922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-28 23:00 | 4 | 28 | 23 | 118 | 2831 | 51.08 | 344.5627 | 0 | 0 | 344.5627 | Heating | 304.0259 | 8.5 | 304.0259 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.8052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 310.2305 | 0 | 62.0461 | 0.6205% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 | 4 | 29 | 0 | 119 | 2832 | 48.02 | 409.9443 | 0 | 0 | 409.9443 | Heating | 361.7155 | 8.5 | 361.7155 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.3431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 369.0975 | 0 | 73.8195 | 0.7382% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 01:00 | 4 | 29 | 1 | 119 | 2833 | 51.08 | 462.0366 | 0 | 0 | 462.0366 | Heating | 407.6794 | 8.5 | 407.6794 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.5359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 415.9994 | 0 | 83.1999 | 0.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 02:00 | 4 | 29 | 2 | 119 | 2834 | 51.08 | 536.1198 | 0 | 0 | 536.1198 | Heating | 473.0469 | 8.5 | 473.0469 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.6094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 482.7009 | 0 | 96.5402 | 0.9654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 03:00 | 4 | 29 | 3 | 119 | 2835 | 50 | 562.6474 | 0 | 0 | 562.6474 | Heating | 496.4536 | 8.5 | 496.4536 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.2907 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 506.5853 | 0 | 101.3171 | 1.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 04:00 | 4 | 29 | 4 | 119 | 2836 | 50 | 561.3126 | 0 | 0 | 561.3126 | Heating | 495.2759 | 8.5 | 495.2759 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.0552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 505.3835 | 0 | 101.0767 | 1.011% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 05:00 | 4 | 29 | 5 | 119 | 2837 | 50 | 564.1251 | 0 | 0 | 564.1251 | Heating | 497.7574 | 8.5 | 497.7574 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.5515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 507.9157 | 0 | 101.5831 | 1.016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 06:00 | 4 | 29 | 6 | 119 | 2838 | 48.92 | 6270.7923 | 0 | 0 | 6270.7923 | Heating | 5533.052 | 8.5 | 5533.052 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1106.6104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5645.9715 | 0 | 1129.1943 | 11.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 07:00 | 4 | 29 | 7 | 119 | 2839 | 48.92 | 4460.167 | 0 | 0 | 4460.167 | Heating | 3935.4415 | 8.5 | 3935.4415 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 787.0883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4015.7566 | 0 | 803.1513 | 8.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 08:00 | 4 | 29 | 8 | 119 | 2840 | 48.02 | 3376.4735 | 0 | 0 | 3376.4735 | Heating | 2979.2413 | 8.5 | 2979.2413 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 595.8483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3040.0421 | 0 | 608.0084 | 6.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 09:00 | 4 | 29 | 9 | 119 | 2841 | 48.02 | 2230.4341 | 0 | 0 | 2230.4341 | Heating | 1968.0301 | 8.5 | 1968.0301 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 393.606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2008.194 | 0 | 401.6388 | 4.016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 10:00 | 4 | 29 | 10 | 119 | 2842 | 48.02 | 1611.122 | 0 | 0 | 1611.122 | Heating | 1421.5782 | 8.5 | 1421.5782 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 284.3156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1450.59 | 0 | 290.118 | 2.901% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 11:00 | 4 | 29 | 11 | 119 | 2843 | 50 | 1003.7509 | 0 | 0 | 1003.7509 | Heating | 885.6625 | 8.5 | 885.6625 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.1325 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 903.7373 | 0 | 180.7475 | 1.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 12:00 | 4 | 29 | 12 | 119 | 2844 | 53.06 | 814.4222 | 0 | 0 | 814.4222 | Heating | 718.6078 | 8.5 | 718.6078 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 143.7216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 733.2733 | 0 | 146.6547 | 1.467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 13:00 | 4 | 29 | 13 | 119 | 2845 | 53.06 | 487.8058 | 12.6518 | 12.6518 | 475.1539 | Heating | 419.2535 | 8.5 | 419.2535 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.8507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 427.8097 | 0 | 85.5619 | 0.8556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 14:00 | 4 | 29 | 14 | 119 | 2846 | 53.06 | 217.105 | 52.2626 | 52.2626 | 164.8424 | Heating | 145.4492 | 8.5 | 145.4492 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.0898 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 148.4175 | 0 | 29.6835 | 0.2968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 15:00 | 4 | 29 | 15 | 119 | 2847 | 51.08 | 148.4064 | 121.3129 | 121.3129 | 27.0936 | Heating | 23.9061 | 8.5 | 23.9061 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.7812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.394 | 0 | 4.8788 | 0.04879% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 16:00 | 4 | 29 | 16 | 119 | 2848 | 48.02 | 113.7038 | 154.9361 | 154.9361 | -41.2323 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 189.3663 | 189.3663 | 0 | 8.5 | 0 | 31.5611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 185.579 | 37.1158 | 0.3712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 17:00 | 4 | 29 | 17 | 119 | 2849 | 48.02 | 88.8859 | 118.4657 | 118.4657 | -29.5798 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 144.7914 | 144.7914 | 0 | 8.5 | 0 | 24.1319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 141.8955 | 28.3791 | 0.2838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 18:00 | 4 | 29 | 18 | 119 | 2850 | 46.04 | 84.6495 | 35.137 | 35.137 | 49.5124 | Heating | 43.6874 | 8.5 | 43.6874 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.7375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.579 | 0 | 8.9158 | 0.08916% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 19:00 | 4 | 29 | 19 | 119 | 2851 | 44.06 | 144.3057 | 19.6092 | 19.6092 | 124.6966 | Heating | 110.0264 | 8.5 | 110.0264 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.0053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 112.2718 | 0 | 22.4544 | 0.2245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 20:00 | 4 | 29 | 20 | 119 | 2852 | 44.06 | 415.2648 | 0 | 0 | 415.2648 | Heating | 366.4101 | 8.5 | 366.4101 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.282 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 373.8878 | 0 | 74.7776 | 0.7478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 21:00 | 4 | 29 | 21 | 119 | 2853 | 42.98 | 177.3105 | 0 | 0 | 177.3105 | Heating | 156.4505 | 8.5 | 156.4505 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.2901 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 159.6433 | 0 | 31.9287 | 0.3193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 22:00 | 4 | 29 | 22 | 119 | 2854 | 42.08 | 229.742 | 0 | 0 | 229.742 | Heating | 202.7135 | 8.5 | 202.7135 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.5427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 206.8505 | 0 | 41.3701 | 0.4137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-29 23:00 | 4 | 29 | 23 | 119 | 2855 | 42.08 | 268.6754 | 0 | 0 | 268.6754 | Heating | 237.0665 | 8.5 | 237.0665 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.4133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 241.9046 | 0 | 48.3809 | 0.4838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 | 4 | 30 | 0 | 120 | 2856 | 41 | 280.0595 | 0 | 0 | 280.0595 | Heating | 247.1114 | 8.5 | 247.1114 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.4223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 252.1544 | 0 | 50.4309 | 0.5043% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 01:00 | 4 | 30 | 1 | 120 | 2857 | 41 | 282.2744 | 0 | 0 | 282.2744 | Heating | 249.0657 | 8.5 | 249.0657 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.8131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 254.1487 | 0 | 50.8297 | 0.5083% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 02:00 | 4 | 30 | 2 | 120 | 2858 | 41 | 289.3054 | 0 | 0 | 289.3054 | Heating | 255.2695 | 8.5 | 255.2695 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.0539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 260.479 | 0 | 52.0958 | 0.521% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 03:00 | 4 | 30 | 3 | 120 | 2859 | 41 | 298.6416 | 0 | 0 | 298.6416 | Heating | 263.5073 | 8.5 | 263.5073 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.7015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 268.885 | 0 | 53.777 | 0.5378% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 04:00 | 4 | 30 | 4 | 120 | 2860 | 39.92 | 318.9627 | 0 | 0 | 318.9627 | Heating | 281.4377 | 8.5 | 281.4377 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 56.2875 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 287.1813 | 0 | 57.4363 | 0.5744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 05:00 | 4 | 30 | 5 | 120 | 2861 | 39.92 | 363.3765 | 0 | 0 | 363.3765 | Heating | 320.6263 | 8.5 | 320.6263 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.1253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 327.1697 | 0 | 65.4339 | 0.6543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 06:00 | 4 | 30 | 6 | 120 | 2862 | 41 | 4132.6877 | 48.8955 | 48.8955 | 4083.7922 | Heating | 3603.3461 | 8.5 | 3603.3461 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 720.6692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3676.8838 | 0 | 735.3768 | 7.354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 07:00 | 4 | 30 | 7 | 120 | 2863 | 42.08 | 3038.6693 | 0 | 0 | 3038.6693 | Heating | 2681.1788 | 8.5 | 2681.1788 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 536.2358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2735.8967 | 0 | 547.1793 | 5.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 08:00 | 4 | 30 | 8 | 120 | 2864 | 42.08 | 2341.838 | 11.1467 | 11.1467 | 2330.6913 | Heating | 2056.4923 | 8.5 | 2056.4923 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.2985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2098.4616 | 0 | 419.6923 | 4.197% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 09:00 | 4 | 30 | 9 | 120 | 2865 | 42.98 | 1392.3485 | 53.0295 | 53.0295 | 1339.319 | Heating | 1181.752 | 8.5 | 1181.752 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 236.3504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1205.8694 | 0 | 241.1739 | 2.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 10:00 | 4 | 30 | 10 | 120 | 2866 | 44.06 | 838.9593 | 129.7901 | 129.7901 | 709.1692 | Heating | 625.7375 | 8.5 | 625.7375 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.1475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 638.5076 | 0 | 127.7015 | 1.277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 11:00 | 4 | 30 | 11 | 120 | 2867 | 44.06 | 298.9338 | 227.512 | 227.512 | 71.4218 | Heating | 63.0193 | 8.5 | 63.0193 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.6039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 64.3054 | 0 | 12.8611 | 0.1286% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 12:00 | 4 | 30 | 12 | 120 | 2868 | 44.06 | 142.2735 | 370.5 | 370.5 | -228.2264 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 452.8333 | 452.8333 | 0 | 8.5 | 0 | 75.4722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 443.7766 | 88.7553 | 0.8876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 13:00 | 4 | 30 | 13 | 120 | 2869 | 44.96 | 81.4135 | 613.8323 | 613.8323 | -532.4188 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 750.2395 | 750.2395 | 0 | 8.5 | 0 | 125.0399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 735.2347 | 147.0469 | 1.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 14:00 | 4 | 30 | 14 | 120 | 2870 | 44.96 | 53.3179 | 784.5792 | 784.5792 | -731.2613 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 958.9301 | 958.9301 | 0 | 8.5 | 0 | 159.8217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 939.7515 | 187.9503 | 1.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 15:00 | 4 | 30 | 15 | 120 | 2871 | 44.96 | 19.6569 | 1007.7001 | 1007.7001 | -988.0433 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1231.6335 | 1231.6335 | 0 | 8.5 | 0 | 205.2722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1207.0008 | 241.4002 | 2.414% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 16:00 | 4 | 30 | 16 | 120 | 2872 | 44.6 | 5.8047 | 1185.2965 | 1185.2965 | -1179.4918 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1448.6957 | 1448.6957 | 0 | 8.5 | 0 | 241.4493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1419.7218 | 283.9444 | 2.839% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 17:00 | 4 | 30 | 17 | 120 | 2873 | 44.96 | 0.75813 | 1071.2547 | 1071.2547 | -1070.4966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1309.3114 | 1309.3114 | 0 | 8.5 | 0 | 218.2186 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1283.1251 | 256.625 | 2.566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 18:00 | 4 | 30 | 18 | 120 | 2874 | 46.04 | 0.43807 | 326.067 | 326.067 | -325.6289 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 398.5263 | 398.5263 | 0 | 8.5 | 0 | 66.421 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 390.5558 | 78.1112 | 0.7811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 19:00 | 4 | 30 | 19 | 120 | 2875 | 46.58 | 6.1245 | 236.5588 | 236.5588 | -230.4343 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 289.1275 | 289.1275 | 0 | 8.5 | 0 | 48.1879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 283.3449 | 56.669 | 0.5667% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 20:00 | 4 | 30 | 20 | 120 | 2876 | 46.76 | 15.2591 | 148.19 | 148.19 | -132.9309 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 181.1211 | 181.1211 | 0 | 8.5 | 0 | 30.1868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 177.4987 | 35.4997 | 0.355% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 21:00 | 4 | 30 | 21 | 120 | 2877 | 47.3 | 26.2748 | 112.0289 | 112.0289 | -85.7541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 136.9242 | 136.9242 | 0 | 8.5 | 0 | 22.8207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 134.1857 | 26.8371 | 0.2684% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 22:00 | 4 | 30 | 22 | 120 | 2878 | 47.48 | 43.2998 | 0 | 0 | 43.2998 | Heating | 38.2057 | 8.5 | 38.2057 | 0 | 4.2894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.6411 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 38.9854 | 0 | 7.7971 | 0.07797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-04-30 23:00 | 4 | 30 | 23 | 120 | 2879 | 47.84 | 53.9823 | 0 | 0 | 53.9823 | Heating | 47.6314 | 8.5 | 47.6314 | 0 | 4.3201 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.5263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 48.6035 | 0 | 9.7207 | 0.09721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 | 5 | 1 | 0 | 121 | 2880 | 48.56 | 66.256 | 0 | 0 | 66.256 | Heating | 58.4612 | 8.5 | 58.4612 | 0 | 4.3829 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.6922 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 59.6543 | 0 | 11.9309 | 0.1193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 01:00 | 5 | 1 | 1 | 121 | 2881 | 48.56 | 72.6534 | 0 | 0 | 72.6534 | Heating | 64.106 | 8.5 | 64.106 | 0 | 4.3829 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.8212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.4142 | 0 | 13.0828 | 0.1308% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 02:00 | 5 | 1 | 2 | 121 | 2882 | 48.2 | 76.6424 | 0 | 0 | 76.6424 | Heating | 67.6256 | 8.5 | 67.6256 | 0 | 4.3513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.5251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 69.0057 | 0 | 13.8011 | 0.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 03:00 | 5 | 1 | 3 | 121 | 2883 | 48.2 | 77.2687 | 0 | 0 | 77.2687 | Heating | 68.1782 | 8.5 | 68.1782 | 0 | 4.3513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.6356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 69.5696 | 0 | 13.9139 | 0.1391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 04:00 | 5 | 1 | 4 | 121 | 2884 | 48.02 | 73.187 | 0 | 0 | 73.187 | Heating | 64.5768 | 8.5 | 64.5768 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.9154 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.8947 | 0 | 13.1789 | 0.1318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 05:00 | 5 | 1 | 5 | 121 | 2885 | 48.2 | 85.9298 | 0 | 0 | 85.9298 | Heating | 75.8204 | 8.5 | 75.8204 | 0 | 4.3513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.1641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.3678 | 0 | 15.4736 | 0.1547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 06:00 | 5 | 1 | 6 | 121 | 2886 | 50.36 | 1639.5631 | 93.0554 | 93.0554 | 1546.5077 | Heating | 1364.5656 | 8.5 | 1364.5656 | 0 | 4.5471 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.9131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1392.4139 | 0 | 278.4828 | 2.785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 07:00 | 5 | 1 | 7 | 121 | 2887 | 48.92 | 1310.5766 | 1.6114 | 1.6114 | 1308.9651 | Heating | 1154.9692 | 8.5 | 1154.9692 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.9938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1178.54 | 0 | 235.708 | 2.357% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 08:00 | 5 | 1 | 8 | 121 | 2888 | 48.92 | 712.1073 | 201.5389 | 201.5389 | 510.5684 | Heating | 450.5015 | 8.5 | 450.5015 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 90.1003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 459.6954 | 0 | 91.9391 | 0.9194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 09:00 | 5 | 1 | 9 | 121 | 2889 | 55.94 | 51.3115 | 471.2271 | 471.2271 | -419.9155 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 575.9442 | 575.9442 | 0 | 8.5 | 0 | 95.9907 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 564.4253 | 112.8851 | 1.129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 10:00 | 5 | 1 | 10 | 121 | 2890 | 57.92 | 30.1148 | 731.2593 | 731.2593 | -701.1445 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 893.7614 | 893.7614 | 0 | 8.5 | 0 | 148.9602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 875.8862 | 175.1772 | 1.752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 11:00 | 5 | 1 | 11 | 121 | 2891 | 57.92 | 53.7959 | 817.9397 | 817.9397 | -764.1438 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 999.7041 | 999.7041 | 0 | 8.5 | 0 | 166.6173 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 979.71 | 195.942 | 1.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 12:00 | 5 | 1 | 12 | 121 | 2892 | 66.02 | 78.6245 | 858.3884 | 858.3884 | -779.7639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1049.1414 | 1049.1414 | 0 | 8.5 | 0 | 174.8569 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1028.1586 | 205.6317 | 2.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 13:00 | 5 | 1 | 13 | 121 | 2893 | 68 | 86.4646 | 930.8957 | 930.8957 | -844.4311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1137.7614 | 1137.7614 | 0 | 8.5 | 0 | 189.6269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1115.0062 | 223.0012 | 2.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 14:00 | 5 | 1 | 14 | 121 | 2894 | 68 | 82.8298 | 1068.7389 | 1068.7389 | -985.9092 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1306.2365 | 1306.2365 | 0 | 8.5 | 0 | 217.7061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1280.1118 | 256.0224 | 2.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 15:00 | 5 | 1 | 15 | 121 | 2895 | 69.08 | 56.4188 | 961.74 | 961.74 | -905.3212 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1175.46 | 1175.46 | 0 | 8.5 | 0 | 195.91 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1151.9508 | 230.3902 | 2.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 16:00 | 5 | 1 | 16 | 121 | 2896 | 66.92 | 33.0207 | 820.5366 | 820.5366 | -787.5159 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1002.8781 | 1002.8781 | 0 | 8.5 | 0 | 167.1464 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 982.8205 | 196.5641 | 1.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 17:00 | 5 | 1 | 17 | 121 | 2897 | 66.92 | 29.3786 | 624.716 | 624.716 | -595.3374 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 763.5418 | 763.5418 | 0 | 8.5 | 0 | 127.257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 748.271 | 149.6542 | 1.497% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 18:00 | 5 | 1 | 18 | 121 | 2898 | 62.06 | 24.3717 | 298.4105 | 298.4105 | -274.0387 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 364.7239 | 364.7239 | 0 | 8.5 | 0 | 60.7873 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 357.4294 | 71.4859 | 0.7149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 19:00 | 5 | 1 | 19 | 121 | 2899 | 60.08 | 49.3758 | 238.7601 | 238.7601 | -189.3843 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 291.8179 | 291.8179 | 0 | 8.5 | 0 | 48.6363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 285.9815 | 57.1963 | 0.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 20:00 | 5 | 1 | 20 | 121 | 2900 | 60.08 | 238.1701 | 132.2099 | 132.2099 | 105.9602 | Heating | 93.4943 | 8.5 | 93.4943 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.6989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 95.4023 | 0 | 19.0805 | 0.1908% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 21:00 | 5 | 1 | 21 | 121 | 2901 | 55.04 | 96.7079 | 93.2118 | 93.2118 | 3.4961 | Heating | 3.0848 | 8.5 | 3.0848 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.61696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.1477 | 0 | 0.62955 | 0.006295% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 22:00 | 5 | 1 | 22 | 121 | 2902 | 53.96 | 122.7539 | 0 | 0 | 122.7539 | Heating | 108.3122 | 8.5 | 108.3122 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.6624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 110.5227 | 0 | 22.1045 | 0.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-01 23:00 | 5 | 1 | 23 | 121 | 2903 | 53.96 | 191.3105 | 0 | 0 | 191.3105 | Heating | 168.8034 | 8.5 | 168.8034 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.7607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 172.2484 | 0 | 34.4497 | 0.3445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 | 5 | 2 | 0 | 122 | 2904 | 51.08 | 279.3831 | 0 | 0 | 279.3831 | Heating | 246.5145 | 8.5 | 246.5145 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.3029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 251.5454 | 0 | 50.3091 | 0.5031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 01:00 | 5 | 2 | 1 | 122 | 2905 | 50 | 339.339 | 0 | 0 | 339.339 | Heating | 299.4168 | 8.5 | 299.4168 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.8834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 305.5273 | 0 | 61.1055 | 0.6111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 02:00 | 5 | 2 | 2 | 122 | 2906 | 50 | 400.5476 | 0 | 0 | 400.5476 | Heating | 353.4244 | 8.5 | 353.4244 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.6849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 360.6371 | 0 | 72.1274 | 0.7213% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 03:00 | 5 | 2 | 3 | 122 | 2907 | 44.96 | 425.3217 | 0 | 0 | 425.3217 | Heating | 375.2838 | 8.5 | 375.2838 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.0568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 382.9427 | 0 | 76.5885 | 0.7659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 04:00 | 5 | 2 | 4 | 122 | 2908 | 42.08 | 444.4919 | 0 | 0 | 444.4919 | Heating | 392.1987 | 8.5 | 392.1987 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.4397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 400.2028 | 0 | 80.0406 | 0.8004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 05:00 | 5 | 2 | 5 | 122 | 2909 | 42.08 | 462.7503 | 0 | 0 | 462.7503 | Heating | 408.3091 | 8.5 | 408.3091 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.6618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 416.6419 | 0 | 83.3284 | 0.8333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 06:00 | 5 | 2 | 6 | 122 | 2910 | 44.06 | 4906.6432 | 26.9375 | 26.9375 | 4879.7058 | Heating | 4305.6227 | 8.5 | 4305.6227 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 861.1245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4393.4926 | 0 | 878.6985 | 8.787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 07:00 | 5 | 2 | 7 | 122 | 2911 | 51.08 | 3259.0992 | 0 | 0 | 3259.0992 | Heating | 2875.6758 | 8.5 | 2875.6758 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 575.1352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2934.363 | 0 | 586.8726 | 5.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 08:00 | 5 | 2 | 8 | 122 | 2912 | 51.08 | 2330.9817 | 11.4535 | 11.4535 | 2319.5281 | Heating | 2046.6425 | 8.5 | 2046.6425 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.3285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2088.4107 | 0 | 417.6821 | 4.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 09:00 | 5 | 2 | 9 | 122 | 2913 | 53.96 | 1075.736 | 88.7106 | 88.7106 | 987.0254 | Heating | 870.9048 | 8.5 | 870.9048 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.181 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 888.6783 | 0 | 177.7357 | 1.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 10:00 | 5 | 2 | 10 | 122 | 2914 | 55.04 | 283.0764 | 309.66 | 309.66 | -26.5835 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 378.4733 | 378.4733 | 0 | 8.5 | 0 | 63.0789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 370.9038 | 74.1808 | 0.7418% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 11:00 | 5 | 2 | 11 | 122 | 2915 | 55.04 | 79.6045 | 586.4419 | 586.4419 | -506.8374 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 716.7624 | 716.7624 | 0 | 8.5 | 0 | 119.4604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 702.4271 | 140.4854 | 1.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 12:00 | 5 | 2 | 12 | 122 | 2916 | 60.08 | 31.7683 | 801.359 | 801.359 | -769.5907 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 979.4388 | 979.4388 | 0 | 8.5 | 0 | 163.2398 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 959.85 | 191.97 | 1.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 13:00 | 5 | 2 | 13 | 122 | 2917 | 60.08 | 14.2824 | 1123.7177 | 1123.7177 | -1109.4353 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1373.4328 | 1373.4328 | 0 | 8.5 | 0 | 228.9055 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1345.9641 | 269.1928 | 2.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 14:00 | 5 | 2 | 14 | 122 | 2918 | 60.08 | 8.1964 | 1509.3789 | 1509.3789 | -1501.1825 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1844.7964 | 1844.7964 | 0 | 8.5 | 0 | 307.4661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1807.9004 | 361.5801 | 3.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 15:00 | 5 | 2 | 15 | 122 | 2919 | 60.08 | 6.8748 | 1583.3821 | 1583.3821 | -1576.5073 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1935.2448 | 1935.2448 | 0 | 8.5 | 0 | 322.5408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1896.5399 | 379.308 | 3.793% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 16:00 | 5 | 2 | 16 | 122 | 2920 | 60.08 | 9.0342 | 1167.5999 | 1167.5999 | -1158.5657 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1427.0666 | 1427.0666 | 0 | 8.5 | 0 | 237.8444 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1398.5252 | 279.705 | 2.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 17:00 | 5 | 2 | 17 | 122 | 2921 | 60.08 | 14.5089 | 542.8243 | 542.8243 | -528.3155 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 663.452 | 663.452 | 0 | 8.5 | 0 | 110.5753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 650.1829 | 130.0366 | 1.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 18:00 | 5 | 2 | 18 | 122 | 2922 | 57.02 | 28.4609 | 225.6224 | 225.6224 | -197.1615 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 275.7607 | 275.7607 | 0 | 8.5 | 0 | 45.9601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 270.2455 | 54.0491 | 0.5405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 19:00 | 5 | 2 | 19 | 122 | 2923 | 55.94 | 59.919 | 175.0691 | 175.0691 | -115.1501 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 213.9733 | 213.9733 | 0 | 8.5 | 0 | 35.6622 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 209.6938 | 41.9388 | 0.4194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 20:00 | 5 | 2 | 20 | 122 | 2924 | 55.94 | 222.126 | 77.8357 | 77.8357 | 144.2903 | Heating | 127.315 | 8.5 | 127.315 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 129.9132 | 0 | 25.9826 | 0.2598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 21:00 | 5 | 2 | 21 | 122 | 2925 | 51.08 | 125.8062 | 43.5281 | 43.5281 | 82.2781 | Heating | 72.5983 | 8.5 | 72.5983 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.5197 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 74.0799 | 0 | 14.816 | 0.1482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 22:00 | 5 | 2 | 22 | 122 | 2926 | 50 | 179.9715 | 0 | 0 | 179.9715 | Heating | 158.7984 | 8.5 | 158.7984 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.7597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 162.0392 | 0 | 32.4078 | 0.3241% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-02 23:00 | 5 | 2 | 23 | 122 | 2927 | 50 | 239.3047 | 0 | 0 | 239.3047 | Heating | 211.1512 | 8.5 | 211.1512 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 42.2302 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 215.4604 | 0 | 43.0921 | 0.4309% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 | 5 | 3 | 0 | 123 | 2928 | 50 | 296.2793 | 0 | 0 | 296.2793 | Heating | 261.4229 | 8.5 | 261.4229 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.2846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 266.7581 | 0 | 53.3516 | 0.5335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 01:00 | 5 | 3 | 1 | 123 | 2929 | 48.92 | 344.2421 | 0 | 0 | 344.2421 | Heating | 303.7431 | 8.5 | 303.7431 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.7486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 309.9419 | 0 | 61.9884 | 0.6199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 02:00 | 5 | 3 | 2 | 123 | 2930 | 48.92 | 388.1328 | 0 | 0 | 388.1328 | Heating | 342.4701 | 8.5 | 342.4701 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 349.4593 | 0 | 69.8919 | 0.6989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 03:00 | 5 | 3 | 3 | 123 | 2931 | 50 | 430.8686 | 0 | 0 | 430.8686 | Heating | 380.1781 | 8.5 | 380.1781 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.0356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 387.9369 | 0 | 77.5874 | 0.7759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 04:00 | 5 | 3 | 4 | 123 | 2932 | 50 | 459.3663 | 0 | 0 | 459.3663 | Heating | 405.3232 | 8.5 | 405.3232 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.0646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 413.5951 | 0 | 82.719 | 0.8272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 05:00 | 5 | 3 | 5 | 123 | 2933 | 50 | 449.604 | 0 | 0 | 449.604 | Heating | 396.7094 | 8.5 | 396.7094 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.3419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 404.8055 | 0 | 80.9611 | 0.8096% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 06:00 | 5 | 3 | 6 | 123 | 2934 | 50 | 4694.4703 | 37.7671 | 37.7671 | 4656.7032 | Heating | 4108.8558 | 8.5 | 4108.8558 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 821.7712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4192.71 | 0 | 838.542 | 8.385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 07:00 | 5 | 3 | 7 | 123 | 2935 | 51.08 | 3349.1373 | 0 | 0 | 3349.1373 | Heating | 2955.1211 | 8.5 | 2955.1211 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.0242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3015.4297 | 0 | 603.0859 | 6.031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 08:00 | 5 | 3 | 8 | 123 | 2936 | 51.08 | 2721.3965 | 0 | 0 | 2721.3965 | Heating | 2401.2322 | 8.5 | 2401.2322 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 480.2464 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2450.237 | 0 | 490.0474 | 4.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 09:00 | 5 | 3 | 9 | 123 | 2937 | 55.94 | 2012.8374 | 1.5797 | 1.5797 | 2011.2577 | Heating | 1774.6392 | 8.5 | 1774.6392 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 354.9278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1810.8563 | 0 | 362.1713 | 3.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 10:00 | 5 | 3 | 10 | 123 | 2938 | 60.98 | 1704.4936 | 14.5279 | 14.5279 | 1689.9657 | Heating | 1491.1462 | 8.5 | 1491.1462 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 298.2292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1521.5777 | 0 | 304.3155 | 3.043% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 11:00 | 5 | 3 | 11 | 123 | 2939 | 60.98 | 1300.9736 | 51.8472 | 51.8472 | 1249.1264 | Heating | 1102.1704 | 8.5 | 1102.1704 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 220.4341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1124.6637 | 0 | 224.9327 | 2.249% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 12:00 | 5 | 3 | 12 | 123 | 2940 | 62.96 | 1032.9894 | 80.4117 | 80.4117 | 952.5778 | Heating | 840.5098 | 8.5 | 840.5098 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 857.6631 | 0 | 171.5326 | 1.715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 13:00 | 5 | 3 | 13 | 123 | 2941 | 62.96 | 790.6229 | 227.6168 | 227.6168 | 563.0061 | Heating | 496.7701 | 8.5 | 496.7701 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 506.9083 | 0 | 101.3817 | 1.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 14:00 | 5 | 3 | 14 | 123 | 2942 | 62.96 | 504.7863 | 414.5665 | 414.5665 | 90.2199 | Heating | 79.6058 | 8.5 | 79.6058 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.9212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 81.2304 | 0 | 16.2461 | 0.1625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 15:00 | 5 | 3 | 15 | 123 | 2943 | 64.04 | 260.1247 | 418.6512 | 418.6512 | -158.5265 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 511.6848 | 511.6848 | 0 | 8.5 | 0 | 85.2808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 501.4511 | 100.2902 | 1.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 16:00 | 5 | 3 | 16 | 123 | 2944 | 60.08 | 175.5979 | 422.7961 | 422.7961 | -247.1982 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 516.7508 | 516.7508 | 0 | 8.5 | 0 | 86.1251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 506.4157 | 101.2831 | 1.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 17:00 | 5 | 3 | 17 | 123 | 2945 | 60.08 | 138.9671 | 398.7839 | 398.7839 | -259.8167 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 487.4025 | 487.4025 | 0 | 8.5 | 0 | 81.2338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 477.6545 | 95.5309 | 0.9553% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 18:00 | 5 | 3 | 18 | 123 | 2946 | 55.94 | 123.6903 | 213.153 | 213.153 | -89.4627 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 260.5203 | 260.5203 | 0 | 8.5 | 0 | 43.4201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 255.3099 | 51.062 | 0.5106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 19:00 | 5 | 3 | 19 | 123 | 2947 | 53.96 | 492.0437 | 161.821 | 161.821 | 330.2227 | Heating | 291.373 | 8.5 | 291.373 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.2746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 297.3194 | 0 | 59.4639 | 0.5946% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 20:00 | 5 | 3 | 20 | 123 | 2948 | 53.96 | 1014.5094 | 63.8801 | 63.8801 | 950.6293 | Heating | 838.7906 | 8.5 | 838.7906 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 167.7581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 855.9088 | 0 | 171.1818 | 1.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 21:00 | 5 | 3 | 21 | 123 | 2949 | 50 | 318.2497 | 38.8544 | 38.8544 | 279.3953 | Heating | 246.5253 | 8.5 | 246.5253 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.3051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 251.5564 | 0 | 50.3113 | 0.5031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 22:00 | 5 | 3 | 22 | 123 | 2950 | 50 | 465.9358 | 0 | 0 | 465.9358 | Heating | 411.1198 | 8.5 | 411.1198 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 419.51 | 0 | 83.902 | 0.839% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-03 23:00 | 5 | 3 | 23 | 123 | 2951 | 50 | 620.9175 | 0 | 0 | 620.9175 | Heating | 547.8684 | 8.5 | 547.8684 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.5737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 559.0494 | 0 | 111.8099 | 1.118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 | 5 | 4 | 0 | 124 | 2952 | 50 | 754.1939 | 0 | 0 | 754.1939 | Heating | 665.4652 | 8.5 | 665.4652 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 679.0462 | 0 | 135.8092 | 1.358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 01:00 | 5 | 4 | 1 | 124 | 2953 | 48.92 | 842.1496 | 0 | 0 | 842.1496 | Heating | 743.0732 | 8.5 | 743.0732 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.6146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 758.238 | 0 | 151.6476 | 1.516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 02:00 | 5 | 4 | 2 | 124 | 2954 | 48.92 | 922.6516 | 0 | 0 | 922.6516 | Heating | 814.1044 | 8.5 | 814.1044 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.8209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 830.7188 | 0 | 166.1438 | 1.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 03:00 | 5 | 4 | 3 | 124 | 2955 | 46.94 | 993.9917 | 0 | 0 | 993.9917 | Heating | 877.0515 | 8.5 | 877.0515 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.4103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 894.9505 | 0 | 178.9901 | 1.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 04:00 | 5 | 4 | 4 | 124 | 2956 | 48.92 | 1070.9577 | 0 | 0 | 1070.9577 | Heating | 944.9627 | 8.5 | 944.9627 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.9925 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 964.2477 | 0 | 192.8495 | 1.928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 05:00 | 5 | 4 | 5 | 124 | 2957 | 48.92 | 1111.1328 | 0 | 0 | 1111.1328 | Heating | 980.4113 | 8.5 | 980.4113 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.0823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1000.4197 | 0 | 200.0839 | 2.001% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 06:00 | 5 | 4 | 6 | 124 | 2958 | 48.92 | 8259.1432 | 0 | 0 | 8259.1432 | Heating | 7287.4793 | 8.5 | 7287.4793 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1457.4959 | 30% | 1 | 58.3% | 0% | 0% | 0% | 23.5601 | 0 | 0 | 0 | 23.5601 | 7436.2034 | 0 | 1487.2407 | 14.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.8347
2007-05-04 07:00 | 5 | 4 | 7 | 124 | 2959 | 50 | 4909.6016 | 0 | 0 | 4909.6016 | Heating | 4332.0014 | 8.5 | 4332.0014 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 866.4003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4420.4096 | 0 | 884.0819 | 8.841% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 08:00 | 5 | 4 | 8 | 124 | 2960 | 50 | 3230.7308 | 1.4209 | 1.4209 | 3229.3099 | Heating | 2849.3911 | 8.5 | 2849.3911 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 569.8782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2907.5419 | 0 | 581.5084 | 5.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 09:00 | 5 | 4 | 9 | 124 | 2961 | 50 | 1700.4339 | 17.1463 | 17.1463 | 1683.2876 | Heating | 1485.2538 | 8.5 | 1485.2538 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.0508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1515.5651 | 0 | 303.113 | 3.031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 10:00 | 5 | 4 | 10 | 124 | 2962 | 50 | 731.4325 | 22.1683 | 22.1683 | 709.2641 | Heating | 625.8213 | 8.5 | 625.8213 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.1643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 638.5932 | 0 | 127.7186 | 1.277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 11:00 | 5 | 4 | 11 | 124 | 2963 | 50 | 228.9769 | 26.4113 | 26.4113 | 202.5656 | Heating | 178.7343 | 8.5 | 178.7343 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.7469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 182.382 | 0 | 36.4764 | 0.3648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 12:00 | 5 | 4 | 12 | 124 | 2964 | 53.06 | 140.7468 | 35.5892 | 35.5892 | 105.1576 | Heating | 92.7862 | 8.5 | 92.7862 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.5572 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 94.6797 | 0 | 18.9359 | 0.1894% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 13:00 | 5 | 4 | 13 | 124 | 2965 | 53.06 | 81.0766 | 48.5586 | 48.5586 | 32.518 | Heating | 28.6924 | 8.5 | 28.6924 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.7385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 29.2779 | 0 | 5.8556 | 0.05856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 14:00 | 5 | 4 | 14 | 124 | 2966 | 53.06 | 40.0979 | 63.8846 | 63.8846 | -23.7867 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 78.0811 | 78.0811 | 0 | 8.5 | 0 | 13.0135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 76.5195 | 15.3039 | 0.153% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 15:00 | 5 | 4 | 15 | 124 | 2967 | 50 | 12.788 | 320.6566 | 320.6566 | -307.8686 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 391.9137 | 391.9137 | 0 | 8.5 | 0 | 65.3189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 384.0754 | 76.8151 | 0.7682% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 16:00 | 5 | 4 | 16 | 124 | 2968 | 50 | 3.7017 | 550.1561 | 550.1561 | -546.4543 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 672.413 | 672.413 | 0 | 8.5 | 0 | 112.0688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 658.9647 | 131.7929 | 1.318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 17:00 | 5 | 4 | 17 | 124 | 2969 | 50 | 1.6165 | 345.1986 | 345.1986 | -343.5821 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 421.9094 | 421.9094 | 0 | 8.5 | 0 | 70.3182 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 413.4712 | 82.6942 | 0.8269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 18:00 | 5 | 4 | 18 | 124 | 2970 | 51.08 | 2.5667 | 0 | 0 | 2.5667 | Heating | 2.2647 | 8.5 | 2.2647 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.45294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.3109 | 0 | 0.46219 | 0.004622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 19:00 | 5 | 4 | 19 | 124 | 2971 | 50 | 15.6509 | 0 | 0 | 15.6509 | Heating | 13.8097 | 8.5 | 13.8097 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.0915 | 0 | 2.8183 | 0.02818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 20:00 | 5 | 4 | 20 | 124 | 2972 | 50 | 137.0263 | 0 | 0 | 137.0263 | Heating | 120.9056 | 8.5 | 120.9056 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.1811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 123.373 | 0 | 24.6746 | 0.2467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 21:00 | 5 | 4 | 21 | 124 | 2973 | 48.02 | 619.5444 | 0 | 0 | 619.5444 | Heating | 546.6568 | 8.5 | 546.6568 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.3314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 557.8131 | 0 | 111.5626 | 1.116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 22:00 | 5 | 4 | 22 | 124 | 2974 | 48.02 | 122.3687 | 0 | 0 | 122.3687 | Heating | 107.9724 | 8.5 | 107.9724 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.5945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 110.1759 | 0 | 22.0352 | 0.2204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-04 23:00 | 5 | 4 | 23 | 124 | 2975 | 48.02 | 205.0217 | 0 | 0 | 205.0217 | Heating | 180.9015 | 8.5 | 180.9015 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.1803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 184.5934 | 0 | 36.9187 | 0.3692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 | 5 | 5 | 0 | 125 | 2976 | 48.02 | 262.7885 | 0 | 0 | 262.7885 | Heating | 231.8722 | 8.5 | 231.8722 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 46.3744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 236.6043 | 0 | 47.3209 | 0.4732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 01:00 | 5 | 5 | 1 | 125 | 2977 | 46.94 | 286.0765 | 0 | 0 | 286.0765 | Heating | 252.4204 | 8.5 | 252.4204 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.4841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 257.5718 | 0 | 51.5144 | 0.5151% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 02:00 | 5 | 5 | 2 | 125 | 2978 | 46.94 | 291.7305 | 0 | 0 | 291.7305 | Heating | 257.4092 | 8.5 | 257.4092 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.4818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 262.6625 | 0 | 52.5325 | 0.5253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 03:00 | 5 | 5 | 3 | 125 | 2979 | 46.94 | 282.5466 | 0 | 0 | 282.5466 | Heating | 249.3058 | 8.5 | 249.3058 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.8612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 254.3937 | 0 | 50.8787 | 0.5088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 04:00 | 5 | 5 | 4 | 125 | 2980 | 46.94 | 316.6485 | 0 | 0 | 316.6485 | Heating | 279.3957 | 8.5 | 279.3957 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.8791 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 285.0977 | 0 | 57.0195 | 0.5702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 05:00 | 5 | 5 | 5 | 125 | 2981 | 46.94 | 341.0237 | 0 | 0 | 341.0237 | Heating | 300.9032 | 8.5 | 300.9032 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.1806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 307.0441 | 0 | 61.4088 | 0.6141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 06:00 | 5 | 5 | 6 | 125 | 2982 | 46.04 | 332.3309 | 0 | 0 | 332.3309 | Heating | 293.2332 | 8.5 | 293.2332 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.6466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 299.2175 | 0 | 59.8435 | 0.5984% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 07:00 | 5 | 5 | 7 | 125 | 2983 | 46.94 | 299.1007 | 0 | 0 | 299.1007 | Heating | 263.9124 | 8.5 | 263.9124 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.7825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 269.2984 | 0 | 53.8597 | 0.5386% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 08:00 | 5 | 5 | 8 | 125 | 2984 | 46.94 | 3241.6165 | 0 | 0 | 3241.6165 | Heating | 2860.2499 | 8.5 | 2860.2499 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 572.05 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2918.6223 | 0 | 583.7245 | 5.837% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 09:00 | 5 | 5 | 9 | 125 | 2985 | 48.92 | 2001.5892 | 0 | 0 | 2001.5892 | Heating | 1766.1081 | 8.5 | 1766.1081 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 353.2216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1802.1511 | 0 | 360.4302 | 3.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 10:00 | 5 | 5 | 10 | 125 | 2986 | 51.98 | 1152.2221 | 0 | 0 | 1152.2221 | Heating | 1016.6666 | 8.5 | 1016.6666 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 203.3333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1037.4148 | 0 | 207.483 | 2.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 11:00 | 5 | 5 | 11 | 125 | 2987 | 51.98 | 469.4617 | 0 | 0 | 469.4617 | Heating | 414.2309 | 8.5 | 414.2309 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.8462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 422.6846 | 0 | 84.5369 | 0.8454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 12:00 | 5 | 5 | 12 | 125 | 2988 | 57.02 | 21.5868 | 0 | 0 | 21.5868 | Heating | 19.0472 | 8.5 | 19.0472 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.8094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.4359 | 0 | 3.8872 | 0.03887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 13:00 | 5 | 5 | 13 | 125 | 2989 | 60.08 | 4.9336 | 0 | 0 | 4.9336 | Heating | 4.3532 | 8.5 | 4.3532 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.87063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.442 | 0 | 0.8884 | 0.008884% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 14:00 | 5 | 5 | 14 | 125 | 2990 | 60.08 | 1.4687 | 0 | 0 | 1.4687 | Heating | 1.2959 | 8.5 | 1.2959 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.25919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.3224 | 0 | 0.26448 | 0.002645% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 15:00 | 5 | 5 | 15 | 125 | 2991 | 62.06 | 6.7933 | 0 | 0 | 6.7933 | Heating | 5.9941 | 8.5 | 5.9941 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1988 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.1164 | 0 | 1.2233 | 0.01223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 16:00 | 5 | 5 | 16 | 125 | 2992 | 62.06 | 15.4734 | 0 | 0 | 15.4734 | Heating | 13.653 | 8.5 | 13.653 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.9317 | 0 | 2.7863 | 0.02786% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 17:00 | 5 | 5 | 17 | 125 | 2993 | 62.06 | 162.7566 | 0 | 0 | 162.7566 | Heating | 143.6088 | 8.5 | 143.6088 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.7218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 146.5395 | 0 | 29.3079 | 0.2931% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 18:00 | 5 | 5 | 18 | 125 | 2994 | 57.92 | 575.4656 | 0 | 0 | 575.4656 | Heating | 507.7637 | 8.5 | 507.7637 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.5527 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 518.1263 | 0 | 103.6253 | 1.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 19:00 | 5 | 5 | 19 | 125 | 2995 | 55.94 | 22.4012 | 0 | 0 | 22.4012 | Heating | 19.7657 | 8.5 | 19.7657 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.9531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.1691 | 0 | 4.0338 | 0.04034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 20:00 | 5 | 5 | 20 | 125 | 2996 | 55.94 | 38.34 | 0 | 0 | 38.34 | Heating | 33.8294 | 8.5 | 33.8294 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.5198 | 0 | 6.904 | 0.06904% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 21:00 | 5 | 5 | 21 | 125 | 2997 | 55.04 | 36.1028 | 0 | 0 | 36.1028 | Heating | 31.8554 | 8.5 | 31.8554 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.3711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 32.5055 | 0 | 6.5011 | 0.06501% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 22:00 | 5 | 5 | 22 | 125 | 2998 | 51.98 | 52.1352 | 0 | 0 | 52.1352 | Heating | 46.0016 | 8.5 | 46.0016 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.2003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 46.9404 | 0 | 9.3881 | 0.09388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-05 23:00 | 5 | 5 | 23 | 125 | 2999 | 51.98 | 120.82 | 0 | 0 | 120.82 | Heating | 106.6059 | 8.5 | 106.6059 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.3212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 108.7815 | 0 | 21.7563 | 0.2176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 | 5 | 6 | 0 | 126 | 3000 | 48.92 | 147.3924 | 0 | 0 | 147.3924 | Heating | 130.0521 | 8.5 | 130.0521 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.0104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 132.7063 | 0 | 26.5413 | 0.2654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 01:00 | 5 | 6 | 1 | 126 | 3001 | 42.98 | 130.1933 | 0 | 0 | 130.1933 | Heating | 114.8765 | 8.5 | 114.8765 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.9753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 117.2209 | 0 | 23.4442 | 0.2344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 02:00 | 5 | 6 | 2 | 126 | 3002 | 42.98 | 155.7583 | 0 | 0 | 155.7583 | Heating | 137.4338 | 8.5 | 137.4338 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.4868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 140.2386 | 0 | 28.0477 | 0.2805% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 03:00 | 5 | 6 | 3 | 126 | 3003 | 44.96 | 206.135 | 0 | 0 | 206.135 | Heating | 181.8838 | 8.5 | 181.8838 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.3768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 185.5957 | 0 | 37.1191 | 0.3712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 04:00 | 5 | 6 | 4 | 126 | 3004 | 42.08 | 246.6082 | 0 | 0 | 246.6082 | Heating | 217.5955 | 8.5 | 217.5955 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.5191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 222.0362 | 0 | 44.4072 | 0.4441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 05:00 | 5 | 6 | 5 | 126 | 3005 | 42.08 | 309.6596 | 0 | 0 | 309.6596 | Heating | 273.229 | 8.5 | 273.229 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.6458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 278.8051 | 0 | 55.761 | 0.5576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 06:00 | 5 | 6 | 6 | 126 | 3006 | 46.04 | 4099.2758 | 35.7438 | 35.7438 | 4063.532 | Heating | 3585.4694 | 8.5 | 3585.4694 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 717.0939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3658.6422 | 0 | 731.7284 | 7.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 07:00 | 5 | 6 | 7 | 126 | 3007 | 48.92 | 3041.9785 | 0 | 0 | 3041.9785 | Heating | 2684.0987 | 8.5 | 2684.0987 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 536.8197 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2738.8762 | 0 | 547.7752 | 5.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 08:00 | 5 | 6 | 8 | 126 | 3008 | 48.92 | 2354.9409 | 0 | 0 | 2354.9409 | Heating | 2077.889 | 8.5 | 2077.889 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 415.5778 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2120.2949 | 0 | 424.059 | 4.241% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 09:00 | 5 | 6 | 9 | 126 | 3009 | 55.94 | 1672.6366 | 0 | 0 | 1672.6366 | Heating | 1475.8558 | 8.5 | 1475.8558 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.1712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1505.9754 | 0 | 301.1951 | 3.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 10:00 | 5 | 6 | 10 | 126 | 3010 | 59 | 1395.972 | 0.57142 | 0.57142 | 1395.4006 | Heating | 1231.2358 | 8.5 | 1231.2358 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 246.2472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1256.3631 | 0 | 251.2726 | 2.513% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 11:00 | 5 | 6 | 11 | 126 | 3011 | 60.98 | 1087.2835 | 10.4077 | 10.4077 | 1076.8759 | Heating | 950.1846 | 8.5 | 950.1846 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.0369 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 969.5761 | 0 | 193.9152 | 1.939% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 12:00 | 5 | 6 | 12 | 126 | 3012 | 60.08 | 873.8172 | 18.2167 | 18.2167 | 855.6006 | Heating | 754.9417 | 8.5 | 754.9417 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.9883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 770.3486 | 0 | 154.0697 | 1.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 13:00 | 5 | 6 | 13 | 126 | 3013 | 59 | 722.2124 | 99.7299 | 99.7299 | 622.4824 | Heating | 549.2492 | 8.5 | 549.2492 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.8498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 560.4584 | 0 | 112.0917 | 1.121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 14:00 | 5 | 6 | 14 | 126 | 3014 | 59 | 562.9208 | 152.788 | 152.788 | 410.1328 | Heating | 361.8819 | 8.5 | 361.8819 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.3764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 369.2673 | 0 | 73.8535 | 0.7385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 15:00 | 5 | 6 | 15 | 126 | 3015 | 60.98 | 467.6088 | 177.7019 | 177.7019 | 289.9069 | Heating | 255.8002 | 8.5 | 255.8002 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.16 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 261.0206 | 0 | 52.2041 | 0.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 16:00 | 5 | 6 | 16 | 126 | 3016 | 62.06 | 432.3766 | 182.2567 | 182.2567 | 250.1199 | Heating | 220.6941 | 8.5 | 220.6941 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.1388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 225.198 | 0 | 45.0396 | 0.4504% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 17:00 | 5 | 6 | 17 | 126 | 3017 | 62.06 | 479.3252 | 112.8847 | 112.8847 | 366.4405 | Heating | 323.3298 | 8.5 | 323.3298 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 329.9284 | 0 | 65.9857 | 0.6599% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 18:00 | 5 | 6 | 18 | 126 | 3018 | 57.92 | 785.1158 | 13.0848 | 13.0848 | 772.0311 | Heating | 681.2039 | 8.5 | 681.2039 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.2408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 695.106 | 0 | 139.0212 | 1.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 19:00 | 5 | 6 | 19 | 126 | 3019 | 55.04 | 1045.2193 | 3.2065 | 3.2065 | 1042.0128 | Heating | 919.4231 | 8.5 | 919.4231 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.8846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 938.1868 | 0 | 187.6374 | 1.876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 20:00 | 5 | 6 | 20 | 126 | 3020 | 55.04 | 1229.6967 | 0 | 0 | 1229.6967 | Heating | 1085.0265 | 8.5 | 1085.0265 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.0053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1107.1699 | 0 | 221.434 | 2.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 21:00 | 5 | 6 | 21 | 126 | 3021 | 51.98 | 288.5082 | 0 | 0 | 288.5082 | Heating | 254.5661 | 8.5 | 254.5661 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.9132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 259.7613 | 0 | 51.9523 | 0.5195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 22:00 | 5 | 6 | 22 | 126 | 3022 | 48.92 | 300.2602 | 0 | 0 | 300.2602 | Heating | 264.9354 | 8.5 | 264.9354 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.9871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 270.3423 | 0 | 54.0685 | 0.5407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-06 23:00 | 5 | 6 | 23 | 126 | 3023 | 48.92 | 307.1437 | 0 | 0 | 307.1437 | Heating | 271.0092 | 8.5 | 271.0092 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.2018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 276.54 | 0 | 55.308 | 0.5531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 | 5 | 7 | 0 | 127 | 3024 | 44.96 | 309.8321 | 0 | 0 | 309.8321 | Heating | 273.3812 | 8.5 | 273.3812 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.6762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 278.9604 | 0 | 55.7921 | 0.5579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 01:00 | 5 | 7 | 1 | 127 | 3025 | 39.92 | 299.4007 | 0 | 0 | 299.4007 | Heating | 264.1771 | 8.5 | 264.1771 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.8354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 269.5684 | 0 | 53.9137 | 0.5391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 02:00 | 5 | 7 | 2 | 127 | 3026 | 39.92 | 296.3681 | 0 | 0 | 296.3681 | Heating | 261.5013 | 8.5 | 261.5013 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.3003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 266.838 | 0 | 53.3676 | 0.5337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 03:00 | 5 | 7 | 3 | 127 | 3027 | 41 | 302.7448 | 0 | 0 | 302.7448 | Heating | 267.1277 | 8.5 | 267.1277 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.4255 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 272.5793 | 0 | 54.5159 | 0.5452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 04:00 | 5 | 7 | 4 | 127 | 3028 | 41 | 307.2278 | 0 | 0 | 307.2278 | Heating | 271.0833 | 8.5 | 271.0833 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.2167 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 276.6156 | 0 | 55.3231 | 0.5532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 05:00 | 5 | 7 | 5 | 127 | 3029 | 41 | 327.6728 | 0 | 0 | 327.6728 | Heating | 289.123 | 8.5 | 289.123 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.8246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 295.0235 | 0 | 59.0047 | 0.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 06:00 | 5 | 7 | 6 | 127 | 3030 | 39.02 | 3812.2905 | 49.8539 | 49.8539 | 3762.4366 | Heating | 3319.797 | 8.5 | 3319.797 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 663.9594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3387.548 | 0 | 677.5096 | 6.775% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 07:00 | 5 | 7 | 7 | 127 | 3031 | 46.04 | 2683.6365 | 0 | 0 | 2683.6365 | Heating | 2367.9145 | 8.5 | 2367.9145 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 473.5829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2416.2393 | 0 | 483.2479 | 4.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 08:00 | 5 | 7 | 8 | 127 | 3032 | 46.04 | 1961.4098 | 0.45065 | 0.45065 | 1960.9591 | Heating | 1730.258 | 8.5 | 1730.258 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.0516 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1765.5694 | 0 | 353.1139 | 3.531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 09:00 | 5 | 7 | 9 | 127 | 3033 | 53.06 | 1008.1296 | 36.0881 | 36.0881 | 972.0415 | Heating | 857.6836 | 8.5 | 857.6836 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.5367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 875.1874 | 0 | 175.0375 | 1.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 10:00 | 5 | 7 | 10 | 127 | 3034 | 55.94 | 370.9303 | 130.2752 | 130.2752 | 240.6551 | Heating | 212.3427 | 8.5 | 212.3427 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 42.4685 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 216.6763 | 0 | 43.3353 | 0.4334% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 11:00 | 5 | 7 | 11 | 127 | 3035 | 55.94 | 115.3482 | 285.1913 | 285.1913 | -169.8431 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 348.5672 | 348.5672 | 0 | 8.5 | 0 | 58.0945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 341.5958 | 68.3192 | 0.6832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 12:00 | 5 | 7 | 12 | 127 | 3036 | 59 | 57.2241 | 436.9403 | 436.9403 | -379.7162 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 534.0381 | 534.0381 | 0 | 8.5 | 0 | 89.0063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 523.3573 | 104.6715 | 1.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 13:00 | 5 | 7 | 13 | 127 | 3037 | 62.96 | 32.719 | 732.3869 | 732.3869 | -699.6679 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 895.1396 | 895.1396 | 0 | 8.5 | 0 | 149.1899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 877.2368 | 175.4474 | 1.754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 14:00 | 5 | 7 | 14 | 127 | 3038 | 62.96 | 20.9317 | 1005.2101 | 1005.2101 | -984.2784 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1228.5901 | 1228.5901 | 0 | 8.5 | 0 | 204.765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1204.0183 | 240.8037 | 2.408% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 15:00 | 5 | 7 | 15 | 127 | 3039 | 64.04 | 14.0102 | 1142.9575 | 1142.9575 | -1128.9473 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1396.948 | 1396.948 | 0 | 8.5 | 0 | 232.8247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1369.009 | 273.8018 | 2.738% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 16:00 | 5 | 7 | 16 | 127 | 3040 | 64.94 | 6.5921 | 1112.1413 | 1112.1413 | -1105.5492 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1359.2838 | 1359.2838 | 0 | 8.5 | 0 | 226.5473 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1332.0981 | 266.4196 | 2.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 17:00 | 5 | 7 | 17 | 127 | 3041 | 64.94 | 2.0186 | 906.4347 | 906.4347 | -904.4161 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1107.8646 | 1107.8646 | 0 | 8.5 | 0 | 184.6441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1085.7073 | 217.1415 | 2.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 18:00 | 5 | 7 | 18 | 127 | 3042 | 64.04 | 1.2905 | 295.7795 | 295.7795 | -294.4891 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 361.5083 | 361.5083 | 0 | 8.5 | 0 | 60.2514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 354.2782 | 70.8556 | 0.7086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 19:00 | 5 | 7 | 19 | 127 | 3043 | 62.96 | 12.2077 | 241.2738 | 241.2738 | -229.0661 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 294.8902 | 294.8902 | 0 | 8.5 | 0 | 49.1484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 288.9924 | 57.7985 | 0.578% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 20:00 | 5 | 7 | 20 | 127 | 3044 | 62.96 | 37.8595 | 129.6344 | 129.6344 | -91.7749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 158.4421 | 158.4421 | 0 | 8.5 | 0 | 26.407 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 155.2733 | 31.0547 | 0.3105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 21:00 | 5 | 7 | 21 | 127 | 3045 | 53.96 | 77.7849 | 75.1187 | 75.1187 | 2.6663 | Heating | 2.3526 | 8.5 | 2.3526 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.47052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.4006 | 0 | 0.48012 | 0.004801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 22:00 | 5 | 7 | 22 | 127 | 3046 | 51.08 | 149.6038 | 0 | 0 | 149.6038 | Heating | 132.0034 | 8.5 | 132.0034 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.4007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 134.6973 | 0 | 26.9395 | 0.2694% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-07 23:00 | 5 | 7 | 23 | 127 | 3047 | 51.08 | 195.9436 | 0 | 0 | 195.9436 | Heating | 172.8914 | 8.5 | 172.8914 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.5783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 176.4198 | 0 | 35.284 | 0.3528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 | 5 | 8 | 0 | 128 | 3048 | 46.94 | 237.0441 | 0 | 0 | 237.0441 | Heating | 209.1566 | 8.5 | 209.1566 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.8313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 213.4251 | 0 | 42.685 | 0.4269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 01:00 | 5 | 8 | 1 | 128 | 3049 | 46.94 | 293.0082 | 0 | 0 | 293.0082 | Heating | 258.5367 | 8.5 | 258.5367 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.7073 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 263.8129 | 0 | 52.7626 | 0.5276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 02:00 | 5 | 8 | 2 | 128 | 3050 | 46.94 | 345.8141 | 0 | 0 | 345.8141 | Heating | 305.1301 | 8.5 | 305.1301 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 311.3572 | 0 | 62.2714 | 0.6227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 03:00 | 5 | 8 | 3 | 128 | 3051 | 46.94 | 390.6521 | 0 | 0 | 390.6521 | Heating | 344.693 | 8.5 | 344.693 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.9386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 351.7276 | 0 | 70.3455 | 0.7035% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 04:00 | 5 | 8 | 4 | 128 | 3052 | 46.94 | 454.5448 | 0 | 0 | 454.5448 | Heating | 401.069 | 8.5 | 401.069 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.2138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 409.254 | 0 | 81.8508 | 0.8185% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 05:00 | 5 | 8 | 5 | 128 | 3053 | 46.94 | 542.1014 | 0 | 0 | 542.1014 | Heating | 478.3248 | 8.5 | 478.3248 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 488.0865 | 0 | 97.6173 | 0.9762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 06:00 | 5 | 8 | 6 | 128 | 3054 | 44.96 | 5678.3645 | 0 | 0 | 5678.3645 | Heating | 5010.3216 | 8.5 | 5010.3216 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1002.0643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5112.573 | 0 | 1022.5146 | 10.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 07:00 | 5 | 8 | 7 | 128 | 3055 | 48.92 | 4035.4434 | 0 | 0 | 4035.4434 | Heating | 3560.6853 | 8.5 | 3560.6853 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 712.1371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3633.3524 | 0 | 726.6705 | 7.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 08:00 | 5 | 8 | 8 | 128 | 3056 | 48.92 | 3138.2387 | 42.1254 | 42.1254 | 3096.1133 | Heating | 2731.8647 | 8.5 | 2731.8647 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 546.3729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2787.6171 | 0 | 557.5234 | 5.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 09:00 | 5 | 8 | 9 | 128 | 3057 | 57.92 | 2151.6865 | 114.5681 | 114.5681 | 2037.1183 | Heating | 1797.4573 | 8.5 | 1797.4573 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 359.4915 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1834.1402 | 0 | 366.828 | 3.668% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 10:00 | 5 | 8 | 10 | 128 | 3058 | 60.98 | 1608.5522 | 157.8325 | 157.8325 | 1450.7197 | Heating | 1280.0468 | 8.5 | 1280.0468 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 256.0094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1306.1702 | 0 | 261.234 | 2.612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 11:00 | 5 | 8 | 11 | 128 | 3059 | 60.98 | 1031.5488 | 156.9997 | 156.9997 | 874.5491 | Heating | 771.661 | 8.5 | 771.661 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.3322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 787.4092 | 0 | 157.4818 | 1.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 12:00 | 5 | 8 | 12 | 128 | 3060 | 66.02 | 517.1488 | 238.4561 | 238.4561 | 278.6927 | Heating | 245.9053 | 8.5 | 245.9053 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.1811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 250.9238 | 0 | 50.1848 | 0.5018% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 13:00 | 5 | 8 | 13 | 128 | 3061 | 68 | 299.1847 | 390.5321 | 390.5321 | -91.3474 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 477.317 | 477.317 | 0 | 8.5 | 0 | 79.5528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 467.7707 | 93.5541 | 0.9355% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 14:00 | 5 | 8 | 14 | 128 | 3062 | 68 | 220.6741 | 495.3731 | 495.3731 | -274.699 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 605.456 | 605.456 | 0 | 8.5 | 0 | 100.9093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 593.3469 | 118.6694 | 1.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 15:00 | 5 | 8 | 15 | 128 | 3063 | 71.06 | 181.2423 | 483.2479 | 483.2479 | -302.0056 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 590.6363 | 590.6363 | 0 | 8.5 | 0 | 98.4394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 578.8236 | 115.7647 | 1.158% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 16:00 | 5 | 8 | 16 | 128 | 3064 | 71.06 | 142.7556 | 457.9126 | 457.9126 | -315.157 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 559.6709 | 559.6709 | 0 | 8.5 | 0 | 93.2785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 548.4775 | 109.6955 | 1.097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 17:00 | 5 | 8 | 17 | 128 | 3065 | 71.06 | 132.2657 | 414.1876 | 414.1876 | -281.9219 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 506.2293 | 506.2293 | 0 | 8.5 | 0 | 84.3716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 496.1047 | 99.2209 | 0.9922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 18:00 | 5 | 8 | 18 | 128 | 3066 | 71.96 | 171.9058 | 223.9231 | 223.9231 | -52.0173 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 273.6837 | 273.6837 | 0 | 8.5 | 0 | 45.614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 268.2101 | 53.642 | 0.5364% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 19:00 | 5 | 8 | 19 | 128 | 3067 | 68 | 523.8816 | 166.385 | 166.385 | 357.4965 | Heating | 315.4381 | 8.5 | 315.4381 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.0876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 321.8756 | 0 | 64.3751 | 0.6438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 20:00 | 5 | 8 | 20 | 128 | 3068 | 68 | 1122.2505 | 60.7385 | 60.7385 | 1061.5121 | Heating | 936.6283 | 8.5 | 936.6283 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 187.3257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 955.7432 | 0 | 191.1486 | 1.911% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 21:00 | 5 | 8 | 21 | 128 | 3069 | 64.04 | 342.2715 | 32.9904 | 32.9904 | 309.2811 | Heating | 272.8951 | 8.5 | 272.8951 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 278.4644 | 0 | 55.6929 | 0.5569% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 22:00 | 5 | 8 | 22 | 128 | 3070 | 62.06 | 448.665 | 0 | 0 | 448.665 | Heating | 395.8809 | 8.5 | 395.8809 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.1762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 403.9601 | 0 | 80.792 | 0.8079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-08 23:00 | 5 | 8 | 23 | 128 | 3071 | 62.06 | 551.0888 | 0 | 0 | 551.0888 | Heating | 486.2548 | 8.5 | 486.2548 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 97.251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 496.1784 | 0 | 99.2357 | 0.9924% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 | 5 | 9 | 0 | 129 | 3072 | 60.08 | 670.8113 | 0 | 0 | 670.8113 | Heating | 591.8923 | 8.5 | 591.8923 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.3785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 603.9718 | 0 | 120.7944 | 1.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 01:00 | 5 | 9 | 1 | 129 | 3073 | 57.92 | 784.2144 | 0 | 0 | 784.2144 | Heating | 691.9539 | 8.5 | 691.9539 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.3908 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 706.0754 | 0 | 141.2151 | 1.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 02:00 | 5 | 9 | 2 | 129 | 3074 | 57.92 | 862.7829 | 0 | 0 | 862.7829 | Heating | 761.279 | 8.5 | 761.279 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.2558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 776.8153 | 0 | 155.3631 | 1.554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 03:00 | 5 | 9 | 3 | 129 | 3075 | 57.02 | 968.6142 | 0 | 0 | 968.6142 | Heating | 854.6596 | 8.5 | 854.6596 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.9319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 872.1016 | 0 | 174.4203 | 1.744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 04:00 | 5 | 9 | 4 | 129 | 3076 | 57.02 | 1037.5075 | 0 | 0 | 1037.5075 | Heating | 915.4478 | 8.5 | 915.4478 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.0896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 934.1304 | 0 | 186.8261 | 1.868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 05:00 | 5 | 9 | 5 | 129 | 3077 | 55.94 | 1090.1034 | 0 | 0 | 1090.1034 | Heating | 961.856 | 8.5 | 961.856 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 192.3712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 981.4857 | 0 | 196.2971 | 1.963% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 06:00 | 5 | 9 | 6 | 129 | 3078 | 55.94 | 9185.5084 | 0 | 0 | 9185.5084 | Heating | 8104.8604 | 8.5 | 8104.8604 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1620.9721 | 32.42% | 1 | 64.84% | 0% | 0% | 0% | 30.086 | 0 | 0 | 0 | 30.086 | 8270.2657 | 0 | 1654.0531 | 16.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.3606
2007-05-09 07:00 | 5 | 9 | 7 | 129 | 3079 | 57.02 | 6003.8559 | 0 | 0 | 6003.8559 | Heating | 5297.5199 | 8.5 | 5297.5199 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1059.504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5405.6326 | 0 | 1081.1265 | 10.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 08:00 | 5 | 9 | 8 | 129 | 3080 | 57.02 | 3803.0629 | 2.1456 | 2.1456 | 3800.9173 | Heating | 3353.7506 | 8.5 | 3353.7506 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 670.7501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3422.1944 | 0 | 684.4389 | 6.844% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 09:00 | 5 | 9 | 9 | 129 | 3081 | 62.06 | 2075.044 | 21.477 | 21.477 | 2053.567 | Heating | 1811.9709 | 8.5 | 1811.9709 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.3942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1848.9499 | 0 | 369.79 | 3.698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 10:00 | 5 | 9 | 10 | 129 | 3082 | 64.04 | 1249.2109 | 68.8811 | 68.8811 | 1180.3298 | Heating | 1041.4675 | 8.5 | 1041.4675 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 208.2935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1062.7219 | 0 | 212.5444 | 2.125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 11:00 | 5 | 9 | 11 | 129 | 3083 | 64.04 | 448.1497 | 119.5057 | 119.5057 | 328.644 | Heating | 289.98 | 8.5 | 289.98 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.996 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 295.8979 | 0 | 59.1796 | 0.5918% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 12:00 | 5 | 9 | 12 | 129 | 3084 | 66.02 | 174.6056 | 210.4102 | 210.4102 | -35.8046 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 257.168 | 257.168 | 0 | 8.5 | 0 | 42.8613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 252.0247 | 50.4049 | 0.504% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 13:00 | 5 | 9 | 13 | 129 | 3085 | 66.02 | 109.7488 | 418.6565 | 418.6565 | -308.9076 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 511.6912 | 511.6912 | 0 | 8.5 | 0 | 85.2819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 501.4574 | 100.2915 | 1.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 14:00 | 5 | 9 | 14 | 129 | 3086 | 66.02 | 70.364 | 603.4694 | 603.4694 | -533.1054 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 737.5737 | 737.5737 | 0 | 8.5 | 0 | 122.929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 722.8222 | 144.5644 | 1.446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 15:00 | 5 | 9 | 15 | 129 | 3087 | 64.94 | 21.2321 | 993.8444 | 993.8444 | -972.6123 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1214.6987 | 1214.6987 | 0 | 8.5 | 0 | 202.4498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1190.4047 | 238.0809 | 2.381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 16:00 | 5 | 9 | 16 | 129 | 3088 | 64.94 | 1.7862 | 1645.4091 | 1645.4091 | -1643.6229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2011.0555 | 2011.0555 | 0 | 8.5 | 0 | 335.1759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1970.8344 | 394.1669 | 3.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 17:00 | 5 | 9 | 17 | 129 | 3089 | 64.94 | 0 | 1796.5272 | 1796.5272 | -1796.5272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2195.7554 | 2195.7554 | 0 | 8.5 | 0 | 365.9592 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2151.8403 | 430.3681 | 4.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 18:00 | 5 | 9 | 18 | 129 | 3090 | 62.96 | 0 | 1044.5392 | 1044.5392 | -1044.5392 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1276.659 | 1276.659 | 0 | 8.5 | 0 | 212.7765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1251.1258 | 250.2252 | 2.502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 19:00 | 5 | 9 | 19 | 129 | 3091 | 62.96 | 0 | 471.5215 | 471.5215 | -471.5215 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 576.3041 | 576.3041 | 0 | 8.5 | 0 | 96.0507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 564.778 | 112.9556 | 1.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 20:00 | 5 | 9 | 20 | 129 | 3092 | 62.96 | 0.61674 | 179.8001 | 179.8001 | -179.1834 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 219.7557 | 219.7557 | 0 | 8.5 | 0 | 36.626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 215.3606 | 43.0721 | 0.4307% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 21:00 | 5 | 9 | 21 | 129 | 3093 | 62.06 | 8.0576 | 124.8127 | 124.8127 | -116.7551 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 152.5489 | 152.5489 | 0 | 8.5 | 0 | 25.4248 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 149.4979 | 29.8996 | 0.299% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 22:00 | 5 | 9 | 22 | 129 | 3094 | 62.06 | 31.0722 | 0 | 0 | 31.0722 | Heating | 27.4166 | 8.5 | 27.4166 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.4833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 27.9761 | 0 | 5.5952 | 0.05595% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-09 23:00 | 5 | 9 | 23 | 129 | 3095 | 62.06 | 78.2459 | 0 | 0 | 78.2459 | Heating | 69.0405 | 8.5 | 69.0405 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.8081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 70.4495 | 0 | 14.0899 | 0.1409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 | 5 | 10 | 0 | 130 | 3096 | 62.96 | 124.9394 | 0 | 0 | 124.9394 | Heating | 110.2407 | 8.5 | 110.2407 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.0481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 112.4905 | 0 | 22.4981 | 0.225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 01:00 | 5 | 10 | 1 | 130 | 3097 | 62.96 | 149.4944 | 0 | 0 | 149.4944 | Heating | 131.9068 | 8.5 | 131.9068 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.3814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 134.5988 | 0 | 26.9198 | 0.2692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 02:00 | 5 | 10 | 2 | 130 | 3098 | 62.96 | 181.036 | 0 | 0 | 181.036 | Heating | 159.7376 | 8.5 | 159.7376 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.9475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 162.9976 | 0 | 32.5995 | 0.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 03:00 | 5 | 10 | 3 | 130 | 3099 | 62.96 | 206.3791 | 0 | 0 | 206.3791 | Heating | 182.0992 | 8.5 | 182.0992 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.4198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 185.8155 | 0 | 37.1631 | 0.3716% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 04:00 | 5 | 10 | 4 | 130 | 3100 | 62.06 | 217.4393 | 0 | 0 | 217.4393 | Heating | 191.8582 | 8.5 | 191.8582 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.3716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 195.7737 | 0 | 39.1547 | 0.3915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 05:00 | 5 | 10 | 5 | 130 | 3101 | 62.06 | 216.1996 | 0 | 0 | 216.1996 | Heating | 190.7644 | 8.5 | 190.7644 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.1529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 194.6575 | 0 | 38.9315 | 0.3893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 06:00 | 5 | 10 | 6 | 130 | 3102 | 62.96 | 2726.5175 | 81.1224 | 81.1224 | 2645.3951 | Heating | 2334.1722 | 8.5 | 2334.1722 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 466.8344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2381.8083 | 0 | 476.3617 | 4.764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 07:00 | 5 | 10 | 7 | 130 | 3103 | 62.06 | 1509.2589 | 20.6585 | 20.6585 | 1488.6004 | Heating | 1313.4709 | 8.5 | 1313.4709 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 262.6942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1340.2765 | 0 | 268.0553 | 2.681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 08:00 | 5 | 10 | 8 | 130 | 3104 | 62.06 | 559.3458 | 371.8084 | 371.8084 | 187.5374 | Heating | 165.4742 | 8.5 | 165.4742 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.0948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 168.8512 | 0 | 33.7702 | 0.3377% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 09:00 | 5 | 10 | 9 | 130 | 3105 | 66.02 | 8.5057 | 1286.7854 | 1286.7854 | -1278.2797 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1572.7377 | 1572.7377 | 0 | 8.5 | 0 | 262.123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1541.283 | 308.2566 | 3.083% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 10:00 | 5 | 10 | 10 | 130 | 3106 | 69.08 | 0 | 3027.2113 | 3027.2113 | -3027.2113 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3699.9249 | 3699.9249 | 0 | 8.5 | 0 | 616.6541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3625.9264 | 725.1853 | 7.252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 11:00 | 5 | 10 | 11 | 130 | 3107 | 69.98 | 0 | 5025.997 | 5025.997 | -5025.997 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6142.8852 | 6142.8852 | 0 | 8.5 | 0 | 1023.8142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6020.0275 | 1204.0055 | 12.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 12:00 | 5 | 10 | 12 | 130 | 3108 | 75.02 | 0 | 6212.1608 | 6212.1608 | -6212.1608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7592.641 | 7592.641 | 0 | 8.5 | 0 | 1265.4402 | 30% | 1 | 50.62% | 0% | 0% | 0% | 17.023 | 0 | 0 | 0 | 17.023 | 0 | 7440.7881 | 1488.1576 | 14.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2976
2007-05-10 13:00 | 5 | 10 | 13 | 130 | 3109 | 75.02 | 0 | 7288.4527 | 7288.4527 | -7288.4527 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8908.1089 | 8908.1089 | 0 | 8.5 | 0 | 1484.6848 | 30% | 1 | 59.39% | 0% | 0% | 0% | 24.5833 | 0 | 0 | 0 | 24.5833 | 0 | 8729.9467 | 1745.9893 | 17.46% | 1 | 34.92% | 0% | 0% | 3.6239 | 0 | 0 | 3.6239 | 28.2072
2007-05-10 14:00 | 5 | 10 | 14 | 130 | 3110 | 75.02 | 0 | 8078.9359 | 8078.9359 | -8078.9359 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9874.255 | 9874.255 | 0 | 8.5 | 0 | 1645.7092 | 32.91% | 1 | 65.83% | 0% | 0% | 0% | 31.1525 | 0 | 0 | 0 | 31.1525 | 0 | 9676.7699 | 1935.354 | 19.35% | 1 | 38.71% | 0% | 0% | 4.5923 | 0 | 0 | 4.5923 | 35.7448
2007-05-10 15:00 | 5 | 10 | 15 | 130 | 3111 | 80.6 | 0 | 8358.0198 | 8358.0198 | -8358.0198 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10215.3575 | 10215.3575 | 0 | 8.5 | 0 | 1702.5596 | 34.05% | 1 | 68.1% | 0% | 0% | 0% | 33.6834 | 0 | 0 | 0 | 33.6834 | 0 | 10011.0504 | 2002.2101 | 20.02% | 1 | 40.04% | 0% | 0% | 4.9654 | 0 | 0 | 4.9654 | 38.6488
2007-05-10 16:00 | 5 | 10 | 16 | 130 | 3112 | 78.98 | 0 | 8123.7729 | 8123.7729 | -8123.7729 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9929.0557 | 9929.0557 | 0 | 8.5 | 0 | 1654.8426 | 33.1% | 1 | 66.19% | 0% | 0% | 0% | 31.5516 | 0 | 0 | 0 | 31.5516 | 0 | 9730.4746 | 1946.0949 | 19.46% | 1 | 38.92% | 0% | 0% | 4.6511 | 0 | 0 | 4.6511 | 36.2027
2007-05-10 17:00 | 5 | 10 | 17 | 130 | 3113 | 78.98 | 0 | 7326.2356 | 7326.2356 | -7326.2356 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8954.288 | 8954.288 | 0 | 8.5 | 0 | 1492.3813 | 30% | 1 | 59.7% | 0% | 0% | 0% | 24.8774 | 0 | 0 | 0 | 24.8774 | 0 | 8775.2022 | 1755.0404 | 17.55% | 1 | 35.1% | 0% | 0% | 3.6673 | 0 | 0 | 3.6673 | 28.5446
2007-05-10 18:00 | 5 | 10 | 18 | 130 | 3114 | 75.92 | 0 | 4840.6763 | 4840.6763 | -4840.6763 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5916.3821 | 5916.3821 | 0 | 8.5 | 0 | 986.0637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5798.0545 | 1159.6109 | 11.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 19:00 | 5 | 10 | 19 | 130 | 3115 | 73.04 | 0 | 4118.6063 | 4118.6063 | -4118.6063 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5033.8522 | 5033.8522 | 0 | 8.5 | 0 | 838.9754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4933.1752 | 986.635 | 9.866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 20:00 | 5 | 10 | 20 | 130 | 3116 | 73.04 | 0 | 3241.7378 | 3241.7378 | -3241.7378 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3962.124 | 3962.124 | 0 | 8.5 | 0 | 660.354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3882.8815 | 776.5763 | 7.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 21:00 | 5 | 10 | 21 | 130 | 3117 | 69.98 | 0 | 1430.5719 | 1430.5719 | -1430.5719 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1748.4768 | 1748.4768 | 0 | 8.5 | 0 | 291.4128 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1713.5072 | 342.7014 | 3.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 22:00 | 5 | 10 | 22 | 130 | 3118 | 66.02 | 0 | 245.3439 | 245.3439 | -245.3439 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 299.8647 | 299.8647 | 0 | 8.5 | 0 | 49.9775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 293.8674 | 58.7735 | 0.5877% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-10 23:00 | 5 | 10 | 23 | 130 | 3119 | 66.02 | 0 | 129.5086 | 129.5086 | -129.5086 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 158.2883 | 158.2883 | 0 | 8.5 | 0 | 26.3814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 155.1225 | 31.0245 | 0.3102% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 | 5 | 11 | 0 | 131 | 3120 | 62.96 | 0 | 17.4463 | 17.4463 | -17.4463 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 21.3233 | 21.3233 | 0 | 8.5 | 0 | 3.5539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 20.8968 | 4.1794 | 0.04179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 01:00 | 5 | 11 | 1 | 131 | 3121 | 62.06 | 0 | 0.078906 | 0.078906 | -0.078906 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.096441 | 0.096441 | 0 | 8.5 | 0 | 0.016073 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.094512 | 0.018902 | 0.000189% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 02:00 | 5 | 11 | 2 | 131 | 3122 | 62.06 | 0.66111 | 0 | 0 | 0.66111 | Heating | 0.58333 | 8.5 | 0.58333 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.11667 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.59524 | 0 | 0.11905 | 0.00119% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 03:00 | 5 | 11 | 3 | 131 | 3123 | 57.02 | 7.5526 | 0 | 0 | 7.5526 | Heating | 6.6641 | 8.5 | 6.6641 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.8001 | 0 | 1.36 | 0.0136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 04:00 | 5 | 11 | 4 | 131 | 3124 | 57.02 | 17.1675 | 0 | 0 | 17.1675 | Heating | 15.1478 | 8.5 | 15.1478 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.0296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.4569 | 0 | 3.0914 | 0.03091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 05:00 | 5 | 11 | 5 | 131 | 3125 | 57.02 | 26.3077 | 0 | 0 | 26.3077 | Heating | 23.2127 | 8.5 | 23.2127 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.6864 | 0 | 4.7373 | 0.04737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 06:00 | 5 | 11 | 6 | 131 | 3126 | 57.02 | 1355.6215 | 149.6541 | 149.6541 | 1205.9674 | Heating | 1064.0889 | 8.5 | 1064.0889 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.8178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1085.805 | 0 | 217.161 | 2.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 07:00 | 5 | 11 | 7 | 131 | 3127 | 59 | 602.979 | 130.8423 | 130.8423 | 472.1367 | Heating | 416.5912 | 8.5 | 416.5912 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.3182 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 425.093 | 0 | 85.0186 | 0.8502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 08:00 | 5 | 11 | 8 | 131 | 3128 | 59 | 14.9845 | 635.8492 | 635.8492 | -620.8648 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 777.1491 | 777.1491 | 0 | 8.5 | 0 | 129.5248 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 761.6061 | 152.3212 | 1.523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 09:00 | 5 | 11 | 9 | 131 | 3129 | 64.94 | 0 | 1382.2042 | 1382.2042 | -1382.2042 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1689.3606 | 1689.3606 | 0 | 8.5 | 0 | 281.5601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1655.5734 | 331.1147 | 3.311% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 10:00 | 5 | 11 | 10 | 131 | 3130 | 66.02 | 0 | 3359.1448 | 3359.1448 | -3359.1448 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4105.6214 | 4105.6214 | 0 | 8.5 | 0 | 684.2702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4023.5089 | 804.7018 | 8.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 11:00 | 5 | 11 | 11 | 131 | 3131 | 66.02 | 0 | 4894.747 | 4894.747 | -4894.747 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5982.4686 | 5982.4686 | 0 | 8.5 | 0 | 997.0781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5862.8192 | 1172.5638 | 11.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 12:00 | 5 | 11 | 12 | 131 | 3132 | 69.98 | 0 | 5903.1011 | 5903.1011 | -5903.1011 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7214.9013 | 7214.9013 | 0 | 8.5 | 0 | 1202.4836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7070.6033 | 1414.1207 | 14.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 13:00 | 5 | 11 | 13 | 131 | 3133 | 71.96 | 0 | 6573.3594 | 6573.3594 | -6573.3594 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8034.1059 | 8034.1059 | 0 | 8.5 | 0 | 1339.0176 | 30% | 1 | 53.56% | 0% | 0% | 0% | 19.3861 | 0 | 0 | 0 | 19.3861 | 0 | 7873.4238 | 1574.6848 | 15.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.6606
2007-05-11 14:00 | 5 | 11 | 14 | 131 | 3134 | 71.96 | 0 | 6826.4083 | 6826.4083 | -6826.4083 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8343.3879 | 8343.3879 | 0 | 8.5 | 0 | 1390.5646 | 30% | 1 | 55.62% | 0% | 0% | 0% | 21.1456 | 0 | 0 | 0 | 21.1456 | 0 | 8176.5201 | 1635.304 | 16.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.4202
2007-05-11 15:00 | 5 | 11 | 15 | 131 | 3135 | 73.94 | 0 | 7128.7143 | 7128.7143 | -7128.7143 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8712.8731 | 8712.8731 | 0 | 8.5 | 0 | 1452.1455 | 30% | 1 | 58.09% | 0% | 0% | 0% | 23.3617 | 0 | 0 | 0 | 23.3617 | 0 | 8538.6156 | 1707.7231 | 17.08% | 1 | 34.15% | 0% | 0% | 3.4438 | 0 | 0 | 3.4438 | 26.8055
2007-05-11 16:00 | 5 | 11 | 16 | 131 | 3136 | 73.04 | 0 | 7553.9651 | 7553.9651 | -7553.9651 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9232.624 | 9232.624 | 0 | 8.5 | 0 | 1538.7707 | 30.78% | 1 | 61.55% | 0% | 0% | 0% | 26.692 | 0 | 0 | 0 | 26.692 | 0 | 9047.9716 | 1809.5943 | 18.1% | 1 | 36.19% | 0% | 0% | 3.9348 | 0 | 0 | 3.9348 | 30.6268
2007-05-11 17:00 | 5 | 11 | 17 | 131 | 3137 | 71.96 | 0 | 7323.5025 | 7323.5025 | -7323.5025 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8950.9476 | 8950.9476 | 0 | 8.5 | 0 | 1491.8246 | 30% | 1 | 59.67% | 0% | 0% | 0% | 24.856 | 0 | 0 | 0 | 24.856 | 0 | 8771.9286 | 1754.3857 | 17.54% | 1 | 35.09% | 0% | 0% | 3.6641 | 0 | 0 | 3.6641 | 28.5202
2007-05-11 18:00 | 5 | 11 | 18 | 131 | 3138 | 71.06 | 0 | 4895.6198 | 4895.6198 | -4895.6198 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5983.5353 | 5983.5353 | 0 | 8.5 | 0 | 997.2559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5863.8645 | 1172.7729 | 11.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 19:00 | 5 | 11 | 19 | 131 | 3139 | 68 | 0 | 3529.3801 | 3529.3801 | -3529.3801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4313.6867 | 4313.6867 | 0 | 8.5 | 0 | 718.9478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4227.413 | 845.4826 | 8.455% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 20:00 | 5 | 11 | 20 | 131 | 3140 | 68 | 0 | 2028.3736 | 2028.3736 | -2028.3736 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2479.1233 | 2479.1233 | 0 | 8.5 | 0 | 413.1872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2429.5408 | 485.9082 | 4.859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 21:00 | 5 | 11 | 21 | 131 | 3141 | 60.98 | 0 | 717.9491 | 717.9491 | -717.9491 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 877.4934 | 877.4934 | 0 | 8.5 | 0 | 146.2489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 859.9435 | 171.9887 | 1.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 22:00 | 5 | 11 | 22 | 131 | 3142 | 57.02 | 0 | 308.2009 | 308.2009 | -308.2009 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 376.6899 | 376.6899 | 0 | 8.5 | 0 | 62.7817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 369.1561 | 73.8312 | 0.7383% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-11 23:00 | 5 | 11 | 23 | 131 | 3143 | 57.02 | 0 | 102.7826 | 102.7826 | -102.7826 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 125.6232 | 125.6232 | 0 | 8.5 | 0 | 20.9372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 123.1107 | 24.6221 | 0.2462% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 | 5 | 12 | 0 | 132 | 3144 | 53.96 | 0 | 21.5624 | 21.5624 | -21.5624 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 26.354 | 26.354 | 0 | 8.5 | 0 | 4.3923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 25.8269 | 5.1654 | 0.05165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 01:00 | 5 | 12 | 1 | 132 | 3145 | 51.98 | 1.9453 | 0.4949 | 0.4949 | 1.4504 | Heating | 1.2798 | 8.5 | 1.2798 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.25595 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.3059 | 0 | 0.26117 | 0.002612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 02:00 | 5 | 12 | 2 | 132 | 3146 | 51.98 | 7.2912 | 0 | 0 | 7.2912 | Heating | 6.4334 | 8.5 | 6.4334 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.5647 | 0 | 1.3129 | 0.01313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 03:00 | 5 | 12 | 3 | 132 | 3147 | 55.94 | 8.8503 | 0 | 0 | 8.8503 | Heating | 7.8091 | 8.5 | 7.8091 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.9685 | 0 | 1.5937 | 0.01594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 04:00 | 5 | 12 | 4 | 132 | 3148 | 55.04 | 23.3675 | 0 | 0 | 23.3675 | Heating | 20.6184 | 8.5 | 20.6184 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.1237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.0391 | 0 | 4.2078 | 0.04208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 05:00 | 5 | 12 | 5 | 132 | 3149 | 55.04 | 34.4519 | 0 | 0 | 34.4519 | Heating | 30.3988 | 8.5 | 30.3988 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.0798 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 31.0191 | 0 | 6.2038 | 0.06204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 06:00 | 5 | 12 | 6 | 132 | 3150 | 57.92 | 33.3747 | 0 | 0 | 33.3747 | Heating | 29.4483 | 8.5 | 29.4483 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.8897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.0492 | 0 | 6.0098 | 0.0601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 07:00 | 5 | 12 | 7 | 132 | 3151 | 62.06 | 24.1632 | 0 | 0 | 24.1632 | Heating | 21.3205 | 8.5 | 21.3205 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.2641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.7556 | 0 | 4.3511 | 0.04351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 08:00 | 5 | 12 | 8 | 132 | 3152 | 62.06 | 1832.6209 | 0 | 0 | 1832.6209 | Heating | 1617.0185 | 8.5 | 1617.0185 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.4037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1650.0189 | 0 | 330.0038 | 3.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 09:00 | 5 | 12 | 9 | 132 | 3153 | 69.98 | 814.0774 | 0 | 0 | 814.0774 | Heating | 718.3036 | 8.5 | 718.3036 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 143.6607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 732.9629 | 0 | 146.5926 | 1.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 10:00 | 5 | 12 | 10 | 132 | 3154 | 73.04 | 60.6363 | 0 | 0 | 60.6363 | Heating | 53.5026 | 8.5 | 53.5026 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.7005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 54.5945 | 0 | 10.9189 | 0.1092% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 11:00 | 5 | 12 | 11 | 132 | 3155 | 73.04 | 0 | 163.5914 | 163.5914 | -163.5914 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 199.9451 | 199.9451 | 0 | 8.5 | 0 | 33.3242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 195.9462 | 39.1892 | 0.3919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 12:00 | 5 | 12 | 12 | 132 | 3156 | 80.06 | 0 | 1237.209 | 1237.209 | -1237.209 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1512.1444 | 1512.1444 | 0 | 8.5 | 0 | 252.0241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1481.9015 | 296.3803 | 2.964% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 13:00 | 5 | 12 | 13 | 132 | 3157 | 82.94 | 0 | 2171.5199 | 2171.5199 | -2171.5199 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2654.0798 | 2654.0798 | 0 | 8.5 | 0 | 442.3466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2600.9982 | 520.1996 | 5.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 14:00 | 5 | 12 | 14 | 132 | 3158 | 82.94 | 0 | 3461.6972 | 3461.6972 | -3461.6972 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4230.9632 | 4230.9632 | 0 | 8.5 | 0 | 705.1605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4146.344 | 829.2688 | 8.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 15:00 | 5 | 12 | 15 | 132 | 3159 | 84.92 | 0 | 4135.1541 | 4135.1541 | -4135.1541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5054.0772 | 5054.0772 | 0 | 8.5 | 0 | 842.3462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4952.9957 | 990.5991 | 9.906% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 16:00 | 5 | 12 | 16 | 132 | 3160 | 84.02 | 0 | 4486.9726 | 4486.9726 | -4486.9726 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5484.0777 | 5484.0777 | 0 | 8.5 | 0 | 914.0129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5374.3961 | 1074.8792 | 10.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 17:00 | 5 | 12 | 17 | 132 | 3161 | 84.02 | 0 | 4843.1945 | 4843.1945 | -4843.1945 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5919.4599 | 5919.4599 | 0 | 8.5 | 0 | 986.5767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5801.0707 | 1160.2141 | 11.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 18:00 | 5 | 12 | 18 | 132 | 3162 | 80.96 | 0 | 3225.1494 | 3225.1494 | -3225.1494 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3941.8493 | 3941.8493 | 0 | 8.5 | 0 | 656.9749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3863.0123 | 772.6025 | 7.726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 19:00 | 5 | 12 | 19 | 132 | 3163 | 78.08 | 0 | 1119.6555 | 1119.6555 | -1119.6555 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1368.4678 | 1368.4678 | 0 | 8.5 | 0 | 228.078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1341.0984 | 268.2197 | 2.682% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 20:00 | 5 | 12 | 20 | 132 | 3164 | 78.08 | 0 | 843.7119 | 843.7119 | -843.7119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1031.2034 | 1031.2034 | 0 | 8.5 | 0 | 171.8672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1010.5793 | 202.1159 | 2.021% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 21:00 | 5 | 12 | 21 | 132 | 3165 | 69.98 | 0 | 478.27 | 478.27 | -478.27 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 584.5523 | 584.5523 | 0 | 8.5 | 0 | 97.4254 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 572.8612 | 114.5722 | 1.146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 22:00 | 5 | 12 | 22 | 132 | 3166 | 68 | 0 | 263.0048 | 263.0048 | -263.0048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 321.4503 | 321.4503 | 0 | 8.5 | 0 | 53.575 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 315.0213 | 63.0043 | 0.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-12 23:00 | 5 | 12 | 23 | 132 | 3167 | 68 | 0 | 135.9424 | 135.9424 | -135.9424 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 166.1519 | 166.1519 | 0 | 8.5 | 0 | 27.692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 162.8288 | 32.5658 | 0.3257% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 | 5 | 13 | 0 | 133 | 3168 | 64.04 | 0 | 53.4091 | 53.4091 | -53.4091 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 65.2778 | 65.2778 | 0 | 8.5 | 0 | 10.8796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 63.9722 | 12.7944 | 0.1279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 01:00 | 5 | 13 | 1 | 133 | 3169 | 64.94 | 0 | 21.351 | 21.351 | -21.351 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 26.0957 | 26.0957 | 0 | 8.5 | 0 | 4.3493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 25.5737 | 5.1147 | 0.05115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 02:00 | 5 | 13 | 2 | 133 | 3170 | 64.94 | 0 | 13.0074 | 13.0074 | -13.0074 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15.8979 | 15.8979 | 0 | 8.5 | 0 | 2.6497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 15.5799 | 3.116 | 0.03116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 03:00 | 5 | 13 | 3 | 133 | 3171 | 64.04 | 0 | 6.4457 | 6.4457 | -6.4457 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7.878 | 7.878 | 0 | 8.5 | 0 | 1.313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7.7205 | 1.5441 | 0.01544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 04:00 | 5 | 13 | 4 | 133 | 3172 | 62.96 | 0 | 0.37171 | 0.37171 | -0.37171 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.45431 | 0.45431 | 0 | 8.5 | 0 | 0.075719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.44523 | 0.089046 | 0.0008905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 05:00 | 5 | 13 | 5 | 133 | 3173 | 62.96 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-05-13 06:00 | 5 | 13 | 6 | 133 | 3174 | 62.06 | 675.0887 | 396.865 | 396.865 | 278.2237 | Heating | 245.4915 | 8.5 | 245.4915 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.0983 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 250.5015 | 0 | 50.1003 | 0.501% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 07:00 | 5 | 13 | 7 | 133 | 3175 | 60.98 | 236.1535 | 326.9201 | 326.9201 | -90.7667 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 399.5691 | 399.5691 | 0 | 8.5 | 0 | 66.5948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 391.5777 | 78.3155 | 0.7832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 08:00 | 5 | 13 | 8 | 133 | 3176 | 60.98 | 0 | 2689.1051 | 2689.1051 | -2689.1051 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3286.684 | 3286.684 | 0 | 8.5 | 0 | 547.7807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3220.9503 | 644.1901 | 6.442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 09:00 | 5 | 13 | 9 | 133 | 3177 | 60.98 | 0 | 3963.9398 | 3963.9398 | -3963.9398 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4844.8153 | 4844.8153 | 0 | 8.5 | 0 | 807.4692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4747.919 | 949.5838 | 9.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 10:00 | 5 | 13 | 10 | 133 | 3178 | 62.06 | 0 | 6727.176 | 6727.176 | -6727.176 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8222.104 | 8222.104 | 0 | 8.5 | 0 | 1370.3507 | 30% | 1 | 54.81% | 0% | 0% | 0% | 20.4453 | 0 | 0 | 0 | 20.4453 | 0 | 8057.662 | 1611.5324 | 16.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.7199
2007-05-13 11:00 | 5 | 13 | 11 | 133 | 3179 | 62.06 | 0 | 9366.818 | 9366.818 | -9366.818 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11448.3331 | 11448.3331 | 0 | 8.5 | 0 | 1908.0555 | 38.16% | 1 | 76.32% | 0% | 0% | 0% | 43.7764 | 0 | 0 | 0 | 43.7764 | 0 | 11219.3665 | 2243.8733 | 22.44% | 1 | 44.88% | 0% | 0% | 6.4532 | 0 | 0 | 6.4532 | 50.2297
2007-05-13 12:00 | 5 | 13 | 12 | 133 | 3180 | 64.94 | 0 | 11130.2518 | 11130.2518 | -11130.2518 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13603.641 | 13603.641 | 0 | 8.5 | 0 | 2267.2735 | 45.35% | 1 | 90.69% | 0% | 0% | 0% | 65.0939 | 0 | 0 | 0 | 65.0939 | 0 | 13331.5682 | 2666.3136 | 26.66% | 1 | 53.33% | 0% | 0% | 9.5957 | 0 | 0 | 9.5957 | 74.6896
2007-05-13 13:00 | 5 | 13 | 13 | 133 | 3181 | 69.08 | 0 | 12488.3864 | 12488.3864 | -12488.3864 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15263.5834 | 15263.5834 | 0 | 8.5 | 0 | 2543.9306 | 50.88% | 2 | 50.88% | 50.88% | 0% | 0% | 17.2256 | 17.2256 | 0 | 0 | 34.4512 | 0 | 14958.3117 | 2991.6623 | 29.92% | 1 | 59.83% | 0% | 0% | 12.5049 | 0 | 0 | 12.5049 | 46.9561
2007-05-13 14:00 | 5 | 13 | 14 | 133 | 3182 | 69.08 | 0 | 13480.5017 | 13480.5017 | -13480.5017 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16476.1688 | 16476.1688 | 0 | 8.5 | 0 | 2746.0281 | 54.92% | 2 | 54.92% | 54.92% | 0% | 0% | 20.5368 | 20.5368 | 0 | 0 | 41.0737 | 0 | 16146.6454 | 3229.3291 | 32.29% | 1 | 64.59% | 0% | 0% | 14.9087 | 0 | 0 | 14.9087 | 55.9824
2007-05-13 15:00 | 5 | 13 | 15 | 133 | 3183 | 71.06 | 0 | 13801.0861 | 13801.0861 | -13801.0861 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16867.9942 | 16867.9942 | 0 | 8.5 | 0 | 2811.3324 | 56.23% | 2 | 56.23% | 56.23% | 0% | 0% | 21.6775 | 21.6775 | 0 | 0 | 43.3551 | 0 | 16530.6343 | 3306.1269 | 33.06% | 1 | 33.06% | 33.06% | 0% | 3.1956 | 3.1956 | 0 | 6.3911 | 49.7462
2007-05-13 16:00 | 5 | 13 | 16 | 133 | 3184 | 73.04 | 0 | 13278.0252 | 13278.0252 | -13278.0252 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16228.6975 | 16228.6975 | 0 | 8.5 | 0 | 2704.7829 | 54.1% | 2 | 54.1% | 54.1% | 0% | 0% | 19.8343 | 19.8343 | 0 | 0 | 39.6686 | 0 | 15904.1236 | 3180.8247 | 31.81% | 1 | 63.62% | 0% | 0% | 14.3987 | 0 | 0 | 14.3987 | 54.0673
2007-05-13 17:00 | 5 | 13 | 17 | 133 | 3185 | 73.04 | 0 | 12748.8459 | 12748.8459 | -12748.8459 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15581.9227 | 15581.9227 | 0 | 8.5 | 0 | 2596.9871 | 51.94% | 2 | 51.94% | 51.94% | 0% | 0% | 18.0631 | 18.0631 | 0 | 0 | 36.1262 | 0 | 15270.2843 | 3054.0569 | 30.54% | 1 | 61.08% | 0% | 0% | 13.1129 | 0 | 0 | 13.1129 | 49.2391
2007-05-13 18:00 | 5 | 13 | 18 | 133 | 3186 | 71.96 | 0 | 8214.3479 | 8214.3479 | -8214.3479 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10039.7586 | 10039.7586 | 0 | 8.5 | 0 | 1673.2931 | 33.47% | 1 | 66.93% | 0% | 0% | 0% | 32.3666 | 0 | 0 | 0 | 32.3666 | 0 | 9838.9634 | 1967.7927 | 19.68% | 1 | 39.36% | 0% | 0% | 4.7713 | 0 | 0 | 4.7713 | 37.1378
2007-05-13 19:00 | 5 | 13 | 19 | 133 | 3187 | 71.06 | 0 | 6344.638 | 6344.638 | -6344.638 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7754.5575 | 7754.5575 | 0 | 8.5 | 0 | 1292.4263 | 30% | 1 | 51.7% | 0% | 0% | 0% | 17.8696 | 0 | 0 | 0 | 17.8696 | 0 | 7599.4664 | 1519.8933 | 15.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.1441
2007-05-13 20:00 | 5 | 13 | 20 | 133 | 3188 | 71.06 | 0 | 4467.8203 | 4467.8203 | -4467.8203 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5460.6693 | 5460.6693 | 0 | 8.5 | 0 | 910.1115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5351.4559 | 1070.2912 | 10.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 21:00 | 5 | 13 | 21 | 133 | 3189 | 66.92 | 0 | 1920.8804 | 1920.8804 | -1920.8804 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2347.7428 | 2347.7428 | 0 | 8.5 | 0 | 391.2905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2300.7879 | 460.1576 | 4.602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 22:00 | 5 | 13 | 22 | 133 | 3190 | 62.06 | 0 | 487.1268 | 487.1268 | -487.1268 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 595.3772 | 595.3772 | 0 | 8.5 | 0 | 99.2295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 583.4696 | 116.6939 | 1.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-13 23:00 | 5 | 13 | 23 | 133 | 3191 | 62.06 | 0 | 267.8724 | 267.8724 | -267.8724 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 327.3995 | 327.3995 | 0 | 8.5 | 0 | 54.5666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 320.8516 | 64.1703 | 0.6417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 | 5 | 14 | 0 | 134 | 3192 | 57.92 | 0 | 135.898 | 135.898 | -135.898 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 166.0976 | 166.0976 | 0 | 8.5 | 0 | 27.6829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 162.7756 | 32.5551 | 0.3256% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 01:00 | 5 | 14 | 1 | 134 | 3193 | 57.92 | 0 | 51.9308 | 51.9308 | -51.9308 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 63.471 | 63.471 | 0 | 8.5 | 0 | 10.5785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 62.2016 | 12.4403 | 0.1244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 02:00 | 5 | 14 | 2 | 134 | 3194 | 57.92 | 0.18115 | 4.4845 | 4.4845 | -4.3033 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5.481 | 5.481 | 0 | 8.5 | 0 | 0.9135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5.3714 | 1.0743 | 0.01074% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 03:00 | 5 | 14 | 3 | 134 | 3195 | 53.96 | 5.2295 | 0 | 0 | 5.2295 | Heating | 4.6143 | 8.5 | 4.6143 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.92286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.7085 | 0 | 0.94169 | 0.009417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 04:00 | 5 | 14 | 4 | 134 | 3196 | 51.98 | 12.1313 | 0 | 0 | 12.1313 | Heating | 10.7041 | 8.5 | 10.7041 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.9225 | 0 | 2.1845 | 0.02185% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 05:00 | 5 | 14 | 5 | 134 | 3197 | 51.98 | 18.8372 | 0 | 0 | 18.8372 | Heating | 16.621 | 8.5 | 16.621 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.3242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.9602 | 0 | 3.392 | 0.03392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 06:00 | 5 | 14 | 6 | 134 | 3198 | 51.08 | 1559.5233 | 206.8217 | 206.8217 | 1352.7016 | Heating | 1193.5602 | 8.5 | 1193.5602 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1217.9186 | 0 | 243.5837 | 2.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 07:00 | 5 | 14 | 7 | 134 | 3199 | 50 | 1026.2902 | 199.2546 | 199.2546 | 827.0356 | Heating | 729.7373 | 8.5 | 729.7373 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.9475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 744.6299 | 0 | 148.926 | 1.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 08:00 | 5 | 14 | 8 | 134 | 3200 | 50 | 326.3937 | 997.5816 | 997.5816 | -671.1878 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1219.2664 | 1219.2664 | 0 | 8.5 | 0 | 203.2111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1194.881 | 238.9762 | 2.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 09:00 | 5 | 14 | 9 | 134 | 3201 | 55.94 | 1.1304 | 1990.5845 | 1990.5845 | -1989.454 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2432.9366 | 2432.9366 | 0 | 8.5 | 0 | 405.4894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2384.2778 | 476.8556 | 4.769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 10:00 | 5 | 14 | 10 | 134 | 3202 | 62.96 | 0 | 2977.4726 | 2977.4726 | -2977.4726 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3639.1332 | 3639.1332 | 0 | 8.5 | 0 | 606.5222 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3566.3506 | 713.2701 | 7.133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 11:00 | 5 | 14 | 11 | 134 | 3203 | 62.96 | 0 | 3607.2769 | 3607.2769 | -3607.2769 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4408.8939 | 4408.8939 | 0 | 8.5 | 0 | 734.8157 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4320.7161 | 864.1432 | 8.641% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 12:00 | 5 | 14 | 12 | 134 | 3204 | 69.98 | 0 | 4509.8681 | 4509.8681 | -4509.8681 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5512.061 | 5512.061 | 0 | 8.5 | 0 | 918.6768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5401.8198 | 1080.364 | 10.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 13:00 | 5 | 14 | 13 | 134 | 3205 | 71.96 | 0 | 5464.9198 | 5464.9198 | -5464.9198 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6679.3464 | 6679.3464 | 0 | 8.5 | 0 | 1113.2244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6545.7595 | 1309.1519 | 13.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 14:00 | 5 | 14 | 14 | 134 | 3206 | 71.96 | 0 | 5995.7794 | 5995.7794 | -5995.7794 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7328.1748 | 7328.1748 | 0 | 8.5 | 0 | 1221.3625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7181.6113 | 1436.3223 | 14.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 15:00 | 5 | 14 | 15 | 134 | 3207 | 77 | 0 | 6010.258 | 6010.258 | -6010.258 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7345.8709 | 7345.8709 | 0 | 8.5 | 0 | 1224.3118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7198.9535 | 1439.7907 | 14.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 16:00 | 5 | 14 | 16 | 134 | 3208 | 77 | 0 | 5467.4581 | 5467.4581 | -5467.4581 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6682.4488 | 6682.4488 | 0 | 8.5 | 0 | 1113.7415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6548.7998 | 1309.76 | 13.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 17:00 | 5 | 14 | 17 | 134 | 3209 | 77 | 0 | 4609.2861 | 4609.2861 | -4609.2861 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5633.5719 | 5633.5719 | 0 | 8.5 | 0 | 938.9286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5520.9004 | 1104.1801 | 11.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 18:00 | 5 | 14 | 18 | 134 | 3210 | 75.92 | 0 | 1811.9643 | 1811.9643 | -1811.9643 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2214.623 | 2214.623 | 0 | 8.5 | 0 | 369.1038 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2170.3305 | 434.0661 | 4.341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 19:00 | 5 | 14 | 19 | 134 | 3211 | 73.94 | 0 | 654.4076 | 654.4076 | -654.4076 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 799.8315 | 799.8315 | 0 | 8.5 | 0 | 133.3052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 783.8348 | 156.767 | 1.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 20:00 | 5 | 14 | 20 | 134 | 3212 | 73.94 | 0 | 380.4787 | 380.4787 | -380.4787 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 465.0295 | 465.0295 | 0 | 8.5 | 0 | 77.5049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 455.729 | 91.1458 | 0.9115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 21:00 | 5 | 14 | 21 | 134 | 3213 | 69.08 | 1.68 | 267.1847 | 267.1847 | -265.5048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 326.5591 | 326.5591 | 0 | 8.5 | 0 | 54.4265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 320.028 | 64.0056 | 0.6401% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 22:00 | 5 | 14 | 22 | 134 | 3214 | 66.02 | 12.1472 | 0 | 0 | 12.1472 | Heating | 10.7181 | 8.5 | 10.7181 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.9369 | 0 | 2.1874 | 0.02187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-14 23:00 | 5 | 14 | 23 | 134 | 3215 | 66.02 | 25.6432 | 0 | 0 | 25.6432 | Heating | 22.6264 | 8.5 | 22.6264 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.0881 | 0 | 4.6176 | 0.04618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 | 5 | 15 | 0 | 135 | 3216 | 64.94 | 38.3881 | 0 | 0 | 38.3881 | Heating | 33.8718 | 8.5 | 33.8718 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.5631 | 0 | 6.9126 | 0.06913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 01:00 | 5 | 15 | 1 | 135 | 3217 | 64.04 | 48.1636 | 0 | 0 | 48.1636 | Heating | 42.4973 | 8.5 | 42.4973 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.4995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.3645 | 0 | 8.6729 | 0.08673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 02:00 | 5 | 15 | 2 | 135 | 3218 | 64.04 | 52.6928 | 0 | 0 | 52.6928 | Heating | 46.4936 | 8.5 | 46.4936 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.2987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.4425 | 0 | 9.4885 | 0.09488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 03:00 | 5 | 15 | 3 | 135 | 3219 | 62.96 | 74.6858 | 0 | 0 | 74.6858 | Heating | 65.8992 | 8.5 | 65.8992 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.1798 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 67.2441 | 0 | 13.4488 | 0.1345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 04:00 | 5 | 15 | 4 | 135 | 3220 | 64.04 | 101.6215 | 0 | 0 | 101.6215 | Heating | 89.666 | 8.5 | 89.666 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.9332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 91.4959 | 0 | 18.2992 | 0.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 05:00 | 5 | 15 | 5 | 135 | 3221 | 62.96 | 115.3196 | 0 | 0 | 115.3196 | Heating | 101.7526 | 8.5 | 101.7526 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.3505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 103.8292 | 0 | 20.7658 | 0.2077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 06:00 | 5 | 15 | 6 | 135 | 3222 | 62.06 | 3080.194 | 109.8875 | 109.8875 | 2970.3065 | Heating | 2620.8586 | 8.5 | 2620.8586 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 524.1717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2674.3456 | 0 | 534.8691 | 5.349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 07:00 | 5 | 15 | 7 | 135 | 3223 | 62.96 | 2089.423 | 1.6595 | 1.6595 | 2087.7635 | Heating | 1842.1443 | 8.5 | 1842.1443 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.4289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1879.7391 | 0 | 375.9478 | 3.759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 08:00 | 5 | 15 | 8 | 135 | 3224 | 64.04 | 1372.8135 | 189.666 | 189.666 | 1183.1475 | Heating | 1043.9537 | 8.5 | 1043.9537 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 208.7907 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1065.2589 | 0 | 213.0518 | 2.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 09:00 | 5 | 15 | 9 | 135 | 3225 | 66.02 | 285.2527 | 611.9657 | 611.9657 | -326.713 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 747.9581 | 747.9581 | 0 | 8.5 | 0 | 124.6597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 732.9989 | 146.5998 | 1.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 10:00 | 5 | 15 | 10 | 135 | 3226 | 64.94 | 30.2935 | 928.2941 | 928.2941 | -898.0006 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1134.5817 | 1134.5817 | 0 | 8.5 | 0 | 189.0969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1111.89 | 222.378 | 2.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 11:00 | 5 | 15 | 11 | 135 | 3227 | 64.94 | 16.0495 | 1067.1832 | 1067.1832 | -1051.1337 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1304.335 | 1304.335 | 0 | 8.5 | 0 | 217.3892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1278.2483 | 255.6497 | 2.556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 12:00 | 5 | 15 | 12 | 135 | 3228 | 66.92 | 5.1599 | 1465.7636 | 1465.7636 | -1460.6037 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1791.4888 | 1791.4888 | 0 | 8.5 | 0 | 298.5815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1755.659 | 351.1318 | 3.511% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 13:00 | 5 | 15 | 13 | 135 | 3229 | 69.98 | 0.67302 | 2315.3819 | 2315.3819 | -2314.7088 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2829.9112 | 2829.9112 | 0 | 8.5 | 0 | 471.6519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2773.3129 | 554.6626 | 5.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 14:00 | 5 | 15 | 14 | 135 | 3230 | 71.96 | 0 | 3018.8829 | 3018.8829 | -3018.8829 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3689.7458 | 3689.7458 | 0 | 8.5 | 0 | 614.9576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3615.9509 | 723.1902 | 7.232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 15:00 | 5 | 15 | 15 | 135 | 3231 | 71.06 | 0 | 3138.8457 | 3138.8457 | -3138.8457 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3836.367 | 3836.367 | 0 | 8.5 | 0 | 639.3945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3759.6396 | 751.9279 | 7.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 16:00 | 5 | 15 | 16 | 135 | 3232 | 69.08 | 0 | 2683.0716 | 2683.0716 | -2683.0716 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3279.3098 | 3279.3098 | 0 | 8.5 | 0 | 546.5516 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3213.7236 | 642.7447 | 6.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 17:00 | 5 | 15 | 17 | 135 | 3233 | 69.08 | 0 | 2341.4502 | 2341.4502 | -2341.4502 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2861.7724 | 2861.7724 | 0 | 8.5 | 0 | 476.9621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2804.537 | 560.9074 | 5.609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 18:00 | 5 | 15 | 18 | 135 | 3234 | 69.08 | 0 | 856.3211 | 856.3211 | -856.3211 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1046.6146 | 1046.6146 | 0 | 8.5 | 0 | 174.4358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1025.6823 | 205.1365 | 2.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 19:00 | 5 | 15 | 19 | 135 | 3235 | 69.98 | 0 | 413.5995 | 413.5995 | -413.5995 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 505.5105 | 505.5105 | 0 | 8.5 | 0 | 84.2517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 495.4003 | 99.0801 | 0.9908% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 20:00 | 5 | 15 | 20 | 135 | 3236 | 69.98 | 0.63082 | 276.8397 | 276.8397 | -276.2089 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 338.3596 | 338.3596 | 0 | 8.5 | 0 | 56.3933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 331.5924 | 66.3185 | 0.6632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 21:00 | 5 | 15 | 21 | 135 | 3237 | 69.98 | 4.5736 | 211.2884 | 211.2884 | -206.7148 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 258.2414 | 258.2414 | 0 | 8.5 | 0 | 43.0402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 253.0766 | 50.6153 | 0.5062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 22:00 | 5 | 15 | 22 | 135 | 3238 | 69.98 | 13.7766 | 0 | 0 | 13.7766 | Heating | 12.1558 | 8.5 | 12.1558 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.4039 | 0 | 2.4808 | 0.02481% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-15 23:00 | 5 | 15 | 23 | 135 | 3239 | 69.98 | 25.6827 | 0 | 0 | 25.6827 | Heating | 22.6612 | 8.5 | 22.6612 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.1237 | 0 | 4.6247 | 0.04625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 | 5 | 16 | 0 | 136 | 3240 | 69.8 | 45.127 | 0 | 0 | 45.127 | Heating | 39.8179 | 8.5 | 39.8179 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.9636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.6306 | 0 | 8.1261 | 0.08126% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 01:00 | 5 | 16 | 1 | 136 | 3241 | 69.98 | 70.7581 | 0 | 0 | 70.7581 | Heating | 62.4336 | 8.5 | 62.4336 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.4867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 63.7077 | 0 | 12.7415 | 0.1274% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 02:00 | 5 | 16 | 2 | 136 | 3242 | 69.98 | 94.6356 | 0 | 0 | 94.6356 | Heating | 83.502 | 8.5 | 83.502 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.7004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 85.2061 | 0 | 17.0412 | 0.1704% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 03:00 | 5 | 16 | 3 | 136 | 3243 | 69.8 | 123.9144 | 0 | 0 | 123.9144 | Heating | 109.3362 | 8.5 | 109.3362 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.8672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 111.5676 | 0 | 22.3135 | 0.2231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 04:00 | 5 | 16 | 4 | 136 | 3244 | 69.08 | 148.9285 | 0 | 0 | 148.9285 | Heating | 131.4075 | 8.5 | 131.4075 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.2815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 134.0893 | 0 | 26.8179 | 0.2682% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 05:00 | 5 | 16 | 5 | 136 | 3245 | 69.08 | 158.0775 | 0 | 0 | 158.0775 | Heating | 139.4801 | 8.5 | 139.4801 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 142.3266 | 0 | 28.4653 | 0.2847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 06:00 | 5 | 16 | 6 | 136 | 3246 | 66.92 | 2987.3364 | 97.3243 | 97.3243 | 2890.0121 | Heating | 2550.0107 | 8.5 | 2550.0107 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 510.0021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2602.0517 | 0 | 520.4103 | 5.204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 07:00 | 5 | 16 | 7 | 136 | 3247 | 66.02 | 2038.5776 | 0.1052 | 0.1052 | 2038.4724 | Heating | 1798.6521 | 8.5 | 1798.6521 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 359.7304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1835.3593 | 0 | 367.0719 | 3.671% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 08:00 | 5 | 16 | 8 | 136 | 3248 | 66.02 | 1454.94 | 116.3932 | 116.3932 | 1338.5469 | Heating | 1181.0708 | 8.5 | 1181.0708 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 236.2142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1205.1742 | 0 | 241.0348 | 2.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 09:00 | 5 | 16 | 9 | 136 | 3249 | 69.08 | 589.5678 | 411.9619 | 411.9619 | 177.6058 | Heating | 156.711 | 8.5 | 156.711 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.3422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 159.9092 | 0 | 31.9818 | 0.3198% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 10:00 | 5 | 16 | 10 | 136 | 3250 | 71.06 | 166.2537 | 738.7136 | 738.7136 | -572.4599 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 902.8722 | 902.8722 | 0 | 8.5 | 0 | 150.4787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 884.8148 | 176.963 | 1.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 11:00 | 5 | 16 | 11 | 136 | 3251 | 71.06 | 42.8952 | 985.5052 | 985.5052 | -942.6099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1204.5063 | 1204.5063 | 0 | 8.5 | 0 | 200.7511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1180.4162 | 236.0832 | 2.361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 12:00 | 5 | 16 | 12 | 136 | 3252 | 73.4 | 20.4219 | 1060.821 | 1060.821 | -1040.3991 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1296.559 | 1296.559 | 0 | 8.5 | 0 | 216.0932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1270.6278 | 254.1256 | 2.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 13:00 | 5 | 16 | 13 | 136 | 3253 | 73.04 | 16.2957 | 1278.8811 | 1278.8811 | -1262.5854 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1563.0769 | 1563.0769 | 0 | 8.5 | 0 | 260.5128 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1531.8154 | 306.3631 | 3.064% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 14:00 | 5 | 16 | 14 | 136 | 3254 | 73.04 | 12.4527 | 1533.4141 | 1533.4141 | -1520.9614 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1874.1728 | 1874.1728 | 0 | 8.5 | 0 | 312.3621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1836.6894 | 367.3379 | 3.673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 15:00 | 5 | 16 | 15 | 136 | 3255 | 71.06 | 2.4884 | 2342.0375 | 2342.0375 | -2339.5491 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2862.4903 | 2862.4903 | 0 | 8.5 | 0 | 477.0817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2805.2405 | 561.0481 | 5.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 16:00 | 5 | 16 | 16 | 136 | 3256 | 69.98 | 0.60666 | 2063.9075 | 2063.9075 | -2063.3009 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2522.5536 | 2522.5536 | 0 | 8.5 | 0 | 420.4256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2472.1026 | 494.4205 | 4.944% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 17:00 | 5 | 16 | 17 | 136 | 3257 | 71.06 | 4.7835 | 848.3009 | 848.3009 | -843.5174 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1036.8123 | 1036.8123 | 0 | 8.5 | 0 | 172.802 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1016.076 | 203.2152 | 2.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 18:00 | 5 | 16 | 18 | 136 | 3258 | 69.98 | 8.4424 | 320.3603 | 320.3603 | -311.9179 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 391.5515 | 391.5515 | 0 | 8.5 | 0 | 65.2586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 383.7204 | 76.7441 | 0.7674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 19:00 | 5 | 16 | 19 | 136 | 3259 | 69.98 | 10.7726 | 295.476 | 295.476 | -284.7034 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 361.1373 | 361.1373 | 0 | 8.5 | 0 | 60.1896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 353.9146 | 70.7829 | 0.7078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 20:00 | 5 | 16 | 20 | 136 | 3260 | 69.98 | 17.0727 | 188.3956 | 188.3956 | -171.3229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 230.2612 | 230.2612 | 0 | 8.5 | 0 | 38.3769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 225.656 | 45.1312 | 0.4513% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 21:00 | 5 | 16 | 21 | 136 | 3261 | 62.6 | 19.2111 | 154.9302 | 154.9302 | -135.7192 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 189.3592 | 189.3592 | 0 | 8.5 | 0 | 31.5599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 185.572 | 37.1144 | 0.3711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 22:00 | 5 | 16 | 22 | 136 | 3262 | 53.06 | 25.7454 | 0 | 0 | 25.7454 | Heating | 22.7166 | 8.5 | 22.7166 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.1802 | 0 | 4.636 | 0.04636% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-16 23:00 | 5 | 16 | 23 | 136 | 3263 | 51.08 | 37.3362 | 0 | 0 | 37.3362 | Heating | 32.9437 | 8.5 | 32.9437 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.5887 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 33.616 | 0 | 6.7232 | 0.06723% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 | 5 | 17 | 0 | 137 | 3264 | 50 | 62.4882 | 0 | 0 | 62.4882 | Heating | 55.1366 | 8.5 | 55.1366 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.0273 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.2619 | 0 | 11.2524 | 0.1125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 01:00 | 5 | 17 | 1 | 137 | 3265 | 48.02 | 89.3312 | 0 | 0 | 89.3312 | Heating | 78.8216 | 8.5 | 78.8216 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.7643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 80.4302 | 0 | 16.086 | 0.1609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 02:00 | 5 | 17 | 2 | 137 | 3266 | 46.94 | 97.5582 | 0 | 0 | 97.5582 | Heating | 86.0808 | 8.5 | 86.0808 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.2162 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 87.8375 | 0 | 17.5675 | 0.1757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 03:00 | 5 | 17 | 3 | 137 | 3267 | 48.02 | 111.8323 | 0 | 0 | 111.8323 | Heating | 98.6756 | 8.5 | 98.6756 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.7351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 100.6894 | 0 | 20.1379 | 0.2014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 04:00 | 5 | 17 | 4 | 137 | 3268 | 46.94 | 126.9452 | 0 | 0 | 126.9452 | Heating | 112.0104 | 8.5 | 112.0104 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.4021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 114.2964 | 0 | 22.8593 | 0.2286% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 05:00 | 5 | 17 | 5 | 137 | 3269 | 46.94 | 114.9304 | 0 | 0 | 114.9304 | Heating | 101.4091 | 8.5 | 101.4091 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.2818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 103.4787 | 0 | 20.6957 | 0.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 06:00 | 5 | 17 | 6 | 137 | 3270 | 46.04 | 1860.6377 | 85.4432 | 85.4432 | 1775.1945 | Heating | 1566.3481 | 8.5 | 1566.3481 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.2696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1598.3144 | 0 | 319.6629 | 3.197% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 07:00 | 5 | 17 | 7 | 137 | 3271 | 48.02 | 1406.5327 | 4.8314 | 4.8314 | 1401.7013 | Heating | 1236.7953 | 8.5 | 1236.7953 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.3591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1262.036 | 0 | 252.4072 | 2.524% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 08:00 | 5 | 17 | 8 | 137 | 3272 | 48.02 | 800.3056 | 388.6497 | 388.6497 | 411.6559 | Heating | 363.2258 | 8.5 | 363.2258 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.6452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 370.6385 | 0 | 74.1277 | 0.7413% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 09:00 | 5 | 17 | 9 | 137 | 3273 | 48.92 | 101.749 | 876.8296 | 876.8296 | -775.0806 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1071.6806 | 1071.6806 | 0 | 8.5 | 0 | 178.6134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1050.247 | 210.0494 | 2.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 10:00 | 5 | 17 | 10 | 137 | 3274 | 51.98 | 44.1859 | 1129.6919 | 1129.6919 | -1085.5059 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1380.7345 | 1380.7345 | 0 | 8.5 | 0 | 230.1224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1353.1198 | 270.624 | 2.706% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 11:00 | 5 | 17 | 11 | 137 | 3275 | 51.98 | 23.2959 | 1186.1573 | 1186.1573 | -1162.8614 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1449.7478 | 1449.7478 | 0 | 8.5 | 0 | 241.6246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1420.7528 | 284.1506 | 2.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 12:00 | 5 | 17 | 12 | 137 | 3276 | 57.92 | 6.5091 | 1959.9577 | 1959.9577 | -1953.4486 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2395.5039 | 2395.5039 | 0 | 8.5 | 0 | 399.2506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2347.5938 | 469.5188 | 4.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 13:00 | 5 | 17 | 13 | 137 | 3277 | 59 | 0.032579 | 3236.3142 | 3236.3142 | -3236.2816 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3955.4951 | 3955.4951 | 0 | 8.5 | 0 | 659.2492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3876.3852 | 775.277 | 7.753% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 14:00 | 5 | 17 | 14 | 137 | 3278 | 59 | 0 | 4272.4078 | 4272.4078 | -4272.4078 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5221.8317 | 5221.8317 | 0 | 8.5 | 0 | 870.3053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5117.3951 | 1023.479 | 10.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 15:00 | 5 | 17 | 15 | 137 | 3279 | 62.96 | 0 | 4960.6308 | 4960.6308 | -4960.6308 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6062.9932 | 6062.9932 | 0 | 8.5 | 0 | 1010.4989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5941.7333 | 1188.3467 | 11.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 16:00 | 5 | 17 | 16 | 137 | 3280 | 62.96 | 0 | 5433.3608 | 5433.3608 | -5433.3608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6640.7743 | 6640.7743 | 0 | 8.5 | 0 | 1106.7957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6507.9588 | 1301.5918 | 13.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 17:00 | 5 | 17 | 17 | 137 | 3281 | 62.96 | 0 | 5020.4646 | 5020.4646 | -5020.4646 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6136.1234 | 6136.1234 | 0 | 8.5 | 0 | 1022.6872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6013.4009 | 1202.6802 | 12.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 18:00 | 5 | 17 | 18 | 137 | 3282 | 59 | 0 | 2979.2504 | 2979.2504 | -2979.2504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3641.306 | 3641.306 | 0 | 8.5 | 0 | 606.8843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3568.4799 | 713.696 | 7.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 19:00 | 5 | 17 | 19 | 137 | 3283 | 55.94 | 0 | 1913.112 | 1913.112 | -1913.112 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2338.248 | 2338.248 | 0 | 8.5 | 0 | 389.708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2291.4831 | 458.2966 | 4.583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 20:00 | 5 | 17 | 20 | 137 | 3284 | 55.94 | 0 | 599.9376 | 599.9376 | -599.9376 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 733.2571 | 733.2571 | 0 | 8.5 | 0 | 122.2095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 718.592 | 143.7184 | 1.437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 21:00 | 5 | 17 | 21 | 137 | 3285 | 51.08 | 0 | 312.0491 | 312.0491 | -312.0491 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 381.3934 | 381.3934 | 0 | 8.5 | 0 | 63.5656 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 373.7655 | 74.7531 | 0.7475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 22:00 | 5 | 17 | 22 | 137 | 3286 | 50 | 3.2691 | 0 | 0 | 3.2691 | Heating | 2.8845 | 8.5 | 2.8845 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.5769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.9434 | 0 | 0.58868 | 0.005887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-17 23:00 | 5 | 17 | 23 | 137 | 3287 | 50 | 14.3606 | 0 | 0 | 14.3606 | Heating | 12.6712 | 8.5 | 12.6712 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.9297 | 0 | 2.5859 | 0.02586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 | 5 | 18 | 0 | 138 | 3288 | 46.94 | 24.962 | 0 | 0 | 24.962 | Heating | 22.0253 | 8.5 | 22.0253 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.4051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.4748 | 0 | 4.495 | 0.04495% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 01:00 | 5 | 18 | 1 | 138 | 3289 | 42.98 | 34.1905 | 0 | 0 | 34.1905 | Heating | 30.1681 | 8.5 | 30.1681 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.0336 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.7837 | 0 | 6.1567 | 0.06157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 02:00 | 5 | 18 | 2 | 138 | 3290 | 42.98 | 52.9657 | 0 | 0 | 52.9657 | Heating | 46.7345 | 8.5 | 46.7345 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.3469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.6882 | 0 | 9.5376 | 0.09538% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 03:00 | 5 | 18 | 3 | 138 | 3291 | 42.98 | 82.6569 | 0 | 0 | 82.6569 | Heating | 72.9325 | 8.5 | 72.9325 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.5865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 74.421 | 0 | 14.8842 | 0.1488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 04:00 | 5 | 18 | 4 | 138 | 3292 | 39.92 | 134.9192 | 0 | 0 | 134.9192 | Heating | 119.0463 | 8.5 | 119.0463 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.8093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 121.4759 | 0 | 24.2952 | 0.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 05:00 | 5 | 18 | 5 | 138 | 3293 | 39.92 | 179.8322 | 0 | 0 | 179.8322 | Heating | 158.6755 | 8.5 | 158.6755 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.7351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 161.9137 | 0 | 32.3827 | 0.3238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 06:00 | 5 | 18 | 6 | 138 | 3294 | 46.04 | 3180.3294 | 78.2099 | 78.2099 | 3102.1195 | Heating | 2737.1642 | 8.5 | 2737.1642 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 547.4328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2793.0247 | 0 | 558.6049 | 5.586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 07:00 | 5 | 18 | 7 | 138 | 3295 | 48.92 | 2489.8572 | 0 | 0 | 2489.8572 | Heating | 2196.9328 | 8.5 | 2196.9328 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 439.3866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2241.7682 | 0 | 448.3536 | 4.484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 08:00 | 5 | 18 | 8 | 138 | 3296 | 48.92 | 2281.4611 | 0 | 0 | 2281.4611 | Heating | 2013.0539 | 8.5 | 2013.0539 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.6108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2054.1367 | 0 | 410.8273 | 4.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 09:00 | 5 | 18 | 9 | 138 | 3297 | 55.04 | 1798.3612 | 0 | 0 | 1798.3612 | Heating | 1586.7893 | 8.5 | 1586.7893 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.3579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1619.1727 | 0 | 323.8345 | 3.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 10:00 | 5 | 18 | 10 | 138 | 3298 | 57.92 | 1172.0702 | 1.5395 | 1.5395 | 1170.5307 | Heating | 1032.8212 | 8.5 | 1032.8212 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.5642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1053.8992 | 0 | 210.7798 | 2.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 11:00 | 5 | 18 | 11 | 138 | 3299 | 57.92 | 382.1977 | 28.7363 | 28.7363 | 353.4614 | Heating | 311.8777 | 8.5 | 311.8777 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.3755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 318.2425 | 0 | 63.6485 | 0.6365% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 12:00 | 5 | 18 | 12 | 138 | 3300 | 62.96 | 105.0951 | 86.169 | 86.169 | 18.9261 | Heating | 16.6995 | 8.5 | 16.6995 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.3399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.0403 | 0 | 3.4081 | 0.03408% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 13:00 | 5 | 18 | 13 | 138 | 3301 | 64.04 | 52.1932 | 147.6479 | 147.6479 | -95.4548 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 180.4586 | 180.4586 | 0 | 8.5 | 0 | 30.0764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 176.8494 | 35.3699 | 0.3537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 14:00 | 5 | 18 | 14 | 138 | 3302 | 64.04 | 29.7 | 101.8425 | 101.8425 | -72.1425 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 124.4742 | 124.4742 | 0 | 8.5 | 0 | 20.7457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 121.9847 | 24.3969 | 0.244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 15:00 | 5 | 18 | 15 | 138 | 3303 | 62.06 | 15.2852 | 139.2017 | 139.2017 | -123.9165 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 170.1354 | 170.1354 | 0 | 8.5 | 0 | 28.3559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 166.7327 | 33.3465 | 0.3335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 16:00 | 5 | 18 | 16 | 138 | 3304 | 60.08 | 4.84 | 393.6825 | 393.6825 | -388.8424 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 481.1674 | 481.1674 | 0 | 8.5 | 0 | 80.1946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 471.5441 | 94.3088 | 0.9431% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 17:00 | 5 | 18 | 17 | 138 | 3305 | 60.08 | 2.0171 | 278.4649 | 278.4649 | -276.4478 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 340.346 | 340.346 | 0 | 8.5 | 0 | 56.7243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 333.5391 | 66.7078 | 0.6671% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 18:00 | 5 | 18 | 18 | 138 | 3306 | 60.08 | 3.279 | 0 | 0 | 3.279 | Heating | 2.8932 | 8.5 | 2.8932 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.57864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.9523 | 0 | 0.59045 | 0.005905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 19:00 | 5 | 18 | 19 | 138 | 3307 | 57.92 | 32.7556 | 0 | 0 | 32.7556 | Heating | 28.902 | 8.5 | 28.902 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.7804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 29.4919 | 0 | 5.8984 | 0.05898% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 20:00 | 5 | 18 | 20 | 138 | 3308 | 57.92 | 358.9722 | 0 | 0 | 358.9722 | Heating | 316.7402 | 8.5 | 316.7402 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 323.2042 | 0 | 64.6408 | 0.6464% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 21:00 | 5 | 18 | 21 | 138 | 3309 | 53.96 | 1091.7726 | 0 | 0 | 1091.7726 | Heating | 963.3287 | 8.5 | 963.3287 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 192.6657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 982.9885 | 0 | 196.5977 | 1.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 22:00 | 5 | 18 | 22 | 138 | 3310 | 51.08 | 171.1924 | 0 | 0 | 171.1924 | Heating | 151.0521 | 8.5 | 151.0521 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.2104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 154.1348 | 0 | 30.827 | 0.3083% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-18 23:00 | 5 | 18 | 23 | 138 | 3311 | 51.08 | 236.2896 | 0 | 0 | 236.2896 | Heating | 208.4908 | 8.5 | 208.4908 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.6982 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 212.7457 | 0 | 42.5491 | 0.4255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 | 5 | 19 | 0 | 139 | 3312 | 46.04 | 295.0564 | 0 | 0 | 295.0564 | Heating | 260.3439 | 8.5 | 260.3439 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.0688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 265.657 | 0 | 53.1314 | 0.5313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 01:00 | 5 | 19 | 1 | 139 | 3313 | 44.96 | 335.1551 | 0 | 0 | 335.1551 | Heating | 295.7251 | 8.5 | 295.7251 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 301.7603 | 0 | 60.3521 | 0.6035% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 02:00 | 5 | 19 | 2 | 139 | 3314 | 44.96 | 386.2552 | 0 | 0 | 386.2552 | Heating | 340.8134 | 8.5 | 340.8134 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.1627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 347.7688 | 0 | 69.5538 | 0.6955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 03:00 | 5 | 19 | 3 | 139 | 3315 | 44.96 | 437.0638 | 0 | 0 | 437.0638 | Heating | 385.6445 | 8.5 | 385.6445 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.1289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 393.5148 | 0 | 78.703 | 0.787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 04:00 | 5 | 19 | 4 | 139 | 3316 | 39.02 | 464.2755 | 0 | 0 | 464.2755 | Heating | 409.6548 | 8.5 | 409.6548 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 418.0151 | 0 | 83.603 | 0.836% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 05:00 | 5 | 19 | 5 | 139 | 3317 | 39.02 | 472.7927 | 0 | 0 | 472.7927 | Heating | 417.17 | 8.5 | 417.17 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 425.6837 | 0 | 85.1367 | 0.8514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 06:00 | 5 | 19 | 6 | 139 | 3318 | 42.98 | 484.9229 | 0 | 0 | 484.9229 | Heating | 427.8732 | 8.5 | 427.8732 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.5746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 436.6053 | 0 | 87.3211 | 0.8732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 07:00 | 5 | 19 | 7 | 139 | 3319 | 50 | 479.3565 | 0 | 0 | 479.3565 | Heating | 422.9616 | 8.5 | 422.9616 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.5923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 431.5935 | 0 | 86.3187 | 0.8632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 08:00 | 5 | 19 | 8 | 139 | 3320 | 50 | 4978.7997 | 0 | 0 | 4978.7997 | Heating | 4393.0585 | 8.5 | 4393.0585 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 878.6117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4482.7128 | 0 | 896.5426 | 8.965% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 09:00 | 5 | 19 | 9 | 139 | 3321 | 55.04 | 3171.7298 | 0 | 0 | 3171.7298 | Heating | 2798.5851 | 8.5 | 2798.5851 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 559.717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2855.6991 | 0 | 571.1398 | 5.711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 10:00 | 5 | 19 | 10 | 139 | 3322 | 60.08 | 2335.8118 | 0 | 0 | 2335.8118 | Heating | 2061.0104 | 8.5 | 2061.0104 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.2021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2103.0718 | 0 | 420.6144 | 4.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 11:00 | 5 | 19 | 11 | 139 | 3323 | 60.08 | 1698.6157 | 0 | 0 | 1698.6157 | Heating | 1498.7786 | 8.5 | 1498.7786 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 299.7557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1529.3659 | 0 | 305.8732 | 3.059% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 12:00 | 5 | 19 | 12 | 139 | 3324 | 64.04 | 954.0147 | 0 | 0 | 954.0147 | Heating | 841.7777 | 8.5 | 841.7777 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.3555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 858.9568 | 0 | 171.7914 | 1.718% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 13:00 | 5 | 19 | 13 | 139 | 3325 | 66.02 | 700.2609 | 0 | 0 | 700.2609 | Heating | 617.8772 | 8.5 | 617.8772 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.5754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 630.487 | 0 | 126.0974 | 1.261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 14:00 | 5 | 19 | 14 | 139 | 3326 | 66.02 | 407.4348 | 0 | 0 | 407.4348 | Heating | 359.5013 | 8.5 | 359.5013 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.9003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 366.838 | 0 | 73.3676 | 0.7337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 15:00 | 5 | 19 | 15 | 139 | 3327 | 69.98 | 181.2216 | 0 | 0 | 181.2216 | Heating | 159.9014 | 8.5 | 159.9014 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.9803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 163.1647 | 0 | 32.6329 | 0.3263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 16:00 | 5 | 19 | 16 | 139 | 3328 | 68 | 161.6977 | 0 | 0 | 161.6977 | Heating | 142.6745 | 8.5 | 142.6745 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.5349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 145.5862 | 0 | 29.1172 | 0.2912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 17:00 | 5 | 19 | 17 | 139 | 3329 | 68 | 896.1534 | 0 | 0 | 896.1534 | Heating | 790.7236 | 8.5 | 790.7236 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.1447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 806.8608 | 0 | 161.3722 | 1.614% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 18:00 | 5 | 19 | 18 | 139 | 3330 | 64.94 | 1206.9665 | 0 | 0 | 1206.9665 | Heating | 1064.9704 | 8.5 | 1064.9704 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.9941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1086.7045 | 0 | 217.3409 | 2.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 19:00 | 5 | 19 | 19 | 139 | 3331 | 60.98 | 100.0763 | 0 | 0 | 100.0763 | Heating | 88.3026 | 8.5 | 88.3026 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.6605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 90.1047 | 0 | 18.0209 | 0.1802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 20:00 | 5 | 19 | 20 | 139 | 3332 | 60.98 | 152.9127 | 0 | 0 | 152.9127 | Heating | 134.923 | 8.5 | 134.923 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.9846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 137.6765 | 0 | 27.5353 | 0.2754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 21:00 | 5 | 19 | 21 | 139 | 3333 | 57.02 | 189.2853 | 0 | 0 | 189.2853 | Heating | 167.0164 | 8.5 | 167.0164 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.4033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 170.4249 | 0 | 34.085 | 0.3408% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 22:00 | 5 | 19 | 22 | 139 | 3334 | 57.02 | 222.917 | 0 | 0 | 222.917 | Heating | 196.6914 | 8.5 | 196.6914 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.3383 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 200.7056 | 0 | 40.1411 | 0.4014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-19 23:00 | 5 | 19 | 23 | 139 | 3335 | 57.02 | 284.4058 | 0 | 0 | 284.4058 | Heating | 250.9463 | 8.5 | 250.9463 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.1893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 256.0676 | 0 | 51.2135 | 0.5121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 | 5 | 20 | 0 | 140 | 3336 | 50 | 353.246 | 0 | 0 | 353.246 | Heating | 311.6876 | 8.5 | 311.6876 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.3375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 318.0486 | 0 | 63.6097 | 0.6361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 01:00 | 5 | 20 | 1 | 140 | 3337 | 48.02 | 374.9414 | 0 | 0 | 374.9414 | Heating | 330.8306 | 8.5 | 330.8306 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 66.1661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 337.5823 | 0 | 67.5165 | 0.6752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 02:00 | 5 | 20 | 2 | 140 | 3338 | 48.02 | 397.7985 | 0 | 0 | 397.7985 | Heating | 350.9987 | 8.5 | 350.9987 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.1997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 358.162 | 0 | 71.6324 | 0.7163% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 03:00 | 5 | 20 | 3 | 140 | 3339 | 42.08 | 408.7747 | 0 | 0 | 408.7747 | Heating | 360.6836 | 8.5 | 360.6836 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.1367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 368.0445 | 0 | 73.6089 | 0.7361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 04:00 | 5 | 20 | 4 | 140 | 3340 | 42.98 | 382.3656 | 0 | 0 | 382.3656 | Heating | 337.3814 | 8.5 | 337.3814 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 67.4763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 344.2667 | 0 | 68.8533 | 0.6885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 05:00 | 5 | 20 | 5 | 140 | 3341 | 42.98 | 356.8738 | 0 | 0 | 356.8738 | Heating | 314.8887 | 8.5 | 314.8887 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.9777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 321.315 | 0 | 64.263 | 0.6426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 06:00 | 5 | 20 | 6 | 140 | 3342 | 46.94 | 3975.0054 | 31.4202 | 31.4202 | 3943.5852 | Heating | 3479.634 | 8.5 | 3479.634 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 695.9268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3550.6469 | 0 | 710.1294 | 7.101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 07:00 | 5 | 20 | 7 | 140 | 3343 | 55.94 | 2223.6924 | 0 | 0 | 2223.6924 | Heating | 1962.0815 | 8.5 | 1962.0815 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 392.4163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2002.124 | 0 | 400.4248 | 4.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 08:00 | 5 | 20 | 8 | 140 | 3344 | 55.94 | 1015.3431 | 47.7283 | 47.7283 | 967.6148 | Heating | 853.7778 | 8.5 | 853.7778 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.7556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 871.2018 | 0 | 174.2404 | 1.742% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 09:00 | 5 | 20 | 9 | 140 | 3345 | 64.04 | 44.2467 | 156.9228 | 156.9228 | -112.6761 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 191.7945 | 191.7945 | 0 | 8.5 | 0 | 31.9657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 187.9586 | 37.5917 | 0.3759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 10:00 | 5 | 20 | 10 | 140 | 3346 | 66.92 | 2.3304 | 962.3947 | 962.3947 | -960.0642 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1176.2601 | 1176.2601 | 0 | 8.5 | 0 | 196.0434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1152.7349 | 230.547 | 2.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 11:00 | 5 | 20 | 11 | 140 | 3347 | 66.92 | 0 | 2962.311 | 2962.311 | -2962.311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3620.6023 | 3620.6023 | 0 | 8.5 | 0 | 603.4337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3548.1903 | 709.6381 | 7.096% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 12:00 | 5 | 20 | 12 | 140 | 3348 | 69.98 | 0 | 5038.2202 | 5038.2202 | -5038.2202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6157.8247 | 6157.8247 | 0 | 8.5 | 0 | 1026.3041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6034.6682 | 1206.9336 | 12.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 13:00 | 5 | 20 | 13 | 140 | 3349 | 71.96 | 0 | 6760.4248 | 6760.4248 | -6760.4248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8262.7414 | 8262.7414 | 0 | 8.5 | 0 | 1377.1236 | 30% | 1 | 55.08% | 0% | 0% | 0% | 20.6785 | 0 | 0 | 0 | 20.6785 | 0 | 8097.4866 | 1619.4973 | 16.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.953
2007-05-20 14:00 | 5 | 20 | 14 | 140 | 3350 | 71.96 | 0 | 7585.8904 | 7585.8904 | -7585.8904 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9271.6439 | 9271.6439 | 0 | 8.5 | 0 | 1545.274 | 30.91% | 1 | 61.81% | 0% | 0% | 0% | 26.9522 | 0 | 0 | 0 | 26.9522 | 0 | 9086.211 | 1817.2422 | 18.17% | 1 | 36.34% | 0% | 0% | 3.9731 | 0 | 0 | 3.9731 | 30.9253
2007-05-20 15:00 | 5 | 20 | 15 | 140 | 3351 | 73.94 | 0 | 7495.6588 | 7495.6588 | -7495.6588 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9161.3608 | 9161.3608 | 0 | 8.5 | 0 | 1526.8935 | 30.54% | 1 | 61.08% | 0% | 0% | 0% | 26.2205 | 0 | 0 | 0 | 26.2205 | 0 | 8978.1336 | 1795.6267 | 17.96% | 1 | 35.91% | 0% | 0% | 3.8653 | 0 | 0 | 3.8653 | 30.0858
2007-05-20 16:00 | 5 | 20 | 16 | 140 | 3352 | 71.96 | 0 | 7337.2844 | 7337.2844 | -7337.2844 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8967.792 | 8967.792 | 0 | 8.5 | 0 | 1494.632 | 30% | 1 | 59.79% | 0% | 0% | 0% | 24.9638 | 0 | 0 | 0 | 24.9638 | 0 | 8788.4362 | 1757.6872 | 17.58% | 1 | 35.15% | 0% | 0% | 3.68 | 0 | 0 | 3.68 | 28.6438
2007-05-20 17:00 | 5 | 20 | 17 | 140 | 3353 | 71.96 | 0 | 6884.8697 | 6884.8697 | -6884.8697 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8414.8408 | 8414.8408 | 0 | 8.5 | 0 | 1402.4735 | 30% | 1 | 56.1% | 0% | 0% | 0% | 21.5645 | 0 | 0 | 0 | 21.5645 | 0 | 8246.544 | 1649.3088 | 16.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.839
2007-05-20 18:00 | 5 | 20 | 18 | 140 | 3354 | 69.98 | 0 | 4654.8368 | 4654.8368 | -4654.8368 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5689.245 | 5689.245 | 0 | 8.5 | 0 | 948.2075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5575.4601 | 1115.092 | 11.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 19:00 | 5 | 20 | 19 | 140 | 3355 | 66.02 | 0 | 3778.2368 | 3778.2368 | -3778.2368 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4617.845 | 4617.845 | 0 | 8.5 | 0 | 769.6408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4525.4881 | 905.0976 | 9.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 20:00 | 5 | 20 | 20 | 140 | 3356 | 66.02 | 0 | 2749.4106 | 2749.4106 | -2749.4106 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3360.3907 | 3360.3907 | 0 | 8.5 | 0 | 560.0651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3293.1829 | 658.6366 | 6.586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 21:00 | 5 | 20 | 21 | 140 | 3357 | 62.06 | 0 | 1220.2749 | 1220.2749 | -1220.2749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1491.4471 | 1491.4471 | 0 | 8.5 | 0 | 248.5745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1461.6182 | 292.3236 | 2.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 22:00 | 5 | 20 | 22 | 140 | 3358 | 60.08 | 0 | 127.0122 | 127.0122 | -127.0122 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 155.2372 | 155.2372 | 0 | 8.5 | 0 | 25.8729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 152.1324 | 30.4265 | 0.3043% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-20 23:00 | 5 | 20 | 23 | 140 | 3359 | 60.08 | 0 | 43.3967 | 43.3967 | -43.3967 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 53.0405 | 53.0405 | 0 | 8.5 | 0 | 8.8401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 51.9797 | 10.3959 | 0.104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 | 5 | 21 | 0 | 141 | 3360 | 53.96 | 0 | 2.1484 | 2.1484 | -2.1484 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.6258 | 2.6258 | 0 | 8.5 | 0 | 0.43764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.5733 | 0.51466 | 0.005147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 01:00 | 5 | 21 | 1 | 141 | 3361 | 53.06 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-05-21 02:00 | 5 | 21 | 2 | 141 | 3362 | 53.06 | 2.3087 | 0 | 0 | 2.3087 | Heating | 2.0371 | 8.5 | 2.0371 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.40742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.0787 | 0 | 0.41574 | 0.004157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 03:00 | 5 | 21 | 3 | 141 | 3363 | 48.92 | 14.0594 | 0 | 0 | 14.0594 | Heating | 12.4053 | 8.5 | 12.4053 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.6585 | 0 | 2.5317 | 0.02532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 04:00 | 5 | 21 | 4 | 141 | 3364 | 46.94 | 21.7911 | 0 | 0 | 21.7911 | Heating | 19.2274 | 8.5 | 19.2274 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.8455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.6198 | 0 | 3.924 | 0.03924% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 05:00 | 5 | 21 | 5 | 141 | 3365 | 46.94 | 23.0203 | 0 | 0 | 23.0203 | Heating | 20.312 | 8.5 | 20.312 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.0624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.7266 | 0 | 4.1453 | 0.04145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 06:00 | 5 | 21 | 6 | 141 | 3366 | 50 | 1511.5679 | 115.2655 | 115.2655 | 1396.3024 | Heating | 1232.0315 | 8.5 | 1232.0315 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 246.4063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1257.175 | 0 | 251.435 | 2.514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 07:00 | 5 | 21 | 7 | 141 | 3367 | 55.94 | 551.2063 | 113.2145 | 113.2145 | 437.9918 | Heating | 386.4633 | 8.5 | 386.4633 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.2927 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 394.3503 | 0 | 78.8701 | 0.7887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 08:00 | 5 | 21 | 8 | 141 | 3368 | 55.94 | 8.743 | 1440.6997 | 1440.6997 | -1431.9568 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1760.8552 | 1760.8552 | 0 | 8.5 | 0 | 293.4759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1725.6381 | 345.1276 | 3.451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 09:00 | 5 | 21 | 9 | 141 | 3369 | 66.02 | 0 | 2158.79 | 2158.79 | -2158.79 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2638.5211 | 2638.5211 | 0 | 8.5 | 0 | 439.7535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2585.7506 | 517.1501 | 5.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 10:00 | 5 | 21 | 10 | 141 | 3370 | 69.98 | 0 | 2886.0509 | 2886.0509 | -2886.0509 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3527.3955 | 3527.3955 | 0 | 8.5 | 0 | 587.8993 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3456.8476 | 691.3695 | 6.914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 11:00 | 5 | 21 | 11 | 141 | 3371 | 69.98 | 0 | 3035.3204 | 3035.3204 | -3035.3204 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3709.836 | 3709.836 | 0 | 8.5 | 0 | 618.306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3635.6393 | 727.1279 | 7.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 12:00 | 5 | 21 | 12 | 141 | 3372 | 75.02 | 0 | 2350.4661 | 2350.4661 | -2350.4661 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2872.7919 | 2872.7919 | 0 | 8.5 | 0 | 478.7987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2815.3361 | 563.0672 | 5.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 13:00 | 5 | 21 | 13 | 141 | 3373 | 75.02 | 0.15776 | 1825.4312 | 1825.4312 | -1825.2734 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2231.0826 | 2231.0826 | 0 | 8.5 | 0 | 371.8471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2186.4609 | 437.2922 | 4.373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 14:00 | 5 | 21 | 14 | 141 | 3374 | 75.02 | 0.43675 | 1886.4151 | 1886.4151 | -1885.9784 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2305.6185 | 2305.6185 | 0 | 8.5 | 0 | 384.2698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2259.5061 | 451.9012 | 4.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 15:00 | 5 | 21 | 15 | 141 | 3375 | 77 | 0 | 2556.9975 | 2556.9975 | -2556.9975 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3125.2192 | 3125.2192 | 0 | 8.5 | 0 | 520.8699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3062.7148 | 612.543 | 6.125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 16:00 | 5 | 21 | 16 | 141 | 3376 | 75.02 | 0 | 2706.949 | 2706.949 | -2706.949 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3308.4932 | 3308.4932 | 0 | 8.5 | 0 | 551.4155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3242.3233 | 648.4647 | 6.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 17:00 | 5 | 21 | 17 | 141 | 3377 | 75.02 | 0 | 2710.0143 | 2710.0143 | -2710.0143 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3312.2397 | 3312.2397 | 0 | 8.5 | 0 | 552.0399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3245.9949 | 649.199 | 6.492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 18:00 | 5 | 21 | 18 | 141 | 3378 | 73.94 | 0 | 1837.6285 | 1837.6285 | -1837.6285 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2245.9904 | 2245.9904 | 0 | 8.5 | 0 | 374.3317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2201.0706 | 440.2141 | 4.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 19:00 | 5 | 21 | 19 | 141 | 3379 | 71.96 | 0 | 1039.8327 | 1039.8327 | -1039.8327 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1270.9067 | 1270.9067 | 0 | 8.5 | 0 | 211.8178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1245.4886 | 249.0977 | 2.491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 20:00 | 5 | 21 | 20 | 141 | 3380 | 71.96 | 0.035931 | 284.6563 | 284.6563 | -284.6203 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 347.9132 | 347.9132 | 0 | 8.5 | 0 | 57.9855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 340.9549 | 68.191 | 0.6819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 21:00 | 5 | 21 | 21 | 141 | 3381 | 66.92 | 0.52689 | 219.0374 | 219.0374 | -218.5105 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 267.7124 | 267.7124 | 0 | 8.5 | 0 | 44.6187 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 262.3582 | 52.4716 | 0.5247% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 22:00 | 5 | 21 | 22 | 141 | 3382 | 64.94 | 5.7771 | 0 | 0 | 5.7771 | Heating | 5.0974 | 8.5 | 5.0974 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.0195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.2015 | 0 | 1.0403 | 0.0104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-21 23:00 | 5 | 21 | 23 | 141 | 3383 | 64.94 | 26.5005 | 0 | 0 | 26.5005 | Heating | 23.3828 | 8.5 | 23.3828 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.86 | 0 | 4.772 | 0.04772% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 | 5 | 22 | 0 | 142 | 3384 | 62.96 | 58.3768 | 0 | 0 | 58.3768 | Heating | 51.509 | 8.5 | 51.509 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.3018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 52.5602 | 0 | 10.512 | 0.1051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 01:00 | 5 | 22 | 1 | 142 | 3385 | 62.06 | 90.9659 | 0 | 0 | 90.9659 | Heating | 80.264 | 8.5 | 80.264 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.0528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 81.9021 | 0 | 16.3804 | 0.1638% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 02:00 | 5 | 22 | 2 | 142 | 3386 | 62.06 | 139.0068 | 0 | 0 | 139.0068 | Heating | 122.653 | 8.5 | 122.653 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.5306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 125.1561 | 0 | 25.0312 | 0.2503% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 03:00 | 5 | 22 | 3 | 142 | 3387 | 60.98 | 207.2088 | 0 | 0 | 207.2088 | Heating | 182.8313 | 8.5 | 182.8313 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.5663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 186.5625 | 0 | 37.3125 | 0.3731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 04:00 | 5 | 22 | 4 | 142 | 3388 | 59 | 271.8441 | 0 | 0 | 271.8441 | Heating | 239.8624 | 8.5 | 239.8624 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.9725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 244.7576 | 0 | 48.9515 | 0.4895% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 05:00 | 5 | 22 | 5 | 142 | 3389 | 59 | 318.2876 | 0 | 0 | 318.2876 | Heating | 280.842 | 8.5 | 280.842 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 56.1684 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 286.5734 | 0 | 57.3147 | 0.5731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 06:00 | 5 | 22 | 6 | 142 | 3390 | 60.98 | 4406.316 | 24.4289 | 24.4289 | 4381.8871 | Heating | 3866.371 | 8.5 | 3866.371 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 773.2742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3945.2765 | 0 | 789.0553 | 7.891% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 07:00 | 5 | 22 | 7 | 142 | 3391 | 62.6 | 2428.415 | 19.2319 | 19.2319 | 2409.1831 | Heating | 2125.7498 | 8.5 | 2125.7498 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 425.15 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2169.1325 | 0 | 433.8265 | 4.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 08:00 | 5 | 22 | 8 | 142 | 3392 | 62.06 | 1314.7831 | 239.0846 | 239.0846 | 1075.6985 | Heating | 949.1457 | 8.5 | 949.1457 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 189.8291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 968.5161 | 0 | 193.7032 | 1.937% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 09:00 | 5 | 22 | 9 | 142 | 3393 | 62.96 | 207.6277 | 611.6894 | 611.6894 | -404.0616 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 747.6204 | 747.6204 | 0 | 8.5 | 0 | 124.6034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 732.668 | 146.5336 | 1.465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 10:00 | 5 | 22 | 10 | 142 | 3394 | 62.06 | 22.0731 | 1062.0099 | 1062.0099 | -1039.9369 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1298.0121 | 1298.0121 | 0 | 8.5 | 0 | 216.3354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1272.0519 | 254.4104 | 2.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 11:00 | 5 | 22 | 11 | 142 | 3395 | 64.04 | 3.545 | 1590.4576 | 1590.4576 | -1586.9126 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1943.8926 | 1943.8926 | 0 | 8.5 | 0 | 323.9821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1905.0148 | 381.003 | 3.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 12:00 | 5 | 22 | 12 | 142 | 3396 | 64.04 | 0.11331 | 2793.5864 | 2793.5864 | -2793.4731 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3414.3834 | 3414.3834 | 0 | 8.5 | 0 | 569.0639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3346.0958 | 669.2192 | 6.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 13:00 | 5 | 22 | 13 | 142 | 3397 | 62.96 | 0 | 3885.7393 | 3885.7393 | -3885.7393 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4749.2369 | 4749.2369 | 0 | 8.5 | 0 | 791.5395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4654.2522 | 930.8504 | 9.309% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 14:00 | 5 | 22 | 14 | 142 | 3398 | 62.96 | 0 | 5225.8647 | 5225.8647 | -5225.8647 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6387.1679 | 6387.1679 | 0 | 8.5 | 0 | 1064.528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6259.4246 | 1251.8849 | 12.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 15:00 | 5 | 22 | 15 | 142 | 3399 | 62.06 | 0 | 5542.3394 | 5542.3394 | -5542.3394 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6773.9704 | 6773.9704 | 0 | 8.5 | 0 | 1128.9951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6638.491 | 1327.6982 | 13.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 16:00 | 5 | 22 | 16 | 142 | 3400 | 60.98 | 0 | 5267.8701 | 5267.8701 | -5267.8701 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6438.5079 | 6438.5079 | 0 | 8.5 | 0 | 1073.0847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6309.7378 | 1261.9476 | 12.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 17:00 | 5 | 22 | 17 | 142 | 3401 | 60.08 | 0 | 4976.0735 | 4976.0735 | -4976.0735 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6081.8677 | 6081.8677 | 0 | 8.5 | 0 | 1013.6446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5960.2303 | 1192.0461 | 11.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 18:00 | 5 | 22 | 18 | 142 | 3402 | 62.06 | 0 | 2587.1494 | 2587.1494 | -2587.1494 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3162.0715 | 3162.0715 | 0 | 8.5 | 0 | 527.0119 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3098.8301 | 619.766 | 6.198% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 19:00 | 5 | 22 | 19 | 142 | 3403 | 60.08 | 0 | 1154.6712 | 1154.6712 | -1154.6712 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1411.2648 | 1411.2648 | 0 | 8.5 | 0 | 235.2108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1383.0395 | 276.6079 | 2.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 20:00 | 5 | 22 | 20 | 142 | 3404 | 60.08 | 0.41506 | 314.5704 | 314.5704 | -314.1553 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 384.4749 | 384.4749 | 0 | 8.5 | 0 | 64.0791 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 376.7854 | 75.3571 | 0.7536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 21:00 | 5 | 22 | 21 | 142 | 3405 | 60.08 | 4.3829 | 230.9038 | 230.9038 | -226.5209 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 282.2158 | 282.2158 | 0 | 8.5 | 0 | 47.036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 276.5715 | 55.3143 | 0.5531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 22:00 | 5 | 22 | 22 | 142 | 3406 | 60.08 | 15.8749 | 0 | 0 | 15.8749 | Heating | 14.0073 | 8.5 | 14.0073 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.8015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.2931 | 0 | 2.8586 | 0.02859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-22 23:00 | 5 | 22 | 23 | 142 | 3407 | 60.08 | 40.1959 | 0 | 0 | 40.1959 | Heating | 35.4669 | 8.5 | 35.4669 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.0934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 36.1908 | 0 | 7.2382 | 0.07238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 | 5 | 23 | 0 | 143 | 3408 | 59 | 70.3826 | 0 | 0 | 70.3826 | Heating | 62.1023 | 8.5 | 62.1023 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.4205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 63.3697 | 0 | 12.6739 | 0.1267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 01:00 | 5 | 23 | 1 | 143 | 3409 | 57.92 | 100.4389 | 0 | 0 | 100.4389 | Heating | 88.6226 | 8.5 | 88.6226 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.7245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 90.4312 | 0 | 18.0862 | 0.1809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 02:00 | 5 | 23 | 2 | 143 | 3410 | 57.02 | 163.0271 | 0 | 0 | 163.0271 | Heating | 143.8475 | 8.5 | 143.8475 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.7695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 146.7831 | 0 | 29.3566 | 0.2936% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 03:00 | 5 | 23 | 3 | 143 | 3411 | 55.94 | 231.9254 | 0 | 0 | 231.9254 | Heating | 204.6401 | 8.5 | 204.6401 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.928 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 208.8164 | 0 | 41.7633 | 0.4176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 04:00 | 5 | 23 | 4 | 143 | 3412 | 55.94 | 301.2968 | 0 | 0 | 301.2968 | Heating | 265.8501 | 8.5 | 265.8501 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.17 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 271.2756 | 0 | 54.2551 | 0.5426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 05:00 | 5 | 23 | 5 | 143 | 3413 | 55.94 | 341.412 | 0 | 0 | 341.412 | Heating | 301.2459 | 8.5 | 301.2459 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.2492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 307.3938 | 0 | 61.4788 | 0.6148% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 06:00 | 5 | 23 | 6 | 143 | 3414 | 57.02 | 4409.8677 | 39.1432 | 39.1432 | 4370.7245 | Heating | 3856.5216 | 8.5 | 3856.5216 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 771.3043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3935.2262 | 0 | 787.0452 | 7.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 07:00 | 5 | 23 | 7 | 143 | 3415 | 60.08 | 2651.1126 | 1.8574 | 1.8574 | 2649.2552 | Heating | 2337.5781 | 8.5 | 2337.5781 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.5156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2385.2838 | 0 | 477.0568 | 4.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 08:00 | 5 | 23 | 8 | 143 | 3416 | 60.08 | 1643.2605 | 164.0319 | 164.0319 | 1479.2286 | Heating | 1305.2017 | 8.5 | 1305.2017 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.0403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1331.8385 | 0 | 266.3677 | 2.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 09:00 | 5 | 23 | 9 | 143 | 3417 | 60.98 | 352.8738 | 584.1211 | 584.1211 | -231.2473 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 713.9258 | 713.9258 | 0 | 8.5 | 0 | 118.9876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 699.6473 | 139.9295 | 1.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 10:00 | 5 | 23 | 10 | 143 | 3418 | 60.98 | 22.8043 | 1100.2555 | 1100.2555 | -1077.4513 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1344.7567 | 1344.7567 | 0 | 8.5 | 0 | 224.1261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1317.8616 | 263.5723 | 2.636% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 11:00 | 5 | 23 | 11 | 143 | 3419 | 60.98 | 1.4331 | 2016.8999 | 2016.8999 | -2015.4668 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2465.0999 | 2465.0999 | 0 | 8.5 | 0 | 410.85 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2415.7979 | 483.1596 | 4.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 12:00 | 5 | 23 | 12 | 143 | 3420 | 64.04 | 0 | 3349.2154 | 3349.2154 | -3349.2154 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4093.4855 | 4093.4855 | 0 | 8.5 | 0 | 682.2476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4011.6158 | 802.3232 | 8.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 13:00 | 5 | 23 | 13 | 143 | 3421 | 64.04 | 0 | 4846.4957 | 4846.4957 | -4846.4957 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5923.4947 | 5923.4947 | 0 | 8.5 | 0 | 987.2491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5805.0248 | 1161.005 | 11.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 14:00 | 5 | 23 | 14 | 143 | 3422 | 64.04 | 0 | 5763.1145 | 5763.1145 | -5763.1145 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7043.8066 | 7043.8066 | 0 | 8.5 | 0 | 1173.9678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6902.9305 | 1380.5861 | 13.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 15:00 | 5 | 23 | 15 | 143 | 3423 | 64.04 | 0 | 6099.1993 | 6099.1993 | -6099.1993 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7454.5769 | 7454.5769 | 0 | 8.5 | 0 | 1242.4295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7305.4853 | 1461.0971 | 14.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 16:00 | 5 | 23 | 16 | 143 | 3424 | 64.94 | 0 | 5923.3496 | 5923.3496 | -5923.3496 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7239.6495 | 7239.6495 | 0 | 8.5 | 0 | 1206.6082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7094.8565 | 1418.9713 | 14.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 17:00 | 5 | 23 | 17 | 143 | 3425 | 64.94 | 0 | 5524.5721 | 5524.5721 | -5524.5721 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6752.2548 | 6752.2548 | 0 | 8.5 | 0 | 1125.3758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6617.2098 | 1323.442 | 13.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 18:00 | 5 | 23 | 18 | 143 | 3426 | 60.08 | 0 | 3627.9914 | 3627.9914 | -3627.9914 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4434.2117 | 4434.2117 | 0 | 8.5 | 0 | 739.0353 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4345.5275 | 869.1055 | 8.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 19:00 | 5 | 23 | 19 | 143 | 3427 | 57.92 | 0 | 2435.1596 | 2435.1596 | -2435.1596 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2976.3062 | 2976.3062 | 0 | 8.5 | 0 | 496.051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2916.78 | 583.356 | 5.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 20:00 | 5 | 23 | 20 | 143 | 3428 | 57.02 | 0 | 713.5052 | 713.5052 | -713.5052 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 872.0619 | 872.0619 | 0 | 8.5 | 0 | 145.3437 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 854.6207 | 170.9241 | 1.709% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 21:00 | 5 | 23 | 21 | 143 | 3429 | 57.02 | 0.80397 | 289.3728 | 289.3728 | -288.5688 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 353.6779 | 353.6779 | 0 | 8.5 | 0 | 58.9463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 346.6043 | 69.3209 | 0.6932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 22:00 | 5 | 23 | 22 | 143 | 3430 | 55.94 | 11.5217 | 0 | 0 | 11.5217 | Heating | 10.1662 | 8.5 | 10.1662 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.3737 | 0 | 2.0747 | 0.02075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-23 23:00 | 5 | 23 | 23 | 143 | 3431 | 55.94 | 31.6397 | 0 | 0 | 31.6397 | Heating | 27.9174 | 8.5 | 27.9174 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.5835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 28.4871 | 0 | 5.6974 | 0.05697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 | 5 | 24 | 0 | 144 | 3432 | 55.04 | 55.7072 | 0 | 0 | 55.7072 | Heating | 49.1534 | 8.5 | 49.1534 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.8307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 50.1566 | 0 | 10.0313 | 0.1003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 01:00 | 5 | 24 | 1 | 144 | 3433 | 53.96 | 84.7375 | 0 | 0 | 84.7375 | Heating | 74.7684 | 8.5 | 74.7684 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.9537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 76.2943 | 0 | 15.2589 | 0.1526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 02:00 | 5 | 24 | 2 | 144 | 3434 | 53.96 | 141.1636 | 0 | 0 | 141.1636 | Heating | 124.5561 | 8.5 | 124.5561 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.9112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 127.098 | 0 | 25.4196 | 0.2542% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 03:00 | 5 | 24 | 3 | 144 | 3435 | 55.04 | 194.1385 | 0 | 0 | 194.1385 | Heating | 171.2987 | 8.5 | 171.2987 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.2597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 174.7946 | 0 | 34.9589 | 0.3496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 04:00 | 5 | 24 | 4 | 144 | 3436 | 55.04 | 256.0177 | 0 | 0 | 256.0177 | Heating | 225.898 | 8.5 | 225.898 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.1796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 230.5082 | 0 | 46.1016 | 0.461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 05:00 | 5 | 24 | 5 | 144 | 3437 | 55.04 | 307.4677 | 0 | 0 | 307.4677 | Heating | 271.2951 | 8.5 | 271.2951 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 276.8317 | 0 | 55.3663 | 0.5537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 06:00 | 5 | 24 | 6 | 144 | 3438 | 55.04 | 4115.2352 | 77.3411 | 77.3411 | 4037.8941 | Heating | 3562.8477 | 8.5 | 3562.8477 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 712.5695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3635.5589 | 0 | 727.1118 | 7.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 07:00 | 5 | 24 | 7 | 144 | 3439 | 55.94 | 2152.0782 | 60.9143 | 60.9143 | 2091.1639 | Heating | 1845.1446 | 8.5 | 1845.1446 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.0289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1882.8006 | 0 | 376.5601 | 3.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 08:00 | 5 | 24 | 8 | 144 | 3440 | 55.94 | 699.7498 | 640.7979 | 640.7979 | 58.9519 | Heating | 52.0164 | 8.5 | 52.0164 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.4033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 53.078 | 0 | 10.6156 | 0.1062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 09:00 | 5 | 24 | 9 | 144 | 3441 | 57.02 | 8.7814 | 1432.5804 | 1432.5804 | -1423.799 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1750.9316 | 1750.9316 | 0 | 8.5 | 0 | 291.8219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1715.913 | 343.1826 | 3.432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 10:00 | 5 | 24 | 10 | 144 | 3442 | 59 | 0.68006 | 2572.4262 | 2572.4262 | -2571.7461 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3144.0765 | 3144.0765 | 0 | 8.5 | 0 | 524.0127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3081.1949 | 616.239 | 6.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 11:00 | 5 | 24 | 11 | 144 | 3443 | 59 | 0 | 4416.6655 | 4416.6655 | -4416.6655 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5398.1468 | 5398.1468 | 0 | 8.5 | 0 | 899.6911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5290.1838 | 1058.0368 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 12:00 | 5 | 24 | 12 | 144 | 3444 | 64.04 | 0 | 5339.0072 | 5339.0072 | -5339.0072 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6525.4532 | 6525.4532 | 0 | 8.5 | 0 | 1087.5755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6394.9441 | 1278.9888 | 12.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 13:00 | 5 | 24 | 13 | 144 | 3445 | 68 | 0 | 6099.366 | 6099.366 | -6099.366 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7454.7806 | 7454.7806 | 0 | 8.5 | 0 | 1242.4634 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7305.685 | 1461.137 | 14.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 14:00 | 5 | 24 | 14 | 144 | 3446 | 68 | 0 | 6778.3557 | 6778.3557 | -6778.3557 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8284.6569 | 8284.6569 | 0 | 8.5 | 0 | 1380.7762 | 30% | 1 | 55.23% | 0% | 0% | 0% | 20.8048 | 0 | 0 | 0 | 20.8048 | 0 | 8118.9638 | 1623.7928 | 16.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.0794
2007-05-24 15:00 | 5 | 24 | 15 | 144 | 3447 | 62.06 | 0 | 7027.4155 | 7027.4155 | -7027.4155 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8589.0634 | 8589.0634 | 0 | 8.5 | 0 | 1431.5106 | 30% | 1 | 57.26% | 0% | 0% | 0% | 22.6052 | 0 | 0 | 0 | 22.6052 | 0 | 8417.2822 | 1683.4564 | 16.83% | 1 | 33.67% | 0% | 0% | 3.3323 | 0 | 0 | 3.3323 | 25.9375
2007-05-24 16:00 | 5 | 24 | 16 | 144 | 3448 | 62.06 | 0 | 7146.1968 | 7146.1968 | -7146.1968 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8734.2406 | 8734.2406 | 0 | 8.5 | 0 | 1455.7068 | 30% | 1 | 58.23% | 0% | 0% | 0% | 23.4937 | 0 | 0 | 0 | 23.4937 | 0 | 8559.5558 | 1711.9112 | 17.12% | 1 | 34.24% | 0% | 0% | 3.4633 | 0 | 0 | 3.4633 | 26.957
2007-05-24 17:00 | 5 | 24 | 17 | 144 | 3449 | 62.06 | 0 | 6937.3617 | 6937.3617 | -6937.3617 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8478.9977 | 8478.9977 | 0 | 8.5 | 0 | 1413.1663 | 30% | 1 | 56.53% | 0% | 0% | 0% | 21.9445 | 0 | 0 | 0 | 21.9445 | 0 | 8309.4177 | 1661.8835 | 16.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.219
2007-05-24 18:00 | 5 | 24 | 18 | 144 | 3450 | 62.06 | 0 | 4571.6449 | 4571.6449 | -4571.6449 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5587.566 | 5587.566 | 0 | 8.5 | 0 | 931.261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5475.8147 | 1095.1629 | 10.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 19:00 | 5 | 24 | 19 | 144 | 3451 | 60.98 | 0 | 3637.8609 | 3637.8609 | -3637.8609 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4446.2744 | 4446.2744 | 0 | 8.5 | 0 | 741.0457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4357.3489 | 871.4698 | 8.715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 20:00 | 5 | 24 | 20 | 144 | 3452 | 60.98 | 0 | 1186.0756 | 1186.0756 | -1186.0756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1449.6479 | 1449.6479 | 0 | 8.5 | 0 | 241.608 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1420.6549 | 284.131 | 2.841% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 21:00 | 5 | 24 | 21 | 144 | 3453 | 57.92 | 0 | 379.1588 | 379.1588 | -379.1588 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 463.4163 | 463.4163 | 0 | 8.5 | 0 | 77.236 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 454.148 | 90.8296 | 0.9083% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 22:00 | 5 | 24 | 22 | 144 | 3454 | 57.92 | 2.7513 | 0 | 0 | 2.7513 | Heating | 2.4276 | 8.5 | 2.4276 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.48552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.4772 | 0 | 0.49543 | 0.004954% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-24 23:00 | 5 | 24 | 23 | 144 | 3455 | 57.92 | 21.4278 | 0 | 0 | 21.4278 | Heating | 18.9069 | 8.5 | 18.9069 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.7814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.2927 | 0 | 3.8585 | 0.03859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 | 5 | 25 | 0 | 145 | 3456 | 53.96 | 38.2718 | 0 | 0 | 38.2718 | Heating | 33.7693 | 8.5 | 33.7693 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.4584 | 0 | 6.8917 | 0.06892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 01:00 | 5 | 25 | 1 | 145 | 3457 | 55.94 | 57.6601 | 0 | 0 | 57.6601 | Heating | 50.8766 | 8.5 | 50.8766 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.1753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 51.9149 | 0 | 10.383 | 0.1038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 02:00 | 5 | 25 | 2 | 145 | 3458 | 55.94 | 101.579 | 0 | 0 | 101.579 | Heating | 89.6286 | 8.5 | 89.6286 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.9257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 91.4577 | 0 | 18.2915 | 0.1829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 03:00 | 5 | 25 | 3 | 145 | 3459 | 53.06 | 169.2447 | 0 | 0 | 169.2447 | Heating | 149.3336 | 8.5 | 149.3336 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.8667 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 152.3812 | 0 | 30.4762 | 0.3048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 04:00 | 5 | 25 | 4 | 145 | 3460 | 51.98 | 235.1664 | 0 | 0 | 235.1664 | Heating | 207.4997 | 8.5 | 207.4997 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.4999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 211.7344 | 0 | 42.3469 | 0.4235% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 05:00 | 5 | 25 | 5 | 145 | 3461 | 51.98 | 284.6173 | 0 | 0 | 284.6173 | Heating | 251.1329 | 8.5 | 251.1329 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.2266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 256.258 | 0 | 51.2516 | 0.5125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 06:00 | 5 | 25 | 6 | 145 | 3462 | 53.06 | 4080.016 | 27.1281 | 27.1281 | 4052.8879 | Heating | 3576.0776 | 8.5 | 3576.0776 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 715.2155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3649.0587 | 0 | 729.8117 | 7.298% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 07:00 | 5 | 25 | 7 | 145 | 3463 | 57.02 | 1961.62 | 13.2766 | 13.2766 | 1948.3435 | Heating | 1719.1266 | 8.5 | 1719.1266 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.8253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1754.2108 | 0 | 350.8422 | 3.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 08:00 | 5 | 25 | 8 | 145 | 3464 | 57.02 | 873.4096 | 104.7355 | 104.7355 | 768.6741 | Heating | 678.2419 | 8.5 | 678.2419 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.6484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 692.0835 | 0 | 138.4167 | 1.384% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 09:00 | 5 | 25 | 9 | 145 | 3465 | 66.02 | 10.743 | 264.5668 | 264.5668 | -253.8238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 323.3594 | 323.3594 | 0 | 8.5 | 0 | 53.8932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 316.8922 | 63.3784 | 0.6338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 10:00 | 5 | 25 | 10 | 145 | 3466 | 69.08 | 0 | 963.9544 | 963.9544 | -963.9544 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1178.1664 | 1178.1664 | 0 | 8.5 | 0 | 196.3611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1154.6031 | 230.9206 | 2.309% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 11:00 | 5 | 25 | 11 | 145 | 3467 | 69.08 | 0 | 2442.7897 | 2442.7897 | -2442.7897 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2985.6318 | 2985.6318 | 0 | 8.5 | 0 | 497.6053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2925.9192 | 585.1838 | 5.852% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 12:00 | 5 | 25 | 12 | 145 | 3468 | 73.94 | 0 | 3345.9505 | 3345.9505 | -3345.9505 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4089.495 | 4089.495 | 0 | 8.5 | 0 | 681.5825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4007.7051 | 801.541 | 8.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 13:00 | 5 | 25 | 13 | 145 | 3469 | 75.92 | 0 | 4101.9712 | 4101.9712 | -4101.9712 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5013.5203 | 5013.5203 | 0 | 8.5 | 0 | 835.5867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4913.2499 | 982.65 | 9.826% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 14:00 | 5 | 25 | 14 | 145 | 3470 | 75.92 | 0 | 4468.5035 | 4468.5035 | -4468.5035 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5461.5043 | 5461.5043 | 0 | 8.5 | 0 | 910.2507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5352.2742 | 1070.4548 | 10.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 15:00 | 5 | 25 | 15 | 145 | 3471 | 75.92 | 0 | 5042.5334 | 5042.5334 | -5042.5334 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6163.0964 | 6163.0964 | 0 | 8.5 | 0 | 1027.1827 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6039.8345 | 1207.9669 | 12.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 16:00 | 5 | 25 | 16 | 145 | 3472 | 75.02 | 0 | 5456.7943 | 5456.7943 | -5456.7943 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6669.4153 | 6669.4153 | 0 | 8.5 | 0 | 1111.5692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6536.027 | 1307.2054 | 13.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 17:00 | 5 | 25 | 17 | 145 | 3473 | 75.02 | 0 | 5240.8541 | 5240.8541 | -5240.8541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6405.4884 | 6405.4884 | 0 | 8.5 | 0 | 1067.5814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6277.3786 | 1255.4757 | 12.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 18:00 | 5 | 25 | 18 | 145 | 3474 | 73.94 | 0 | 3192.1974 | 3192.1974 | -3192.1974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3901.5746 | 3901.5746 | 0 | 8.5 | 0 | 650.2624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3823.5431 | 764.7086 | 7.647% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 19:00 | 5 | 25 | 19 | 145 | 3475 | 71.06 | 0 | 2424.2539 | 2424.2539 | -2424.2539 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2962.977 | 2962.977 | 0 | 8.5 | 0 | 493.8295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2903.7175 | 580.7435 | 5.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 20:00 | 5 | 25 | 20 | 145 | 3476 | 71.06 | 0 | 1606.622 | 1606.622 | -1606.622 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1963.6491 | 1963.6491 | 0 | 8.5 | 0 | 327.2748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1924.3761 | 384.8752 | 3.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 21:00 | 5 | 25 | 21 | 145 | 3477 | 66.92 | 0 | 588.6929 | 588.6929 | -588.6929 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 719.5136 | 719.5136 | 0 | 8.5 | 0 | 119.9189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 705.1233 | 141.0247 | 1.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 22:00 | 5 | 25 | 22 | 145 | 3478 | 64.04 | 0 | 304.575 | 304.575 | -304.575 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 372.2583 | 372.2583 | 0 | 8.5 | 0 | 62.043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 364.8131 | 72.9626 | 0.7296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-25 23:00 | 5 | 25 | 23 | 145 | 3479 | 64.04 | 0 | 111.531 | 111.531 | -111.531 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 136.3157 | 136.3157 | 0 | 8.5 | 0 | 22.7193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 133.5894 | 26.7179 | 0.2672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 | 5 | 26 | 0 | 146 | 3480 | 57.02 | 0 | 26.0318 | 26.0318 | -26.0318 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 31.8166 | 31.8166 | 0 | 8.5 | 0 | 5.3028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 31.1803 | 6.2361 | 0.06236% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 01:00 | 5 | 26 | 1 | 146 | 3481 | 55.94 | 0 | 1.1103 | 1.1103 | -1.1103 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.357 | 1.357 | 0 | 8.5 | 0 | 0.22616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.3298 | 0.26597 | 0.00266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 02:00 | 5 | 26 | 2 | 146 | 3482 | 55.94 | 5.0564 | 0 | 0 | 5.0564 | Heating | 4.4615 | 8.5 | 4.4615 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.89231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.5526 | 0 | 0.91052 | 0.009105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 03:00 | 5 | 26 | 3 | 146 | 3483 | 57.92 | 8.9204 | 0 | 0 | 8.9204 | Heating | 7.8709 | 8.5 | 7.8709 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.0316 | 0 | 1.6063 | 0.01606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 04:00 | 5 | 26 | 4 | 146 | 3484 | 57.92 | 9.3179 | 0 | 0 | 9.3179 | Heating | 8.2217 | 8.5 | 8.2217 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.3894 | 0 | 1.6779 | 0.01678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 05:00 | 5 | 26 | 5 | 146 | 3485 | 57.92 | 11.9855 | 0 | 0 | 11.9855 | Heating | 10.5755 | 8.5 | 10.5755 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.7913 | 0 | 2.1583 | 0.02158% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 06:00 | 5 | 26 | 6 | 146 | 3486 | 60.08 | 9.336 | 0 | 0 | 9.336 | Heating | 8.2377 | 8.5 | 8.2377 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.4058 | 0 | 1.6812 | 0.01681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 07:00 | 5 | 26 | 7 | 146 | 3487 | 60.98 | 7.2535 | 0 | 0 | 7.2535 | Heating | 6.4002 | 8.5 | 6.4002 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.28 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.5308 | 0 | 1.3062 | 0.01306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 08:00 | 5 | 26 | 8 | 146 | 3488 | 60.98 | 1333.8993 | 0 | 0 | 1333.8993 | Heating | 1176.97 | 8.5 | 1176.97 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1200.9897 | 0 | 240.1979 | 2.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 09:00 | 5 | 26 | 9 | 146 | 3489 | 62.96 | 681.2468 | 0 | 0 | 681.2468 | Heating | 601.1001 | 8.5 | 601.1001 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.22 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 613.3675 | 0 | 122.6735 | 1.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 10:00 | 5 | 26 | 10 | 146 | 3490 | 66.02 | 199.7657 | 0 | 0 | 199.7657 | Heating | 176.2638 | 8.5 | 176.2638 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.2528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 179.8611 | 0 | 35.9722 | 0.3597% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 11:00 | 5 | 26 | 11 | 146 | 3491 | 66.02 | 1.68 | 0 | 0 | 1.68 | Heating | 1.4823 | 8.5 | 1.4823 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.29646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.5126 | 0 | 0.30251 | 0.003025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 12:00 | 5 | 26 | 12 | 146 | 3492 | 77 | 0 | 1.1432 | 1.1432 | -1.1432 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.3972 | 1.3972 | 0 | 8.5 | 0 | 0.23287 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.3693 | 0.27386 | 0.002739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 13:00 | 5 | 26 | 13 | 146 | 3493 | 82.04 | 0 | 19.4089 | 19.4089 | -19.4089 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23.722 | 23.722 | 0 | 8.5 | 0 | 3.9537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 23.2476 | 4.6495 | 0.0465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 14:00 | 5 | 26 | 14 | 146 | 3494 | 82.04 | 0 | 100.7866 | 100.7866 | -100.7866 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 123.1836 | 123.1836 | 0 | 8.5 | 0 | 20.5306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 120.7199 | 24.144 | 0.2414% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 15:00 | 5 | 26 | 15 | 146 | 3495 | 82.04 | 0 | 243.1556 | 243.1556 | -243.1556 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 297.1902 | 297.1902 | 0 | 8.5 | 0 | 49.5317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 291.2464 | 58.2493 | 0.5825% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 16:00 | 5 | 26 | 16 | 146 | 3496 | 80.96 | 0 | 734.0392 | 734.0392 | -734.0392 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 897.159 | 897.159 | 0 | 8.5 | 0 | 149.5265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 879.2158 | 175.8432 | 1.758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 17:00 | 5 | 26 | 17 | 146 | 3497 | 80.96 | 0 | 348.928 | 348.928 | -348.928 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 426.4676 | 426.4676 | 0 | 8.5 | 0 | 71.0779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 417.9382 | 83.5876 | 0.8359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 18:00 | 5 | 26 | 18 | 146 | 3498 | 80.06 | 0 | 149.4206 | 149.4206 | -149.4206 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 182.6252 | 182.6252 | 0 | 8.5 | 0 | 30.4375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 178.9727 | 35.7945 | 0.3579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 19:00 | 5 | 26 | 19 | 146 | 3499 | 77 | 0 | 76.2748 | 76.2748 | -76.2748 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 93.2248 | 93.2248 | 0 | 8.5 | 0 | 15.5375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 91.3603 | 18.2721 | 0.1827% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 20:00 | 5 | 26 | 20 | 146 | 3500 | 77 | 0 | 43.7167 | 43.7167 | -43.7167 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 53.4315 | 53.4315 | 0 | 8.5 | 0 | 8.9052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 52.3629 | 10.4726 | 0.1047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 21:00 | 5 | 26 | 21 | 146 | 3501 | 75.92 | 0 | 30.7887 | 30.7887 | -30.7887 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 37.6307 | 37.6307 | 0 | 8.5 | 0 | 6.2718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 36.878 | 7.3756 | 0.07376% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 22:00 | 5 | 26 | 22 | 146 | 3502 | 71.96 | 0 | 6.5144 | 6.5144 | -6.5144 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7.962 | 7.962 | 0 | 8.5 | 0 | 1.327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7.8027 | 1.5605 | 0.01561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-26 23:00 | 5 | 26 | 23 | 146 | 3503 | 71.96 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-05-27 | 5 | 27 | 0 | 147 | 3504 | 64.94 | 0.41311 | 0 | 0 | 0.41311 | Heating | 0.36451 | 8.5 | 0.36451 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.072902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.37195 | 0 | 0.07439 | 0.0007439% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 01:00 | 5 | 27 | 1 | 147 | 3505 | 64.04 | 1.7435 | 0 | 0 | 1.7435 | Heating | 1.5384 | 8.5 | 1.5384 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.30767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.5698 | 0 | 0.31395 | 0.00314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 02:00 | 5 | 27 | 2 | 147 | 3506 | 64.04 | 3.02 | 0 | 0 | 3.02 | Heating | 2.6647 | 8.5 | 2.6647 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.53295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.7191 | 0 | 0.54382 | 0.005438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 03:00 | 5 | 27 | 3 | 147 | 3507 | 64.04 | 4.0419 | 0 | 0 | 4.0419 | Heating | 3.5664 | 8.5 | 3.5664 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.71328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.6392 | 0 | 0.72784 | 0.007278% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 04:00 | 5 | 27 | 4 | 147 | 3508 | 64.04 | 4.5417 | 0 | 0 | 4.5417 | Heating | 4.0074 | 8.5 | 4.0074 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.80147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.0891 | 0 | 0.81783 | 0.008178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 05:00 | 5 | 27 | 5 | 147 | 3509 | 64.04 | 5.4527 | 0 | 0 | 5.4527 | Heating | 4.8112 | 8.5 | 4.8112 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.96223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.9094 | 0 | 0.98187 | 0.009819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 06:00 | 5 | 27 | 6 | 147 | 3510 | 66.02 | 958.5693 | 222.7147 | 222.7147 | 735.8546 | Heating | 649.2835 | 8.5 | 649.2835 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.8567 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 662.5342 | 0 | 132.5068 | 1.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 07:00 | 5 | 27 | 7 | 147 | 3511 | 69.08 | 402.2067 | 149.6502 | 149.6502 | 252.5565 | Heating | 222.844 | 8.5 | 222.844 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.5688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 227.3918 | 0 | 45.4784 | 0.4548% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 08:00 | 5 | 27 | 8 | 147 | 3512 | 69.08 | 0 | 1779.9743 | 1779.9743 | -1779.9743 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2175.5241 | 2175.5241 | 0 | 8.5 | 0 | 362.5874 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2132.0136 | 426.4027 | 4.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 09:00 | 5 | 27 | 9 | 147 | 3513 | 75.02 | 0 | 3668.8739 | 3668.8739 | -3668.8739 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4484.1792 | 4484.1792 | 0 | 8.5 | 0 | 747.3632 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4394.4956 | 878.8991 | 8.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 10:00 | 5 | 27 | 10 | 147 | 3514 | 77 | 0 | 5965.1989 | 5965.1989 | -5965.1989 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7290.7986 | 7290.7986 | 0 | 8.5 | 0 | 1215.1331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7144.9827 | 1428.9965 | 14.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 11:00 | 5 | 27 | 11 | 147 | 3515 | 77 | 0 | 7570.2224 | 7570.2224 | -7570.2224 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9252.494 | 9252.494 | 0 | 8.5 | 0 | 1542.0823 | 30.84% | 1 | 61.68% | 0% | 0% | 0% | 26.8243 | 0 | 0 | 0 | 26.8243 | 0 | 9067.4441 | 1813.4888 | 18.13% | 1 | 36.27% | 0% | 0% | 3.9543 | 0 | 0 | 3.9543 | 30.7786
2007-05-27 12:00 | 5 | 27 | 12 | 147 | 3516 | 84.02 | 0 | 8674.8654 | 8674.8654 | -8674.8654 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10602.6133 | 10602.6133 | 0 | 8.5 | 0 | 1767.1022 | 35.34% | 1 | 70.68% | 0% | 0% | 0% | 36.693 | 0 | 0 | 0 | 36.693 | 0 | 10390.561 | 2078.1122 | 20.78% | 1 | 41.56% | 0% | 0% | 5.409 | 0 | 0 | 5.409 | 42.102
2007-05-27 13:00 | 5 | 27 | 13 | 147 | 3517 | 82.04 | 0 | 9837.8058 | 9837.8058 | -9837.8058 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12023.9848 | 12023.9848 | 0 | 8.5 | 0 | 2003.9975 | 40.08% | 1 | 80.16% | 0% | 0% | 0% | 49.0055 | 0 | 0 | 0 | 49.0055 | 0 | 11783.5051 | 2356.701 | 23.57% | 1 | 47.13% | 0% | 0% | 7.2241 | 0 | 0 | 7.2241 | 56.2295
2007-05-27 14:00 | 5 | 27 | 14 | 147 | 3518 | 82.04 | 0 | 7358.734 | 7358.734 | -7358.734 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8994.0083 | 8994.0083 | 0 | 8.5 | 0 | 1499.0014 | 30% | 1 | 59.96% | 0% | 0% | 0% | 25.1319 | 0 | 0 | 0 | 25.1319 | 0 | 8814.1281 | 1762.8256 | 17.63% | 1 | 35.26% | 0% | 0% | 3.7048 | 0 | 0 | 3.7048 | 28.8367
2007-05-27 15:00 | 5 | 27 | 15 | 147 | 3519 | 84.92 | 0 | 4605.8346 | 4605.8346 | -4605.8346 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5629.3534 | 5629.3534 | 0 | 8.5 | 0 | 938.2256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5516.7663 | 1103.3533 | 11.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 16:00 | 5 | 27 | 16 | 147 | 3520 | 82.94 | 0 | 4413.8896 | 4413.8896 | -4413.8896 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5394.754 | 5394.754 | 0 | 8.5 | 0 | 899.1257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5286.8589 | 1057.3718 | 10.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 17:00 | 5 | 27 | 17 | 147 | 3521 | 82.94 | 0 | 4740.2076 | 4740.2076 | -4740.2076 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5793.587 | 5793.587 | 0 | 8.5 | 0 | 965.5978 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5677.7153 | 1135.5431 | 11.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 18:00 | 5 | 27 | 18 | 147 | 3522 | 82.04 | 0 | 3479.8157 | 3479.8157 | -3479.8157 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4253.1081 | 4253.1081 | 0 | 8.5 | 0 | 708.8514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4168.046 | 833.6092 | 8.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 19:00 | 5 | 27 | 19 | 147 | 3523 | 78.98 | 0 | 2742.681 | 2742.681 | -2742.681 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3352.1656 | 3352.1656 | 0 | 8.5 | 0 | 558.6943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3285.1223 | 657.0245 | 6.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 20:00 | 5 | 27 | 20 | 147 | 3524 | 78.98 | 0 | 1363.6954 | 1363.6954 | -1363.6954 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1666.7388 | 1666.7388 | 0 | 8.5 | 0 | 277.7898 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1633.4041 | 326.6808 | 3.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 21:00 | 5 | 27 | 21 | 147 | 3525 | 75.92 | 0 | 528.2643 | 528.2643 | -528.2643 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 645.6563 | 645.6563 | 0 | 8.5 | 0 | 107.6094 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 632.7432 | 126.5486 | 1.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 22:00 | 5 | 27 | 22 | 147 | 3526 | 69.98 | 0 | 80.529 | 80.529 | -80.529 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 98.4244 | 98.4244 | 0 | 8.5 | 0 | 16.4041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 96.4559 | 19.2912 | 0.1929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-27 23:00 | 5 | 27 | 23 | 147 | 3527 | 69.98 | 0 | 25.3132 | 25.3132 | -25.3132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 30.9384 | 30.9384 | 0 | 8.5 | 0 | 5.1564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 30.3196 | 6.0639 | 0.06064% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 | 5 | 28 | 0 | 148 | 3528 | 62.06 | 0 | 0.13381 | 0.13381 | -0.13381 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.16355 | 0.16355 | 0 | 8.5 | 0 | 0.027258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.16028 | 0.032055 | 0.0003206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 01:00 | 5 | 28 | 1 | 148 | 3529 | 62.06 | 5.3959 | 0 | 0 | 5.3959 | Heating | 4.7611 | 8.5 | 4.7611 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.95222 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.8583 | 0 | 0.97165 | 0.009717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 02:00 | 5 | 28 | 2 | 148 | 3530 | 62.06 | 12.4652 | 0 | 0 | 12.4652 | Heating | 10.9987 | 8.5 | 10.9987 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.2231 | 0 | 2.2446 | 0.02245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 03:00 | 5 | 28 | 3 | 148 | 3531 | 60.08 | 19.1818 | 0 | 0 | 19.1818 | Heating | 16.9251 | 8.5 | 16.9251 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.2705 | 0 | 3.4541 | 0.03454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 04:00 | 5 | 28 | 4 | 148 | 3532 | 57.92 | 25.5134 | 0 | 0 | 25.5134 | Heating | 22.5118 | 8.5 | 22.5118 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5024 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.9712 | 0 | 4.5942 | 0.04594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 05:00 | 5 | 28 | 5 | 148 | 3533 | 57.92 | 28.1699 | 0 | 0 | 28.1699 | Heating | 24.8558 | 8.5 | 24.8558 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.9712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 25.3631 | 0 | 5.0726 | 0.05073% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 06:00 | 5 | 28 | 6 | 148 | 3534 | 57.02 | 1587.0916 | 162.3004 | 162.3004 | 1424.7912 | Heating | 1257.1687 | 8.5 | 1257.1687 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.4337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1282.8252 | 0 | 256.565 | 2.566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 07:00 | 5 | 28 | 7 | 148 | 3535 | 55.04 | 1277.7087 | 11.9834 | 11.9834 | 1265.7253 | Heating | 1116.8164 | 8.5 | 1116.8164 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.3633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1139.6086 | 0 | 227.9217 | 2.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 08:00 | 5 | 28 | 8 | 148 | 3536 | 55.04 | 838.9819 | 415.3938 | 415.3938 | 423.5881 | Heating | 373.7542 | 8.5 | 373.7542 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.7508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 381.3818 | 0 | 76.2764 | 0.7628% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 09:00 | 5 | 28 | 9 | 148 | 3537 | 53.96 | 262.2679 | 742.3303 | 742.3303 | -480.0624 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 907.2926 | 907.2926 | 0 | 8.5 | 0 | 151.2154 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 889.1467 | 177.8293 | 1.778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 10:00 | 5 | 28 | 10 | 148 | 3538 | 53.6 | 165.9836 | 817.7629 | 817.7629 | -651.7792 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 999.4879 | 999.4879 | 0 | 8.5 | 0 | 166.5813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 979.4982 | 195.8996 | 1.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 11:00 | 5 | 28 | 11 | 148 | 3539 | 53.96 | 72.4976 | 816.145 | 816.145 | -743.6475 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 997.5106 | 997.5106 | 0 | 8.5 | 0 | 166.2518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 977.5604 | 195.5121 | 1.955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 12:00 | 5 | 28 | 12 | 148 | 3540 | 55.04 | 69.4971 | 888.2921 | 888.2921 | -818.795 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1085.6904 | 1085.6904 | 0 | 8.5 | 0 | 180.9484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1063.9766 | 212.7953 | 2.128% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 13:00 | 5 | 28 | 13 | 148 | 3541 | 55.04 | 74.9942 | 973.5594 | 973.5594 | -898.5652 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1189.906 | 1189.906 | 0 | 8.5 | 0 | 198.3177 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1166.1079 | 233.2216 | 2.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 14:00 | 5 | 28 | 14 | 148 | 3542 | 55.94 | 87.2283 | 1001.739 | 1001.739 | -914.5108 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1224.3477 | 1224.3477 | 0 | 8.5 | 0 | 204.0579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1199.8607 | 239.9721 | 2.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 15:00 | 5 | 28 | 15 | 148 | 3543 | 60.08 | 81.8442 | 848.0439 | 848.0439 | -766.1997 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1036.498 | 1036.498 | 0 | 8.5 | 0 | 172.7497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1015.7681 | 203.1536 | 2.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 16:00 | 5 | 28 | 16 | 148 | 3544 | 59 | 57.8557 | 680.7384 | 680.7384 | -622.8827 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 832.0136 | 832.0136 | 0 | 8.5 | 0 | 138.6689 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 815.3733 | 163.0747 | 1.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 17:00 | 5 | 28 | 17 | 148 | 3545 | 59 | 37.7009 | 553.8257 | 553.8257 | -516.1248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 676.898 | 676.898 | 0 | 8.5 | 0 | 112.8163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 663.3601 | 132.672 | 1.327% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 18:00 | 5 | 28 | 18 | 148 | 3546 | 57.92 | 12.8583 | 284.401 | 284.401 | -271.5427 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 347.6012 | 347.6012 | 0 | 8.5 | 0 | 57.9335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 340.6492 | 68.1298 | 0.6813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 19:00 | 5 | 28 | 19 | 148 | 3547 | 55.94 | 13.2287 | 253.4833 | 253.4833 | -240.2546 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 309.8129 | 309.8129 | 0 | 8.5 | 0 | 51.6355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 303.6167 | 60.7233 | 0.6072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 20:00 | 5 | 28 | 20 | 148 | 3548 | 55.94 | 53.2133 | 133.2722 | 133.2722 | -80.0589 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 162.8882 | 162.8882 | 0 | 8.5 | 0 | 27.148 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 159.6304 | 31.9261 | 0.3193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 21:00 | 5 | 28 | 21 | 148 | 3549 | 53.96 | 58.1089 | 74.784 | 74.784 | -16.6751 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 91.4027 | 91.4027 | 0 | 8.5 | 0 | 15.2338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 89.5746 | 17.9149 | 0.1791% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 22:00 | 5 | 28 | 22 | 148 | 3550 | 53.96 | 109.1138 | 0 | 0 | 109.1138 | Heating | 96.2769 | 8.5 | 96.2769 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.2554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 98.2417 | 0 | 19.6483 | 0.1965% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-28 23:00 | 5 | 28 | 23 | 148 | 3551 | 53.96 | 189.1421 | 0 | 0 | 189.1421 | Heating | 166.8901 | 8.5 | 166.8901 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.378 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 170.296 | 0 | 34.0592 | 0.3406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 | 5 | 29 | 0 | 149 | 3552 | 53.96 | 276.8938 | 0 | 0 | 276.8938 | Heating | 244.318 | 8.5 | 244.318 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.8636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 249.3041 | 0 | 49.8608 | 0.4986% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 01:00 | 5 | 29 | 1 | 149 | 3553 | 51.98 | 385.9024 | 0 | 0 | 385.9024 | Heating | 340.5021 | 8.5 | 340.5021 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.1004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 347.4511 | 0 | 69.4902 | 0.6949% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 02:00 | 5 | 29 | 2 | 149 | 3554 | 51.98 | 440.0901 | 0 | 0 | 440.0901 | Heating | 388.3148 | 8.5 | 388.3148 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 396.2396 | 0 | 79.2479 | 0.7925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 03:00 | 5 | 29 | 3 | 149 | 3555 | 46.04 | 453.5827 | 0 | 0 | 453.5827 | Heating | 400.22 | 8.5 | 400.22 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 408.3878 | 0 | 81.6776 | 0.8168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 04:00 | 5 | 29 | 4 | 149 | 3556 | 44.96 | 499.0622 | 0 | 0 | 499.0622 | Heating | 440.349 | 8.5 | 440.349 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.0698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 449.3357 | 0 | 89.8671 | 0.8987% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 05:00 | 5 | 29 | 5 | 149 | 3557 | 44.96 | 485.5879 | 0 | 0 | 485.5879 | Heating | 428.4599 | 8.5 | 428.4599 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 437.204 | 0 | 87.4408 | 0.8744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 06:00 | 5 | 29 | 6 | 149 | 3558 | 48.2 | 5068.6798 | 26.7379 | 26.7379 | 5041.9419 | Heating | 4448.7723 | 8.5 | 4448.7723 | 0 | 4.3513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 889.7545 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4539.5636 | 0 | 907.9127 | 9.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 07:00 | 5 | 29 | 7 | 149 | 3559 | 53.96 | 3184.2076 | 0 | 0 | 3184.2076 | Heating | 2809.595 | 8.5 | 2809.595 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 561.919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2866.9336 | 0 | 573.3867 | 5.734% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 08:00 | 5 | 29 | 8 | 149 | 3560 | 53.96 | 1969.6365 | 52.8754 | 52.8754 | 1916.7612 | Heating | 1691.2599 | 8.5 | 1691.2599 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 338.252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1725.7754 | 0 | 345.1551 | 3.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 09:00 | 5 | 29 | 9 | 149 | 3561 | 57.92 | 728.1635 | 205.4797 | 205.4797 | 522.6838 | Heating | 461.1916 | 8.5 | 461.1916 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.2383 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 470.6036 | 0 | 94.1207 | 0.9412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 10:00 | 5 | 29 | 10 | 149 | 3562 | 60.08 | 165.9148 | 412.7793 | 412.7793 | -246.8645 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 504.508 | 504.508 | 0 | 8.5 | 0 | 84.0847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 494.4179 | 98.8836 | 0.9888% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 11:00 | 5 | 29 | 11 | 149 | 3563 | 60.08 | 55.5558 | 670.448 | 670.448 | -614.8922 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 819.4365 | 819.4365 | 0 | 8.5 | 0 | 136.5727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 803.0477 | 160.6095 | 1.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 12:00 | 5 | 29 | 12 | 149 | 3564 | 64.94 | 21.6777 | 930.6901 | 930.6901 | -909.0124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1137.5101 | 1137.5101 | 0 | 8.5 | 0 | 189.585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1114.7599 | 222.952 | 2.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 13:00 | 5 | 29 | 13 | 149 | 3565 | 68 | 8.6433 | 1680.3795 | 1680.3795 | -1671.7361 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2053.7971 | 2053.7971 | 0 | 8.5 | 0 | 342.2995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2012.7212 | 402.5442 | 4.025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 14:00 | 5 | 29 | 14 | 149 | 3566 | 68 | 1.3822 | 2781.2727 | 2781.2727 | -2779.8904 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3399.3333 | 3399.3333 | 0 | 8.5 | 0 | 566.5555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3331.3466 | 666.2693 | 6.663% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 15:00 | 5 | 29 | 15 | 149 | 3567 | 69.08 | 0 | 3058.0443 | 3058.0443 | -3058.0443 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3737.6098 | 3737.6098 | 0 | 8.5 | 0 | 622.935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3662.8576 | 732.5715 | 7.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 16:00 | 5 | 29 | 16 | 149 | 3568 | 69.98 | 0 | 3062.7008 | 3062.7008 | -3062.7008 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3743.301 | 3743.301 | 0 | 8.5 | 0 | 623.8835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3668.435 | 733.687 | 7.337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 17:00 | 5 | 29 | 17 | 149 | 3569 | 69.8 | 0 | 3106.0862 | 3106.0862 | -3106.0862 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3796.3276 | 3796.3276 | 0 | 8.5 | 0 | 632.7213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3720.4011 | 744.0802 | 7.441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 18:00 | 5 | 29 | 18 | 149 | 3570 | 68 | 0 | 1859.2222 | 1859.2222 | -1859.2222 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2272.3827 | 2272.3827 | 0 | 8.5 | 0 | 378.7305 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2226.9351 | 445.387 | 4.454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 19:00 | 5 | 29 | 19 | 149 | 3571 | 66.02 | 0 | 898.272 | 898.272 | -898.272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1097.888 | 1097.888 | 0 | 8.5 | 0 | 182.9813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1075.9302 | 215.186 | 2.152% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 20:00 | 5 | 29 | 20 | 149 | 3572 | 66.02 | 3.6216 | 299.3776 | 299.3776 | -295.756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 365.906 | 365.906 | 0 | 8.5 | 0 | 60.9843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 358.5879 | 71.7176 | 0.7172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 21:00 | 5 | 29 | 21 | 149 | 3573 | 64.94 | 26.8091 | 203.1958 | 203.1958 | -176.3867 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 248.3505 | 248.3505 | 0 | 8.5 | 0 | 41.3917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 243.3834 | 48.6767 | 0.4868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 22:00 | 5 | 29 | 22 | 149 | 3574 | 62.06 | 72.498 | 0 | 0 | 72.498 | Heating | 63.9688 | 8.5 | 63.9688 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.7938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.2743 | 0 | 13.0549 | 0.1305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-29 23:00 | 5 | 29 | 23 | 149 | 3575 | 62.06 | 151.1734 | 0 | 0 | 151.1734 | Heating | 133.3883 | 8.5 | 133.3883 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.6777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 136.1105 | 0 | 27.2221 | 0.2722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 | 5 | 30 | 0 | 150 | 3576 | 57.92 | 225.2875 | 0 | 0 | 225.2875 | Heating | 198.7831 | 8.5 | 198.7831 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.7566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 202.8399 | 0 | 40.568 | 0.4057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 01:00 | 5 | 30 | 1 | 150 | 3577 | 57.92 | 301.6711 | 0 | 0 | 301.6711 | Heating | 266.1804 | 8.5 | 266.1804 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.2361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 271.6127 | 0 | 54.3225 | 0.5432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 02:00 | 5 | 30 | 2 | 150 | 3578 | 57.92 | 376.2987 | 0 | 0 | 376.2987 | Heating | 332.0282 | 8.5 | 332.0282 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 66.4056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 338.8043 | 0 | 67.7609 | 0.6776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 03:00 | 5 | 30 | 3 | 150 | 3579 | 57.02 | 453.918 | 0 | 0 | 453.918 | Heating | 400.5159 | 8.5 | 400.5159 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.1032 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 408.6897 | 0 | 81.7379 | 0.8174% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 04:00 | 5 | 30 | 4 | 150 | 3580 | 55.94 | 507.3338 | 0 | 0 | 507.3338 | Heating | 447.6475 | 8.5 | 447.6475 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 89.5295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 456.7831 | 0 | 91.3566 | 0.9136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 05:00 | 5 | 30 | 5 | 150 | 3581 | 55.94 | 524.6614 | 0 | 0 | 524.6614 | Heating | 462.9365 | 8.5 | 462.9365 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.5873 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 472.3842 | 0 | 94.4768 | 0.9448% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 06:00 | 5 | 30 | 6 | 150 | 3582 | 57.02 | 5106.9369 | 0 | 0 | 5106.9369 | Heating | 4506.1208 | 8.5 | 4506.1208 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 901.2242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4598.0824 | 0 | 919.6165 | 9.196% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 07:00 | 5 | 30 | 7 | 150 | 3583 | 60.98 | 2921.3552 | 0 | 0 | 2921.3552 | Heating | 2577.6664 | 8.5 | 2577.6664 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 515.5333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2630.2718 | 0 | 526.0544 | 5.261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 08:00 | 5 | 30 | 8 | 150 | 3584 | 60.98 | 1663.171 | 81.1152 | 81.1152 | 1582.0557 | Heating | 1395.9315 | 8.5 | 1395.9315 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.1863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1424.4199 | 0 | 284.884 | 2.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 09:00 | 5 | 30 | 9 | 150 | 3585 | 66.02 | 351.5176 | 392.7571 | 392.7571 | -41.2395 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 480.0364 | 480.0364 | 0 | 8.5 | 0 | 80.0061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 470.4357 | 94.0871 | 0.9409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 10:00 | 5 | 30 | 10 | 150 | 3586 | 66.92 | 27.649 | 1152.8218 | 1152.8218 | -1125.1727 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1409.0044 | 1409.0044 | 0 | 8.5 | 0 | 234.8341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1380.8243 | 276.1649 | 2.762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 11:00 | 5 | 30 | 11 | 150 | 3587 | 66.92 | 0.42875 | 2478.0246 | 2478.0246 | -2477.5959 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3028.6968 | 3028.6968 | 0 | 8.5 | 0 | 504.7828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2968.1228 | 593.6246 | 5.936% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 12:00 | 5 | 30 | 12 | 150 | 3588 | 71.96 | 0 | 4274.0238 | 4274.0238 | -4274.0238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5223.8068 | 5223.8068 | 0 | 8.5 | 0 | 870.6345 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5119.3307 | 1023.8661 | 10.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 13:00 | 5 | 30 | 13 | 150 | 3589 | 71.96 | 0 | 5193.7403 | 5193.7403 | -5193.7403 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6347.9049 | 6347.9049 | 0 | 8.5 | 0 | 1057.9841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6220.9468 | 1244.1894 | 12.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 14:00 | 5 | 30 | 14 | 150 | 3590 | 71.96 | 0 | 5625.1229 | 5625.1229 | -5625.1229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6875.1502 | 6875.1502 | 0 | 8.5 | 0 | 1145.8584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6737.6472 | 1347.5294 | 13.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 15:00 | 5 | 30 | 15 | 150 | 3591 | 62.96 | 0 | 5557.8396 | 5557.8396 | -5557.8396 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6792.915 | 6792.915 | 0 | 8.5 | 0 | 1132.1525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6657.0567 | 1331.4113 | 13.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 16:00 | 5 | 30 | 16 | 150 | 3592 | 68 | 0 | 5288.6972 | 5288.6972 | -5288.6972 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6463.9633 | 6463.9633 | 0 | 8.5 | 0 | 1077.3272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6334.684 | 1266.9368 | 12.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 17:00 | 5 | 30 | 17 | 150 | 3593 | 68 | 0 | 4886.8412 | 4886.8412 | -4886.8412 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5972.8059 | 5972.8059 | 0 | 8.5 | 0 | 995.4676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5853.3498 | 1170.67 | 11.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 18:00 | 5 | 30 | 18 | 150 | 3594 | 57.92 | 0 | 2928.4662 | 2928.4662 | -2928.4662 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3579.2365 | 3579.2365 | 0 | 8.5 | 0 | 596.5394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3507.6518 | 701.5304 | 7.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 19:00 | 5 | 30 | 19 | 150 | 3595 | 57.02 | 0 | 1961.6786 | 1961.6786 | -1961.6786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2397.6071 | 2397.6071 | 0 | 8.5 | 0 | 399.6012 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2349.655 | 469.931 | 4.699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 20:00 | 5 | 30 | 20 | 150 | 3596 | 57.02 | 0 | 629.6669 | 629.6669 | -629.6669 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 769.5929 | 769.5929 | 0 | 8.5 | 0 | 128.2655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 754.2011 | 150.8402 | 1.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 21:00 | 5 | 30 | 21 | 150 | 3597 | 57.02 | 0 | 273.0596 | 273.0596 | -273.0596 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 333.7395 | 333.7395 | 0 | 8.5 | 0 | 55.6233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 327.0647 | 65.4129 | 0.6541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-30 22:00 | 5 | 30 | 22 | 150 | 3598 | 55.04 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-05-30 23:00 | 5 | 30 | 23 | 150 | 3599 | 55.04 | 6.3199 | 0 | 0 | 6.3199 | Heating | 5.5764 | 8.5 | 5.5764 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.6902 | 0 | 1.138 | 0.01138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 | 5 | 31 | 0 | 151 | 3600 | 51.98 | 20.4484 | 0 | 0 | 20.4484 | Heating | 18.0427 | 8.5 | 18.0427 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.6085 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.4109 | 0 | 3.6822 | 0.03682% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 01:00 | 5 | 31 | 1 | 151 | 3601 | 53.06 | 31.412 | 0 | 0 | 31.412 | Heating | 27.7165 | 8.5 | 27.7165 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.5433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 28.2821 | 0 | 5.6564 | 0.05656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 02:00 | 5 | 31 | 2 | 151 | 3602 | 53.06 | 39.4339 | 0 | 0 | 39.4339 | Heating | 34.7946 | 8.5 | 34.7946 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.9589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.5047 | 0 | 7.1009 | 0.07101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 03:00 | 5 | 31 | 3 | 151 | 3603 | 48.92 | 50.9323 | 0 | 0 | 50.9323 | Heating | 44.9403 | 8.5 | 44.9403 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.9881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 45.8574 | 0 | 9.1715 | 0.09171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 04:00 | 5 | 31 | 4 | 151 | 3604 | 48.02 | 65.6338 | 0 | 0 | 65.6338 | Heating | 57.9122 | 8.5 | 57.9122 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.5824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 59.0941 | 0 | 11.8188 | 0.1182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 05:00 | 5 | 31 | 5 | 151 | 3605 | 48.02 | 64.3399 | 0 | 0 | 64.3399 | Heating | 56.7705 | 8.5 | 56.7705 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.3541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 57.9291 | 0 | 11.5858 | 0.1159% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 06:00 | 5 | 31 | 6 | 151 | 3606 | 51.98 | 1706.4389 | 157.3338 | 157.3338 | 1549.1051 | Heating | 1366.8575 | 8.5 | 1366.8575 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 273.3715 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1394.7525 | 0 | 278.9505 | 2.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 07:00 | 5 | 31 | 7 | 151 | 3607 | 55.94 | 1040.8069 | 44.017 | 44.017 | 996.7899 | Heating | 879.5205 | 8.5 | 879.5205 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.9041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 897.4699 | 0 | 179.494 | 1.795% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 08:00 | 5 | 31 | 8 | 151 | 3608 | 55.94 | 203.8195 | 974.9072 | 974.9072 | -771.0877 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1191.5533 | 1191.5533 | 0 | 8.5 | 0 | 198.5922 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1167.7222 | 233.5444 | 2.335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 09:00 | 5 | 31 | 9 | 151 | 3609 | 62.06 | 0.53779 | 2116.7523 | 2116.7523 | -2116.2145 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2587.1417 | 2587.1417 | 0 | 8.5 | 0 | 431.1903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2535.3989 | 507.0798 | 5.071% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 10:00 | 5 | 31 | 10 | 151 | 3610 | 64.04 | 0 | 3395.5295 | 3395.5295 | -3395.5295 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4150.0916 | 4150.0916 | 0 | 8.5 | 0 | 691.6819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4067.0898 | 813.418 | 8.134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 11:00 | 5 | 31 | 11 | 151 | 3611 | 64.04 | 0 | 5179.7933 | 5179.7933 | -5179.7933 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6330.8585 | 6330.8585 | 0 | 8.5 | 0 | 1055.1431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6204.2413 | 1240.8483 | 12.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 12:00 | 5 | 31 | 12 | 151 | 3612 | 66.92 | 0 | 5703.6783 | 5703.6783 | -5703.6783 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6971.1624 | 6971.1624 | 0 | 8.5 | 0 | 1161.8604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6831.7391 | 1366.3478 | 13.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 13:00 | 5 | 31 | 13 | 151 | 3613 | 69.08 | 0 | 6198.2542 | 6198.2542 | -6198.2542 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7575.644 | 7575.644 | 0 | 8.5 | 0 | 1262.6073 | 30% | 1 | 50.5% | 0% | 0% | 0% | 16.9355 | 0 | 0 | 0 | 16.9355 | 0 | 7424.1311 | 1484.8262 | 14.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.21
2007-05-31 14:00 | 5 | 31 | 14 | 151 | 3614 | 69.08 | 0 | 6457.1257 | 6457.1257 | -6457.1257 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7892.0425 | 7892.0425 | 0 | 8.5 | 0 | 1315.3404 | 30% | 1 | 52.61% | 0% | 0% | 0% | 18.6067 | 0 | 0 | 0 | 18.6067 | 0 | 7734.2016 | 1546.8403 | 15.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.8812
2007-05-31 15:00 | 5 | 31 | 15 | 151 | 3615 | 69.08 | 0 | 6164.3059 | 6164.3059 | -6164.3059 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7534.1517 | 7534.1517 | 0 | 8.5 | 0 | 1255.6919 | 30% | 1 | 50.23% | 0% | 0% | 0% | 16.7229 | 0 | 0 | 0 | 16.7229 | 0 | 7383.4686 | 1476.6937 | 14.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9975
2007-05-31 16:00 | 5 | 31 | 16 | 151 | 3616 | 69.08 | 0 | 6305.0525 | 6305.0525 | -6305.0525 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7706.1752 | 7706.1752 | 0 | 8.5 | 0 | 1284.3625 | 30% | 1 | 51.37% | 0% | 0% | 0% | 17.6142 | 0 | 0 | 0 | 17.6142 | 0 | 7552.0517 | 1510.4103 | 15.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.8887
2007-05-31 17:00 | 5 | 31 | 17 | 151 | 3617 | 69.08 | 0 | 6425.9182 | 6425.9182 | -6425.9182 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7853.9 | 7853.9 | 0 | 8.5 | 0 | 1308.9833 | 30% | 1 | 52.36% | 0% | 0% | 0% | 18.4005 | 0 | 0 | 0 | 18.4005 | 0 | 7696.822 | 1539.3644 | 15.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.675
2007-05-31 18:00 | 5 | 31 | 18 | 151 | 3618 | 66.92 | 0 | 3973.4043 | 3973.4043 | -3973.4043 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4856.3831 | 4856.3831 | 0 | 8.5 | 0 | 809.3972 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4759.2554 | 951.8511 | 9.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 19:00 | 5 | 31 | 19 | 151 | 3619 | 61.88 | 0 | 3167.9885 | 3167.9885 | -3167.9885 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3871.9859 | 3871.9859 | 0 | 8.5 | 0 | 645.331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3794.5462 | 758.9092 | 7.589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 20:00 | 5 | 31 | 20 | 151 | 3620 | 59 | 0 | 2265.3162 | 2265.3162 | -2265.3162 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2768.7198 | 2768.7198 | 0 | 8.5 | 0 | 461.4533 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2713.3454 | 542.6691 | 5.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 21:00 | 5 | 31 | 21 | 151 | 3621 | 55.4 | 0 | 1165.0618 | 1165.0618 | -1165.0618 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1423.9644 | 1423.9644 | 0 | 8.5 | 0 | 237.3274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1395.4851 | 279.097 | 2.791% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 22:00 | 5 | 31 | 22 | 151 | 3622 | 57.38 | 0 | 99.7789 | 99.7789 | -99.7789 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 121.952 | 121.952 | 0 | 8.5 | 0 | 20.3253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 119.513 | 23.9026 | 0.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-05-31 23:00 | 5 | 31 | 23 | 151 | 3623 | 59.72 | 0 | 22.3486 | 22.3486 | -22.3486 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 27.3149 | 27.3149 | 0 | 8.5 | 0 | 4.5525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 26.7686 | 5.3537 | 0.05354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 | 6 | 1 | 0 | 152 | 3624 | 62.24 | 0 | 0.28117 | 0.28117 | -0.28117 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.34365 | 0.34365 | 0 | 8.5 | 0 | 0.057276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.33678 | 0.067356 | 0.0006736% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 01:00 | 6 | 1 | 1 | 152 | 3625 | 65.48 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-01 02:00 | 6 | 1 | 2 | 152 | 3626 | 64.58 | 0.08027 | 0 | 0 | 0.08027 | Heating | 0.070827 | 8.5 | 0.070827 | 0 | 6.2633 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.014165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.072272 | 0 | 0.014454 | 0.0001445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 03:00 | 6 | 1 | 3 | 152 | 3627 | 64.76 | 3.9831 | 0 | 0 | 3.9831 | Heating | 3.5145 | 8.5 | 3.5145 | 0 | 6.2902 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.7029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.5862 | 0 | 0.71725 | 0.007172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 04:00 | 6 | 1 | 4 | 152 | 3628 | 65.12 | 9.2526 | 0 | 0 | 9.2526 | Heating | 8.1641 | 8.5 | 8.1641 | 0 | 6.3446 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.3307 | 0 | 1.6661 | 0.01666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 05:00 | 6 | 1 | 5 | 152 | 3629 | 65.48 | 13.8814 | 0 | 0 | 13.8814 | Heating | 12.2483 | 8.5 | 12.2483 | 0 | 6.3996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.4982 | 0 | 2.4996 | 0.025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 06:00 | 6 | 1 | 6 | 152 | 3630 | 66.56 | 1147.2804 | 158.6593 | 158.6593 | 988.6211 | Heating | 872.3127 | 8.5 | 872.3127 | 0 | 6.5679 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.4625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 890.115 | 0 | 178.023 | 1.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 07:00 | 6 | 1 | 7 | 152 | 3631 | 66.02 | 741.603 | 87.8935 | 87.8935 | 653.7095 | Heating | 576.8025 | 8.5 | 576.8025 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.3605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 588.574 | 0 | 117.7148 | 1.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 08:00 | 6 | 1 | 8 | 152 | 3632 | 66.02 | 193.8722 | 281.9313 | 281.9313 | -88.0592 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 344.5827 | 344.5827 | 0 | 8.5 | 0 | 57.4305 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 337.6911 | 67.5382 | 0.6754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 09:00 | 6 | 1 | 9 | 152 | 3633 | 68 | 0 | 1323.6455 | 1323.6455 | -1323.6455 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1617.7889 | 1617.7889 | 0 | 8.5 | 0 | 269.6315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1585.4331 | 317.0866 | 3.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 10:00 | 6 | 1 | 10 | 152 | 3634 | 66.02 | 0 | 2986.6495 | 2986.6495 | -2986.6495 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3650.3494 | 3650.3494 | 0 | 8.5 | 0 | 608.3916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3577.3424 | 715.4685 | 7.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 11:00 | 6 | 1 | 11 | 152 | 3635 | 66.02 | 0 | 6040.9374 | 6040.9374 | -6040.9374 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7383.368 | 7383.368 | 0 | 8.5 | 0 | 1230.5613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7235.7006 | 1447.1401 | 14.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 12:00 | 6 | 1 | 12 | 152 | 3636 | 71.96 | 0 | 7598.4386 | 7598.4386 | -7598.4386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9286.9806 | 9286.9806 | 0 | 8.5 | 0 | 1547.8301 | 30.96% | 1 | 61.91% | 0% | 0% | 0% | 27.0548 | 0 | 0 | 0 | 27.0548 | 0 | 9101.241 | 1820.2482 | 18.2% | 1 | 36.4% | 0% | 0% | 3.9883 | 0 | 0 | 3.9883 | 31.0431
2007-06-01 13:00 | 6 | 1 | 13 | 152 | 3637 | 77 | 0 | 9126.3604 | 9126.3604 | -9126.3604 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11154.4404 | 11154.4404 | 0 | 8.5 | 0 | 1859.0734 | 37.18% | 1 | 74.36% | 0% | 0% | 0% | 41.2347 | 0 | 0 | 0 | 41.2347 | 0 | 10931.3516 | 2186.2703 | 21.86% | 1 | 43.73% | 0% | 0% | 6.0786 | 0 | 0 | 6.0786 | 47.3133
2007-06-01 14:00 | 6 | 1 | 14 | 152 | 3638 | 77 | 0 | 9343.8251 | 9343.8251 | -9343.8251 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11420.2307 | 11420.2307 | 0 | 8.5 | 0 | 1903.3718 | 38.07% | 1 | 76.13% | 0% | 0% | 0% | 43.5297 | 0 | 0 | 0 | 43.5297 | 0 | 11191.8261 | 2238.3652 | 22.38% | 1 | 44.77% | 0% | 0% | 6.4169 | 0 | 0 | 6.4169 | 49.9465
2007-06-01 15:00 | 6 | 1 | 15 | 152 | 3639 | 75.92 | 0 | 9010.7111 | 9010.7111 | -9010.7111 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11013.0914 | 11013.0914 | 0 | 8.5 | 0 | 1835.5152 | 36.71% | 1 | 73.42% | 0% | 0% | 0% | 40.0428 | 0 | 0 | 0 | 40.0428 | 0 | 10792.8296 | 2158.5659 | 21.59% | 1 | 43.17% | 0% | 0% | 5.9029 | 0 | 0 | 5.9029 | 45.9457
2007-06-01 16:00 | 6 | 1 | 16 | 152 | 3640 | 73.94 | 0 | 8576.6155 | 8576.6155 | -8576.6155 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10482.5301 | 10482.5301 | 0 | 8.5 | 0 | 1747.0884 | 34.94% | 1 | 69.88% | 0% | 0% | 0% | 35.7442 | 0 | 0 | 0 | 35.7442 | 0 | 10272.8795 | 2054.5759 | 20.55% | 1 | 41.09% | 0% | 0% | 5.2692 | 0 | 0 | 5.2692 | 41.0134
2007-06-01 17:00 | 6 | 1 | 17 | 152 | 3641 | 73.94 | 0 | 8319.333 | 8319.333 | -8319.333 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10168.0737 | 10168.0737 | 0 | 8.5 | 0 | 1694.6789 | 33.89% | 1 | 67.79% | 0% | 0% | 0% | 33.3259 | 0 | 0 | 0 | 33.3259 | 0 | 9964.7122 | 1992.9424 | 19.93% | 1 | 39.86% | 0% | 0% | 4.9127 | 0 | 0 | 4.9127 | 38.2386
2007-06-01 18:00 | 6 | 1 | 18 | 152 | 3642 | 75.92 | 0 | 5639.0753 | 5639.0753 | -5639.0753 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6892.2032 | 6892.2032 | 0 | 8.5 | 0 | 1148.7005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6754.3591 | 1350.8718 | 13.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 19:00 | 6 | 1 | 19 | 152 | 3643 | 73.04 | 0 | 2431.8375 | 2431.8375 | -2431.8375 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2972.2459 | 2972.2459 | 0 | 8.5 | 0 | 495.3743 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2912.8009 | 582.5602 | 5.826% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 20:00 | 6 | 1 | 20 | 152 | 3644 | 73.04 | 0 | 563.4222 | 563.4222 | -563.4222 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 688.6272 | 688.6272 | 0 | 8.5 | 0 | 114.7712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 674.8546 | 134.9709 | 1.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 21:00 | 6 | 1 | 21 | 152 | 3645 | 71.06 | 0 | 440.7053 | 440.7053 | -440.7053 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 538.6398 | 538.6398 | 0 | 8.5 | 0 | 89.7733 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 527.8671 | 105.5734 | 1.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 22:00 | 6 | 1 | 22 | 152 | 3646 | 66.92 | 0 | 335.9253 | 335.9253 | -335.9253 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 410.5754 | 410.5754 | 0 | 8.5 | 0 | 68.4292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 402.3639 | 80.4728 | 0.8047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-01 23:00 | 6 | 1 | 23 | 152 | 3647 | 66.92 | 0 | 82.0647 | 82.0647 | -82.0647 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 100.3013 | 100.3013 | 0 | 8.5 | 0 | 16.7169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 98.2953 | 19.6591 | 0.1966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 | 6 | 2 | 0 | 153 | 3648 | 64.04 | 12.4963 | 0 | 0 | 12.4963 | Heating | 11.0261 | 8.5 | 11.0261 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.2052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.2511 | 0 | 2.2502 | 0.0225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 01:00 | 6 | 2 | 1 | 153 | 3649 | 62.06 | 29.7761 | 0 | 0 | 29.7761 | Heating | 26.2731 | 8.5 | 26.2731 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.2546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 26.8092 | 0 | 5.3618 | 0.05362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 02:00 | 6 | 2 | 2 | 153 | 3650 | 62.06 | 45.5433 | 0 | 0 | 45.5433 | Heating | 40.1853 | 8.5 | 40.1853 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.0371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 41.0054 | 0 | 8.2011 | 0.08201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 03:00 | 6 | 2 | 3 | 153 | 3651 | 59 | 60.9048 | 0 | 0 | 60.9048 | Heating | 53.7396 | 8.5 | 53.7396 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.7479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 54.8363 | 0 | 10.9673 | 0.1097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 04:00 | 6 | 2 | 4 | 153 | 3652 | 59 | 86.0713 | 0 | 0 | 86.0713 | Heating | 75.9453 | 8.5 | 75.9453 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.1891 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.4952 | 0 | 15.499 | 0.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 05:00 | 6 | 2 | 5 | 153 | 3653 | 59 | 111.5136 | 0 | 0 | 111.5136 | Heating | 98.3943 | 8.5 | 98.3943 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.6789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 100.4024 | 0 | 20.0805 | 0.2008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 06:00 | 6 | 2 | 6 | 153 | 3654 | 62.06 | 133.8783 | 0 | 0 | 133.8783 | Heating | 118.1279 | 8.5 | 118.1279 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.6256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 120.5387 | 0 | 24.1077 | 0.2411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 07:00 | 6 | 2 | 7 | 153 | 3655 | 66.92 | 145.3997 | 0 | 0 | 145.3997 | Heating | 128.2938 | 8.5 | 128.2938 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.6588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 130.9121 | 0 | 26.1824 | 0.2618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 08:00 | 6 | 2 | 8 | 153 | 3656 | 66.92 | 3518.7606 | 0 | 0 | 3518.7606 | Heating | 3104.7888 | 8.5 | 3104.7888 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 620.9578 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3168.1518 | 0 | 633.6304 | 6.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 09:00 | 6 | 2 | 9 | 153 | 3657 | 73.04 | 2451.5604 | 0 | 0 | 2451.5604 | Heating | 2163.1415 | 8.5 | 2163.1415 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 432.6283 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2207.2872 | 0 | 441.4574 | 4.415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 10:00 | 6 | 2 | 10 | 153 | 3658 | 75.92 | 1824.3046 | 0 | 0 | 1824.3046 | Heating | 1609.6805 | 8.5 | 1609.6805 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.9361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1642.5311 | 0 | 328.5062 | 3.285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 11:00 | 6 | 2 | 11 | 153 | 3659 | 75.92 | 1545.7941 | 0 | 0 | 1545.7941 | Heating | 1363.9359 | 8.5 | 1363.9359 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.7872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1391.7714 | 0 | 278.3543 | 2.784% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 12:00 | 6 | 2 | 12 | 153 | 3660 | 80.96 | 925.052 | 0 | 0 | 925.052 | Heating | 816.2223 | 8.5 | 816.2223 | 0 | 9.3522 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.2445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 832.8799 | 0 | 166.576 | 1.666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 13:00 | 6 | 2 | 13 | 153 | 3661 | 82.04 | 459.9106 | 0 | 0 | 459.9106 | Heating | 405.8034 | 8.5 | 405.8034 | 0 | 9.6047 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.1607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 414.0851 | 0 | 82.817 | 0.8282% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 14:00 | 6 | 2 | 14 | 153 | 3662 | 82.04 | 73.332 | 0 | 0 | 73.332 | Heating | 64.7047 | 8.5 | 64.7047 | 0 | 9.6047 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.9409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 66.0252 | 0 | 13.205 | 0.1321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 15:00 | 6 | 2 | 15 | 153 | 3663 | 84.02 | 17.9764 | 0 | 0 | 17.9764 | Heating | 15.8616 | 8.5 | 15.8616 | 0 | 10.0848 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.1723 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.1853 | 0 | 3.2371 | 0.03237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 16:00 | 6 | 2 | 16 | 153 | 3664 | 82.94 | 11.1317 | 0 | 0 | 11.1317 | Heating | 9.8221 | 8.5 | 9.8221 | 0 | 9.8202 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.9644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.0226 | 0 | 2.0045 | 0.02005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 17:00 | 6 | 2 | 17 | 153 | 3665 | 82.94 | 263.5794 | 0 | 0 | 263.5794 | Heating | 232.5701 | 8.5 | 232.5701 | 0 | 9.8202 | 0 | 0 | 0 | 0 | 8.5 | 0 | 46.514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 237.3164 | 0 | 47.4633 | 0.4746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 18:00 | 6 | 2 | 18 | 153 | 3666 | 80.96 | 705.5649 | 0 | 0 | 705.5649 | Heating | 622.5572 | 8.5 | 622.5572 | 0 | 9.3522 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.5114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 635.2625 | 0 | 127.0525 | 1.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 19:00 | 6 | 2 | 19 | 153 | 3667 | 80.06 | 20.6616 | 0 | 0 | 20.6616 | Heating | 18.2309 | 8.5 | 18.2309 | 0 | 9.1467 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.6462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.6029 | 0 | 3.7206 | 0.03721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 20:00 | 6 | 2 | 20 | 153 | 3668 | 80.06 | 68.2125 | 0 | 0 | 68.2125 | Heating | 60.1875 | 8.5 | 60.1875 | 0 | 9.1467 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.0375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 61.4158 | 0 | 12.2832 | 0.1228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 21:00 | 6 | 2 | 21 | 153 | 3669 | 75.92 | 134.7016 | 0 | 0 | 134.7016 | Heating | 118.8544 | 8.5 | 118.8544 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.7709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 121.28 | 0 | 24.256 | 0.2426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 22:00 | 6 | 2 | 22 | 153 | 3670 | 75.02 | 212.7598 | 0 | 0 | 212.7598 | Heating | 187.7292 | 8.5 | 187.7292 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 37.5458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 191.5604 | 0 | 38.3121 | 0.3831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-02 23:00 | 6 | 2 | 23 | 153 | 3671 | 75.02 | 303.671 | 0 | 0 | 303.671 | Heating | 267.945 | 8.5 | 267.945 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 273.4132 | 0 | 54.6826 | 0.5468% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 | 6 | 3 | 0 | 154 | 3672 | 73.04 | 389.8611 | 0 | 0 | 389.8611 | Heating | 343.9951 | 8.5 | 343.9951 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 351.0154 | 0 | 70.2031 | 0.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 01:00 | 6 | 3 | 1 | 154 | 3673 | 73.04 | 465.8307 | 0 | 0 | 465.8307 | Heating | 411.027 | 8.5 | 411.027 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.2054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 419.4154 | 0 | 83.8831 | 0.8388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 02:00 | 6 | 3 | 2 | 154 | 3674 | 73.04 | 533.745 | 0 | 0 | 533.745 | Heating | 470.9514 | 8.5 | 470.9514 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.1903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 480.5627 | 0 | 96.1125 | 0.9611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 03:00 | 6 | 3 | 3 | 154 | 3675 | 71.6 | 602.4789 | 0 | 0 | 602.4789 | Heating | 531.599 | 8.5 | 531.599 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.3198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.448 | 0 | 108.4896 | 1.085% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 04:00 | 6 | 3 | 4 | 154 | 3676 | 71.6 | 683.5078 | 0 | 0 | 683.5078 | Heating | 603.0951 | 8.5 | 603.0951 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 615.4032 | 0 | 123.0806 | 1.231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 05:00 | 6 | 3 | 5 | 154 | 3677 | 69.98 | 734.0735 | 0 | 0 | 734.0735 | Heating | 647.7119 | 8.5 | 647.7119 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.5424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 660.9305 | 0 | 132.1861 | 1.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 06:00 | 6 | 3 | 6 | 154 | 3678 | 71.06 | 6904.7187 | 0 | 0 | 6904.7187 | Heating | 6092.3989 | 8.5 | 6092.3989 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1218.4798 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6216.7335 | 0 | 1243.3467 | 12.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 07:00 | 6 | 3 | 7 | 154 | 3679 | 71.06 | 4145.8246 | 0 | 0 | 4145.8246 | Heating | 3658.0805 | 8.5 | 3658.0805 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 731.6161 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3732.7352 | 0 | 746.547 | 7.465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 08:00 | 6 | 3 | 8 | 154 | 3680 | 71.06 | 2746.1153 | 27.2284 | 27.2284 | 2718.8869 | Heating | 2399.0179 | 8.5 | 2399.0179 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 479.8036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2447.9774 | 0 | 489.5955 | 4.896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 09:00 | 6 | 3 | 9 | 154 | 3681 | 73.94 | 1416.2792 | 116.2726 | 116.2726 | 1300.0066 | Heating | 1147.0646 | 8.5 | 1147.0646 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.4129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1170.4741 | 0 | 234.0948 | 2.341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 10:00 | 6 | 3 | 10 | 154 | 3682 | 75.02 | 822.0353 | 183.9061 | 183.9061 | 638.1292 | Heating | 563.0552 | 8.5 | 563.0552 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 574.5461 | 0 | 114.9092 | 1.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 11:00 | 6 | 3 | 11 | 154 | 3683 | 75.02 | 244.1306 | 195.385 | 195.385 | 48.7456 | Heating | 43.0108 | 8.5 | 43.0108 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.6022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.8886 | 0 | 8.7777 | 0.08778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 12:00 | 6 | 3 | 12 | 154 | 3684 | 75.92 | 120.7831 | 261.8678 | 261.8678 | -141.0848 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 320.0607 | 320.0607 | 0 | 8.5 | 0 | 53.3435 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 313.6595 | 62.7319 | 0.6273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 13:00 | 6 | 3 | 13 | 154 | 3685 | 77 | 75.5711 | 511.3889 | 511.3889 | -435.8179 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 625.0309 | 625.0309 | 0 | 8.5 | 0 | 104.1718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 612.5303 | 122.5061 | 1.225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 14:00 | 6 | 3 | 14 | 154 | 3686 | 77 | 30.9118 | 904.0369 | 904.0369 | -873.1251 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1104.934 | 1104.934 | 0 | 8.5 | 0 | 184.1557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1082.8353 | 216.5671 | 2.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 15:00 | 6 | 3 | 15 | 154 | 3687 | 75.92 | 7.1876 | 1424.5056 | 1424.5056 | -1417.318 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1741.0624 | 1741.0624 | 0 | 8.5 | 0 | 290.1771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1706.2411 | 341.2482 | 3.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 16:00 | 6 | 3 | 16 | 154 | 3688 | 75.02 | 1.5238 | 1830.6298 | 1830.6298 | -1829.106 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2237.4364 | 2237.4364 | 0 | 8.5 | 0 | 372.9061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2192.6877 | 438.5375 | 4.385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 17:00 | 6 | 3 | 17 | 154 | 3689 | 75.02 | 0 | 1890.6122 | 1890.6122 | -1890.6122 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2310.7482 | 2310.7482 | 0 | 8.5 | 0 | 385.1247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2264.5332 | 452.9066 | 4.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 18:00 | 6 | 3 | 18 | 154 | 3690 | 75.02 | 0 | 731.4416 | 731.4416 | -731.4416 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 893.9842 | 893.9842 | 0 | 8.5 | 0 | 148.9974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 876.1045 | 175.2209 | 1.752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 19:00 | 6 | 3 | 19 | 154 | 3691 | 71.06 | 0.074092 | 314.9796 | 314.9796 | -314.9055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 384.975 | 384.975 | 0 | 8.5 | 0 | 64.1625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 377.2755 | 75.4551 | 0.7546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 20:00 | 6 | 3 | 20 | 154 | 3692 | 71.06 | 7.164 | 193.579 | 193.579 | -186.415 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 236.5966 | 236.5966 | 0 | 8.5 | 0 | 39.4328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 231.8646 | 46.3729 | 0.4637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 21:00 | 6 | 3 | 21 | 154 | 3693 | 68 | 46.5432 | 121.9406 | 121.9406 | -75.3974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 149.0385 | 149.0385 | 0 | 8.5 | 0 | 24.8397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 146.0577 | 29.2115 | 0.2921% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 22:00 | 6 | 3 | 22 | 154 | 3694 | 64.94 | 114.508 | 0 | 0 | 114.508 | Heating | 101.0364 | 8.5 | 101.0364 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.2073 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 103.0984 | 0 | 20.6197 | 0.2062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-03 23:00 | 6 | 3 | 23 | 154 | 3695 | 64.94 | 172.5213 | 0 | 0 | 172.5213 | Heating | 152.2247 | 8.5 | 152.2247 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.4449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 155.3313 | 0 | 31.0663 | 0.3107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 | 6 | 4 | 0 | 155 | 3696 | 62.96 | 203.7939 | 0 | 0 | 203.7939 | Heating | 179.8181 | 8.5 | 179.8181 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.9636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 183.4879 | 0 | 36.6976 | 0.367% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 01:00 | 6 | 4 | 1 | 155 | 3697 | 64.4 | 221.284 | 0 | 0 | 221.284 | Heating | 195.2506 | 8.5 | 195.2506 | 0 | 6.2364 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.0501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 199.2353 | 0 | 39.8471 | 0.3985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 02:00 | 6 | 4 | 2 | 155 | 3698 | 62.96 | 258.337 | 0 | 0 | 258.337 | Heating | 227.9444 | 8.5 | 227.9444 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.5889 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 232.5963 | 0 | 46.5193 | 0.4652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 03:00 | 6 | 4 | 3 | 155 | 3699 | 64.04 | 300.7862 | 0 | 0 | 300.7862 | Heating | 265.3996 | 8.5 | 265.3996 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.0799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 270.8159 | 0 | 54.1632 | 0.5416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 04:00 | 6 | 4 | 4 | 155 | 3700 | 64.04 | 340.9679 | 0 | 0 | 340.9679 | Heating | 300.854 | 8.5 | 300.854 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.1708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 306.9939 | 0 | 61.3988 | 0.614% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 05:00 | 6 | 4 | 5 | 155 | 3701 | 64.04 | 353.8118 | 0 | 0 | 353.8118 | Heating | 312.1869 | 8.5 | 312.1869 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.4374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 318.5581 | 0 | 63.7116 | 0.6371% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 06:00 | 6 | 4 | 6 | 155 | 3702 | 64.94 | 3867.7976 | 59.3425 | 59.3425 | 3808.4551 | Heating | 3360.4015 | 8.5 | 3360.4015 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 672.0803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3428.9812 | 0 | 685.7962 | 6.858% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 07:00 | 6 | 4 | 7 | 155 | 3703 | 68 | 2095.3482 | 8.5821 | 8.5821 | 2086.7661 | Heating | 1841.2642 | 8.5 | 1841.2642 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.2528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1878.841 | 0 | 375.7682 | 3.758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 08:00 | 6 | 4 | 8 | 155 | 3704 | 68 | 1098.6766 | 188.0146 | 188.0146 | 910.662 | Heating | 803.5253 | 8.5 | 803.5253 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.7051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 819.9238 | 0 | 163.9848 | 1.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 09:00 | 6 | 4 | 9 | 155 | 3705 | 71.96 | 91.8377 | 538.1727 | 538.1727 | -446.335 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 657.7667 | 657.7667 | 0 | 8.5 | 0 | 109.6278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 644.6114 | 128.9223 | 1.289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 10:00 | 6 | 4 | 10 | 155 | 3706 | 73.94 | 11.0137 | 1297.8399 | 1297.8399 | -1286.8262 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1586.2488 | 1586.2488 | 0 | 8.5 | 0 | 264.3748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1554.5238 | 310.9048 | 3.109% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 11:00 | 6 | 4 | 11 | 155 | 3707 | 73.94 | 0.24937 | 2523.3038 | 2523.3038 | -2523.0544 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3084.038 | 3084.038 | 0 | 8.5 | 0 | 514.0063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3022.3572 | 604.4714 | 6.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 12:00 | 6 | 4 | 12 | 155 | 3708 | 77 | 0 | 4466.7248 | 4466.7248 | -4466.7248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5459.3303 | 5459.3303 | 0 | 8.5 | 0 | 909.8884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5350.1437 | 1070.0287 | 10.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 13:00 | 6 | 4 | 13 | 155 | 3709 | 80.06 | 0 | 5746.2056 | 5746.2056 | -5746.2056 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7023.1402 | 7023.1402 | 0 | 8.5 | 0 | 1170.5234 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6882.6774 | 1376.5355 | 13.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 14:00 | 6 | 4 | 14 | 155 | 3710 | 80.06 | 0 | 6796.3345 | 6796.3345 | -6796.3345 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8306.6311 | 8306.6311 | 0 | 8.5 | 0 | 1384.4385 | 30% | 1 | 55.38% | 0% | 0% | 0% | 20.932 | 0 | 0 | 0 | 20.932 | 0 | 8140.4985 | 1628.0997 | 16.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.2065
2007-06-04 15:00 | 6 | 4 | 15 | 155 | 3711 | 78.98 | 0 | 7382.3894 | 7382.3894 | -7382.3894 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9022.9203 | 9022.9203 | 0 | 8.5 | 0 | 1503.8201 | 30.08% | 1 | 60.15% | 0% | 0% | 0% | 25.3181 | 0 | 0 | 0 | 25.3181 | 0 | 8842.4619 | 1768.4924 | 17.68% | 1 | 35.37% | 0% | 0% | 3.7322 | 0 | 0 | 3.7322 | 29.0504
2007-06-04 16:00 | 6 | 4 | 16 | 155 | 3712 | 82.04 | 0 | 7662.9449 | 7662.9449 | -7662.9449 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9365.8216 | 9365.8216 | 0 | 8.5 | 0 | 1560.9703 | 31.22% | 1 | 62.44% | 0% | 0% | 0% | 27.586 | 0 | 0 | 0 | 27.586 | 0 | 9178.5052 | 1835.701 | 18.36% | 1 | 36.71% | 0% | 0% | 4.0666 | 0 | 0 | 4.0666 | 31.6526
2007-06-04 17:00 | 6 | 4 | 17 | 155 | 3713 | 82.04 | 0 | 7692.6481 | 7692.6481 | -7692.6481 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9402.1254 | 9402.1254 | 0 | 8.5 | 0 | 1567.0209 | 31.34% | 1 | 62.68% | 0% | 0% | 0% | 27.8326 | 0 | 0 | 0 | 27.8326 | 0 | 9214.0829 | 1842.8166 | 18.43% | 1 | 36.86% | 0% | 0% | 4.1029 | 0 | 0 | 4.1029 | 31.9355
2007-06-04 18:00 | 6 | 4 | 18 | 155 | 3714 | 80.06 | 0 | 5259.2371 | 5259.2371 | -5259.2371 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6427.9565 | 6427.9565 | 0 | 8.5 | 0 | 1071.3261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6299.3974 | 1259.8795 | 12.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 19:00 | 6 | 4 | 19 | 155 | 3715 | 77 | 0 | 4591.1026 | 4591.1026 | -4591.1026 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5611.3476 | 5611.3476 | 0 | 8.5 | 0 | 935.2246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5499.1206 | 1099.8241 | 11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 20:00 | 6 | 4 | 20 | 155 | 3716 | 77 | 0 | 3435.2876 | 3435.2876 | -3435.2876 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4198.6848 | 4198.6848 | 0 | 8.5 | 0 | 699.7808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4114.7111 | 822.9422 | 8.229% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 21:00 | 6 | 4 | 21 | 155 | 3717 | 71.96 | 0 | 1391.5125 | 1391.5125 | -1391.5125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1700.7375 | 1700.7375 | 0 | 8.5 | 0 | 283.4562 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1666.7227 | 333.3445 | 3.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 22:00 | 6 | 4 | 22 | 155 | 3718 | 69.98 | 0 | 97.4155 | 97.4155 | -97.4155 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 119.0633 | 119.0633 | 0 | 8.5 | 0 | 19.8439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 116.6821 | 23.3364 | 0.2334% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-04 23:00 | 6 | 4 | 23 | 155 | 3719 | 69.98 | 0 | 16.2471 | 16.2471 | -16.2471 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19.8576 | 19.8576 | 0 | 8.5 | 0 | 3.3096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 19.4605 | 3.8921 | 0.03892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 | 6 | 5 | 0 | 156 | 3720 | 69.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-05 01:00 | 6 | 5 | 1 | 156 | 3721 | 69.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-05 02:00 | 6 | 5 | 2 | 156 | 3722 | 69.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-05 03:00 | 6 | 5 | 3 | 156 | 3723 | 71.06 | 0.73808 | 0 | 0 | 0.73808 | Heating | 0.65125 | 8.5 | 0.65125 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.13025 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.66454 | 0 | 0.13291 | 0.001329% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 04:00 | 6 | 5 | 4 | 156 | 3724 | 69.08 | 2.156 | 0 | 0 | 2.156 | Heating | 1.9024 | 8.5 | 1.9024 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.38048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.9412 | 0 | 0.38824 | 0.003882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 05:00 | 6 | 5 | 5 | 156 | 3725 | 69.08 | 0.74826 | 0 | 0 | 0.74826 | Heating | 0.66023 | 8.5 | 0.66023 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.13205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.67371 | 0 | 0.13474 | 0.001347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 06:00 | 6 | 5 | 6 | 156 | 3726 | 64.94 | 692.5766 | 414.972 | 414.972 | 277.6046 | Heating | 244.9452 | 8.5 | 244.9452 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 249.9441 | 0 | 49.9888 | 0.4999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 07:00 | 6 | 5 | 7 | 156 | 3727 | 66.02 | 316.7965 | 306.4747 | 306.4747 | 10.3218 | Heating | 9.1074 | 8.5 | 9.1074 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.8215 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.2933 | 0 | 1.8587 | 0.01859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 08:00 | 6 | 5 | 8 | 156 | 3728 | 66.02 | 25.0154 | 1813.2198 | 1813.2198 | -1788.2044 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2216.1576 | 2216.1576 | 0 | 8.5 | 0 | 369.3596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2171.8344 | 434.3669 | 4.344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 09:00 | 6 | 5 | 9 | 156 | 3729 | 71.96 | 0.60285 | 2913.63 | 2913.63 | -2913.0272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3561.1034 | 3561.1034 | 0 | 8.5 | 0 | 593.5172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3489.8813 | 697.9763 | 6.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 10:00 | 6 | 5 | 10 | 156 | 3730 | 75.92 | 0 | 4084.3973 | 4084.3973 | -4084.3973 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4992.0411 | 4992.0411 | 0 | 8.5 | 0 | 832.0069 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4892.2003 | 978.4401 | 9.784% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 11:00 | 6 | 5 | 11 | 156 | 3731 | 75.92 | 0 | 6639.7524 | 6639.7524 | -6639.7524 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8115.2529 | 8115.2529 | 0 | 8.5 | 0 | 1352.5421 | 30% | 1 | 54.1% | 0% | 0% | 0% | 19.8394 | 0 | 0 | 0 | 19.8394 | 0 | 7952.9478 | 1590.5896 | 15.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.1139
2007-06-05 12:00 | 6 | 5 | 12 | 156 | 3732 | 82.94 | 0 | 7805.9909 | 7805.9909 | -7805.9909 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9540.6555 | 9540.6555 | 0 | 8.5 | 0 | 1590.1093 | 31.8% | 1 | 63.6% | 0% | 0% | 0% | 28.7848 | 0 | 0 | 0 | 28.7848 | 0 | 9349.8424 | 1869.9685 | 18.7% | 1 | 37.4% | 0% | 0% | 4.2433 | 0 | 0 | 4.2433 | 33.0281
2007-06-05 13:00 | 6 | 5 | 13 | 156 | 3733 | 84.2 | 0 | 8038.3448 | 8038.3448 | -8038.3448 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9824.6436 | 9824.6436 | 0 | 8.5 | 0 | 1637.4406 | 32.75% | 1 | 65.5% | 0% | 0% | 0% | 30.7937 | 0 | 0 | 0 | 30.7937 | 0 | 9628.1507 | 1925.6301 | 19.26% | 1 | 38.51% | 0% | 0% | 4.5394 | 0 | 0 | 4.5394 | 35.3331
2007-06-05 14:00 | 6 | 5 | 14 | 156 | 3734 | 82.94 | 0 | 8696.4451 | 8696.4451 | -8696.4451 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10628.9885 | 10628.9885 | 0 | 8.5 | 0 | 1771.4981 | 35.43% | 1 | 70.86% | 0% | 0% | 0% | 36.9032 | 0 | 0 | 0 | 36.9032 | 0 | 10416.4087 | 2083.2817 | 20.83% | 1 | 41.67% | 0% | 0% | 5.44 | 0 | 0 | 5.44 | 42.3433
2007-06-05 15:00 | 6 | 5 | 15 | 156 | 3735 | 82.94 | 0 | 8458.2761 | 8458.2761 | -8458.2761 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10337.893 | 10337.893 | 0 | 8.5 | 0 | 1722.9822 | 34.46% | 1 | 68.92% | 0% | 0% | 0% | 34.62 | 0 | 0 | 0 | 34.62 | 0 | 10131.1352 | 2026.227 | 20.26% | 1 | 40.52% | 0% | 0% | 5.1035 | 0 | 0 | 5.1035 | 39.7234
2007-06-05 16:00 | 6 | 5 | 16 | 156 | 3736 | 78.8 | 0 | 8048.5389 | 8048.5389 | -8048.5389 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9837.1031 | 9837.1031 | 0 | 8.5 | 0 | 1639.5172 | 32.79% | 1 | 65.58% | 0% | 0% | 0% | 30.8836 | 0 | 0 | 0 | 30.8836 | 0 | 9640.361 | 1928.0722 | 19.28% | 1 | 38.56% | 0% | 0% | 4.5527 | 0 | 0 | 4.5527 | 35.4363
2007-06-05 17:00 | 6 | 5 | 17 | 156 | 3737 | 80.06 | 0 | 7643.5457 | 7643.5457 | -7643.5457 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9342.1115 | 9342.1115 | 0 | 8.5 | 0 | 1557.0186 | 31.14% | 1 | 62.28% | 0% | 0% | 0% | 27.4256 | 0 | 0 | 0 | 27.4256 | 0 | 9155.2692 | 1831.0538 | 18.31% | 1 | 36.62% | 0% | 0% | 4.0429 | 0 | 0 | 4.0429 | 31.4686
2007-06-05 18:00 | 6 | 5 | 18 | 156 | 3738 | 78.98 | 0 | 4799.339 | 4799.339 | -4799.339 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5865.8588 | 5865.8588 | 0 | 8.5 | 0 | 977.6431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5748.5416 | 1149.7083 | 11.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 19:00 | 6 | 5 | 19 | 156 | 3739 | 77 | 0 | 2160.5158 | 2160.5158 | -2160.5158 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2640.6305 | 2640.6305 | 0 | 8.5 | 0 | 440.1051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2587.8179 | 517.5636 | 5.176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 20:00 | 6 | 5 | 20 | 156 | 3740 | 77 | 0 | 412.9227 | 412.9227 | -412.9227 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 504.6833 | 504.6833 | 0 | 8.5 | 0 | 84.1139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 494.5896 | 98.9179 | 0.9892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 21:00 | 6 | 5 | 21 | 156 | 3741 | 73.94 | 0 | 285.8642 | 285.8642 | -285.8642 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 349.3896 | 349.3896 | 0 | 8.5 | 0 | 58.2316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 342.4018 | 68.4804 | 0.6848% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 22:00 | 6 | 5 | 22 | 156 | 3742 | 71.96 | 2.7881 | 0 | 0 | 2.7881 | Heating | 2.4601 | 8.5 | 2.4601 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.49203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.5103 | 0 | 0.50207 | 0.005021% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-05 23:00 | 6 | 5 | 23 | 156 | 3743 | 71.96 | 8.5471 | 0 | 0 | 8.5471 | Heating | 7.5416 | 8.5 | 7.5416 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.6955 | 0 | 1.5391 | 0.01539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 | 6 | 6 | 0 | 157 | 3744 | 69.98 | 15.2667 | 0 | 0 | 15.2667 | Heating | 13.4706 | 8.5 | 13.4706 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.6941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.7455 | 0 | 2.7491 | 0.02749% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 01:00 | 6 | 6 | 1 | 157 | 3745 | 68 | 20.9347 | 0 | 0 | 20.9347 | Heating | 18.4718 | 8.5 | 18.4718 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.6944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.8488 | 0 | 3.7698 | 0.0377% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 02:00 | 6 | 6 | 2 | 157 | 3746 | 68 | 24.9573 | 0 | 0 | 24.9573 | Heating | 22.0211 | 8.5 | 22.0211 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.4042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.4705 | 0 | 4.4941 | 0.04494% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 03:00 | 6 | 6 | 3 | 157 | 3747 | 66.92 | 28.22 | 0 | 0 | 28.22 | Heating | 24.9 | 8.5 | 24.9 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.98 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 25.4081 | 0 | 5.0816 | 0.05082% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 04:00 | 6 | 6 | 4 | 157 | 3748 | 66.02 | 30.2145 | 0 | 0 | 30.2145 | Heating | 26.6599 | 8.5 | 26.6599 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 27.2039 | 0 | 5.4408 | 0.05441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 05:00 | 6 | 6 | 5 | 157 | 3749 | 66.02 | 29.4361 | 0 | 0 | 29.4361 | Heating | 25.973 | 8.5 | 25.973 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.1946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 26.5031 | 0 | 5.3006 | 0.05301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 06:00 | 6 | 6 | 6 | 157 | 3750 | 62.06 | 1569.8091 | 148.1481 | 148.1481 | 1421.661 | Heating | 1254.4067 | 8.5 | 1254.4067 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 250.8813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1280.0069 | 0 | 256.0014 | 2.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 07:00 | 6 | 6 | 7 | 157 | 3751 | 60.98 | 1171.842 | 23.6454 | 23.6454 | 1148.1966 | Heating | 1013.1146 | 8.5 | 1013.1146 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.6229 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1033.7904 | 0 | 206.7581 | 2.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 08:00 | 6 | 6 | 8 | 157 | 3752 | 60.98 | 713.1001 | 634.4669 | 634.4669 | 78.6332 | Heating | 69.3823 | 8.5 | 69.3823 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.8765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 70.7982 | 0 | 14.1596 | 0.1416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 09:00 | 6 | 6 | 9 | 157 | 3753 | 62.6 | 109.9441 | 937.4605 | 937.4605 | -827.5163 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1145.785 | 1145.785 | 0 | 8.5 | 0 | 190.9642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1122.8693 | 224.5739 | 2.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 10:00 | 6 | 6 | 10 | 157 | 3754 | 62.6 | 25.7113 | 1173.9859 | 1173.9859 | -1148.2746 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1434.8717 | 1434.8717 | 0 | 8.5 | 0 | 239.1453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1406.1742 | 281.2348 | 2.812% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 11:00 | 6 | 6 | 11 | 157 | 3755 | 62.96 | 19.3895 | 1255.2578 | 1255.2578 | -1235.8683 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1534.204 | 1534.204 | 0 | 8.5 | 0 | 255.7007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1503.5199 | 300.704 | 3.007% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 12:00 | 6 | 6 | 12 | 157 | 3756 | 68 | 18.2989 | 1286.0652 | 1286.0652 | -1267.7663 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1571.8575 | 1571.8575 | 0 | 8.5 | 0 | 261.9763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1540.4204 | 308.0841 | 3.081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 13:00 | 6 | 6 | 13 | 157 | 3757 | 73.94 | 15.0351 | 1445.5019 | 1445.5019 | -1430.4668 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1766.7246 | 1766.7246 | 0 | 8.5 | 0 | 294.4541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1731.3901 | 346.278 | 3.463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 14:00 | 6 | 6 | 14 | 157 | 3758 | 73.94 | 12.6888 | 1528.2859 | 1528.2859 | -1515.5971 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1867.905 | 1867.905 | 0 | 8.5 | 0 | 311.3175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1830.5469 | 366.1094 | 3.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 15:00 | 6 | 6 | 15 | 157 | 3759 | 71.6 | 11.8336 | 1302.8624 | 1302.8624 | -1291.0288 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1592.3874 | 1592.3874 | 0 | 8.5 | 0 | 265.3979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1560.5396 | 312.1079 | 3.121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 16:00 | 6 | 6 | 16 | 157 | 3760 | 68 | 6.1509 | 1569.1848 | 1569.1848 | -1563.0339 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1917.8926 | 1917.8926 | 0 | 8.5 | 0 | 319.6488 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1879.5347 | 375.9069 | 3.759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 17:00 | 6 | 6 | 17 | 157 | 3761 | 66.92 | 2.4147 | 1273.2723 | 1273.2723 | -1270.8576 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1556.2217 | 1556.2217 | 0 | 8.5 | 0 | 259.3703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1525.0972 | 305.0194 | 3.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 18:00 | 6 | 6 | 18 | 157 | 3762 | 62.96 | 0.20841 | 383.6829 | 383.6829 | -383.4745 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 468.9457 | 468.9457 | 0 | 8.5 | 0 | 78.1576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 459.5668 | 91.9134 | 0.9191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 19:00 | 6 | 6 | 19 | 157 | 3763 | 60.08 | 1.9155 | 346.0588 | 346.0588 | -344.1433 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 422.9608 | 422.9608 | 0 | 8.5 | 0 | 70.4935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 414.5016 | 82.9003 | 0.829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 20:00 | 6 | 6 | 20 | 157 | 3764 | 60.08 | 5.3358 | 239.5595 | 239.5595 | -234.2237 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 292.7949 | 292.7949 | 0 | 8.5 | 0 | 48.7991 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 286.939 | 57.3878 | 0.5739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 21:00 | 6 | 6 | 21 | 157 | 3765 | 57.02 | 7.5733 | 203.6379 | 203.6379 | -196.0646 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 248.8907 | 248.8907 | 0 | 8.5 | 0 | 41.4818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 243.9129 | 48.7826 | 0.4878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 22:00 | 6 | 6 | 22 | 157 | 3766 | 55.04 | 11.9612 | 0 | 0 | 11.9612 | Heating | 10.554 | 8.5 | 10.554 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.7693 | 0 | 2.1539 | 0.02154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-06 23:00 | 6 | 6 | 23 | 157 | 3767 | 55.04 | 18.518 | 0 | 0 | 18.518 | Heating | 16.3394 | 8.5 | 16.3394 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.2679 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.6729 | 0 | 3.3346 | 0.03335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 | 6 | 7 | 0 | 158 | 3768 | 53.96 | 25.6009 | 0 | 0 | 25.6009 | Heating | 22.589 | 8.5 | 22.589 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.05 | 0 | 4.61 | 0.0461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 01:00 | 6 | 7 | 1 | 158 | 3769 | 51.98 | 34.5675 | 0 | 0 | 34.5675 | Heating | 30.5007 | 8.5 | 30.5007 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.1001 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 31.1232 | 0 | 6.2246 | 0.06225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 02:00 | 6 | 7 | 2 | 158 | 3770 | 51.98 | 43.951 | 0 | 0 | 43.951 | Heating | 38.7803 | 8.5 | 38.7803 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.7561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 39.5717 | 0 | 7.9143 | 0.07914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 03:00 | 6 | 7 | 3 | 158 | 3771 | 51.98 | 52.3256 | 0 | 0 | 52.3256 | Heating | 46.1697 | 8.5 | 46.1697 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.2339 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.1119 | 0 | 9.4224 | 0.09422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 04:00 | 6 | 7 | 4 | 158 | 3772 | 51.08 | 67.366 | 0 | 0 | 67.366 | Heating | 59.4406 | 8.5 | 59.4406 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.8881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 60.6537 | 0 | 12.1307 | 0.1213% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 05:00 | 6 | 7 | 5 | 158 | 3773 | 51.08 | 63.3362 | 0 | 0 | 63.3362 | Heating | 55.8848 | 8.5 | 55.8848 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.177 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 57.0254 | 0 | 11.4051 | 0.1141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 06:00 | 6 | 7 | 6 | 158 | 3774 | 53.06 | 1527.6193 | 215.9968 | 215.9968 | 1311.6225 | Heating | 1157.3139 | 8.5 | 1157.3139 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.4628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1180.9326 | 0 | 236.1865 | 2.362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 07:00 | 6 | 7 | 7 | 158 | 3775 | 57.92 | 1113.6603 | 56.6003 | 56.6003 | 1057.0601 | Heating | 932.7001 | 8.5 | 932.7001 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 186.54 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 951.7348 | 0 | 190.347 | 1.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 08:00 | 6 | 7 | 8 | 158 | 3776 | 57.92 | 566.3589 | 819.7402 | 819.7402 | -253.3813 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1001.9047 | 1001.9047 | 0 | 8.5 | 0 | 166.9841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 981.8666 | 196.3733 | 1.964% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 09:00 | 6 | 7 | 9 | 158 | 3777 | 64.04 | 22.1986 | 1247.3983 | 1247.3983 | -1225.1998 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1524.5979 | 1524.5979 | 0 | 8.5 | 0 | 254.0997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1494.106 | 298.8212 | 2.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 10:00 | 6 | 7 | 10 | 158 | 3778 | 66.92 | 6.5245 | 1876.7259 | 1876.7259 | -1870.2014 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2293.7761 | 2293.7761 | 0 | 8.5 | 0 | 382.296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2247.9006 | 449.5801 | 4.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 11:00 | 6 | 7 | 11 | 158 | 3779 | 66.92 | 0.34623 | 2425.1469 | 2425.1469 | -2424.8007 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2964.0684 | 2964.0684 | 0 | 8.5 | 0 | 494.0114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2904.7871 | 580.9574 | 5.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 12:00 | 6 | 7 | 12 | 158 | 3780 | 69.98 | 0 | 3215.1361 | 3215.1361 | -3215.1361 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3929.6108 | 3929.6108 | 0 | 8.5 | 0 | 654.9351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3851.0186 | 770.2037 | 7.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 13:00 | 6 | 7 | 13 | 158 | 3781 | 71.06 | 0 | 4683.0983 | 4683.0983 | -4683.0983 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5723.7869 | 5723.7869 | 0 | 8.5 | 0 | 953.9645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5609.3111 | 1121.8622 | 11.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 14:00 | 6 | 7 | 14 | 158 | 3782 | 71.06 | 0 | 5717.7989 | 5717.7989 | -5717.7989 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6988.4209 | 6988.4209 | 0 | 8.5 | 0 | 1164.7368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6848.6525 | 1369.7305 | 13.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 15:00 | 6 | 7 | 15 | 158 | 3783 | 69.08 | 0 | 6874.8269 | 6874.8269 | -6874.8269 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8402.5662 | 8402.5662 | 0 | 8.5 | 0 | 1400.4277 | 30% | 1 | 56.02% | 0% | 0% | 0% | 21.4922 | 0 | 0 | 0 | 21.4922 | 0 | 8234.5148 | 1646.903 | 16.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.7667
2007-06-07 16:00 | 6 | 7 | 16 | 158 | 3784 | 69.98 | 0 | 6670.3916 | 6670.3916 | -6670.3916 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8152.7009 | 8152.7009 | 0 | 8.5 | 0 | 1358.7835 | 30% | 1 | 54.35% | 0% | 0% | 0% | 20.0506 | 0 | 0 | 0 | 20.0506 | 0 | 7989.6469 | 1597.9294 | 15.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.3251
2007-06-07 17:00 | 6 | 7 | 17 | 158 | 3785 | 69.98 | 0 | 6212.0217 | 6212.0217 | -6212.0217 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7592.4709 | 7592.4709 | 0 | 8.5 | 0 | 1265.4118 | 30% | 1 | 50.62% | 0% | 0% | 0% | 17.0221 | 0 | 0 | 0 | 17.0221 | 0 | 7440.6215 | 1488.1243 | 14.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2967
2007-06-07 18:00 | 6 | 7 | 18 | 158 | 3786 | 66.92 | 0 | 3812.9952 | 3812.9952 | -3812.9952 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4660.3274 | 4660.3274 | 0 | 8.5 | 0 | 776.7212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4567.1209 | 913.4242 | 9.134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 19:00 | 6 | 7 | 19 | 158 | 3787 | 64.94 | 0 | 2497.0024 | 2497.0024 | -2497.0024 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3051.8918 | 3051.8918 | 0 | 8.5 | 0 | 508.6486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2990.8539 | 598.1708 | 5.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 20:00 | 6 | 7 | 20 | 158 | 3788 | 64.94 | 0 | 1115.9672 | 1115.9672 | -1115.9672 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1363.9599 | 1363.9599 | 0 | 8.5 | 0 | 227.3266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1336.6807 | 267.3361 | 2.673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 21:00 | 6 | 7 | 21 | 158 | 3789 | 60.08 | 0 | 393.0478 | 393.0478 | -393.0478 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 480.3917 | 480.3917 | 0 | 8.5 | 0 | 80.0653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 470.7839 | 94.1568 | 0.9416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 22:00 | 6 | 7 | 22 | 158 | 3790 | 57.92 | 0 | 13.5534 | 13.5534 | -13.5534 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16.5652 | 16.5652 | 0 | 8.5 | 0 | 2.7609 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 16.2339 | 3.2468 | 0.03247% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-07 23:00 | 6 | 7 | 23 | 158 | 3791 | 57.92 | 0 | 0.13246 | 0.13246 | -0.13246 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.16189 | 0.16189 | 0 | 8.5 | 0 | 0.026982 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.15866 | 0.031731 | 0.0003173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 | 6 | 8 | 0 | 159 | 3792 | 53.96 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-08 01:00 | 6 | 8 | 1 | 159 | 3793 | 53.96 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-08 02:00 | 6 | 8 | 2 | 159 | 3794 | 53.96 | 0.82582 | 0 | 0 | 0.82582 | Heating | 0.72866 | 8.5 | 0.72866 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.14573 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.74353 | 0 | 0.14871 | 0.001487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 03:00 | 6 | 8 | 3 | 159 | 3795 | 50 | 1.9674 | 0 | 0 | 1.9674 | Heating | 1.736 | 8.5 | 1.736 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.34719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.7714 | 0 | 0.35428 | 0.003543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 04:00 | 6 | 8 | 4 | 159 | 3796 | 51.08 | 2.4657 | 0 | 0 | 2.4657 | Heating | 2.1756 | 8.5 | 2.1756 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.43512 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.22 | 0 | 0.444 | 0.00444% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 05:00 | 6 | 8 | 5 | 159 | 3797 | 51.08 | 1.8108 | 0 | 0 | 1.8108 | Heating | 1.5977 | 8.5 | 1.5977 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.31955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.6304 | 0 | 0.32607 | 0.003261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 06:00 | 6 | 8 | 6 | 159 | 3798 | 53.06 | 695.8636 | 354.5524 | 354.5524 | 341.3112 | Heating | 301.157 | 8.5 | 301.157 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.2314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 307.303 | 0 | 61.4606 | 0.6146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 07:00 | 6 | 8 | 7 | 159 | 3799 | 55.94 | 282.7307 | 155.7034 | 155.7034 | 127.0273 | Heating | 112.0829 | 8.5 | 112.0829 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.4166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 114.3703 | 0 | 22.8741 | 0.2287% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 08:00 | 6 | 8 | 8 | 159 | 3800 | 55.94 | 1.8721 | 579.7266 | 579.7266 | -577.8545 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 708.5547 | 708.5547 | 0 | 8.5 | 0 | 118.0925 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 694.3836 | 138.8767 | 1.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 09:00 | 6 | 8 | 9 | 159 | 3801 | 62.06 | 0 | 906.8741 | 906.8741 | -906.8741 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1108.4017 | 1108.4017 | 0 | 8.5 | 0 | 184.7336 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1086.2337 | 217.2467 | 2.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 10:00 | 6 | 8 | 10 | 159 | 3802 | 64.04 | 0 | 2186.1841 | 2186.1841 | -2186.1841 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2672.0028 | 2672.0028 | 0 | 8.5 | 0 | 445.3338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2618.5627 | 523.7125 | 5.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 11:00 | 6 | 8 | 11 | 159 | 3803 | 64.04 | 0 | 4440.7297 | 4440.7297 | -4440.7297 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5427.5586 | 5427.5586 | 0 | 8.5 | 0 | 904.5931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5319.0074 | 1063.8015 | 10.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 12:00 | 6 | 8 | 12 | 159 | 3804 | 64.04 | 0 | 6460.1237 | 6460.1237 | -6460.1237 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7895.7068 | 7895.7068 | 0 | 8.5 | 0 | 1315.9511 | 30% | 1 | 52.64% | 0% | 0% | 0% | 18.6266 | 0 | 0 | 0 | 18.6266 | 0 | 7737.7926 | 1547.5585 | 15.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.9011
2007-06-08 13:00 | 6 | 8 | 13 | 159 | 3805 | 64.04 | 0 | 7010.334 | 7010.334 | -7010.334 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8568.186 | 8568.186 | 0 | 8.5 | 0 | 1428.031 | 30% | 1 | 57.12% | 0% | 0% | 0% | 22.479 | 0 | 0 | 0 | 22.479 | 0 | 8396.8222 | 1679.3644 | 16.79% | 1 | 33.59% | 0% | 0% | 3.3137 | 0 | 0 | 3.3137 | 25.7927
2007-06-08 14:00 | 6 | 8 | 14 | 159 | 3806 | 64.04 | 0 | 7571.7238 | 7571.7238 | -7571.7238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9254.3291 | 9254.3291 | 0 | 8.5 | 0 | 1542.3882 | 30.85% | 1 | 61.7% | 0% | 0% | 0% | 26.8365 | 0 | 0 | 0 | 26.8365 | 0 | 9069.2425 | 1813.8485 | 18.14% | 1 | 36.28% | 0% | 0% | 3.9561 | 0 | 0 | 3.9561 | 30.7926
2007-06-08 15:00 | 6 | 8 | 15 | 159 | 3807 | 62.6 | 0 | 8160.748 | 8160.748 | -8160.748 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9974.2476 | 9974.2476 | 0 | 8.5 | 0 | 1662.3746 | 33.25% | 1 | 66.49% | 0% | 0% | 0% | 31.8829 | 0 | 0 | 0 | 31.8829 | 0 | 9774.7626 | 1954.9525 | 19.55% | 1 | 39.1% | 0% | 0% | 4.7 | 0 | 0 | 4.7 | 36.5828
2007-06-08 16:00 | 6 | 8 | 16 | 159 | 3808 | 68 | 0 | 7460.9782 | 7460.9782 | -7460.9782 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9118.9734 | 9118.9734 | 0 | 8.5 | 0 | 1519.8289 | 30.4% | 1 | 60.79% | 0% | 0% | 0% | 25.9423 | 0 | 0 | 0 | 25.9423 | 0 | 8936.5939 | 1787.3188 | 17.87% | 1 | 35.75% | 0% | 0% | 3.8243 | 0 | 0 | 3.8243 | 29.7666
2007-06-08 17:00 | 6 | 8 | 17 | 159 | 3809 | 68 | 0 | 6177.921 | 6177.921 | -6177.921 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7550.7923 | 7550.7923 | 0 | 8.5 | 0 | 1258.4654 | 30% | 1 | 50.34% | 0% | 0% | 0% | 16.808 | 0 | 0 | 0 | 16.808 | 0 | 7399.7764 | 1479.9553 | 14.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.0825
2007-06-08 18:00 | 6 | 8 | 18 | 159 | 3810 | 66.92 | 0 | 3345.6705 | 3345.6705 | -3345.6705 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4089.1529 | 4089.1529 | 0 | 8.5 | 0 | 681.5255 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4007.3698 | 801.474 | 8.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 19:00 | 6 | 8 | 19 | 159 | 3811 | 62.96 | 0 | 2031.7648 | 2031.7648 | -2031.7648 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2483.2681 | 2483.2681 | 0 | 8.5 | 0 | 413.878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2433.6027 | 486.7205 | 4.867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 20:00 | 6 | 8 | 20 | 159 | 3812 | 62.96 | 0 | 1070.3456 | 1070.3456 | -1070.3456 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1308.2002 | 1308.2002 | 0 | 8.5 | 0 | 218.0334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1282.0362 | 256.4072 | 2.564% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 21:00 | 6 | 8 | 21 | 159 | 3813 | 57.92 | 0 | 361.8745 | 361.8745 | -361.8745 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 442.2911 | 442.2911 | 0 | 8.5 | 0 | 73.7152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 433.4453 | 86.6891 | 0.8669% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 22:00 | 6 | 8 | 22 | 159 | 3814 | 55.94 | 0 | 261.4436 | 261.4436 | -261.4436 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 319.5421 | 319.5421 | 0 | 8.5 | 0 | 53.257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 313.1513 | 62.6303 | 0.6263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-08 23:00 | 6 | 8 | 23 | 159 | 3815 | 55.94 | 0 | 158.6694 | 158.6694 | -158.6694 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 193.9293 | 193.9293 | 0 | 8.5 | 0 | 32.3215 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 190.0507 | 38.0101 | 0.3801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 | 6 | 9 | 0 | 160 | 3816 | 53.06 | 0 | 43.67 | 43.67 | -43.67 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 53.3744 | 53.3744 | 0 | 8.5 | 0 | 8.8957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 52.307 | 10.4614 | 0.1046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 01:00 | 6 | 9 | 1 | 160 | 3817 | 50 | 0 | 2.0751 | 2.0751 | -2.0751 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.5362 | 2.5362 | 0 | 8.5 | 0 | 0.4227 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.4854 | 0.49709 | 0.004971% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 02:00 | 6 | 9 | 2 | 160 | 3818 | 50 | 1.4489 | 0 | 0 | 1.4489 | Heating | 1.2784 | 8.5 | 1.2784 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.25568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.3045 | 0 | 0.2609 | 0.002609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 03:00 | 6 | 9 | 3 | 160 | 3819 | 48.02 | 8.6145 | 0 | 0 | 8.6145 | Heating | 7.601 | 8.5 | 7.601 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.7561 | 0 | 1.5512 | 0.01551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 04:00 | 6 | 9 | 4 | 160 | 3820 | 44.96 | 19.1711 | 0 | 0 | 19.1711 | Heating | 16.9157 | 8.5 | 16.9157 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.3831 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.2609 | 0 | 3.4522 | 0.03452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 05:00 | 6 | 9 | 5 | 160 | 3821 | 44.96 | 27.4512 | 0 | 0 | 27.4512 | Heating | 24.2217 | 8.5 | 24.2217 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.8443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.716 | 0 | 4.9432 | 0.04943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 06:00 | 6 | 9 | 6 | 160 | 3822 | 48.92 | 22.9623 | 0 | 0 | 22.9623 | Heating | 20.2609 | 8.5 | 20.2609 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.0522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.6743 | 0 | 4.1349 | 0.04135% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 07:00 | 6 | 9 | 7 | 160 | 3823 | 51.08 | 11.5865 | 0 | 0 | 11.5865 | Heating | 10.2234 | 8.5 | 10.2234 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.432 | 0 | 2.0864 | 0.02086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 08:00 | 6 | 9 | 8 | 160 | 3824 | 51.08 | 1603.4762 | 0 | 0 | 1603.4762 | Heating | 1414.8319 | 8.5 | 1414.8319 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 282.9664 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1443.706 | 0 | 288.7412 | 2.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 09:00 | 6 | 9 | 9 | 160 | 3825 | 57.92 | 701.1421 | 0 | 0 | 701.1421 | Heating | 618.6548 | 8.5 | 618.6548 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 631.2804 | 0 | 126.2561 | 1.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 10:00 | 6 | 9 | 10 | 160 | 3826 | 57.92 | 84.0908 | 0 | 0 | 84.0908 | Heating | 74.1978 | 8.5 | 74.1978 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.8396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 75.712 | 0 | 15.1424 | 0.1514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 11:00 | 6 | 9 | 11 | 160 | 3827 | 57.92 | 0 | 0.40709 | 0.40709 | -0.40709 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.49756 | 0.49756 | 0 | 8.5 | 0 | 0.082927 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.48761 | 0.097522 | 0.0009752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 12:00 | 6 | 9 | 12 | 160 | 3828 | 57.02 | 0 | 143.3594 | 143.3594 | -143.3594 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 175.217 | 175.217 | 0 | 8.5 | 0 | 29.2028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 171.7127 | 34.3425 | 0.3434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 13:00 | 6 | 9 | 13 | 160 | 3829 | 55.94 | 0 | 592.6223 | 592.6223 | -592.6223 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 724.3162 | 724.3162 | 0 | 8.5 | 0 | 120.7194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 709.8299 | 141.966 | 1.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 14:00 | 6 | 9 | 14 | 160 | 3830 | 55.94 | 0 | 1123.9598 | 1123.9598 | -1123.9598 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1373.7287 | 1373.7287 | 0 | 8.5 | 0 | 228.9548 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1346.2541 | 269.2508 | 2.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 15:00 | 6 | 9 | 15 | 160 | 3831 | 55.04 | 0 | 1469.398 | 1469.398 | -1469.398 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1795.9308 | 1795.9308 | 0 | 8.5 | 0 | 299.3218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1760.0122 | 352.0024 | 3.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 16:00 | 6 | 9 | 16 | 160 | 3832 | 55.04 | 0 | 1668.2046 | 1668.2046 | -1668.2046 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2038.9168 | 2038.9168 | 0 | 8.5 | 0 | 339.8195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1998.1384 | 399.6277 | 3.996% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 17:00 | 6 | 9 | 17 | 160 | 3833 | 55.04 | 0 | 1183.1293 | 1183.1293 | -1183.1293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1446.0469 | 1446.0469 | 0 | 8.5 | 0 | 241.0078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1417.126 | 283.4252 | 2.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 18:00 | 6 | 9 | 18 | 160 | 3834 | 55.04 | 0 | 717.8941 | 717.8941 | -717.8941 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 877.4261 | 877.4261 | 0 | 8.5 | 0 | 146.2377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 859.8776 | 171.9755 | 1.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 19:00 | 6 | 9 | 19 | 160 | 3835 | 53.6 | 0 | 442.4052 | 442.4052 | -442.4052 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 540.7175 | 540.7175 | 0 | 8.5 | 0 | 90.1196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 529.9032 | 105.9806 | 1.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 20:00 | 6 | 9 | 20 | 160 | 3836 | 53.96 | 0 | 190.8018 | 190.8018 | -190.8018 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 233.2022 | 233.2022 | 0 | 8.5 | 0 | 38.867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 228.5381 | 45.7076 | 0.4571% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 21:00 | 6 | 9 | 21 | 160 | 3837 | 53.6 | 0 | 71.3015 | 71.3015 | -71.3015 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 87.1463 | 87.1463 | 0 | 8.5 | 0 | 14.5244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 85.4033 | 17.0807 | 0.1708% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 22:00 | 6 | 9 | 22 | 160 | 3838 | 55.04 | 0 | 9.8532 | 9.8532 | -9.8532 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12.0428 | 12.0428 | 0 | 8.5 | 0 | 2.0071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 11.8019 | 2.3604 | 0.0236% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-09 23:00 | 6 | 9 | 23 | 160 | 3839 | 55.04 | 3.509 | 0 | 0 | 3.509 | Heating | 3.0962 | 8.5 | 3.0962 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.61924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.1594 | 0 | 0.63188 | 0.006319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 | 6 | 10 | 0 | 161 | 3840 | 55.94 | 13.4432 | 0 | 0 | 13.4432 | Heating | 11.8617 | 8.5 | 11.8617 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.3723 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.1038 | 0 | 2.4208 | 0.02421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 01:00 | 6 | 10 | 1 | 161 | 3841 | 55.94 | 24.0825 | 0 | 0 | 24.0825 | Heating | 21.2493 | 8.5 | 21.2493 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.2499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.6829 | 0 | 4.3366 | 0.04337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 02:00 | 6 | 10 | 2 | 161 | 3842 | 55.94 | 37.4288 | 0 | 0 | 37.4288 | Heating | 33.0254 | 8.5 | 33.0254 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.6051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 33.6994 | 0 | 6.7399 | 0.0674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 03:00 | 6 | 10 | 3 | 161 | 3843 | 55.94 | 81.4999 | 0 | 0 | 81.4999 | Heating | 71.9117 | 8.5 | 71.9117 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.3823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 73.3792 | 0 | 14.6758 | 0.1468% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 04:00 | 6 | 10 | 4 | 161 | 3844 | 55.4 | 154.1898 | 0 | 0 | 154.1898 | Heating | 136.0498 | 8.5 | 136.0498 | 0 | 5.0667 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.21 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 138.8264 | 0 | 27.7653 | 0.2777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 05:00 | 6 | 10 | 5 | 161 | 3845 | 55.94 | 189.8889 | 0 | 0 | 189.8889 | Heating | 167.549 | 8.5 | 167.549 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.5098 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 170.9684 | 0 | 34.1937 | 0.3419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 06:00 | 6 | 10 | 6 | 161 | 3846 | 57.02 | 3892.928 | 56.2063 | 56.2063 | 3836.7218 | Heating | 3385.3427 | 8.5 | 3385.3427 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 677.0685 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3454.4314 | 0 | 690.8863 | 6.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 07:00 | 6 | 10 | 7 | 161 | 3847 | 57.92 | 1844.4168 | 101.8458 | 101.8458 | 1742.5709 | Heating | 1537.5626 | 8.5 | 1537.5626 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 307.5125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1568.9414 | 0 | 313.7883 | 3.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 08:00 | 6 | 10 | 8 | 161 | 3848 | 57.92 | 642.5273 | 542.0965 | 542.0965 | 100.4308 | Heating | 88.6154 | 8.5 | 88.6154 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.7231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 90.4239 | 0 | 18.0848 | 0.1808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 09:00 | 6 | 10 | 9 | 161 | 3849 | 62.6 | 2.8197 | 1529.3504 | 1529.3504 | -1526.5306 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1869.206 | 1869.206 | 0 | 8.5 | 0 | 311.5343 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1831.8219 | 366.3644 | 3.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 10:00 | 6 | 10 | 10 | 161 | 3850 | 64.94 | 0 | 3021.0696 | 3021.0696 | -3021.0696 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3692.4185 | 3692.4185 | 0 | 8.5 | 0 | 615.4031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3618.5701 | 723.714 | 7.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 11:00 | 6 | 10 | 11 | 161 | 3851 | 64.94 | 0 | 4734.1798 | 4734.1798 | -4734.1798 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5786.2197 | 5786.2197 | 0 | 8.5 | 0 | 964.37 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5670.4953 | 1134.0991 | 11.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 12:00 | 6 | 10 | 12 | 161 | 3852 | 69.8 | 0 | 5872.6108 | 5872.6108 | -5872.6108 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7177.6354 | 7177.6354 | 0 | 8.5 | 0 | 1196.2726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7034.0827 | 1406.8165 | 14.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 13:00 | 6 | 10 | 13 | 161 | 3853 | 66.2 | 0 | 7048.2687 | 7048.2687 | -7048.2687 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8614.5506 | 8614.5506 | 0 | 8.5 | 0 | 1435.7584 | 30% | 1 | 57.43% | 0% | 0% | 0% | 22.7598 | 0 | 0 | 0 | 22.7598 | 0 | 8442.2596 | 1688.4519 | 16.88% | 1 | 33.77% | 0% | 0% | 3.3551 | 0 | 0 | 3.3551 | 26.1149
2007-06-10 14:00 | 6 | 10 | 14 | 161 | 3854 | 64.94 | 0 | 7902.9425 | 7902.9425 | -7902.9425 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9659.152 | 9659.152 | 0 | 8.5 | 0 | 1609.8587 | 32.2% | 1 | 64.39% | 0% | 0% | 0% | 29.6137 | 0 | 0 | 0 | 29.6137 | 0 | 9465.969 | 1893.1938 | 18.93% | 1 | 37.86% | 0% | 0% | 4.3655 | 0 | 0 | 4.3655 | 33.9792
2007-06-10 15:00 | 6 | 10 | 15 | 161 | 3855 | 71.06 | 0 | 8235.27 | 8235.27 | -8235.27 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10065.33 | 10065.33 | 0 | 8.5 | 0 | 1677.555 | 33.55% | 1 | 67.1% | 0% | 0% | 0% | 32.5565 | 0 | 0 | 0 | 32.5565 | 0 | 9864.0234 | 1972.8047 | 19.73% | 1 | 39.46% | 0% | 0% | 4.7993 | 0 | 0 | 4.7993 | 37.3558
2007-06-10 16:00 | 6 | 10 | 16 | 161 | 3856 | 69.98 | 0 | 8106.1801 | 8106.1801 | -8106.1801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9907.5534 | 9907.5534 | 0 | 8.5 | 0 | 1651.2589 | 33.03% | 1 | 66.05% | 0% | 0% | 0% | 31.3947 | 0 | 0 | 0 | 31.3947 | 0 | 9709.4023 | 1941.8805 | 19.42% | 1 | 38.84% | 0% | 0% | 4.628 | 0 | 0 | 4.628 | 36.0227
2007-06-10 17:00 | 6 | 10 | 17 | 161 | 3857 | 69.98 | 0 | 8011.703 | 8011.703 | -8011.703 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9792.0814 | 9792.0814 | 0 | 8.5 | 0 | 1632.0136 | 32.64% | 1 | 65.28% | 0% | 0% | 0% | 30.5595 | 0 | 0 | 0 | 30.5595 | 0 | 9596.2398 | 1919.248 | 19.19% | 1 | 38.38% | 0% | 0% | 4.5049 | 0 | 0 | 4.5049 | 35.0643
2007-06-10 18:00 | 6 | 10 | 18 | 161 | 3858 | 66.02 | 0 | 5573.7643 | 5573.7643 | -5573.7643 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6812.3786 | 6812.3786 | 0 | 8.5 | 0 | 1135.3964 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6676.131 | 1335.2262 | 13.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 19:00 | 6 | 10 | 19 | 161 | 3859 | 64.94 | 0 | 4683.6366 | 4683.6366 | -4683.6366 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5724.4447 | 5724.4447 | 0 | 8.5 | 0 | 954.0741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5609.9558 | 1121.9912 | 11.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 20:00 | 6 | 10 | 20 | 161 | 3860 | 64.94 | 0 | 3352.8639 | 3352.8639 | -3352.8639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4097.9447 | 4097.9447 | 0 | 8.5 | 0 | 682.9908 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4015.9858 | 803.1972 | 8.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 21:00 | 6 | 10 | 21 | 161 | 3861 | 60.08 | 0 | 1620.1582 | 1620.1582 | -1620.1582 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1980.1934 | 1980.1934 | 0 | 8.5 | 0 | 330.0322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1940.5895 | 388.1179 | 3.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 22:00 | 6 | 10 | 22 | 161 | 3862 | 57.92 | 0 | 309.061 | 309.061 | -309.061 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 377.7412 | 377.7412 | 0 | 8.5 | 0 | 62.9569 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 370.1864 | 74.0373 | 0.7404% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-10 23:00 | 6 | 10 | 23 | 161 | 3863 | 57.92 | 0 | 199.0743 | 199.0743 | -199.0743 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 243.3131 | 243.3131 | 0 | 8.5 | 0 | 40.5522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 238.4468 | 47.6894 | 0.4769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 | 6 | 11 | 0 | 162 | 3864 | 57.92 | 0 | 102.6693 | 102.6693 | -102.6693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 125.4846 | 125.4846 | 0 | 8.5 | 0 | 20.9141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 122.9749 | 24.595 | 0.2459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 01:00 | 6 | 11 | 1 | 162 | 3865 | 57.92 | 0 | 59.7659 | 59.7659 | -59.7659 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 73.0472 | 73.0472 | 0 | 8.5 | 0 | 12.1745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 71.5863 | 14.3173 | 0.1432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 02:00 | 6 | 11 | 2 | 162 | 3866 | 57.92 | 0 | 26.9876 | 26.9876 | -26.9876 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 32.9849 | 32.9849 | 0 | 8.5 | 0 | 5.4975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 32.3252 | 6.465 | 0.06465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 03:00 | 6 | 11 | 3 | 162 | 3867 | 53.96 | 0 | 11.6756 | 11.6756 | -11.6756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14.2702 | 14.2702 | 0 | 8.5 | 0 | 2.3784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.9848 | 2.797 | 0.02797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 04:00 | 6 | 11 | 4 | 162 | 3868 | 53.6 | 0 | 5.6222 | 5.6222 | -5.6222 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6.8716 | 6.8716 | 0 | 8.5 | 0 | 1.1453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6.7342 | 1.3468 | 0.01347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 05:00 | 6 | 11 | 5 | 162 | 3869 | 53.96 | 0 | 14.981 | 14.981 | -14.981 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18.3101 | 18.3101 | 0 | 8.5 | 0 | 3.0517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 17.9439 | 3.5888 | 0.03589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 06:00 | 6 | 11 | 6 | 162 | 3870 | 55.94 | 297.8924 | 687.8279 | 687.8279 | -389.9354 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 840.6785 | 840.6785 | 0 | 8.5 | 0 | 140.1131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 823.865 | 164.773 | 1.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 07:00 | 6 | 11 | 7 | 162 | 3871 | 60.08 | 71.6045 | 539.9427 | 539.9427 | -468.3381 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 659.9299 | 659.9299 | 0 | 8.5 | 0 | 109.9883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 646.7313 | 129.3463 | 1.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 08:00 | 6 | 11 | 8 | 162 | 3872 | 60.08 | 0 | 2565.9438 | 2565.9438 | -2565.9438 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3136.1536 | 3136.1536 | 0 | 8.5 | 0 | 522.6923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3073.4305 | 614.6861 | 6.147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 09:00 | 6 | 11 | 9 | 162 | 3873 | 66.02 | 0 | 3014.8986 | 3014.8986 | -3014.8986 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3684.8761 | 3684.8761 | 0 | 8.5 | 0 | 614.146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3611.1785 | 722.2357 | 7.222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 10:00 | 6 | 11 | 10 | 162 | 3874 | 66.92 | 0 | 3273.4315 | 3273.4315 | -3273.4315 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4000.8607 | 4000.8607 | 0 | 8.5 | 0 | 666.8101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3920.8435 | 784.1687 | 7.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 11:00 | 6 | 11 | 11 | 162 | 3875 | 66.92 | 0 | 4151.4423 | 4151.4423 | -4151.4423 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5073.9851 | 5073.9851 | 0 | 8.5 | 0 | 845.6642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4972.5054 | 994.5011 | 9.945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 12:00 | 6 | 11 | 12 | 162 | 3876 | 73.04 | 0 | 4840.9751 | 4840.9751 | -4840.9751 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5916.7473 | 5916.7473 | 0 | 8.5 | 0 | 986.1246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5798.4124 | 1159.6825 | 11.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 13:00 | 6 | 11 | 13 | 162 | 3877 | 71.96 | 0 | 4891.1909 | 4891.1909 | -4891.1909 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5978.1222 | 5978.1222 | 0 | 8.5 | 0 | 996.3537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5858.5598 | 1171.712 | 11.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 14:00 | 6 | 11 | 14 | 162 | 3878 | 71.96 | 0 | 4601.1521 | 4601.1521 | -4601.1521 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5623.6304 | 5623.6304 | 0 | 8.5 | 0 | 937.2717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5511.1578 | 1102.2316 | 11.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 15:00 | 6 | 11 | 15 | 162 | 3879 | 77 | 0 | 3688.4048 | 3688.4048 | -3688.4048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4508.0503 | 4508.0503 | 0 | 8.5 | 0 | 751.3417 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4417.8893 | 883.5779 | 8.836% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 16:00 | 6 | 11 | 16 | 162 | 3880 | 75.02 | 0 | 3492.3929 | 3492.3929 | -3492.3929 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4268.4802 | 4268.4802 | 0 | 8.5 | 0 | 711.4134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4183.1106 | 836.6221 | 8.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 17:00 | 6 | 11 | 17 | 162 | 3881 | 75.02 | 0 | 2864.1543 | 2864.1543 | -2864.1543 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3500.633 | 3500.633 | 0 | 8.5 | 0 | 583.4388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3430.6204 | 686.1241 | 6.861% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 18:00 | 6 | 11 | 18 | 162 | 3882 | 75.02 | 0 | 856.0065 | 856.0065 | -856.0065 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1046.2302 | 1046.2302 | 0 | 8.5 | 0 | 174.3717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1025.3056 | 205.0611 | 2.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 19:00 | 6 | 11 | 19 | 162 | 3883 | 71.96 | 0 | 550.8633 | 550.8633 | -550.8633 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 673.2773 | 673.2773 | 0 | 8.5 | 0 | 112.2129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 659.8118 | 131.9624 | 1.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 20:00 | 6 | 11 | 20 | 162 | 3884 | 71.96 | 0 | 420.8363 | 420.8363 | -420.8363 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 514.3554 | 514.3554 | 0 | 8.5 | 0 | 85.7259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 504.0683 | 100.8137 | 1.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 21:00 | 6 | 11 | 21 | 162 | 3885 | 66.92 | 0 | 349.3101 | 349.3101 | -349.3101 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 426.9346 | 426.9346 | 0 | 8.5 | 0 | 71.1558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 418.3959 | 83.6792 | 0.8368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 22:00 | 6 | 11 | 22 | 162 | 3886 | 66.02 | 0 | 5.7056 | 5.7056 | -5.7056 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6.9735 | 6.9735 | 0 | 8.5 | 0 | 1.1622 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6.834 | 1.3668 | 0.01367% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-11 23:00 | 6 | 11 | 23 | 162 | 3887 | 66.02 | 0.94795 | 0 | 0 | 0.94795 | Heating | 0.83643 | 8.5 | 0.83643 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.16729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.85349 | 0 | 0.1707 | 0.001707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 | 6 | 12 | 0 | 163 | 3888 | 64.04 | 4.7451 | 0 | 0 | 4.7451 | Heating | 4.1868 | 8.5 | 4.1868 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.83736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.2723 | 0 | 0.85445 | 0.008545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 01:00 | 6 | 12 | 1 | 163 | 3889 | 62.06 | 6.8197 | 0 | 0 | 6.8197 | Heating | 6.0174 | 8.5 | 6.0174 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2035 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.1402 | 0 | 1.228 | 0.01228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 02:00 | 6 | 12 | 2 | 163 | 3890 | 62.06 | 10.6317 | 0 | 0 | 10.6317 | Heating | 9.3809 | 8.5 | 9.3809 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.8762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.5724 | 0 | 1.9145 | 0.01914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 03:00 | 6 | 12 | 3 | 163 | 3891 | 60.98 | 15.2149 | 0 | 0 | 15.2149 | Heating | 13.4249 | 8.5 | 13.4249 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.685 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.6989 | 0 | 2.7398 | 0.0274% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 04:00 | 6 | 12 | 4 | 163 | 3892 | 60.98 | 16.9674 | 0 | 0 | 16.9674 | Heating | 14.9712 | 8.5 | 14.9712 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.9942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.2767 | 0 | 3.0553 | 0.03055% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 05:00 | 6 | 12 | 5 | 163 | 3893 | 60.98 | 16.314 | 0 | 0 | 16.314 | Heating | 14.3947 | 8.5 | 14.3947 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.8789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.6885 | 0 | 2.9377 | 0.02938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 06:00 | 6 | 12 | 6 | 163 | 3894 | 60.98 | 1266.6153 | 360.672 | 360.672 | 905.9434 | Heating | 799.3618 | 8.5 | 799.3618 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 159.8724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 815.6753 | 0 | 163.1351 | 1.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 07:00 | 6 | 12 | 7 | 163 | 3895 | 62.6 | 910.7931 | 109.2438 | 109.2438 | 801.5493 | Heating | 707.2494 | 8.5 | 707.2494 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.4499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 721.6831 | 0 | 144.3366 | 1.443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 08:00 | 6 | 12 | 8 | 163 | 3896 | 62.06 | 471.4142 | 954.2057 | 954.2057 | -482.7916 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1166.2515 | 1166.2515 | 0 | 8.5 | 0 | 194.3752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1142.9264 | 228.5853 | 2.286% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 09:00 | 6 | 12 | 9 | 163 | 3897 | 62.06 | 19.2339 | 1202.6746 | 1202.6746 | -1183.4408 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1469.9357 | 1469.9357 | 0 | 8.5 | 0 | 244.9893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1440.5369 | 288.1074 | 2.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 10:00 | 6 | 12 | 10 | 163 | 3898 | 62.6 | 16.8921 | 1337.6342 | 1337.6342 | -1320.7421 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1634.8863 | 1634.8863 | 0 | 8.5 | 0 | 272.481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1602.1885 | 320.4377 | 3.204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 11:00 | 6 | 12 | 11 | 163 | 3899 | 62.06 | 17.5432 | 1356.549 | 1356.549 | -1339.0058 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1658.0043 | 1658.0043 | 0 | 8.5 | 0 | 276.334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1624.8442 | 324.9688 | 3.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 12:00 | 6 | 12 | 12 | 163 | 3900 | 64.4 | 21.7615 | 1312.7699 | 1312.7699 | -1291.0084 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1604.4966 | 1604.4966 | 0 | 8.5 | 0 | 267.4161 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1572.4066 | 314.4813 | 3.145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 13:00 | 6 | 12 | 13 | 163 | 3901 | 64.4 | 24.8253 | 1384.6215 | 1384.6215 | -1359.7962 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1692.3151 | 1692.3151 | 0 | 8.5 | 0 | 282.0525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1658.4688 | 331.6938 | 3.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 14:00 | 6 | 12 | 14 | 163 | 3902 | 64.04 | 23.2171 | 1415.7564 | 1415.7564 | -1392.5393 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1730.369 | 1730.369 | 0 | 8.5 | 0 | 288.3948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1695.7616 | 339.1523 | 3.392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 15:00 | 6 | 12 | 15 | 163 | 3903 | 64.4 | 24.5655 | 1157.5718 | 1157.5718 | -1133.0063 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1414.81 | 1414.81 | 0 | 8.5 | 0 | 235.8017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1386.5138 | 277.3028 | 2.773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 16:00 | 6 | 12 | 16 | 163 | 3904 | 64.04 | 27.7 | 860.4881 | 860.4881 | -832.7881 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1051.7076 | 1051.7076 | 0 | 8.5 | 0 | 175.2846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1030.6735 | 206.1347 | 2.061% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 17:00 | 6 | 12 | 17 | 163 | 3905 | 64.04 | 30.1007 | 658.7091 | 658.7091 | -628.6084 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 805.0889 | 805.0889 | 0 | 8.5 | 0 | 134.1815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 788.9871 | 157.7974 | 1.578% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 18:00 | 6 | 12 | 18 | 163 | 3906 | 64.04 | 28.9333 | 281.3537 | 281.3537 | -252.4204 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 343.8767 | 343.8767 | 0 | 8.5 | 0 | 57.3128 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 336.9992 | 67.3998 | 0.674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 19:00 | 6 | 12 | 19 | 163 | 3907 | 64.04 | 39.7884 | 241.4932 | 241.4932 | -201.7048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 295.1583 | 295.1583 | 0 | 8.5 | 0 | 49.1931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 289.2552 | 57.851 | 0.5785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 20:00 | 6 | 12 | 20 | 163 | 3908 | 64.04 | 140.969 | 138.7299 | 138.7299 | 2.2392 | Heating | 1.9757 | 8.5 | 1.9757 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.39515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.0161 | 0 | 0.40321 | 0.004032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 21:00 | 6 | 12 | 21 | 163 | 3909 | 62.96 | 56.451 | 98.0065 | 98.0065 | -41.5555 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 119.7857 | 119.7857 | 0 | 8.5 | 0 | 19.9643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 117.39 | 23.478 | 0.2348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 22:00 | 6 | 12 | 22 | 163 | 3910 | 62.6 | 95.8024 | 0 | 0 | 95.8024 | Heating | 84.5315 | 8.5 | 84.5315 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.9063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 86.2567 | 0 | 17.2513 | 0.1725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-12 23:00 | 6 | 12 | 23 | 163 | 3911 | 62.96 | 128.4882 | 0 | 0 | 128.4882 | Heating | 113.3719 | 8.5 | 113.3719 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.6744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 115.6856 | 0 | 23.1371 | 0.2314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 | 6 | 13 | 0 | 164 | 3912 | 62.06 | 166.0039 | 0 | 0 | 166.0039 | Heating | 146.474 | 8.5 | 146.474 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.2948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 149.4633 | 0 | 29.8927 | 0.2989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 01:00 | 6 | 13 | 1 | 164 | 3913 | 60.98 | 196.5204 | 0 | 0 | 196.5204 | Heating | 173.4003 | 8.5 | 173.4003 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.6801 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 176.9391 | 0 | 35.3878 | 0.3539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 02:00 | 6 | 13 | 2 | 164 | 3914 | 60.98 | 233.2388 | 0 | 0 | 233.2388 | Heating | 205.799 | 8.5 | 205.799 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.1598 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 209.9989 | 0 | 41.9998 | 0.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 03:00 | 6 | 13 | 3 | 164 | 3915 | 60.8 | 263.909 | 0 | 0 | 263.909 | Heating | 232.8609 | 8.5 | 232.8609 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 46.5722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 237.6132 | 0 | 47.5226 | 0.4752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 04:00 | 6 | 13 | 4 | 164 | 3916 | 60.98 | 279.2894 | 0 | 0 | 279.2894 | Heating | 246.4318 | 8.5 | 246.4318 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.2864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 251.4611 | 0 | 50.2922 | 0.5029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 05:00 | 6 | 13 | 5 | 164 | 3917 | 60.98 | 281.9727 | 0 | 0 | 281.9727 | Heating | 248.7994 | 8.5 | 248.7994 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.7599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 253.877 | 0 | 50.7754 | 0.5078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 06:00 | 6 | 13 | 6 | 164 | 3918 | 60.8 | 3545.4174 | 64.8979 | 64.8979 | 3480.5195 | Heating | 3071.0466 | 8.5 | 3071.0466 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 614.2093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3133.721 | 0 | 626.7442 | 6.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 07:00 | 6 | 13 | 7 | 164 | 3919 | 60.98 | 2310.1982 | 0 | 0 | 2310.1982 | Heating | 2038.4102 | 8.5 | 2038.4102 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 407.682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2080.0104 | 0 | 416.0021 | 4.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 08:00 | 6 | 13 | 8 | 164 | 3920 | 60.98 | 1679.7449 | 42.2828 | 42.2828 | 1637.4621 | Heating | 1444.8195 | 8.5 | 1444.8195 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 288.9639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1474.3056 | 0 | 294.8611 | 2.949% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 09:00 | 6 | 13 | 9 | 164 | 3921 | 62.06 | 796.2753 | 244.3675 | 244.3675 | 551.9078 | Heating | 486.9775 | 8.5 | 486.9775 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 97.3955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 496.9158 | 0 | 99.3832 | 0.9938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 10:00 | 6 | 13 | 10 | 164 | 3922 | 62.6 | 311.5791 | 616.8436 | 616.8436 | -305.2645 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 753.92 | 753.92 | 0 | 8.5 | 0 | 125.6533 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 738.8416 | 147.7683 | 1.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 11:00 | 6 | 13 | 11 | 164 | 3923 | 62.96 | 125.1507 | 795.4855 | 795.4855 | -670.3348 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 972.2601 | 972.2601 | 0 | 8.5 | 0 | 162.0433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 952.8149 | 190.563 | 1.906% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 12:00 | 6 | 13 | 12 | 164 | 3924 | 64.4 | 57.4003 | 1017.0399 | 1017.0399 | -959.6396 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1243.0487 | 1243.0487 | 0 | 8.5 | 0 | 207.1748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1218.1877 | 243.6375 | 2.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 13:00 | 6 | 13 | 13 | 164 | 3925 | 64.04 | 5.9507 | 2184.4785 | 2184.4785 | -2178.5278 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2669.9181 | 2669.9181 | 0 | 8.5 | 0 | 444.9864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2616.5198 | 523.304 | 5.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 14:00 | 6 | 13 | 14 | 164 | 3926 | 64.04 | 5.4811 | 2009.0053 | 2009.0053 | -2003.5243 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2455.451 | 2455.451 | 0 | 8.5 | 0 | 409.2418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2406.3419 | 481.2684 | 4.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 15:00 | 6 | 13 | 15 | 164 | 3927 | 64.94 | 4.9054 | 2077.2096 | 2077.2096 | -2072.3042 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2538.8118 | 2538.8118 | 0 | 8.5 | 0 | 423.1353 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2488.0355 | 497.6071 | 4.976% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 16:00 | 6 | 13 | 16 | 164 | 3928 | 64.4 | 0 | 2364.1971 | 2364.1971 | -2364.1971 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2889.5742 | 2889.5742 | 0 | 8.5 | 0 | 481.5957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2831.7827 | 566.3565 | 5.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 17:00 | 6 | 13 | 17 | 164 | 3929 | 64.94 | 0 | 1774.1142 | 1774.1142 | -1774.1142 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2168.3617 | 2168.3617 | 0 | 8.5 | 0 | 361.3936 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2124.9945 | 424.9989 | 4.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 18:00 | 6 | 13 | 18 | 164 | 3930 | 64.4 | 0 | 413.5432 | 413.5432 | -413.5432 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 505.4417 | 505.4417 | 0 | 8.5 | 0 | 84.2403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 495.3329 | 99.0666 | 0.9907% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 19:00 | 6 | 13 | 19 | 164 | 3931 | 64.4 | 0 | 361.2318 | 361.2318 | -361.2318 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 441.5055 | 441.5055 | 0 | 8.5 | 0 | 73.5843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 432.6754 | 86.5351 | 0.8654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 20:00 | 6 | 13 | 20 | 164 | 3932 | 64.94 | 0.71032 | 249.6156 | 249.6156 | -248.9053 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 305.0858 | 305.0858 | 0 | 8.5 | 0 | 50.8476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 298.984 | 59.7968 | 0.598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 21:00 | 6 | 13 | 21 | 164 | 3933 | 64.04 | 7.9438 | 202.8261 | 202.8261 | -194.8824 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 247.8986 | 247.8986 | 0 | 8.5 | 0 | 41.3164 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 242.9406 | 48.5881 | 0.4859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 22:00 | 6 | 13 | 22 | 164 | 3934 | 64.04 | 39.4196 | 0 | 0 | 39.4196 | Heating | 34.782 | 8.5 | 34.782 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.9564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.4918 | 0 | 7.0984 | 0.07098% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-13 23:00 | 6 | 13 | 23 | 164 | 3935 | 64.04 | 101.5165 | 0 | 0 | 101.5165 | Heating | 89.5733 | 8.5 | 89.5733 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.9147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 91.4014 | 0 | 18.2803 | 0.1828% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 | 6 | 14 | 0 | 165 | 3936 | 64.04 | 138.0835 | 0 | 0 | 138.0835 | Heating | 121.8384 | 8.5 | 121.8384 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.3677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 124.3249 | 0 | 24.865 | 0.2486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 01:00 | 6 | 14 | 1 | 165 | 3937 | 62.96 | 185.8563 | 0 | 0 | 185.8563 | Heating | 163.9908 | 8.5 | 163.9908 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.7982 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 167.3376 | 0 | 33.4675 | 0.3347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 02:00 | 6 | 14 | 2 | 165 | 3938 | 62.96 | 245.0258 | 0 | 0 | 245.0258 | Heating | 216.1993 | 8.5 | 216.1993 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.2399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 220.6115 | 0 | 44.1223 | 0.4412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 03:00 | 6 | 14 | 3 | 165 | 3939 | 60.8 | 309.0816 | 0 | 0 | 309.0816 | Heating | 272.7191 | 8.5 | 272.7191 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.5438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 278.2848 | 0 | 55.657 | 0.5566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 04:00 | 6 | 14 | 4 | 165 | 3940 | 60.8 | 324.8318 | 0 | 0 | 324.8318 | Heating | 286.6163 | 8.5 | 286.6163 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.3233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 292.4656 | 0 | 58.4931 | 0.5849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 05:00 | 6 | 14 | 5 | 165 | 3941 | 60.08 | 268.8484 | 0 | 0 | 268.8484 | Heating | 237.2191 | 8.5 | 237.2191 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.4438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 242.0603 | 0 | 48.4121 | 0.4841% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 06:00 | 6 | 14 | 6 | 165 | 3942 | 60.8 | 2890.6143 | 87.9493 | 87.9493 | 2802.6651 | Heating | 2472.9398 | 8.5 | 2472.9398 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2523.4079 | 0 | 504.6816 | 5.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 07:00 | 6 | 14 | 7 | 165 | 3943 | 60.8 | 1399.4434 | 100.8293 | 100.8293 | 1298.6141 | Heating | 1145.836 | 8.5 | 1145.836 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.1672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1169.2204 | 0 | 233.8441 | 2.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 08:00 | 6 | 14 | 8 | 165 | 3944 | 62.06 | 512.0743 | 749.9305 | 749.9305 | -237.8563 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 916.5818 | 916.5818 | 0 | 8.5 | 0 | 152.7636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 898.2501 | 179.65 | 1.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 09:00 | 6 | 14 | 9 | 165 | 3945 | 69.08 | 16.4342 | 1516.7466 | 1516.7466 | -1500.3124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1853.8014 | 1853.8014 | 0 | 8.5 | 0 | 308.9669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1816.7253 | 363.3451 | 3.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 10:00 | 6 | 14 | 10 | 165 | 3946 | 69.08 | 1.7691 | 2494.093 | 2494.093 | -2492.3239 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3048.3359 | 3048.3359 | 0 | 8.5 | 0 | 508.056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2987.3692 | 597.4738 | 5.975% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 11:00 | 6 | 14 | 11 | 165 | 3947 | 69.08 | 0 | 3957.4735 | 3957.4735 | -3957.4735 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4836.9121 | 4836.9121 | 0 | 8.5 | 0 | 806.152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4740.1739 | 948.0348 | 9.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 12:00 | 6 | 14 | 12 | 165 | 3948 | 69.98 | 0 | 5268.8935 | 5268.8935 | -5268.8935 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6439.7588 | 6439.7588 | 0 | 8.5 | 0 | 1073.2931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6310.9636 | 1262.1927 | 12.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 13:00 | 6 | 14 | 13 | 165 | 3949 | 69.8 | 0 | 6592.2606 | 6592.2606 | -6592.2606 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8057.2074 | 8057.2074 | 0 | 8.5 | 0 | 1342.8679 | 30% | 1 | 53.71% | 0% | 0% | 0% | 19.5145 | 0 | 0 | 0 | 19.5145 | 0 | 7896.0632 | 1579.2126 | 15.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.7891
2007-06-14 14:00 | 6 | 14 | 14 | 165 | 3950 | 69.08 | 0 | 7389.3456 | 7389.3456 | -7389.3456 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9031.4225 | 9031.4225 | 0 | 8.5 | 0 | 1505.2371 | 30.1% | 1 | 60.21% | 0% | 0% | 0% | 25.373 | 0 | 0 | 0 | 25.373 | 0 | 8850.794 | 1770.1588 | 17.7% | 1 | 35.4% | 0% | 0% | 3.7403 | 0 | 0 | 3.7403 | 29.1134
2007-06-14 15:00 | 6 | 14 | 15 | 165 | 3951 | 71.96 | 0 | 7720.4653 | 7720.4653 | -7720.4653 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9436.1242 | 9436.1242 | 0 | 8.5 | 0 | 1572.6874 | 31.45% | 1 | 62.91% | 0% | 0% | 0% | 28.0646 | 0 | 0 | 0 | 28.0646 | 0 | 9247.4017 | 1849.4803 | 18.49% | 1 | 36.99% | 0% | 0% | 4.1371 | 0 | 0 | 4.1371 | 32.2017
2007-06-14 16:00 | 6 | 14 | 16 | 165 | 3952 | 75.02 | 0 | 7841.2754 | 7841.2754 | -7841.2754 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9583.781 | 9583.781 | 0 | 8.5 | 0 | 1597.2968 | 31.95% | 1 | 63.89% | 0% | 0% | 0% | 29.0849 | 0 | 0 | 0 | 29.0849 | 0 | 9392.1054 | 1878.4211 | 18.78% | 1 | 37.57% | 0% | 0% | 4.2875 | 0 | 0 | 4.2875 | 33.3724
2007-06-14 17:00 | 6 | 14 | 17 | 165 | 3953 | 75.02 | 0 | 7658.6477 | 7658.6477 | -7658.6477 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9360.5694 | 9360.5694 | 0 | 8.5 | 0 | 1560.0949 | 31.2% | 1 | 62.4% | 0% | 0% | 0% | 27.5504 | 0 | 0 | 0 | 27.5504 | 0 | 9173.358 | 1834.6716 | 18.35% | 1 | 36.69% | 0% | 0% | 4.0613 | 0 | 0 | 4.0613 | 31.6117
2007-06-14 18:00 | 6 | 14 | 18 | 165 | 3954 | 75.02 | 0 | 5142.0229 | 5142.0229 | -5142.0229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6284.6946 | 6284.6946 | 0 | 8.5 | 0 | 1047.4491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6159.0007 | 1231.8001 | 12.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 19:00 | 6 | 14 | 19 | 165 | 3955 | 68 | 0 | 4435.8587 | 4435.8587 | -4435.8587 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5421.6051 | 5421.6051 | 0 | 8.5 | 0 | 903.6009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5313.173 | 1062.6346 | 10.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 20:00 | 6 | 14 | 20 | 165 | 3956 | 66.02 | 0 | 2623.0303 | 2623.0303 | -2623.0303 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3205.9259 | 3205.9259 | 0 | 8.5 | 0 | 534.321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3141.8074 | 628.3615 | 6.284% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 21:00 | 6 | 14 | 21 | 165 | 3957 | 62.6 | 0 | 914.7421 | 914.7421 | -914.7421 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1118.0181 | 1118.0181 | 0 | 8.5 | 0 | 186.3363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1095.6577 | 219.1315 | 2.191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 22:00 | 6 | 14 | 22 | 165 | 3958 | 60.8 | 0 | 20.7224 | 20.7224 | -20.7224 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 25.3274 | 25.3274 | 0 | 8.5 | 0 | 4.2212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 24.8209 | 4.9642 | 0.04964% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-14 23:00 | 6 | 14 | 23 | 165 | 3959 | 60.08 | 2.6595 | 0 | 0 | 2.6595 | Heating | 2.3466 | 8.5 | 2.3466 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.46933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.3945 | 0 | 0.4789 | 0.004789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 | 6 | 15 | 0 | 166 | 3960 | 57.02 | 21.0308 | 0 | 0 | 21.0308 | Heating | 18.5566 | 8.5 | 18.5566 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.7113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.9353 | 0 | 3.7871 | 0.03787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 01:00 | 6 | 15 | 1 | 166 | 3961 | 53.96 | 36.2583 | 0 | 0 | 36.2583 | Heating | 31.9926 | 8.5 | 31.9926 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.3985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 32.6455 | 0 | 6.5291 | 0.06529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 02:00 | 6 | 15 | 2 | 166 | 3962 | 53.96 | 49.1436 | 0 | 0 | 49.1436 | Heating | 43.362 | 8.5 | 43.362 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.6724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.2469 | 0 | 8.8494 | 0.08849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 03:00 | 6 | 15 | 3 | 166 | 3963 | 51.08 | 53.6896 | 0 | 0 | 53.6896 | Heating | 47.3732 | 8.5 | 47.3732 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.4746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 48.34 | 0 | 9.668 | 0.09668% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 04:00 | 6 | 15 | 4 | 166 | 3964 | 50 | 64.5359 | 0 | 0 | 64.5359 | Heating | 56.9434 | 8.5 | 56.9434 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.3887 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 58.1055 | 0 | 11.6211 | 0.1162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 05:00 | 6 | 15 | 5 | 166 | 3965 | 50 | 77.6335 | 0 | 0 | 77.6335 | Heating | 68.5002 | 8.5 | 68.5002 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.7 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 69.8981 | 0 | 13.9796 | 0.1398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 06:00 | 6 | 15 | 6 | 166 | 3966 | 55.04 | 2297.1505 | 120.0368 | 120.0368 | 2177.1137 | Heating | 1920.9827 | 8.5 | 1920.9827 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.1965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1960.1864 | 0 | 392.0373 | 3.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 07:00 | 6 | 15 | 7 | 166 | 3967 | 59 | 1134.0969 | 47.0938 | 47.0938 | 1087.0031 | Heating | 959.1204 | 8.5 | 959.1204 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.8241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 978.6943 | 0 | 195.7389 | 1.957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 08:00 | 6 | 15 | 8 | 166 | 3968 | 59 | 314.9352 | 224.2821 | 224.2821 | 90.6531 | Heating | 79.988 | 8.5 | 79.988 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.9976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 81.6204 | 0 | 16.3241 | 0.1632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 09:00 | 6 | 15 | 9 | 166 | 3969 | 64.94 | 0 | 1010.1539 | 1010.1539 | -1010.1539 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1234.6325 | 1234.6325 | 0 | 8.5 | 0 | 205.7721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1209.9399 | 241.988 | 2.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 10:00 | 6 | 15 | 10 | 166 | 3970 | 69.08 | 0 | 1847.0774 | 1847.0774 | -1847.0774 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2257.5391 | 2257.5391 | 0 | 8.5 | 0 | 376.2565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2212.3883 | 442.4777 | 4.425% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 11:00 | 6 | 15 | 11 | 166 | 3971 | 69.08 | 0 | 3412.868 | 3412.868 | -3412.868 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4171.2831 | 4171.2831 | 0 | 8.5 | 0 | 695.2139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4087.8575 | 817.5715 | 8.176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 12:00 | 6 | 15 | 12 | 166 | 3972 | 71.96 | 0 | 4471.4206 | 4471.4206 | -4471.4206 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5465.0697 | 5465.0697 | 0 | 8.5 | 0 | 910.8449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5355.7683 | 1071.1537 | 10.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 13:00 | 6 | 15 | 13 | 166 | 3973 | 73.94 | 0 | 5015.2131 | 5015.2131 | -5015.2131 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6129.7049 | 6129.7049 | 0 | 8.5 | 0 | 1021.6175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6007.1108 | 1201.4222 | 12.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 14:00 | 6 | 15 | 14 | 166 | 3974 | 73.94 | 0 | 5537.3158 | 5537.3158 | -5537.3158 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6767.8305 | 6767.8305 | 0 | 8.5 | 0 | 1127.9717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6632.4739 | 1326.4948 | 13.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 15:00 | 6 | 15 | 15 | 166 | 3975 | 75.92 | 0 | 6237.6927 | 6237.6927 | -6237.6927 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7623.8466 | 7623.8466 | 0 | 8.5 | 0 | 1270.6411 | 30% | 1 | 50.83% | 0% | 0% | 0% | 17.1844 | 0 | 0 | 0 | 17.1844 | 0 | 7471.3697 | 1494.2739 | 14.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.4589
2007-06-15 16:00 | 6 | 15 | 16 | 166 | 3976 | 75.92 | 0 | 6947.8511 | 6947.8511 | -6947.8511 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8491.818 | 8491.818 | 0 | 8.5 | 0 | 1415.303 | 30% | 1 | 56.61% | 0% | 0% | 0% | 22.0209 | 0 | 0 | 0 | 22.0209 | 0 | 8321.9816 | 1664.3963 | 16.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.2954
2007-06-15 17:00 | 6 | 15 | 17 | 166 | 3977 | 75.92 | 0 | 7217.0884 | 7217.0884 | -7217.0884 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8820.8859 | 8820.8859 | 0 | 8.5 | 0 | 1470.1476 | 30% | 1 | 58.81% | 0% | 0% | 0% | 24.0332 | 0 | 0 | 0 | 24.0332 | 0 | 8644.4682 | 1728.8936 | 17.29% | 1 | 34.58% | 0% | 0% | 3.5428 | 0 | 0 | 3.5428 | 27.576
2007-06-15 18:00 | 6 | 15 | 18 | 166 | 3978 | 73.94 | 0 | 5184.4735 | 5184.4735 | -5184.4735 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6336.5787 | 6336.5787 | 0 | 8.5 | 0 | 1056.0964 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6209.8471 | 1241.9694 | 12.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 19:00 | 6 | 15 | 19 | 166 | 3979 | 71.96 | 0 | 4520.239 | 4520.239 | -4520.239 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5524.7366 | 5524.7366 | 0 | 8.5 | 0 | 920.7894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5414.2419 | 1082.8484 | 10.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 20:00 | 6 | 15 | 20 | 166 | 3980 | 71.96 | 0 | 3508.4917 | 3508.4917 | -3508.4917 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4288.1566 | 4288.1566 | 0 | 8.5 | 0 | 714.6928 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4202.3934 | 840.4787 | 8.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 21:00 | 6 | 15 | 21 | 166 | 3981 | 64.04 | 0 | 1991.6956 | 1991.6956 | -1991.6956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2434.2947 | 2434.2947 | 0 | 8.5 | 0 | 405.7158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2385.6088 | 477.1218 | 4.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 22:00 | 6 | 15 | 22 | 166 | 3982 | 60.98 | 0 | 877.9363 | 877.9363 | -877.9363 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1073.0332 | 1073.0332 | 0 | 8.5 | 0 | 178.8389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1051.5726 | 210.3145 | 2.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-15 23:00 | 6 | 15 | 23 | 166 | 3983 | 60.98 | 0 | 803.5361 | 803.5361 | -803.5361 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 982.0997 | 982.0997 | 0 | 8.5 | 0 | 163.6833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 962.4577 | 192.4915 | 1.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 | 6 | 16 | 0 | 167 | 3984 | 57.92 | 0 | 670.8181 | 670.8181 | -670.8181 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 819.8888 | 819.8888 | 0 | 8.5 | 0 | 136.6481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 803.4911 | 160.6982 | 1.607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 01:00 | 6 | 16 | 1 | 167 | 3985 | 57.02 | 0 | 570.2737 | 570.2737 | -570.2737 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 697.0012 | 697.0012 | 0 | 8.5 | 0 | 116.1669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 683.0612 | 136.6122 | 1.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 02:00 | 6 | 16 | 2 | 167 | 3986 | 57.02 | 0 | 299.6803 | 299.6803 | -299.6803 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 366.276 | 366.276 | 0 | 8.5 | 0 | 61.046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 358.9505 | 71.7901 | 0.7179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 03:00 | 6 | 16 | 3 | 167 | 3987 | 55.04 | 0 | 224.3603 | 224.3603 | -224.3603 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 274.2182 | 274.2182 | 0 | 8.5 | 0 | 45.703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 268.7338 | 53.7468 | 0.5375% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 04:00 | 6 | 16 | 4 | 167 | 3988 | 53.06 | 0 | 194.5132 | 194.5132 | -194.5132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 237.7383 | 237.7383 | 0 | 8.5 | 0 | 39.623 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 232.9835 | 46.5967 | 0.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 05:00 | 6 | 16 | 5 | 167 | 3989 | 53.06 | 0 | 200.183 | 200.183 | -200.183 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 244.6682 | 244.6682 | 0 | 8.5 | 0 | 40.778 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 239.7748 | 47.955 | 0.4795% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 06:00 | 6 | 16 | 6 | 167 | 3990 | 57.02 | 0 | 574.3059 | 574.3059 | -574.3059 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 701.9295 | 701.9295 | 0 | 8.5 | 0 | 116.9882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 687.8909 | 137.5782 | 1.376% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 07:00 | 6 | 16 | 7 | 167 | 3991 | 59 | 0 | 552.2503 | 552.2503 | -552.2503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 674.9726 | 674.9726 | 0 | 8.5 | 0 | 112.4954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 661.4732 | 132.2946 | 1.323% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 08:00 | 6 | 16 | 8 | 167 | 3992 | 59 | 0 | 679.6353 | 679.6353 | -679.6353 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 830.6653 | 830.6653 | 0 | 8.5 | 0 | 138.4442 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 814.052 | 162.8104 | 1.628% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 09:00 | 6 | 16 | 9 | 167 | 3993 | 66.02 | 0 | 907.23 | 907.23 | -907.23 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1108.8366 | 1108.8366 | 0 | 8.5 | 0 | 184.8061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1086.6599 | 217.332 | 2.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 10:00 | 6 | 16 | 10 | 167 | 3994 | 68 | 0 | 706.2439 | 706.2439 | -706.2439 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 863.187 | 863.187 | 0 | 8.5 | 0 | 143.8645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 845.9232 | 169.1846 | 1.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 11:00 | 6 | 16 | 11 | 167 | 3995 | 68 | 0 | 2481.5723 | 2481.5723 | -2481.5723 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3033.0328 | 3033.0328 | 0 | 8.5 | 0 | 505.5055 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2972.3722 | 594.4744 | 5.945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 12:00 | 6 | 16 | 12 | 167 | 3996 | 64.94 | 0 | 5510.0185 | 5510.0185 | -5510.0185 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6734.4671 | 6734.4671 | 0 | 8.5 | 0 | 1122.4112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6599.7778 | 1319.9556 | 13.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 13:00 | 6 | 16 | 13 | 167 | 3997 | 62.96 | 0 | 6747.3724 | 6747.3724 | -6747.3724 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8246.7885 | 8246.7885 | 0 | 8.5 | 0 | 1374.4647 | 30% | 1 | 54.98% | 0% | 0% | 0% | 20.5868 | 0 | 0 | 0 | 20.5868 | 0 | 8081.8527 | 1616.3705 | 16.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.8613
2007-06-16 14:00 | 6 | 16 | 14 | 167 | 3998 | 62.96 | 0 | 7316.2965 | 7316.2965 | -7316.2965 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8942.1402 | 8942.1402 | 0 | 8.5 | 0 | 1490.3567 | 30% | 1 | 59.61% | 0% | 0% | 0% | 24.7998 | 0 | 0 | 0 | 24.7998 | 0 | 8763.2974 | 1752.6595 | 17.53% | 1 | 35.05% | 0% | 0% | 3.6558 | 0 | 0 | 3.6558 | 28.4557
2007-06-16 15:00 | 6 | 16 | 15 | 167 | 3999 | 66.92 | 0 | 7094.2481 | 7094.2481 | -7094.2481 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8670.7477 | 8670.7477 | 0 | 8.5 | 0 | 1445.1246 | 30% | 1 | 57.8% | 0% | 0% | 0% | 23.1027 | 0 | 0 | 0 | 23.1027 | 0 | 8497.3328 | 1699.4666 | 16.99% | 1 | 33.99% | 0% | 0% | 3.4057 | 0 | 0 | 3.4057 | 26.5084
2007-06-16 16:00 | 6 | 16 | 16 | 167 | 4000 | 68 | 0 | 7374.2194 | 7374.2194 | -7374.2194 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9012.9348 | 9012.9348 | 0 | 8.5 | 0 | 1502.1558 | 30.04% | 1 | 60.09% | 0% | 0% | 0% | 25.2537 | 0 | 0 | 0 | 25.2537 | 0 | 8832.6761 | 1766.5352 | 17.67% | 1 | 35.33% | 0% | 0% | 3.7227 | 0 | 0 | 3.7227 | 28.9765
2007-06-16 17:00 | 6 | 16 | 17 | 167 | 4001 | 68 | 0 | 7567.4801 | 7567.4801 | -7567.4801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9249.1423 | 9249.1423 | 0 | 8.5 | 0 | 1541.5237 | 30.83% | 1 | 61.66% | 0% | 0% | 0% | 26.802 | 0 | 0 | 0 | 26.802 | 0 | 9064.1595 | 1812.8319 | 18.13% | 1 | 36.26% | 0% | 0% | 3.951 | 0 | 0 | 3.951 | 30.7529
2007-06-16 18:00 | 6 | 16 | 18 | 167 | 4002 | 69.08 | 0 | 6603.2234 | 6603.2234 | -6603.2234 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8070.6064 | 8070.6064 | 0 | 8.5 | 0 | 1345.1011 | 30% | 1 | 53.8% | 0% | 0% | 0% | 19.5892 | 0 | 0 | 0 | 19.5892 | 0 | 7909.1943 | 1581.8389 | 15.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.8638
2007-06-16 19:00 | 6 | 16 | 19 | 167 | 4003 | 68 | 0 | 2440.4229 | 2440.4229 | -2440.4229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2982.7391 | 2982.7391 | 0 | 8.5 | 0 | 497.1232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2923.0843 | 584.6169 | 5.846% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 20:00 | 6 | 16 | 20 | 167 | 4004 | 68 | 0 | 1933.4375 | 1933.4375 | -1933.4375 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2363.0903 | 2363.0903 | 0 | 8.5 | 0 | 393.8484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2315.8285 | 463.1657 | 4.632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 21:00 | 6 | 16 | 21 | 167 | 4005 | 64.94 | 0 | 1867.8457 | 1867.8457 | -1867.8457 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2282.9226 | 2282.9226 | 0 | 8.5 | 0 | 380.4871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2237.2641 | 447.4528 | 4.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 22:00 | 6 | 16 | 22 | 167 | 4006 | 64.04 | 0 | 1162.8387 | 1162.8387 | -1162.8387 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1421.2473 | 1421.2473 | 0 | 8.5 | 0 | 236.8745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1392.8223 | 278.5645 | 2.786% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-16 23:00 | 6 | 16 | 23 | 167 | 4007 | 64.04 | 0 | 651.9328 | 651.9328 | -651.9328 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 796.8068 | 796.8068 | 0 | 8.5 | 0 | 132.8011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 780.8707 | 156.1741 | 1.562% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 | 6 | 17 | 0 | 168 | 4008 | 64.04 | 0 | 502.4191 | 502.4191 | -502.4191 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 614.0678 | 614.0678 | 0 | 8.5 | 0 | 102.3446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 601.7864 | 120.3573 | 1.204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 01:00 | 6 | 17 | 1 | 168 | 4009 | 64.04 | 0 | 215.6235 | 215.6235 | -215.6235 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 263.5398 | 263.5398 | 0 | 8.5 | 0 | 43.9233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 258.269 | 51.6538 | 0.5165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 02:00 | 6 | 17 | 2 | 168 | 4010 | 64.04 | 0 | 49.5881 | 49.5881 | -49.5881 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 60.6077 | 60.6077 | 0 | 8.5 | 0 | 10.1013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 59.3955 | 11.8791 | 0.1188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 03:00 | 6 | 17 | 3 | 168 | 4011 | 64.4 | 0 | 9.2495 | 9.2495 | -9.2495 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11.3049 | 11.3049 | 0 | 8.5 | 0 | 1.8842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 11.0788 | 2.2158 | 0.02216% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 04:00 | 6 | 17 | 4 | 168 | 4012 | 62.6 | 4.6881 | 0 | 0 | 4.6881 | Heating | 4.1366 | 8.5 | 4.1366 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.82732 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.221 | 0 | 0.8442 | 0.008442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 05:00 | 6 | 17 | 5 | 168 | 4013 | 60.98 | 18.9202 | 0 | 0 | 18.9202 | Heating | 16.6943 | 8.5 | 16.6943 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.3389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.035 | 0 | 3.407 | 0.03407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 06:00 | 6 | 17 | 6 | 168 | 4014 | 60.08 | 1744.886 | 215.146 | 215.146 | 1529.74 | Heating | 1349.7706 | 8.5 | 1349.7706 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 269.9541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1377.3169 | 0 | 275.4634 | 2.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 07:00 | 6 | 17 | 7 | 168 | 4015 | 62.6 | 1235.8584 | 227.3021 | 227.3021 | 1008.5563 | Heating | 889.9026 | 8.5 | 889.9026 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.9805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 908.0639 | 0 | 181.6128 | 1.816% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 08:00 | 6 | 17 | 8 | 168 | 4016 | 60.98 | 719.9749 | 836.8092 | 836.8092 | -116.8343 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1022.7668 | 1022.7668 | 0 | 8.5 | 0 | 170.4611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1002.3115 | 200.4623 | 2.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 09:00 | 6 | 17 | 9 | 168 | 4017 | 62.06 | 51.2806 | 1156.1882 | 1156.1882 | -1104.9076 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1413.119 | 1413.119 | 0 | 8.5 | 0 | 235.5198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1384.8566 | 276.9713 | 2.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 10:00 | 6 | 17 | 10 | 168 | 4018 | 64.4 | 3.5108 | 1464.3469 | 1464.3469 | -1460.8361 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1789.7573 | 1789.7573 | 0 | 8.5 | 0 | 298.2929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1753.9622 | 350.7924 | 3.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 11:00 | 6 | 17 | 11 | 168 | 4019 | 64.04 | 0.15145 | 1893.9318 | 1893.9318 | -1893.7803 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2314.8055 | 2314.8055 | 0 | 8.5 | 0 | 385.8009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2268.5094 | 453.7019 | 4.537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 12:00 | 6 | 17 | 12 | 168 | 4020 | 66.02 | 0 | 2508.0652 | 2508.0652 | -2508.0652 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3065.413 | 3065.413 | 0 | 8.5 | 0 | 510.9022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3004.1048 | 600.821 | 6.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 13:00 | 6 | 17 | 13 | 168 | 4021 | 68 | 0 | 3067.139 | 3067.139 | -3067.139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3748.7255 | 3748.7255 | 0 | 8.5 | 0 | 624.7876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3673.751 | 734.7502 | 7.348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 14:00 | 6 | 17 | 14 | 168 | 4022 | 68 | 0 | 3587.2841 | 3587.2841 | -3587.2841 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4384.4584 | 4384.4584 | 0 | 8.5 | 0 | 730.7431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4296.7692 | 859.3538 | 8.594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 15:00 | 6 | 17 | 15 | 168 | 4023 | 66.02 | 0 | 3549.0128 | 3549.0128 | -3549.0128 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4337.6823 | 4337.6823 | 0 | 8.5 | 0 | 722.9471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4250.9287 | 850.1857 | 8.502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 16:00 | 6 | 17 | 16 | 168 | 4024 | 66.92 | 0 | 2992.1386 | 2992.1386 | -2992.1386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3657.0583 | 3657.0583 | 0 | 8.5 | 0 | 609.5097 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3583.9171 | 716.7834 | 7.168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 17:00 | 6 | 17 | 17 | 168 | 4025 | 66.92 | 0 | 2307.6009 | 2307.6009 | -2307.6009 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2820.4011 | 2820.4011 | 0 | 8.5 | 0 | 470.0668 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2763.9931 | 552.7986 | 5.528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 18:00 | 6 | 17 | 18 | 168 | 4026 | 69.98 | 0 | 659.1364 | 659.1364 | -659.1364 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 805.6111 | 805.6111 | 0 | 8.5 | 0 | 134.2685 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 789.4989 | 157.8998 | 1.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 19:00 | 6 | 17 | 19 | 168 | 4027 | 69.08 | 0 | 479.4987 | 479.4987 | -479.4987 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 586.054 | 586.054 | 0 | 8.5 | 0 | 97.6757 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 574.3329 | 114.8666 | 1.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 20:00 | 6 | 17 | 20 | 168 | 4028 | 69.08 | 1.2272 | 308.631 | 308.631 | -307.4038 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 377.2156 | 377.2156 | 0 | 8.5 | 0 | 62.8693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 369.6713 | 73.9343 | 0.7393% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 21:00 | 6 | 17 | 21 | 168 | 4029 | 59 | 7.7174 | 226.8634 | 226.8634 | -219.146 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 277.2775 | 277.2775 | 0 | 8.5 | 0 | 46.2129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 271.7319 | 54.3464 | 0.5435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 22:00 | 6 | 17 | 22 | 168 | 4030 | 59 | 25.2007 | 0 | 0 | 25.2007 | Heating | 22.2359 | 8.5 | 22.2359 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.4472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.6897 | 0 | 4.5379 | 0.04538% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-17 23:00 | 6 | 17 | 23 | 168 | 4031 | 59 | 43.5644 | 0 | 0 | 43.5644 | Heating | 38.4392 | 8.5 | 38.4392 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.6878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 39.2236 | 0 | 7.8447 | 0.07845% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 | 6 | 18 | 0 | 169 | 4032 | 57.02 | 69.7668 | 0 | 0 | 69.7668 | Heating | 61.5589 | 8.5 | 61.5589 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.3118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 62.8152 | 0 | 12.563 | 0.1256% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 01:00 | 6 | 18 | 1 | 169 | 4033 | 55.94 | 112.529 | 0 | 0 | 112.529 | Heating | 99.2903 | 8.5 | 99.2903 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.8581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 101.3167 | 0 | 20.2633 | 0.2026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 02:00 | 6 | 18 | 2 | 169 | 4034 | 55.94 | 160.4406 | 0 | 0 | 160.4406 | Heating | 141.5652 | 8.5 | 141.5652 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 144.4543 | 0 | 28.8909 | 0.2889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 03:00 | 6 | 18 | 3 | 169 | 4035 | 53.96 | 205.4586 | 0 | 0 | 205.4586 | Heating | 181.287 | 8.5 | 181.287 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.2574 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 184.9868 | 0 | 36.9974 | 0.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 04:00 | 6 | 18 | 4 | 169 | 4036 | 53.06 | 252.1844 | 0 | 0 | 252.1844 | Heating | 222.5157 | 8.5 | 222.5157 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.5031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 227.0568 | 0 | 45.4114 | 0.4541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 05:00 | 6 | 18 | 5 | 169 | 4037 | 53.06 | 275.3428 | 0 | 0 | 275.3428 | Heating | 242.9496 | 8.5 | 242.9496 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.5899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 247.9077 | 0 | 49.5815 | 0.4958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 06:00 | 6 | 18 | 6 | 169 | 4038 | 59 | 4100.0051 | 34.6488 | 34.6488 | 4065.3562 | Heating | 3587.079 | 8.5 | 3587.079 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 717.4158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3660.2847 | 0 | 732.0569 | 7.321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 07:00 | 6 | 18 | 7 | 169 | 4039 | 62.96 | 2223.8094 | 49.4085 | 49.4085 | 2174.4009 | Heating | 1918.589 | 8.5 | 1918.589 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 383.7178 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1957.7439 | 0 | 391.5488 | 3.915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 08:00 | 6 | 18 | 8 | 169 | 4040 | 62.96 | 1197.9614 | 366.706 | 366.706 | 831.2555 | Heating | 733.4607 | 8.5 | 733.4607 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 146.6921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 748.4293 | 0 | 149.6859 | 1.497% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 09:00 | 6 | 18 | 9 | 169 | 4041 | 71.06 | 136.7973 | 796.9915 | 796.9915 | -660.1941 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 974.1007 | 974.1007 | 0 | 8.5 | 0 | 162.3501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 954.6187 | 190.9237 | 1.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 10:00 | 6 | 18 | 10 | 169 | 4042 | 73.04 | 12.5581 | 1321.0735 | 1321.0735 | -1308.5154 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1614.6454 | 1614.6454 | 0 | 8.5 | 0 | 269.1076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1582.3525 | 316.4705 | 3.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 11:00 | 6 | 18 | 11 | 169 | 4043 | 73.04 | 2.2715 | 1761.6839 | 1761.6839 | -1759.4124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2153.1692 | 2153.1692 | 0 | 8.5 | 0 | 358.8615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2110.1058 | 422.0212 | 4.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 12:00 | 6 | 18 | 12 | 169 | 4044 | 80.06 | 0.68108 | 2082.1041 | 2082.1041 | -2081.423 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2544.7939 | 2544.7939 | 0 | 8.5 | 0 | 424.1323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2493.8981 | 498.7796 | 4.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 13:00 | 6 | 18 | 13 | 169 | 4045 | 80.96 | 0.022481 | 3185.9418 | 3185.9418 | -3185.9193 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3893.9288 | 3893.9288 | 0 | 8.5 | 0 | 648.9881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3816.0503 | 763.2101 | 7.632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 14:00 | 6 | 18 | 14 | 169 | 4046 | 80.96 | 0 | 3663.2144 | 3663.2144 | -3663.2144 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4477.262 | 4477.262 | 0 | 8.5 | 0 | 746.2103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4387.7168 | 877.5434 | 8.775% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 15:00 | 6 | 18 | 15 | 169 | 4047 | 84.02 | 0 | 3780.4057 | 3780.4057 | -3780.4057 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4620.4958 | 4620.4958 | 0 | 8.5 | 0 | 770.0826 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4528.0859 | 905.6172 | 9.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 16:00 | 6 | 18 | 16 | 169 | 4048 | 84.02 | 0 | 3691.8386 | 3691.8386 | -3691.8386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4512.2472 | 4512.2472 | 0 | 8.5 | 0 | 752.0412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4422.0022 | 884.4004 | 8.844% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 17:00 | 6 | 18 | 17 | 169 | 4049 | 84.02 | 0 | 3382.8306 | 3382.8306 | -3382.8306 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4134.5708 | 4134.5708 | 0 | 8.5 | 0 | 689.0951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4051.8793 | 810.3759 | 8.104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 18:00 | 6 | 18 | 18 | 169 | 4050 | 82.04 | 0 | 1873.0723 | 1873.0723 | -1873.0723 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2289.3106 | 2289.3106 | 0 | 8.5 | 0 | 381.5518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2243.5244 | 448.7049 | 4.487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 19:00 | 6 | 18 | 19 | 169 | 4051 | 80.06 | 0 | 1142.4667 | 1142.4667 | -1142.4667 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1396.3482 | 1396.3482 | 0 | 8.5 | 0 | 232.7247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1368.4213 | 273.6843 | 2.737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 20:00 | 6 | 18 | 20 | 169 | 4052 | 80.06 | 0 | 357.5577 | 357.5577 | -357.5577 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 437.0149 | 437.0149 | 0 | 8.5 | 0 | 72.8358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 428.2746 | 85.6549 | 0.8565% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 21:00 | 6 | 18 | 21 | 169 | 4053 | 75.02 | 0 | 273.2193 | 273.2193 | -273.2193 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 333.9346 | 333.9346 | 0 | 8.5 | 0 | 55.6558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 327.256 | 65.4512 | 0.6545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 22:00 | 6 | 18 | 22 | 169 | 4054 | 71.96 | 4.2939 | 0 | 0 | 4.2939 | Heating | 3.7887 | 8.5 | 3.7887 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.75774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.866 | 0 | 0.7732 | 0.007732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-18 23:00 | 6 | 18 | 23 | 169 | 4055 | 71.96 | 22.8568 | 0 | 0 | 22.8568 | Heating | 20.1677 | 8.5 | 20.1677 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.0335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.5793 | 0 | 4.1159 | 0.04116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 | 6 | 19 | 0 | 170 | 4056 | 69.98 | 36.6022 | 0 | 0 | 36.6022 | Heating | 32.2961 | 8.5 | 32.2961 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.4592 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 32.9552 | 0 | 6.591 | 0.06591% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 01:00 | 6 | 19 | 1 | 170 | 4057 | 69.08 | 49.822 | 0 | 0 | 49.822 | Heating | 43.9606 | 8.5 | 43.9606 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.7921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.8578 | 0 | 8.9716 | 0.08972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 02:00 | 6 | 19 | 2 | 170 | 4058 | 69.08 | 67.7114 | 0 | 0 | 67.7114 | Heating | 59.7454 | 8.5 | 59.7454 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.9491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 60.9647 | 0 | 12.1929 | 0.1219% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 03:00 | 6 | 19 | 3 | 170 | 4059 | 66.02 | 86.3976 | 0 | 0 | 86.3976 | Heating | 76.2332 | 8.5 | 76.2332 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.2466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.789 | 0 | 15.5578 | 0.1556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 04:00 | 6 | 19 | 4 | 170 | 4060 | 64.94 | 102.9353 | 0 | 0 | 102.9353 | Heating | 90.8253 | 8.5 | 90.8253 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.1651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 92.6789 | 0 | 18.5358 | 0.1854% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 05:00 | 6 | 19 | 5 | 170 | 4061 | 64.94 | 167.8836 | 0 | 0 | 167.8836 | Heating | 148.1326 | 8.5 | 148.1326 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.6265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 151.1557 | 0 | 30.2311 | 0.3023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 06:00 | 6 | 19 | 6 | 170 | 4062 | 66.02 | 3065.7747 | 113.9435 | 113.9435 | 2951.8312 | Heating | 2604.557 | 8.5 | 2604.557 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 520.9114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2657.7112 | 0 | 531.5422 | 5.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 07:00 | 6 | 19 | 7 | 170 | 4063 | 68 | 1561.869 | 88.7279 | 88.7279 | 1473.1412 | Heating | 1299.8304 | 8.5 | 1299.8304 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 259.9661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1326.3576 | 0 | 265.2715 | 2.653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 08:00 | 6 | 19 | 8 | 170 | 4064 | 68 | 521.7851 | 751.5107 | 751.5107 | -229.7256 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 918.5131 | 918.5131 | 0 | 8.5 | 0 | 153.0855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 900.1428 | 180.0286 | 1.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 09:00 | 6 | 19 | 9 | 170 | 4065 | 73.04 | 3.6803 | 1965.7508 | 1965.7508 | -1962.0706 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2402.5843 | 2402.5843 | 0 | 8.5 | 0 | 400.4307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2354.5326 | 470.9065 | 4.709% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 10:00 | 6 | 19 | 10 | 170 | 4066 | 77 | 0 | 3356.2922 | 3356.2922 | -3356.2922 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4102.1349 | 4102.1349 | 0 | 8.5 | 0 | 683.6891 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4020.0922 | 804.0184 | 8.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 11:00 | 6 | 19 | 11 | 170 | 4067 | 77 | 0 | 4951.4189 | 4951.4189 | -4951.4189 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6051.7342 | 6051.7342 | 0 | 8.5 | 0 | 1008.6224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5930.6995 | 1186.1399 | 11.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 12:00 | 6 | 19 | 12 | 170 | 4068 | 82.94 | 0 | 5921.9923 | 5921.9923 | -5921.9923 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7237.9905 | 7237.9905 | 0 | 8.5 | 0 | 1206.3318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7093.2307 | 1418.6461 | 14.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 13:00 | 6 | 19 | 13 | 170 | 4069 | 82.94 | 0 | 6937.8886 | 6937.8886 | -6937.8886 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8479.6416 | 8479.6416 | 0 | 8.5 | 0 | 1413.2736 | 30% | 1 | 56.53% | 0% | 0% | 0% | 21.9483 | 0 | 0 | 0 | 21.9483 | 0 | 8310.0488 | 1662.0098 | 16.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.2229
2007-06-19 14:00 | 6 | 19 | 14 | 170 | 4070 | 82.94 | 0 | 7097.5645 | 7097.5645 | -7097.5645 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8674.801 | 8674.801 | 0 | 8.5 | 0 | 1445.8002 | 30% | 1 | 57.83% | 0% | 0% | 0% | 23.1276 | 0 | 0 | 0 | 23.1276 | 0 | 8501.305 | 1700.261 | 17% | 1 | 34.01% | 0% | 0% | 3.4093 | 0 | 0 | 3.4093 | 26.5369
2007-06-19 15:00 | 6 | 19 | 15 | 170 | 4071 | 84.92 | 0 | 6143.7775 | 6143.7775 | -6143.7775 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7509.0613 | 7509.0613 | 0 | 8.5 | 0 | 1251.5102 | 30% | 1 | 50.06% | 0% | 0% | 0% | 16.5951 | 0 | 0 | 0 | 16.5951 | 0 | 7358.8801 | 1471.776 | 14.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8697
2007-06-19 16:00 | 6 | 19 | 16 | 170 | 4072 | 84.92 | 0 | 4613.2434 | 4613.2434 | -4613.2434 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5638.4086 | 5638.4086 | 0 | 8.5 | 0 | 939.7348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5525.6405 | 1105.1281 | 11.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 17:00 | 6 | 19 | 17 | 170 | 4073 | 84.92 | 0 | 2891.1441 | 2891.1441 | -2891.1441 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3533.6205 | 3533.6205 | 0 | 8.5 | 0 | 588.9368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3462.9481 | 692.5896 | 6.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 18:00 | 6 | 19 | 18 | 170 | 4074 | 82.94 | 0 | 683.1838 | 683.1838 | -683.1838 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 835.0024 | 835.0024 | 0 | 8.5 | 0 | 139.1671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 818.3024 | 163.6605 | 1.637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 19:00 | 6 | 19 | 19 | 170 | 4075 | 80.96 | 0.38007 | 387.8559 | 387.8559 | -387.4758 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 474.0461 | 474.0461 | 0 | 8.5 | 0 | 79.0077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 464.5652 | 92.913 | 0.9291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 20:00 | 6 | 19 | 20 | 170 | 4076 | 80.96 | 3.7055 | 276.1175 | 276.1175 | -272.412 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 337.477 | 337.477 | 0 | 8.5 | 0 | 56.2462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 330.7274 | 66.1455 | 0.6615% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 21:00 | 6 | 19 | 21 | 170 | 4077 | 78.98 | 6.2427 | 235.5953 | 235.5953 | -229.3526 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 287.9498 | 287.9498 | 0 | 8.5 | 0 | 47.9916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 282.1908 | 56.4382 | 0.5644% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 22:00 | 6 | 19 | 22 | 170 | 4078 | 77 | 14.3637 | 0 | 0 | 14.3637 | Heating | 12.6739 | 8.5 | 12.6739 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.9325 | 0 | 2.5865 | 0.02587% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-19 23:00 | 6 | 19 | 23 | 170 | 4079 | 77 | 24.861 | 0 | 0 | 24.861 | Heating | 21.9362 | 8.5 | 21.9362 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.3872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.3839 | 0 | 4.4768 | 0.04477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 | 6 | 20 | 0 | 171 | 4080 | 73.04 | 32.7225 | 0 | 0 | 32.7225 | Heating | 28.8728 | 8.5 | 28.8728 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.7746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 29.462 | 0 | 5.8924 | 0.05892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 01:00 | 6 | 20 | 1 | 171 | 4081 | 73.04 | 38.4912 | 0 | 0 | 38.4912 | Heating | 33.9628 | 8.5 | 33.9628 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7926 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.6559 | 0 | 6.9312 | 0.06931% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 02:00 | 6 | 20 | 2 | 171 | 4082 | 73.04 | 44.2844 | 0 | 0 | 44.2844 | Heating | 39.0744 | 8.5 | 39.0744 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.8149 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 39.8719 | 0 | 7.9744 | 0.07974% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 03:00 | 6 | 20 | 3 | 171 | 4083 | 71.06 | 45.4199 | 0 | 0 | 45.4199 | Heating | 40.0764 | 8.5 | 40.0764 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.0153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.8943 | 0 | 8.1789 | 0.08179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 04:00 | 6 | 20 | 4 | 171 | 4084 | 69.8 | 46.425 | 0 | 0 | 46.425 | Heating | 40.9632 | 8.5 | 40.9632 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.1926 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 41.7992 | 0 | 8.3598 | 0.0836% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 05:00 | 6 | 20 | 5 | 171 | 4085 | 69.08 | 46.83 | 0 | 0 | 46.83 | Heating | 41.3206 | 8.5 | 41.3206 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.2641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.1639 | 0 | 8.4328 | 0.08433% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 06:00 | 6 | 20 | 6 | 171 | 4086 | 69.98 | 1636.3117 | 199.8504 | 199.8504 | 1436.4613 | Heating | 1267.4658 | 8.5 | 1267.4658 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.4932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1293.3325 | 0 | 258.6665 | 2.587% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 07:00 | 6 | 20 | 7 | 171 | 4087 | 71.96 | 1227.5662 | 21.8273 | 21.8273 | 1205.7388 | Heating | 1063.8872 | 8.5 | 1063.8872 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.7774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1085.5992 | 0 | 217.1198 | 2.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 08:00 | 6 | 20 | 8 | 171 | 4088 | 71.96 | 758.8279 | 549.9319 | 549.9319 | 208.896 | Heating | 184.32 | 8.5 | 184.32 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 188.0816 | 0 | 37.6163 | 0.3762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 09:00 | 6 | 20 | 9 | 171 | 4089 | 78.98 | 76.2131 | 966.0141 | 966.0141 | -889.801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1180.6839 | 1180.6839 | 0 | 8.5 | 0 | 196.7807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1157.0702 | 231.414 | 2.314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 10:00 | 6 | 20 | 10 | 171 | 4090 | 80.06 | 18.6419 | 1248.2759 | 1248.2759 | -1229.634 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1525.6705 | 1525.6705 | 0 | 8.5 | 0 | 254.2784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1495.1571 | 299.0314 | 2.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 11:00 | 6 | 20 | 11 | 171 | 4091 | 80.06 | 7.5718 | 1816.7329 | 1816.7329 | -1809.1611 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2220.4513 | 2220.4513 | 0 | 8.5 | 0 | 370.0752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2176.0423 | 435.2085 | 4.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 12:00 | 6 | 20 | 12 | 171 | 4092 | 84.02 | 0.78173 | 2798.2489 | 2798.2489 | -2797.4672 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3420.082 | 3420.082 | 0 | 8.5 | 0 | 570.0137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3351.6804 | 670.3361 | 6.703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 13:00 | 6 | 20 | 13 | 171 | 4093 | 84.02 | 0 | 4368.755 | 4368.755 | -4368.755 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5339.5894 | 5339.5894 | 0 | 8.5 | 0 | 889.9316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5232.7977 | 1046.5595 | 10.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 14:00 | 6 | 20 | 14 | 171 | 4094 | 84.02 | 0 | 5676.5497 | 5676.5497 | -5676.5497 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6938.0052 | 6938.0052 | 0 | 8.5 | 0 | 1156.3342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6799.2451 | 1359.849 | 13.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 15:00 | 6 | 20 | 15 | 171 | 4095 | 84.02 | 0 | 5985.174 | 5985.174 | -5985.174 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7315.2127 | 7315.2127 | 0 | 8.5 | 0 | 1219.2021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7168.9084 | 1433.7817 | 14.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 16:00 | 6 | 20 | 16 | 171 | 4096 | 84.92 | 0 | 5867.6529 | 5867.6529 | -5867.6529 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7171.5758 | 7171.5758 | 0 | 8.5 | 0 | 1195.2626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7028.1443 | 1405.6289 | 14.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 17:00 | 6 | 20 | 17 | 171 | 4097 | 84.92 | 0 | 5628.2964 | 5628.2964 | -5628.2964 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6879.0289 | 6879.0289 | 0 | 8.5 | 0 | 1146.5048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6741.4483 | 1348.2897 | 13.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 18:00 | 6 | 20 | 18 | 171 | 4098 | 80.96 | 0 | 3411.6587 | 3411.6587 | -3411.6587 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4169.805 | 4169.805 | 0 | 8.5 | 0 | 694.9675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4086.4089 | 817.2818 | 8.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 19:00 | 6 | 20 | 19 | 171 | 4099 | 78.98 | 0 | 2473.2044 | 2473.2044 | -2473.2044 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3022.8053 | 3022.8053 | 0 | 8.5 | 0 | 503.8009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2962.3492 | 592.4698 | 5.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 20:00 | 6 | 20 | 20 | 171 | 4100 | 78.98 | 0 | 870.8124 | 870.8124 | -870.8124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1064.3263 | 1064.3263 | 0 | 8.5 | 0 | 177.3877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1043.0397 | 208.6079 | 2.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 21:00 | 6 | 20 | 21 | 171 | 4101 | 73.94 | 0 | 328.2693 | 328.2693 | -328.2693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 401.2181 | 401.2181 | 0 | 8.5 | 0 | 66.8697 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 393.1937 | 78.6387 | 0.7864% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 22:00 | 6 | 20 | 22 | 171 | 4102 | 73.04 | 0.31223 | 0 | 0 | 0.31223 | Heating | 0.2755 | 8.5 | 0.2755 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.055099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.28112 | 0 | 0.056224 | 0.0005622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-20 23:00 | 6 | 20 | 23 | 171 | 4103 | 73.04 | 23.3993 | 0 | 0 | 23.3993 | Heating | 20.6465 | 8.5 | 20.6465 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.1293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.0678 | 0 | 4.2136 | 0.04214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 | 6 | 21 | 0 | 172 | 4104 | 71.06 | 48.6546 | 0 | 0 | 48.6546 | Heating | 42.9306 | 8.5 | 42.9306 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.5861 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.8067 | 0 | 8.7613 | 0.08761% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 01:00 | 6 | 21 | 1 | 172 | 4105 | 69.08 | 97.3713 | 0 | 0 | 97.3713 | Heating | 85.9159 | 8.5 | 85.9159 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.1832 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 87.6693 | 0 | 17.5339 | 0.1753% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 02:00 | 6 | 21 | 2 | 172 | 4106 | 69.08 | 157.5857 | 0 | 0 | 157.5857 | Heating | 139.0462 | 8.5 | 139.0462 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.8092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 141.8839 | 0 | 28.3768 | 0.2838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 03:00 | 6 | 21 | 3 | 172 | 4107 | 66.02 | 222.0434 | 0 | 0 | 222.0434 | Heating | 195.9207 | 8.5 | 195.9207 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.1841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 199.9191 | 0 | 39.9838 | 0.3998% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 04:00 | 6 | 21 | 4 | 172 | 4108 | 66.02 | 291.3509 | 0 | 0 | 291.3509 | Heating | 257.0743 | 8.5 | 257.0743 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.4149 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 262.3207 | 0 | 52.4641 | 0.5246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 05:00 | 6 | 21 | 5 | 172 | 4109 | 66.02 | 323.2171 | 0 | 0 | 323.2171 | Heating | 285.1915 | 8.5 | 285.1915 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.0383 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 291.0118 | 0 | 58.2024 | 0.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 06:00 | 6 | 21 | 6 | 172 | 4110 | 68 | 4221.2732 | 79.0745 | 79.0745 | 4142.1987 | Heating | 3654.8812 | 8.5 | 3654.8812 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 730.9762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3729.4706 | 0 | 745.8941 | 7.459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 07:00 | 6 | 21 | 7 | 172 | 4111 | 69.08 | 2142.5504 | 57.3593 | 57.3593 | 2085.1911 | Heating | 1839.8745 | 8.5 | 1839.8745 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 367.9749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1877.423 | 0 | 375.4846 | 3.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 08:00 | 6 | 21 | 8 | 172 | 4112 | 69.08 | 968.2555 | 507.5697 | 507.5697 | 460.6858 | Heating | 406.4875 | 8.5 | 406.4875 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.2975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 414.7831 | 0 | 82.9566 | 0.8296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 09:00 | 6 | 21 | 9 | 172 | 4113 | 75.92 | 26.3892 | 1214.3367 | 1214.3367 | -1187.9475 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1484.1893 | 1484.1893 | 0 | 8.5 | 0 | 247.3649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1454.5055 | 290.9011 | 2.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 10:00 | 6 | 21 | 10 | 172 | 4114 | 78.08 | 1.3578 | 2411.1512 | 2411.1512 | -2409.7934 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2946.9626 | 2946.9626 | 0 | 8.5 | 0 | 491.1604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2888.0233 | 577.6047 | 5.776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 11:00 | 6 | 21 | 11 | 172 | 4115 | 78.08 | 0 | 3837.2519 | 3837.2519 | -3837.2519 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4689.9745 | 4689.9745 | 0 | 8.5 | 0 | 781.6624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4596.175 | 919.235 | 9.192% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 12:00 | 6 | 21 | 12 | 172 | 4116 | 78.08 | 0 | 4866.1391 | 4866.1391 | -4866.1391 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5947.5034 | 5947.5034 | 0 | 8.5 | 0 | 991.2506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5828.5533 | 1165.7107 | 11.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 13:00 | 6 | 21 | 13 | 172 | 4117 | 80.96 | 0 | 5577.3217 | 5577.3217 | -5577.3217 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6816.7265 | 6816.7265 | 0 | 8.5 | 0 | 1136.1211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6680.392 | 1336.0784 | 13.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 14:00 | 6 | 21 | 14 | 172 | 4118 | 80.96 | 0 | 6333.3162 | 6333.3162 | -6333.3162 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7740.7198 | 7740.7198 | 0 | 8.5 | 0 | 1290.12 | 30% | 1 | 51.6% | 0% | 0% | 0% | 17.7963 | 0 | 0 | 0 | 17.7963 | 0 | 7585.9054 | 1517.1811 | 15.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.0709
2007-06-21 15:00 | 6 | 21 | 15 | 172 | 4119 | 82.04 | 0 | 6794.3959 | 6794.3959 | -6794.3959 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8304.2616 | 8304.2616 | 0 | 8.5 | 0 | 1384.0436 | 30% | 1 | 55.36% | 0% | 0% | 0% | 20.9183 | 0 | 0 | 0 | 20.9183 | 0 | 8138.1764 | 1627.6353 | 16.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.1928
2007-06-21 16:00 | 6 | 21 | 16 | 172 | 4120 | 80.96 | 0 | 6850.2281 | 6850.2281 | -6850.2281 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8372.501 | 8372.501 | 0 | 8.5 | 0 | 1395.4168 | 30% | 1 | 55.82% | 0% | 0% | 0% | 21.3157 | 0 | 0 | 0 | 21.3157 | 0 | 8205.051 | 1641.0102 | 16.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.5903
2007-06-21 17:00 | 6 | 21 | 17 | 172 | 4121 | 80.96 | 0 | 6695.8599 | 6695.8599 | -6695.8599 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8183.8288 | 8183.8288 | 0 | 8.5 | 0 | 1363.9715 | 30% | 1 | 54.56% | 0% | 0% | 0% | 20.2271 | 0 | 0 | 0 | 20.2271 | 0 | 8020.1522 | 1604.0304 | 16.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.5016
2007-06-21 18:00 | 6 | 21 | 18 | 172 | 4122 | 78.98 | 0 | 4454.5955 | 4454.5955 | -4454.5955 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5444.5056 | 5444.5056 | 0 | 8.5 | 0 | 907.4176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5335.6154 | 1067.1231 | 10.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 19:00 | 6 | 21 | 19 | 172 | 4123 | 75.92 | 0 | 3773.2475 | 3773.2475 | -3773.2475 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4611.7469 | 4611.7469 | 0 | 8.5 | 0 | 768.6245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4519.5119 | 903.9024 | 9.039% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 20:00 | 6 | 21 | 20 | 172 | 4124 | 75.92 | 0 | 1695.1132 | 1695.1132 | -1695.1132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2071.805 | 2071.805 | 0 | 8.5 | 0 | 345.3008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2030.3689 | 406.0738 | 4.061% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 21:00 | 6 | 21 | 21 | 172 | 4125 | 71.96 | 0 | 415.766 | 415.766 | -415.766 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 508.1584 | 508.1584 | 0 | 8.5 | 0 | 84.6931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 497.9953 | 99.5991 | 0.996% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 22:00 | 6 | 21 | 22 | 172 | 4126 | 69.98 | 0.062374 | 0.56502 | 0.56502 | -0.50264 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.69058 | 0.69058 | 0 | 8.5 | 0 | 0.1151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.67677 | 0.13535 | 0.001354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-21 23:00 | 6 | 21 | 23 | 172 | 4127 | 69.98 | 10.9065 | 0 | 0 | 10.9065 | Heating | 9.6234 | 8.5 | 9.6234 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.9247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.8198 | 0 | 1.964 | 0.01964% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 | 6 | 22 | 0 | 173 | 4128 | 64.94 | 19.5584 | 0 | 0 | 19.5584 | Heating | 17.2574 | 8.5 | 17.2574 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.4515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.6096 | 0 | 3.5219 | 0.03522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 01:00 | 6 | 22 | 1 | 173 | 4129 | 62.96 | 21.5789 | 0 | 0 | 21.5789 | Heating | 19.0402 | 8.5 | 19.0402 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.4287 | 0 | 3.8857 | 0.03886% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 02:00 | 6 | 22 | 2 | 173 | 4130 | 62.96 | 26.3712 | 0 | 0 | 26.3712 | Heating | 23.2687 | 8.5 | 23.2687 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.7436 | 0 | 4.7487 | 0.04749% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 03:00 | 6 | 22 | 3 | 173 | 4131 | 60.98 | 39.117 | 0 | 0 | 39.117 | Heating | 34.515 | 8.5 | 34.515 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.2194 | 0 | 7.0439 | 0.07044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 04:00 | 6 | 22 | 4 | 173 | 4132 | 60.08 | 52.9637 | 0 | 0 | 52.9637 | Heating | 46.7327 | 8.5 | 46.7327 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.3465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.6864 | 0 | 9.5373 | 0.09537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 05:00 | 6 | 22 | 5 | 173 | 4133 | 60.08 | 59.4412 | 0 | 0 | 59.4412 | Heating | 52.4481 | 8.5 | 52.4481 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.4896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 53.5185 | 0 | 10.7037 | 0.107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 06:00 | 6 | 22 | 6 | 173 | 4134 | 60.98 | 2055.3352 | 90.0427 | 90.0427 | 1965.2925 | Heating | 1734.0816 | 8.5 | 1734.0816 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.8163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1769.471 | 0 | 353.8942 | 3.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 07:00 | 6 | 22 | 7 | 173 | 4135 | 64.04 | 969.7109 | 32.2783 | 32.2783 | 937.4327 | Heating | 827.1465 | 8.5 | 827.1465 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.4293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 844.027 | 0 | 168.8054 | 1.688% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 08:00 | 6 | 22 | 8 | 173 | 4136 | 64.04 | 332.958 | 195.2349 | 195.2349 | 137.7231 | Heating | 121.5204 | 8.5 | 121.5204 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.3041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 124.0004 | 0 | 24.8001 | 0.248% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 09:00 | 6 | 22 | 9 | 173 | 4137 | 71.06 | 0 | 548.7466 | 548.7466 | -548.7466 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 670.6903 | 670.6903 | 0 | 8.5 | 0 | 111.7817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 657.2765 | 131.4553 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 10:00 | 6 | 22 | 10 | 173 | 4138 | 73.94 | 0 | 1297.9508 | 1297.9508 | -1297.9508 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1586.3843 | 1586.3843 | 0 | 8.5 | 0 | 264.3974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1554.6567 | 310.9313 | 3.109% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 11:00 | 6 | 22 | 11 | 173 | 4139 | 73.94 | 0 | 3120.0285 | 3120.0285 | -3120.0285 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3813.3682 | 3813.3682 | 0 | 8.5 | 0 | 635.5614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3737.1008 | 747.4202 | 7.474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 12:00 | 6 | 22 | 12 | 173 | 4140 | 75.92 | 0 | 4371.4809 | 4371.4809 | -4371.4809 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5342.9211 | 5342.9211 | 0 | 8.5 | 0 | 890.4869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5236.0627 | 1047.2125 | 10.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 13:00 | 6 | 22 | 13 | 173 | 4141 | 77 | 0 | 5441.8013 | 5441.8013 | -5441.8013 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6651.0904 | 6651.0904 | 0 | 8.5 | 0 | 1108.5151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6518.0686 | 1303.6137 | 13.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 14:00 | 6 | 22 | 14 | 173 | 4142 | 77 | 0 | 6195.5019 | 6195.5019 | -6195.5019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7572.2801 | 7572.2801 | 0 | 8.5 | 0 | 1262.0467 | 30% | 1 | 50.48% | 0% | 0% | 0% | 16.9182 | 0 | 0 | 0 | 16.9182 | 0 | 7420.8345 | 1484.1669 | 14.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.1928
2007-06-22 15:00 | 6 | 22 | 15 | 173 | 4143 | 73.94 | 0 | 6589.0246 | 6589.0246 | -6589.0246 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8053.2523 | 8053.2523 | 0 | 8.5 | 0 | 1342.2087 | 30% | 1 | 53.69% | 0% | 0% | 0% | 19.4925 | 0 | 0 | 0 | 19.4925 | 0 | 7892.1873 | 1578.4375 | 15.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.767
2007-06-22 16:00 | 6 | 22 | 16 | 173 | 4144 | 75.02 | 0 | 6697.7133 | 6697.7133 | -6697.7133 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8186.094 | 8186.094 | 0 | 8.5 | 0 | 1364.349 | 30% | 1 | 54.57% | 0% | 0% | 0% | 20.24 | 0 | 0 | 0 | 20.24 | 0 | 8022.3722 | 1604.4744 | 16.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.5145
2007-06-22 17:00 | 6 | 22 | 17 | 173 | 4145 | 75.02 | 0 | 6272.9394 | 6272.9394 | -6272.9394 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7666.9259 | 7666.9259 | 0 | 8.5 | 0 | 1277.821 | 30% | 1 | 51.11% | 0% | 0% | 0% | 17.4085 | 0 | 0 | 0 | 17.4085 | 0 | 7513.5874 | 1502.7175 | 15.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.6831
2007-06-22 18:00 | 6 | 22 | 18 | 173 | 4146 | 69.98 | 0 | 4145.7624 | 4145.7624 | -4145.7624 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5067.043 | 5067.043 | 0 | 8.5 | 0 | 844.5072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4965.7021 | 993.1404 | 9.931% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 19:00 | 6 | 22 | 19 | 173 | 4147 | 71.06 | 0 | 3103.6761 | 3103.6761 | -3103.6761 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3793.3819 | 3793.3819 | 0 | 8.5 | 0 | 632.2303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3717.5143 | 743.5029 | 7.435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 20:00 | 6 | 22 | 20 | 173 | 4148 | 71.06 | 0 | 2045.3749 | 2045.3749 | -2045.3749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2499.9026 | 2499.9026 | 0 | 8.5 | 0 | 416.6504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2449.9046 | 489.9809 | 4.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 21:00 | 6 | 22 | 21 | 173 | 4149 | 68 | 0 | 854.8328 | 854.8328 | -854.8328 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1044.7956 | 1044.7956 | 0 | 8.5 | 0 | 174.1326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1023.8997 | 204.7799 | 2.048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 22:00 | 6 | 22 | 22 | 173 | 4150 | 68 | 0 | 406.7123 | 406.7123 | -406.7123 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 497.0928 | 497.0928 | 0 | 8.5 | 0 | 82.8488 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 487.151 | 97.4302 | 0.9743% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-22 23:00 | 6 | 22 | 23 | 173 | 4151 | 68 | 0 | 311.928 | 311.928 | -311.928 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 381.2454 | 381.2454 | 0 | 8.5 | 0 | 63.5409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 373.6205 | 74.7241 | 0.7472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 | 6 | 23 | 0 | 174 | 4152 | 68 | 0 | 226.0762 | 226.0762 | -226.0762 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 276.3153 | 276.3153 | 0 | 8.5 | 0 | 46.0526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 270.789 | 54.1578 | 0.5416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 01:00 | 6 | 23 | 1 | 174 | 4153 | 66.2 | 0 | 132.1741 | 132.1741 | -132.1741 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 161.5461 | 161.5461 | 0 | 8.5 | 0 | 26.9243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 158.3152 | 31.663 | 0.3166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 02:00 | 6 | 23 | 2 | 174 | 4154 | 66.92 | 0 | 69.9674 | 69.9674 | -69.9674 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 85.5157 | 85.5157 | 0 | 8.5 | 0 | 14.2526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 83.8054 | 16.7611 | 0.1676% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 03:00 | 6 | 23 | 3 | 174 | 4155 | 68 | 0 | 46.5968 | 46.5968 | -46.5968 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 56.9516 | 56.9516 | 0 | 8.5 | 0 | 9.4919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 55.8126 | 11.1625 | 0.1116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 04:00 | 6 | 23 | 4 | 174 | 4156 | 68 | 0 | 28.7174 | 28.7174 | -28.7174 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 35.099 | 35.099 | 0 | 8.5 | 0 | 5.8498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 34.397 | 6.8794 | 0.06879% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 05:00 | 6 | 23 | 5 | 174 | 4157 | 66.92 | 0 | 8.5851 | 8.5851 | -8.5851 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10.4929 | 10.4929 | 0 | 8.5 | 0 | 1.7488 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 10.283 | 2.0566 | 0.02057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 06:00 | 6 | 23 | 6 | 174 | 4158 | 68 | 0 | 2.4015 | 2.4015 | -2.4015 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.9352 | 2.9352 | 0 | 8.5 | 0 | 0.48919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.8765 | 0.57529 | 0.005753% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 07:00 | 6 | 23 | 7 | 174 | 4159 | 69.8 | 0 | 11.4807 | 11.4807 | -11.4807 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14.0319 | 14.0319 | 0 | 8.5 | 0 | 2.3387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.7513 | 2.7503 | 0.0275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 08:00 | 6 | 23 | 8 | 174 | 4160 | 71.96 | 448.0484 | 23.867 | 23.867 | 424.1813 | Heating | 374.2776 | 8.5 | 374.2776 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.8555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 381.916 | 0 | 76.3832 | 0.7638% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 09:00 | 6 | 23 | 9 | 174 | 4161 | 75.02 | 0 | 244.4217 | 244.4217 | -244.4217 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 298.7377 | 298.7377 | 0 | 8.5 | 0 | 49.7896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 292.7629 | 58.5526 | 0.5855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 10:00 | 6 | 23 | 10 | 174 | 4162 | 75.92 | 0 | 648.3471 | 648.3471 | -648.3471 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 792.4243 | 792.4243 | 0 | 8.5 | 0 | 132.0707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 776.5758 | 155.3152 | 1.553% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 11:00 | 6 | 23 | 11 | 174 | 4163 | 75.92 | 0 | 1073.5737 | 1073.5737 | -1073.5737 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1312.1457 | 1312.1457 | 0 | 8.5 | 0 | 218.6909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1285.9028 | 257.1806 | 2.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 12:00 | 6 | 23 | 12 | 174 | 4164 | 78.98 | 0 | 2790.7724 | 2790.7724 | -2790.7724 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3410.9441 | 3410.9441 | 0 | 8.5 | 0 | 568.4907 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3342.7252 | 668.545 | 6.685% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 13:00 | 6 | 23 | 13 | 174 | 4165 | 80.06 | 0 | 3446.9183 | 3446.9183 | -3446.9183 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4212.9002 | 4212.9002 | 0 | 8.5 | 0 | 702.15 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4128.6422 | 825.7284 | 8.257% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 14:00 | 6 | 23 | 14 | 174 | 4166 | 80.06 | 0 | 3378.3814 | 3378.3814 | -3378.3814 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4129.1328 | 4129.1328 | 0 | 8.5 | 0 | 688.1888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4046.5502 | 809.31 | 8.093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 15:00 | 6 | 23 | 15 | 174 | 4167 | 80.96 | 0 | 3505.2398 | 3505.2398 | -3505.2398 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4284.182 | 4284.182 | 0 | 8.5 | 0 | 714.0303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4198.4984 | 839.6997 | 8.397% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 16:00 | 6 | 23 | 16 | 174 | 4168 | 80.06 | 0 | 3609.2857 | 3609.2857 | -3609.2857 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4411.3492 | 4411.3492 | 0 | 8.5 | 0 | 735.2249 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4323.1222 | 864.6244 | 8.646% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 17:00 | 6 | 23 | 17 | 174 | 4169 | 80.06 | 0 | 3579.5027 | 3579.5027 | -3579.5027 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4374.9477 | 4374.9477 | 0 | 8.5 | 0 | 729.158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4287.4487 | 857.4897 | 8.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 18:00 | 6 | 23 | 18 | 174 | 4170 | 78.98 | 0 | 3132.9953 | 3132.9953 | -3132.9953 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3829.2165 | 3829.2165 | 0 | 8.5 | 0 | 638.2028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3752.6322 | 750.5264 | 7.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 19:00 | 6 | 23 | 19 | 174 | 4171 | 78.08 | 0 | 1421.473 | 1421.473 | -1421.473 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1737.3559 | 1737.3559 | 0 | 8.5 | 0 | 289.5593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1702.6088 | 340.5218 | 3.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 20:00 | 6 | 23 | 20 | 174 | 4172 | 78.08 | 0 | 1214.2788 | 1214.2788 | -1214.2788 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1484.1186 | 1484.1186 | 0 | 8.5 | 0 | 247.3531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1454.4362 | 290.8872 | 2.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 21:00 | 6 | 23 | 21 | 174 | 4173 | 71.96 | 0 | 552.9746 | 552.9746 | -552.9746 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 675.8578 | 675.8578 | 0 | 8.5 | 0 | 112.643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 662.3406 | 132.4681 | 1.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 22:00 | 6 | 23 | 22 | 174 | 4174 | 71.96 | 0 | 277.0561 | 277.0561 | -277.0561 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 338.6241 | 338.6241 | 0 | 8.5 | 0 | 56.4374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 331.8516 | 66.3703 | 0.6637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-23 23:00 | 6 | 23 | 23 | 174 | 4175 | 71.96 | 0 | 110.4154 | 110.4154 | -110.4154 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 134.9521 | 134.9521 | 0 | 8.5 | 0 | 22.492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 132.2531 | 26.4506 | 0.2645% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 | 6 | 24 | 0 | 175 | 4176 | 71.06 | 0 | 21.5786 | 21.5786 | -21.5786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 26.3739 | 26.3739 | 0 | 8.5 | 0 | 4.3956 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 25.8464 | 5.1693 | 0.05169% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 01:00 | 6 | 24 | 1 | 175 | 4177 | 71.96 | 2.2183 | 0 | 0 | 2.2183 | Heating | 1.9573 | 8.5 | 1.9573 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.39146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.9973 | 0 | 0.39945 | 0.003995% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 02:00 | 6 | 24 | 2 | 175 | 4178 | 71.96 | 8.7897 | 0 | 0 | 8.7897 | Heating | 7.7556 | 8.5 | 7.7556 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.9139 | 0 | 1.5828 | 0.01583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 03:00 | 6 | 24 | 3 | 175 | 4179 | 73.04 | 18.1365 | 0 | 0 | 18.1365 | Heating | 16.0028 | 8.5 | 16.0028 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.2006 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.3294 | 0 | 3.2659 | 0.03266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 04:00 | 6 | 24 | 4 | 175 | 4180 | 71.96 | 25.0453 | 0 | 0 | 25.0453 | Heating | 22.0988 | 8.5 | 22.0988 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.4198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.5498 | 0 | 4.51 | 0.0451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 05:00 | 6 | 24 | 5 | 175 | 4181 | 71.96 | 23.6707 | 0 | 0 | 23.6707 | Heating | 20.886 | 8.5 | 20.886 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.1772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.3122 | 0 | 4.2624 | 0.04262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 06:00 | 6 | 24 | 6 | 175 | 4182 | 73.04 | 1696.9179 | 264.5961 | 264.5961 | 1432.3219 | Heating | 1263.8134 | 8.5 | 1263.8134 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.7627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1289.6055 | 0 | 257.9211 | 2.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 07:00 | 6 | 24 | 7 | 175 | 4183 | 75.92 | 492.4131 | 428.7386 | 428.7386 | 63.6745 | Heating | 56.1834 | 8.5 | 56.1834 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.2367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 57.3299 | 0 | 11.466 | 0.1147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 08:00 | 6 | 24 | 8 | 175 | 4184 | 75.92 | 0 | 3007.662 | 3007.662 | -3007.662 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3676.0313 | 3676.0313 | 0 | 8.5 | 0 | 612.6719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3602.5107 | 720.5021 | 7.205% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 09:00 | 6 | 24 | 9 | 175 | 4185 | 78.08 | 0 | 4139.7296 | 4139.7296 | -4139.7296 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5059.6695 | 5059.6695 | 0 | 8.5 | 0 | 843.2782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4958.4761 | 991.6952 | 9.917% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 10:00 | 6 | 24 | 10 | 175 | 4186 | 84.02 | 0 | 5240.5529 | 5240.5529 | -5240.5529 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6405.1202 | 6405.1202 | 0 | 8.5 | 0 | 1067.52 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6277.0178 | 1255.4036 | 12.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 11:00 | 6 | 24 | 11 | 175 | 4187 | 84.02 | 0 | 6601.0358 | 6601.0358 | -6601.0358 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8067.9326 | 8067.9326 | 0 | 8.5 | 0 | 1344.6554 | 30% | 1 | 53.79% | 0% | 0% | 0% | 19.5743 | 0 | 0 | 0 | 19.5743 | 0 | 7906.574 | 1581.3148 | 15.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.8488
2007-06-24 12:00 | 6 | 24 | 12 | 175 | 4188 | 86 | 0 | 7514.1043 | 7514.1043 | -7514.1043 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9183.9052 | 9183.9052 | 0 | 8.5 | 0 | 1530.6509 | 30.61% | 1 | 61.23% | 0% | 0% | 0% | 26.3692 | 0 | 0 | 0 | 26.3692 | 0 | 9000.2271 | 1800.0454 | 18% | 1 | 36% | 0% | 0% | 3.8872 | 0 | 0 | 3.8872 | 30.2563
2007-06-24 13:00 | 6 | 24 | 13 | 175 | 4189 | 77 | 0 | 7479.9139 | 7479.9139 | -7479.9139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9142.1169 | 9142.1169 | 0 | 8.5 | 0 | 1523.6862 | 30.47% | 1 | 60.95% | 0% | 0% | 0% | 26.094 | 0 | 0 | 0 | 26.094 | 0 | 8959.2746 | 1791.8549 | 17.92% | 1 | 35.84% | 0% | 0% | 3.8466 | 0 | 0 | 3.8466 | 29.9406
2007-06-24 14:00 | 6 | 24 | 14 | 175 | 4190 | 77 | 0 | 7148.5149 | 7148.5149 | -7148.5149 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8737.0738 | 8737.0738 | 0 | 8.5 | 0 | 1456.179 | 30% | 1 | 58.25% | 0% | 0% | 0% | 23.5112 | 0 | 0 | 0 | 23.5112 | 0 | 8562.3323 | 1712.4665 | 17.12% | 1 | 34.25% | 0% | 0% | 3.4659 | 0 | 0 | 3.4659 | 26.9771
2007-06-24 15:00 | 6 | 24 | 15 | 175 | 4191 | 78.8 | 0 | 7241.4099 | 7241.4099 | -7241.4099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8850.6121 | 8850.6121 | 0 | 8.5 | 0 | 1475.102 | 30% | 1 | 59% | 0% | 0% | 0% | 24.2199 | 0 | 0 | 0 | 24.2199 | 0 | 8673.5998 | 1734.72 | 17.35% | 1 | 34.69% | 0% | 0% | 3.5703 | 0 | 0 | 3.5703 | 27.7902
2007-06-24 16:00 | 6 | 24 | 16 | 175 | 4192 | 80.06 | 0 | 6548.4915 | 6548.4915 | -6548.4915 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8003.7118 | 8003.7118 | 0 | 8.5 | 0 | 1333.952 | 30% | 1 | 53.36% | 0% | 0% | 0% | 19.2178 | 0 | 0 | 0 | 19.2178 | 0 | 7843.6376 | 1568.7275 | 15.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.4923
2007-06-24 17:00 | 6 | 24 | 17 | 175 | 4193 | 80.06 | 0 | 5272.1153 | 5272.1153 | -5272.1153 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6443.6965 | 6443.6965 | 0 | 8.5 | 0 | 1073.9494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6314.8225 | 1262.9645 | 12.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 18:00 | 6 | 24 | 18 | 175 | 4194 | 80.06 | 0 | 2610.1372 | 2610.1372 | -2610.1372 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3190.1677 | 3190.1677 | 0 | 8.5 | 0 | 531.6946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3126.3644 | 625.2729 | 6.253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 19:00 | 6 | 24 | 19 | 175 | 4195 | 77 | 0 | 1311.6932 | 1311.6932 | -1311.6932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1603.1805 | 1603.1805 | 0 | 8.5 | 0 | 267.1968 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1571.1169 | 314.2234 | 3.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 20:00 | 6 | 24 | 20 | 175 | 4196 | 77 | 0 | 507.1971 | 507.1971 | -507.1971 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 619.9076 | 619.9076 | 0 | 8.5 | 0 | 103.3179 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 607.5095 | 121.5019 | 1.215% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 21:00 | 6 | 24 | 21 | 175 | 4197 | 71.96 | 0 | 349.4148 | 349.4148 | -349.4148 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 427.0625 | 427.0625 | 0 | 8.5 | 0 | 71.1771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 418.5212 | 83.7042 | 0.837% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 22:00 | 6 | 24 | 22 | 175 | 4198 | 69.98 | 1.256 | 1.1826 | 1.1826 | 0.073405 | Heating | 0.064769 | 8.5 | 0.064769 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.012954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.066091 | 0 | 0.013218 | 0.0001322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-24 23:00 | 6 | 24 | 23 | 175 | 4199 | 69.98 | 13.6853 | 0 | 0 | 13.6853 | Heating | 12.0752 | 8.5 | 12.0752 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.3217 | 0 | 2.4643 | 0.02464% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 | 6 | 25 | 0 | 176 | 4200 | 66.92 | 28.779 | 0 | 0 | 28.779 | Heating | 25.3933 | 8.5 | 25.3933 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.0787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 25.9115 | 0 | 5.1823 | 0.05182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 01:00 | 6 | 25 | 1 | 176 | 4201 | 66.02 | 39.5394 | 0 | 0 | 39.5394 | Heating | 34.8877 | 8.5 | 34.8877 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.9775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.5997 | 0 | 7.1199 | 0.0712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 02:00 | 6 | 25 | 2 | 176 | 4202 | 66.02 | 52.5149 | 0 | 0 | 52.5149 | Heating | 46.3367 | 8.5 | 46.3367 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.2673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.2823 | 0 | 9.4565 | 0.09456% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 03:00 | 6 | 25 | 3 | 176 | 4203 | 62.96 | 70.8329 | 0 | 0 | 70.8329 | Heating | 62.4996 | 8.5 | 62.4996 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.4999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 63.7751 | 0 | 12.755 | 0.1276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 04:00 | 6 | 25 | 4 | 176 | 4204 | 60.98 | 99.2133 | 0 | 0 | 99.2133 | Heating | 87.5412 | 8.5 | 87.5412 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.5082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 89.3277 | 0 | 17.8655 | 0.1787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 05:00 | 6 | 25 | 5 | 176 | 4205 | 60.98 | 134.0034 | 0 | 0 | 134.0034 | Heating | 118.2383 | 8.5 | 118.2383 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.6477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 120.6513 | 0 | 24.1303 | 0.2413% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 06:00 | 6 | 25 | 6 | 176 | 4206 | 64.04 | 3183.4532 | 118.3005 | 118.3005 | 3065.1526 | Heating | 2704.5464 | 8.5 | 2704.5464 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 540.9093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2759.7412 | 0 | 551.9482 | 5.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 07:00 | 6 | 25 | 7 | 176 | 4207 | 68 | 1752.5194 | 61.832 | 61.832 | 1690.6874 | Heating | 1491.783 | 8.5 | 1491.783 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 298.3566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1522.2276 | 0 | 304.4455 | 3.044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 08:00 | 6 | 25 | 8 | 176 | 4208 | 68 | 949.3872 | 411.2151 | 411.2151 | 538.1721 | Heating | 474.8578 | 8.5 | 474.8578 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.9716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 484.5487 | 0 | 96.9097 | 0.9691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 09:00 | 6 | 25 | 9 | 176 | 4209 | 73.04 | 124.7628 | 857.6724 | 857.6724 | -732.9096 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1048.2663 | 1048.2663 | 0 | 8.5 | 0 | 174.711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1027.301 | 205.4602 | 2.055% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 10:00 | 6 | 25 | 10 | 176 | 4210 | 75.02 | 15.2579 | 1114.3712 | 1114.3712 | -1099.1133 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1362.0092 | 1362.0092 | 0 | 8.5 | 0 | 227.0015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1334.769 | 266.9538 | 2.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 11:00 | 6 | 25 | 11 | 176 | 4211 | 75.02 | 5.0796 | 1460.9111 | 1460.9111 | -1455.8314 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1785.558 | 1785.558 | 0 | 8.5 | 0 | 297.593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1749.8468 | 349.9694 | 3.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 12:00 | 6 | 25 | 12 | 176 | 4212 | 78.98 | 2.8433 | 1641.527 | 1641.527 | -1638.6837 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2006.3108 | 2006.3108 | 0 | 8.5 | 0 | 334.3851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1966.1845 | 393.2369 | 3.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 13:00 | 6 | 25 | 13 | 176 | 4213 | 80.06 | 1.6505 | 2046.8247 | 2046.8247 | -2045.1742 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2501.6746 | 2501.6746 | 0 | 8.5 | 0 | 416.9458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2451.6411 | 490.3282 | 4.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 14:00 | 6 | 25 | 14 | 176 | 4214 | 80.06 | 0.68154 | 2427.8442 | 2427.8442 | -2427.1627 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2967.3652 | 2967.3652 | 0 | 8.5 | 0 | 494.5609 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2908.0179 | 581.6036 | 5.816% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 15:00 | 6 | 25 | 15 | 176 | 4215 | 80.96 | 0 | 2418.3082 | 2418.3082 | -2418.3082 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2955.71 | 2955.71 | 0 | 8.5 | 0 | 492.6183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2896.5958 | 579.3192 | 5.793% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 16:00 | 6 | 25 | 16 | 176 | 4216 | 80.96 | 0 | 2265.5122 | 2265.5122 | -2265.5122 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2768.9594 | 2768.9594 | 0 | 8.5 | 0 | 461.4932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2713.5802 | 542.716 | 5.427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 17:00 | 6 | 25 | 17 | 176 | 4217 | 80.96 | 0 | 1921.7714 | 1921.7714 | -1921.7714 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2348.8317 | 2348.8317 | 0 | 8.5 | 0 | 391.4719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2301.8551 | 460.371 | 4.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 18:00 | 6 | 25 | 18 | 176 | 4218 | 78.98 | 0 | 648.8376 | 648.8376 | -648.8376 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 793.0237 | 793.0237 | 0 | 8.5 | 0 | 132.1706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 777.1632 | 155.4326 | 1.554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 19:00 | 6 | 25 | 19 | 176 | 4219 | 77 | 0 | 427.1135 | 427.1135 | -427.1135 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 522.0276 | 522.0276 | 0 | 8.5 | 0 | 87.0046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 511.5871 | 102.3174 | 1.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 20:00 | 6 | 25 | 20 | 176 | 4220 | 77 | 0.97089 | 300.6342 | 300.6342 | -299.6633 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 367.4418 | 367.4418 | 0 | 8.5 | 0 | 61.2403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 360.0929 | 72.0186 | 0.7202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 21:00 | 6 | 25 | 21 | 176 | 4221 | 71.06 | 9.3317 | 220.0178 | 220.0178 | -210.6862 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 268.9107 | 268.9107 | 0 | 8.5 | 0 | 44.8185 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 263.5325 | 52.7065 | 0.5271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 22:00 | 6 | 25 | 22 | 176 | 4222 | 69.08 | 29.9886 | 0 | 0 | 29.9886 | Heating | 26.4606 | 8.5 | 26.4606 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.2921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 27.0006 | 0 | 5.4001 | 0.054% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-25 23:00 | 6 | 25 | 23 | 176 | 4223 | 69.08 | 57.4627 | 0 | 0 | 57.4627 | Heating | 50.7024 | 8.5 | 50.7024 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.1405 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 51.7371 | 0 | 10.3474 | 0.1035% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 | 6 | 26 | 0 | 177 | 4224 | 64.94 | 95.5705 | 0 | 0 | 95.5705 | Heating | 84.3269 | 8.5 | 84.3269 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.8654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 86.0478 | 0 | 17.2096 | 0.1721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 01:00 | 6 | 26 | 1 | 177 | 4225 | 64.04 | 136.4389 | 0 | 0 | 136.4389 | Heating | 120.3873 | 8.5 | 120.3873 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.0775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 122.8442 | 0 | 24.5688 | 0.2457% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 02:00 | 6 | 26 | 2 | 177 | 4226 | 64.04 | 230.0499 | 0 | 0 | 230.0499 | Heating | 202.9852 | 8.5 | 202.9852 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 207.1278 | 0 | 41.4256 | 0.4143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 03:00 | 6 | 26 | 3 | 177 | 4227 | 62.96 | 308.0016 | 0 | 0 | 308.0016 | Heating | 271.7661 | 8.5 | 271.7661 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.3532 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 277.3123 | 0 | 55.4625 | 0.5546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 04:00 | 6 | 26 | 4 | 177 | 4228 | 60.98 | 306.4423 | 0 | 0 | 306.4423 | Heating | 270.3903 | 8.5 | 270.3903 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.0781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 275.9084 | 0 | 55.1817 | 0.5518% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 05:00 | 6 | 26 | 5 | 177 | 4229 | 60.98 | 297.071 | 0 | 0 | 297.071 | Heating | 262.1214 | 8.5 | 262.1214 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.4243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 267.4709 | 0 | 53.4942 | 0.5349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 06:00 | 6 | 26 | 6 | 177 | 4230 | 64.04 | 3968.4865 | 56.0687 | 56.0687 | 3912.4178 | Heating | 3452.1334 | 8.5 | 3452.1334 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 690.4267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3522.5851 | 0 | 704.517 | 7.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 07:00 | 6 | 26 | 7 | 177 | 4231 | 68 | 2177.8228 | 2.4889 | 2.4889 | 2175.3339 | Heating | 1919.4123 | 8.5 | 1919.4123 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 383.8825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1958.584 | 0 | 391.7168 | 3.917% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 08:00 | 6 | 26 | 8 | 177 | 4232 | 68 | 971.9706 | 281.2853 | 281.2853 | 690.6853 | Heating | 609.4282 | 8.5 | 609.4282 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.8856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 621.8656 | 0 | 124.3731 | 1.244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 09:00 | 6 | 26 | 9 | 177 | 4233 | 71.06 | 30.6519 | 802.1304 | 802.1304 | -771.4785 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 980.3816 | 980.3816 | 0 | 8.5 | 0 | 163.3969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 960.774 | 192.1548 | 1.922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 10:00 | 6 | 26 | 10 | 177 | 4234 | 73.94 | 3.9522 | 1731.0686 | 1731.0686 | -1727.1164 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2115.7505 | 2115.7505 | 0 | 8.5 | 0 | 352.6251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2073.4355 | 414.6871 | 4.147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 11:00 | 6 | 26 | 11 | 177 | 4235 | 73.94 | 0 | 3106.035 | 3106.035 | -3106.035 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3796.265 | 3796.265 | 0 | 8.5 | 0 | 632.7108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3720.3397 | 744.0679 | 7.441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 12:00 | 6 | 26 | 12 | 177 | 4236 | 78.08 | 0 | 4060.7119 | 4060.7119 | -4060.7119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4963.0924 | 4963.0924 | 0 | 8.5 | 0 | 827.1821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4863.8305 | 972.7661 | 9.728% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 13:00 | 6 | 26 | 13 | 177 | 4237 | 75.92 | 0 | 4778.7506 | 4778.7506 | -4778.7506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5840.6951 | 5840.6951 | 0 | 8.5 | 0 | 973.4492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5723.8812 | 1144.7762 | 11.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 14:00 | 6 | 26 | 14 | 177 | 4238 | 75.92 | 0 | 5157.9171 | 5157.9171 | -5157.9171 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6304.1209 | 6304.1209 | 0 | 8.5 | 0 | 1050.6868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6178.0385 | 1235.6077 | 12.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 15:00 | 6 | 26 | 15 | 177 | 4239 | 71.96 | 0 | 5098.1061 | 5098.1061 | -5098.1061 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6231.0185 | 6231.0185 | 0 | 8.5 | 0 | 1038.5031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6106.3981 | 1221.2796 | 12.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 16:00 | 6 | 26 | 16 | 177 | 4240 | 71.06 | 0 | 4789.92 | 4789.92 | -4789.92 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5854.3467 | 5854.3467 | 0 | 8.5 | 0 | 975.7244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5737.2597 | 1147.4519 | 11.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 17:00 | 6 | 26 | 17 | 177 | 4241 | 71.06 | 0 | 4162.5568 | 4162.5568 | -4162.5568 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5087.5694 | 5087.5694 | 0 | 8.5 | 0 | 847.9282 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4985.818 | 997.1636 | 9.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 18:00 | 6 | 26 | 18 | 177 | 4242 | 71.06 | 0 | 2293.2277 | 2293.2277 | -2293.2277 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2802.8338 | 2802.8338 | 0 | 8.5 | 0 | 467.139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2746.7771 | 549.3554 | 5.494% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 19:00 | 6 | 26 | 19 | 177 | 4243 | 69.08 | 0 | 1584.9524 | 1584.9524 | -1584.9524 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1937.1641 | 1937.1641 | 0 | 8.5 | 0 | 322.8607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1898.4208 | 379.6842 | 3.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 20:00 | 6 | 26 | 20 | 177 | 4244 | 69.08 | 0 | 599.3874 | 599.3874 | -599.3874 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 732.5846 | 732.5846 | 0 | 8.5 | 0 | 122.0974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 717.9329 | 143.5866 | 1.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 21:00 | 6 | 26 | 21 | 177 | 4245 | 68 | 0 | 287.7384 | 287.7384 | -287.7384 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 351.6803 | 351.6803 | 0 | 8.5 | 0 | 58.6134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 344.6466 | 68.9293 | 0.6893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-26 22:00 | 6 | 26 | 22 | 177 | 4246 | 66.92 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-06-26 23:00 | 6 | 26 | 23 | 177 | 4247 | 66.92 | 2.1168 | 0 | 0 | 2.1168 | Heating | 1.8678 | 8.5 | 1.8678 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.37355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.9059 | 0 | 0.38118 | 0.003812% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 | 6 | 27 | 0 | 178 | 4248 | 66.92 | 4.6544 | 0 | 0 | 4.6544 | Heating | 4.1068 | 8.5 | 4.1068 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.82136 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.1906 | 0 | 0.83812 | 0.008381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 01:00 | 6 | 27 | 1 | 178 | 4249 | 64.94 | 9.272 | 0 | 0 | 9.272 | Heating | 8.1812 | 8.5 | 8.1812 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.3482 | 0 | 1.6696 | 0.0167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 02:00 | 6 | 27 | 2 | 178 | 4250 | 64.94 | 16.8514 | 0 | 0 | 16.8514 | Heating | 14.8689 | 8.5 | 14.8689 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.9738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.1723 | 0 | 3.0345 | 0.03034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 03:00 | 6 | 27 | 3 | 178 | 4251 | 62.06 | 24.1423 | 0 | 0 | 24.1423 | Heating | 21.302 | 8.5 | 21.302 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.2604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.7367 | 0 | 4.3473 | 0.04347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 04:00 | 6 | 27 | 4 | 178 | 4252 | 62.06 | 31.3957 | 0 | 0 | 31.3957 | Heating | 27.7021 | 8.5 | 27.7021 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.5404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 28.2674 | 0 | 5.6535 | 0.05653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 05:00 | 6 | 27 | 5 | 178 | 4253 | 62.06 | 29.7427 | 0 | 0 | 29.7427 | Heating | 26.2435 | 8.5 | 26.2435 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.2487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 26.7791 | 0 | 5.3558 | 0.05356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 06:00 | 6 | 27 | 6 | 178 | 4254 | 64.94 | 1501.3761 | 229.479 | 229.479 | 1271.8971 | Heating | 1122.2622 | 8.5 | 1122.2622 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.4524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1145.1655 | 0 | 229.0331 | 2.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 07:00 | 6 | 27 | 7 | 178 | 4255 | 66.92 | 505.0837 | 318.9988 | 318.9988 | 186.0849 | Heating | 164.1926 | 8.5 | 164.1926 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.8385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 167.5434 | 0 | 33.5087 | 0.3351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 08:00 | 6 | 27 | 8 | 178 | 4256 | 66.92 | 0.16285 | 2509.9064 | 2509.9064 | -2509.7436 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3067.6634 | 3067.6634 | 0 | 8.5 | 0 | 511.2772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3006.3102 | 601.262 | 6.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 09:00 | 6 | 27 | 9 | 178 | 4257 | 68 | 0 | 3915.5754 | 3915.5754 | -3915.5754 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4785.7033 | 4785.7033 | 0 | 8.5 | 0 | 797.6172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4689.9892 | 937.9978 | 9.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 10:00 | 6 | 27 | 10 | 178 | 4258 | 71.96 | 0 | 6036.2459 | 6036.2459 | -6036.2459 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7377.6339 | 7377.6339 | 0 | 8.5 | 0 | 1229.6057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7230.0813 | 1446.0163 | 14.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 11:00 | 6 | 27 | 11 | 178 | 4259 | 71.96 | 0 | 8012.9981 | 8012.9981 | -8012.9981 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9793.6644 | 9793.6644 | 0 | 8.5 | 0 | 1632.2774 | 32.65% | 1 | 65.29% | 0% | 0% | 0% | 30.5708 | 0 | 0 | 0 | 30.5708 | 0 | 9597.7911 | 1919.5582 | 19.2% | 1 | 38.39% | 0% | 0% | 4.5066 | 0 | 0 | 4.5066 | 35.0774
2007-06-27 12:00 | 6 | 27 | 12 | 178 | 4260 | 78.98 | 0 | 8977.9139 | 8977.9139 | -8977.9139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10973.0059 | 10973.0059 | 0 | 8.5 | 0 | 1828.8343 | 36.58% | 1 | 73.15% | 0% | 0% | 0% | 39.7084 | 0 | 0 | 0 | 39.7084 | 0 | 10753.5458 | 2150.7092 | 21.51% | 1 | 43.01% | 0% | 0% | 5.8536 | 0 | 0 | 5.8536 | 45.5619
2007-06-27 13:00 | 6 | 27 | 13 | 178 | 4261 | 82.04 | 0 | 9645.3492 | 9645.3492 | -9645.3492 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11788.7602 | 11788.7602 | 0 | 8.5 | 0 | 1964.7934 | 39.3% | 1 | 78.59% | 0% | 0% | 0% | 46.8285 | 0 | 0 | 0 | 46.8285 | 0 | 11552.985 | 2310.597 | 23.11% | 1 | 46.21% | 0% | 0% | 6.9032 | 0 | 0 | 6.9032 | 53.7316
2007-06-27 14:00 | 6 | 27 | 14 | 178 | 4262 | 82.04 | 0 | 10689.2838 | 10689.2838 | -10689.2838 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13064.6802 | 13064.6802 | 0 | 8.5 | 0 | 2177.4467 | 43.55% | 1 | 87.1% | 0% | 0% | 0% | 59.3144 | 0 | 0 | 0 | 59.3144 | 0 | 12803.3866 | 2560.6773 | 25.61% | 1 | 51.21% | 0% | 0% | 8.7438 | 0 | 0 | 8.7438 | 68.0582
2007-06-27 15:00 | 6 | 27 | 15 | 178 | 4263 | 82.04 | 0 | 11592.8487 | 11592.8487 | -11592.8487 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14169.0373 | 14169.0373 | 0 | 8.5 | 0 | 2361.5062 | 47.23% | 1 | 94.46% | 0% | 0% | 0% | 71.4852 | 0 | 0 | 0 | 71.4852 | 0 | 13885.6565 | 2777.1313 | 27.77% | 1 | 55.54% | 0% | 0% | 10.5379 | 0 | 0 | 10.5379 | 82.0231
2007-06-27 16:00 | 6 | 27 | 16 | 178 | 4264 | 80.06 | 0 | 11972.0873 | 11972.0873 | -11972.0873 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14632.5512 | 14632.5512 | 0 | 8.5 | 0 | 2438.7585 | 48.78% | 1 | 97.55% | 0% | 0% | 0% | 76.9785 | 0 | 0 | 0 | 76.9785 | 0 | 14339.9002 | 2867.98 | 28.68% | 1 | 57.36% | 0% | 0% | 11.3477 | 0 | 0 | 11.3477 | 88.3262
2007-06-27 17:00 | 6 | 27 | 17 | 178 | 4265 | 80.06 | 0 | 10636.1917 | 10636.1917 | -10636.1917 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12999.7899 | 12999.7899 | 0 | 8.5 | 0 | 2166.6316 | 43.33% | 1 | 86.67% | 0% | 0% | 0% | 58.639 | 0 | 0 | 0 | 58.639 | 0 | 12739.7941 | 2547.9588 | 25.48% | 1 | 50.96% | 0% | 0% | 8.6442 | 0 | 0 | 8.6442 | 67.2832
2007-06-27 18:00 | 6 | 27 | 18 | 178 | 4266 | 78.98 | 0 | 6241.5728 | 6241.5728 | -6241.5728 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7628.589 | 7628.589 | 0 | 8.5 | 0 | 1271.4315 | 30% | 1 | 50.86% | 0% | 0% | 0% | 17.209 | 0 | 0 | 0 | 17.209 | 0 | 7476.0172 | 1495.2034 | 14.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.4835
2007-06-27 19:00 | 6 | 27 | 19 | 178 | 4267 | 78.08 | 0 | 5079.8255 | 5079.8255 | -5079.8255 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6208.6756 | 6208.6756 | 0 | 8.5 | 0 | 1034.7793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6084.5021 | 1216.9004 | 12.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 20:00 | 6 | 27 | 20 | 178 | 4268 | 78.08 | 0 | 4115.621 | 4115.621 | -4115.621 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5030.2035 | 5030.2035 | 0 | 8.5 | 0 | 838.3672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4929.5994 | 985.9199 | 9.859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 21:00 | 6 | 27 | 21 | 178 | 4269 | 75.92 | 0 | 1974.0202 | 1974.0202 | -1974.0202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2412.6913 | 2412.6913 | 0 | 8.5 | 0 | 402.1152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2364.4375 | 472.8875 | 4.729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 22:00 | 6 | 27 | 22 | 178 | 4270 | 75.02 | 0 | 600.1472 | 600.1472 | -600.1472 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 733.5133 | 733.5133 | 0 | 8.5 | 0 | 122.2522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 718.843 | 143.7686 | 1.438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-27 23:00 | 6 | 27 | 23 | 178 | 4271 | 75.02 | 0 | 661.0786 | 661.0786 | -661.0786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 807.9849 | 807.9849 | 0 | 8.5 | 0 | 134.6641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 791.8252 | 158.365 | 1.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 | 6 | 28 | 0 | 179 | 4272 | 75.02 | 0 | 570.7843 | 570.7843 | -570.7843 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 697.6252 | 697.6252 | 0 | 8.5 | 0 | 116.2709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 683.6727 | 136.7345 | 1.367% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 01:00 | 6 | 28 | 1 | 179 | 4273 | 75.02 | 0 | 412.0556 | 412.0556 | -412.0556 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 503.6235 | 503.6235 | 0 | 8.5 | 0 | 83.9372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 493.551 | 98.7102 | 0.9871% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 02:00 | 6 | 28 | 2 | 179 | 4274 | 75.02 | 0 | 465.2652 | 465.2652 | -465.2652 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 568.6575 | 568.6575 | 0 | 8.5 | 0 | 94.7763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 557.2844 | 111.4569 | 1.115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 03:00 | 6 | 28 | 3 | 179 | 4275 | 75.92 | 0 | 500.731 | 500.731 | -500.731 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 612.0046 | 612.0046 | 0 | 8.5 | 0 | 102.0008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 599.7645 | 119.9529 | 1.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 04:00 | 6 | 28 | 4 | 179 | 4276 | 75.02 | 0 | 363.33 | 363.33 | -363.33 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 444.07 | 444.07 | 0 | 8.5 | 0 | 74.0117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 435.1886 | 87.0377 | 0.8704% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 05:00 | 6 | 28 | 5 | 179 | 4277 | 75.02 | 0 | 165.9646 | 165.9646 | -165.9646 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 202.8456 | 202.8456 | 0 | 8.5 | 0 | 33.8076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 198.7887 | 39.7577 | 0.3976% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 06:00 | 6 | 28 | 6 | 179 | 4278 | 75.02 | 38.6985 | 2223.5 | 2223.5 | -2184.8015 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2717.6111 | 2717.6111 | 0 | 8.5 | 0 | 452.9352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2663.2589 | 532.6518 | 5.327% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 07:00 | 6 | 28 | 7 | 179 | 4279 | 77 | 0 | 3269.3551 | 3269.3551 | -3269.3551 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3995.8784 | 3995.8784 | 0 | 8.5 | 0 | 665.9797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3915.9609 | 783.1922 | 7.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 08:00 | 6 | 28 | 8 | 179 | 4280 | 77 | 0 | 5300.1368 | 5300.1368 | -5300.1368 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6477.9449 | 6477.9449 | 0 | 8.5 | 0 | 1079.6575 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6348.386 | 1269.6772 | 12.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 09:00 | 6 | 28 | 9 | 179 | 4281 | 78.08 | 0 | 7301.8188 | 7301.8188 | -7301.8188 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8924.4452 | 8924.4452 | 0 | 8.5 | 0 | 1487.4075 | 30% | 1 | 59.5% | 0% | 0% | 0% | 24.6871 | 0 | 0 | 0 | 24.6871 | 0 | 8745.9563 | 1749.1913 | 17.49% | 1 | 34.98% | 0% | 0% | 3.6392 | 0 | 0 | 3.6392 | 28.3263
2007-06-28 10:00 | 6 | 28 | 10 | 179 | 4282 | 82.94 | 0 | 9657.2461 | 9657.2461 | -9657.2461 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11803.3008 | 11803.3008 | 0 | 8.5 | 0 | 1967.2168 | 39.34% | 1 | 78.69% | 0% | 0% | 0% | 46.9614 | 0 | 0 | 0 | 46.9614 | 0 | 11567.2347 | 2313.4469 | 23.13% | 1 | 46.27% | 0% | 0% | 6.9228 | 0 | 0 | 6.9228 | 53.8842
2007-06-28 11:00 | 6 | 28 | 11 | 179 | 4283 | 82.94 | 0 | 11446.7831 | 11446.7831 | -11446.7831 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13990.5127 | 13990.5127 | 0 | 8.5 | 0 | 2331.7521 | 46.64% | 1 | 93.27% | 0% | 0% | 0% | 69.4305 | 0 | 0 | 0 | 69.4305 | 0 | 13710.7024 | 2742.1405 | 27.42% | 1 | 54.84% | 0% | 0% | 10.235 | 0 | 0 | 10.235 | 79.6655
2007-06-28 12:00 | 6 | 28 | 12 | 179 | 4284 | 82.94 | 0 | 12664.5441 | 12664.5441 | -12664.5441 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15478.8873 | 15478.8873 | 0 | 8.5 | 0 | 2579.8145 | 51.6% | 2 | 51.6% | 51.6% | 0% | 0% | 17.7896 | 17.7896 | 0 | 0 | 35.5791 | 0 | 15169.3095 | 3033.8619 | 30.34% | 1 | 60.68% | 0% | 0% | 12.9143 | 0 | 0 | 12.9143 | 48.4935
2007-06-28 13:00 | 6 | 28 | 13 | 179 | 4285 | 80.96 | 0 | 13631.119 | 13631.119 | -13631.119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16660.2566 | 16660.2566 | 0 | 8.5 | 0 | 2776.7094 | 55.53% | 2 | 55.53% | 55.53% | 0% | 0% | 21.0684 | 21.0684 | 0 | 0 | 42.1368 | 0 | 16327.0515 | 3265.4103 | 32.65% | 1 | 65.31% | 0% | 0% | 15.2946 | 0 | 0 | 15.2946 | 57.4315
2007-06-28 14:00 | 6 | 28 | 14 | 179 | 4286 | 80.96 | 0 | 14362.8101 | 14362.8101 | -14362.8101 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17554.5457 | 17554.5457 | 0 | 8.5 | 0 | 2925.7576 | 58.52% | 2 | 58.52% | 58.52% | 0% | 0% | 23.7608 | 23.7608 | 0 | 0 | 47.5215 | 0 | 17203.4548 | 3440.691 | 34.41% | 1 | 34.41% | 34.41% | 0% | 3.5027 | 3.5027 | 0 | 7.0053 | 54.5268
2007-06-28 15:00 | 6 | 28 | 15 | 179 | 4287 | 80.96 | 0 | 14675.655 | 14675.655 | -14675.655 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17936.9117 | 17936.9117 | 0 | 8.5 | 0 | 2989.4853 | 59.79% | 2 | 59.79% | 59.79% | 0% | 0% | 24.968 | 24.968 | 0 | 0 | 49.936 | 0 | 17578.1735 | 3515.6347 | 35.16% | 1 | 35.16% | 35.16% | 0% | 3.6806 | 3.6806 | 0 | 7.3613 | 57.2973
2007-06-28 16:00 | 6 | 28 | 16 | 179 | 4288 | 82.94 | 0 | 14433.014 | 14433.014 | -14433.014 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17640.3505 | 17640.3505 | 0 | 8.5 | 0 | 2940.0584 | 58.8% | 2 | 58.8% | 58.8% | 0% | 0% | 24.0287 | 24.0287 | 0 | 0 | 48.0575 | 0 | 17287.5435 | 3457.5087 | 34.58% | 1 | 34.58% | 34.58% | 0% | 3.5422 | 3.5422 | 0 | 7.0843 | 55.1418
2007-06-28 17:00 | 6 | 28 | 17 | 179 | 4289 | 82.94 | 0 | 13899.0703 | 13899.0703 | -13899.0703 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16987.7526 | 16987.7526 | 0 | 8.5 | 0 | 2831.2921 | 56.63% | 2 | 56.63% | 56.63% | 0% | 0% | 22.0332 | 22.0332 | 0 | 0 | 44.0663 | 0 | 16647.9975 | 3329.5995 | 33.3% | 1 | 33.3% | 33.3% | 0% | 3.248 | 3.248 | 0 | 6.496 | 50.5623
2007-06-28 18:00 | 6 | 28 | 18 | 179 | 4290 | 78.98 | 0 | 8890.5276 | 8890.5276 | -8890.5276 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10866.2004 | 10866.2004 | 0 | 8.5 | 0 | 1811.0334 | 36.22% | 1 | 72.44% | 0% | 0% | 0% | 38.825 | 0 | 0 | 0 | 38.825 | 0 | 10648.8763 | 2129.7753 | 21.3% | 1 | 42.6% | 0% | 0% | 5.7233 | 0 | 0 | 5.7233 | 44.5484
2007-06-28 19:00 | 6 | 28 | 19 | 179 | 4291 | 71.6 | 0 | 7446.4406 | 7446.4406 | -7446.4406 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9101.2052 | 9101.2052 | 0 | 8.5 | 0 | 1516.8675 | 30.34% | 1 | 60.67% | 0% | 0% | 0% | 25.8262 | 0 | 0 | 0 | 25.8262 | 0 | 8919.1811 | 1783.8362 | 17.84% | 1 | 35.68% | 0% | 0% | 3.8071 | 0 | 0 | 3.8071 | 29.6333
2007-06-28 20:00 | 6 | 28 | 20 | 179 | 4292 | 73.04 | 0 | 6215.6148 | 6215.6148 | -6215.6148 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7596.8626 | 7596.8626 | 0 | 8.5 | 0 | 1266.1438 | 30% | 1 | 50.65% | 0% | 0% | 0% | 17.0448 | 0 | 0 | 0 | 17.0448 | 0 | 7444.9253 | 1488.9851 | 14.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3193
2007-06-28 21:00 | 6 | 28 | 21 | 179 | 4293 | 71.06 | 0 | 2851.5347 | 2851.5347 | -2851.5347 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3485.2091 | 3485.2091 | 0 | 8.5 | 0 | 580.8682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3415.5049 | 683.101 | 6.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 22:00 | 6 | 28 | 22 | 179 | 4294 | 69.98 | 0 | 952.9505 | 952.9505 | -952.9505 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1164.7172 | 1164.7172 | 0 | 8.5 | 0 | 194.1195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1141.4229 | 228.2846 | 2.283% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-28 23:00 | 6 | 28 | 23 | 179 | 4295 | 69.98 | 0 | 799.9094 | 799.9094 | -799.9094 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 977.6671 | 977.6671 | 0 | 8.5 | 0 | 162.9445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 958.1137 | 191.6227 | 1.916% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 | 6 | 29 | 0 | 180 | 4296 | 71.06 | 0 | 667.9509 | 667.9509 | -667.9509 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 816.3845 | 816.3845 | 0 | 8.5 | 0 | 136.0641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 800.0568 | 160.0114 | 1.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 01:00 | 6 | 29 | 1 | 180 | 4297 | 69.98 | 0 | 631.5466 | 631.5466 | -631.5466 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 771.8903 | 771.8903 | 0 | 8.5 | 0 | 128.6484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 756.4525 | 151.2905 | 1.513% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 02:00 | 6 | 29 | 2 | 180 | 4298 | 69.98 | 0 | 342.2445 | 342.2445 | -342.2445 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 418.2988 | 418.2988 | 0 | 8.5 | 0 | 69.7165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 409.9328 | 81.9866 | 0.8199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 03:00 | 6 | 29 | 3 | 180 | 4299 | 69.08 | 0 | 229.8001 | 229.8001 | -229.8001 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 280.8667 | 280.8667 | 0 | 8.5 | 0 | 46.8111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 275.2494 | 55.0499 | 0.5505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 04:00 | 6 | 29 | 4 | 180 | 4300 | 68 | 0 | 99.0104 | 99.0104 | -99.0104 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 121.0128 | 121.0128 | 0 | 8.5 | 0 | 20.1688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 118.5925 | 23.7185 | 0.2372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 05:00 | 6 | 29 | 5 | 180 | 4301 | 68 | 0 | 21.0367 | 21.0367 | -21.0367 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 25.7115 | 25.7115 | 0 | 8.5 | 0 | 4.2853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 25.1973 | 5.0395 | 0.05039% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 06:00 | 6 | 29 | 6 | 180 | 4302 | 68 | 625.3875 | 623.1905 | 623.1905 | 2.1971 | Heating | 1.9386 | 8.5 | 1.9386 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.38772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.9782 | 0 | 0.39563 | 0.003956% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 07:00 | 6 | 29 | 7 | 180 | 4303 | 71.06 | 3.4685 | 872.2324 | 872.2324 | -868.7639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1066.0618 | 1066.0618 | 0 | 8.5 | 0 | 177.677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1044.7406 | 208.9481 | 2.089% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 08:00 | 6 | 29 | 8 | 180 | 4304 | 71.06 | 0 | 1849.3243 | 1849.3243 | -1849.3243 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2260.2853 | 2260.2853 | 0 | 8.5 | 0 | 376.7142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2215.0796 | 443.0159 | 4.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 09:00 | 6 | 29 | 9 | 180 | 4305 | 73.94 | 0 | 2283.2584 | 2283.2584 | -2283.2584 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2790.6491 | 2790.6491 | 0 | 8.5 | 0 | 465.1082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2734.8361 | 546.9672 | 5.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 10:00 | 6 | 29 | 10 | 180 | 4306 | 75.02 | 0 | 3918.0838 | 3918.0838 | -3918.0838 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4788.7691 | 4788.7691 | 0 | 8.5 | 0 | 798.1282 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4692.9938 | 938.5988 | 9.386% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 11:00 | 6 | 29 | 11 | 180 | 4307 | 75.02 | 0 | 5018.874 | 5018.874 | -5018.874 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6134.1794 | 6134.1794 | 0 | 8.5 | 0 | 1022.3632 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6011.4958 | 1202.2992 | 12.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 12:00 | 6 | 29 | 12 | 180 | 4308 | 75.02 | 0 | 5419.1471 | 5419.1471 | -5419.1471 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6623.402 | 6623.402 | 0 | 8.5 | 0 | 1103.9003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6490.9339 | 1298.1868 | 12.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 13:00 | 6 | 29 | 13 | 180 | 4309 | 75.92 | 0 | 5667.3796 | 5667.3796 | -5667.3796 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6926.7973 | 6926.7973 | 0 | 8.5 | 0 | 1154.4662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6788.2614 | 1357.6523 | 13.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 14:00 | 6 | 29 | 14 | 180 | 4310 | 75.92 | 0 | 5759.913 | 5759.913 | -5759.913 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7039.8937 | 7039.8937 | 0 | 8.5 | 0 | 1173.3156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6899.0958 | 1379.8192 | 13.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 15:00 | 6 | 29 | 15 | 180 | 4311 | 75.92 | 0 | 5985.3486 | 5985.3486 | -5985.3486 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7315.4261 | 7315.4261 | 0 | 8.5 | 0 | 1219.2377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7169.1176 | 1433.8235 | 14.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 16:00 | 6 | 29 | 16 | 180 | 4312 | 75.02 | 0 | 6087.5749 | 6087.5749 | -6087.5749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7440.3694 | 7440.3694 | 0 | 8.5 | 0 | 1240.0616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7291.562 | 1458.3124 | 14.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 17:00 | 6 | 29 | 17 | 180 | 4313 | 75.02 | 0 | 5533.4064 | 5533.4064 | -5533.4064 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6763.0522 | 6763.0522 | 0 | 8.5 | 0 | 1127.1754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6627.7912 | 1325.5582 | 13.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 18:00 | 6 | 29 | 18 | 180 | 4314 | 71.06 | 0 | 3258.9085 | 3258.9085 | -3258.9085 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3983.1104 | 3983.1104 | 0 | 8.5 | 0 | 663.8517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3903.4482 | 780.6896 | 7.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 19:00 | 6 | 29 | 19 | 180 | 4315 | 68 | 0 | 2221.858 | 2221.858 | -2221.858 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2715.6042 | 2715.6042 | 0 | 8.5 | 0 | 452.6007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2661.2921 | 532.2584 | 5.323% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 20:00 | 6 | 29 | 20 | 180 | 4316 | 68 | 0 | 616.6877 | 616.6877 | -616.6877 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 753.7294 | 753.7294 | 0 | 8.5 | 0 | 125.6216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 738.6548 | 147.731 | 1.477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 21:00 | 6 | 29 | 21 | 180 | 4317 | 62.06 | 0 | 222.5972 | 222.5972 | -222.5972 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 272.0632 | 272.0632 | 0 | 8.5 | 0 | 45.3439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 266.622 | 53.3244 | 0.5332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 22:00 | 6 | 29 | 22 | 180 | 4318 | 60.98 | 0 | 67.55 | 67.55 | -67.55 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 82.5611 | 82.5611 | 0 | 8.5 | 0 | 13.7602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 80.9099 | 16.182 | 0.1618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-29 23:00 | 6 | 29 | 23 | 180 | 4319 | 60.98 | 3.6178 | 2.0686 | 2.0686 | 1.5492 | Heating | 1.367 | 8.5 | 1.367 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.27339 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.3949 | 0 | 0.27897 | 0.00279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 | 6 | 30 | 0 | 181 | 4320 | 57.02 | 8.1924 | 0 | 0 | 8.1924 | Heating | 7.2286 | 8.5 | 7.2286 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.3761 | 0 | 1.4752 | 0.01475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 01:00 | 6 | 30 | 1 | 181 | 4321 | 55.04 | 12.5795 | 0 | 0 | 12.5795 | Heating | 11.0995 | 8.5 | 11.0995 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.2199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.3261 | 0 | 2.2652 | 0.02265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 02:00 | 6 | 30 | 2 | 181 | 4322 | 55.04 | 25.9986 | 0 | 0 | 25.9986 | Heating | 22.9399 | 8.5 | 22.9399 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.4081 | 0 | 4.6816 | 0.04682% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 03:00 | 6 | 30 | 3 | 181 | 4323 | 53.96 | 41.008 | 0 | 0 | 41.008 | Heating | 36.1836 | 8.5 | 36.1836 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.2367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 36.922 | 0 | 7.3844 | 0.07384% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 04:00 | 6 | 30 | 4 | 181 | 4324 | 51.08 | 55.3838 | 0 | 0 | 55.3838 | Heating | 48.8681 | 8.5 | 48.8681 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.7736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 49.8654 | 0 | 9.9731 | 0.09973% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 05:00 | 6 | 30 | 5 | 181 | 4325 | 51.08 | 62.7453 | 0 | 0 | 62.7453 | Heating | 55.3635 | 8.5 | 55.3635 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.0727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.4933 | 0 | 11.2987 | 0.113% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 06:00 | 6 | 30 | 6 | 181 | 4326 | 55.94 | 30.8994 | 0 | 0 | 30.8994 | Heating | 27.2642 | 8.5 | 27.2642 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.4528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 27.8206 | 0 | 5.5641 | 0.05564% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 07:00 | 6 | 30 | 7 | 181 | 4327 | 59 | 6.729 | 0 | 0 | 6.729 | Heating | 5.9374 | 8.5 | 5.9374 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1875 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.0586 | 0 | 1.2117 | 0.01212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 08:00 | 6 | 30 | 8 | 181 | 4328 | 59 | 1385.8402 | 0 | 0 | 1385.8402 | Heating | 1222.8002 | 8.5 | 1222.8002 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 244.56 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1247.7553 | 0 | 249.5511 | 2.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 09:00 | 6 | 30 | 9 | 181 | 4329 | 62.96 | 437.2543 | 5.5217 | 5.5217 | 431.7327 | Heating | 380.9406 | 8.5 | 380.9406 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.1881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 388.7149 | 0 | 77.743 | 0.7774% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 10:00 | 6 | 30 | 10 | 181 | 4330 | 64.04 | 0 | 20.5285 | 20.5285 | -20.5285 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 25.0904 | 25.0904 | 0 | 8.5 | 0 | 4.1817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 24.5886 | 4.9177 | 0.04918% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 11:00 | 6 | 30 | 11 | 181 | 4331 | 64.04 | 0 | 141.7293 | 141.7293 | -141.7293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 173.2247 | 173.2247 | 0 | 8.5 | 0 | 28.8708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 169.7602 | 33.952 | 0.3395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 12:00 | 6 | 30 | 12 | 181 | 4332 | 68 | 0 | 550.6436 | 550.6436 | -550.6436 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 673.0088 | 673.0088 | 0 | 8.5 | 0 | 112.1681 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 659.5486 | 131.9097 | 1.319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 13:00 | 6 | 30 | 13 | 181 | 4333 | 69.08 | 0 | 1333.2809 | 1333.2809 | -1333.2809 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1629.5655 | 1629.5655 | 0 | 8.5 | 0 | 271.5943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1596.9742 | 319.3948 | 3.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 14:00 | 6 | 30 | 14 | 181 | 4334 | 69.08 | 0 | 1733.515 | 1733.515 | -1733.515 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2118.7405 | 2118.7405 | 0 | 8.5 | 0 | 353.1234 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2076.3657 | 415.2731 | 4.153% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 15:00 | 6 | 30 | 15 | 181 | 4335 | 69.98 | 0 | 1594.4873 | 1594.4873 | -1594.4873 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1948.8178 | 1948.8178 | 0 | 8.5 | 0 | 324.803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1909.8415 | 381.9683 | 3.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 16:00 | 6 | 30 | 16 | 181 | 4336 | 69.98 | 0 | 2128.5702 | 2128.5702 | -2128.5702 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2601.5858 | 2601.5858 | 0 | 8.5 | 0 | 433.5976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2549.5541 | 509.9108 | 5.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 17:00 | 6 | 30 | 17 | 181 | 4337 | 69.98 | 0 | 1949.5429 | 1949.5429 | -1949.5429 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2382.7746 | 2382.7746 | 0 | 8.5 | 0 | 397.1291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2335.1192 | 467.0238 | 4.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 18:00 | 6 | 30 | 18 | 181 | 4338 | 68 | 0 | 934.2691 | 934.2691 | -934.2691 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1141.8845 | 1141.8845 | 0 | 8.5 | 0 | 190.3141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1119.0468 | 223.8094 | 2.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 19:00 | 6 | 30 | 19 | 181 | 4339 | 61.88 | 0 | 386.7399 | 386.7399 | -386.7399 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 472.682 | 472.682 | 0 | 8.5 | 0 | 78.7803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 463.2284 | 92.6457 | 0.9265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 20:00 | 6 | 30 | 20 | 181 | 4340 | 60.26 | 0 | 298.2561 | 298.2561 | -298.2561 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 364.5352 | 364.5352 | 0 | 8.5 | 0 | 60.7559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 357.2445 | 71.4489 | 0.7145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 21:00 | 6 | 30 | 21 | 181 | 4341 | 57.74 | 0 | 167.7209 | 167.7209 | -167.7209 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 204.9923 | 204.9923 | 0 | 8.5 | 0 | 34.1654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 200.8924 | 40.1785 | 0.4018% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 22:00 | 6 | 30 | 22 | 181 | 4342 | 59.36 | 0 | 80.7587 | 80.7587 | -80.7587 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 98.7051 | 98.7051 | 0 | 8.5 | 0 | 16.4508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 96.731 | 19.3462 | 0.1935% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-06-30 23:00 | 6 | 30 | 23 | 181 | 4343 | 61.7 | 0 | 57.6132 | 57.6132 | -57.6132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 70.4161 | 70.4161 | 0 | 8.5 | 0 | 11.736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 69.0078 | 13.8016 | 0.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 | 7 | 1 | 0 | 182 | 4344 | 64.22 | 0 | 45.1262 | 45.1262 | -45.1262 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 55.1543 | 55.1543 | 0 | 8.5 | 0 | 9.1924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 54.0512 | 10.8102 | 0.1081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 01:00 | 7 | 1 | 1 | 182 | 4345 | 67.1 | 0 | 100.0019 | 100.0019 | -100.0019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 122.2245 | 122.2245 | 0 | 8.5 | 0 | 20.3707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 119.78 | 23.956 | 0.2396% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 02:00 | 7 | 1 | 2 | 182 | 4346 | 67.28 | 0 | 199.0938 | 199.0938 | -199.0938 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 243.3368 | 243.3368 | 0 | 8.5 | 0 | 40.5561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 238.4701 | 47.694 | 0.4769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 03:00 | 7 | 1 | 3 | 182 | 4347 | 67.28 | 0 | 338.8691 | 338.8691 | -338.8691 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 414.1734 | 414.1734 | 0 | 8.5 | 0 | 69.0289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 405.8899 | 81.178 | 0.8118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 04:00 | 7 | 1 | 4 | 182 | 4348 | 67.1 | 0 | 272.2512 | 272.2512 | -272.2512 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 332.7515 | 332.7515 | 0 | 8.5 | 0 | 55.4586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 326.0965 | 65.2193 | 0.6522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 05:00 | 7 | 1 | 5 | 182 | 4349 | 67.46 | 0 | 436.2485 | 436.2485 | -436.2485 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 533.1926 | 533.1926 | 0 | 8.5 | 0 | 88.8654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 522.5288 | 104.5058 | 1.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 06:00 | 7 | 1 | 6 | 182 | 4350 | 67.82 | 0 | 1803.2991 | 1803.2991 | -1803.2991 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2204.0323 | 2204.0323 | 0 | 8.5 | 0 | 367.3387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2159.9516 | 431.9903 | 4.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 07:00 | 7 | 1 | 7 | 182 | 4351 | 68 | 0 | 2453.6952 | 2453.6952 | -2453.6952 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2998.9607 | 2998.9607 | 0 | 8.5 | 0 | 499.8268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2938.9815 | 587.7963 | 5.878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 08:00 | 7 | 1 | 8 | 182 | 4352 | 68 | 0 | 4483.9777 | 4483.9777 | -4483.9777 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5480.4171 | 5480.4171 | 0 | 8.5 | 0 | 913.4029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5370.8088 | 1074.1618 | 10.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 09:00 | 7 | 1 | 9 | 182 | 4353 | 68 | 0 | 6223.7041 | 6223.7041 | -6223.7041 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7606.7494 | 7606.7494 | 0 | 8.5 | 0 | 1267.7916 | 30% | 1 | 50.71% | 0% | 0% | 0% | 17.0959 | 0 | 0 | 0 | 17.0959 | 0 | 7454.6144 | 1490.9229 | 14.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3704
2007-07-01 10:00 | 7 | 1 | 10 | 182 | 4354 | 68 | 0 | 7829.8417 | 7829.8417 | -7829.8417 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9569.8065 | 9569.8065 | 0 | 8.5 | 0 | 1594.9678 | 31.9% | 1 | 63.8% | 0% | 0% | 0% | 28.9875 | 0 | 0 | 0 | 28.9875 | 0 | 9378.4104 | 1875.6821 | 18.76% | 1 | 37.51% | 0% | 0% | 4.2732 | 0 | 0 | 4.2732 | 33.2606
2007-07-01 11:00 | 7 | 1 | 11 | 182 | 4355 | 69.98 | 0 | 9662.4367 | 9662.4367 | -9662.4367 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11809.6448 | 11809.6448 | 0 | 8.5 | 0 | 1968.2741 | 39.37% | 1 | 78.73% | 0% | 0% | 0% | 47.0195 | 0 | 0 | 0 | 47.0195 | 0 | 11573.4519 | 2314.6904 | 23.15% | 1 | 46.29% | 0% | 0% | 6.9313 | 0 | 0 | 6.9313 | 53.9508
2007-07-01 12:00 | 7 | 1 | 12 | 182 | 4356 | 73.04 | 0 | 11264.1903 | 11264.1903 | -11264.1903 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13767.3436 | 13767.3436 | 0 | 8.5 | 0 | 2294.5573 | 45.89% | 1 | 91.78% | 0% | 0% | 0% | 66.9096 | 0 | 0 | 0 | 66.9096 | 0 | 13491.9968 | 2698.3994 | 26.98% | 1 | 53.97% | 0% | 0% | 9.8634 | 0 | 0 | 9.8634 | 76.773
2007-07-01 13:00 | 7 | 1 | 13 | 182 | 4357 | 78.98 | 0 | 12654.1674 | 12654.1674 | -12654.1674 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15466.2046 | 15466.2046 | 0 | 8.5 | 0 | 2577.7008 | 51.55% | 2 | 51.55% | 51.55% | 0% | 0% | 17.7561 | 17.7561 | 0 | 0 | 35.5121 | 0 | 15156.8805 | 3031.3761 | 30.31% | 1 | 60.63% | 0% | 0% | 12.89 | 0 | 0 | 12.89 | 48.4022
2007-07-01 14:00 | 7 | 1 | 14 | 182 | 4358 | 78.98 | 0 | 13576.3882 | 13576.3882 | -13576.3882 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16593.3634 | 16593.3634 | 0 | 8.5 | 0 | 2765.5606 | 55.31% | 2 | 55.31% | 55.31% | 0% | 0% | 20.8744 | 20.8744 | 0 | 0 | 41.7487 | 0 | 16261.4961 | 3252.2992 | 32.52% | 1 | 65.05% | 0% | 0% | 15.1538 | 0 | 0 | 15.1538 | 56.9025
2007-07-01 15:00 | 7 | 1 | 15 | 182 | 4359 | 75.92 | 0 | 13739.8337 | 13739.8337 | -13739.8337 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16793.13 | 16793.13 | 0 | 8.5 | 0 | 2798.855 | 55.98% | 2 | 55.98% | 55.98% | 0% | 0% | 21.4569 | 21.4569 | 0 | 0 | 42.9138 | 0 | 16457.2674 | 3291.4535 | 32.91% | 1 | 65.83% | 0% | 0% | 15.5766 | 0 | 0 | 15.5766 | 58.4904
2007-07-01 16:00 | 7 | 1 | 16 | 182 | 4360 | 73.94 | 0 | 13345.4433 | 13345.4433 | -13345.4433 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16311.0974 | 16311.0974 | 0 | 8.5 | 0 | 2718.5162 | 54.37% | 2 | 54.37% | 54.37% | 0% | 0% | 20.0667 | 20.0667 | 0 | 0 | 40.1334 | 0 | 15984.8755 | 3196.9751 | 31.97% | 1 | 63.94% | 0% | 0% | 14.5674 | 0 | 0 | 14.5674 | 54.7008
2007-07-01 17:00 | 7 | 1 | 17 | 182 | 4361 | 73.94 | 0 | 12588.6571 | 12588.6571 | -12588.6571 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15386.1365 | 15386.1365 | 0 | 8.5 | 0 | 2564.3561 | 51.29% | 2 | 51.29% | 51.29% | 0% | 0% | 17.5454 | 17.5454 | 0 | 0 | 35.0907 | 0 | 15078.4138 | 3015.6828 | 30.16% | 1 | 60.31% | 0% | 0% | 12.7371 | 0 | 0 | 12.7371 | 47.8278
2007-07-01 18:00 | 7 | 1 | 18 | 182 | 4362 | 71.96 | 0 | 8498.7962 | 8498.7962 | -8498.7962 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10387.4176 | 10387.4176 | 0 | 8.5 | 0 | 1731.2363 | 34.62% | 1 | 69.25% | 0% | 0% | 0% | 35.0026 | 0 | 0 | 0 | 35.0026 | 0 | 10179.6692 | 2035.9338 | 20.36% | 1 | 40.72% | 0% | 0% | 5.1599 | 0 | 0 | 5.1599 | 40.1625
2007-07-01 19:00 | 7 | 1 | 19 | 182 | 4363 | 69.98 | 0 | 7524.5594 | 7524.5594 | -7524.5594 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9196.6838 | 9196.6838 | 0 | 8.5 | 0 | 1532.7806 | 30.66% | 1 | 61.31% | 0% | 0% | 0% | 26.4536 | 0 | 0 | 0 | 26.4536 | 0 | 9012.7501 | 1802.55 | 18.03% | 1 | 36.05% | 0% | 0% | 3.8996 | 0 | 0 | 3.8996 | 30.3532
2007-07-01 20:00 | 7 | 1 | 20 | 182 | 4364 | 69.98 | 0 | 5908.7324 | 5908.7324 | -5908.7324 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7221.7841 | 7221.7841 | 0 | 8.5 | 0 | 1203.6307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7077.3484 | 1415.4697 | 14.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 21:00 | 7 | 1 | 21 | 182 | 4365 | 66.92 | 0 | 2483.9931 | 2483.9931 | -2483.9931 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3035.9915 | 3035.9915 | 0 | 8.5 | 0 | 505.9986 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2975.2717 | 595.0543 | 5.951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 22:00 | 7 | 1 | 22 | 182 | 4366 | 66.02 | 0 | 589.3424 | 589.3424 | -589.3424 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 720.3074 | 720.3074 | 0 | 8.5 | 0 | 120.0512 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 705.9013 | 141.1803 | 1.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-01 23:00 | 7 | 1 | 23 | 182 | 4367 | 66.02 | 0 | 306.149 | 306.149 | -306.149 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 374.1821 | 374.1821 | 0 | 8.5 | 0 | 62.3637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 366.6985 | 73.3397 | 0.7334% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 | 7 | 2 | 0 | 183 | 4368 | 66.02 | 0 | 132.2943 | 132.2943 | -132.2943 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 161.693 | 161.693 | 0 | 8.5 | 0 | 26.9488 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 158.4591 | 31.6918 | 0.3169% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 01:00 | 7 | 2 | 1 | 183 | 4369 | 62.96 | 0 | 45.2083 | 45.2083 | -45.2083 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 55.2545 | 55.2545 | 0 | 8.5 | 0 | 9.2091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 54.1494 | 10.8299 | 0.1083% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 02:00 | 7 | 2 | 2 | 183 | 4370 | 62.96 | 0 | 15.0564 | 15.0564 | -15.0564 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18.4023 | 18.4023 | 0 | 8.5 | 0 | 3.067 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 18.0342 | 3.6068 | 0.03607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 03:00 | 7 | 2 | 3 | 183 | 4371 | 62.96 | 0 | 3.9969 | 3.9969 | -3.9969 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4.8851 | 4.8851 | 0 | 8.5 | 0 | 0.81419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4.7874 | 0.95749 | 0.009575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 04:00 | 7 | 2 | 4 | 183 | 4372 | 62.06 | 0 | 1.263 | 1.263 | -1.263 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.5436 | 1.5436 | 0 | 8.5 | 0 | 0.25727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.5128 | 0.30255 | 0.003026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 05:00 | 7 | 2 | 5 | 183 | 4373 | 62.06 | 0 | 8.9052 | 8.9052 | -8.9052 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10.8842 | 10.8842 | 0 | 8.5 | 0 | 1.814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 10.6665 | 2.1333 | 0.02133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 06:00 | 7 | 2 | 6 | 183 | 4374 | 62.96 | 542.75 | 951.6361 | 951.6361 | -408.8861 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1163.1107 | 1163.1107 | 0 | 8.5 | 0 | 193.8518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1139.8485 | 227.9697 | 2.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 07:00 | 7 | 2 | 7 | 183 | 4375 | 64.94 | 0 | 1972.1939 | 1972.1939 | -1972.1939 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2410.4592 | 2410.4592 | 0 | 8.5 | 0 | 401.7432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2362.25 | 472.45 | 4.725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 08:00 | 7 | 2 | 8 | 183 | 4376 | 64.94 | 0 | 4025.1178 | 4025.1178 | -4025.1178 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4919.5884 | 4919.5884 | 0 | 8.5 | 0 | 819.9314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4821.1967 | 964.2393 | 9.642% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 09:00 | 7 | 2 | 9 | 183 | 4377 | 69.98 | 0 | 5094.1905 | 5094.1905 | -5094.1905 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6226.2329 | 6226.2329 | 0 | 8.5 | 0 | 1037.7055 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6101.7082 | 1220.3416 | 12.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 10:00 | 7 | 2 | 10 | 183 | 4378 | 71.06 | 0 | 6356.9763 | 6356.9763 | -6356.9763 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7769.6377 | 7769.6377 | 0 | 8.5 | 0 | 1294.9396 | 30% | 1 | 51.8% | 0% | 0% | 0% | 17.9496 | 0 | 0 | 0 | 17.9496 | 0 | 7614.245 | 1522.849 | 15.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.2241
2007-07-02 11:00 | 7 | 2 | 11 | 183 | 4379 | 71.06 | 0 | 7050.5489 | 7050.5489 | -7050.5489 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8617.3375 | 8617.3375 | 0 | 8.5 | 0 | 1436.2229 | 30% | 1 | 57.45% | 0% | 0% | 0% | 22.7767 | 0 | 0 | 0 | 22.7767 | 0 | 8444.9907 | 1688.9981 | 16.89% | 1 | 33.78% | 0% | 0% | 3.3576 | 0 | 0 | 3.3576 | 26.1343
2007-07-02 12:00 | 7 | 2 | 12 | 183 | 4380 | 73.04 | 0 | 7474.0119 | 7474.0119 | -7474.0119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9134.9034 | 9134.9034 | 0 | 8.5 | 0 | 1522.4839 | 30.45% | 1 | 60.9% | 0% | 0% | 0% | 26.0467 | 0 | 0 | 0 | 26.0467 | 0 | 8952.2053 | 1790.4411 | 17.9% | 1 | 35.81% | 0% | 0% | 3.8396 | 0 | 0 | 3.8396 | 29.8863
2007-07-02 13:00 | 7 | 2 | 13 | 183 | 4381 | 75.02 | 0 | 7952.0065 | 7952.0065 | -7952.0065 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9719.1191 | 9719.1191 | 0 | 8.5 | 0 | 1619.8532 | 32.4% | 1 | 64.79% | 0% | 0% | 0% | 30.0383 | 0 | 0 | 0 | 30.0383 | 0 | 9524.7367 | 1904.9473 | 19.05% | 1 | 38.1% | 0% | 0% | 4.4281 | 0 | 0 | 4.4281 | 34.4663
2007-07-02 14:00 | 7 | 2 | 14 | 183 | 4382 | 75.02 | 0 | 8067.569 | 8067.569 | -8067.569 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9860.3621 | 9860.3621 | 0 | 8.5 | 0 | 1643.3937 | 32.87% | 1 | 65.74% | 0% | 0% | 0% | 31.0518 | 0 | 0 | 0 | 31.0518 | 0 | 9663.1549 | 1932.631 | 19.33% | 1 | 38.65% | 0% | 0% | 4.5775 | 0 | 0 | 4.5775 | 35.6293
2007-07-02 15:00 | 7 | 2 | 15 | 183 | 4383 | 77 | 0 | 7546.6093 | 7546.6093 | -7546.6093 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9223.6336 | 9223.6336 | 0 | 8.5 | 0 | 1537.2723 | 30.75% | 1 | 61.49% | 0% | 0% | 0% | 26.6322 | 0 | 0 | 0 | 26.6322 | 0 | 9039.1609 | 1807.8322 | 18.08% | 1 | 36.16% | 0% | 0% | 3.926 | 0 | 0 | 3.926 | 30.5582
2007-07-02 16:00 | 7 | 2 | 16 | 183 | 4384 | 75.92 | 0 | 6687.6972 | 6687.6972 | -6687.6972 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8173.8521 | 8173.8521 | 0 | 8.5 | 0 | 1362.3087 | 30% | 1 | 54.49% | 0% | 0% | 0% | 20.1704 | 0 | 0 | 0 | 20.1704 | 0 | 8010.3751 | 1602.075 | 16.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.445
2007-07-02 17:00 | 7 | 2 | 17 | 183 | 4385 | 75.92 | 0 | 5576.4358 | 5576.4358 | -5576.4358 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6815.6437 | 6815.6437 | 0 | 8.5 | 0 | 1135.9406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6679.3309 | 1335.8662 | 13.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 18:00 | 7 | 2 | 18 | 183 | 4386 | 73.04 | 0 | 2773.568 | 2773.568 | -2773.568 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3389.9165 | 3389.9165 | 0 | 8.5 | 0 | 564.9861 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3322.1181 | 664.4236 | 6.644% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 19:00 | 7 | 2 | 19 | 183 | 4387 | 71.96 | 0 | 1707.7269 | 1707.7269 | -1707.7269 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2087.2217 | 2087.2217 | 0 | 8.5 | 0 | 347.8703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2045.4773 | 409.0955 | 4.091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 20:00 | 7 | 2 | 20 | 183 | 4388 | 71.96 | 0 | 698.8673 | 698.8673 | -698.8673 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 854.1712 | 854.1712 | 0 | 8.5 | 0 | 142.3619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 837.0878 | 167.4176 | 1.674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 21:00 | 7 | 2 | 21 | 183 | 4389 | 64.94 | 0 | 459.5697 | 459.5697 | -459.5697 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 561.6963 | 561.6963 | 0 | 8.5 | 0 | 93.616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 550.4623 | 110.0925 | 1.101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 22:00 | 7 | 2 | 22 | 183 | 4390 | 64.04 | 0 | 38.7957 | 38.7957 | -38.7957 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 47.417 | 47.417 | 0 | 8.5 | 0 | 7.9028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 46.4686 | 9.2937 | 0.09294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-02 23:00 | 7 | 2 | 23 | 183 | 4391 | 64.04 | 0.25781 | 1.9868 | 1.9868 | -1.729 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.4283 | 2.4283 | 0 | 8.5 | 0 | 0.40471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.3797 | 0.47594 | 0.004759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 | 7 | 3 | 0 | 184 | 4392 | 57.92 | 7.1269 | 0 | 0 | 7.1269 | Heating | 6.2885 | 8.5 | 6.2885 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.4168 | 0 | 1.2834 | 0.01283% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 01:00 | 7 | 3 | 1 | 184 | 4393 | 57.92 | 16.0827 | 0 | 0 | 16.0827 | Heating | 14.1907 | 8.5 | 14.1907 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.8381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.4803 | 0 | 2.8961 | 0.02896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 02:00 | 7 | 3 | 2 | 184 | 4394 | 57.92 | 28.1565 | 0 | 0 | 28.1565 | Heating | 24.844 | 8.5 | 24.844 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.9688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 25.351 | 0 | 5.0702 | 0.0507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 03:00 | 7 | 3 | 3 | 184 | 4395 | 53.96 | 38.6966 | 0 | 0 | 38.6966 | Heating | 34.144 | 8.5 | 34.144 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.8288 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.8409 | 0 | 6.9682 | 0.06968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 04:00 | 7 | 3 | 4 | 184 | 4396 | 53.06 | 50.0078 | 0 | 0 | 50.0078 | Heating | 44.1246 | 8.5 | 44.1246 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.8249 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 45.0251 | 0 | 9.005 | 0.09005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 05:00 | 7 | 3 | 5 | 184 | 4397 | 53.06 | 42.4846 | 0 | 0 | 42.4846 | Heating | 37.4864 | 8.5 | 37.4864 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.4973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 38.2514 | 0 | 7.6503 | 0.0765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 06:00 | 7 | 3 | 6 | 184 | 4398 | 57.02 | 2067.4925 | 154.8679 | 154.8679 | 1912.6246 | Heating | 1687.61 | 8.5 | 1687.61 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 337.522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1722.051 | 0 | 344.4102 | 3.444% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 07:00 | 7 | 3 | 7 | 184 | 4399 | 60.98 | 835.2634 | 197.3976 | 197.3976 | 637.8657 | Heating | 562.8227 | 8.5 | 562.8227 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.5645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 574.3089 | 0 | 114.8618 | 1.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 08:00 | 7 | 3 | 8 | 184 | 4400 | 60.98 | 106.2717 | 1845.8625 | 1845.8625 | -1739.5909 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2256.0542 | 2256.0542 | 0 | 8.5 | 0 | 376.009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2210.9331 | 442.1866 | 4.422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 09:00 | 7 | 3 | 9 | 184 | 4401 | 68 | 0 | 2774.5293 | 2774.5293 | -2774.5293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3391.0913 | 3391.0913 | 0 | 8.5 | 0 | 565.1819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3323.2695 | 664.6539 | 6.647% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 10:00 | 7 | 3 | 10 | 184 | 4402 | 69.98 | 0 | 3401.5273 | 3401.5273 | -3401.5273 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4157.4222 | 4157.4222 | 0 | 8.5 | 0 | 692.9037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4074.2738 | 814.8548 | 8.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 11:00 | 7 | 3 | 11 | 184 | 4403 | 69.98 | 0 | 5142.3853 | 5142.3853 | -5142.3853 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6285.1375 | 6285.1375 | 0 | 8.5 | 0 | 1047.5229 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6159.4348 | 1231.887 | 12.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 12:00 | 7 | 3 | 12 | 184 | 4404 | 75.92 | 0 | 6651.0789 | 6651.0789 | -6651.0789 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8129.0964 | 8129.0964 | 0 | 8.5 | 0 | 1354.8494 | 30% | 1 | 54.19% | 0% | 0% | 0% | 19.9173 | 0 | 0 | 0 | 19.9173 | 0 | 7966.5145 | 1593.3029 | 15.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.1918
2007-07-03 13:00 | 7 | 3 | 13 | 184 | 4405 | 75.92 | 0 | 8188.8406 | 8188.8406 | -8188.8406 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10008.5829 | 10008.5829 | 0 | 8.5 | 0 | 1668.0972 | 33.36% | 1 | 66.72% | 0% | 0% | 0% | 32.1359 | 0 | 0 | 0 | 32.1359 | 0 | 9808.4113 | 1961.6823 | 19.62% | 1 | 39.23% | 0% | 0% | 4.7373 | 0 | 0 | 4.7373 | 36.8731
2007-07-03 14:00 | 7 | 3 | 14 | 184 | 4406 | 75.92 | 0 | 9194.5705 | 9194.5705 | -9194.5705 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11237.8084 | 11237.8084 | 0 | 8.5 | 0 | 1872.9681 | 37.46% | 1 | 74.92% | 0% | 0% | 0% | 41.947 | 0 | 0 | 0 | 41.947 | 0 | 11013.0522 | 2202.6104 | 22.03% | 1 | 44.05% | 0% | 0% | 6.1836 | 0 | 0 | 6.1836 | 48.1306
2007-07-03 15:00 | 7 | 3 | 15 | 184 | 4407 | 77 | 0 | 9411.5344 | 9411.5344 | -9411.5344 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11502.9864 | 11502.9864 | 0 | 8.5 | 0 | 1917.1644 | 38.34% | 1 | 76.69% | 0% | 0% | 0% | 44.2586 | 0 | 0 | 0 | 44.2586 | 0 | 11272.9267 | 2254.5853 | 22.55% | 1 | 45.09% | 0% | 0% | 6.5243 | 0 | 0 | 6.5243 | 50.7829
2007-07-03 16:00 | 7 | 3 | 16 | 184 | 4408 | 77 | 0 | 9340.9544 | 9340.9544 | -9340.9544 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11416.722 | 11416.722 | 0 | 8.5 | 0 | 1902.787 | 38.06% | 1 | 76.11% | 0% | 0% | 0% | 43.4989 | 0 | 0 | 0 | 43.4989 | 0 | 11188.3876 | 2237.6775 | 22.38% | 1 | 44.75% | 0% | 0% | 6.4123 | 0 | 0 | 6.4123 | 49.9113
2007-07-03 17:00 | 7 | 3 | 17 | 184 | 4409 | 77 | 0 | 8753.3099 | 8753.3099 | -8753.3099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10698.4899 | 10698.4899 | 0 | 8.5 | 0 | 1783.0817 | 35.66% | 1 | 71.32% | 0% | 0% | 0% | 37.4606 | 0 | 0 | 0 | 37.4606 | 0 | 10484.5201 | 2096.904 | 20.97% | 1 | 41.94% | 0% | 0% | 5.5222 | 0 | 0 | 5.5222 | 42.9828
2007-07-03 18:00 | 7 | 3 | 18 | 184 | 4410 | 75.92 | 0 | 5485.1802 | 5485.1802 | -5485.1802 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6704.1092 | 6704.1092 | 0 | 8.5 | 0 | 1117.3515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6570.027 | 1314.0054 | 13.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 19:00 | 7 | 3 | 19 | 184 | 4411 | 73.94 | 0 | 4558.1126 | 4558.1126 | -4558.1126 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5571.0266 | 5571.0266 | 0 | 8.5 | 0 | 928.5044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5459.606 | 1091.9212 | 10.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 20:00 | 7 | 3 | 20 | 184 | 4412 | 73.94 | 0 | 3291.6519 | 3291.6519 | -3291.6519 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4023.1301 | 4023.1301 | 0 | 8.5 | 0 | 670.5217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3942.6675 | 788.5335 | 7.885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 21:00 | 7 | 3 | 21 | 184 | 4413 | 66.02 | 0 | 1287.3827 | 1287.3827 | -1287.3827 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1573.4678 | 1573.4678 | 0 | 8.5 | 0 | 262.2446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1541.9984 | 308.3997 | 3.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 22:00 | 7 | 3 | 22 | 184 | 4414 | 64.94 | 0 | 233.7405 | 233.7405 | -233.7405 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 285.6828 | 285.6828 | 0 | 8.5 | 0 | 47.6138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 279.9691 | 55.9938 | 0.5599% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-03 23:00 | 7 | 3 | 23 | 184 | 4415 | 64.94 | 0 | 91.3667 | 91.3667 | -91.3667 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 111.6704 | 111.6704 | 0 | 8.5 | 0 | 18.6117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 109.437 | 21.8874 | 0.2189% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 | 7 | 4 | 0 | 185 | 4416 | 60.98 | 0 | 26.4827 | 26.4827 | -26.4827 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 32.3677 | 32.3677 | 0 | 8.5 | 0 | 5.3946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 31.7203 | 6.3441 | 0.06344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 01:00 | 7 | 4 | 1 | 185 | 4417 | 60.98 | 0 | 2.4795 | 2.4795 | -2.4795 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3.0305 | 3.0305 | 0 | 8.5 | 0 | 0.50508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.9699 | 0.59397 | 0.00594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 02:00 | 7 | 4 | 2 | 185 | 4418 | 60.98 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-04 03:00 | 7 | 4 | 3 | 185 | 4419 | 59 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-04 04:00 | 7 | 4 | 4 | 185 | 4420 | 60.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-04 05:00 | 7 | 4 | 5 | 185 | 4421 | 60.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-04 06:00 | 7 | 4 | 6 | 185 | 4422 | 60.98 | 596.0559 | 519.482 | 519.482 | 76.5739 | Heating | 67.5652 | 8.5 | 67.5652 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 68.9441 | 0 | 13.7888 | 0.1379% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 07:00 | 7 | 4 | 7 | 185 | 4423 | 62.06 | 181.2175 | 575.1365 | 575.1365 | -393.919 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 702.9447 | 702.9447 | 0 | 8.5 | 0 | 117.1574 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 688.8858 | 137.7772 | 1.378% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 08:00 | 7 | 4 | 8 | 185 | 4424 | 62.06 | 0 | 3259.4581 | 3259.4581 | -3259.4581 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3983.7822 | 3983.7822 | 0 | 8.5 | 0 | 663.9637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3904.1065 | 780.8213 | 7.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 09:00 | 7 | 4 | 9 | 185 | 4425 | 62.96 | 0 | 4939.7059 | 4939.7059 | -4939.7059 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6037.4183 | 6037.4183 | 0 | 8.5 | 0 | 1006.2364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5916.67 | 1183.334 | 11.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 10:00 | 7 | 4 | 10 | 185 | 4426 | 62.96 | 0 | 7417.2661 | 7417.2661 | -7417.2661 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9065.5474 | 9065.5474 | 0 | 8.5 | 0 | 1510.9246 | 30.22% | 1 | 60.44% | 0% | 0% | 0% | 25.5941 | 0 | 0 | 0 | 25.5941 | 0 | 8884.2364 | 1776.8473 | 17.77% | 1 | 35.54% | 0% | 0% | 3.7729 | 0 | 0 | 3.7729 | 29.367
2007-07-04 11:00 | 7 | 4 | 11 | 185 | 4427 | 62.96 | 0 | 9220.255 | 9220.255 | -9220.255 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11269.2005 | 11269.2005 | 0 | 8.5 | 0 | 1878.2001 | 37.56% | 1 | 75.13% | 0% | 0% | 0% | 42.217 | 0 | 0 | 0 | 42.217 | 0 | 11043.8165 | 2208.7633 | 22.09% | 1 | 44.18% | 0% | 0% | 6.2234 | 0 | 0 | 6.2234 | 48.4404
2007-07-04 12:00 | 7 | 4 | 12 | 185 | 4428 | 62.96 | 0 | 10659.6966 | 10659.6966 | -10659.6966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13028.518 | 13028.518 | 0 | 8.5 | 0 | 2171.4197 | 43.43% | 1 | 86.86% | 0% | 0% | 0% | 58.9375 | 0 | 0 | 0 | 58.9375 | 0 | 12767.9477 | 2553.5895 | 25.54% | 1 | 51.07% | 0% | 0% | 8.6882 | 0 | 0 | 8.6882 | 67.6257
2007-07-04 13:00 | 7 | 4 | 13 | 185 | 4429 | 64.94 | 0 | 12025.0429 | 12025.0429 | -12025.0429 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14697.2747 | 14697.2747 | 0 | 8.5 | 0 | 2449.5458 | 48.99% | 1 | 97.98% | 0% | 0% | 0% | 77.7639 | 0 | 0 | 0 | 77.7639 | 0 | 14403.3292 | 2880.6658 | 28.81% | 1 | 57.61% | 0% | 0% | 11.4635 | 0 | 0 | 11.4635 | 89.2273
2007-07-04 14:00 | 7 | 4 | 14 | 185 | 4430 | 64.94 | 0 | 12914.2679 | 12914.2679 | -12914.2679 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15784.1052 | 15784.1052 | 0 | 8.5 | 0 | 2630.6842 | 52.61% | 2 | 52.61% | 52.61% | 0% | 0% | 18.6067 | 18.6067 | 0 | 0 | 37.2135 | 0 | 15468.4231 | 3093.6846 | 30.94% | 1 | 61.87% | 0% | 0% | 13.5076 | 0 | 0 | 13.5076 | 50.721
2007-07-04 15:00 | 7 | 4 | 15 | 185 | 4431 | 68 | 0 | 13294.6208 | 13294.6208 | -13294.6208 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16248.981 | 16248.981 | 0 | 8.5 | 0 | 2708.1635 | 54.16% | 2 | 54.16% | 54.16% | 0% | 0% | 19.8914 | 19.8914 | 0 | 0 | 39.7827 | 0 | 15924.0014 | 3184.8003 | 31.85% | 1 | 63.7% | 0% | 0% | 14.4401 | 0 | 0 | 14.4401 | 54.2228
2007-07-04 16:00 | 7 | 4 | 16 | 185 | 4432 | 68 | 0 | 13412.0894 | 13412.0894 | -13412.0894 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16392.5537 | 16392.5537 | 0 | 8.5 | 0 | 2732.0923 | 54.64% | 2 | 54.64% | 54.64% | 0% | 0% | 20.2979 | 20.2979 | 0 | 0 | 40.5958 | 0 | 16064.7027 | 3212.9405 | 32.13% | 1 | 64.26% | 0% | 0% | 14.7353 | 0 | 0 | 14.7353 | 55.3311
2007-07-04 17:00 | 7 | 4 | 17 | 185 | 4433 | 68 | 0 | 13054.408 | 13054.408 | -13054.408 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15955.3875 | 15955.3875 | 0 | 8.5 | 0 | 2659.2312 | 53.18% | 2 | 53.18% | 53.18% | 0% | 0% | 19.0744 | 19.0744 | 0 | 0 | 38.1488 | 0 | 15636.2797 | 3127.2559 | 31.27% | 1 | 62.55% | 0% | 0% | 13.8471 | 0 | 0 | 13.8471 | 51.9959
2007-07-04 18:00 | 7 | 4 | 18 | 185 | 4434 | 68 | 0 | 8695.4429 | 8695.4429 | -8695.4429 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10627.7635 | 10627.7635 | 0 | 8.5 | 0 | 1771.2939 | 35.43% | 1 | 70.85% | 0% | 0% | 0% | 36.8935 | 0 | 0 | 0 | 36.8935 | 0 | 10415.2083 | 2083.0417 | 20.83% | 1 | 41.66% | 0% | 0% | 5.4386 | 0 | 0 | 5.4386 | 42.3321
2007-07-04 19:00 | 7 | 4 | 19 | 185 | 4435 | 68 | 0 | 7799.0652 | 7799.0652 | -7799.0652 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9532.1908 | 9532.1908 | 0 | 8.5 | 0 | 1588.6985 | 31.77% | 1 | 63.55% | 0% | 0% | 0% | 28.7261 | 0 | 0 | 0 | 28.7261 | 0 | 9341.547 | 1868.3094 | 18.68% | 1 | 37.37% | 0% | 0% | 4.2346 | 0 | 0 | 4.2346 | 32.9607
2007-07-04 20:00 | 7 | 4 | 20 | 185 | 4436 | 68 | 0 | 6562.3903 | 6562.3903 | -6562.3903 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8020.6993 | 8020.6993 | 0 | 8.5 | 0 | 1336.7832 | 30% | 1 | 53.47% | 0% | 0% | 0% | 19.3117 | 0 | 0 | 0 | 19.3117 | 0 | 7860.2853 | 1572.0571 | 15.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.5863
2007-07-04 21:00 | 7 | 4 | 21 | 185 | 4437 | 62.96 | 0 | 2881.3026 | 2881.3026 | -2881.3026 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3521.592 | 3521.592 | 0 | 8.5 | 0 | 586.932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3451.1602 | 690.232 | 6.902% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 22:00 | 7 | 4 | 22 | 185 | 4438 | 62.06 | 0 | 933.139 | 933.139 | -933.139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1140.5033 | 1140.5033 | 0 | 8.5 | 0 | 190.0839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1117.6932 | 223.5386 | 2.235% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-04 23:00 | 7 | 4 | 23 | 185 | 4439 | 62.06 | 0 | 937.5524 | 937.5524 | -937.5524 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1145.8973 | 1145.8973 | 0 | 8.5 | 0 | 190.9829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1122.9794 | 224.5959 | 2.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 | 7 | 5 | 0 | 186 | 4440 | 60.08 | 0 | 763.3838 | 763.3838 | -763.3838 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 933.0246 | 933.0246 | 0 | 8.5 | 0 | 155.5041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 914.3641 | 182.8728 | 1.829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 01:00 | 7 | 5 | 1 | 186 | 4441 | 57.92 | 0 | 689.3127 | 689.3127 | -689.3127 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 842.4933 | 842.4933 | 0 | 8.5 | 0 | 140.4156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 825.6435 | 165.1287 | 1.651% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 02:00 | 7 | 5 | 2 | 186 | 4442 | 60.08 | 0 | 598.9387 | 598.9387 | -598.9387 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 732.0362 | 732.0362 | 0 | 8.5 | 0 | 122.006 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 717.3954 | 143.4791 | 1.435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 03:00 | 7 | 5 | 3 | 186 | 4443 | 59 | 0 | 484.8651 | 484.8651 | -484.8651 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 592.6128 | 592.6128 | 0 | 8.5 | 0 | 98.7688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 580.7606 | 116.1521 | 1.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 04:00 | 7 | 5 | 4 | 186 | 4444 | 57.92 | 0 | 246.0191 | 246.0191 | -246.0191 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 300.6901 | 300.6901 | 0 | 8.5 | 0 | 50.115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 294.6762 | 58.9352 | 0.5894% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 05:00 | 7 | 5 | 5 | 186 | 4445 | 57.92 | 0 | 240.7528 | 240.7528 | -240.7528 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 294.2534 | 294.2534 | 0 | 8.5 | 0 | 49.0422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 288.3683 | 57.6737 | 0.5767% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 06:00 | 7 | 5 | 6 | 186 | 4446 | 60.98 | 33.3211 | 3096.3478 | 3096.3478 | -3063.0267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3784.4251 | 3784.4251 | 0 | 8.5 | 0 | 630.7375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3708.7366 | 741.7473 | 7.417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 07:00 | 7 | 5 | 7 | 186 | 4447 | 64.04 | 0 | 3527.8809 | 3527.8809 | -3527.8809 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4311.8544 | 4311.8544 | 0 | 8.5 | 0 | 718.6424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4225.6173 | 845.1235 | 8.451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 08:00 | 7 | 5 | 8 | 186 | 4448 | 64.04 | 0 | 6048.1517 | 6048.1517 | -6048.1517 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7392.1854 | 7392.1854 | 0 | 8.5 | 0 | 1232.0309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7244.3417 | 1448.8683 | 14.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 09:00 | 7 | 5 | 9 | 186 | 4449 | 71.96 | 0 | 8975.6293 | 8975.6293 | -8975.6293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10970.2136 | 10970.2136 | 0 | 8.5 | 0 | 1828.3689 | 36.57% | 1 | 73.13% | 0% | 0% | 0% | 39.6851 | 0 | 0 | 0 | 39.6851 | 0 | 10750.8093 | 2150.1619 | 21.5% | 1 | 43% | 0% | 0% | 5.8501 | 0 | 0 | 5.8501 | 45.5353
2007-07-05 10:00 | 7 | 5 | 10 | 186 | 4450 | 75.02 | 0 | 11436.1405 | 11436.1405 | -11436.1405 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13977.5051 | 13977.5051 | 0 | 8.5 | 0 | 2329.5842 | 46.59% | 1 | 93.18% | 0% | 0% | 0% | 69.2822 | 0 | 0 | 0 | 69.2822 | 0 | 13697.955 | 2739.591 | 27.4% | 1 | 54.79% | 0% | 0% | 10.2131 | 0 | 0 | 10.2131 | 79.4953
2007-07-05 11:00 | 7 | 5 | 11 | 186 | 4451 | 75.02 | 0 | 13105.4778 | 13105.4778 | -13105.4778 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16017.8062 | 16017.8062 | 0 | 8.5 | 0 | 2669.6344 | 53.39% | 2 | 53.39% | 53.39% | 0% | 0% | 19.2465 | 19.2465 | 0 | 0 | 38.4929 | 0 | 15697.45 | 3139.49 | 31.39% | 1 | 62.79% | 0% | 0% | 13.972 | 0 | 0 | 13.972 | 52.4649
2007-07-05 12:00 | 7 | 5 | 12 | 186 | 4452 | 78.08 | 0 | 14071.2556 | 14071.2556 | -14071.2556 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17198.2012 | 17198.2012 | 0 | 8.5 | 0 | 2866.3669 | 57.33% | 2 | 57.33% | 57.33% | 0% | 0% | 22.666 | 22.666 | 0 | 0 | 45.332 | 0 | 16854.2372 | 3370.8474 | 33.71% | 1 | 33.71% | 33.71% | 0% | 3.3413 | 3.3413 | 0 | 6.6826 | 52.0146
2007-07-05 13:00 | 7 | 5 | 13 | 186 | 4453 | 80.06 | 0 | 15051.4587 | 15051.4587 | -15051.4587 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18396.2273 | 18396.2273 | 0 | 8.5 | 0 | 3066.0379 | 61.32% | 2 | 61.32% | 61.32% | 0% | 0% | 26.4631 | 26.4631 | 0 | 0 | 52.9262 | 0 | 18028.3027 | 3605.6605 | 36.06% | 1 | 36.06% | 36.06% | 0% | 3.901 | 3.901 | 0 | 7.802 | 60.7282
2007-07-05 14:00 | 7 | 5 | 14 | 186 | 4454 | 80.06 | 0 | 15162.7293 | 15162.7293 | -15162.7293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18532.2248 | 18532.2248 | 0 | 8.5 | 0 | 3088.7041 | 61.77% | 2 | 61.77% | 61.77% | 0% | 0% | 26.9152 | 26.9152 | 0 | 0 | 53.8304 | 0 | 18161.5803 | 3632.3161 | 36.32% | 1 | 36.32% | 36.32% | 0% | 3.9677 | 3.9677 | 0 | 7.9353 | 61.7657
2007-07-05 15:00 | 7 | 5 | 15 | 186 | 4455 | 82.94 | 0 | 14651.0631 | 14651.0631 | -14651.0631 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17906.8549 | 17906.8549 | 0 | 8.5 | 0 | 2984.4758 | 59.69% | 2 | 59.69% | 59.69% | 0% | 0% | 24.8719 | 24.8719 | 0 | 0 | 49.7438 | 0 | 17548.7178 | 3509.7436 | 35.1% | 1 | 35.1% | 35.1% | 0% | 3.6665 | 3.6665 | 0 | 7.3329 | 57.0767
2007-07-05 16:00 | 7 | 5 | 16 | 186 | 4456 | 82.04 | 0 | 13777.4927 | 13777.4927 | -13777.4927 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16839.1578 | 16839.1578 | 0 | 8.5 | 0 | 2806.5263 | 56.13% | 2 | 56.13% | 56.13% | 0% | 0% | 21.5924 | 21.5924 | 0 | 0 | 43.1848 | 0 | 16502.3746 | 3300.4749 | 33% | 1 | 33% | 33% | 0% | 3.183 | 3.183 | 0 | 6.366 | 49.5508
2007-07-05 17:00 | 7 | 5 | 17 | 186 | 4457 | 82.04 | 0 | 12769.1188 | 12769.1188 | -12769.1188 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15606.7008 | 15606.7008 | 0 | 8.5 | 0 | 2601.1168 | 52.02% | 2 | 52.02% | 52.02% | 0% | 0% | 18.1292 | 18.1292 | 0 | 0 | 36.2585 | 0 | 15294.5668 | 3058.9134 | 30.59% | 1 | 61.18% | 0% | 0% | 13.1609 | 0 | 0 | 13.1609 | 49.4194
2007-07-05 18:00 | 7 | 5 | 18 | 186 | 4458 | 78.98 | 0 | 8102.2016 | 8102.2016 | -8102.2016 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9902.6908 | 9902.6908 | 0 | 8.5 | 0 | 1650.4485 | 33.01% | 1 | 66.02% | 0% | 0% | 0% | 31.3592 | 0 | 0 | 0 | 31.3592 | 0 | 9704.637 | 1940.9274 | 19.41% | 1 | 38.82% | 0% | 0% | 4.6228 | 0 | 0 | 4.6228 | 35.982
2007-07-05 19:00 | 7 | 5 | 19 | 186 | 4459 | 75.92 | 0 | 6977.1173 | 6977.1173 | -6977.1173 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8527.5878 | 8527.5878 | 0 | 8.5 | 0 | 1421.2646 | 30% | 1 | 56.85% | 0% | 0% | 0% | 22.2348 | 0 | 0 | 0 | 22.2348 | 0 | 8357.036 | 1671.4072 | 16.71% | 1 | 33.43% | 0% | 0% | 3.2777 | 0 | 0 | 3.2777 | 25.5125
2007-07-05 20:00 | 7 | 5 | 20 | 186 | 4460 | 75.92 | 0 | 5305.9344 | 5305.9344 | -5305.9344 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6485.0309 | 6485.0309 | 0 | 8.5 | 0 | 1080.8385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6355.3303 | 1271.0661 | 12.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 21:00 | 7 | 5 | 21 | 186 | 4461 | 69.98 | 0 | 2325.1184 | 2325.1184 | -2325.1184 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2841.8113 | 2841.8113 | 0 | 8.5 | 0 | 473.6352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2784.9751 | 556.995 | 5.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 22:00 | 7 | 5 | 22 | 186 | 4462 | 69.08 | 0 | 540.9978 | 540.9978 | -540.9978 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 661.2196 | 661.2196 | 0 | 8.5 | 0 | 110.2033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 647.9952 | 129.599 | 1.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-05 23:00 | 7 | 5 | 23 | 186 | 4463 | 69.08 | 0 | 282.344 | 282.344 | -282.344 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 345.0871 | 345.0871 | 0 | 8.5 | 0 | 57.5145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 338.1853 | 67.6371 | 0.6764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 | 7 | 6 | 0 | 187 | 4464 | 66.02 | 0 | 107.3835 | 107.3835 | -107.3835 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 131.2465 | 131.2465 | 0 | 8.5 | 0 | 21.8744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 128.6216 | 25.7243 | 0.2572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 01:00 | 7 | 6 | 1 | 187 | 4465 | 62.96 | 0 | 29.285 | 29.285 | -29.285 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 35.7928 | 35.7928 | 0 | 8.5 | 0 | 5.9655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 35.0769 | 7.0154 | 0.07015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 02:00 | 7 | 6 | 2 | 187 | 4466 | 62.96 | 1.1305 | 0.84619 | 0.84619 | 0.28435 | Heating | 0.2509 | 8.5 | 0.2509 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.05018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.25602 | 0 | 0.051204 | 0.000512% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 03:00 | 7 | 6 | 3 | 187 | 4467 | 60.98 | 7.1663 | 0 | 0 | 7.1663 | Heating | 6.3232 | 8.5 | 6.3232 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.4523 | 0 | 1.2905 | 0.0129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 04:00 | 7 | 6 | 4 | 187 | 4468 | 60.08 | 14.6285 | 0 | 0 | 14.6285 | Heating | 12.9075 | 8.5 | 12.9075 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.1709 | 0 | 2.6342 | 0.02634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 05:00 | 7 | 6 | 5 | 187 | 4469 | 60.08 | 11.9083 | 0 | 0 | 11.9083 | Heating | 10.5073 | 8.5 | 10.5073 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.7217 | 0 | 2.1443 | 0.02144% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 06:00 | 7 | 6 | 6 | 187 | 4470 | 62.96 | 1416.6524 | 185.2455 | 185.2455 | 1231.4069 | Heating | 1086.5355 | 8.5 | 1086.5355 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.3071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1108.7097 | 0 | 221.7419 | 2.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 07:00 | 7 | 6 | 7 | 187 | 4471 | 64.94 | 539.4533 | 149.3153 | 149.3153 | 390.138 | Heating | 344.2394 | 8.5 | 344.2394 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.8479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 351.2647 | 0 | 70.2529 | 0.7025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 08:00 | 7 | 6 | 8 | 187 | 4472 | 64.94 | 57.5898 | 467.8038 | 467.8038 | -410.2139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 571.7601 | 571.7601 | 0 | 8.5 | 0 | 95.2934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 560.3249 | 112.065 | 1.121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 09:00 | 7 | 6 | 9 | 187 | 4473 | 73.04 | 0 | 649.4701 | 649.4701 | -649.4701 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 793.7967 | 793.7967 | 0 | 8.5 | 0 | 132.2995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 777.9208 | 155.5842 | 1.556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 10:00 | 7 | 6 | 10 | 187 | 4474 | 77 | 0 | 803.739 | 803.739 | -803.739 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 982.3477 | 982.3477 | 0 | 8.5 | 0 | 163.7246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 962.7007 | 192.5401 | 1.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 11:00 | 7 | 6 | 11 | 187 | 4475 | 77 | 0 | 1553.9107 | 1553.9107 | -1553.9107 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1899.2242 | 1899.2242 | 0 | 8.5 | 0 | 316.5374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1861.2397 | 372.2479 | 3.722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 12:00 | 7 | 6 | 12 | 187 | 4476 | 82.04 | 0 | 2004.6893 | 2004.6893 | -2004.6893 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2450.1758 | 2450.1758 | 0 | 8.5 | 0 | 408.3626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2401.1723 | 480.2345 | 4.802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 13:00 | 7 | 6 | 13 | 187 | 4477 | 82.94 | 0 | 2316.8332 | 2316.8332 | -2316.8332 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2831.685 | 2831.685 | 0 | 8.5 | 0 | 471.9475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2775.0513 | 555.0103 | 5.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 14:00 | 7 | 6 | 14 | 187 | 4478 | 82.94 | 0 | 2177.9386 | 2177.9386 | -2177.9386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2661.925 | 2661.925 | 0 | 8.5 | 0 | 443.6542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2608.6865 | 521.7373 | 5.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 15:00 | 7 | 6 | 15 | 187 | 4479 | 84.92 | 0 | 2025.1428 | 2025.1428 | -2025.1428 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2475.1746 | 2475.1746 | 0 | 8.5 | 0 | 412.5291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2425.6711 | 485.1342 | 4.851% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 16:00 | 7 | 6 | 16 | 187 | 4480 | 84.02 | 0 | 2049.4378 | 2049.4378 | -2049.4378 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2504.8685 | 2504.8685 | 0 | 8.5 | 0 | 417.4781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2454.7711 | 490.9542 | 4.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 17:00 | 7 | 6 | 17 | 187 | 4481 | 84.02 | 0 | 1776.8598 | 1776.8598 | -1776.8598 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2171.7175 | 2171.7175 | 0 | 8.5 | 0 | 361.9529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2128.2832 | 425.6566 | 4.257% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 18:00 | 7 | 6 | 18 | 187 | 4482 | 82.04 | 0 | 332.9721 | 332.9721 | -332.9721 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 406.9659 | 406.9659 | 0 | 8.5 | 0 | 67.8277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 398.8266 | 79.7653 | 0.7977% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 19:00 | 7 | 6 | 19 | 187 | 4483 | 80.96 | 0 | 129.0341 | 129.0341 | -129.0341 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 157.7083 | 157.7083 | 0 | 8.5 | 0 | 26.2847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 154.5541 | 30.9108 | 0.3091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 20:00 | 7 | 6 | 20 | 187 | 4484 | 80.96 | 0 | 87.7301 | 87.7301 | -87.7301 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 107.2257 | 107.2257 | 0 | 8.5 | 0 | 17.8709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 105.0812 | 21.0162 | 0.2102% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 21:00 | 7 | 6 | 21 | 187 | 4485 | 78.08 | 0 | 58.199 | 58.199 | -58.199 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 71.1321 | 71.1321 | 0 | 8.5 | 0 | 11.8553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 69.7094 | 13.9419 | 0.1394% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 22:00 | 7 | 6 | 22 | 187 | 4486 | 77 | 0 | 24.4793 | 24.4793 | -24.4793 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 29.9192 | 29.9192 | 0 | 8.5 | 0 | 4.9865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 29.3208 | 5.8642 | 0.05864% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-06 23:00 | 7 | 6 | 23 | 187 | 4487 | 77 | 0 | 0.57192 | 0.57192 | -0.57192 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.69901 | 0.69901 | 0 | 8.5 | 0 | 0.1165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.68503 | 0.13701 | 0.00137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 | 7 | 7 | 0 | 188 | 4488 | 73.04 | 1.3313 | 0 | 0 | 1.3313 | Heating | 1.1747 | 8.5 | 1.1747 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.23494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.1987 | 0 | 0.23973 | 0.002397% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 01:00 | 7 | 7 | 1 | 188 | 4489 | 73.4 | 4.3045 | 0 | 0 | 4.3045 | Heating | 3.7981 | 8.5 | 3.7981 | 0 | 7.7605 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.75962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.8756 | 0 | 0.77512 | 0.007751% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 02:00 | 7 | 7 | 2 | 188 | 4490 | 73.04 | 7.4284 | 0 | 0 | 7.4284 | Heating | 6.5545 | 8.5 | 6.5545 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.6882 | 0 | 1.3376 | 0.01338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 03:00 | 7 | 7 | 3 | 188 | 4491 | 71.96 | 11.4271 | 0 | 0 | 11.4271 | Heating | 10.0827 | 8.5 | 10.0827 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0165 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.2885 | 0 | 2.0577 | 0.02058% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 04:00 | 7 | 7 | 4 | 188 | 4492 | 69.98 | 16.7802 | 0 | 0 | 16.7802 | Heating | 14.8061 | 8.5 | 14.8061 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.9612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.1082 | 0 | 3.0216 | 0.03022% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 05:00 | 7 | 7 | 5 | 188 | 4493 | 69.98 | 17.9512 | 0 | 0 | 17.9512 | Heating | 15.8393 | 8.5 | 15.8393 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.1679 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.1625 | 0 | 3.2325 | 0.03233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 06:00 | 7 | 7 | 6 | 188 | 4494 | 73.04 | 15.4576 | 0 | 0 | 15.4576 | Heating | 13.6391 | 8.5 | 13.6391 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.9174 | 0 | 2.7835 | 0.02783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 07:00 | 7 | 7 | 7 | 188 | 4495 | 73.94 | 13.9959 | 0 | 0 | 13.9959 | Heating | 12.3493 | 8.5 | 12.3493 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.6013 | 0 | 2.5203 | 0.0252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 08:00 | 7 | 7 | 8 | 188 | 4496 | 75.02 | 1508.9185 | 0 | 0 | 1508.9185 | Heating | 1331.3987 | 8.5 | 1331.3987 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.2797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1358.5701 | 0 | 271.714 | 2.717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 09:00 | 7 | 7 | 9 | 188 | 4497 | 77 | 493.1772 | 0 | 0 | 493.1772 | Heating | 435.1564 | 8.5 | 435.1564 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.0313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 444.0371 | 0 | 88.8074 | 0.8881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 10:00 | 7 | 7 | 10 | 188 | 4498 | 78.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-07 11:00 | 7 | 7 | 11 | 188 | 4499 | 78.08 | 0 | 161.9902 | 161.9902 | -161.9902 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 197.988 | 197.988 | 0 | 8.5 | 0 | 32.998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 194.0283 | 38.8057 | 0.3881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 12:00 | 7 | 7 | 12 | 188 | 4500 | 82.04 | 0 | 1190.0105 | 1190.0105 | -1190.0105 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1454.4573 | 1454.4573 | 0 | 8.5 | 0 | 242.4095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1425.3681 | 285.0736 | 2.851% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 13:00 | 7 | 7 | 13 | 188 | 4501 | 86 | 0 | 2678.6887 | 2678.6887 | -2678.6887 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3273.9529 | 3273.9529 | 0 | 8.5 | 0 | 545.6588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3208.4738 | 641.6948 | 6.417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 14:00 | 7 | 7 | 14 | 188 | 4502 | 86 | 0 | 3539.1373 | 3539.1373 | -3539.1373 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4325.6123 | 4325.6123 | 0 | 8.5 | 0 | 720.9354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4239.1 | 847.82 | 8.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 15:00 | 7 | 7 | 15 | 188 | 4503 | 78.98 | 0 | 4094.2199 | 4094.2199 | -4094.2199 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5004.0465 | 5004.0465 | 0 | 8.5 | 0 | 834.0078 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4903.9656 | 980.7931 | 9.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 16:00 | 7 | 7 | 16 | 188 | 4504 | 80.96 | 0 | 4753.6474 | 4753.6474 | -4753.6474 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5810.0135 | 5810.0135 | 0 | 8.5 | 0 | 968.3356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5693.8132 | 1138.7626 | 11.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 17:00 | 7 | 7 | 17 | 188 | 4505 | 80.96 | 0 | 4582.9558 | 4582.9558 | -4582.9558 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5601.3904 | 5601.3904 | 0 | 8.5 | 0 | 933.5651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5489.3626 | 1097.8725 | 10.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 18:00 | 7 | 7 | 18 | 188 | 4506 | 78.98 | 0 | 3582.4661 | 3582.4661 | -3582.4661 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4378.5697 | 4378.5697 | 0 | 8.5 | 0 | 729.7616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4290.9983 | 858.1997 | 8.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 19:00 | 7 | 7 | 19 | 188 | 4507 | 78.08 | 0 | 1357.0372 | 1357.0372 | -1357.0372 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1658.601 | 1658.601 | 0 | 8.5 | 0 | 276.4335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1625.429 | 325.0858 | 3.251% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 20:00 | 7 | 7 | 20 | 188 | 4508 | 78.08 | 0 | 1054.1909 | 1054.1909 | -1054.1909 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1288.4555 | 1288.4555 | 0 | 8.5 | 0 | 214.7426 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1262.6864 | 252.5373 | 2.525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 21:00 | 7 | 7 | 21 | 188 | 4509 | 75.92 | 0 | 841.0381 | 841.0381 | -841.0381 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1027.9355 | 1027.9355 | 0 | 8.5 | 0 | 171.3226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1007.3768 | 201.4754 | 2.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 22:00 | 7 | 7 | 22 | 188 | 4510 | 75.02 | 0 | 726.485 | 726.485 | -726.485 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 887.9261 | 887.9261 | 0 | 8.5 | 0 | 147.9877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 870.1676 | 174.0335 | 1.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-07 23:00 | 7 | 7 | 23 | 188 | 4511 | 75.02 | 0 | 393.2431 | 393.2431 | -393.2431 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 480.6304 | 480.6304 | 0 | 8.5 | 0 | 80.1051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 471.0178 | 94.2036 | 0.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 | 7 | 8 | 0 | 189 | 4512 | 73.94 | 0 | 264.4756 | 264.4756 | -264.4756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 323.2479 | 323.2479 | 0 | 8.5 | 0 | 53.8747 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 316.783 | 63.3566 | 0.6336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 01:00 | 7 | 8 | 1 | 189 | 4513 | 73.94 | 0 | 175.6958 | 175.6958 | -175.6958 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 214.7393 | 214.7393 | 0 | 8.5 | 0 | 35.7899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 210.4446 | 42.0889 | 0.4209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 02:00 | 7 | 8 | 2 | 189 | 4514 | 73.94 | 0 | 126.7774 | 126.7774 | -126.7774 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 154.9501 | 154.9501 | 0 | 8.5 | 0 | 25.825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 151.8511 | 30.3702 | 0.3037% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 03:00 | 7 | 8 | 3 | 189 | 4515 | 73.94 | 0 | 107.8966 | 107.8966 | -107.8966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 131.8737 | 131.8737 | 0 | 8.5 | 0 | 21.9789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 129.2362 | 25.8472 | 0.2585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 04:00 | 7 | 8 | 4 | 189 | 4516 | 73.94 | 0 | 104.7802 | 104.7802 | -104.7802 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 128.0647 | 128.0647 | 0 | 8.5 | 0 | 21.3441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 125.5034 | 25.1007 | 0.251% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 05:00 | 7 | 8 | 5 | 189 | 4517 | 73.94 | 0 | 199.0783 | 199.0783 | -199.0783 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 243.3179 | 243.3179 | 0 | 8.5 | 0 | 40.553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 238.4515 | 47.6903 | 0.4769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 06:00 | 7 | 8 | 6 | 189 | 4518 | 73.94 | 103.2717 | 1532.2457 | 1532.2457 | -1428.974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1872.7447 | 1872.7447 | 0 | 8.5 | 0 | 312.1241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1835.2898 | 367.058 | 3.671% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 07:00 | 7 | 8 | 7 | 189 | 4519 | 75.02 | 0 | 1735.0365 | 1735.0365 | -1735.0365 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2120.6001 | 2120.6001 | 0 | 8.5 | 0 | 353.4334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2078.1881 | 415.6376 | 4.156% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 08:00 | 7 | 8 | 8 | 189 | 4520 | 75.02 | 0 | 4309.0861 | 4309.0861 | -4309.0861 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5266.6607 | 5266.6607 | 0 | 8.5 | 0 | 877.7768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5161.3275 | 1032.2655 | 10.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 09:00 | 7 | 8 | 9 | 189 | 4521 | 73.04 | 0 | 5016.3756 | 5016.3756 | -5016.3756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6131.1257 | 6131.1257 | 0 | 8.5 | 0 | 1021.8543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6008.5032 | 1201.7006 | 12.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 10:00 | 7 | 8 | 10 | 189 | 4522 | 75.92 | 0 | 6213.3229 | 6213.3229 | -6213.3229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7594.0614 | 7594.0614 | 0 | 8.5 | 0 | 1265.6769 | 30% | 1 | 50.63% | 0% | 0% | 0% | 17.0304 | 0 | 0 | 0 | 17.0304 | 0 | 7442.1801 | 1488.436 | 14.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3049
2007-07-08 11:00 | 7 | 8 | 11 | 189 | 4523 | 75.92 | 0 | 7866.3962 | 7866.3962 | -7866.3962 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9614.4843 | 9614.4843 | 0 | 8.5 | 0 | 1602.414 | 32.05% | 1 | 64.1% | 0% | 0% | 0% | 29.2997 | 0 | 0 | 0 | 29.2997 | 0 | 9422.1946 | 1884.4389 | 18.84% | 1 | 37.69% | 0% | 0% | 4.3192 | 0 | 0 | 4.3192 | 33.6189
2007-07-08 12:00 | 7 | 8 | 12 | 189 | 4524 | 77 | 0 | 9584.2099 | 9584.2099 | -9584.2099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11714.0343 | 11714.0343 | 0 | 8.5 | 0 | 1952.3391 | 39.05% | 1 | 78.09% | 0% | 0% | 0% | 46.1486 | 0 | 0 | 0 | 46.1486 | 0 | 11479.7536 | 2295.9507 | 22.96% | 1 | 45.92% | 0% | 0% | 6.8029 | 0 | 0 | 6.8029 | 52.9515
2007-07-08 13:00 | 7 | 8 | 13 | 189 | 4525 | 78.08 | 0 | 11261.4665 | 11261.4665 | -11261.4665 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13764.0146 | 13764.0146 | 0 | 8.5 | 0 | 2294.0024 | 45.88% | 1 | 91.76% | 0% | 0% | 0% | 66.8724 | 0 | 0 | 0 | 66.8724 | 0 | 13488.7343 | 2697.7469 | 26.98% | 1 | 53.95% | 0% | 0% | 9.8579 | 0 | 0 | 9.8579 | 76.7303
2007-07-08 14:00 | 7 | 8 | 14 | 189 | 4526 | 78.08 | 0 | 11813.9291 | 11813.9291 | -11813.9291 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14439.2466 | 14439.2466 | 0 | 8.5 | 0 | 2406.5411 | 48.13% | 1 | 96.26% | 0% | 0% | 0% | 74.6596 | 0 | 0 | 0 | 74.6596 | 0 | 14150.4617 | 2830.0923 | 28.3% | 1 | 56.6% | 0% | 0% | 11.0058 | 0 | 0 | 11.0058 | 85.6654
2007-07-08 15:00 | 7 | 8 | 15 | 189 | 4527 | 80.96 | 0 | 11046.6537 | 11046.6537 | -11046.6537 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13501.4657 | 13501.4657 | 0 | 8.5 | 0 | 2250.2443 | 45% | 1 | 90.01% | 0% | 0% | 0% | 63.9748 | 0 | 0 | 0 | 63.9748 | 0 | 13231.4364 | 2646.2873 | 26.46% | 1 | 52.93% | 0% | 0% | 9.4308 | 0 | 0 | 9.4308 | 73.4056
2007-07-08 16:00 | 7 | 8 | 16 | 189 | 4528 | 78.98 | 0 | 9962.3871 | 9962.3871 | -9962.3871 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12176.251 | 12176.251 | 0 | 8.5 | 0 | 2029.3752 | 40.59% | 1 | 81.18% | 0% | 0% | 0% | 50.4446 | 0 | 0 | 0 | 50.4446 | 0 | 11932.7259 | 2386.5452 | 23.87% | 1 | 47.73% | 0% | 0% | 7.4362 | 0 | 0 | 7.4362 | 57.8808
2007-07-08 17:00 | 7 | 8 | 17 | 189 | 4529 | 78.98 | 0 | 9006.5331 | 9006.5331 | -9006.5331 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11007.9849 | 11007.9849 | 0 | 8.5 | 0 | 1834.6642 | 36.69% | 1 | 73.39% | 0% | 0% | 0% | 40.0001 | 0 | 0 | 0 | 40.0001 | 0 | 10787.8252 | 2157.565 | 21.58% | 1 | 43.15% | 0% | 0% | 5.8966 | 0 | 0 | 5.8966 | 45.8967
2007-07-08 18:00 | 7 | 8 | 18 | 189 | 4530 | 78.08 | 0 | 5808.5427 | 5808.5427 | -5808.5427 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7099.3299 | 7099.3299 | 0 | 8.5 | 0 | 1183.2217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6957.3433 | 1391.4687 | 13.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 19:00 | 7 | 8 | 19 | 189 | 4531 | 73.94 | 0 | 4914.1653 | 4914.1653 | -4914.1653 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6006.202 | 6006.202 | 0 | 8.5 | 0 | 1001.0337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5886.078 | 1177.2156 | 11.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 20:00 | 7 | 8 | 20 | 189 | 4532 | 73.94 | 0 | 3851.6835 | 3851.6835 | -3851.6835 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4707.6131 | 4707.6131 | 0 | 8.5 | 0 | 784.6022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4613.4609 | 922.6922 | 9.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 21:00 | 7 | 8 | 21 | 189 | 4533 | 69.98 | 0 | 2034.4915 | 2034.4915 | -2034.4915 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2486.6007 | 2486.6007 | 0 | 8.5 | 0 | 414.4335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2436.8687 | 487.3737 | 4.874% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 22:00 | 7 | 8 | 22 | 189 | 4534 | 68 | 0 | 501.5829 | 501.5829 | -501.5829 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 613.0457 | 613.0457 | 0 | 8.5 | 0 | 102.1743 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 600.7848 | 120.157 | 1.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-08 23:00 | 7 | 8 | 23 | 189 | 4535 | 68 | 0 | 363.1482 | 363.1482 | -363.1482 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 443.8478 | 443.8478 | 0 | 8.5 | 0 | 73.9746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 434.9708 | 86.9942 | 0.8699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 | 7 | 9 | 0 | 190 | 4536 | 64.94 | 0 | 260.9932 | 260.9932 | -260.9932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 318.9917 | 318.9917 | 0 | 8.5 | 0 | 53.1653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 312.6119 | 62.5224 | 0.6252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 01:00 | 7 | 9 | 1 | 190 | 4537 | 64.04 | 0 | 202.3384 | 202.3384 | -202.3384 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 247.3025 | 247.3025 | 0 | 8.5 | 0 | 41.2171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 242.3565 | 48.4713 | 0.4847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 02:00 | 7 | 9 | 2 | 190 | 4538 | 64.04 | 0 | 89.9158 | 89.9158 | -89.9158 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 109.8971 | 109.8971 | 0 | 8.5 | 0 | 18.3162 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 107.6991 | 21.5398 | 0.2154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 03:00 | 7 | 9 | 3 | 190 | 4539 | 62.96 | 0 | 14.8202 | 14.8202 | -14.8202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18.1136 | 18.1136 | 0 | 8.5 | 0 | 3.0189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 17.7513 | 3.5503 | 0.0355% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 04:00 | 7 | 9 | 4 | 190 | 4540 | 62.96 | 1.0801 | 0 | 0 | 1.0801 | Heating | 0.95304 | 8.5 | 0.95304 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.19061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.97249 | 0 | 0.1945 | 0.001945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 05:00 | 7 | 9 | 5 | 190 | 4541 | 62.96 | 0.29885 | 0 | 0 | 0.29885 | Heating | 0.26369 | 8.5 | 0.26369 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.052738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.26907 | 0 | 0.053814 | 0.0005381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 06:00 | 7 | 9 | 6 | 190 | 4542 | 62.96 | 652.7433 | 903.0301 | 903.0301 | -250.2869 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1103.7035 | 1103.7035 | 0 | 8.5 | 0 | 183.9506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1081.6294 | 216.3259 | 2.163% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 07:00 | 7 | 9 | 7 | 190 | 4543 | 64.04 | 0 | 2473.6512 | 2473.6512 | -2473.6512 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3023.3515 | 3023.3515 | 0 | 8.5 | 0 | 503.8919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2962.8844 | 592.5769 | 5.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 08:00 | 7 | 9 | 8 | 190 | 4544 | 64.94 | 0 | 5250.1862 | 5250.1862 | -5250.1862 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6416.8942 | 6416.8942 | 0 | 8.5 | 0 | 1069.4824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6288.5563 | 1257.7113 | 12.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 09:00 | 7 | 9 | 9 | 190 | 4545 | 66.92 | 0 | 7676.6869 | 7676.6869 | -7676.6869 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9382.6173 | 9382.6173 | 0 | 8.5 | 0 | 1563.7696 | 31.28% | 1 | 62.55% | 0% | 0% | 0% | 27.6999 | 0 | 0 | 0 | 27.6999 | 0 | 9194.965 | 1838.993 | 18.39% | 1 | 36.78% | 0% | 0% | 4.0833 | 0 | 0 | 4.0833 | 31.7833
2007-07-09 10:00 | 7 | 9 | 10 | 190 | 4546 | 71.96 | 0 | 9894.2853 | 9894.2853 | -9894.2853 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12093.0154 | 12093.0154 | 0 | 8.5 | 0 | 2015.5026 | 40.31% | 1 | 80.62% | 0% | 0% | 0% | 49.655 | 0 | 0 | 0 | 49.655 | 0 | 11851.1551 | 2370.231 | 23.7% | 1 | 47.4% | 0% | 0% | 7.3198 | 0 | 0 | 7.3198 | 56.9748
2007-07-09 11:00 | 7 | 9 | 11 | 190 | 4547 | 71.96 | 0 | 10942.6892 | 10942.6892 | -10942.6892 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13374.3979 | 13374.3979 | 0 | 8.5 | 0 | 2229.0663 | 44.58% | 1 | 89.16% | 0% | 0% | 0% | 62.5985 | 0 | 0 | 0 | 62.5985 | 0 | 13106.9099 | 2621.382 | 26.21% | 1 | 52.43% | 0% | 0% | 9.2279 | 0 | 0 | 9.2279 | 71.8264
2007-07-09 12:00 | 7 | 9 | 12 | 190 | 4548 | 75.92 | 0 | 11353.5786 | 11353.5786 | -11353.5786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13876.596 | 13876.596 | 0 | 8.5 | 0 | 2312.766 | 46.26% | 1 | 92.51% | 0% | 0% | 0% | 68.1371 | 0 | 0 | 0 | 68.1371 | 0 | 13599.0641 | 2719.8128 | 27.2% | 1 | 54.4% | 0% | 0% | 10.0443 | 0 | 0 | 10.0443 | 78.1815
2007-07-09 13:00 | 7 | 9 | 13 | 190 | 4549 | 73.94 | 0 | 11706.1894 | 11706.1894 | -11706.1894 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14307.5649 | 14307.5649 | 0 | 8.5 | 0 | 2384.5941 | 47.69% | 1 | 95.38% | 0% | 0% | 0% | 73.1029 | 0 | 0 | 0 | 73.1029 | 0 | 14021.4136 | 2804.2827 | 28.04% | 1 | 56.09% | 0% | 0% | 10.7764 | 0 | 0 | 10.7764 | 83.8792
2007-07-09 14:00 | 7 | 9 | 14 | 190 | 4550 | 73.94 | 0 | 12243.7881 | 12243.7881 | -12243.7881 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14964.6299 | 14964.6299 | 0 | 8.5 | 0 | 2494.105 | 49.88% | 1 | 99.76% | 0% | 0% | 0% | 81.056 | 0 | 0 | 0 | 81.056 | 0 | 14665.3373 | 2933.0675 | 29.33% | 1 | 58.66% | 0% | 0% | 11.9488 | 0 | 0 | 11.9488 | 93.0047
2007-07-09 15:00 | 7 | 9 | 15 | 190 | 4551 | 75.02 | 0 | 12812.0489 | 12812.0489 | -12812.0489 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15659.1709 | 15659.1709 | 0 | 8.5 | 0 | 2609.8618 | 52.2% | 2 | 52.2% | 52.2% | 0% | 0% | 18.2697 | 18.2697 | 0 | 0 | 36.5395 | 0 | 15345.9875 | 3069.1975 | 30.69% | 1 | 61.38% | 0% | 0% | 13.2629 | 0 | 0 | 13.2629 | 49.8024
2007-07-09 16:00 | 7 | 9 | 16 | 190 | 4552 | 75.02 | 0 | 12872.4565 | 12872.4565 | -12872.4565 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15733.0024 | 15733.0024 | 0 | 8.5 | 0 | 2622.1671 | 52.44% | 2 | 52.44% | 52.44% | 0% | 0% | 18.4685 | 18.4685 | 0 | 0 | 36.9369 | 0 | 15418.3424 | 3083.6685 | 30.84% | 1 | 61.67% | 0% | 0% | 13.4072 | 0 | 0 | 13.4072 | 50.3441
2007-07-09 17:00 | 7 | 9 | 17 | 190 | 4553 | 75.02 | 0 | 12215.3782 | 12215.3782 | -12215.3782 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14929.9066 | 14929.9066 | 0 | 8.5 | 0 | 2488.3178 | 49.77% | 1 | 99.53% | 0% | 0% | 0% | 80.624 | 0 | 0 | 0 | 80.624 | 0 | 14631.3085 | 2926.2617 | 29.26% | 1 | 58.53% | 0% | 0% | 11.8851 | 0 | 0 | 11.8851 | 92.5091
2007-07-09 18:00 | 7 | 9 | 18 | 190 | 4554 | 71.96 | 0 | 7921.826 | 7921.826 | -7921.826 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9682.2318 | 9682.2318 | 0 | 8.5 | 0 | 1613.7053 | 32.27% | 1 | 64.55% | 0% | 0% | 0% | 29.7767 | 0 | 0 | 0 | 29.7767 | 0 | 9488.5871 | 1897.7174 | 18.98% | 1 | 37.95% | 0% | 0% | 4.3895 | 0 | 0 | 4.3895 | 34.1662
2007-07-09 19:00 | 7 | 9 | 19 | 190 | 4555 | 71.06 | 0 | 6883.2167 | 6883.2167 | -6883.2167 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8412.8205 | 8412.8205 | 0 | 8.5 | 0 | 1402.1367 | 30% | 1 | 56.09% | 0% | 0% | 0% | 21.5526 | 0 | 0 | 0 | 21.5526 | 0 | 8244.564 | 1648.9128 | 16.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.8271
2007-07-09 20:00 | 7 | 9 | 20 | 190 | 4556 | 68 | 0 | 5489.6536 | 5489.6536 | -5489.6536 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6709.5766 | 6709.5766 | 0 | 8.5 | 0 | 1118.2628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6575.3851 | 1315.077 | 13.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 21:00 | 7 | 9 | 21 | 190 | 4557 | 68 | 0 | 2502.0202 | 2502.0202 | -2502.0202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3058.0247 | 3058.0247 | 0 | 8.5 | 0 | 509.6708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2996.8642 | 599.3728 | 5.994% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 22:00 | 7 | 9 | 22 | 190 | 4558 | 66.92 | 0 | 709.3038 | 709.3038 | -709.3038 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 866.9268 | 866.9268 | 0 | 8.5 | 0 | 144.4878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 849.5883 | 169.9177 | 1.699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-09 23:00 | 7 | 9 | 23 | 190 | 4559 | 66.92 | 0 | 484.5534 | 484.5534 | -484.5534 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 592.2319 | 592.2319 | 0 | 8.5 | 0 | 98.7053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 580.3873 | 116.0775 | 1.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 | 7 | 10 | 0 | 191 | 4560 | 66.92 | 0 | 282.0776 | 282.0776 | -282.0776 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 344.7616 | 344.7616 | 0 | 8.5 | 0 | 57.4603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 337.8663 | 67.5733 | 0.6757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 01:00 | 7 | 10 | 1 | 191 | 4561 | 66.2 | 0 | 129.2889 | 129.2889 | -129.2889 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 158.0198 | 158.0198 | 0 | 8.5 | 0 | 26.3366 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 154.8594 | 30.9719 | 0.3097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 02:00 | 7 | 10 | 2 | 191 | 4562 | 66.92 | 0 | 50.2504 | 50.2504 | -50.2504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 61.4172 | 61.4172 | 0 | 8.5 | 0 | 10.2362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 60.1888 | 12.0378 | 0.1204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 03:00 | 7 | 10 | 3 | 191 | 4563 | 66.92 | 0 | 18.4279 | 18.4279 | -18.4279 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 22.523 | 22.523 | 0 | 8.5 | 0 | 3.7538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 22.0726 | 4.4145 | 0.04415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 04:00 | 7 | 10 | 4 | 191 | 4564 | 66.92 | 0 | 1.7554 | 1.7554 | -1.7554 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.1455 | 2.1455 | 0 | 8.5 | 0 | 0.35758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.1026 | 0.42052 | 0.004205% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 05:00 | 7 | 10 | 5 | 191 | 4565 | 66.92 | 0 | 0.83236 | 0.83236 | -0.83236 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.0173 | 1.0173 | 0 | 8.5 | 0 | 0.16955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.99698 | 0.1994 | 0.001994% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 06:00 | 7 | 10 | 6 | 191 | 4566 | 66.02 | 620.5668 | 620.5897 | 620.5897 | -0.022914 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 758.4985 | 758.4985 | 0 | 8.5 | 0 | 126.4164 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 743.3286 | 148.6657 | 1.487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 07:00 | 7 | 10 | 7 | 191 | 4567 | 64.94 | 203.3437 | 831.5163 | 831.5163 | -628.1726 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1016.2977 | 1016.2977 | 0 | 8.5 | 0 | 169.3829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 995.9717 | 199.1943 | 1.992% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 08:00 | 7 | 10 | 8 | 191 | 4568 | 64.94 | 0 | 3355.8923 | 3355.8923 | -3355.8923 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4101.6461 | 4101.6461 | 0 | 8.5 | 0 | 683.6077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4019.6132 | 803.9226 | 8.039% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 09:00 | 7 | 10 | 9 | 191 | 4569 | 71.96 | 0 | 4438.5067 | 4438.5067 | -4438.5067 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5424.8415 | 5424.8415 | 0 | 8.5 | 0 | 904.1403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5316.3447 | 1063.2689 | 10.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 10:00 | 7 | 10 | 10 | 191 | 4570 | 75.02 | 0 | 5854.0253 | 5854.0253 | -5854.0253 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7154.9198 | 7154.9198 | 0 | 8.5 | 0 | 1192.4866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7011.8214 | 1402.3643 | 14.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 11:00 | 7 | 10 | 11 | 191 | 4571 | 75.02 | 0 | 6798.7175 | 6798.7175 | -6798.7175 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8309.5436 | 8309.5436 | 0 | 8.5 | 0 | 1384.9239 | 30% | 1 | 55.4% | 0% | 0% | 0% | 20.9489 | 0 | 0 | 0 | 20.9489 | 0 | 8143.3528 | 1628.6706 | 16.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.2234
2007-07-10 12:00 | 7 | 10 | 12 | 191 | 4572 | 77 | 0 | 7474.4427 | 7474.4427 | -7474.4427 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9135.4299 | 9135.4299 | 0 | 8.5 | 0 | 1522.5717 | 30.45% | 1 | 60.9% | 0% | 0% | 0% | 26.0501 | 0 | 0 | 0 | 26.0501 | 0 | 8952.7213 | 1790.5443 | 17.91% | 1 | 35.81% | 0% | 0% | 3.8401 | 0 | 0 | 3.8401 | 29.8903
2007-07-10 13:00 | 7 | 10 | 13 | 191 | 4573 | 80.96 | 0 | 8226.4123 | 8226.4123 | -8226.4123 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10054.5039 | 10054.5039 | 0 | 8.5 | 0 | 1675.7507 | 33.52% | 1 | 67.03% | 0% | 0% | 0% | 32.476 | 0 | 0 | 0 | 32.476 | 0 | 9853.4139 | 1970.6828 | 19.71% | 1 | 39.41% | 0% | 0% | 4.7874 | 0 | 0 | 4.7874 | 37.2634
2007-07-10 14:00 | 7 | 10 | 14 | 191 | 4574 | 80.96 | 0 | 8833.9659 | 8833.9659 | -8833.9659 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10797.0694 | 10797.0694 | 0 | 8.5 | 0 | 1799.5116 | 35.99% | 1 | 71.98% | 0% | 0% | 0% | 38.2593 | 0 | 0 | 0 | 38.2593 | 0 | 10581.128 | 2116.2256 | 21.16% | 1 | 42.32% | 0% | 0% | 5.6399 | 0 | 0 | 5.6399 | 43.8992
2007-07-10 15:00 | 7 | 10 | 15 | 191 | 4575 | 78.98 | 0 | 9023.6008 | 9023.6008 | -9023.6008 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11028.8454 | 11028.8454 | 0 | 8.5 | 0 | 1838.1409 | 36.76% | 1 | 73.53% | 0% | 0% | 0% | 40.1747 | 0 | 0 | 0 | 40.1747 | 0 | 10808.2685 | 2161.6537 | 21.62% | 1 | 43.23% | 0% | 0% | 5.9223 | 0 | 0 | 5.9223 | 46.097
2007-07-10 16:00 | 7 | 10 | 16 | 191 | 4576 | 80.96 | 0 | 9020.8369 | 9020.8369 | -9020.8369 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11025.4673 | 11025.4673 | 0 | 8.5 | 0 | 1837.5779 | 36.75% | 1 | 73.5% | 0% | 0% | 0% | 40.1464 | 0 | 0 | 0 | 40.1464 | 0 | 10804.958 | 2160.9916 | 21.61% | 1 | 43.22% | 0% | 0% | 5.9181 | 0 | 0 | 5.9181 | 46.0645
2007-07-10 17:00 | 7 | 10 | 17 | 191 | 4577 | 80.96 | 0 | 8446.8323 | 8446.8323 | -8446.8323 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10323.9062 | 10323.9062 | 0 | 8.5 | 0 | 1720.651 | 34.41% | 1 | 68.83% | 0% | 0% | 0% | 34.5123 | 0 | 0 | 0 | 34.5123 | 0 | 10117.4281 | 2023.4856 | 20.23% | 1 | 40.47% | 0% | 0% | 5.0876 | 0 | 0 | 5.0876 | 39.5999
2007-07-10 18:00 | 7 | 10 | 18 | 191 | 4578 | 78.98 | 0 | 5152.6327 | 5152.6327 | -5152.6327 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6297.6622 | 6297.6622 | 0 | 8.5 | 0 | 1049.6104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6171.7089 | 1234.3418 | 12.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 19:00 | 7 | 10 | 19 | 191 | 4579 | 75.92 | 0 | 4176.9054 | 4176.9054 | -4176.9054 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5105.1067 | 5105.1067 | 0 | 8.5 | 0 | 850.8511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5003.0045 | 1000.6009 | 10.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 20:00 | 7 | 10 | 20 | 191 | 4580 | 75.92 | 0 | 2131.5138 | 2131.5138 | -2131.5138 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2605.1836 | 2605.1836 | 0 | 8.5 | 0 | 434.1973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2553.0799 | 510.616 | 5.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 21:00 | 7 | 10 | 21 | 191 | 4581 | 71.96 | 0 | 741.9784 | 741.9784 | -741.9784 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 906.8625 | 906.8625 | 0 | 8.5 | 0 | 151.1438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 888.7253 | 177.7451 | 1.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 22:00 | 7 | 10 | 22 | 191 | 4582 | 69.98 | 0 | 36.9378 | 36.9378 | -36.9378 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 45.1462 | 45.1462 | 0 | 8.5 | 0 | 7.5244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 44.2433 | 8.8487 | 0.08849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-10 23:00 | 7 | 10 | 23 | 191 | 4583 | 69.98 | 6.6247 | 0 | 0 | 6.6247 | Heating | 5.8453 | 8.5 | 5.8453 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.9646 | 0 | 1.1929 | 0.01193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 | 7 | 11 | 0 | 192 | 4584 | 64.94 | 21.7293 | 0 | 0 | 21.7293 | Heating | 19.1729 | 8.5 | 19.1729 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.8346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.5642 | 0 | 3.9128 | 0.03913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 01:00 | 7 | 11 | 1 | 192 | 4585 | 66.02 | 38.5559 | 0 | 0 | 38.5559 | Heating | 34.0199 | 8.5 | 34.0199 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.7142 | 0 | 6.9428 | 0.06943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 02:00 | 7 | 11 | 2 | 192 | 4586 | 66.02 | 52.0584 | 0 | 0 | 52.0584 | Heating | 45.9339 | 8.5 | 45.9339 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.1868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 46.8713 | 0 | 9.3743 | 0.09374% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 03:00 | 7 | 11 | 3 | 192 | 4587 | 60.98 | 72.4162 | 0 | 0 | 72.4162 | Heating | 63.8967 | 8.5 | 63.8967 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.7793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.2007 | 0 | 13.0401 | 0.1304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 04:00 | 7 | 11 | 4 | 192 | 4588 | 59 | 104.6535 | 0 | 0 | 104.6535 | Heating | 92.3413 | 8.5 | 92.3413 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.4683 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 94.2258 | 0 | 18.8452 | 0.1885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 05:00 | 7 | 11 | 5 | 192 | 4589 | 59 | 94.7757 | 0 | 0 | 94.7757 | Heating | 83.6256 | 8.5 | 83.6256 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.7251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 85.3323 | 0 | 17.0665 | 0.1707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 06:00 | 7 | 11 | 6 | 192 | 4590 | 62.06 | 2675.1216 | 198.6386 | 198.6386 | 2476.483 | Heating | 2185.132 | 8.5 | 2185.132 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 437.0264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2229.7266 | 0 | 445.9453 | 4.459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 07:00 | 7 | 11 | 7 | 192 | 4591 | 68 | 1233.362 | 225.3155 | 225.3155 | 1008.0465 | Heating | 889.4528 | 8.5 | 889.4528 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.8906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 907.6049 | 0 | 181.521 | 1.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 08:00 | 7 | 11 | 8 | 192 | 4592 | 68 | 292.8971 | 1749.0576 | 1749.0576 | -1456.1606 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2137.7371 | 2137.7371 | 0 | 8.5 | 0 | 356.2895 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2094.9824 | 418.9965 | 4.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 09:00 | 7 | 11 | 9 | 192 | 4593 | 73.94 | 0 | 3072.0372 | 3072.0372 | -3072.0372 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3754.7121 | 3754.7121 | 0 | 8.5 | 0 | 625.7853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3679.6178 | 735.9236 | 7.359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 10:00 | 7 | 11 | 10 | 192 | 4594 | 77 | 0 | 4419.0042 | 4419.0042 | -4419.0042 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5401.0051 | 5401.0051 | 0 | 8.5 | 0 | 900.1675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5292.985 | 1058.597 | 10.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 11:00 | 7 | 11 | 11 | 192 | 4595 | 77 | 0 | 6324.5018 | 6324.5018 | -6324.5018 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7729.9466 | 7729.9466 | 0 | 8.5 | 0 | 1288.3244 | 30% | 1 | 51.53% | 0% | 0% | 0% | 17.7394 | 0 | 0 | 0 | 17.7394 | 0 | 7575.3477 | 1515.0695 | 15.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.014
2007-07-11 12:00 | 7 | 11 | 12 | 192 | 4596 | 82.04 | 0 | 7666.9506 | 7666.9506 | -7666.9506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9370.7175 | 9370.7175 | 0 | 8.5 | 0 | 1561.7862 | 31.24% | 1 | 62.47% | 0% | 0% | 0% | 27.6192 | 0 | 0 | 0 | 27.6192 | 0 | 9183.3031 | 1836.6606 | 18.37% | 1 | 36.73% | 0% | 0% | 4.0714 | 0 | 0 | 4.0714 | 31.6906
2007-07-11 13:00 | 7 | 11 | 13 | 192 | 4597 | 86 | 0 | 8993.1421 | 8993.1421 | -8993.1421 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10991.6182 | 10991.6182 | 0 | 8.5 | 0 | 1831.9364 | 36.64% | 1 | 73.28% | 0% | 0% | 0% | 39.8635 | 0 | 0 | 0 | 39.8635 | 0 | 10771.7858 | 2154.3572 | 21.54% | 1 | 43.09% | 0% | 0% | 5.8764 | 0 | 0 | 5.8764 | 45.7399
2007-07-11 14:00 | 7 | 11 | 14 | 192 | 4598 | 86 | 0 | 9619.8083 | 9619.8083 | -9619.8083 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11757.5435 | 11757.5435 | 0 | 8.5 | 0 | 1959.5906 | 39.19% | 1 | 78.38% | 0% | 0% | 0% | 46.5437 | 0 | 0 | 0 | 46.5437 | 0 | 11522.3926 | 2304.4785 | 23.04% | 1 | 46.09% | 0% | 0% | 6.8612 | 0 | 0 | 6.8612 | 53.4049
2007-07-11 15:00 | 7 | 11 | 15 | 192 | 4599 | 86 | 0 | 9337.9978 | 9337.9978 | -9337.9978 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11413.1084 | 11413.1084 | 0 | 8.5 | 0 | 1902.1847 | 38.04% | 1 | 76.09% | 0% | 0% | 0% | 43.4673 | 0 | 0 | 0 | 43.4673 | 0 | 11184.8462 | 2236.9692 | 22.37% | 1 | 44.74% | 0% | 0% | 6.4077 | 0 | 0 | 6.4077 | 49.8749
2007-07-11 16:00 | 7 | 11 | 16 | 192 | 4600 | 86 | 0 | 8813.5803 | 8813.5803 | -8813.5803 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10772.1537 | 10772.1537 | 0 | 8.5 | 0 | 1795.3589 | 35.91% | 1 | 71.81% | 0% | 0% | 0% | 38.0565 | 0 | 0 | 0 | 38.0565 | 0 | 10556.7106 | 2111.3421 | 21.11% | 1 | 42.23% | 0% | 0% | 5.6101 | 0 | 0 | 5.6101 | 43.6666
2007-07-11 17:00 | 7 | 11 | 17 | 192 | 4601 | 86 | 0 | 8192.0109 | 8192.0109 | -8192.0109 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10012.4577 | 10012.4577 | 0 | 8.5 | 0 | 1668.743 | 33.37% | 1 | 66.75% | 0% | 0% | 0% | 32.1645 | 0 | 0 | 0 | 32.1645 | 0 | 9812.2086 | 1962.4417 | 19.62% | 1 | 39.25% | 0% | 0% | 4.7415 | 0 | 0 | 4.7415 | 36.906
2007-07-11 18:00 | 7 | 11 | 18 | 192 | 4602 | 82.04 | 0 | 5114.7141 | 5114.7141 | -5114.7141 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6251.3172 | 6251.3172 | 0 | 8.5 | 0 | 1041.8862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6126.2909 | 1225.2582 | 12.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 19:00 | 7 | 11 | 19 | 192 | 4603 | 78.08 | 0 | 4360.9947 | 4360.9947 | -4360.9947 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5330.1046 | 5330.1046 | 0 | 8.5 | 0 | 888.3508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5223.5025 | 1044.7005 | 10.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 20:00 | 7 | 11 | 20 | 192 | 4604 | 78.08 | 0 | 3238.1658 | 3238.1658 | -3238.1658 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3957.7582 | 3957.7582 | 0 | 8.5 | 0 | 659.6264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3878.603 | 775.7206 | 7.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 21:00 | 7 | 11 | 21 | 192 | 4605 | 73.04 | 0 | 1422.4019 | 1422.4019 | -1422.4019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1738.4912 | 1738.4912 | 0 | 8.5 | 0 | 289.7485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1703.7214 | 340.7443 | 3.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 22:00 | 7 | 11 | 22 | 192 | 4606 | 71.96 | 0 | 162.1993 | 162.1993 | -162.1993 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 198.2436 | 198.2436 | 0 | 8.5 | 0 | 33.0406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 194.2787 | 38.8557 | 0.3886% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-11 23:00 | 7 | 11 | 23 | 192 | 4607 | 71.96 | 0 | 48.3143 | 48.3143 | -48.3143 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 59.0508 | 59.0508 | 0 | 8.5 | 0 | 9.8418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 57.8698 | 11.574 | 0.1157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 | 7 | 12 | 0 | 193 | 4608 | 68 | 0 | 10.6702 | 10.6702 | -10.6702 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13.0414 | 13.0414 | 0 | 8.5 | 0 | 2.1736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 12.7806 | 2.5561 | 0.02556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 01:00 | 7 | 12 | 1 | 193 | 4609 | 66.92 | 0 | 0.063666 | 0.063666 | -0.063666 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.077814 | 0.077814 | 0 | 8.5 | 0 | 0.012969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.076257 | 0.015251 | 0.0001525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 02:00 | 7 | 12 | 2 | 193 | 4610 | 66.92 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-12 03:00 | 7 | 12 | 3 | 193 | 4611 | 66.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-12 04:00 | 7 | 12 | 4 | 193 | 4612 | 66.02 | 0.073801 | 0 | 0 | 0.073801 | Heating | 0.065119 | 8.5 | 0.065119 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.013024 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.066448 | 0 | 0.01329 | 0.0001329% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 05:00 | 7 | 12 | 5 | 193 | 4613 | 66.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-12 06:00 | 7 | 12 | 6 | 193 | 4614 | 66.02 | 592.2372 | 533.8245 | 533.8245 | 58.4127 | Heating | 51.5406 | 8.5 | 51.5406 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.3081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 52.5925 | 0 | 10.5185 | 0.1052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 07:00 | 7 | 12 | 7 | 193 | 4615 | 69.08 | 152.7591 | 528.6794 | 528.6794 | -375.9203 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 646.1637 | 646.1637 | 0 | 8.5 | 0 | 107.6939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 633.2404 | 126.6481 | 1.266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 08:00 | 7 | 12 | 8 | 193 | 4616 | 69.08 | 0 | 3225.3472 | 3225.3472 | -3225.3472 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3942.091 | 3942.091 | 0 | 8.5 | 0 | 657.0152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3863.2492 | 772.6498 | 7.726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 09:00 | 7 | 12 | 9 | 193 | 4617 | 77 | 0 | 3979.1679 | 3979.1679 | -3979.1679 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4863.4274 | 4863.4274 | 0 | 8.5 | 0 | 810.5712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4766.1588 | 953.2318 | 9.532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 10:00 | 7 | 12 | 10 | 193 | 4618 | 78.98 | 0 | 4556.0177 | 4556.0177 | -4556.0177 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5568.466 | 5568.466 | 0 | 8.5 | 0 | 928.0777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5457.0967 | 1091.4193 | 10.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 11:00 | 7 | 12 | 11 | 193 | 4619 | 78.98 | 0 | 5949.25 | 5949.25 | -5949.25 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7271.3055 | 7271.3055 | 0 | 8.5 | 0 | 1211.8843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7125.8794 | 1425.1759 | 14.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 12:00 | 7 | 12 | 12 | 193 | 4620 | 84.02 | 0 | 7121.9335 | 7121.9335 | -7121.9335 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8704.5854 | 8704.5854 | 0 | 8.5 | 0 | 1450.7642 | 30% | 1 | 58.03% | 0% | 0% | 0% | 23.3106 | 0 | 0 | 0 | 23.3106 | 0 | 8530.4937 | 1706.0987 | 17.06% | 1 | 34.12% | 0% | 0% | 3.4363 | 0 | 0 | 3.4363 | 26.7469
2007-07-12 13:00 | 7 | 12 | 13 | 193 | 4621 | 86 | 0 | 8020.3488 | 8020.3488 | -8020.3488 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9802.6486 | 9802.6486 | 0 | 8.5 | 0 | 1633.7748 | 32.68% | 1 | 65.35% | 0% | 0% | 0% | 30.6354 | 0 | 0 | 0 | 30.6354 | 0 | 9606.5956 | 1921.3191 | 19.21% | 1 | 38.43% | 0% | 0% | 4.5161 | 0 | 0 | 4.5161 | 35.1514
2007-07-12 14:00 | 7 | 12 | 14 | 193 | 4622 | 86 | 0 | 9071.1622 | 9071.1622 | -9071.1622 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11086.976 | 11086.976 | 0 | 8.5 | 0 | 1847.8293 | 36.96% | 1 | 73.91% | 0% | 0% | 0% | 40.6634 | 0 | 0 | 0 | 40.6634 | 0 | 10865.2365 | 2173.0473 | 21.73% | 1 | 43.46% | 0% | 0% | 5.9943 | 0 | 0 | 5.9943 | 46.6577
2007-07-12 15:00 | 7 | 12 | 15 | 193 | 4623 | 87.08 | 0 | 9608.5469 | 9608.5469 | -9608.5469 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11743.7795 | 11743.7795 | 0 | 8.5 | 0 | 1957.2966 | 39.15% | 1 | 78.29% | 0% | 0% | 0% | 46.4185 | 0 | 0 | 0 | 46.4185 | 0 | 11508.904 | 2301.7808 | 23.02% | 1 | 46.04% | 0% | 0% | 6.8427 | 0 | 0 | 6.8427 | 53.2612
2007-07-12 16:00 | 7 | 12 | 16 | 193 | 4624 | 86 | 0 | 9885.1194 | 9885.1194 | -9885.1194 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12081.8126 | 12081.8126 | 0 | 8.5 | 0 | 2013.6354 | 40.27% | 1 | 80.55% | 0% | 0% | 0% | 49.5492 | 0 | 0 | 0 | 49.5492 | 0 | 11840.1764 | 2368.0353 | 23.68% | 1 | 47.36% | 0% | 0% | 7.3042 | 0 | 0 | 7.3042 | 56.8535
2007-07-12 17:00 | 7 | 12 | 17 | 193 | 4625 | 86 | 0 | 9914.2851 | 9914.2851 | -9914.2851 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12117.4596 | 12117.4596 | 0 | 8.5 | 0 | 2019.5766 | 40.39% | 1 | 80.78% | 0% | 0% | 0% | 49.8861 | 0 | 0 | 0 | 49.8861 | 0 | 11875.1104 | 2375.0221 | 23.75% | 1 | 47.5% | 0% | 0% | 7.3539 | 0 | 0 | 7.3539 | 57.24
2007-07-12 18:00 | 7 | 12 | 18 | 193 | 4626 | 84.02 | 0 | 6518.697 | 6518.697 | -6518.697 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7967.2964 | 7967.2964 | 0 | 8.5 | 0 | 1327.8827 | 30% | 1 | 53.12% | 0% | 0% | 0% | 19.0173 | 0 | 0 | 0 | 19.0173 | 0 | 7807.9505 | 1561.5901 | 15.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.2918
2007-07-12 19:00 | 7 | 12 | 19 | 193 | 4627 | 80.96 | 0 | 6020.3154 | 6020.3154 | -6020.3154 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7358.1633 | 7358.1633 | 0 | 8.5 | 0 | 1226.3606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7211.0001 | 1442.2 | 14.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 20:00 | 7 | 12 | 20 | 193 | 4628 | 80.96 | 0 | 5300.4988 | 5300.4988 | -5300.4988 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6478.3874 | 6478.3874 | 0 | 8.5 | 0 | 1079.7312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6348.8197 | 1269.7639 | 12.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 21:00 | 7 | 12 | 21 | 193 | 4629 | 75.02 | 0 | 2537.5133 | 2537.5133 | -2537.5133 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3101.4051 | 3101.4051 | 0 | 8.5 | 0 | 516.9009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3039.377 | 607.8754 | 6.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 22:00 | 7 | 12 | 22 | 193 | 4630 | 75.92 | 0 | 880.1815 | 880.1815 | -880.1815 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1075.7774 | 1075.7774 | 0 | 8.5 | 0 | 179.2962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1054.2618 | 210.8524 | 2.109% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-12 23:00 | 7 | 12 | 23 | 193 | 4631 | 75.92 | 0 | 990.5597 | 990.5597 | -990.5597 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1210.6841 | 1210.6841 | 0 | 8.5 | 0 | 201.7807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1186.4705 | 237.2941 | 2.373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 | 7 | 13 | 0 | 194 | 4632 | 71.06 | 0 | 919.4087 | 919.4087 | -919.4087 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1123.7218 | 1123.7218 | 0 | 8.5 | 0 | 187.287 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1101.2474 | 220.2495 | 2.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 01:00 | 7 | 13 | 1 | 194 | 4633 | 69.98 | 0 | 804.2362 | 804.2362 | -804.2362 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 982.9554 | 982.9554 | 0 | 8.5 | 0 | 163.8259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 963.2963 | 192.6593 | 1.927% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 02:00 | 7 | 13 | 2 | 194 | 4634 | 69.98 | 0 | 733.1047 | 733.1047 | -733.1047 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 896.0168 | 896.0168 | 0 | 8.5 | 0 | 149.3361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 878.0965 | 175.6193 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 03:00 | 7 | 13 | 3 | 194 | 4635 | 66.92 | 0 | 830.9262 | 830.9262 | -830.9262 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1015.5765 | 1015.5765 | 0 | 8.5 | 0 | 169.2627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 995.265 | 199.053 | 1.991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 04:00 | 7 | 13 | 4 | 194 | 4636 | 66.92 | 0 | 824.031 | 824.031 | -824.031 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1007.149 | 1007.149 | 0 | 8.5 | 0 | 167.8582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 987.0061 | 197.4012 | 1.974% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 05:00 | 7 | 13 | 5 | 194 | 4637 | 66.92 | 0 | 880.1956 | 880.1956 | -880.1956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1075.7946 | 1075.7946 | 0 | 8.5 | 0 | 179.2991 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1054.2788 | 210.8558 | 2.109% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 06:00 | 7 | 13 | 6 | 194 | 4638 | 69.08 | 0 | 2667.8385 | 2667.8385 | -2667.8385 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3260.6915 | 3260.6915 | 0 | 8.5 | 0 | 543.4486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3195.4777 | 639.0955 | 6.391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 07:00 | 7 | 13 | 7 | 194 | 4639 | 73.94 | 0 | 2376.0908 | 2376.0908 | -2376.0908 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2904.111 | 2904.111 | 0 | 8.5 | 0 | 484.0185 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2846.0288 | 569.2058 | 5.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 08:00 | 7 | 13 | 8 | 194 | 4640 | 73.94 | 0 | 3139.3288 | 3139.3288 | -3139.3288 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3836.9574 | 3836.9574 | 0 | 8.5 | 0 | 639.4929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3760.2182 | 752.0436 | 7.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 09:00 | 7 | 13 | 9 | 194 | 4641 | 78.98 | 0 | 6054.5396 | 6054.5396 | -6054.5396 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7399.9929 | 7399.9929 | 0 | 8.5 | 0 | 1233.3321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7251.993 | 1450.3986 | 14.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 10:00 | 7 | 13 | 10 | 194 | 4642 | 80.96 | 0 | 8035.0626 | 8035.0626 | -8035.0626 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9820.6321 | 9820.6321 | 0 | 8.5 | 0 | 1636.772 | 32.74% | 1 | 65.47% | 0% | 0% | 0% | 30.7648 | 0 | 0 | 0 | 30.7648 | 0 | 9624.2195 | 1924.8439 | 19.25% | 1 | 38.5% | 0% | 0% | 4.5352 | 0 | 0 | 4.5352 | 35.2999
2007-07-13 11:00 | 7 | 13 | 11 | 194 | 4643 | 80.96 | 0 | 9553.226 | 9553.226 | -9553.226 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11676.1651 | 11676.1651 | 0 | 8.5 | 0 | 1946.0275 | 38.92% | 1 | 77.84% | 0% | 0% | 0% | 45.8061 | 0 | 0 | 0 | 45.8061 | 0 | 11442.6418 | 2288.5284 | 22.89% | 1 | 45.77% | 0% | 0% | 6.7525 | 0 | 0 | 6.7525 | 52.5586
2007-07-13 12:00 | 7 | 13 | 12 | 194 | 4644 | 84.92 | 0 | 11037.7091 | 11037.7091 | -11037.7091 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13490.5333 | 13490.5333 | 0 | 8.5 | 0 | 2248.4222 | 44.97% | 1 | 89.94% | 0% | 0% | 0% | 63.8558 | 0 | 0 | 0 | 63.8558 | 0 | 13220.7226 | 2644.1445 | 26.44% | 1 | 52.88% | 0% | 0% | 9.4132 | 0 | 0 | 9.4132 | 73.269
2007-07-13 13:00 | 7 | 13 | 13 | 194 | 4645 | 86 | 0 | 11424.0858 | 11424.0858 | -11424.0858 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13962.7716 | 13962.7716 | 0 | 8.5 | 0 | 2327.1286 | 46.54% | 1 | 93.09% | 0% | 0% | 0% | 69.1143 | 0 | 0 | 0 | 69.1143 | 0 | 13683.5161 | 2736.7032 | 27.37% | 1 | 54.73% | 0% | 0% | 10.1884 | 0 | 0 | 10.1884 | 79.3027
2007-07-13 14:00 | 7 | 13 | 14 | 194 | 4646 | 86 | 0 | 11244.6906 | 11244.6906 | -11244.6906 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13743.5108 | 13743.5108 | 0 | 8.5 | 0 | 2290.5851 | 45.81% | 1 | 91.62% | 0% | 0% | 0% | 66.6435 | 0 | 0 | 0 | 66.6435 | 0 | 13468.6405 | 2693.7281 | 26.94% | 1 | 53.87% | 0% | 0% | 9.8242 | 0 | 0 | 9.8242 | 76.4677
2007-07-13 15:00 | 7 | 13 | 15 | 194 | 4647 | 87.08 | 0 | 10976.5541 | 10976.5541 | -10976.5541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13415.7884 | 13415.7884 | 0 | 8.5 | 0 | 2235.9647 | 44.72% | 1 | 89.44% | 0% | 0% | 0% | 63.045 | 0 | 0 | 0 | 63.045 | 0 | 13147.4726 | 2629.4945 | 26.29% | 1 | 52.59% | 0% | 0% | 9.2937 | 0 | 0 | 9.2937 | 72.3387
2007-07-13 16:00 | 7 | 13 | 16 | 194 | 4648 | 86 | 0 | 10744.1801 | 10744.1801 | -10744.1801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13131.7757 | 13131.7757 | 0 | 8.5 | 0 | 2188.6293 | 43.77% | 1 | 87.55% | 0% | 0% | 0% | 60.0174 | 0 | 0 | 0 | 60.0174 | 0 | 12869.1402 | 2573.828 | 25.74% | 1 | 51.48% | 0% | 0% | 8.8474 | 0 | 0 | 8.8474 | 68.8648
2007-07-13 17:00 | 7 | 13 | 17 | 194 | 4649 | 86 | 0 | 9846.457 | 9846.457 | -9846.457 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12034.5586 | 12034.5586 | 0 | 8.5 | 0 | 2005.7598 | 40.12% | 1 | 80.23% | 0% | 0% | 0% | 49.1046 | 0 | 0 | 0 | 49.1046 | 0 | 11793.8674 | 2358.7735 | 23.59% | 1 | 47.18% | 0% | 0% | 7.2387 | 0 | 0 | 7.2387 | 56.3433
2007-07-13 18:00 | 7 | 13 | 18 | 194 | 4650 | 84.92 | 0 | 6160.6014 | 6160.6014 | -6160.6014 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7529.624 | 7529.624 | 0 | 8.5 | 0 | 1254.9373 | 30% | 1 | 50.2% | 0% | 0% | 0% | 16.6998 | 0 | 0 | 0 | 16.6998 | 0 | 7379.0315 | 1475.8063 | 14.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9744
2007-07-13 19:00 | 7 | 13 | 19 | 194 | 4651 | 82.94 | 0 | 4643.5369 | 4643.5369 | -4643.5369 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5675.4339 | 5675.4339 | 0 | 8.5 | 0 | 945.9057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5561.9253 | 1112.3851 | 11.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 20:00 | 7 | 13 | 20 | 194 | 4652 | 82.94 | 0 | 3197.8344 | 3197.8344 | -3197.8344 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3908.4642 | 3908.4642 | 0 | 8.5 | 0 | 651.4107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3830.2949 | 766.059 | 7.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 21:00 | 7 | 13 | 21 | 194 | 4653 | 78.98 | 0 | 1597.8636 | 1597.8636 | -1597.8636 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1952.9444 | 1952.9444 | 0 | 8.5 | 0 | 325.4907 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1913.8855 | 382.7771 | 3.828% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 22:00 | 7 | 13 | 22 | 194 | 4654 | 77 | 0 | 917.6578 | 917.6578 | -917.6578 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1121.5818 | 1121.5818 | 0 | 8.5 | 0 | 186.9303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1099.1501 | 219.83 | 2.198% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-13 23:00 | 7 | 13 | 23 | 194 | 4655 | 77 | 0 | 498.2983 | 498.2983 | -498.2983 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 609.0313 | 609.0313 | 0 | 8.5 | 0 | 101.5052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 596.8507 | 119.3701 | 1.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 | 7 | 14 | 0 | 195 | 4656 | 73.94 | 0 | 275.8649 | 275.8649 | -275.8649 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 337.1682 | 337.1682 | 0 | 8.5 | 0 | 56.1947 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 330.4249 | 66.085 | 0.6608% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 01:00 | 7 | 14 | 1 | 195 | 4657 | 73.04 | 0 | 112.6106 | 112.6106 | -112.6106 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 137.6351 | 137.6351 | 0 | 8.5 | 0 | 22.9392 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 134.8824 | 26.9765 | 0.2698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 02:00 | 7 | 14 | 2 | 195 | 4658 | 73.04 | 0 | 45.5541 | 45.5541 | -45.5541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 55.6773 | 55.6773 | 0 | 8.5 | 0 | 9.2795 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 54.5637 | 10.9127 | 0.1091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 03:00 | 7 | 14 | 3 | 195 | 4659 | 69.08 | 0 | 19.5693 | 19.5693 | -19.5693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23.918 | 23.918 | 0 | 8.5 | 0 | 3.9863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 23.4397 | 4.6879 | 0.04688% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 04:00 | 7 | 14 | 4 | 195 | 4660 | 68 | 0 | 9.2233 | 9.2233 | -9.2233 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11.2729 | 11.2729 | 0 | 8.5 | 0 | 1.8788 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 11.0474 | 2.2095 | 0.02209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 05:00 | 7 | 14 | 5 | 195 | 4661 | 68 | 0 | 14.821 | 14.821 | -14.821 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18.1146 | 18.1146 | 0 | 8.5 | 0 | 3.0191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 17.7523 | 3.5505 | 0.0355% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 06:00 | 7 | 14 | 6 | 195 | 4662 | 68 | 0 | 47.4975 | 47.4975 | -47.4975 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 58.0525 | 58.0525 | 0 | 8.5 | 0 | 9.6754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 56.8915 | 11.3783 | 0.1138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 07:00 | 7 | 14 | 7 | 195 | 4663 | 71.96 | 0 | 161.5949 | 161.5949 | -161.5949 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 197.5049 | 197.5049 | 0 | 8.5 | 0 | 32.9175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 193.5548 | 38.711 | 0.3871% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 08:00 | 7 | 14 | 8 | 195 | 4664 | 71.96 | 187.9063 | 527.6522 | 527.6522 | -339.7459 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 644.9082 | 644.9082 | 0 | 8.5 | 0 | 107.4847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 632.0101 | 126.402 | 1.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 09:00 | 7 | 14 | 9 | 195 | 4665 | 77 | 0 | 705.7267 | 705.7267 | -705.7267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 862.5549 | 862.5549 | 0 | 8.5 | 0 | 143.7591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 845.3038 | 169.0608 | 1.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 10:00 | 7 | 14 | 10 | 195 | 4666 | 77 | 0 | 889.5619 | 889.5619 | -889.5619 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1087.2424 | 1087.2424 | 0 | 8.5 | 0 | 181.2071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1065.4975 | 213.0995 | 2.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 11:00 | 7 | 14 | 11 | 195 | 4667 | 78.98 | 0 | 1582.8806 | 1582.8806 | -1582.8806 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1934.6319 | 1934.6319 | 0 | 8.5 | 0 | 322.4386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1895.9392 | 379.1878 | 3.792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 12:00 | 7 | 14 | 12 | 195 | 4668 | 80.06 | 0 | 3355.4808 | 3355.4808 | -3355.4808 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4101.1431 | 4101.1431 | 0 | 8.5 | 0 | 683.5239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4019.1203 | 803.8241 | 8.038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 13:00 | 7 | 14 | 13 | 195 | 4669 | 80.96 | 0 | 4244.267 | 4244.267 | -4244.267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5187.4374 | 5187.4374 | 0 | 8.5 | 0 | 864.5729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5083.6887 | 1016.7377 | 10.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 14:00 | 7 | 14 | 14 | 195 | 4670 | 80.96 | 0 | 4867.5576 | 4867.5576 | -4867.5576 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5949.237 | 5949.237 | 0 | 8.5 | 0 | 991.5395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5830.2523 | 1166.0505 | 11.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 15:00 | 7 | 14 | 15 | 195 | 4671 | 82.04 | 0 | 5539.8253 | 5539.8253 | -5539.8253 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6770.8976 | 6770.8976 | 0 | 8.5 | 0 | 1128.4829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6635.4797 | 1327.0959 | 13.27% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 16:00 | 7 | 14 | 16 | 195 | 4672 | 82.94 | 0 | 6014.018 | 6014.018 | -6014.018 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7350.4665 | 7350.4665 | 0 | 8.5 | 0 | 1225.0777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7203.4572 | 1440.6914 | 14.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 17:00 | 7 | 14 | 17 | 195 | 4673 | 82.94 | 0 | 5846.7401 | 5846.7401 | -5846.7401 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7146.0157 | 7146.0157 | 0 | 8.5 | 0 | 1191.0026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7003.0954 | 1400.6191 | 14.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 18:00 | 7 | 14 | 18 | 195 | 4674 | 78.98 | 0 | 4769.8998 | 4769.8998 | -4769.8998 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5829.8775 | 5829.8775 | 0 | 8.5 | 0 | 971.6463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5713.28 | 1142.656 | 11.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 19:00 | 7 | 14 | 19 | 195 | 4675 | 78.08 | 0 | 1972.1518 | 1972.1518 | -1972.1518 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2410.4078 | 2410.4078 | 0 | 8.5 | 0 | 401.7346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2362.1997 | 472.4399 | 4.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 20:00 | 7 | 14 | 20 | 195 | 4676 | 78.08 | 0 | 1492.9527 | 1492.9527 | -1492.9527 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1824.7199 | 1824.7199 | 0 | 8.5 | 0 | 304.12 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1788.2255 | 357.6451 | 3.576% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 21:00 | 7 | 14 | 21 | 195 | 4677 | 77 | 0 | 1215.1852 | 1215.1852 | -1215.1852 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1485.2264 | 1485.2264 | 0 | 8.5 | 0 | 247.5377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1455.5219 | 291.1044 | 2.911% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 22:00 | 7 | 14 | 22 | 195 | 4678 | 75.92 | 0 | 571.8136 | 571.8136 | -571.8136 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 698.8833 | 698.8833 | 0 | 8.5 | 0 | 116.4805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 684.9056 | 136.9811 | 1.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-14 23:00 | 7 | 14 | 23 | 195 | 4679 | 75.92 | 0 | 297.5612 | 297.5612 | -297.5612 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 363.6859 | 363.6859 | 0 | 8.5 | 0 | 60.6143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 356.4122 | 71.2824 | 0.7128% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 | 7 | 15 | 0 | 196 | 4680 | 73.94 | 0 | 104.2802 | 104.2802 | -104.2802 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 127.4536 | 127.4536 | 0 | 8.5 | 0 | 21.2423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 124.9046 | 24.9809 | 0.2498% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 01:00 | 7 | 15 | 1 | 196 | 4681 | 73.94 | 0 | 20.3533 | 20.3533 | -20.3533 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 24.8763 | 24.8763 | 0 | 8.5 | 0 | 4.1461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 24.3788 | 4.8758 | 0.04876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 02:00 | 7 | 15 | 2 | 196 | 4682 | 73.94 | 2.1381 | 0 | 0 | 2.1381 | Heating | 1.8866 | 8.5 | 1.8866 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.37732 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.9251 | 0 | 0.38502 | 0.00385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 03:00 | 7 | 15 | 3 | 196 | 4683 | 73.04 | 9.4743 | 0 | 0 | 9.4743 | Heating | 8.3597 | 8.5 | 8.3597 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6719 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.5303 | 0 | 1.7061 | 0.01706% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 04:00 | 7 | 15 | 4 | 196 | 4684 | 71.06 | 21.4774 | 0 | 0 | 21.4774 | Heating | 18.9506 | 8.5 | 18.9506 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.7901 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.3374 | 0 | 3.8675 | 0.03867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 05:00 | 7 | 15 | 5 | 196 | 4685 | 71.06 | 15.5733 | 0 | 0 | 15.5733 | Heating | 13.7411 | 8.5 | 13.7411 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.0216 | 0 | 2.8043 | 0.02804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 06:00 | 7 | 15 | 6 | 196 | 4686 | 71.96 | 1429.563 | 638.9831 | 638.9831 | 790.5798 | Heating | 697.5704 | 8.5 | 697.5704 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.5141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 711.8066 | 0 | 142.3613 | 1.424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 07:00 | 7 | 15 | 7 | 196 | 4687 | 71.96 | 281.6607 | 1221.3581 | 1221.3581 | -939.6974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1492.7711 | 1492.7711 | 0 | 8.5 | 0 | 248.7952 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1462.9156 | 292.5831 | 2.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 08:00 | 7 | 15 | 8 | 196 | 4688 | 68 | 0 | 4351.4105 | 4351.4105 | -4351.4105 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5318.3906 | 5318.3906 | 0 | 8.5 | 0 | 886.3984 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5212.0228 | 1042.4046 | 10.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 09:00 | 7 | 15 | 9 | 196 | 4689 | 66.02 | 0 | 5884.192 | 5884.192 | -5884.192 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7191.7903 | 7191.7903 | 0 | 8.5 | 0 | 1198.6317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7047.9545 | 1409.5909 | 14.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 10:00 | 7 | 15 | 10 | 196 | 4690 | 66.02 | 0 | 8644.0156 | 8644.0156 | -8644.0156 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10564.9079 | 10564.9079 | 0 | 8.5 | 0 | 1760.818 | 35.22% | 1 | 70.43% | 0% | 0% | 0% | 36.3935 | 0 | 0 | 0 | 36.3935 | 0 | 10353.6098 | 2070.722 | 20.71% | 1 | 41.41% | 0% | 0% | 5.3649 | 0 | 0 | 5.3649 | 41.7584
2007-07-15 11:00 | 7 | 15 | 11 | 196 | 4691 | 64.94 | 0 | 10429.7469 | 10429.7469 | -10429.7469 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12747.4684 | 12747.4684 | 0 | 8.5 | 0 | 2124.5781 | 42.49% | 1 | 84.98% | 0% | 0% | 0% | 56.0542 | 0 | 0 | 0 | 56.0542 | 0 | 12492.519 | 2498.5038 | 24.99% | 1 | 49.97% | 0% | 0% | 8.2632 | 0 | 0 | 8.2632 | 64.3174
2007-07-15 12:00 | 7 | 15 | 12 | 196 | 4692 | 71.06 | 0 | 11798.3117 | 11798.3117 | -11798.3117 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14420.1588 | 14420.1588 | 0 | 8.5 | 0 | 2403.3598 | 48.07% | 1 | 96.13% | 0% | 0% | 0% | 74.4328 | 0 | 0 | 0 | 74.4328 | 0 | 14131.7556 | 2826.3511 | 28.26% | 1 | 56.53% | 0% | 0% | 10.9724 | 0 | 0 | 10.9724 | 85.4052
2007-07-15 13:00 | 7 | 15 | 13 | 196 | 4693 | 71.96 | 0 | 13067.8464 | 13067.8464 | -13067.8464 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15971.8123 | 15971.8123 | 0 | 8.5 | 0 | 2661.9687 | 53.24% | 2 | 53.24% | 53.24% | 0% | 0% | 19.1196 | 19.1196 | 0 | 0 | 38.2392 | 0 | 15652.3761 | 3130.4752 | 31.3% | 1 | 62.61% | 0% | 0% | 13.8799 | 0 | 0 | 13.8799 | 52.1191
2007-07-15 14:00 | 7 | 15 | 14 | 196 | 4694 | 71.96 | 0 | 14081.2945 | 14081.2945 | -14081.2945 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17210.471 | 17210.471 | 0 | 8.5 | 0 | 2868.4118 | 57.37% | 2 | 57.37% | 57.37% | 0% | 0% | 22.7032 | 22.7032 | 0 | 0 | 45.4064 | 0 | 16866.2616 | 3373.2523 | 33.73% | 1 | 33.73% | 33.73% | 0% | 3.3468 | 3.3468 | 0 | 6.6935 | 52.1
2007-07-15 15:00 | 7 | 15 | 15 | 196 | 4695 | 75.02 | 0 | 14920.8083 | 14920.8083 | -14920.8083 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18236.5435 | 18236.5435 | 0 | 8.5 | 0 | 3039.4239 | 60.79% | 2 | 60.79% | 60.79% | 0% | 0% | 25.9377 | 25.9377 | 0 | 0 | 51.8755 | 0 | 17871.8126 | 3574.3625 | 35.74% | 1 | 35.74% | 35.74% | 0% | 3.8236 | 3.8236 | 0 | 7.6472 | 59.5226
2007-07-15 16:00 | 7 | 15 | 16 | 196 | 4696 | 73.94 | 0 | 15499.2852 | 15499.2852 | -15499.2852 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18943.5707 | 18943.5707 | 0 | 8.5 | 0 | 3157.2618 | 63.15% | 2 | 63.15% | 63.15% | 0% | 0% | 28.3091 | 28.3091 | 0 | 0 | 56.6182 | 0 | 18564.6993 | 3712.9399 | 37.13% | 1 | 37.13% | 37.13% | 0% | 4.1732 | 4.1732 | 0 | 8.3463 | 64.9645
2007-07-15 17:00 | 7 | 15 | 17 | 196 | 4697 | 73.94 | 0 | 15276.4032 | 15276.4032 | -15276.4032 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18671.1594 | 18671.1594 | 0 | 8.5 | 0 | 3111.8599 | 62.24% | 2 | 62.24% | 62.24% | 0% | 0% | 27.3816 | 27.3816 | 0 | 0 | 54.7631 | 0 | 18297.7363 | 3659.5473 | 36.6% | 1 | 36.6% | 36.6% | 0% | 4.0364 | 4.0364 | 0 | 8.0728 | 62.8359
2007-07-15 18:00 | 7 | 15 | 18 | 196 | 4698 | 71.96 | 0 | 10669.4829 | 10669.4829 | -10669.4829 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13040.4791 | 13040.4791 | 0 | 8.5 | 0 | 2173.4132 | 43.47% | 1 | 86.94% | 0% | 0% | 0% | 59.062 | 0 | 0 | 0 | 59.062 | 0 | 12779.6696 | 2555.9339 | 25.56% | 1 | 51.12% | 0% | 0% | 8.7066 | 0 | 0 | 8.7066 | 67.7686
2007-07-15 19:00 | 7 | 15 | 19 | 196 | 4699 | 69.98 | 0 | 9504.2958 | 9504.2958 | -9504.2958 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11616.3616 | 11616.3616 | 0 | 8.5 | 0 | 1936.0603 | 38.72% | 1 | 77.44% | 0% | 0% | 0% | 45.2683 | 0 | 0 | 0 | 45.2683 | 0 | 11384.0343 | 2276.8069 | 22.77% | 1 | 45.54% | 0% | 0% | 6.6732 | 0 | 0 | 6.6732 | 51.9415
2007-07-15 20:00 | 7 | 15 | 20 | 196 | 4700 | 69.98 | 0 | 7846.0764 | 7846.0764 | -7846.0764 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9589.6489 | 9589.6489 | 0 | 8.5 | 0 | 1598.2748 | 31.97% | 1 | 63.93% | 0% | 0% | 0% | 29.1259 | 0 | 0 | 0 | 29.1259 | 0 | 9397.8559 | 1879.5712 | 18.8% | 1 | 37.59% | 0% | 0% | 4.2936 | 0 | 0 | 4.2936 | 33.4195
2007-07-15 21:00 | 7 | 15 | 21 | 196 | 4701 | 64.94 | 0 | 3333.2056 | 3333.2056 | -3333.2056 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4073.9179 | 4073.9179 | 0 | 8.5 | 0 | 678.9863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3992.4396 | 798.4879 | 7.985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 22:00 | 7 | 15 | 22 | 196 | 4702 | 62.06 | 0 | 1190.8747 | 1190.8747 | -1190.8747 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1455.5135 | 1455.5135 | 0 | 8.5 | 0 | 242.5856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1426.4032 | 285.2806 | 2.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-15 23:00 | 7 | 15 | 23 | 196 | 4703 | 62.06 | 0 | 1104.1454 | 1104.1454 | -1104.1454 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1349.5111 | 1349.5111 | 0 | 8.5 | 0 | 224.9185 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1322.5208 | 264.5042 | 2.645% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 | 7 | 16 | 0 | 197 | 4704 | 59 | 0 | 859.3387 | 859.3387 | -859.3387 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1050.3028 | 1050.3028 | 0 | 8.5 | 0 | 175.0505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1029.2967 | 205.8593 | 2.059% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 01:00 | 7 | 16 | 1 | 197 | 4705 | 59 | 0 | 851.3806 | 851.3806 | -851.3806 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1040.5763 | 1040.5763 | 0 | 8.5 | 0 | 173.4294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1019.7648 | 203.953 | 2.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 02:00 | 7 | 16 | 2 | 197 | 4706 | 59 | 0 | 874.0729 | 874.0729 | -874.0729 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1068.3113 | 1068.3113 | 0 | 8.5 | 0 | 178.0519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1046.9451 | 209.389 | 2.094% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 03:00 | 7 | 16 | 3 | 197 | 4707 | 55.94 | 0 | 758.7498 | 758.7498 | -758.7498 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 927.3609 | 927.3609 | 0 | 8.5 | 0 | 154.5602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 908.8137 | 181.7627 | 1.818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 04:00 | 7 | 16 | 4 | 197 | 4708 | 55.94 | 0 | 601.0482 | 601.0482 | -601.0482 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 734.6144 | 734.6144 | 0 | 8.5 | 0 | 122.4357 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 719.9222 | 143.9844 | 1.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 05:00 | 7 | 16 | 5 | 197 | 4709 | 55.94 | 0 | 701.713 | 701.713 | -701.713 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 857.6492 | 857.6492 | 0 | 8.5 | 0 | 142.9415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 840.4962 | 168.0992 | 1.681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 06:00 | 7 | 16 | 6 | 197 | 4710 | 57.92 | 0 | 3773.4288 | 3773.4288 | -3773.4288 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4611.9686 | 4611.9686 | 0 | 8.5 | 0 | 768.6614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4519.7292 | 903.9458 | 9.039% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 07:00 | 7 | 16 | 7 | 197 | 4711 | 60.08 | 0 | 4009.1475 | 4009.1475 | -4009.1475 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4900.0692 | 4900.0692 | 0 | 8.5 | 0 | 816.6782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4802.0678 | 960.4136 | 9.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 08:00 | 7 | 16 | 8 | 197 | 4712 | 60.08 | 0 | 6461.4195 | 6461.4195 | -6461.4195 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7897.2905 | 7897.2905 | 0 | 8.5 | 0 | 1316.2151 | 30% | 1 | 52.65% | 0% | 0% | 0% | 18.6351 | 0 | 0 | 0 | 18.6351 | 0 | 7739.3447 | 1547.8689 | 15.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.9097
2007-07-16 09:00 | 7 | 16 | 9 | 197 | 4713 | 66.02 | 0 | 9807.799 | 9807.799 | -9807.799 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11987.3099 | 11987.3099 | 0 | 8.5 | 0 | 1997.885 | 39.96% | 1 | 79.92% | 0% | 0% | 0% | 48.6624 | 0 | 0 | 0 | 48.6624 | 0 | 11747.5637 | 2349.5127 | 23.5% | 1 | 46.99% | 0% | 0% | 7.1735 | 0 | 0 | 7.1735 | 55.8359
2007-07-16 10:00 | 7 | 16 | 10 | 197 | 4714 | 68 | 0 | 11961.5693 | 11961.5693 | -11961.5693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14619.6959 | 14619.6959 | 0 | 8.5 | 0 | 2436.616 | 48.73% | 1 | 97.46% | 0% | 0% | 0% | 76.823 | 0 | 0 | 0 | 76.823 | 0 | 14327.3019 | 2865.4604 | 28.65% | 1 | 57.31% | 0% | 0% | 11.3248 | 0 | 0 | 11.3248 | 88.1478
2007-07-16 11:00 | 7 | 16 | 11 | 197 | 4715 | 68 | 0 | 13536.0501 | 13536.0501 | -13536.0501 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16544.0612 | 16544.0612 | 0 | 8.5 | 0 | 2757.3435 | 55.15% | 2 | 55.15% | 55.15% | 0% | 0% | 20.732 | 20.732 | 0 | 0 | 41.464 | 0 | 16213.18 | 3242.636 | 32.43% | 1 | 64.85% | 0% | 0% | 15.0504 | 0 | 0 | 15.0504 | 56.5144
2007-07-16 12:00 | 7 | 16 | 12 | 197 | 4716 | 71.96 | 0 | 14776.6979 | 14776.6979 | -14776.6979 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18060.4086 | 18060.4086 | 0 | 8.5 | 0 | 3010.0681 | 60.2% | 2 | 60.2% | 60.2% | 0% | 0% | 25.3652 | 25.3652 | 0 | 0 | 50.7303 | 0 | 17699.2004 | 3539.8401 | 35.4% | 1 | 35.4% | 35.4% | 0% | 3.7392 | 3.7392 | 0 | 7.4783 | 58.2087
2007-07-16 13:00 | 7 | 16 | 13 | 197 | 4717 | 73.04 | 0 | 16081.545 | 16081.545 | -16081.545 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19655.2217 | 19655.2217 | 0 | 8.5 | 0 | 3275.8703 | 65.52% | 2 | 65.52% | 65.52% | 0% | 0% | 30.8151 | 30.8151 | 0 | 0 | 61.6302 | 0 | 19262.1172 | 3852.4234 | 38.52% | 1 | 38.52% | 38.52% | 0% | 4.5426 | 4.5426 | 0 | 9.0851 | 70.7153
2007-07-16 14:00 | 7 | 16 | 14 | 197 | 4718 | 73.04 | 0 | 16520.1972 | 16520.1972 | -16520.1972 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 20191.3521 | 20191.3521 | 0 | 8.5 | 0 | 3365.2254 | 67.3% | 2 | 67.3% | 67.3% | 0% | 0% | 32.7827 | 32.7827 | 0 | 0 | 65.5654 | 0 | 19787.5251 | 3957.505 | 39.58% | 1 | 39.58% | 39.58% | 0% | 4.8326 | 4.8326 | 0 | 9.6652 | 75.2306
2007-07-16 15:00 | 7 | 16 | 15 | 197 | 4719 | 75.92 | 0 | 15932.4487 | 15932.4487 | -15932.4487 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19472.9929 | 19472.9929 | 0 | 8.5 | 0 | 3245.4988 | 64.91% | 2 | 64.91% | 64.91% | 0% | 0% | 30.1619 | 30.1619 | 0 | 0 | 60.3239 | 0 | 19083.533 | 3816.7066 | 38.17% | 1 | 38.17% | 38.17% | 0% | 4.4463 | 4.4463 | 0 | 8.8926 | 69.2165
2007-07-16 16:00 | 7 | 16 | 16 | 197 | 4720 | 75.92 | 0 | 14677.0822 | 14677.0822 | -14677.0822 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17938.656 | 17938.656 | 0 | 8.5 | 0 | 2989.776 | 59.8% | 2 | 59.8% | 59.8% | 0% | 0% | 24.9736 | 24.9736 | 0 | 0 | 49.9472 | 0 | 17579.8828 | 3515.9766 | 35.16% | 1 | 35.16% | 35.16% | 0% | 3.6814 | 3.6814 | 0 | 7.3629 | 57.3101
2007-07-16 17:00 | 7 | 16 | 17 | 197 | 4721 | 75.92 | 0 | 13733.0686 | 13733.0686 | -13733.0686 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16784.8617 | 16784.8617 | 0 | 8.5 | 0 | 2797.4769 | 55.95% | 2 | 55.95% | 55.95% | 0% | 0% | 21.4326 | 21.4326 | 0 | 0 | 42.8652 | 0 | 16449.1644 | 3289.8329 | 32.9% | 1 | 65.8% | 0% | 0% | 15.559 | 0 | 0 | 15.559 | 58.4242
2007-07-16 18:00 | 7 | 16 | 18 | 197 | 4722 | 75.92 | 0 | 9066.5305 | 9066.5305 | -9066.5305 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11081.315 | 11081.315 | 0 | 8.5 | 0 | 1846.8858 | 36.94% | 1 | 73.88% | 0% | 0% | 0% | 40.6156 | 0 | 0 | 0 | 40.6156 | 0 | 10859.6887 | 2171.9377 | 21.72% | 1 | 43.44% | 0% | 0% | 5.9873 | 0 | 0 | 5.9873 | 46.6029
2007-07-16 19:00 | 7 | 16 | 19 | 197 | 4723 | 71.96 | 0 | 8240.8496 | 8240.8496 | -8240.8496 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10072.1496 | 10072.1496 | 0 | 8.5 | 0 | 1678.6916 | 33.57% | 1 | 67.15% | 0% | 0% | 0% | 32.6072 | 0 | 0 | 0 | 32.6072 | 0 | 9870.7066 | 1974.1413 | 19.74% | 1 | 39.48% | 0% | 0% | 4.8068 | 0 | 0 | 4.8068 | 37.414
2007-07-16 20:00 | 7 | 16 | 20 | 197 | 4724 | 71.96 | 0 | 7170.3149 | 7170.3149 | -7170.3149 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8763.7182 | 8763.7182 | 0 | 8.5 | 0 | 1460.6197 | 30% | 1 | 58.42% | 0% | 0% | 0% | 23.6764 | 0 | 0 | 0 | 23.6764 | 0 | 8588.4439 | 1717.6888 | 17.18% | 1 | 34.35% | 0% | 0% | 3.4902 | 0 | 0 | 3.4902 | 27.1667
2007-07-16 21:00 | 7 | 16 | 21 | 197 | 4725 | 64.94 | 0 | 3375.9817 | 3375.9817 | -3375.9817 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4126.1999 | 4126.1999 | 0 | 8.5 | 0 | 687.7 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4043.6759 | 808.7352 | 8.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 22:00 | 7 | 16 | 22 | 197 | 4726 | 62.06 | 0 | 1368.641 | 1368.641 | -1368.641 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1672.7835 | 1672.7835 | 0 | 8.5 | 0 | 278.7973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1639.3278 | 327.8656 | 3.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-16 23:00 | 7 | 16 | 23 | 197 | 4727 | 62.06 | 0 | 1379.8254 | 1379.8254 | -1379.8254 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1686.4533 | 1686.4533 | 0 | 8.5 | 0 | 281.0756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1652.7243 | 330.5449 | 3.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 | 7 | 17 | 0 | 198 | 4728 | 60.08 | 0 | 1183.3226 | 1183.3226 | -1183.3226 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1446.2832 | 1446.2832 | 0 | 8.5 | 0 | 241.0472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1417.3576 | 283.4715 | 2.835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 01:00 | 7 | 17 | 1 | 198 | 4729 | 57.92 | 0 | 920.9002 | 920.9002 | -920.9002 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1125.5447 | 1125.5447 | 0 | 8.5 | 0 | 187.5908 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1103.0338 | 220.6068 | 2.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 02:00 | 7 | 17 | 2 | 198 | 4730 | 57.92 | 0 | 927.2457 | 927.2457 | -927.2457 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1133.3003 | 1133.3003 | 0 | 8.5 | 0 | 188.8834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1110.6343 | 222.1269 | 2.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 03:00 | 7 | 17 | 3 | 198 | 4731 | 53.96 | 0 | 835.3881 | 835.3881 | -835.3881 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1021.0299 | 1021.0299 | 0 | 8.5 | 0 | 170.1717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1000.6093 | 200.1219 | 2.001% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 04:00 | 7 | 17 | 4 | 198 | 4732 | 55.04 | 0 | 720.2652 | 720.2652 | -720.2652 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 880.3241 | 880.3241 | 0 | 8.5 | 0 | 146.7207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 862.7176 | 172.5435 | 1.725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 05:00 | 7 | 17 | 5 | 198 | 4733 | 55.04 | 0 | 834.9659 | 834.9659 | -834.9659 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1020.5138 | 1020.5138 | 0 | 8.5 | 0 | 170.0856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1000.1036 | 200.0207 | 2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 06:00 | 7 | 17 | 6 | 198 | 4734 | 55.94 | 0 | 4386.9741 | 4386.9741 | -4386.9741 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5361.8572 | 5361.8572 | 0 | 8.5 | 0 | 893.6429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5254.6201 | 1050.924 | 10.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 07:00 | 7 | 17 | 7 | 198 | 4735 | 60.98 | 0 | 4443.4162 | 4443.4162 | -4443.4162 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5430.842 | 5430.842 | 0 | 8.5 | 0 | 905.1403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5322.2251 | 1064.445 | 10.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 08:00 | 7 | 17 | 8 | 198 | 4736 | 60.98 | 0 | 6587.2607 | 6587.2607 | -6587.2607 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8051.0964 | 8051.0964 | 0 | 8.5 | 0 | 1341.8494 | 30% | 1 | 53.67% | 0% | 0% | 0% | 19.4805 | 0 | 0 | 0 | 19.4805 | 0 | 7890.0744 | 1578.0149 | 15.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.755
2007-07-17 09:00 | 7 | 17 | 9 | 198 | 4737 | 69.08 | 0 | 9484.693 | 9484.693 | -9484.693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11592.4026 | 11592.4026 | 0 | 8.5 | 0 | 1932.0671 | 38.64% | 1 | 77.28% | 0% | 0% | 0% | 45.0539 | 0 | 0 | 0 | 45.0539 | 0 | 11360.5545 | 2272.1109 | 22.72% | 1 | 45.44% | 0% | 0% | 6.6416 | 0 | 0 | 6.6416 | 51.6954
2007-07-17 10:00 | 7 | 17 | 10 | 198 | 4738 | 71.06 | 0 | 11427.4664 | 11427.4664 | -11427.4664 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13966.9034 | 13966.9034 | 0 | 8.5 | 0 | 2327.8172 | 46.56% | 1 | 93.11% | 0% | 0% | 0% | 69.1613 | 0 | 0 | 0 | 69.1613 | 0 | 13687.5654 | 2737.5131 | 27.38% | 1 | 54.75% | 0% | 0% | 10.1953 | 0 | 0 | 10.1953 | 79.3567
2007-07-17 11:00 | 7 | 17 | 11 | 198 | 4739 | 71.06 | 0 | 12773.5312 | 12773.5312 | -12773.5312 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15612.0937 | 15612.0937 | 0 | 8.5 | 0 | 2602.0156 | 52.04% | 2 | 52.04% | 52.04% | 0% | 0% | 18.1437 | 18.1437 | 0 | 0 | 36.2873 | 0 | 15299.8518 | 3059.9704 | 30.6% | 1 | 61.2% | 0% | 0% | 13.1714 | 0 | 0 | 13.1714 | 49.4587
2007-07-17 12:00 | 7 | 17 | 12 | 198 | 4740 | 78.08 | 0 | 13593.2299 | 13593.2299 | -13593.2299 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16613.9477 | 16613.9477 | 0 | 8.5 | 0 | 2768.9913 | 55.38% | 2 | 55.38% | 55.38% | 0% | 0% | 20.934 | 20.934 | 0 | 0 | 41.8679 | 0 | 16281.6687 | 3256.3337 | 32.56% | 1 | 65.13% | 0% | 0% | 15.197 | 0 | 0 | 15.197 | 57.065
2007-07-17 13:00 | 7 | 17 | 13 | 198 | 4741 | 80.06 | 0 | 14273.566 | 14273.566 | -14273.566 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17445.4695 | 17445.4695 | 0 | 8.5 | 0 | 2907.5783 | 58.15% | 2 | 58.15% | 58.15% | 0% | 0% | 23.4226 | 23.4226 | 0 | 0 | 46.8451 | 0 | 17096.5601 | 3419.312 | 34.19% | 1 | 34.19% | 34.19% | 0% | 3.4528 | 3.4528 | 0 | 6.9056 | 53.7507
2007-07-17 14:00 | 7 | 17 | 14 | 198 | 4742 | 80.06 | 0 | 14885.7168 | 14885.7168 | -14885.7168 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18193.6539 | 18193.6539 | 0 | 8.5 | 0 | 3032.2756 | 60.65% | 2 | 60.65% | 60.65% | 0% | 0% | 25.7976 | 25.7976 | 0 | 0 | 51.5953 | 0 | 17829.7808 | 3565.9562 | 35.66% | 1 | 35.66% | 35.66% | 0% | 3.8029 | 3.8029 | 0 | 7.6059 | 59.2011
2007-07-17 15:00 | 7 | 17 | 15 | 198 | 4743 | 78.98 | 0 | 15299.989 | 15299.989 | -15299.989 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18699.9865 | 18699.9865 | 0 | 8.5 | 0 | 3116.6644 | 62.33% | 2 | 62.33% | 62.33% | 0% | 0% | 27.4789 | 27.4789 | 0 | 0 | 54.9578 | 0 | 18325.9868 | 3665.1974 | 36.65% | 1 | 36.65% | 36.65% | 0% | 4.0508 | 4.0508 | 0 | 8.1015 | 63.0593
2007-07-17 16:00 | 7 | 17 | 16 | 198 | 4744 | 78.98 | 0 | 15352.5756 | 15352.5756 | -15352.5756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18764.259 | 18764.259 | 0 | 8.5 | 0 | 3127.3765 | 62.55% | 2 | 62.55% | 62.55% | 0% | 0% | 27.6966 | 27.6966 | 0 | 0 | 55.3932 | 0 | 18388.9739 | 3677.7948 | 36.78% | 1 | 36.78% | 36.78% | 0% | 4.0829 | 4.0829 | 0 | 8.1657 | 63.5589
2007-07-17 17:00 | 7 | 17 | 17 | 198 | 4745 | 78.98 | 0 | 14921.6707 | 14921.6707 | -14921.6707 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18237.5975 | 18237.5975 | 0 | 8.5 | 0 | 3039.5996 | 60.79% | 2 | 60.79% | 60.79% | 0% | 0% | 25.9412 | 25.9412 | 0 | 0 | 51.8824 | 0 | 17872.8455 | 3574.5691 | 35.75% | 1 | 35.75% | 35.75% | 0% | 3.8241 | 3.8241 | 0 | 7.6482 | 59.5305
2007-07-17 18:00 | 7 | 17 | 18 | 198 | 4746 | 75.92 | 0 | 10090.3107 | 10090.3107 | -10090.3107 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12332.6019 | 12332.6019 | 0 | 8.5 | 0 | 2055.4337 | 41.11% | 1 | 82.22% | 0% | 0% | 0% | 51.9468 | 0 | 0 | 0 | 51.9468 | 0 | 12085.9499 | 2417.19 | 24.17% | 1 | 48.34% | 0% | 0% | 7.6577 | 0 | 0 | 7.6577 | 59.6045
2007-07-17 19:00 | 7 | 17 | 19 | 198 | 4747 | 75.92 | 0 | 9084.1103 | 9084.1103 | -9084.1103 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11102.8015 | 11102.8015 | 0 | 8.5 | 0 | 1850.4669 | 37.01% | 1 | 74.02% | 0% | 0% | 0% | 40.797 | 0 | 0 | 0 | 40.797 | 0 | 10880.7454 | 2176.1491 | 21.76% | 1 | 43.52% | 0% | 0% | 6.014 | 0 | 0 | 6.014 | 46.811
2007-07-17 20:00 | 7 | 17 | 20 | 198 | 4748 | 75.92 | 0 | 7785.4282 | 7785.4282 | -7785.4282 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9515.5233 | 9515.5233 | 0 | 8.5 | 0 | 1585.9206 | 31.72% | 1 | 63.44% | 0% | 0% | 0% | 28.6107 | 0 | 0 | 0 | 28.6107 | 0 | 9325.2129 | 1865.0426 | 18.65% | 1 | 37.3% | 0% | 0% | 4.2176 | 0 | 0 | 4.2176 | 32.8283
2007-07-17 21:00 | 7 | 17 | 21 | 198 | 4749 | 75.02 | 0 | 3406.9624 | 3406.9624 | -3406.9624 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4164.0652 | 4164.0652 | 0 | 8.5 | 0 | 694.0109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4080.7839 | 816.1568 | 8.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 22:00 | 7 | 17 | 22 | 198 | 4750 | 73.04 | 0 | 1449.3908 | 1449.3908 | -1449.3908 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1771.4776 | 1771.4776 | 0 | 8.5 | 0 | 295.2463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1736.048 | 347.2096 | 3.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-17 23:00 | 7 | 17 | 23 | 198 | 4751 | 73.04 | 0 | 1402.7068 | 1402.7068 | -1402.7068 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1714.4194 | 1714.4194 | 0 | 8.5 | 0 | 285.7366 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1680.131 | 336.0262 | 3.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 | 7 | 18 | 0 | 199 | 4752 | 71.06 | 0 | 1211.5125 | 1211.5125 | -1211.5125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1480.7375 | 1480.7375 | 0 | 8.5 | 0 | 246.7896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1451.1228 | 290.2246 | 2.902% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 01:00 | 7 | 18 | 1 | 199 | 4753 | 71.06 | 0 | 1295.1522 | 1295.1522 | -1295.1522 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1582.9638 | 1582.9638 | 0 | 8.5 | 0 | 263.8273 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1551.3045 | 310.2609 | 3.103% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 02:00 | 7 | 18 | 2 | 199 | 4754 | 71.06 | 0 | 1125.9026 | 1125.9026 | -1125.9026 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1376.1031 | 1376.1031 | 0 | 8.5 | 0 | 229.3505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1348.5811 | 269.7162 | 2.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 03:00 | 7 | 18 | 3 | 199 | 4755 | 69.98 | 0 | 813.6379 | 813.6379 | -813.6379 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 994.4463 | 994.4463 | 0 | 8.5 | 0 | 165.7411 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 974.5574 | 194.9115 | 1.949% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 04:00 | 7 | 18 | 4 | 199 | 4756 | 69.98 | 0 | 491.4865 | 491.4865 | -491.4865 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 600.7057 | 600.7057 | 0 | 8.5 | 0 | 100.1176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 588.6916 | 117.7383 | 1.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 05:00 | 7 | 18 | 5 | 199 | 4757 | 69.98 | 0 | 631.0961 | 631.0961 | -631.0961 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 771.3397 | 771.3397 | 0 | 8.5 | 0 | 128.5566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 755.9129 | 151.1826 | 1.512% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 06:00 | 7 | 18 | 6 | 199 | 4758 | 71.06 | 0 | 4627.9094 | 4627.9094 | -4627.9094 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5656.3337 | 5656.3337 | 0 | 8.5 | 0 | 942.7223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5543.207 | 1108.6414 | 11.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 07:00 | 7 | 18 | 7 | 199 | 4759 | 71.96 | 0 | 5665.2014 | 5665.2014 | -5665.2014 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6924.1351 | 6924.1351 | 0 | 8.5 | 0 | 1154.0225 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6785.6524 | 1357.1305 | 13.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 08:00 | 7 | 18 | 8 | 199 | 4760 | 71.96 | 0 | 8394.1918 | 8394.1918 | -8394.1918 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10259.5678 | 10259.5678 | 0 | 8.5 | 0 | 1709.928 | 34.2% | 1 | 68.4% | 0% | 0% | 0% | 34.0197 | 0 | 0 | 0 | 34.0197 | 0 | 10054.3764 | 2010.8753 | 20.11% | 1 | 40.22% | 0% | 0% | 5.015 | 0 | 0 | 5.015 | 39.0346
2007-07-18 09:00 | 7 | 18 | 9 | 199 | 4761 | 73.94 | 0 | 11519.0878 | 11519.0878 | -11519.0878 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14078.8851 | 14078.8851 | 0 | 8.5 | 0 | 2346.4809 | 46.93% | 1 | 93.86% | 0% | 0% | 0% | 70.4434 | 0 | 0 | 0 | 70.4434 | 0 | 13797.3074 | 2759.4615 | 27.59% | 1 | 55.19% | 0% | 0% | 10.3843 | 0 | 0 | 10.3843 | 80.8277
2007-07-18 10:00 | 7 | 18 | 10 | 199 | 4762 | 75.92 | 0 | 12880.2462 | 12880.2462 | -12880.2462 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15742.5231 | 15742.5231 | 0 | 8.5 | 0 | 2623.7539 | 52.48% | 2 | 52.48% | 52.48% | 0% | 0% | 18.4942 | 18.4942 | 0 | 0 | 36.9884 | 0 | 15427.6727 | 3085.5345 | 30.86% | 1 | 61.71% | 0% | 0% | 13.4259 | 0 | 0 | 13.4259 | 50.4142
2007-07-18 11:00 | 7 | 18 | 11 | 199 | 4763 | 75.92 | 0 | 14107.9638 | 14107.9638 | -14107.9638 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17243.0669 | 17243.0669 | 0 | 8.5 | 0 | 2873.8445 | 57.48% | 2 | 57.48% | 57.48% | 0% | 0% | 22.8022 | 22.8022 | 0 | 0 | 45.6045 | 0 | 16898.2055 | 3379.6411 | 33.8% | 1 | 33.8% | 33.8% | 0% | 3.3614 | 3.3614 | 0 | 6.7227 | 52.3272
2007-07-18 12:00 | 7 | 18 | 12 | 199 | 4764 | 82.04 | 0 | 14922.8311 | 14922.8311 | -14922.8311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18239.0158 | 18239.0158 | 0 | 8.5 | 0 | 3039.836 | 60.8% | 2 | 60.8% | 60.8% | 0% | 0% | 25.9458 | 25.9458 | 0 | 0 | 51.8916 | 0 | 17874.2355 | 3574.8471 | 35.75% | 1 | 35.75% | 35.75% | 0% | 3.8248 | 3.8248 | 0 | 7.6495 | 59.5412
2007-07-18 13:00 | 7 | 18 | 13 | 199 | 4765 | 82.94 | 0 | 15577.9721 | 15577.9721 | -15577.9721 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19039.7437 | 19039.7437 | 0 | 8.5 | 0 | 3173.2906 | 63.47% | 2 | 63.47% | 63.47% | 0% | 0% | 28.6408 | 28.6408 | 0 | 0 | 57.2815 | 0 | 18658.9488 | 3731.7898 | 37.32% | 1 | 37.32% | 37.32% | 0% | 4.222 | 4.222 | 0 | 8.4441 | 65.7256
2007-07-18 14:00 | 7 | 18 | 14 | 199 | 4766 | 82.94 | 0 | 16104.4376 | 16104.4376 | -16104.4376 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19683.2015 | 19683.2015 | 0 | 8.5 | 0 | 3280.5336 | 65.61% | 2 | 65.61% | 65.61% | 0% | 0% | 30.9161 | 30.9161 | 0 | 0 | 61.8322 | 0 | 19289.5375 | 3857.9075 | 38.58% | 1 | 38.58% | 38.58% | 0% | 4.5575 | 4.5575 | 0 | 9.1149 | 70.9471
2007-07-18 15:00 | 7 | 18 | 15 | 199 | 4767 | 86 | 0 | 16457.0778 | 16457.0778 | -16457.0778 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 20114.2062 | 20114.2062 | 0 | 8.5 | 0 | 3352.3677 | 67.05% | 2 | 67.05% | 67.05% | 0% | 0% | 32.4953 | 32.4953 | 0 | 0 | 64.9906 | 0 | 19711.9221 | 3942.3844 | 39.42% | 1 | 39.42% | 39.42% | 0% | 4.7903 | 4.7903 | 0 | 9.5805 | 74.5712
2007-07-18 16:00 | 7 | 18 | 16 | 199 | 4768 | 86 | 0 | 16466.9039 | 16466.9039 | -16466.9039 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 20126.2159 | 20126.2159 | 0 | 8.5 | 0 | 3354.3693 | 67.09% | 2 | 67.09% | 67.09% | 0% | 0% | 32.54 | 32.54 | 0 | 0 | 65.0799 | 0 | 19723.6916 | 3944.7383 | 39.45% | 1 | 39.45% | 39.45% | 0% | 4.7968 | 4.7968 | 0 | 9.5937 | 74.6736
2007-07-18 17:00 | 7 | 18 | 17 | 199 | 4769 | 86 | 0 | 16006.5994 | 16006.5994 | -16006.5994 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19563.6215 | 19563.6215 | 0 | 8.5 | 0 | 3260.6036 | 65.21% | 2 | 65.21% | 65.21% | 0% | 0% | 30.4858 | 30.4858 | 0 | 0 | 60.9716 | 0 | 19172.3491 | 3834.4698 | 38.34% | 1 | 38.34% | 38.34% | 0% | 4.494 | 4.494 | 0 | 8.988 | 69.9596
2007-07-18 18:00 | 7 | 18 | 18 | 199 | 4770 | 82.94 | 0 | 11173.0344 | 11173.0344 | -11173.0344 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13655.931 | 13655.931 | 0 | 8.5 | 0 | 2275.9885 | 45.52% | 1 | 91.04% | 0% | 0% | 0% | 65.6708 | 0 | 0 | 0 | 65.6708 | 0 | 13382.8123 | 2676.5625 | 26.77% | 1 | 53.53% | 0% | 0% | 9.6808 | 0 | 0 | 9.6808 | 75.3516
2007-07-18 19:00 | 7 | 18 | 19 | 199 | 4771 | 80.06 | 0 | 10090.7619 | 10090.7619 | -10090.7619 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12333.1535 | 12333.1535 | 0 | 8.5 | 0 | 2055.5256 | 41.11% | 1 | 82.22% | 0% | 0% | 0% | 51.9522 | 0 | 0 | 0 | 51.9522 | 0 | 12086.4904 | 2417.2981 | 24.17% | 1 | 48.35% | 0% | 0% | 7.6585 | 0 | 0 | 7.6585 | 59.6106
2007-07-18 20:00 | 7 | 18 | 20 | 199 | 4772 | 80.06 | 0 | 8538.8002 | 8538.8002 | -8538.8002 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10436.3114 | 10436.3114 | 0 | 8.5 | 0 | 1739.3852 | 34.79% | 1 | 69.58% | 0% | 0% | 0% | 35.3827 | 0 | 0 | 0 | 35.3827 | 0 | 10227.5852 | 2045.517 | 20.46% | 1 | 40.91% | 0% | 0% | 5.2159 | 0 | 0 | 5.2159 | 40.5986
2007-07-18 21:00 | 7 | 18 | 21 | 199 | 4773 | 75.92 | 0 | 3758.8198 | 3758.8198 | -3758.8198 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4594.1131 | 4594.1131 | 0 | 8.5 | 0 | 765.6855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4502.2308 | 900.4462 | 9.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 22:00 | 7 | 18 | 22 | 199 | 4774 | 77 | 0 | 1576.5226 | 1576.5226 | -1576.5226 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1926.861 | 1926.861 | 0 | 8.5 | 0 | 321.1435 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1888.3237 | 377.6647 | 3.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-18 23:00 | 7 | 18 | 23 | 199 | 4775 | 77 | 0 | 1398.7441 | 1398.7441 | -1398.7441 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1709.5761 | 1709.5761 | 0 | 8.5 | 0 | 284.9294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1675.3846 | 335.0769 | 3.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 | 7 | 19 | 0 | 200 | 4776 | 73.04 | 0 | 1000.2674 | 1000.2674 | -1000.2674 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1222.5491 | 1222.5491 | 0 | 8.5 | 0 | 203.7582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1198.0981 | 239.6196 | 2.396% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 01:00 | 7 | 19 | 1 | 200 | 4777 | 71.96 | 0 | 847.3123 | 847.3123 | -847.3123 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1035.6039 | 1035.6039 | 0 | 8.5 | 0 | 172.6007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1014.8918 | 202.9784 | 2.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 02:00 | 7 | 19 | 2 | 200 | 4778 | 71.96 | 0 | 490.6475 | 490.6475 | -490.6475 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 599.6803 | 599.6803 | 0 | 8.5 | 0 | 99.9467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 587.6867 | 117.5373 | 1.175% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 03:00 | 7 | 19 | 3 | 200 | 4779 | 71.96 | 0 | 365.072 | 365.072 | -365.072 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 446.1991 | 446.1991 | 0 | 8.5 | 0 | 74.3665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 437.2751 | 87.455 | 0.8746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 04:00 | 7 | 19 | 4 | 200 | 4780 | 71.96 | 0 | 259.4119 | 259.4119 | -259.4119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 317.0589 | 317.0589 | 0 | 8.5 | 0 | 52.8432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 310.7178 | 62.1436 | 0.6214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 05:00 | 7 | 19 | 5 | 200 | 4781 | 71.96 | 0 | 470.6525 | 470.6525 | -470.6525 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 575.242 | 575.242 | 0 | 8.5 | 0 | 95.8737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 563.7371 | 112.7474 | 1.127% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 06:00 | 7 | 19 | 6 | 200 | 4782 | 71.6 | 14.8894 | 4782.0137 | 4782.0137 | -4767.1243 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5844.6834 | 5844.6834 | 0 | 8.5 | 0 | 974.1139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5727.7897 | 1145.5579 | 11.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 07:00 | 7 | 19 | 7 | 200 | 4783 | 71.96 | 0 | 5345.9629 | 5345.9629 | -5345.9629 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6533.9546 | 6533.9546 | 0 | 8.5 | 0 | 1088.9924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6403.2755 | 1280.6551 | 12.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 08:00 | 7 | 19 | 8 | 200 | 4784 | 73.04 | 0 | 7721.8064 | 7721.8064 | -7721.8064 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9437.7634 | 9437.7634 | 0 | 8.5 | 0 | 1572.9606 | 31.46% | 1 | 62.92% | 0% | 0% | 0% | 28.0758 | 0 | 0 | 0 | 28.0758 | 0 | 9249.0082 | 1849.8016 | 18.5% | 1 | 37% | 0% | 0% | 4.1388 | 0 | 0 | 4.1388 | 32.2146
2007-07-19 09:00 | 7 | 19 | 9 | 200 | 4785 | 78.98 | 0 | 11648.1906 | 11648.1906 | -11648.1906 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14236.6774 | 14236.6774 | 0 | 8.5 | 0 | 2372.7796 | 47.46% | 1 | 94.91% | 0% | 0% | 0% | 72.2725 | 0 | 0 | 0 | 72.2725 | 0 | 13951.9438 | 2790.3888 | 27.9% | 1 | 55.81% | 0% | 0% | 10.654 | 0 | 0 | 10.654 | 82.9264
2007-07-19 10:00 | 7 | 19 | 10 | 200 | 4786 | 80.96 | 0 | 13859.0458 | 13859.0458 | -13859.0458 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16938.8338 | 16938.8338 | 0 | 8.5 | 0 | 2823.139 | 56.46% | 2 | 56.46% | 56.46% | 0% | 0% | 21.8875 | 21.8875 | 0 | 0 | 43.775 | 0 | 16600.0571 | 3320.0114 | 33.2% | 1 | 33.2% | 33.2% | 0% | 3.2265 | 3.2265 | 0 | 6.453 | 50.228
2007-07-19 11:00 | 7 | 19 | 11 | 200 | 4787 | 80.96 | 0 | 15657.2751 | 15657.2751 | -15657.2751 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19136.6696 | 19136.6696 | 0 | 8.5 | 0 | 3189.4449 | 63.79% | 2 | 63.79% | 63.79% | 0% | 0% | 28.9772 | 28.9772 | 0 | 0 | 57.9544 | 0 | 18753.9362 | 3750.7872 | 37.51% | 1 | 37.51% | 37.51% | 0% | 4.2716 | 4.2716 | 0 | 8.5433 | 66.4977
2007-07-19 12:00 | 7 | 19 | 12 | 200 | 4788 | 82.04 | 0 | 17055.2342 | 17055.2342 | -17055.2342 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 20845.2863 | 20845.2863 | 0 | 8.5 | 0 | 3474.2144 | 69.48% | 2 | 69.48% | 69.48% | 0% | 0% | 35.2762 | 35.2762 | 0 | 0 | 70.5525 | 0 | 20428.3805 | 4085.6761 | 40.86% | 1 | 40.86% | 40.86% | 0% | 5.2002 | 5.2002 | 0 | 10.4004 | 80.9529
2007-07-19 13:00 | 7 | 19 | 13 | 200 | 4789 | 87.08 | 0 | 18415.1509 | 18415.1509 | -18415.1509 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 22507.4066 | 22507.4066 | 0 | 8.5 | 0 | 3751.2344 | 75.02% | 2 | 75.02% | 75.02% | 0% | 0% | 42.0836 | 42.0836 | 0 | 0 | 84.1672 | 0 | 22057.2585 | 4411.4517 | 44.11% | 1 | 44.11% | 44.11% | 0% | 6.2037 | 6.2037 | 0 | 12.4074 | 96.5746
2007-07-19 14:00 | 7 | 19 | 14 | 200 | 4790 | 87.08 | 0 | 19184.7204 | 19184.7204 | -19184.7204 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23447.9916 | 23447.9916 | 0 | 8.5 | 0 | 3907.9986 | 78.16% | 2 | 78.16% | 78.16% | 0% | 0% | 46.2389 | 46.2389 | 0 | 0 | 92.4777 | 0 | 22979.0317 | 4595.8063 | 45.96% | 1 | 45.96% | 45.96% | 0% | 6.8162 | 6.8162 | 0 | 13.6325 | 106.1102
2007-07-19 15:00 | 7 | 19 | 15 | 200 | 4791 | 89.96 | 0 | 19398.9563 | 19398.9563 | -19398.9563 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23709.8354 | 23709.8354 | 0 | 8.5 | 0 | 3951.6392 | 79.03% | 2 | 79.03% | 79.03% | 0% | 0% | 47.4351 | 47.4351 | 0 | 0 | 94.8702 | 0 | 23235.6387 | 4647.1277 | 46.47% | 1 | 46.47% | 46.47% | 0% | 6.9926 | 6.9926 | 0 | 13.9852 | 108.8554
2007-07-19 16:00 | 7 | 19 | 16 | 200 | 4792 | 82.94 | 0 | 19184.6422 | 19184.6422 | -19184.6422 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23447.8961 | 23447.8961 | 0 | 8.5 | 0 | 3907.9827 | 78.16% | 2 | 78.16% | 78.16% | 0% | 0% | 46.2384 | 46.2384 | 0 | 0 | 92.4769 | 0 | 22978.9381 | 4595.7876 | 45.96% | 1 | 45.96% | 45.96% | 0% | 6.8162 | 6.8162 | 0 | 13.6324 | 106.1092
2007-07-19 17:00 | 7 | 19 | 17 | 200 | 4793 | 82.94 | 0 | 18116.202 | 18116.202 | -18116.202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 22142.0247 | 22142.0247 | 0 | 8.5 | 0 | 3690.3374 | 73.81% | 2 | 73.81% | 73.81% | 0% | 0% | 40.5288 | 40.5288 | 0 | 0 | 81.0577 | 0 | 21699.1842 | 4339.8368 | 43.4% | 1 | 43.4% | 43.4% | 0% | 5.9745 | 5.9745 | 0 | 11.949 | 93.0067
2007-07-19 18:00 | 7 | 19 | 18 | 200 | 4794 | 73.94 | 0 | 11910.2792 | 11910.2792 | -11910.2792 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14557.0079 | 14557.0079 | 0 | 8.5 | 0 | 2426.168 | 48.52% | 1 | 97.05% | 0% | 0% | 0% | 76.0675 | 0 | 0 | 0 | 76.0675 | 0 | 14265.8678 | 2853.1736 | 28.53% | 1 | 57.06% | 0% | 0% | 11.2134 | 0 | 0 | 11.2134 | 87.2809
2007-07-19 19:00 | 7 | 19 | 19 | 200 | 4795 | 73.94 | 0 | 9324.7886 | 9324.7886 | -9324.7886 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11396.9638 | 11396.9638 | 0 | 8.5 | 0 | 1899.494 | 37.99% | 1 | 75.98% | 0% | 0% | 0% | 43.326 | 0 | 0 | 0 | 43.326 | 0 | 11169.0245 | 2233.8049 | 22.34% | 1 | 44.68% | 0% | 0% | 6.3868 | 0 | 0 | 6.3868 | 49.7128
2007-07-19 20:00 | 7 | 19 | 20 | 200 | 4796 | 73.94 | 0 | 7226.3261 | 7226.3261 | -7226.3261 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8832.1764 | 8832.1764 | 0 | 8.5 | 0 | 1472.0294 | 30% | 1 | 58.88% | 0% | 0% | 0% | 24.104 | 0 | 0 | 0 | 24.104 | 0 | 8655.5329 | 1731.1066 | 17.31% | 1 | 34.62% | 0% | 0% | 3.5533 | 0 | 0 | 3.5533 | 27.6572
2007-07-19 21:00 | 7 | 19 | 21 | 200 | 4797 | 73.04 | 0 | 3336.0202 | 3336.0202 | -3336.0202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4077.358 | 4077.358 | 0 | 8.5 | 0 | 679.5597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3995.8108 | 799.1622 | 7.992% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 22:00 | 7 | 19 | 22 | 200 | 4798 | 73.94 | 0 | 1346.4365 | 1346.4365 | -1346.4365 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1645.6447 | 1645.6447 | 0 | 8.5 | 0 | 274.2741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1612.7318 | 322.5464 | 3.225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-19 23:00 | 7 | 19 | 23 | 200 | 4799 | 73.94 | 0 | 1039.1006 | 1039.1006 | -1039.1006 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1270.0119 | 1270.0119 | 0 | 8.5 | 0 | 211.6686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1244.6116 | 248.9223 | 2.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 | 7 | 20 | 0 | 201 | 4800 | 73.94 | 0 | 849.8597 | 849.8597 | -849.8597 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1038.7175 | 1038.7175 | 0 | 8.5 | 0 | 173.1196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1017.9431 | 203.5886 | 2.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 01:00 | 7 | 20 | 1 | 201 | 4801 | 73.04 | 0 | 527.8053 | 527.8053 | -527.8053 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 645.0954 | 645.0954 | 0 | 8.5 | 0 | 107.5159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 632.1935 | 126.4387 | 1.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 02:00 | 7 | 20 | 2 | 201 | 4802 | 73.04 | 0 | 373.869 | 373.869 | -373.869 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 456.951 | 456.951 | 0 | 8.5 | 0 | 76.1585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 447.812 | 89.5624 | 0.8956% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 03:00 | 7 | 20 | 3 | 201 | 4803 | 71.96 | 0 | 246.8977 | 246.8977 | -246.8977 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 301.7639 | 301.7639 | 0 | 8.5 | 0 | 50.294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 295.7286 | 59.1457 | 0.5915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 04:00 | 7 | 20 | 4 | 201 | 4804 | 71.06 | 0 | 147.2396 | 147.2396 | -147.2396 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 179.9595 | 179.9595 | 0 | 8.5 | 0 | 29.9933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 176.3603 | 35.2721 | 0.3527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 05:00 | 7 | 20 | 5 | 201 | 4805 | 71.06 | 0 | 173.4608 | 173.4608 | -173.4608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 212.0077 | 212.0077 | 0 | 8.5 | 0 | 35.3346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 207.7675 | 41.5535 | 0.4155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 06:00 | 7 | 20 | 6 | 201 | 4806 | 73.94 | 142.2081 | 2069.0465 | 2069.0465 | -1926.8385 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2528.8347 | 2528.8347 | 0 | 8.5 | 0 | 421.4724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2478.258 | 495.6516 | 4.957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 07:00 | 7 | 20 | 7 | 201 | 4807 | 78.08 | 0 | 2238.6927 | 2238.6927 | -2238.6927 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2736.18 | 2736.18 | 0 | 8.5 | 0 | 456.03 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2681.4564 | 536.2913 | 5.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 08:00 | 7 | 20 | 8 | 201 | 4808 | 78.08 | 0 | 2740.0224 | 2740.0224 | -2740.0224 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3348.9163 | 3348.9163 | 0 | 8.5 | 0 | 558.1527 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3281.938 | 656.3876 | 6.564% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 09:00 | 7 | 20 | 9 | 201 | 4809 | 82.04 | 0 | 4962.3645 | 4962.3645 | -4962.3645 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6065.1122 | 6065.1122 | 0 | 8.5 | 0 | 1010.852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5943.8099 | 1188.762 | 11.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 10:00 | 7 | 20 | 10 | 201 | 4810 | 82.94 | 0 | 8062.6757 | 8062.6757 | -8062.6757 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9854.3814 | 9854.3814 | 0 | 8.5 | 0 | 1642.3969 | 32.85% | 1 | 65.7% | 0% | 0% | 0% | 31.0085 | 0 | 0 | 0 | 31.0085 | 0 | 9657.2938 | 1931.4588 | 19.31% | 1 | 38.63% | 0% | 0% | 4.5711 | 0 | 0 | 4.5711 | 35.5796
2007-07-20 11:00 | 7 | 20 | 11 | 201 | 4811 | 82.94 | 0 | 10032.7316 | 10032.7316 | -10032.7316 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12262.2275 | 12262.2275 | 0 | 8.5 | 0 | 2043.7046 | 40.87% | 1 | 81.75% | 0% | 0% | 0% | 51.2676 | 0 | 0 | 0 | 51.2676 | 0 | 12016.983 | 2403.3966 | 24.03% | 1 | 48.07% | 0% | 0% | 7.5575 | 0 | 0 | 7.5575 | 58.8251
2007-07-20 12:00 | 7 | 20 | 12 | 201 | 4812 | 84.02 | 0 | 11891.2202 | 11891.2202 | -11891.2202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14533.7136 | 14533.7136 | 0 | 8.5 | 0 | 2422.2856 | 48.45% | 1 | 96.89% | 0% | 0% | 0% | 75.7878 | 0 | 0 | 0 | 75.7878 | 0 | 14243.0393 | 2848.6079 | 28.49% | 1 | 56.97% | 0% | 0% | 11.1722 | 0 | 0 | 11.1722 | 86.96
2007-07-20 13:00 | 7 | 20 | 13 | 201 | 4813 | 84.92 | 0 | 12855.952 | 12855.952 | -12855.952 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15712.8302 | 15712.8302 | 0 | 8.5 | 0 | 2618.805 | 52.38% | 2 | 52.38% | 52.38% | 0% | 0% | 18.4141 | 18.4141 | 0 | 0 | 36.8281 | 0 | 15398.5736 | 3079.7147 | 30.8% | 1 | 61.59% | 0% | 0% | 13.3677 | 0 | 0 | 13.3677 | 50.1958
2007-07-20 14:00 | 7 | 20 | 14 | 201 | 4814 | 84.92 | 0 | 13760.3608 | 13760.3608 | -13760.3608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16818.2188 | 16818.2188 | 0 | 8.5 | 0 | 2803.0365 | 56.06% | 2 | 56.06% | 56.06% | 0% | 0% | 21.5307 | 21.5307 | 0 | 0 | 43.0614 | 0 | 16481.8544 | 3296.3709 | 32.96% | 1 | 65.93% | 0% | 0% | 15.6302 | 0 | 0 | 15.6302 | 58.6916
2007-07-20 15:00 | 7 | 20 | 15 | 201 | 4815 | 87.08 | 0 | 14625.5632 | 14625.5632 | -14625.5632 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17875.6884 | 17875.6884 | 0 | 8.5 | 0 | 2979.2814 | 59.59% | 2 | 59.59% | 59.59% | 0% | 0% | 24.7724 | 24.7724 | 0 | 0 | 49.5449 | 0 | 17518.1746 | 3503.6349 | 35.04% | 1 | 35.04% | 35.04% | 0% | 3.6518 | 3.6518 | 0 | 7.3036 | 56.8484
2007-07-20 16:00 | 7 | 20 | 16 | 201 | 4816 | 86 | 0 | 15530.7099 | 15530.7099 | -15530.7099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18981.9788 | 18981.9788 | 0 | 8.5 | 0 | 3163.6631 | 63.27% | 2 | 63.27% | 63.27% | 0% | 0% | 28.4413 | 28.4413 | 0 | 0 | 56.8826 | 0 | 18602.3392 | 3720.4678 | 37.2% | 1 | 37.2% | 37.2% | 0% | 4.1926 | 4.1926 | 0 | 8.3853 | 65.2679
2007-07-20 17:00 | 7 | 20 | 17 | 201 | 4817 | 86 | 0 | 15037.2799 | 15037.2799 | -15037.2799 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18378.8977 | 18378.8977 | 0 | 8.5 | 0 | 3063.1496 | 61.26% | 2 | 61.26% | 61.26% | 0% | 0% | 26.4058 | 26.4058 | 0 | 0 | 52.8116 | 0 | 18011.3197 | 3602.2639 | 36.02% | 1 | 36.02% | 36.02% | 0% | 3.8926 | 3.8926 | 0 | 7.7851 | 60.5967
2007-07-20 18:00 | 7 | 20 | 18 | 201 | 4818 | 80.96 | 0 | 10671.7022 | 10671.7022 | -10671.7022 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13043.1916 | 13043.1916 | 0 | 8.5 | 0 | 2173.8653 | 43.48% | 1 | 86.95% | 0% | 0% | 0% | 59.0903 | 0 | 0 | 0 | 59.0903 | 0 | 12782.3278 | 2556.4656 | 25.56% | 1 | 51.13% | 0% | 0% | 8.7107 | 0 | 0 | 8.7107 | 67.801
2007-07-20 19:00 | 7 | 20 | 19 | 201 | 4819 | 80.06 | 0 | 9107.4373 | 9107.4373 | -9107.4373 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11131.3123 | 11131.3123 | 0 | 8.5 | 0 | 1855.2187 | 37.1% | 1 | 74.21% | 0% | 0% | 0% | 41.0383 | 0 | 0 | 0 | 41.0383 | 0 | 10908.686 | 2181.7372 | 21.82% | 1 | 43.63% | 0% | 0% | 6.0496 | 0 | 0 | 6.0496 | 47.088
2007-07-20 20:00 | 7 | 20 | 20 | 201 | 4820 | 80.06 | 0 | 7768.7866 | 7768.7866 | -7768.7866 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9495.1837 | 9495.1837 | 0 | 8.5 | 0 | 1582.5306 | 31.65% | 1 | 63.3% | 0% | 0% | 0% | 28.4702 | 0 | 0 | 0 | 28.4702 | 0 | 9305.28 | 1861.056 | 18.61% | 1 | 37.22% | 0% | 0% | 4.1969 | 0 | 0 | 4.1969 | 32.6671
2007-07-20 21:00 | 7 | 20 | 21 | 201 | 4821 | 73.94 | 0 | 6113.8374 | 6113.8374 | -6113.8374 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7472.4679 | 7472.4679 | 0 | 8.5 | 0 | 1245.4113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7323.0185 | 1464.6037 | 14.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 22:00 | 7 | 20 | 22 | 201 | 4822 | 71.96 | 0 | 2482.1414 | 2482.1414 | -2482.1414 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3033.7284 | 3033.7284 | 0 | 8.5 | 0 | 505.6214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2973.0538 | 594.6108 | 5.946% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-20 23:00 | 7 | 20 | 23 | 201 | 4823 | 71.96 | 0 | 2071.1967 | 2071.1967 | -2071.1967 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2531.4626 | 2531.4626 | 0 | 8.5 | 0 | 421.9104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2480.8334 | 496.1667 | 4.962% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 | 7 | 21 | 0 | 202 | 4824 | 69.98 | 0 | 1758.8405 | 1758.8405 | -1758.8405 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2149.6939 | 2149.6939 | 0 | 8.5 | 0 | 358.2823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2106.7001 | 421.34 | 4.213% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 01:00 | 7 | 21 | 1 | 202 | 4825 | 66.92 | 0 | 1571.6787 | 1571.6787 | -1571.6787 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1920.9406 | 1920.9406 | 0 | 8.5 | 0 | 320.1568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1882.5218 | 376.5044 | 3.765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 02:00 | 7 | 21 | 2 | 202 | 4826 | 66.92 | 0 | 1318.9312 | 1318.9312 | -1318.9312 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1612.027 | 1612.027 | 0 | 8.5 | 0 | 268.6712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1579.7865 | 315.9573 | 3.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 03:00 | 7 | 21 | 3 | 202 | 4827 | 68 | 0 | 1121.209 | 1121.209 | -1121.209 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1370.3665 | 1370.3665 | 0 | 8.5 | 0 | 228.3944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1342.9592 | 268.5918 | 2.686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 04:00 | 7 | 21 | 4 | 202 | 4828 | 66.02 | 0 | 909.4857 | 909.4857 | -909.4857 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1111.5936 | 1111.5936 | 0 | 8.5 | 0 | 185.2656 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1089.3618 | 217.8724 | 2.179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 05:00 | 7 | 21 | 5 | 202 | 4829 | 66.02 | 0 | 1016.7512 | 1016.7512 | -1016.7512 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1242.696 | 1242.696 | 0 | 8.5 | 0 | 207.116 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1217.842 | 243.5684 | 2.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 06:00 | 7 | 21 | 6 | 202 | 4830 | 69.08 | 0 | 1361.267 | 1361.267 | -1361.267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1663.7707 | 1663.7707 | 0 | 8.5 | 0 | 277.2951 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1630.4953 | 326.0991 | 3.261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 07:00 | 7 | 21 | 7 | 202 | 4831 | 71.06 | 0 | 1969.8395 | 1969.8395 | -1969.8395 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2407.5816 | 2407.5816 | 0 | 8.5 | 0 | 401.2636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2359.4299 | 471.886 | 4.719% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 08:00 | 7 | 21 | 8 | 202 | 4832 | 71.06 | 0 | 3326.9956 | 3326.9956 | -3326.9956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4066.3279 | 4066.3279 | 0 | 8.5 | 0 | 677.7213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3985.0014 | 797.0003 | 7.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 09:00 | 7 | 21 | 9 | 202 | 4833 | 75.92 | 0 | 5565.2594 | 5565.2594 | -5565.2594 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6801.9838 | 6801.9838 | 0 | 8.5 | 0 | 1133.664 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6665.9441 | 1333.1888 | 13.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 10:00 | 7 | 21 | 10 | 202 | 4834 | 80.06 | 0 | 8077.0494 | 8077.0494 | -8077.0494 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9871.9493 | 9871.9493 | 0 | 8.5 | 0 | 1645.3249 | 32.91% | 1 | 65.81% | 0% | 0% | 0% | 31.1358 | 0 | 0 | 0 | 31.1358 | 0 | 9674.5103 | 1934.9021 | 19.35% | 1 | 38.7% | 0% | 0% | 4.5898 | 0 | 0 | 4.5898 | 35.7256
2007-07-21 11:00 | 7 | 21 | 11 | 202 | 4835 | 80.06 | 0 | 9291.3455 | 9291.3455 | -9291.3455 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11356.089 | 11356.089 | 0 | 8.5 | 0 | 1892.6815 | 37.85% | 1 | 75.71% | 0% | 0% | 0% | 42.9694 | 0 | 0 | 0 | 42.9694 | 0 | 11128.9672 | 2225.7934 | 22.26% | 1 | 44.52% | 0% | 0% | 6.3343 | 0 | 0 | 6.3343 | 49.3037
2007-07-21 12:00 | 7 | 21 | 12 | 202 | 4836 | 82.94 | 0 | 10653.119 | 10653.119 | -10653.119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13020.4787 | 13020.4787 | 0 | 8.5 | 0 | 2170.0798 | 43.4% | 1 | 86.8% | 0% | 0% | 0% | 58.8539 | 0 | 0 | 0 | 58.8539 | 0 | 12760.0692 | 2552.0138 | 25.52% | 1 | 51.04% | 0% | 0% | 8.6759 | 0 | 0 | 8.6759 | 67.5298
2007-07-21 13:00 | 7 | 21 | 13 | 202 | 4837 | 84.92 | 0 | 11481.5383 | 11481.5383 | -11481.5383 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14032.9913 | 14032.9913 | 0 | 8.5 | 0 | 2338.8319 | 46.78% | 1 | 93.55% | 0% | 0% | 0% | 69.9163 | 0 | 0 | 0 | 69.9163 | 0 | 13752.3315 | 2750.4663 | 27.5% | 1 | 55.01% | 0% | 0% | 10.3066 | 0 | 0 | 10.3066 | 80.223
2007-07-21 14:00 | 7 | 21 | 14 | 202 | 4838 | 84.92 | 0 | 11139.0835 | 11139.0835 | -11139.0835 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13614.4354 | 13614.4354 | 0 | 8.5 | 0 | 2269.0726 | 45.38% | 1 | 90.76% | 0% | 0% | 0% | 65.2127 | 0 | 0 | 0 | 65.2127 | 0 | 13342.1467 | 2668.4293 | 26.68% | 1 | 53.37% | 0% | 0% | 9.6132 | 0 | 0 | 9.6132 | 74.826
2007-07-21 15:00 | 7 | 21 | 15 | 202 | 4839 | 78.08 | 0 | 10295.4219 | 10295.4219 | -10295.4219 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12583.2934 | 12583.2934 | 0 | 8.5 | 0 | 2097.2156 | 41.94% | 1 | 83.89% | 0% | 0% | 0% | 54.4077 | 0 | 0 | 0 | 54.4077 | 0 | 12331.6275 | 2466.3255 | 24.66% | 1 | 49.33% | 0% | 0% | 8.0204 | 0 | 0 | 8.0204 | 62.4281
2007-07-21 16:00 | 7 | 21 | 16 | 202 | 4840 | 73.94 | 0 | 9361.3272 | 9361.3272 | -9361.3272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11441.6222 | 11441.6222 | 0 | 8.5 | 0 | 1906.937 | 38.14% | 1 | 76.28% | 0% | 0% | 0% | 43.7174 | 0 | 0 | 0 | 43.7174 | 0 | 11212.7897 | 2242.5579 | 22.43% | 1 | 44.85% | 0% | 0% | 6.4445 | 0 | 0 | 6.4445 | 50.162
2007-07-21 17:00 | 7 | 21 | 17 | 202 | 4841 | 73.94 | 0 | 8451.0776 | 8451.0776 | -8451.0776 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10329.0949 | 10329.0949 | 0 | 8.5 | 0 | 1721.5158 | 34.43% | 1 | 68.86% | 0% | 0% | 0% | 34.5523 | 0 | 0 | 0 | 34.5523 | 0 | 10122.513 | 2024.5026 | 20.25% | 1 | 40.49% | 0% | 0% | 5.0935 | 0 | 0 | 5.0935 | 39.6457
2007-07-21 18:00 | 7 | 21 | 18 | 202 | 4842 | 78.08 | 0 | 6838.1586 | 6838.1586 | -6838.1586 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8357.7494 | 8357.7494 | 0 | 8.5 | 0 | 1392.9582 | 30% | 1 | 55.72% | 0% | 0% | 0% | 21.2294 | 0 | 0 | 0 | 21.2294 | 0 | 8190.5945 | 1638.1189 | 16.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.504
2007-07-21 19:00 | 7 | 21 | 19 | 202 | 4843 | 75.02 | 0 | 2868.4489 | 2868.4489 | -2868.4489 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3505.882 | 3505.882 | 0 | 8.5 | 0 | 584.3137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3435.7643 | 687.1529 | 6.872% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 20:00 | 7 | 21 | 20 | 202 | 4844 | 75.02 | 0 | 2501.8786 | 2501.8786 | -2501.8786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3057.8516 | 3057.8516 | 0 | 8.5 | 0 | 509.6419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2996.6945 | 599.3389 | 5.993% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 21:00 | 7 | 21 | 21 | 202 | 4845 | 71.06 | 0 | 2180.8916 | 2180.8916 | -2180.8916 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2665.5342 | 2665.5342 | 0 | 8.5 | 0 | 444.2557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2612.2235 | 522.4447 | 5.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 22:00 | 7 | 21 | 22 | 202 | 4846 | 68 | 0 | 2023.2636 | 2023.2636 | -2023.2636 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2472.8777 | 2472.8777 | 0 | 8.5 | 0 | 412.1463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2423.4201 | 484.684 | 4.847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-21 23:00 | 7 | 21 | 23 | 202 | 4847 | 68 | 0 | 1635.6143 | 1635.6143 | -1635.6143 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1999.0842 | 1999.0842 | 0 | 8.5 | 0 | 333.1807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1959.1025 | 391.8205 | 3.918% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 | 7 | 22 | 0 | 203 | 4848 | 68 | 0 | 1135.0993 | 1135.0993 | -1135.0993 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1387.3436 | 1387.3436 | 0 | 8.5 | 0 | 231.2239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1359.5967 | 271.9193 | 2.719% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 01:00 | 7 | 22 | 1 | 203 | 4849 | 64.94 | 0 | 835.9788 | 835.9788 | -835.9788 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1021.7518 | 1021.7518 | 0 | 8.5 | 0 | 170.292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1001.3168 | 200.2634 | 2.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 02:00 | 7 | 22 | 2 | 203 | 4850 | 64.94 | 0 | 421.0413 | 421.0413 | -421.0413 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 514.6061 | 514.6061 | 0 | 8.5 | 0 | 85.7677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 504.3139 | 100.8628 | 1.009% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 03:00 | 7 | 22 | 3 | 203 | 4851 | 64.94 | 0 | 235.9722 | 235.9722 | -235.9722 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 288.4104 | 288.4104 | 0 | 8.5 | 0 | 48.0684 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 282.6422 | 56.5284 | 0.5653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 04:00 | 7 | 22 | 4 | 203 | 4852 | 64.94 | 0 | 104.6611 | 104.6611 | -104.6611 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 127.9191 | 127.9191 | 0 | 8.5 | 0 | 21.3199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 125.3607 | 25.0721 | 0.2507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 05:00 | 7 | 22 | 5 | 203 | 4853 | 64.94 | 0 | 59.9498 | 59.9498 | -59.9498 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 73.272 | 73.272 | 0 | 8.5 | 0 | 12.212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 71.8066 | 14.3613 | 0.1436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 06:00 | 7 | 22 | 6 | 203 | 4854 | 66.02 | 454.9272 | 1482.2933 | 1482.2933 | -1027.3661 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1811.6918 | 1811.6918 | 0 | 8.5 | 0 | 301.9486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1775.458 | 355.0916 | 3.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 07:00 | 7 | 22 | 7 | 203 | 4855 | 68 | 159.3436 | 1170.3967 | 1170.3967 | -1011.0531 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1430.4849 | 1430.4849 | 0 | 8.5 | 0 | 238.4141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1401.8752 | 280.375 | 2.804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 08:00 | 7 | 22 | 8 | 203 | 4856 | 68 | 0 | 3292.2701 | 3292.2701 | -3292.2701 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4023.8856 | 4023.8856 | 0 | 8.5 | 0 | 670.6476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3943.4079 | 788.6816 | 7.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 09:00 | 7 | 22 | 9 | 203 | 4857 | 73.04 | 0 | 4086.2828 | 4086.2828 | -4086.2828 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4994.3456 | 4994.3456 | 0 | 8.5 | 0 | 832.3909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4894.4587 | 978.8917 | 9.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 10:00 | 7 | 22 | 10 | 203 | 4858 | 75.92 | 0 | 4995.539 | 4995.539 | -4995.539 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6105.6587 | 6105.6587 | 0 | 8.5 | 0 | 1017.6098 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5983.5455 | 1196.7091 | 11.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 11:00 | 7 | 22 | 11 | 203 | 4859 | 75.92 | 0 | 6527.4051 | 6527.4051 | -6527.4051 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7977.9396 | 7977.9396 | 0 | 8.5 | 0 | 1329.6566 | 30% | 1 | 53.19% | 0% | 0% | 0% | 19.0758 | 0 | 0 | 0 | 19.0758 | 0 | 7818.3808 | 1563.6762 | 15.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.3503
2007-07-22 12:00 | 7 | 22 | 12 | 203 | 4860 | 78.08 | 0 | 7462.6899 | 7462.6899 | -7462.6899 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9121.0655 | 9121.0655 | 0 | 8.5 | 0 | 1520.1776 | 30.4% | 1 | 60.81% | 0% | 0% | 0% | 25.956 | 0 | 0 | 0 | 25.956 | 0 | 8938.6442 | 1787.7288 | 17.88% | 1 | 35.75% | 0% | 0% | 3.8263 | 0 | 0 | 3.8263 | 29.7823
2007-07-22 13:00 | 7 | 22 | 13 | 203 | 4861 | 78.98 | 0 | 8360.1604 | 8360.1604 | -8360.1604 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10217.9738 | 10217.9738 | 0 | 8.5 | 0 | 1702.9956 | 34.06% | 1 | 68.12% | 0% | 0% | 0% | 33.7033 | 0 | 0 | 0 | 33.7033 | 0 | 10013.6144 | 2002.7229 | 20.03% | 1 | 40.05% | 0% | 0% | 4.9683 | 0 | 0 | 4.9683 | 38.6716
2007-07-22 14:00 | 7 | 22 | 14 | 203 | 4862 | 78.98 | 0 | 8668.307 | 8668.307 | -8668.307 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10594.5974 | 10594.5974 | 0 | 8.5 | 0 | 1765.7662 | 35.32% | 1 | 70.63% | 0% | 0% | 0% | 36.6292 | 0 | 0 | 0 | 36.6292 | 0 | 10382.7055 | 2076.5411 | 20.77% | 1 | 41.53% | 0% | 0% | 5.3996 | 0 | 0 | 5.3996 | 42.0288
2007-07-22 15:00 | 7 | 22 | 15 | 203 | 4863 | 80.06 | 0 | 8379.2001 | 8379.2001 | -8379.2001 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10241.2446 | 10241.2446 | 0 | 8.5 | 0 | 1706.8741 | 34.14% | 1 | 68.27% | 0% | 0% | 0% | 33.8801 | 0 | 0 | 0 | 33.8801 | 0 | 10036.4197 | 2007.2839 | 20.07% | 1 | 40.15% | 0% | 0% | 4.9944 | 0 | 0 | 4.9944 | 38.8745
2007-07-22 16:00 | 7 | 22 | 16 | 203 | 4864 | 78.08 | 0 | 7939.7739 | 7939.7739 | -7939.7739 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9704.1681 | 9704.1681 | 0 | 8.5 | 0 | 1617.3614 | 32.35% | 1 | 64.69% | 0% | 0% | 0% | 29.9321 | 0 | 0 | 0 | 29.9321 | 0 | 9510.0848 | 1902.017 | 19.02% | 1 | 38.04% | 0% | 0% | 4.4124 | 0 | 0 | 4.4124 | 34.3445
2007-07-22 17:00 | 7 | 22 | 17 | 203 | 4865 | 78.08 | 0 | 6984.9268 | 6984.9268 | -6984.9268 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8537.1327 | 8537.1327 | 0 | 8.5 | 0 | 1422.8555 | 30% | 1 | 56.91% | 0% | 0% | 0% | 22.2921 | 0 | 0 | 0 | 22.2921 | 0 | 8366.3901 | 1673.278 | 16.73% | 1 | 33.47% | 0% | 0% | 3.2862 | 0 | 0 | 3.2862 | 25.5783
2007-07-22 18:00 | 7 | 22 | 18 | 203 | 4866 | 77 | 0 | 3723.2377 | 3723.2377 | -3723.2377 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4550.6238 | 4550.6238 | 0 | 8.5 | 0 | 758.4373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4459.6113 | 891.9223 | 8.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 19:00 | 7 | 22 | 19 | 203 | 4867 | 73.94 | 0 | 2294.1416 | 2294.1416 | -2294.1416 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2803.9508 | 2803.9508 | 0 | 8.5 | 0 | 467.3251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2747.8718 | 549.5744 | 5.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 20:00 | 7 | 22 | 20 | 203 | 4868 | 73.94 | 0 | 896.1526 | 896.1526 | -896.1526 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1095.2977 | 1095.2977 | 0 | 8.5 | 0 | 182.5496 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1073.3917 | 214.6783 | 2.147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 21:00 | 7 | 22 | 21 | 203 | 4869 | 68 | 0 | 493.7836 | 493.7836 | -493.7836 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 603.5133 | 603.5133 | 0 | 8.5 | 0 | 100.5856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 591.4431 | 118.2886 | 1.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 22:00 | 7 | 22 | 22 | 203 | 4870 | 66.92 | 0.76187 | 11.1908 | 11.1908 | -10.429 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13.6777 | 13.6777 | 0 | 8.5 | 0 | 2.2796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.4041 | 2.6808 | 0.02681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-22 23:00 | 7 | 22 | 23 | 203 | 4871 | 66.92 | 8.2238 | 0 | 0 | 8.2238 | Heating | 7.2563 | 8.5 | 7.2563 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.4043 | 0 | 1.4809 | 0.01481% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 | 7 | 23 | 0 | 204 | 4872 | 62.06 | 16.4404 | 0 | 0 | 16.4404 | Heating | 14.5063 | 8.5 | 14.5063 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.9013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.8023 | 0 | 2.9605 | 0.0296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 01:00 | 7 | 23 | 1 | 204 | 4873 | 62.96 | 25.3671 | 0 | 0 | 25.3671 | Heating | 22.3827 | 8.5 | 22.3827 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.4765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 22.8395 | 0 | 4.5679 | 0.04568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 02:00 | 7 | 23 | 2 | 204 | 4874 | 62.96 | 34.4866 | 0 | 0 | 34.4866 | Heating | 30.4293 | 8.5 | 30.4293 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.0859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 31.0503 | 0 | 6.2101 | 0.0621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 03:00 | 7 | 23 | 3 | 204 | 4875 | 60.08 | 45.0033 | 0 | 0 | 45.0033 | Heating | 39.7088 | 8.5 | 39.7088 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.9418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.5191 | 0 | 8.1038 | 0.08104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 04:00 | 7 | 23 | 4 | 204 | 4876 | 59 | 61.4419 | 0 | 0 | 61.4419 | Heating | 54.2134 | 8.5 | 54.2134 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.8427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 55.3198 | 0 | 11.064 | 0.1106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 05:00 | 7 | 23 | 5 | 204 | 4877 | 59 | 57.7882 | 0 | 0 | 57.7882 | Heating | 50.9896 | 8.5 | 50.9896 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.1979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 52.0302 | 0 | 10.406 | 0.1041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 06:00 | 7 | 23 | 6 | 204 | 4878 | 60.08 | 2419.5935 | 204.611 | 204.611 | 2214.9825 | Heating | 1954.3963 | 8.5 | 1954.3963 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.8793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1994.282 | 0 | 398.8564 | 3.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 07:00 | 7 | 23 | 7 | 204 | 4879 | 66.02 | 1187.9199 | 269.6265 | 269.6265 | 918.2934 | Heating | 810.2589 | 8.5 | 810.2589 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.0518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 826.7948 | 0 | 165.359 | 1.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 08:00 | 7 | 23 | 8 | 204 | 4880 | 66.02 | 286.5924 | 1723.1378 | 1723.1378 | -1436.5453 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2106.0573 | 2106.0573 | 0 | 8.5 | 0 | 351.0095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2063.9361 | 412.7872 | 4.128% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 09:00 | 7 | 23 | 9 | 204 | 4881 | 73.04 | 0 | 2923.9896 | 2923.9896 | -2923.9896 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3573.7651 | 3573.7651 | 0 | 8.5 | 0 | 595.6275 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3502.2898 | 700.458 | 7.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 10:00 | 7 | 23 | 10 | 204 | 4882 | 73.94 | 0 | 4229.732 | 4229.732 | -4229.732 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5169.6725 | 5169.6725 | 0 | 8.5 | 0 | 861.6121 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5066.279 | 1013.2558 | 10.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 11:00 | 7 | 23 | 11 | 204 | 4883 | 73.94 | 0 | 5486.7639 | 5486.7639 | -5486.7639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6706.0447 | 6706.0447 | 0 | 8.5 | 0 | 1117.6741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6571.9238 | 1314.3848 | 13.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 12:00 | 7 | 23 | 12 | 204 | 4884 | 77 | 0 | 6445.1308 | 6445.1308 | -6445.1308 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7877.3821 | 7877.3821 | 0 | 8.5 | 0 | 1312.897 | 30% | 1 | 52.52% | 0% | 0% | 0% | 18.5273 | 0 | 0 | 0 | 18.5273 | 0 | 7719.8344 | 1543.9669 | 15.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.8018
2007-07-23 13:00 | 7 | 23 | 13 | 204 | 4885 | 78.98 | 0 | 7530.8014 | 7530.8014 | -7530.8014 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9204.3129 | 9204.3129 | 0 | 8.5 | 0 | 1534.0521 | 30.68% | 1 | 61.36% | 0% | 0% | 0% | 26.5041 | 0 | 0 | 0 | 26.5041 | 0 | 9020.2266 | 1804.0453 | 18.04% | 1 | 36.08% | 0% | 0% | 3.9071 | 0 | 0 | 3.9071 | 30.4112
2007-07-23 14:00 | 7 | 23 | 14 | 204 | 4886 | 78.98 | 0 | 8305.0745 | 8305.0745 | -8305.0745 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10150.6466 | 10150.6466 | 0 | 8.5 | 0 | 1691.7744 | 33.84% | 1 | 67.67% | 0% | 0% | 0% | 33.1947 | 0 | 0 | 0 | 33.1947 | 0 | 9947.6336 | 1989.5267 | 19.9% | 1 | 39.79% | 0% | 0% | 4.8934 | 0 | 0 | 4.8934 | 38.088
2007-07-23 15:00 | 7 | 23 | 15 | 204 | 4887 | 80.96 | 0 | 8541.5379 | 8541.5379 | -8541.5379 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10439.6574 | 10439.6574 | 0 | 8.5 | 0 | 1739.9429 | 34.8% | 1 | 69.6% | 0% | 0% | 0% | 35.4088 | 0 | 0 | 0 | 35.4088 | 0 | 10230.8643 | 2046.1729 | 20.46% | 1 | 40.92% | 0% | 0% | 5.2197 | 0 | 0 | 5.2197 | 40.6286
2007-07-23 16:00 | 7 | 23 | 16 | 204 | 4888 | 80.96 | 0 | 8533.1059 | 8533.1059 | -8533.1059 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10429.3516 | 10429.3516 | 0 | 8.5 | 0 | 1738.2253 | 34.76% | 1 | 69.53% | 0% | 0% | 0% | 35.3285 | 0 | 0 | 0 | 35.3285 | 0 | 10220.7646 | 2044.1529 | 20.44% | 1 | 40.88% | 0% | 0% | 5.2079 | 0 | 0 | 5.2079 | 40.5364
2007-07-23 17:00 | 7 | 23 | 17 | 204 | 4889 | 80.96 | 0 | 8159.7769 | 8159.7769 | -8159.7769 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9973.0607 | 9973.0607 | 0 | 8.5 | 0 | 1662.1768 | 33.24% | 1 | 66.49% | 0% | 0% | 0% | 31.8742 | 0 | 0 | 0 | 31.8742 | 0 | 9773.5995 | 1954.7199 | 19.55% | 1 | 39.09% | 0% | 0% | 4.6987 | 0 | 0 | 4.6987 | 36.5728
2007-07-23 18:00 | 7 | 23 | 18 | 204 | 4890 | 77 | 0 | 5222.9393 | 5222.9393 | -5222.9393 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6383.5925 | 6383.5925 | 0 | 8.5 | 0 | 1063.9321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6255.9207 | 1251.1841 | 12.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 19:00 | 7 | 23 | 19 | 204 | 4891 | 73.94 | 0 | 4573.9984 | 4573.9984 | -4573.9984 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5590.4425 | 5590.4425 | 0 | 8.5 | 0 | 931.7404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5478.6337 | 1095.7267 | 10.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 20:00 | 7 | 23 | 20 | 204 | 4892 | 73.94 | 0 | 3419.3364 | 3419.3364 | -3419.3364 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4179.1889 | 4179.1889 | 0 | 8.5 | 0 | 696.5315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4095.6051 | 819.121 | 8.191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 21:00 | 7 | 23 | 21 | 204 | 4893 | 66.92 | 0 | 1360.019 | 1360.019 | -1360.019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1662.2455 | 1662.2455 | 0 | 8.5 | 0 | 277.0409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1629.0005 | 325.8001 | 3.258% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 22:00 | 7 | 23 | 22 | 204 | 4894 | 62.06 | 0 | 170.6124 | 170.6124 | -170.6124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 208.5262 | 208.5262 | 0 | 8.5 | 0 | 34.7544 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 204.3557 | 40.8711 | 0.4087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-23 23:00 | 7 | 23 | 23 | 204 | 4895 | 62.06 | 0 | 35.4048 | 35.4048 | -35.4048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 43.2725 | 43.2725 | 0 | 8.5 | 0 | 7.2121 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 42.4071 | 8.4814 | 0.08481% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 | 7 | 24 | 0 | 205 | 4896 | 62.06 | 0.040862 | 1.1062 | 1.1062 | -1.0654 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.3521 | 1.3521 | 0 | 8.5 | 0 | 0.22534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.325 | 0.265 | 0.00265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 01:00 | 7 | 24 | 1 | 205 | 4897 | 59 | 5.4073 | 0 | 0 | 5.4073 | Heating | 4.7711 | 8.5 | 4.7711 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.95422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.8685 | 0 | 0.97369 | 0.009737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 02:00 | 7 | 24 | 2 | 205 | 4898 | 59 | 15.3232 | 0 | 0 | 15.3232 | Heating | 13.5205 | 8.5 | 13.5205 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.7964 | 0 | 2.7593 | 0.02759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 03:00 | 7 | 24 | 3 | 205 | 4899 | 59 | 29.6522 | 0 | 0 | 29.6522 | Heating | 26.1637 | 8.5 | 26.1637 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.2327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 26.6976 | 0 | 5.3395 | 0.0534% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 04:00 | 7 | 24 | 4 | 205 | 4900 | 55.94 | 42.6616 | 0 | 0 | 42.6616 | Heating | 37.6426 | 8.5 | 37.6426 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.5285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 38.4108 | 0 | 7.6822 | 0.07682% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 05:00 | 7 | 24 | 5 | 205 | 4901 | 55.94 | 38.191 | 0 | 0 | 38.191 | Heating | 33.6979 | 8.5 | 33.6979 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.3857 | 0 | 6.8771 | 0.06877% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 06:00 | 7 | 24 | 6 | 205 | 4902 | 60.08 | 1907.5749 | 298.7832 | 298.7832 | 1608.7917 | Heating | 1419.5221 | 8.5 | 1419.5221 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 283.9044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1448.492 | 0 | 289.6984 | 2.897% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 07:00 | 7 | 24 | 7 | 205 | 4903 | 66.02 | 729.4852 | 424.3957 | 424.3957 | 305.0895 | Heating | 269.1967 | 8.5 | 269.1967 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.8393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 274.6905 | 0 | 54.9381 | 0.5494% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 08:00 | 7 | 24 | 8 | 205 | 4904 | 66.02 | 28.9821 | 2891.2124 | 2891.2124 | -2862.2303 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3533.7041 | 3533.7041 | 0 | 8.5 | 0 | 588.9507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3463.03 | 692.606 | 6.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 09:00 | 7 | 24 | 9 | 205 | 4905 | 73.04 | 0 | 4563.426 | 4563.426 | -4563.426 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5577.5206 | 5577.5206 | 0 | 8.5 | 0 | 929.5868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5465.9702 | 1093.194 | 10.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 10:00 | 7 | 24 | 10 | 205 | 4906 | 75.02 | 0 | 7121.2396 | 7121.2396 | -7121.2396 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8703.7373 | 8703.7373 | 0 | 8.5 | 0 | 1450.6229 | 30% | 1 | 58.02% | 0% | 0% | 0% | 23.3054 | 0 | 0 | 0 | 23.3054 | 0 | 8529.6626 | 1705.9325 | 17.06% | 1 | 34.12% | 0% | 0% | 3.4355 | 0 | 0 | 3.4355 | 26.7409
2007-07-24 11:00 | 7 | 24 | 11 | 205 | 4907 | 75.02 | 0 | 9085.344 | 9085.344 | -9085.344 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11104.3093 | 11104.3093 | 0 | 8.5 | 0 | 1850.7182 | 37.01% | 1 | 74.03% | 0% | 0% | 0% | 40.8097 | 0 | 0 | 0 | 40.8097 | 0 | 10882.2231 | 2176.4446 | 21.76% | 1 | 43.53% | 0% | 0% | 6.0159 | 0 | 0 | 6.0159 | 46.8256
2007-07-24 12:00 | 7 | 24 | 12 | 205 | 4908 | 78.98 | 0 | 10116.3094 | 10116.3094 | -10116.3094 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12364.3782 | 12364.3782 | 0 | 8.5 | 0 | 2060.7297 | 41.21% | 1 | 82.43% | 0% | 0% | 0% | 52.2552 | 0 | 0 | 0 | 52.2552 | 0 | 12117.0906 | 2423.4181 | 24.23% | 1 | 48.47% | 0% | 0% | 7.7031 | 0 | 0 | 7.7031 | 59.9583
2007-07-24 13:00 | 7 | 24 | 13 | 205 | 4909 | 80.96 | 0 | 11013.9553 | 11013.9553 | -11013.9553 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13461.5009 | 13461.5009 | 0 | 8.5 | 0 | 2243.5835 | 44.87% | 1 | 89.74% | 0% | 0% | 0% | 63.5401 | 0 | 0 | 0 | 63.5401 | 0 | 13192.2709 | 2638.4542 | 26.38% | 1 | 52.77% | 0% | 0% | 9.3667 | 0 | 0 | 9.3667 | 72.9068
2007-07-24 14:00 | 7 | 24 | 14 | 205 | 4910 | 80.96 | 0 | 11417.7006 | 11417.7006 | -11417.7006 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13954.9673 | 13954.9673 | 0 | 8.5 | 0 | 2325.8279 | 46.52% | 1 | 93.03% | 0% | 0% | 0% | 69.0255 | 0 | 0 | 0 | 69.0255 | 0 | 13675.868 | 2735.1736 | 27.35% | 1 | 54.7% | 0% | 0% | 10.1753 | 0 | 0 | 10.1753 | 79.2008
2007-07-24 15:00 | 7 | 24 | 15 | 205 | 4911 | 78.98 | 0 | 11524.3864 | 11524.3864 | -11524.3864 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14085.3612 | 14085.3612 | 0 | 8.5 | 0 | 2347.5602 | 46.95% | 1 | 93.9% | 0% | 0% | 0% | 70.5179 | 0 | 0 | 0 | 70.5179 | 0 | 13803.654 | 2760.7308 | 27.61% | 1 | 55.21% | 0% | 0% | 10.3953 | 0 | 0 | 10.3953 | 80.9132
2007-07-24 16:00 | 7 | 24 | 16 | 205 | 4912 | 66.02 | 0 | 11363.2967 | 11363.2967 | -11363.2967 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13888.4737 | 13888.4737 | 0 | 8.5 | 0 | 2314.7456 | 46.29% | 1 | 92.59% | 0% | 0% | 0% | 68.2714 | 0 | 0 | 0 | 68.2714 | 0 | 13610.7042 | 2722.1408 | 27.22% | 1 | 54.44% | 0% | 0% | 10.0641 | 0 | 0 | 10.0641 | 78.3355
2007-07-24 17:00 | 7 | 24 | 17 | 205 | 4913 | 69.98 | 0 | 10772.3361 | 10772.3361 | -10772.3361 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13166.1885 | 13166.1885 | 0 | 8.5 | 0 | 2194.3648 | 43.89% | 1 | 87.77% | 0% | 0% | 0% | 60.3798 | 0 | 0 | 0 | 60.3798 | 0 | 12902.8648 | 2580.573 | 25.81% | 1 | 51.61% | 0% | 0% | 8.9008 | 0 | 0 | 8.9008 | 69.2806
2007-07-24 18:00 | 7 | 24 | 18 | 205 | 4914 | 66.92 | 0 | 6777.2558 | 6777.2558 | -6777.2558 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8283.3127 | 8283.3127 | 0 | 8.5 | 0 | 1380.5521 | 30% | 1 | 55.22% | 0% | 0% | 0% | 20.7971 | 0 | 0 | 0 | 20.7971 | 0 | 8117.6464 | 1623.5293 | 16.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.0716
2007-07-24 19:00 | 7 | 24 | 19 | 205 | 4915 | 66.02 | 0 | 5625.287 | 5625.287 | -5625.287 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6875.3508 | 6875.3508 | 0 | 8.5 | 0 | 1145.8918 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6737.8437 | 1347.5687 | 13.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 20:00 | 7 | 24 | 20 | 205 | 4916 | 66.02 | 0 | 4677.4195 | 4677.4195 | -4677.4195 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5716.8461 | 5716.8461 | 0 | 8.5 | 0 | 952.8077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5602.5091 | 1120.5018 | 11.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 21:00 | 7 | 24 | 21 | 205 | 4917 | 64.94 | 0 | 2256.7027 | 2256.7027 | -2256.7027 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2758.1922 | 2758.1922 | 0 | 8.5 | 0 | 459.6987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2703.0283 | 540.6057 | 5.406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 22:00 | 7 | 24 | 22 | 205 | 4918 | 64.04 | 0 | 736.1042 | 736.1042 | -736.1042 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 899.6829 | 899.6829 | 0 | 8.5 | 0 | 149.9472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 881.6892 | 176.3378 | 1.763% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-24 23:00 | 7 | 24 | 23 | 205 | 4919 | 64.04 | 0 | 777.4939 | 777.4939 | -777.4939 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 950.2703 | 950.2703 | 0 | 8.5 | 0 | 158.3784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 931.2649 | 186.253 | 1.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 | 7 | 25 | 0 | 206 | 4920 | 62.06 | 0 | 642.0509 | 642.0509 | -642.0509 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 784.7289 | 784.7289 | 0 | 8.5 | 0 | 130.7882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 769.0343 | 153.8069 | 1.538% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 01:00 | 7 | 25 | 1 | 206 | 4921 | 60.98 | 0 | 598.4579 | 598.4579 | -598.4579 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 731.4485 | 731.4485 | 0 | 8.5 | 0 | 121.9081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 716.8195 | 143.3639 | 1.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 02:00 | 7 | 25 | 2 | 206 | 4922 | 60.98 | 0 | 548.7504 | 548.7504 | -548.7504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 670.6949 | 670.6949 | 0 | 8.5 | 0 | 111.7825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 657.281 | 131.4562 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 03:00 | 7 | 25 | 3 | 206 | 4923 | 59 | 0 | 488.5413 | 488.5413 | -488.5413 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 597.1061 | 597.1061 | 0 | 8.5 | 0 | 99.5177 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 585.1639 | 117.0328 | 1.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 04:00 | 7 | 25 | 4 | 206 | 4924 | 62.06 | 0 | 431.5228 | 431.5228 | -431.5228 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 527.4167 | 527.4167 | 0 | 8.5 | 0 | 87.9028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 516.8684 | 103.3737 | 1.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 05:00 | 7 | 25 | 5 | 206 | 4925 | 60.98 | 0 | 362.8889 | 362.8889 | -362.8889 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 443.5309 | 443.5309 | 0 | 8.5 | 0 | 73.9218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 434.6603 | 86.9321 | 0.8693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 06:00 | 7 | 25 | 6 | 206 | 4926 | 60.08 | 19.9639 | 1691.7687 | 1691.7687 | -1671.8048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2067.7173 | 2067.7173 | 0 | 8.5 | 0 | 344.6196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2026.363 | 405.2726 | 4.053% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 07:00 | 7 | 25 | 7 | 206 | 4927 | 64.04 | 23.2365 | 1139.1447 | 1139.1447 | -1115.9082 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1392.288 | 1392.288 | 0 | 8.5 | 0 | 232.048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1364.4422 | 272.8884 | 2.729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 08:00 | 7 | 25 | 8 | 206 | 4928 | 64.04 | 0 | 3402.8674 | 3402.8674 | -3402.8674 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4159.0601 | 4159.0601 | 0 | 8.5 | 0 | 693.1767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4075.8789 | 815.1758 | 8.152% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 09:00 | 7 | 25 | 9 | 206 | 4929 | 69.98 | 0 | 4048.991 | 4048.991 | -4048.991 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4948.7668 | 4948.7668 | 0 | 8.5 | 0 | 824.7945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4849.7915 | 969.9583 | 9.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 10:00 | 7 | 25 | 10 | 206 | 4930 | 73.94 | 0 | 4372.714 | 4372.714 | -4372.714 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5344.4282 | 5344.4282 | 0 | 8.5 | 0 | 890.738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5237.5396 | 1047.5079 | 10.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 11:00 | 7 | 25 | 11 | 206 | 4931 | 73.94 | 0 | 5374.3752 | 5374.3752 | -5374.3752 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6568.6808 | 6568.6808 | 0 | 8.5 | 0 | 1094.7801 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6437.3071 | 1287.4614 | 12.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 12:00 | 7 | 25 | 12 | 206 | 4932 | 78.08 | 0 | 6817.1026 | 6817.1026 | -6817.1026 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8332.0143 | 8332.0143 | 0 | 8.5 | 0 | 1388.669 | 30% | 1 | 55.55% | 0% | 0% | 0% | 21.0794 | 0 | 0 | 0 | 21.0794 | 0 | 8165.374 | 1633.0748 | 16.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.3539
2007-07-25 13:00 | 7 | 25 | 13 | 206 | 4933 | 82.04 | 0 | 8235.2352 | 8235.2352 | -8235.2352 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10065.2875 | 10065.2875 | 0 | 8.5 | 0 | 1677.5479 | 33.55% | 1 | 67.1% | 0% | 0% | 0% | 32.5562 | 0 | 0 | 0 | 32.5562 | 0 | 9863.9817 | 1972.7963 | 19.73% | 1 | 39.46% | 0% | 0% | 4.7992 | 0 | 0 | 4.7992 | 37.3554
2007-07-25 14:00 | 7 | 25 | 14 | 206 | 4934 | 82.04 | 0 | 9078.8735 | 9078.8735 | -9078.8735 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11096.4009 | 11096.4009 | 0 | 8.5 | 0 | 1849.4002 | 36.99% | 1 | 73.98% | 0% | 0% | 0% | 40.7429 | 0 | 0 | 0 | 40.7429 | 0 | 10874.4729 | 2174.8946 | 21.75% | 1 | 43.5% | 0% | 0% | 6.0061 | 0 | 0 | 6.0061 | 46.749
2007-07-25 15:00 | 7 | 25 | 15 | 206 | 4935 | 82.04 | 0 | 9165.7242 | 9165.7242 | -9165.7242 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11202.5518 | 11202.5518 | 0 | 8.5 | 0 | 1867.092 | 37.34% | 1 | 74.68% | 0% | 0% | 0% | 41.6449 | 0 | 0 | 0 | 41.6449 | 0 | 10978.5008 | 2195.7002 | 21.96% | 1 | 43.91% | 0% | 0% | 6.139 | 0 | 0 | 6.139 | 47.784
2007-07-25 16:00 | 7 | 25 | 16 | 206 | 4936 | 82.04 | 0 | 9105.4001 | 9105.4001 | -9105.4001 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11128.8223 | 11128.8223 | 0 | 8.5 | 0 | 1854.8037 | 37.1% | 1 | 74.19% | 0% | 0% | 0% | 41.0172 | 0 | 0 | 0 | 41.0172 | 0 | 10906.2459 | 2181.2492 | 21.81% | 1 | 43.62% | 0% | 0% | 6.0465 | 0 | 0 | 6.0465 | 47.0637
2007-07-25 17:00 | 7 | 25 | 17 | 206 | 4937 | 82.04 | 0 | 8755.8541 | 8755.8541 | -8755.8541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10701.5994 | 10701.5994 | 0 | 8.5 | 0 | 1783.5999 | 35.67% | 1 | 71.34% | 0% | 0% | 0% | 37.4857 | 0 | 0 | 0 | 37.4857 | 0 | 10487.5674 | 2097.5135 | 20.98% | 1 | 41.95% | 0% | 0% | 5.5259 | 0 | 0 | 5.5259 | 43.0116
2007-07-25 18:00 | 7 | 25 | 18 | 206 | 4938 | 80.06 | 0 | 5466.0176 | 5466.0176 | -5466.0176 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6680.6881 | 6680.6881 | 0 | 8.5 | 0 | 1113.448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6547.0744 | 1309.4149 | 13.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 19:00 | 7 | 25 | 19 | 206 | 4939 | 78.08 | 0 | 4678.0103 | 4678.0103 | -4678.0103 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5717.5682 | 5717.5682 | 0 | 8.5 | 0 | 952.928 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5603.2168 | 1120.6434 | 11.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 20:00 | 7 | 25 | 20 | 206 | 4940 | 78.08 | 0 | 3578.3553 | 3578.3553 | -3578.3553 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4373.5454 | 4373.5454 | 0 | 8.5 | 0 | 728.9242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4286.0745 | 857.2149 | 8.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 21:00 | 7 | 25 | 21 | 206 | 4941 | 75.02 | 0 | 1867.9408 | 1867.9408 | -1867.9408 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2283.0387 | 2283.0387 | 0 | 8.5 | 0 | 380.5065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2237.3779 | 447.4756 | 4.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 22:00 | 7 | 25 | 22 | 206 | 4942 | 73.94 | 0 | 397.7124 | 397.7124 | -397.7124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 486.0929 | 486.0929 | 0 | 8.5 | 0 | 81.0155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 476.371 | 95.2742 | 0.9527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-25 23:00 | 7 | 25 | 23 | 206 | 4943 | 73.94 | 0 | 192.7293 | 192.7293 | -192.7293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 235.558 | 235.558 | 0 | 8.5 | 0 | 39.2597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 230.8468 | 46.1694 | 0.4617% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 | 7 | 26 | 0 | 207 | 4944 | 73.04 | 0 | 42.5311 | 42.5311 | -42.5311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 51.9825 | 51.9825 | 0 | 8.5 | 0 | 8.6637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 50.9428 | 10.1886 | 0.1019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 01:00 | 7 | 26 | 1 | 207 | 4945 | 71.96 | 0.3757 | 0.65012 | 0.65012 | -0.27443 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.79459 | 0.79459 | 0 | 8.5 | 0 | 0.13243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.7787 | 0.15574 | 0.001557% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 02:00 | 7 | 26 | 2 | 207 | 4946 | 71.96 | 6.8564 | 0 | 0 | 6.8564 | Heating | 6.0498 | 8.5 | 6.0498 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.21 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.1733 | 0 | 1.2347 | 0.01235% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 03:00 | 7 | 26 | 3 | 207 | 4947 | 71.06 | 15.5121 | 0 | 0 | 15.5121 | Heating | 13.6871 | 8.5 | 13.6871 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.9665 | 0 | 2.7933 | 0.02793% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 04:00 | 7 | 26 | 4 | 207 | 4948 | 68 | 27.3005 | 0 | 0 | 27.3005 | Heating | 24.0887 | 8.5 | 24.0887 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.8177 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.5803 | 0 | 4.9161 | 0.04916% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 05:00 | 7 | 26 | 5 | 207 | 4949 | 68 | 26.3248 | 0 | 0 | 26.3248 | Heating | 23.2277 | 8.5 | 23.2277 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.7018 | 0 | 4.7404 | 0.0474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 06:00 | 7 | 26 | 6 | 207 | 4950 | 66.92 | 1463.8279 | 252.7814 | 252.7814 | 1211.0465 | Heating | 1068.5705 | 8.5 | 1068.5705 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 213.7141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1090.378 | 0 | 218.0756 | 2.181% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 07:00 | 7 | 26 | 7 | 207 | 4951 | 69.8 | 831.9683 | 283.9132 | 283.9132 | 548.0551 | Heating | 483.5781 | 8.5 | 483.5781 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.7156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 493.447 | 0 | 98.6894 | 0.9869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 08:00 | 7 | 26 | 8 | 207 | 4952 | 69.08 | 170.6771 | 1833.381 | 1833.381 | -1662.7038 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2240.7989 | 2240.7989 | 0 | 8.5 | 0 | 373.4665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2195.983 | 439.1966 | 4.392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 09:00 | 7 | 26 | 9 | 207 | 4953 | 73.4 | 0 | 2807.4567 | 2807.4567 | -2807.4567 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3431.3359 | 3431.3359 | 0 | 8.5 | 0 | 571.8893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3362.7092 | 672.5418 | 6.725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 10:00 | 7 | 26 | 10 | 207 | 4954 | 75.2 | 0 | 3375.8046 | 3375.8046 | -3375.8046 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4125.9833 | 4125.9833 | 0 | 8.5 | 0 | 687.6639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4043.4637 | 808.6927 | 8.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 11:00 | 7 | 26 | 11 | 207 | 4955 | 75.02 | 0 | 4559.3948 | 4559.3948 | -4559.3948 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5572.5936 | 5572.5936 | 0 | 8.5 | 0 | 928.7656 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5461.1417 | 1092.2283 | 10.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 12:00 | 7 | 26 | 12 | 207 | 4956 | 80.06 | 0 | 5602.5827 | 5602.5827 | -5602.5827 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6847.6011 | 6847.6011 | 0 | 8.5 | 0 | 1141.2669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6710.6491 | 1342.1298 | 13.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 13:00 | 7 | 26 | 13 | 207 | 4957 | 80.06 | 0 | 6490.2125 | 6490.2125 | -6490.2125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7932.482 | 7932.482 | 0 | 8.5 | 0 | 1322.0803 | 30% | 1 | 52.88% | 0% | 0% | 0% | 18.8267 | 0 | 0 | 0 | 18.8267 | 0 | 7773.8323 | 1554.7665 | 15.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.1012
2007-07-26 14:00 | 7 | 26 | 14 | 207 | 4958 | 80.06 | 0 | 7027.1106 | 7027.1106 | -7027.1106 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8588.6907 | 8588.6907 | 0 | 8.5 | 0 | 1431.4485 | 30% | 1 | 57.26% | 0% | 0% | 0% | 22.603 | 0 | 0 | 0 | 22.603 | 0 | 8416.9169 | 1683.3834 | 16.83% | 1 | 33.67% | 0% | 0% | 3.332 | 0 | 0 | 3.332 | 25.9349
2007-07-26 15:00 | 7 | 26 | 15 | 207 | 4959 | 84.02 | 0 | 6888.6806 | 6888.6806 | -6888.6806 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8419.4985 | 8419.4985 | 0 | 8.5 | 0 | 1403.2498 | 30% | 1 | 56.13% | 0% | 0% | 0% | 21.5919 | 0 | 0 | 0 | 21.5919 | 0 | 8251.1085 | 1650.2217 | 16.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.8665
2007-07-26 16:00 | 7 | 26 | 16 | 207 | 4960 | 84.02 | 0 | 6529.4534 | 6529.4534 | -6529.4534 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7980.4431 | 7980.4431 | 0 | 8.5 | 0 | 1330.0739 | 30% | 1 | 53.2% | 0% | 0% | 0% | 19.0895 | 0 | 0 | 0 | 19.0895 | 0 | 7820.8342 | 1564.1668 | 15.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.3641
2007-07-26 17:00 | 7 | 26 | 17 | 207 | 4961 | 84.02 | 0 | 5748.4658 | 5748.4658 | -5748.4658 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7025.9026 | 7025.9026 | 0 | 8.5 | 0 | 1170.9838 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6885.3845 | 1377.0769 | 13.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 18:00 | 7 | 26 | 18 | 207 | 4962 | 80.96 | 0 | 2815.9879 | 2815.9879 | -2815.9879 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3441.7629 | 3441.7629 | 0 | 8.5 | 0 | 573.6272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3372.9277 | 674.5855 | 6.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 19:00 | 7 | 26 | 19 | 207 | 4963 | 77 | 0 | 1581.699 | 1581.699 | -1581.699 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1933.1877 | 1933.1877 | 0 | 8.5 | 0 | 322.1979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1894.5239 | 378.9048 | 3.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 20:00 | 7 | 26 | 20 | 207 | 4964 | 77 | 0 | 538.6428 | 538.6428 | -538.6428 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 658.3413 | 658.3413 | 0 | 8.5 | 0 | 109.7235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 645.1744 | 129.0349 | 1.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 21:00 | 7 | 26 | 21 | 207 | 4965 | 73.94 | 0 | 346.1895 | 346.1895 | -346.1895 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 423.1205 | 423.1205 | 0 | 8.5 | 0 | 70.5201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 414.6581 | 82.9316 | 0.8293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 22:00 | 7 | 26 | 22 | 207 | 4966 | 73.04 | 1.362 | 0.77323 | 0.77323 | 0.58877 | Heating | 0.51951 | 8.5 | 0.51951 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.1039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.53011 | 0 | 0.10602 | 0.00106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-26 23:00 | 7 | 26 | 23 | 207 | 4967 | 73.04 | 9.8633 | 0 | 0 | 9.8633 | Heating | 8.7029 | 8.5 | 8.7029 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.7406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.8805 | 0 | 1.7761 | 0.01776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 | 7 | 27 | 0 | 208 | 4968 | 71.06 | 22.9544 | 0 | 0 | 22.9544 | Heating | 20.2539 | 8.5 | 20.2539 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.0508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.6673 | 0 | 4.1335 | 0.04133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 01:00 | 7 | 27 | 1 | 208 | 4969 | 69.98 | 34.7479 | 0 | 0 | 34.7479 | Heating | 30.6599 | 8.5 | 30.6599 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 31.2857 | 0 | 6.2571 | 0.06257% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 02:00 | 7 | 27 | 2 | 208 | 4970 | 69.98 | 49.534 | 0 | 0 | 49.534 | Heating | 43.7065 | 8.5 | 43.7065 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.7413 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.5984 | 0 | 8.9197 | 0.0892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 03:00 | 7 | 27 | 3 | 208 | 4971 | 69.98 | 84.1825 | 0 | 0 | 84.1825 | Heating | 74.2787 | 8.5 | 74.2787 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.8557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 75.7946 | 0 | 15.1589 | 0.1516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 04:00 | 7 | 27 | 4 | 208 | 4972 | 69.98 | 136.8396 | 0 | 0 | 136.8396 | Heating | 120.7408 | 8.5 | 120.7408 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.1482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 123.2049 | 0 | 24.641 | 0.2464% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 05:00 | 7 | 27 | 5 | 208 | 4973 | 69.98 | 142.5074 | 0 | 0 | 142.5074 | Heating | 125.7418 | 8.5 | 125.7418 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.1484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 128.308 | 0 | 25.6616 | 0.2566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 06:00 | 7 | 27 | 6 | 208 | 4974 | 71.06 | 3090.2265 | 84.2075 | 84.2075 | 3006.019 | Heating | 2652.3697 | 8.5 | 2652.3697 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 530.4739 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2706.4997 | 0 | 541.2999 | 5.413% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 07:00 | 7 | 27 | 7 | 208 | 4975 | 71.96 | 1788.8986 | 50.7669 | 50.7669 | 1738.1317 | Heating | 1533.6457 | 8.5 | 1533.6457 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 306.7291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1564.9445 | 0 | 312.9889 | 3.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 08:00 | 7 | 27 | 8 | 208 | 4976 | 71.96 | 999.8738 | 148.6847 | 148.6847 | 851.1891 | Heating | 751.0492 | 8.5 | 751.0492 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.2098 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 766.3767 | 0 | 153.2753 | 1.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 09:00 | 7 | 27 | 9 | 208 | 4977 | 75.92 | 82.0599 | 220.1189 | 220.1189 | -138.059 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 269.0343 | 269.0343 | 0 | 8.5 | 0 | 44.839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 263.6536 | 52.7307 | 0.5273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 10:00 | 7 | 27 | 10 | 208 | 4978 | 80.06 | 0.93023 | 378.723 | 378.723 | -377.7928 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 462.8837 | 462.8837 | 0 | 8.5 | 0 | 77.1473 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 453.626 | 90.7252 | 0.9073% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 11:00 | 7 | 27 | 11 | 208 | 4979 | 80.06 | 0 | 954.9462 | 954.9462 | -954.9462 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1167.1564 | 1167.1564 | 0 | 8.5 | 0 | 194.5261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1143.8133 | 228.7627 | 2.288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 12:00 | 7 | 27 | 12 | 208 | 4980 | 84.02 | 0 | 1687.7895 | 1687.7895 | -1687.7895 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2062.8539 | 2062.8539 | 0 | 8.5 | 0 | 343.809 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2021.5968 | 404.3194 | 4.043% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 13:00 | 7 | 27 | 13 | 208 | 4981 | 86 | 0 | 2626.7676 | 2626.7676 | -2626.7676 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3210.4938 | 3210.4938 | 0 | 8.5 | 0 | 535.0823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3146.2839 | 629.2568 | 6.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 14:00 | 7 | 27 | 14 | 208 | 4982 | 86 | 0 | 2896.1735 | 2896.1735 | -2896.1735 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3539.7676 | 3539.7676 | 0 | 8.5 | 0 | 589.9613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3468.9722 | 693.7944 | 6.938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 15:00 | 7 | 27 | 15 | 208 | 4983 | 87.08 | 0 | 3324.1012 | 3324.1012 | -3324.1012 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4062.7903 | 4062.7903 | 0 | 8.5 | 0 | 677.1317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3981.5345 | 796.3069 | 7.963% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 16:00 | 7 | 27 | 16 | 208 | 4984 | 87.98 | 0 | 3744.762 | 3744.762 | -3744.762 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4576.9314 | 4576.9314 | 0 | 8.5 | 0 | 762.8219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4485.3927 | 897.0785 | 8.971% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 17:00 | 7 | 27 | 17 | 208 | 4985 | 87.98 | 0 | 3663.8246 | 3663.8246 | -3663.8246 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4478.0079 | 4478.0079 | 0 | 8.5 | 0 | 746.3346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4388.4477 | 877.6895 | 8.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 18:00 | 7 | 27 | 18 | 208 | 4986 | 84.02 | 0 | 1763.8685 | 1763.8685 | -1763.8685 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2155.8393 | 2155.8393 | 0 | 8.5 | 0 | 359.3065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2112.7225 | 422.5445 | 4.225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 19:00 | 7 | 27 | 19 | 208 | 4987 | 82.94 | 0 | 979.932 | 979.932 | -979.932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1197.6946 | 1197.6946 | 0 | 8.5 | 0 | 199.6158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1173.7407 | 234.7481 | 2.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 20:00 | 7 | 27 | 20 | 208 | 4988 | 82.94 | 0 | 214.953 | 214.953 | -214.953 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 262.7203 | 262.7203 | 0 | 8.5 | 0 | 43.7867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 257.4659 | 51.4932 | 0.5149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 21:00 | 7 | 27 | 21 | 208 | 4989 | 80.06 | 0 | 32.9752 | 32.9752 | -32.9752 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 40.303 | 40.303 | 0 | 8.5 | 0 | 6.7172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 39.4969 | 7.8994 | 0.07899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 22:00 | 7 | 27 | 22 | 208 | 4990 | 78.98 | 4.8171 | 0 | 0 | 4.8171 | Heating | 4.2504 | 8.5 | 4.2504 | 0 | 8.9059 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.85008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.3371 | 0 | 0.86743 | 0.008674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-27 23:00 | 7 | 27 | 23 | 208 | 4991 | 78.98 | 27.2402 | 0 | 0 | 27.2402 | Heating | 24.0355 | 8.5 | 24.0355 | 0 | 8.9059 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.8071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.526 | 0 | 4.9052 | 0.04905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 | 7 | 28 | 0 | 209 | 4992 | 73.94 | 48.907 | 0 | 0 | 48.907 | Heating | 43.1532 | 8.5 | 43.1532 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.6306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.0339 | 0 | 8.8068 | 0.08807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 01:00 | 7 | 28 | 1 | 209 | 4993 | 73.04 | 79.794 | 0 | 0 | 79.794 | Heating | 70.4064 | 8.5 | 70.4064 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.0813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 71.8433 | 0 | 14.3687 | 0.1437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 02:00 | 7 | 28 | 2 | 209 | 4994 | 73.04 | 129.9307 | 0 | 0 | 129.9307 | Heating | 114.6447 | 8.5 | 114.6447 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.9289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.9844 | 0 | 23.3969 | 0.234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 03:00 | 7 | 28 | 3 | 209 | 4995 | 69.98 | 190.2186 | 0 | 0 | 190.2186 | Heating | 167.84 | 8.5 | 167.84 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 171.2653 | 0 | 34.2531 | 0.3425% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 04:00 | 7 | 28 | 4 | 209 | 4996 | 69.08 | 254.895 | 0 | 0 | 254.895 | Heating | 224.9073 | 8.5 | 224.9073 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.9815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 229.4973 | 0 | 45.8995 | 0.459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 05:00 | 7 | 28 | 5 | 209 | 4997 | 68 | 248.2523 | 0 | 0 | 248.2523 | Heating | 219.0461 | 8.5 | 219.0461 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.8092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 223.5165 | 0 | 44.7033 | 0.447% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 06:00 | 7 | 28 | 6 | 209 | 4998 | 69.98 | 177.4221 | 0 | 0 | 177.4221 | Heating | 156.5489 | 8.5 | 156.5489 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.3098 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 159.7438 | 0 | 31.9488 | 0.3195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 07:00 | 7 | 28 | 7 | 209 | 4999 | 69.08 | 94.6183 | 0 | 0 | 94.6183 | Heating | 83.4867 | 8.5 | 83.4867 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.6973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 85.1905 | 0 | 17.0381 | 0.1704% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 08:00 | 7 | 28 | 8 | 209 | 5000 | 73.04 | 2293.2837 | 0 | 0 | 2293.2837 | Heating | 2023.4856 | 8.5 | 2023.4856 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.6971 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2064.7813 | 0 | 412.9563 | 4.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 09:00 | 7 | 28 | 9 | 209 | 5001 | 80.06 | 730.1225 | 0 | 0 | 730.1225 | Heating | 644.2257 | 8.5 | 644.2257 | 0 | 9.1467 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.8451 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 657.3732 | 0 | 131.4746 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 10:00 | 7 | 28 | 10 | 209 | 5002 | 82.94 | 0 | 8.5611 | 8.5611 | -8.5611 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10.4636 | 10.4636 | 0 | 8.5 | 0 | 1.7439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 10.2543 | 2.0509 | 0.02051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 11:00 | 7 | 28 | 11 | 209 | 5003 | 82.94 | 0 | 47.717 | 47.717 | -47.717 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 58.3208 | 58.3208 | 0 | 8.5 | 0 | 9.7201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 57.1544 | 11.4309 | 0.1143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 12:00 | 7 | 28 | 12 | 209 | 5004 | 89.06 | 0 | 1024.5079 | 1024.5079 | -1024.5079 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1252.1763 | 1252.1763 | 0 | 8.5 | 0 | 208.6961 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1227.1328 | 245.4266 | 2.454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 13:00 | 7 | 28 | 13 | 209 | 5005 | 89.96 | 0 | 1963.3363 | 1963.3363 | -1963.3363 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2399.6332 | 2399.6332 | 0 | 8.5 | 0 | 399.9389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2351.6405 | 470.3281 | 4.703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 14:00 | 7 | 28 | 14 | 209 | 5006 | 89.96 | 0 | 2424.3568 | 2424.3568 | -2424.3568 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2963.1028 | 2963.1028 | 0 | 8.5 | 0 | 493.8505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2903.8407 | 580.7681 | 5.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 15:00 | 7 | 28 | 15 | 209 | 5007 | 91.04 | 0 | 2829.6378 | 2829.6378 | -2829.6378 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3458.4462 | 3458.4462 | 0 | 8.5 | 0 | 576.4077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3389.2773 | 677.8555 | 6.779% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 16:00 | 7 | 28 | 16 | 209 | 5008 | 80.96 | 0 | 3131.2414 | 3131.2414 | -3131.2414 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3827.0728 | 3827.0728 | 0 | 8.5 | 0 | 637.8455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3750.5313 | 750.1063 | 7.501% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 17:00 | 7 | 28 | 17 | 209 | 5009 | 80.96 | 0 | 2844.7472 | 2844.7472 | -2844.7472 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3476.9133 | 3476.9133 | 0 | 8.5 | 0 | 579.4856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3407.375 | 681.475 | 6.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 18:00 | 7 | 28 | 18 | 209 | 5010 | 82.94 | 0 | 1887.2116 | 1887.2116 | -1887.2116 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2306.592 | 2306.592 | 0 | 8.5 | 0 | 384.432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2260.4602 | 452.092 | 4.521% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 19:00 | 7 | 28 | 19 | 209 | 5011 | 80.96 | 0 | 660.3239 | 660.3239 | -660.3239 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 807.0625 | 807.0625 | 0 | 8.5 | 0 | 134.5104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 790.9213 | 158.1843 | 1.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 20:00 | 7 | 28 | 20 | 209 | 5012 | 80.96 | 0 | 491.095 | 491.095 | -491.095 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 600.2272 | 600.2272 | 0 | 8.5 | 0 | 100.0379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 588.2226 | 117.6445 | 1.176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 21:00 | 7 | 28 | 21 | 209 | 5013 | 78.08 | 0 | 244.0302 | 244.0302 | -244.0302 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 298.2592 | 298.2592 | 0 | 8.5 | 0 | 49.7099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 292.294 | 58.4588 | 0.5846% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 22:00 | 7 | 28 | 22 | 209 | 5014 | 75.92 | 0 | 103.5537 | 103.5537 | -103.5537 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 126.5657 | 126.5657 | 0 | 8.5 | 0 | 21.0943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 124.0343 | 24.8069 | 0.2481% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-28 23:00 | 7 | 28 | 23 | 209 | 5015 | 75.92 | 0 | 21.0449 | 21.0449 | -21.0449 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 25.7215 | 25.7215 | 0 | 8.5 | 0 | 4.2869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 25.2071 | 5.0414 | 0.05041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 | 7 | 29 | 0 | 210 | 5016 | 77 | 0 | 0.44665 | 0.44665 | -0.44665 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.5459 | 0.5459 | 0 | 8.5 | 0 | 0.090983 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.53498 | 0.107 | 0.00107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 01:00 | 7 | 29 | 1 | 210 | 5017 | 75.02 | 1.9734 | 0 | 0 | 1.9734 | Heating | 1.7412 | 8.5 | 1.7412 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.34824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.7768 | 0 | 0.35535 | 0.003554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 02:00 | 7 | 29 | 2 | 210 | 5018 | 75.02 | 7.0282 | 0 | 0 | 7.0282 | Heating | 6.2014 | 8.5 | 6.2014 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.3279 | 0 | 1.2656 | 0.01266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 03:00 | 7 | 29 | 3 | 210 | 5019 | 69.98 | 11.9087 | 0 | 0 | 11.9087 | Heating | 10.5076 | 8.5 | 10.5076 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.7221 | 0 | 2.1444 | 0.02144% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 04:00 | 7 | 29 | 4 | 210 | 5020 | 68 | 16.3301 | 0 | 0 | 16.3301 | Heating | 14.4089 | 8.5 | 14.4089 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.8818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.7029 | 0 | 2.9406 | 0.02941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 05:00 | 7 | 29 | 5 | 210 | 5021 | 68 | 13.8591 | 0 | 0 | 13.8591 | Heating | 12.2286 | 8.5 | 12.2286 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.4782 | 0 | 2.4956 | 0.02496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 06:00 | 7 | 29 | 6 | 210 | 5022 | 69.08 | 1400.2109 | 289.8224 | 289.8224 | 1110.3885 | Heating | 979.7546 | 8.5 | 979.7546 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.9509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 999.7496 | 0 | 199.9499 | 1.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 07:00 | 7 | 29 | 7 | 210 | 5023 | 73.04 | 624.9843 | 156.0435 | 156.0435 | 468.9408 | Heating | 413.7713 | 8.5 | 413.7713 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.7543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 422.2156 | 0 | 84.4431 | 0.8444% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 08:00 | 7 | 29 | 8 | 210 | 5024 | 73.04 | 44.0377 | 1418.8722 | 1418.8722 | -1374.8346 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1734.1772 | 1734.1772 | 0 | 8.5 | 0 | 289.0295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1699.4936 | 339.8987 | 3.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 09:00 | 7 | 29 | 9 | 210 | 5025 | 80.96 | 0 | 2999.32 | 2999.32 | -2999.32 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3665.8355 | 3665.8355 | 0 | 8.5 | 0 | 610.9726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3592.5188 | 718.5038 | 7.185% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 10:00 | 7 | 29 | 10 | 210 | 5026 | 84.02 | 0 | 4672.2076 | 4672.2076 | -4672.2076 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5710.476 | 5710.476 | 0 | 8.5 | 0 | 951.746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5596.2665 | 1119.2533 | 11.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 11:00 | 7 | 29 | 11 | 210 | 5027 | 84.02 | 0 | 6623.9672 | 6623.9672 | -6623.9672 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8095.96 | 8095.96 | 0 | 8.5 | 0 | 1349.3267 | 30% | 1 | 53.97% | 0% | 0% | 0% | 19.7311 | 0 | 0 | 0 | 19.7311 | 0 | 7934.0408 | 1586.8082 | 15.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.0056
2007-07-29 12:00 | 7 | 29 | 12 | 210 | 5028 | 89.06 | 0 | 7928.5019 | 7928.5019 | -7928.5019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9690.3912 | 9690.3912 | 0 | 8.5 | 0 | 1615.0652 | 32.3% | 1 | 64.6% | 0% | 0% | 0% | 29.8345 | 0 | 0 | 0 | 29.8345 | 0 | 9496.5834 | 1899.3167 | 18.99% | 1 | 37.99% | 0% | 0% | 4.398 | 0 | 0 | 4.398 | 34.2325
2007-07-29 13:00 | 7 | 29 | 13 | 210 | 5029 | 91.04 | 0 | 9114.7093 | 9114.7093 | -9114.7093 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11140.2003 | 11140.2003 | 0 | 8.5 | 0 | 1856.7001 | 37.13% | 1 | 74.27% | 0% | 0% | 0% | 41.1137 | 0 | 0 | 0 | 41.1137 | 0 | 10917.3963 | 2183.4793 | 21.83% | 1 | 43.67% | 0% | 0% | 6.0607 | 0 | 0 | 6.0607 | 47.1745
2007-07-29 14:00 | 7 | 29 | 14 | 210 | 5030 | 91.04 | 0 | 9821.8813 | 9821.8813 | -9821.8813 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12004.5216 | 12004.5216 | 0 | 8.5 | 0 | 2000.7536 | 40.02% | 1 | 80.03% | 0% | 0% | 0% | 48.8232 | 0 | 0 | 0 | 48.8232 | 0 | 11764.4312 | 2352.8862 | 23.53% | 1 | 47.06% | 0% | 0% | 7.1972 | 0 | 0 | 7.1972 | 56.0204
2007-07-29 15:00 | 7 | 29 | 15 | 210 | 5031 | 93.92 | 0 | 9721.7277 | 9721.7277 | -9721.7277 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11882.1116 | 11882.1116 | 0 | 8.5 | 0 | 1980.3519 | 39.61% | 1 | 79.21% | 0% | 0% | 0% | 47.6857 | 0 | 0 | 0 | 47.6857 | 0 | 11644.4694 | 2328.8939 | 23.29% | 1 | 46.58% | 0% | 0% | 7.0295 | 0 | 0 | 7.0295 | 54.7153
2007-07-29 16:00 | 7 | 29 | 16 | 210 | 5032 | 91.94 | 0 | 9342.4649 | 9342.4649 | -9342.4649 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11418.5683 | 11418.5683 | 0 | 8.5 | 0 | 1903.0947 | 38.06% | 1 | 76.12% | 0% | 0% | 0% | 43.5151 | 0 | 0 | 0 | 43.5151 | 0 | 11190.1969 | 2238.0394 | 22.38% | 1 | 44.76% | 0% | 0% | 6.4147 | 0 | 0 | 6.4147 | 49.9298
2007-07-29 17:00 | 7 | 29 | 17 | 210 | 5033 | 91.94 | 0 | 8529.386 | 8529.386 | -8529.386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10424.8051 | 10424.8051 | 0 | 8.5 | 0 | 1737.4675 | 34.75% | 1 | 69.5% | 0% | 0% | 0% | 35.2931 | 0 | 0 | 0 | 35.2931 | 0 | 10216.309 | 2043.2618 | 20.43% | 1 | 40.87% | 0% | 0% | 5.2027 | 0 | 0 | 5.2027 | 40.4958
2007-07-29 18:00 | 7 | 29 | 18 | 210 | 5034 | 89.96 | 0 | 5325.3 | 5325.3 | -5325.3 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6508.7 | 6508.7 | 0 | 8.5 | 0 | 1084.7833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6378.526 | 1275.7052 | 12.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 19:00 | 7 | 29 | 19 | 210 | 5035 | 87.98 | 0 | 4278.1619 | 4278.1619 | -4278.1619 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5228.8645 | 5228.8645 | 0 | 8.5 | 0 | 871.4774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5124.2873 | 1024.8575 | 10.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 20:00 | 7 | 29 | 20 | 210 | 5036 | 87.98 | 0 | 3294.7428 | 3294.7428 | -3294.7428 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4026.9079 | 4026.9079 | 0 | 8.5 | 0 | 671.1513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3946.3698 | 789.274 | 7.893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 21:00 | 7 | 29 | 21 | 210 | 5037 | 78.08 | 0 | 1772.5398 | 1772.5398 | -1772.5398 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2166.4375 | 2166.4375 | 0 | 8.5 | 0 | 361.0729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2123.1087 | 424.6217 | 4.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 22:00 | 7 | 29 | 22 | 210 | 5038 | 77 | 0 | 397.9206 | 397.9206 | -397.9206 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 486.3474 | 486.3474 | 0 | 8.5 | 0 | 81.0579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 476.6204 | 95.3241 | 0.9532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-29 23:00 | 7 | 29 | 23 | 210 | 5039 | 77 | 0 | 269.1663 | 269.1663 | -269.1663 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 328.9811 | 328.9811 | 0 | 8.5 | 0 | 54.8302 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 322.4014 | 64.4803 | 0.6448% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 | 7 | 30 | 0 | 211 | 5040 | 75.92 | 0 | 152.3384 | 152.3384 | -152.3384 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 186.1914 | 186.1914 | 0 | 8.5 | 0 | 31.0319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 182.4676 | 36.4935 | 0.3649% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 01:00 | 7 | 30 | 1 | 211 | 5041 | 73.94 | 0 | 75.4124 | 75.4124 | -75.4124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 92.1708 | 92.1708 | 0 | 8.5 | 0 | 15.3618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 90.3273 | 18.0655 | 0.1807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 02:00 | 7 | 30 | 2 | 211 | 5042 | 73.94 | 0 | 34.3956 | 34.3956 | -34.3956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 42.039 | 42.039 | 0 | 8.5 | 0 | 7.0065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 41.1983 | 8.2397 | 0.0824% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 03:00 | 7 | 30 | 3 | 211 | 5043 | 75.02 | 0 | 12.5941 | 12.5941 | -12.5941 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15.3927 | 15.3927 | 0 | 8.5 | 0 | 2.5655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 15.0849 | 3.017 | 0.03017% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 04:00 | 7 | 30 | 4 | 211 | 5044 | 75.02 | 0 | 1.2531 | 1.2531 | -1.2531 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.5316 | 1.5316 | 0 | 8.5 | 0 | 0.25527 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.501 | 0.3002 | 0.003002% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 05:00 | 7 | 30 | 5 | 211 | 5045 | 75.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-07-30 06:00 | 7 | 30 | 6 | 211 | 5046 | 75.02 | 548.1487 | 475.0422 | 475.0422 | 73.1064 | Heating | 64.5057 | 8.5 | 64.5057 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.9011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.8221 | 0 | 13.1644 | 0.1316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 07:00 | 7 | 30 | 7 | 211 | 5047 | 77 | 158.6657 | 438.6709 | 438.6709 | -280.0052 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 536.1533 | 536.1533 | 0 | 8.5 | 0 | 89.3589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 525.4302 | 105.086 | 1.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 08:00 | 7 | 30 | 8 | 211 | 5048 | 77 | 0 | 2579.6704 | 2579.6704 | -2579.6704 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3152.9304 | 3152.9304 | 0 | 8.5 | 0 | 525.4884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3089.8718 | 617.9744 | 6.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 09:00 | 7 | 30 | 9 | 211 | 5049 | 80.06 | 0 | 3194.2169 | 3194.2169 | -3194.2169 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3904.0429 | 3904.0429 | 0 | 8.5 | 0 | 650.6738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3825.9621 | 765.1924 | 7.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 10:00 | 7 | 30 | 10 | 211 | 5050 | 84.02 | 0 | 3516.3496 | 3516.3496 | -3516.3496 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4297.7606 | 4297.7606 | 0 | 8.5 | 0 | 716.2934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4211.8054 | 842.3611 | 8.424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 11:00 | 7 | 30 | 11 | 211 | 5051 | 84.02 | 0 | 4530.8072 | 4530.8072 | -4530.8072 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5537.6533 | 5537.6533 | 0 | 8.5 | 0 | 922.9422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5426.9002 | 1085.38 | 10.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 12:00 | 7 | 30 | 12 | 211 | 5052 | 84.02 | 0 | 6110.6659 | 6110.6659 | -6110.6659 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7468.5917 | 7468.5917 | 0 | 8.5 | 0 | 1244.7653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7319.2198 | 1463.844 | 14.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 13:00 | 7 | 30 | 13 | 211 | 5053 | 82.04 | 0 | 7542.1019 | 7542.1019 | -7542.1019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9218.1246 | 9218.1246 | 0 | 8.5 | 0 | 1536.3541 | 30.73% | 1 | 61.45% | 0% | 0% | 0% | 26.5957 | 0 | 0 | 0 | 26.5957 | 0 | 9033.7621 | 1806.7524 | 18.07% | 1 | 36.14% | 0% | 0% | 3.9206 | 0 | 0 | 3.9206 | 30.5162
2007-07-30 14:00 | 7 | 30 | 14 | 211 | 5054 | 80.06 | 0 | 8657.4364 | 8657.4364 | -8657.4364 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10581.3112 | 10581.3112 | 0 | 8.5 | 0 | 1763.5519 | 35.27% | 1 | 70.54% | 0% | 0% | 0% | 36.5236 | 0 | 0 | 0 | 36.5236 | 0 | 10369.6849 | 2073.937 | 20.74% | 1 | 41.48% | 0% | 0% | 5.3841 | 0 | 0 | 5.3841 | 41.9077
2007-07-30 15:00 | 7 | 30 | 15 | 211 | 5055 | 82.94 | 0 | 9386.0122 | 9386.0122 | -9386.0122 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11471.7927 | 11471.7927 | 0 | 8.5 | 0 | 1911.9654 | 38.24% | 1 | 76.48% | 0% | 0% | 0% | 43.983 | 0 | 0 | 0 | 43.983 | 0 | 11242.3568 | 2248.4714 | 22.48% | 1 | 44.97% | 0% | 0% | 6.4837 | 0 | 0 | 6.4837 | 50.4667
2007-07-30 16:00 | 7 | 30 | 16 | 211 | 5056 | 84.92 | 0 | 9863.0683 | 9863.0683 | -9863.0683 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12054.8613 | 12054.8613 | 0 | 8.5 | 0 | 2009.1435 | 40.18% | 1 | 80.37% | 0% | 0% | 0% | 49.2954 | 0 | 0 | 0 | 49.2954 | 0 | 11813.764 | 2362.7528 | 23.63% | 1 | 47.26% | 0% | 0% | 7.2668 | 0 | 0 | 7.2668 | 56.5622
2007-07-30 17:00 | 7 | 30 | 17 | 211 | 5057 | 84.92 | 0 | 9537.2217 | 9537.2217 | -9537.2217 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11656.6043 | 11656.6043 | 0 | 8.5 | 0 | 1942.7674 | 38.86% | 1 | 77.71% | 0% | 0% | 0% | 45.6298 | 0 | 0 | 0 | 45.6298 | 0 | 11423.4723 | 2284.6945 | 22.85% | 1 | 45.69% | 0% | 0% | 6.7265 | 0 | 0 | 6.7265 | 52.3563
2007-07-30 18:00 | 7 | 30 | 18 | 211 | 5058 | 84.02 | 0 | 5973.1126 | 5973.1126 | -5973.1126 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7300.4709 | 7300.4709 | 0 | 8.5 | 0 | 1216.7452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7154.4615 | 1430.8923 | 14.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 19:00 | 7 | 30 | 19 | 211 | 5059 | 80.06 | 0 | 4936.8237 | 4936.8237 | -4936.8237 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6033.8957 | 6033.8957 | 0 | 8.5 | 0 | 1005.6493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5913.2178 | 1182.6436 | 11.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 20:00 | 7 | 30 | 20 | 211 | 5060 | 80.06 | 0 | 3347.6048 | 3347.6048 | -3347.6048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4091.517 | 4091.517 | 0 | 8.5 | 0 | 681.9195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4009.6867 | 801.9373 | 8.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 21:00 | 7 | 30 | 21 | 211 | 5061 | 71.96 | 0 | 1077.4748 | 1077.4748 | -1077.4748 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1316.9137 | 1316.9137 | 0 | 8.5 | 0 | 219.4856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1290.5754 | 258.1151 | 2.581% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 22:00 | 7 | 30 | 22 | 211 | 5062 | 69.98 | 0 | 143.7391 | 143.7391 | -143.7391 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 175.6812 | 175.6812 | 0 | 8.5 | 0 | 29.2802 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 172.1676 | 34.4335 | 0.3443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-30 23:00 | 7 | 30 | 23 | 211 | 5063 | 69.98 | 0 | 27.0988 | 27.0988 | -27.0988 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 33.1208 | 33.1208 | 0 | 8.5 | 0 | 5.5201 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 32.4584 | 6.4917 | 0.06492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 | 7 | 31 | 0 | 212 | 5064 | 69.98 | 1.6869 | 0 | 0 | 1.6869 | Heating | 1.4884 | 8.5 | 1.4884 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.29768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.5188 | 0 | 0.30376 | 0.003038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 01:00 | 7 | 31 | 1 | 212 | 5065 | 68 | 7.6473 | 0 | 0 | 7.6473 | Heating | 6.7477 | 8.5 | 6.7477 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3495 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.8854 | 0 | 1.3771 | 0.01377% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 02:00 | 7 | 31 | 2 | 212 | 5066 | 68 | 11.8811 | 0 | 0 | 11.8811 | Heating | 10.4833 | 8.5 | 10.4833 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.6973 | 0 | 2.1395 | 0.02139% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 03:00 | 7 | 31 | 3 | 212 | 5067 | 69.08 | 15.6416 | 0 | 0 | 15.6416 | Heating | 13.8014 | 8.5 | 13.8014 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.083 | 0 | 2.8166 | 0.02817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 04:00 | 7 | 31 | 4 | 212 | 5068 | 68 | 17.3325 | 0 | 0 | 17.3325 | Heating | 15.2934 | 8.5 | 15.2934 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.0587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.6055 | 0 | 3.1211 | 0.03121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 05:00 | 7 | 31 | 5 | 212 | 5069 | 68 | 12.7444 | 0 | 0 | 12.7444 | Heating | 11.2451 | 8.5 | 11.2451 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.249 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.4745 | 0 | 2.2949 | 0.02295% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 06:00 | 7 | 31 | 6 | 212 | 5070 | 69.98 | 1442.2907 | 387.3714 | 387.3714 | 1054.9193 | Heating | 930.8112 | 8.5 | 930.8112 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 186.1622 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 949.8073 | 0 | 189.9615 | 1.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 07:00 | 7 | 31 | 7 | 212 | 5071 | 73.04 | 617.383 | 330.8967 | 330.8967 | 286.4862 | Heating | 252.782 | 8.5 | 252.782 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.5564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 257.9408 | 0 | 51.5882 | 0.5159% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 08:00 | 7 | 31 | 8 | 212 | 5072 | 73.04 | 30.9597 | 2924.4273 | 2924.4273 | -2893.4676 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3574.3 | 3574.3 | 0 | 8.5 | 0 | 595.7167 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3502.814 | 700.5628 | 7.006% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 09:00 | 7 | 31 | 9 | 212 | 5073 | 78.08 | 0 | 4374.1454 | 4374.1454 | -4374.1454 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5346.1777 | 5346.1777 | 0 | 8.5 | 0 | 891.0296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5239.2541 | 1047.8508 | 10.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 10:00 | 7 | 31 | 10 | 212 | 5074 | 80.06 | 0 | 6002.7034 | 6002.7034 | -6002.7034 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7336.6375 | 7336.6375 | 0 | 8.5 | 0 | 1222.7729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7189.9048 | 1437.981 | 14.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 11:00 | 7 | 31 | 11 | 212 | 5075 | 80.06 | 0 | 8168.7768 | 8168.7768 | -8168.7768 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9984.0606 | 9984.0606 | 0 | 8.5 | 0 | 1664.0101 | 33.28% | 1 | 66.56% | 0% | 0% | 0% | 31.9551 | 0 | 0 | 0 | 31.9551 | 0 | 9784.3793 | 1956.8759 | 19.57% | 1 | 39.14% | 0% | 0% | 4.7106 | 0 | 0 | 4.7106 | 36.6657
2007-07-31 12:00 | 7 | 31 | 12 | 212 | 5076 | 80.96 | 0 | 9833.8969 | 9833.8969 | -9833.8969 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12019.2073 | 12019.2073 | 0 | 8.5 | 0 | 2003.2012 | 40.06% | 1 | 80.13% | 0% | 0% | 0% | 48.9607 | 0 | 0 | 0 | 48.9607 | 0 | 11778.8232 | 2355.7646 | 23.56% | 1 | 47.12% | 0% | 0% | 7.2175 | 0 | 0 | 7.2175 | 56.1782
2007-07-31 13:00 | 7 | 31 | 13 | 212 | 5077 | 82.94 | 0 | 11362.8003 | 11362.8003 | -11362.8003 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13887.8671 | 13887.8671 | 0 | 8.5 | 0 | 2314.6445 | 46.29% | 1 | 92.59% | 0% | 0% | 0% | 68.2645 | 0 | 0 | 0 | 68.2645 | 0 | 13610.1097 | 2722.0219 | 27.22% | 1 | 54.44% | 0% | 0% | 10.0631 | 0 | 0 | 10.0631 | 78.3276
2007-07-31 14:00 | 7 | 31 | 14 | 212 | 5078 | 82.94 | 0 | 12452.0075 | 12452.0075 | -12452.0075 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15219.1202 | 15219.1202 | 0 | 8.5 | 0 | 2536.52 | 50.73% | 2 | 50.73% | 50.73% | 0% | 0% | 17.1104 | 17.1104 | 0 | 0 | 34.2208 | 0 | 14914.7378 | 2982.9476 | 29.83% | 1 | 59.66% | 0% | 0% | 12.4213 | 0 | 0 | 12.4213 | 46.6421
2007-07-31 15:00 | 7 | 31 | 15 | 212 | 5079 | 84.02 | 0 | 13117.9249 | 13117.9249 | -13117.9249 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16033.0193 | 16033.0193 | 0 | 8.5 | 0 | 2672.1699 | 53.44% | 2 | 53.44% | 53.44% | 0% | 0% | 19.2885 | 19.2885 | 0 | 0 | 38.5771 | 0 | 15712.3589 | 3142.4718 | 31.42% | 1 | 62.85% | 0% | 0% | 14.0025 | 0 | 0 | 14.0025 | 52.5796
2007-07-31 16:00 | 7 | 31 | 16 | 212 | 5080 | 84.92 | 0 | 13349.6895 | 13349.6895 | -13349.6895 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16316.2871 | 16316.2871 | 0 | 8.5 | 0 | 2719.3812 | 54.39% | 2 | 54.39% | 54.39% | 0% | 0% | 20.0814 | 20.0814 | 0 | 0 | 40.1627 | 0 | 15989.9614 | 3197.9923 | 31.98% | 1 | 63.96% | 0% | 0% | 14.5781 | 0 | 0 | 14.5781 | 54.7408
2007-07-31 17:00 | 7 | 31 | 17 | 212 | 5081 | 84.92 | 0 | 12994.8631 | 12994.8631 | -12994.8631 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15882.6105 | 15882.6105 | 0 | 8.5 | 0 | 2647.1018 | 52.94% | 2 | 52.94% | 52.94% | 0% | 0% | 18.8749 | 18.8749 | 0 | 0 | 37.7498 | 0 | 15564.9583 | 3112.9917 | 31.13% | 1 | 62.26% | 0% | 0% | 13.7022 | 0 | 0 | 13.7022 | 51.452
2007-07-31 18:00 | 7 | 31 | 18 | 212 | 5082 | 82.94 | 0 | 8818.4368 | 8818.4368 | -8818.4368 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10778.0894 | 10778.0894 | 0 | 8.5 | 0 | 1796.3482 | 35.93% | 1 | 71.85% | 0% | 0% | 0% | 38.1048 | 0 | 0 | 0 | 38.1048 | 0 | 10562.5276 | 2112.5055 | 21.13% | 1 | 42.25% | 0% | 0% | 5.6172 | 0 | 0 | 5.6172 | 43.7219
2007-07-31 19:00 | 7 | 31 | 19 | 212 | 5083 | 75.02 | 0 | 7978.5755 | 7978.5755 | -7978.5755 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9751.5923 | 9751.5923 | 0 | 8.5 | 0 | 1625.2654 | 32.51% | 1 | 65.01% | 0% | 0% | 0% | 30.2696 | 0 | 0 | 0 | 30.2696 | 0 | 9556.5604 | 1911.3121 | 19.11% | 1 | 38.23% | 0% | 0% | 4.4622 | 0 | 0 | 4.4622 | 34.7318
2007-07-31 20:00 | 7 | 31 | 20 | 212 | 5084 | 72.32 | 0 | 6906.1182 | 6906.1182 | -6906.1182 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8440.8111 | 8440.8111 | 0 | 8.5 | 0 | 1406.8019 | 30% | 1 | 56.27% | 0% | 0% | 0% | 21.7178 | 0 | 0 | 0 | 21.7178 | 0 | 8271.9949 | 1654.399 | 16.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.9924
2007-07-31 21:00 | 7 | 31 | 21 | 212 | 5085 | 69.8 | 0 | 3006.7903 | 3006.7903 | -3006.7903 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3674.9659 | 3674.9659 | 0 | 8.5 | 0 | 612.4943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3601.4666 | 720.2933 | 7.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 22:00 | 7 | 31 | 22 | 212 | 5086 | 66.74 | 0 | 1072.5716 | 1072.5716 | -1072.5716 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1310.9209 | 1310.9209 | 0 | 8.5 | 0 | 218.4868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1284.7024 | 256.9405 | 2.569% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-07-31 23:00 | 7 | 31 | 23 | 212 | 5087 | 64.22 | 0 | 943.4427 | 943.4427 | -943.4427 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1153.0966 | 1153.0966 | 0 | 8.5 | 0 | 192.1828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1130.0347 | 226.0069 | 2.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 | 8 | 1 | 0 | 213 | 5088 | 61.34 | 0 | 661.983 | 661.983 | -661.983 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 809.0903 | 809.0903 | 0 | 8.5 | 0 | 134.8484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 792.9085 | 158.5817 | 1.586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 01:00 | 8 | 1 | 1 | 213 | 5089 | 58.1 | 0 | 257.5273 | 257.5273 | -257.5273 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 314.7556 | 314.7556 | 0 | 8.5 | 0 | 52.4593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 308.4605 | 61.6921 | 0.6169% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 02:00 | 8 | 1 | 2 | 213 | 5090 | 57.56 | 0 | 96.691 | 96.691 | -96.691 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 118.1779 | 118.1779 | 0 | 8.5 | 0 | 19.6963 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 115.8143 | 23.1629 | 0.2316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 03:00 | 8 | 1 | 3 | 213 | 5091 | 57.02 | 0 | 11.6524 | 11.6524 | -11.6524 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14.2419 | 14.2419 | 0 | 8.5 | 0 | 2.3736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.957 | 2.7914 | 0.02791% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 04:00 | 8 | 1 | 4 | 213 | 5092 | 58.82 | 5.0306 | 0 | 0 | 5.0306 | Heating | 4.4388 | 8.5 | 4.4388 | 0 | 5.4727 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.88776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.5294 | 0 | 0.90588 | 0.009059% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 05:00 | 8 | 1 | 5 | 213 | 5093 | 60.62 | 11.7241 | 0 | 0 | 11.7241 | Heating | 10.3448 | 8.5 | 10.3448 | 0 | 5.7049 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.069 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.5559 | 0 | 2.1112 | 0.02111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 06:00 | 8 | 1 | 6 | 213 | 5094 | 63.86 | 1278.7391 | 341.2254 | 341.2254 | 937.5137 | Heating | 827.218 | 8.5 | 827.218 | 0 | 6.1568 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.4436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 844.1 | 0 | 168.82 | 1.688% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 07:00 | 8 | 1 | 7 | 213 | 5095 | 64.04 | 776.4139 | 496.1464 | 496.1464 | 280.2675 | Heating | 247.2949 | 8.5 | 247.2949 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.459 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 252.3417 | 0 | 50.4683 | 0.5047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 08:00 | 8 | 1 | 8 | 213 | 5096 | 64.04 | 144.3352 | 2044.8986 | 2044.8986 | -1900.5634 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2499.3205 | 2499.3205 | 0 | 8.5 | 0 | 416.5534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2449.3341 | 489.8668 | 4.899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 09:00 | 8 | 1 | 9 | 213 | 5097 | 69.98 | 0 | 3106.0417 | 3106.0417 | -3106.0417 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3796.2731 | 3796.2731 | 0 | 8.5 | 0 | 632.7122 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3720.3477 | 744.0695 | 7.441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 10:00 | 8 | 1 | 10 | 213 | 5098 | 73.04 | 0 | 3857.1083 | 3857.1083 | -3857.1083 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4714.2434 | 4714.2434 | 0 | 8.5 | 0 | 785.7072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4619.9586 | 923.9917 | 9.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 11:00 | 8 | 1 | 11 | 213 | 5099 | 73.04 | 0 | 5478.3231 | 5478.3231 | -5478.3231 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6695.7282 | 6695.7282 | 0 | 8.5 | 0 | 1115.9547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6561.8137 | 1312.3627 | 13.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 12:00 | 8 | 1 | 12 | 213 | 5100 | 78.08 | 0 | 6569.4986 | 6569.4986 | -6569.4986 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8029.3872 | 8029.3872 | 0 | 8.5 | 0 | 1338.2312 | 30% | 1 | 53.53% | 0% | 0% | 0% | 19.3599 | 0 | 0 | 0 | 19.3599 | 0 | 7868.7994 | 1573.7599 | 15.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.6344
2007-08-01 13:00 | 8 | 1 | 13 | 213 | 5101 | 80.06 | 0 | 7478.4238 | 7478.4238 | -7478.4238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9140.2957 | 9140.2957 | 0 | 8.5 | 0 | 1523.3826 | 30.47% | 1 | 60.94% | 0% | 0% | 0% | 26.0821 | 0 | 0 | 0 | 26.0821 | 0 | 8957.4898 | 1791.498 | 17.91% | 1 | 35.83% | 0% | 0% | 3.8449 | 0 | 0 | 3.8449 | 29.9269
2007-08-01 14:00 | 8 | 1 | 14 | 213 | 5102 | 80.06 | 0 | 8139.5731 | 8139.5731 | -8139.5731 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9948.3672 | 9948.3672 | 0 | 8.5 | 0 | 1658.0612 | 33.16% | 1 | 66.32% | 0% | 0% | 0% | 31.6929 | 0 | 0 | 0 | 31.6929 | 0 | 9749.3998 | 1949.88 | 19.5% | 1 | 39% | 0% | 0% | 4.672 | 0 | 0 | 4.672 | 36.3649
2007-08-01 15:00 | 8 | 1 | 15 | 213 | 5103 | 82.04 | 0 | 8282.5966 | 8282.5966 | -8282.5966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10123.1736 | 10123.1736 | 0 | 8.5 | 0 | 1687.1956 | 33.74% | 1 | 67.49% | 0% | 0% | 0% | 32.9884 | 0 | 0 | 0 | 32.9884 | 0 | 9920.7101 | 1984.142 | 19.84% | 1 | 39.68% | 0% | 0% | 4.8629 | 0 | 0 | 4.8629 | 37.8514
2007-08-01 16:00 | 8 | 1 | 16 | 213 | 5104 | 80.06 | 0 | 7694.9805 | 7694.9805 | -7694.9805 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9404.9761 | 9404.9761 | 0 | 8.5 | 0 | 1567.496 | 31.35% | 1 | 62.7% | 0% | 0% | 0% | 27.852 | 0 | 0 | 0 | 27.852 | 0 | 9216.8766 | 1843.3753 | 18.43% | 1 | 36.87% | 0% | 0% | 4.1058 | 0 | 0 | 4.1058 | 31.9577
2007-08-01 17:00 | 8 | 1 | 17 | 213 | 5105 | 80.06 | 0 | 7002.2557 | 7002.2557 | -7002.2557 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8558.3125 | 8558.3125 | 0 | 8.5 | 0 | 1426.3854 | 30% | 1 | 57.06% | 0% | 0% | 0% | 22.4195 | 0 | 0 | 0 | 22.4195 | 0 | 8387.1463 | 1677.4293 | 16.77% | 1 | 33.55% | 0% | 0% | 3.3049 | 0 | 0 | 3.3049 | 25.7244
2007-08-01 18:00 | 8 | 1 | 18 | 213 | 5106 | 80.06 | 0 | 4355.8646 | 4355.8646 | -4355.8646 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5323.8345 | 5323.8345 | 0 | 8.5 | 0 | 887.3057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5217.3578 | 1043.4716 | 10.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 19:00 | 8 | 1 | 19 | 213 | 5107 | 78.98 | 0 | 2994.217 | 2994.217 | -2994.217 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3659.5985 | 3659.5985 | 0 | 8.5 | 0 | 609.9331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3586.4066 | 717.2813 | 7.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 20:00 | 8 | 1 | 20 | 213 | 5108 | 78.98 | 0 | 1086.1019 | 1086.1019 | -1086.1019 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1327.4579 | 1327.4579 | 0 | 8.5 | 0 | 221.243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1300.9087 | 260.1817 | 2.602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 21:00 | 8 | 1 | 21 | 213 | 5109 | 75.02 | 0 | 476.8853 | 476.8853 | -476.8853 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 582.8598 | 582.8598 | 0 | 8.5 | 0 | 97.1433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 571.2026 | 114.2405 | 1.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 22:00 | 8 | 1 | 22 | 213 | 5110 | 73.04 | 0 | 14.3449 | 14.3449 | -14.3449 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17.5327 | 17.5327 | 0 | 8.5 | 0 | 2.9221 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 17.1821 | 3.4364 | 0.03436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-01 23:00 | 8 | 1 | 23 | 213 | 5111 | 73.04 | 3.9728 | 0 | 0 | 3.9728 | Heating | 3.5054 | 8.5 | 3.5054 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.70108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.577 | 0 | 0.71539 | 0.007154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 | 8 | 2 | 0 | 214 | 5112 | 71.06 | 15.5063 | 0 | 0 | 15.5063 | Heating | 13.682 | 8.5 | 13.682 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.7364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.9612 | 0 | 2.7922 | 0.02792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 01:00 | 8 | 2 | 1 | 214 | 5113 | 71.06 | 32.7934 | 0 | 0 | 32.7934 | Heating | 28.9353 | 8.5 | 28.9353 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.7871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 29.5259 | 0 | 5.9052 | 0.05905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 02:00 | 8 | 2 | 2 | 214 | 5114 | 71.06 | 46.8106 | 0 | 0 | 46.8106 | Heating | 41.3035 | 8.5 | 41.3035 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.2607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.1464 | 0 | 8.4293 | 0.08429% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 03:00 | 8 | 2 | 3 | 214 | 5115 | 71.06 | 60.903 | 0 | 0 | 60.903 | Heating | 53.738 | 8.5 | 53.738 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.7476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 54.8346 | 0 | 10.9669 | 0.1097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 04:00 | 8 | 2 | 4 | 214 | 5116 | 69.08 | 88.0858 | 0 | 0 | 88.0858 | Heating | 77.7227 | 8.5 | 77.7227 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.5445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 79.3089 | 0 | 15.8618 | 0.1586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 05:00 | 8 | 2 | 5 | 214 | 5117 | 69.08 | 117.5206 | 0 | 0 | 117.5206 | Heating | 103.6947 | 8.5 | 103.6947 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.7389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 105.8109 | 0 | 21.1622 | 0.2116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 06:00 | 8 | 2 | 6 | 214 | 5118 | 68 | 3207.7457 | 170.9567 | 170.9567 | 3036.789 | Heating | 2679.5197 | 8.5 | 2679.5197 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 535.9039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2734.2038 | 0 | 546.8408 | 5.468% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 07:00 | 8 | 2 | 7 | 214 | 5119 | 69.98 | 1695.6094 | 170.7786 | 170.7786 | 1524.8309 | Heating | 1345.439 | 8.5 | 1345.439 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 269.0878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1372.8969 | 0 | 274.5794 | 2.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 08:00 | 8 | 2 | 8 | 214 | 5120 | 69.98 | 628.4694 | 1004.8756 | 1004.8756 | -376.4062 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1228.1813 | 1228.1813 | 0 | 8.5 | 0 | 204.6969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1203.6176 | 240.7235 | 2.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 09:00 | 8 | 2 | 9 | 214 | 5121 | 69.98 | 3.9159 | 2464.0192 | 2464.0192 | -2460.1032 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3011.579 | 3011.579 | 0 | 8.5 | 0 | 501.9298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2951.3474 | 590.2695 | 5.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 10:00 | 8 | 2 | 10 | 214 | 5122 | 71.06 | 0 | 3395.9782 | 3395.9782 | -3395.9782 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4150.64 | 4150.64 | 0 | 8.5 | 0 | 691.7733 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4067.6272 | 813.5254 | 8.135% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 11:00 | 8 | 2 | 11 | 214 | 5123 | 71.06 | 0 | 4983.2386 | 4983.2386 | -4983.2386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6090.625 | 6090.625 | 0 | 8.5 | 0 | 1015.1042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5968.8125 | 1193.7625 | 11.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 12:00 | 8 | 2 | 12 | 214 | 5124 | 71.6 | 0 | 6036.3546 | 6036.3546 | -6036.3546 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7377.7668 | 7377.7668 | 0 | 8.5 | 0 | 1229.6278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7230.2115 | 1446.0423 | 14.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 13:00 | 8 | 2 | 13 | 214 | 5125 | 71.6 | 0 | 6956.7556 | 6956.7556 | -6956.7556 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8502.7013 | 8502.7013 | 0 | 8.5 | 0 | 1417.1169 | 30% | 1 | 56.68% | 0% | 0% | 0% | 22.0858 | 0 | 0 | 0 | 22.0858 | 0 | 8332.6472 | 1666.5294 | 16.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.3604
2007-08-02 14:00 | 8 | 2 | 14 | 214 | 5126 | 71.06 | 0 | 7551.3099 | 7551.3099 | -7551.3099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9229.3787 | 9229.3787 | 0 | 8.5 | 0 | 1538.2298 | 30.76% | 1 | 61.53% | 0% | 0% | 0% | 26.6704 | 0 | 0 | 0 | 26.6704 | 0 | 9044.7911 | 1808.9582 | 18.09% | 1 | 36.18% | 0% | 0% | 3.9316 | 0 | 0 | 3.9316 | 30.602
2007-08-02 15:00 | 8 | 2 | 15 | 214 | 5127 | 71.6 | 0 | 7634.2862 | 7634.2862 | -7634.2862 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9330.7943 | 9330.7943 | 0 | 8.5 | 0 | 1555.1324 | 31.1% | 1 | 62.21% | 0% | 0% | 0% | 27.3493 | 0 | 0 | 0 | 27.3493 | 0 | 9144.1784 | 1828.8357 | 18.29% | 1 | 36.58% | 0% | 0% | 4.0317 | 0 | 0 | 4.0317 | 31.3809
2007-08-02 16:00 | 8 | 2 | 16 | 214 | 5128 | 73.4 | 0 | 7401.1092 | 7401.1092 | -7401.1092 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9045.8001 | 9045.8001 | 0 | 8.5 | 0 | 1507.6334 | 30.15% | 1 | 60.31% | 0% | 0% | 0% | 25.466 | 0 | 0 | 0 | 25.466 | 0 | 8864.8841 | 1772.9768 | 17.73% | 1 | 35.46% | 0% | 0% | 3.754 | 0 | 0 | 3.754 | 29.2201
2007-08-02 17:00 | 8 | 2 | 17 | 214 | 5129 | 73.04 | 0 | 6842.2304 | 6842.2304 | -6842.2304 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8362.726 | 8362.726 | 0 | 8.5 | 0 | 1393.7877 | 30% | 1 | 55.75% | 0% | 0% | 0% | 21.2585 | 0 | 0 | 0 | 21.2585 | 0 | 8195.4715 | 1639.0943 | 16.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.5331
2007-08-02 18:00 | 8 | 2 | 18 | 214 | 5130 | 73.4 | 0 | 4296.9334 | 4296.9334 | -4296.9334 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5251.8075 | 5251.8075 | 0 | 8.5 | 0 | 875.3013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5146.7714 | 1029.3543 | 10.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 19:00 | 8 | 2 | 19 | 214 | 5131 | 71.6 | 0 | 3282.3469 | 3282.3469 | -3282.3469 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4011.7574 | 4011.7574 | 0 | 8.5 | 0 | 668.6262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3931.5222 | 786.3044 | 7.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 20:00 | 8 | 2 | 20 | 214 | 5132 | 71.06 | 0 | 983.599 | 983.599 | -983.599 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1202.1765 | 1202.1765 | 0 | 8.5 | 0 | 200.3628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1178.133 | 235.6266 | 2.356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 21:00 | 8 | 2 | 21 | 214 | 5133 | 68 | 0 | 418.9131 | 418.9131 | -418.9131 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 512.0049 | 512.0049 | 0 | 8.5 | 0 | 85.3341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 501.7648 | 100.353 | 1.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 22:00 | 8 | 2 | 22 | 214 | 5134 | 69.8 | 0.6301 | 0.018452 | 0.018452 | 0.61164 | Heating | 0.53969 | 8.5 | 0.53969 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.10794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.5507 | 0 | 0.11014 | 0.001101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-02 23:00 | 8 | 2 | 23 | 214 | 5135 | 66.2 | 8.177 | 0 | 0 | 8.177 | Heating | 7.215 | 8.5 | 7.215 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.3622 | 0 | 1.4724 | 0.01472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 | 8 | 3 | 0 | 215 | 5136 | 66.2 | 23.0925 | 0 | 0 | 23.0925 | Heating | 20.3757 | 8.5 | 20.3757 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.0751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.7915 | 0 | 4.1583 | 0.04158% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 01:00 | 8 | 3 | 1 | 215 | 5137 | 64.4 | 33.3318 | 0 | 0 | 33.3318 | Heating | 29.4104 | 8.5 | 29.4104 | 0 | 6.2364 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.8821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.0106 | 0 | 6.0021 | 0.06002% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 02:00 | 8 | 3 | 2 | 215 | 5138 | 64.94 | 46.3009 | 0 | 0 | 46.3009 | Heating | 40.8538 | 8.5 | 40.8538 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.1708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 41.6875 | 0 | 8.3375 | 0.08338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 03:00 | 8 | 3 | 3 | 215 | 5139 | 64.04 | 71.7185 | 0 | 0 | 71.7185 | Heating | 63.281 | 8.5 | 63.281 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.6562 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 64.5725 | 0 | 12.9145 | 0.1291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 04:00 | 8 | 3 | 4 | 215 | 5140 | 62.06 | 112.7543 | 0 | 0 | 112.7543 | Heating | 99.4891 | 8.5 | 99.4891 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.8978 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 101.5195 | 0 | 20.3039 | 0.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 05:00 | 8 | 3 | 5 | 215 | 5141 | 62.06 | 155.3413 | 0 | 0 | 155.3413 | Heating | 137.0659 | 8.5 | 137.0659 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.4132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 139.8632 | 0 | 27.9726 | 0.2797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 06:00 | 8 | 3 | 6 | 215 | 5142 | 64.04 | 3278.8243 | 84.388 | 84.388 | 3194.4363 | Heating | 2818.6202 | 8.5 | 2818.6202 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 563.724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2876.1431 | 0 | 575.2286 | 5.752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 07:00 | 8 | 3 | 7 | 215 | 5143 | 66.02 | 1841.3163 | 63.4181 | 63.4181 | 1777.8982 | Heating | 1568.7337 | 8.5 | 1568.7337 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.7467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1600.7487 | 0 | 320.1497 | 3.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 08:00 | 8 | 3 | 8 | 215 | 5144 | 66.02 | 800.6695 | 197.6174 | 197.6174 | 603.052 | Heating | 532.1047 | 8.5 | 532.1047 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.4209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.964 | 0 | 108.5928 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 09:00 | 8 | 3 | 9 | 215 | 5145 | 71.06 | 3.8137 | 282.39 | 282.39 | -278.5762 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 345.1433 | 345.1433 | 0 | 8.5 | 0 | 57.5239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 338.2404 | 67.6481 | 0.6765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 10:00 | 8 | 3 | 10 | 215 | 5146 | 73.04 | 0 | 616.1331 | 616.1331 | -616.1331 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 753.0515 | 753.0515 | 0 | 8.5 | 0 | 125.5086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 737.9905 | 147.5981 | 1.476% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 11:00 | 8 | 3 | 11 | 215 | 5147 | 73.04 | 0 | 2440.3536 | 2440.3536 | -2440.3536 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2982.6544 | 2982.6544 | 0 | 8.5 | 0 | 497.1091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2923.0013 | 584.6003 | 5.846% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 12:00 | 8 | 3 | 12 | 215 | 5148 | 75.92 | 0 | 3567.3808 | 3567.3808 | -3567.3808 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4360.1321 | 4360.1321 | 0 | 8.5 | 0 | 726.6887 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4272.9295 | 854.5859 | 8.546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 13:00 | 8 | 3 | 13 | 215 | 5149 | 77 | 0 | 4393.6506 | 4393.6506 | -4393.6506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5370.0174 | 5370.0174 | 0 | 8.5 | 0 | 895.0029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5262.6171 | 1052.5234 | 10.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 14:00 | 8 | 3 | 14 | 215 | 5150 | 77 | 0 | 4731.6092 | 4731.6092 | -4731.6092 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5783.0779 | 5783.0779 | 0 | 8.5 | 0 | 963.8463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5667.4164 | 1133.4833 | 11.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 15:00 | 8 | 3 | 15 | 215 | 5151 | 78.08 | 0 | 5117.219 | 5117.219 | -5117.219 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6254.3788 | 6254.3788 | 0 | 8.5 | 0 | 1042.3965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6129.2912 | 1225.8582 | 12.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 16:00 | 8 | 3 | 16 | 215 | 5152 | 78.98 | 0 | 5448.4863 | 5448.4863 | -5448.4863 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6659.261 | 6659.261 | 0 | 8.5 | 0 | 1109.8768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6526.0758 | 1305.2152 | 13.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 17:00 | 8 | 3 | 17 | 215 | 5153 | 78.98 | 0 | 5383.9858 | 5383.9858 | -5383.9858 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6580.4271 | 6580.4271 | 0 | 8.5 | 0 | 1096.7378 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6448.8185 | 1289.7637 | 12.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 18:00 | 8 | 3 | 18 | 215 | 5154 | 75.92 | 0 | 3287.8165 | 3287.8165 | -3287.8165 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4018.4424 | 4018.4424 | 0 | 8.5 | 0 | 669.7404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3938.0735 | 787.6147 | 7.876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 19:00 | 8 | 3 | 19 | 215 | 5155 | 73.94 | 0 | 2271.2267 | 2271.2267 | -2271.2267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2775.9437 | 2775.9437 | 0 | 8.5 | 0 | 462.6573 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2720.4249 | 544.085 | 5.441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 20:00 | 8 | 3 | 20 | 215 | 5156 | 73.94 | 0 | 1070.712 | 1070.712 | -1070.712 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1308.648 | 1308.648 | 0 | 8.5 | 0 | 218.108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1282.475 | 256.495 | 2.565% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 21:00 | 8 | 3 | 21 | 215 | 5157 | 66.02 | 0 | 194.0428 | 194.0428 | -194.0428 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 237.1634 | 237.1634 | 0 | 8.5 | 0 | 39.5272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 232.4202 | 46.484 | 0.4648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 22:00 | 8 | 3 | 22 | 215 | 5158 | 62.96 | 0 | 45.1354 | 45.1354 | -45.1354 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 55.1655 | 55.1655 | 0 | 8.5 | 0 | 9.1942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 54.0622 | 10.8124 | 0.1081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-03 23:00 | 8 | 3 | 23 | 215 | 5159 | 62.96 | 0 | 2.298 | 2.298 | -2.298 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.8087 | 2.8087 | 0 | 8.5 | 0 | 0.46812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.7526 | 0.55051 | 0.005505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 | 8 | 4 | 0 | 216 | 5160 | 62.06 | 2.8335 | 0 | 0 | 2.8335 | Heating | 2.5001 | 8.5 | 2.5001 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.50003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.5512 | 0 | 0.51023 | 0.005102% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 01:00 | 8 | 4 | 1 | 216 | 5161 | 60.98 | 10.1553 | 0 | 0 | 10.1553 | Heating | 8.9606 | 8.5 | 8.9606 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.7921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.1434 | 0 | 1.8287 | 0.01829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 02:00 | 8 | 4 | 2 | 216 | 5162 | 60.98 | 26.5581 | 0 | 0 | 26.5581 | Heating | 23.4337 | 8.5 | 23.4337 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.9119 | 0 | 4.7824 | 0.04782% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 03:00 | 8 | 4 | 3 | 216 | 5163 | 60.08 | 38.0814 | 0 | 0 | 38.0814 | Heating | 33.6012 | 8.5 | 33.6012 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.287 | 0 | 6.8574 | 0.06857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 04:00 | 8 | 4 | 4 | 216 | 5164 | 59 | 46.2783 | 0 | 0 | 46.2783 | Heating | 40.8338 | 8.5 | 40.8338 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.1668 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 41.6672 | 0 | 8.3334 | 0.08333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 05:00 | 8 | 4 | 5 | 216 | 5165 | 59 | 62.2575 | 0 | 0 | 62.2575 | Heating | 54.9331 | 8.5 | 54.9331 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.9866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.0542 | 0 | 11.2108 | 0.1121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 06:00 | 8 | 4 | 6 | 216 | 5166 | 60.08 | 48.405 | 0 | 0 | 48.405 | Heating | 42.7103 | 8.5 | 42.7103 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.5421 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.5819 | 0 | 8.7164 | 0.08716% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 07:00 | 8 | 4 | 7 | 216 | 5167 | 62.96 | 17.9586 | 0 | 0 | 17.9586 | Heating | 15.8458 | 8.5 | 15.8458 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.1692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.1692 | 0 | 3.2338 | 0.03234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 08:00 | 8 | 4 | 8 | 216 | 5168 | 62.96 | 1241.7967 | 2.9412 | 2.9412 | 1238.8555 | Heating | 1093.1078 | 8.5 | 1093.1078 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.6216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1115.4161 | 0 | 223.0832 | 2.231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 09:00 | 8 | 4 | 9 | 216 | 5169 | 71.96 | 146.7232 | 152.084 | 152.084 | -5.3609 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 185.8805 | 185.8805 | 0 | 8.5 | 0 | 30.9801 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 182.1629 | 36.4326 | 0.3643% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 10:00 | 8 | 4 | 10 | 216 | 5170 | 73.94 | 0 | 299.6162 | 299.6162 | -299.6162 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 366.1976 | 366.1976 | 0 | 8.5 | 0 | 61.0329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 358.8737 | 71.7747 | 0.7177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 11:00 | 8 | 4 | 11 | 216 | 5171 | 73.94 | 0 | 579.7575 | 579.7575 | -579.7575 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 708.5925 | 708.5925 | 0 | 8.5 | 0 | 118.0987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 694.4206 | 138.8841 | 1.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 12:00 | 8 | 4 | 12 | 216 | 5172 | 80.06 | 0 | 2864.4449 | 2864.4449 | -2864.4449 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3500.9882 | 3500.9882 | 0 | 8.5 | 0 | 583.498 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3430.9684 | 686.1937 | 6.862% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 13:00 | 8 | 4 | 13 | 216 | 5173 | 82.04 | 0 | 3639.0037 | 3639.0037 | -3639.0037 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4447.6712 | 4447.6712 | 0 | 8.5 | 0 | 741.2785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4358.7178 | 871.7436 | 8.717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 14:00 | 8 | 4 | 14 | 216 | 5174 | 82.04 | 0 | 4487.9929 | 4487.9929 | -4487.9929 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5485.3247 | 5485.3247 | 0 | 8.5 | 0 | 914.2208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5375.6182 | 1075.1236 | 10.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 15:00 | 8 | 4 | 15 | 216 | 5175 | 82.94 | 0 | 4558.5158 | 4558.5158 | -4558.5158 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5571.5193 | 5571.5193 | 0 | 8.5 | 0 | 928.5865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5460.0889 | 1092.0178 | 10.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 16:00 | 8 | 4 | 16 | 216 | 5176 | 82.94 | 0 | 4868.8695 | 4868.8695 | -4868.8695 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5950.8405 | 5950.8405 | 0 | 8.5 | 0 | 991.8068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5831.8237 | 1166.3647 | 11.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 17:00 | 8 | 4 | 17 | 216 | 5177 | 82.94 | 0 | 4949.7735 | 4949.7735 | -4949.7735 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6049.7231 | 6049.7231 | 0 | 8.5 | 0 | 1008.2872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5928.7287 | 1185.7457 | 11.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 18:00 | 8 | 4 | 18 | 216 | 5178 | 82.04 | 0 | 4208.0637 | 4208.0637 | -4208.0637 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5143.1889 | 5143.1889 | 0 | 8.5 | 0 | 857.1982 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5040.3252 | 1008.065 | 10.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 19:00 | 8 | 4 | 19 | 216 | 5179 | 80.06 | 0 | 1629.5329 | 1629.5329 | -1629.5329 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1991.6514 | 1991.6514 | 0 | 8.5 | 0 | 331.9419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1951.8183 | 390.3637 | 3.904% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 20:00 | 8 | 4 | 20 | 216 | 5180 | 80.06 | 0 | 1108.8306 | 1108.8306 | -1108.8306 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1355.2374 | 1355.2374 | 0 | 8.5 | 0 | 225.8729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1328.1327 | 265.6265 | 2.656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 21:00 | 8 | 4 | 21 | 216 | 5181 | 75.92 | 0 | 506.353 | 506.353 | -506.353 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 618.8759 | 618.8759 | 0 | 8.5 | 0 | 103.146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 606.4984 | 121.2997 | 1.213% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 22:00 | 8 | 4 | 22 | 216 | 5182 | 73.94 | 0 | 224.1633 | 224.1633 | -224.1633 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 273.9774 | 273.9774 | 0 | 8.5 | 0 | 45.6629 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 268.4979 | 53.6996 | 0.537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-04 23:00 | 8 | 4 | 23 | 216 | 5183 | 73.94 | 0 | 75.604 | 75.604 | -75.604 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 92.4049 | 92.4049 | 0 | 8.5 | 0 | 15.4008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 90.5568 | 18.1114 | 0.1811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 | 8 | 5 | 0 | 217 | 5184 | 73.04 | 0.081586 | 4.8268 | 4.8268 | -4.7452 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5.8994 | 5.8994 | 0 | 8.5 | 0 | 0.98323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5.7814 | 1.1563 | 0.01156% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 01:00 | 8 | 5 | 1 | 217 | 5185 | 73.04 | 3.4204 | 0 | 0 | 3.4204 | Heating | 3.018 | 8.5 | 3.018 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.6036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.0796 | 0 | 0.61592 | 0.006159% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 02:00 | 8 | 5 | 2 | 217 | 5186 | 73.04 | 8.8918 | 0 | 0 | 8.8918 | Heating | 7.8457 | 8.5 | 7.8457 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.0058 | 0 | 1.6012 | 0.01601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 03:00 | 8 | 5 | 3 | 217 | 5187 | 71.96 | 18.59 | 0 | 0 | 18.59 | Heating | 16.403 | 8.5 | 16.403 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.2806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.7377 | 0 | 3.3475 | 0.03348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 04:00 | 8 | 5 | 4 | 217 | 5188 | 71.06 | 27.7969 | 0 | 0 | 27.7969 | Heating | 24.5267 | 8.5 | 24.5267 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.9053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 25.0273 | 0 | 5.0055 | 0.05005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 05:00 | 8 | 5 | 5 | 217 | 5189 | 71.06 | 34.2097 | 0 | 0 | 34.2097 | Heating | 30.185 | 8.5 | 30.185 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.801 | 0 | 6.1602 | 0.0616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 06:00 | 8 | 5 | 6 | 217 | 5190 | 69.8 | 1814.0775 | 228.5195 | 228.5195 | 1585.558 | Heating | 1399.0218 | 8.5 | 1399.0218 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.8044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1427.5733 | 0 | 285.5147 | 2.855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 07:00 | 8 | 5 | 7 | 217 | 5191 | 71.96 | 999.038 | 384.7117 | 384.7117 | 614.3263 | Heating | 542.0526 | 8.5 | 542.0526 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.4105 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 553.1149 | 0 | 110.623 | 1.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 08:00 | 8 | 5 | 8 | 217 | 5192 | 71.96 | 58.9551 | 2497.4166 | 2497.4166 | -2438.4615 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3052.3981 | 3052.3981 | 0 | 8.5 | 0 | 508.733 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2991.3501 | 598.27 | 5.983% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 09:00 | 8 | 5 | 9 | 217 | 5193 | 75.92 | 0 | 4426.7125 | 4426.7125 | -4426.7125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5410.4264 | 5410.4264 | 0 | 8.5 | 0 | 901.7377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5302.2179 | 1060.4436 | 10.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 10:00 | 8 | 5 | 10 | 217 | 5194 | 75.2 | 0 | 7197.8932 | 7197.8932 | -7197.8932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8797.425 | 8797.425 | 0 | 8.5 | 0 | 1466.2375 | 30% | 1 | 58.65% | 0% | 0% | 0% | 23.8864 | 0 | 0 | 0 | 23.8864 | 0 | 8621.4765 | 1724.2953 | 17.24% | 1 | 34.49% | 0% | 0% | 3.5212 | 0 | 0 | 3.5212 | 27.4076
2007-08-05 11:00 | 8 | 5 | 11 | 217 | 5195 | 75.92 | 0 | 9286.733 | 9286.733 | -9286.733 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11350.4514 | 11350.4514 | 0 | 8.5 | 0 | 1891.7419 | 37.83% | 1 | 75.67% | 0% | 0% | 0% | 42.9204 | 0 | 0 | 0 | 42.9204 | 0 | 11123.4424 | 2224.6885 | 22.25% | 1 | 44.49% | 0% | 0% | 6.327 | 0 | 0 | 6.327 | 49.2474
2007-08-05 12:00 | 8 | 5 | 12 | 217 | 5196 | 73.94 | 0 | 10744.4921 | 10744.4921 | -10744.4921 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13132.157 | 13132.157 | 0 | 8.5 | 0 | 2188.6928 | 43.77% | 1 | 87.55% | 0% | 0% | 0% | 60.0214 | 0 | 0 | 0 | 60.0214 | 0 | 12869.5139 | 2573.9028 | 25.74% | 1 | 51.48% | 0% | 0% | 8.848 | 0 | 0 | 8.848 | 68.8694
2007-08-05 13:00 | 8 | 5 | 13 | 217 | 5197 | 77 | 0 | 11607.2159 | 11607.2159 | -11607.2159 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14186.5972 | 14186.5972 | 0 | 8.5 | 0 | 2364.4329 | 47.29% | 1 | 94.58% | 0% | 0% | 0% | 71.6891 | 0 | 0 | 0 | 71.6891 | 0 | 13902.8653 | 2780.5731 | 27.81% | 1 | 55.61% | 0% | 0% | 10.568 | 0 | 0 | 10.568 | 82.2571
2007-08-05 14:00 | 8 | 5 | 14 | 217 | 5198 | 77 | 0 | 12016.0625 | 12016.0625 | -12016.0625 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14686.2986 | 14686.2986 | 0 | 8.5 | 0 | 2447.7164 | 48.95% | 1 | 97.91% | 0% | 0% | 0% | 77.6304 | 0 | 0 | 0 | 77.6304 | 0 | 14392.5726 | 2878.5145 | 28.79% | 1 | 57.57% | 0% | 0% | 11.4438 | 0 | 0 | 11.4438 | 89.0741
2007-08-05 15:00 | 8 | 5 | 15 | 217 | 5199 | 75.02 | 0 | 11943.831 | 11943.831 | -11943.831 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14598.0157 | 14598.0157 | 0 | 8.5 | 0 | 2433.0026 | 48.66% | 1 | 97.32% | 0% | 0% | 0% | 76.5612 | 0 | 0 | 0 | 76.5612 | 0 | 14306.0554 | 2861.2111 | 28.61% | 1 | 57.22% | 0% | 0% | 11.2862 | 0 | 0 | 11.2862 | 87.8474
2007-08-05 16:00 | 8 | 5 | 16 | 217 | 5200 | 73.94 | 0 | 11450.2833 | 11450.2833 | -11450.2833 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13994.7907 | 13994.7907 | 0 | 8.5 | 0 | 2332.4651 | 46.65% | 1 | 93.3% | 0% | 0% | 0% | 69.4794 | 0 | 0 | 0 | 69.4794 | 0 | 13714.8949 | 2742.979 | 27.43% | 1 | 54.86% | 0% | 0% | 10.2422 | 0 | 0 | 10.2422 | 79.7216
2007-08-05 17:00 | 8 | 5 | 17 | 217 | 5201 | 73.94 | 0 | 10955.9844 | 10955.9844 | -10955.9844 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13390.6476 | 13390.6476 | 0 | 8.5 | 0 | 2231.7746 | 44.64% | 1 | 89.27% | 0% | 0% | 0% | 62.7736 | 0 | 0 | 0 | 62.7736 | 0 | 13122.8346 | 2624.5669 | 26.25% | 1 | 52.49% | 0% | 0% | 9.2537 | 0 | 0 | 9.2537 | 72.0272
2007-08-05 18:00 | 8 | 5 | 18 | 217 | 5202 | 71.96 | 0 | 7338.5354 | 7338.5354 | -7338.5354 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8969.321 | 8969.321 | 0 | 8.5 | 0 | 1494.8868 | 30% | 1 | 59.8% | 0% | 0% | 0% | 24.9735 | 0 | 0 | 0 | 24.9735 | 0 | 8789.9346 | 1757.9869 | 17.58% | 1 | 35.16% | 0% | 0% | 3.6814 | 0 | 0 | 3.6814 | 28.655
2007-08-05 19:00 | 8 | 5 | 19 | 217 | 5203 | 69.08 | 0 | 6134.5336 | 6134.5336 | -6134.5336 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7497.7632 | 7497.7632 | 0 | 8.5 | 0 | 1249.6272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7347.808 | 1469.5616 | 14.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 20:00 | 8 | 5 | 20 | 217 | 5204 | 69.08 | 0 | 4906.252 | 4906.252 | -4906.252 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5996.5302 | 5996.5302 | 0 | 8.5 | 0 | 999.4217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5876.5996 | 1175.3199 | 11.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 21:00 | 8 | 5 | 21 | 217 | 5205 | 64.94 | 0 | 2369.1298 | 2369.1298 | -2369.1298 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2895.603 | 2895.603 | 0 | 8.5 | 0 | 482.6005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2837.691 | 567.5382 | 5.675% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 22:00 | 8 | 5 | 22 | 217 | 5206 | 64.04 | 0 | 716.9627 | 716.9627 | -716.9627 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 876.2878 | 876.2878 | 0 | 8.5 | 0 | 146.048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 858.762 | 171.7524 | 1.718% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-05 23:00 | 8 | 5 | 23 | 217 | 5207 | 64.04 | 0 | 730.9207 | 730.9207 | -730.9207 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 893.3475 | 893.3475 | 0 | 8.5 | 0 | 148.8912 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 875.4805 | 175.0961 | 1.751% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 | 8 | 6 | 0 | 218 | 5208 | 60.98 | 0 | 515.5069 | 515.5069 | -515.5069 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 630.0639 | 630.0639 | 0 | 8.5 | 0 | 105.0107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 617.4627 | 123.4925 | 1.235% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 01:00 | 8 | 6 | 1 | 218 | 5209 | 57.92 | 0 | 289.2878 | 289.2878 | -289.2878 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 353.574 | 353.574 | 0 | 8.5 | 0 | 58.929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 346.5025 | 69.3005 | 0.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 02:00 | 8 | 6 | 2 | 218 | 5210 | 57.92 | 0 | 134.9269 | 134.9269 | -134.9269 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 164.9107 | 164.9107 | 0 | 8.5 | 0 | 27.4851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 161.6125 | 32.3225 | 0.3232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 03:00 | 8 | 6 | 3 | 218 | 5211 | 57.02 | 0 | 46.3876 | 46.3876 | -46.3876 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 56.6959 | 56.6959 | 0 | 8.5 | 0 | 9.4493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 55.562 | 11.1124 | 0.1111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 04:00 | 8 | 6 | 4 | 218 | 5212 | 55.94 | 0 | 5.9357 | 5.9357 | -5.9357 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7.2547 | 7.2547 | 0 | 8.5 | 0 | 1.2091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7.1096 | 1.4219 | 0.01422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 05:00 | 8 | 6 | 5 | 218 | 5213 | 55.94 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-06 06:00 | 8 | 6 | 6 | 218 | 5214 | 57.02 | 729.6055 | 709.252 | 709.252 | 20.3535 | Heating | 17.959 | 8.5 | 17.959 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.5918 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.3255 | 0 | 3.6651 | 0.03665% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 07:00 | 8 | 6 | 7 | 218 | 5215 | 62.96 | 186.7696 | 999.8679 | 999.8679 | -813.0983 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1222.0608 | 1222.0608 | 0 | 8.5 | 0 | 203.6768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1197.6196 | 239.5239 | 2.395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 08:00 | 8 | 6 | 8 | 218 | 5216 | 62.96 | 0 | 3924.7217 | 3924.7217 | -3924.7217 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4796.8821 | 4796.8821 | 0 | 8.5 | 0 | 799.4804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4700.9445 | 940.1889 | 9.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 09:00 | 8 | 6 | 9 | 218 | 5217 | 69.08 | 0 | 5657.0732 | 5657.0732 | -5657.0732 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6914.2006 | 6914.2006 | 0 | 8.5 | 0 | 1152.3668 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6775.9166 | 1355.1833 | 13.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 10:00 | 8 | 6 | 10 | 218 | 5218 | 71.06 | 0 | 7962.5068 | 7962.5068 | -7962.5068 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9731.9528 | 9731.9528 | 0 | 8.5 | 0 | 1621.9921 | 32.44% | 1 | 64.88% | 0% | 0% | 0% | 30.1296 | 0 | 0 | 0 | 30.1296 | 0 | 9537.3137 | 1907.4627 | 19.07% | 1 | 38.15% | 0% | 0% | 4.4415 | 0 | 0 | 4.4415 | 34.5711
2007-08-06 11:00 | 8 | 6 | 11 | 218 | 5219 | 71.06 | 0 | 9850.2341 | 9850.2341 | -9850.2341 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12039.175 | 12039.175 | 0 | 8.5 | 0 | 2006.5292 | 40.13% | 1 | 80.26% | 0% | 0% | 0% | 49.148 | 0 | 0 | 0 | 49.148 | 0 | 11798.3915 | 2359.6783 | 23.6% | 1 | 47.19% | 0% | 0% | 7.2451 | 0 | 0 | 7.2451 | 56.3931
2007-08-06 12:00 | 8 | 6 | 12 | 218 | 5220 | 75.92 | 0 | 11153.4025 | 11153.4025 | -11153.4025 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13631.9364 | 13631.9364 | 0 | 8.5 | 0 | 2271.9894 | 45.44% | 1 | 90.88% | 0% | 0% | 0% | 65.4057 | 0 | 0 | 0 | 65.4057 | 0 | 13359.2977 | 2671.8595 | 26.72% | 1 | 53.44% | 0% | 0% | 9.6417 | 0 | 0 | 9.6417 | 75.0474
2007-08-06 13:00 | 8 | 6 | 13 | 218 | 5221 | 75.02 | 0 | 11890.7512 | 11890.7512 | -11890.7512 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14533.1403 | 14533.1403 | 0 | 8.5 | 0 | 2422.1901 | 48.44% | 1 | 96.89% | 0% | 0% | 0% | 75.7809 | 0 | 0 | 0 | 75.7809 | 0 | 14242.4775 | 2848.4955 | 28.48% | 1 | 56.97% | 0% | 0% | 11.1711 | 0 | 0 | 11.1711 | 86.9521
2007-08-06 14:00 | 8 | 6 | 14 | 218 | 5222 | 75.02 | 0 | 11802.5082 | 11802.5082 | -11802.5082 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14425.2878 | 14425.2878 | 0 | 8.5 | 0 | 2404.2146 | 48.08% | 1 | 96.17% | 0% | 0% | 0% | 74.4937 | 0 | 0 | 0 | 74.4937 | 0 | 14136.782 | 2827.3564 | 28.27% | 1 | 56.55% | 0% | 0% | 10.9814 | 0 | 0 | 10.9814 | 85.4751
2007-08-06 15:00 | 8 | 6 | 15 | 218 | 5223 | 75.02 | 0 | 11138.1481 | 11138.1481 | -11138.1481 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13613.2921 | 13613.2921 | 0 | 8.5 | 0 | 2268.882 | 45.38% | 1 | 90.76% | 0% | 0% | 0% | 65.2001 | 0 | 0 | 0 | 65.2001 | 0 | 13341.0263 | 2668.2053 | 26.68% | 1 | 53.36% | 0% | 0% | 9.6114 | 0 | 0 | 9.6114 | 74.8115
2007-08-06 16:00 | 8 | 6 | 16 | 218 | 5224 | 75.92 | 0 | 10626.6037 | 10626.6037 | -10626.6037 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12988.0712 | 12988.0712 | 0 | 8.5 | 0 | 2164.6785 | 43.29% | 1 | 86.59% | 0% | 0% | 0% | 58.5175 | 0 | 0 | 0 | 58.5175 | 0 | 12728.3097 | 2545.6619 | 25.46% | 1 | 50.91% | 0% | 0% | 8.6263 | 0 | 0 | 8.6263 | 67.1438
2007-08-06 17:00 | 8 | 6 | 17 | 218 | 5225 | 75.92 | 0 | 9975.5511 | 9975.5511 | -9975.5511 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12192.3402 | 12192.3402 | 0 | 8.5 | 0 | 2032.0567 | 40.64% | 1 | 81.28% | 0% | 0% | 0% | 50.598 | 0 | 0 | 0 | 50.598 | 0 | 11948.4934 | 2389.6987 | 23.9% | 1 | 47.79% | 0% | 0% | 7.4588 | 0 | 0 | 7.4588 | 58.0568
2007-08-06 18:00 | 8 | 6 | 18 | 218 | 5226 | 71.96 | 0 | 6464.7804 | 6464.7804 | -6464.7804 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7901.3982 | 7901.3982 | 0 | 8.5 | 0 | 1316.8997 | 30% | 1 | 52.68% | 0% | 0% | 0% | 18.6574 | 0 | 0 | 0 | 18.6574 | 0 | 7743.3703 | 1548.6741 | 15.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.932
2007-08-06 19:00 | 8 | 6 | 19 | 218 | 5227 | 69.08 | 0 | 5462.5301 | 5462.5301 | -5462.5301 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6676.4257 | 6676.4257 | 0 | 8.5 | 0 | 1112.7376 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6542.8972 | 1308.5794 | 13.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 20:00 | 8 | 6 | 20 | 218 | 5228 | 69.08 | 0 | 4217.8573 | 4217.8573 | -4217.8573 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5155.159 | 5155.159 | 0 | 8.5 | 0 | 859.1932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5052.0558 | 1010.4112 | 10.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 21:00 | 8 | 6 | 21 | 218 | 5229 | 66.02 | 0 | 2113.5723 | 2113.5723 | -2113.5723 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2583.2551 | 2583.2551 | 0 | 8.5 | 0 | 430.5425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2531.59 | 506.318 | 5.063% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 22:00 | 8 | 6 | 22 | 218 | 5230 | 62.06 | 0 | 579.8942 | 579.8942 | -579.8942 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 708.7596 | 708.7596 | 0 | 8.5 | 0 | 118.1266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 694.5844 | 138.9169 | 1.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-06 23:00 | 8 | 6 | 23 | 218 | 5231 | 62.06 | 0 | 408.5683 | 408.5683 | -408.5683 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 499.3613 | 499.3613 | 0 | 8.5 | 0 | 83.2269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 489.3741 | 97.8748 | 0.9787% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 | 8 | 7 | 0 | 219 | 5232 | 60.98 | 0 | 227.2224 | 227.2224 | -227.2224 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 277.7162 | 277.7162 | 0 | 8.5 | 0 | 46.286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 272.1619 | 54.4324 | 0.5443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 01:00 | 8 | 7 | 1 | 219 | 5233 | 60.98 | 0 | 124.8543 | 124.8543 | -124.8543 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 152.5997 | 152.5997 | 0 | 8.5 | 0 | 25.4333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 149.5477 | 29.9095 | 0.2991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 02:00 | 8 | 7 | 2 | 219 | 5234 | 60.98 | 0 | 61.0103 | 61.0103 | -61.0103 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 74.5681 | 74.5681 | 0 | 8.5 | 0 | 12.428 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 73.0767 | 14.6153 | 0.1462% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 03:00 | 8 | 7 | 3 | 219 | 5235 | 57.92 | 0 | 30.9873 | 30.9873 | -30.9873 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 37.8734 | 37.8734 | 0 | 8.5 | 0 | 6.3122 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 37.1159 | 7.4232 | 0.07423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 04:00 | 8 | 7 | 4 | 219 | 5236 | 57.92 | 0 | 16.5543 | 16.5543 | -16.5543 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 20.2331 | 20.2331 | 0 | 8.5 | 0 | 3.3722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 19.8284 | 3.9657 | 0.03966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 05:00 | 8 | 7 | 5 | 219 | 5237 | 57.92 | 0 | 7.3339 | 7.3339 | -7.3339 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8.9636 | 8.9636 | 0 | 8.5 | 0 | 1.4939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 8.7843 | 1.7569 | 0.01757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 06:00 | 8 | 7 | 6 | 219 | 5238 | 59 | 508.6221 | 690.1378 | 690.1378 | -181.5157 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 843.5018 | 843.5018 | 0 | 8.5 | 0 | 140.5836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 826.6318 | 165.3264 | 1.653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 07:00 | 8 | 7 | 7 | 219 | 5239 | 62.96 | 19.1177 | 1535.4514 | 1535.4514 | -1516.3337 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1876.6629 | 1876.6629 | 0 | 8.5 | 0 | 312.7771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1839.1296 | 367.8259 | 3.678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 08:00 | 8 | 7 | 8 | 219 | 5240 | 62.96 | 0 | 4388.9473 | 4388.9473 | -4388.9473 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5364.2689 | 5364.2689 | 0 | 8.5 | 0 | 894.0448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5256.9836 | 1051.3967 | 10.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 09:00 | 8 | 7 | 9 | 219 | 5241 | 68 | 0 | 5752.5528 | 5752.5528 | -5752.5528 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7030.8978 | 7030.8978 | 0 | 8.5 | 0 | 1171.8163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6890.2799 | 1378.056 | 13.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 10:00 | 8 | 7 | 10 | 219 | 5242 | 71.06 | 0 | 7942.1515 | 7942.1515 | -7942.1515 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9707.0741 | 9707.0741 | 0 | 8.5 | 0 | 1617.8457 | 32.36% | 1 | 64.71% | 0% | 0% | 0% | 29.9527 | 0 | 0 | 0 | 29.9527 | 0 | 9512.9326 | 1902.5865 | 19.03% | 1 | 38.05% | 0% | 0% | 4.4154 | 0 | 0 | 4.4154 | 34.3682
2007-08-07 11:00 | 8 | 7 | 11 | 219 | 5243 | 71.06 | 0 | 9892.9492 | 9892.9492 | -9892.9492 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12091.3823 | 12091.3823 | 0 | 8.5 | 0 | 2015.2304 | 40.3% | 1 | 80.61% | 0% | 0% | 0% | 49.6396 | 0 | 0 | 0 | 49.6396 | 0 | 11849.5547 | 2369.9109 | 23.7% | 1 | 47.4% | 0% | 0% | 7.3176 | 0 | 0 | 7.3176 | 56.9571
2007-08-07 12:00 | 8 | 7 | 12 | 219 | 5244 | 71.96 | 0 | 11011.9865 | 11011.9865 | -11011.9865 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13459.0946 | 13459.0946 | 0 | 8.5 | 0 | 2243.1824 | 44.86% | 1 | 89.73% | 0% | 0% | 0% | 63.514 | 0 | 0 | 0 | 63.514 | 0 | 13189.9127 | 2637.9825 | 26.38% | 1 | 52.76% | 0% | 0% | 9.3628 | 0 | 0 | 9.3628 | 72.8769
2007-08-07 13:00 | 8 | 7 | 13 | 219 | 5245 | 75.02 | 0 | 11466.6578 | 11466.6578 | -11466.6578 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14014.8039 | 14014.8039 | 0 | 8.5 | 0 | 2335.8007 | 46.72% | 1 | 93.43% | 0% | 0% | 0% | 69.7081 | 0 | 0 | 0 | 69.7081 | 0 | 13734.5079 | 2746.9016 | 27.47% | 1 | 54.94% | 0% | 0% | 10.2759 | 0 | 0 | 10.2759 | 79.984
2007-08-07 14:00 | 8 | 7 | 14 | 219 | 5246 | 75.02 | 0 | 11693.5635 | 11693.5635 | -11693.5635 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14292.1331 | 14292.1331 | 0 | 8.5 | 0 | 2382.0222 | 47.64% | 1 | 95.28% | 0% | 0% | 0% | 72.9216 | 0 | 0 | 0 | 72.9216 | 0 | 14006.2904 | 2801.2581 | 28.01% | 1 | 56.03% | 0% | 0% | 10.7496 | 0 | 0 | 10.7496 | 83.6713
2007-08-07 15:00 | 8 | 7 | 15 | 219 | 5247 | 75.02 | 0 | 11666.5414 | 11666.5414 | -11666.5414 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14259.1061 | 14259.1061 | 0 | 8.5 | 0 | 2376.5177 | 47.53% | 1 | 95.06% | 0% | 0% | 0% | 72.5346 | 0 | 0 | 0 | 72.5346 | 0 | 13973.924 | 2794.7848 | 27.95% | 1 | 55.9% | 0% | 0% | 10.6926 | 0 | 0 | 10.6926 | 83.2272
2007-08-07 16:00 | 8 | 7 | 16 | 219 | 5248 | 73.94 | 0 | 11523.671 | 11523.671 | -11523.671 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14084.4868 | 14084.4868 | 0 | 8.5 | 0 | 2347.4145 | 46.95% | 1 | 93.9% | 0% | 0% | 0% | 70.5079 | 0 | 0 | 0 | 70.5079 | 0 | 13802.7971 | 2760.5594 | 27.61% | 1 | 55.21% | 0% | 0% | 10.3938 | 0 | 0 | 10.3938 | 80.9017
2007-08-07 17:00 | 8 | 7 | 17 | 219 | 5249 | 73.94 | 0 | 11443.8936 | 11443.8936 | -11443.8936 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13986.9811 | 13986.9811 | 0 | 8.5 | 0 | 2331.1635 | 46.62% | 1 | 93.25% | 0% | 0% | 0% | 69.3902 | 0 | 0 | 0 | 69.3902 | 0 | 13707.2415 | 2741.4483 | 27.41% | 1 | 54.83% | 0% | 0% | 10.2291 | 0 | 0 | 10.2291 | 79.6193
2007-08-07 18:00 | 8 | 7 | 18 | 219 | 5250 | 71.06 | 0 | 6748.6496 | 6748.6496 | -6748.6496 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8248.3495 | 8248.3495 | 0 | 8.5 | 0 | 1374.7249 | 30% | 1 | 54.99% | 0% | 0% | 0% | 20.5957 | 0 | 0 | 0 | 20.5957 | 0 | 8083.3825 | 1616.6765 | 16.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.8703
2007-08-07 19:00 | 8 | 7 | 19 | 219 | 5251 | 69.08 | 0 | 5399.497 | 5399.497 | -5399.497 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6599.3852 | 6599.3852 | 0 | 8.5 | 0 | 1099.8975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6467.3975 | 1293.4795 | 12.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 20:00 | 8 | 7 | 20 | 219 | 5252 | 69.08 | 0 | 4980.8806 | 4980.8806 | -4980.8806 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6087.743 | 6087.743 | 0 | 8.5 | 0 | 1014.6238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5965.9882 | 1193.1976 | 11.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 21:00 | 8 | 7 | 21 | 219 | 5253 | 64.04 | 0 | 2558.7415 | 2558.7415 | -2558.7415 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3127.3507 | 3127.3507 | 0 | 8.5 | 0 | 521.2251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3064.8037 | 612.9607 | 6.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 22:00 | 8 | 7 | 22 | 219 | 5254 | 62.06 | 0 | 808.7022 | 808.7022 | -808.7022 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 988.4138 | 988.4138 | 0 | 8.5 | 0 | 164.7356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 968.6455 | 193.7291 | 1.937% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-07 23:00 | 8 | 7 | 23 | 219 | 5255 | 62.06 | 0 | 527.9048 | 527.9048 | -527.9048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 645.217 | 645.217 | 0 | 8.5 | 0 | 107.5362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 632.3127 | 126.4625 | 1.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 | 8 | 8 | 0 | 220 | 5256 | 55.94 | 0 | 263.8264 | 263.8264 | -263.8264 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 322.4545 | 322.4545 | 0 | 8.5 | 0 | 53.7424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 316.0054 | 63.2011 | 0.632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 01:00 | 8 | 8 | 1 | 220 | 5257 | 55.94 | 0 | 160.1572 | 160.1572 | -160.1572 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 195.7477 | 195.7477 | 0 | 8.5 | 0 | 32.6246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 191.8327 | 38.3665 | 0.3837% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 02:00 | 8 | 8 | 2 | 220 | 5258 | 55.94 | 0 | 104.7286 | 104.7286 | -104.7286 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 128.0017 | 128.0017 | 0 | 8.5 | 0 | 21.3336 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 125.4416 | 25.0883 | 0.2509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 03:00 | 8 | 8 | 3 | 220 | 5259 | 53.96 | 0 | 73.2057 | 73.2057 | -73.2057 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 89.4737 | 89.4737 | 0 | 8.5 | 0 | 14.9123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 87.6842 | 17.5368 | 0.1754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 04:00 | 8 | 8 | 4 | 220 | 5260 | 51.08 | 0 | 60.3623 | 60.3623 | -60.3623 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 73.7762 | 73.7762 | 0 | 8.5 | 0 | 12.296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 72.3007 | 14.4601 | 0.1446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 05:00 | 8 | 8 | 5 | 220 | 5261 | 51.08 | 0 | 59.5646 | 59.5646 | -59.5646 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 72.8012 | 72.8012 | 0 | 8.5 | 0 | 12.1335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 71.3452 | 14.269 | 0.1427% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 06:00 | 8 | 8 | 6 | 220 | 5262 | 51.08 | 353.042 | 1169.4292 | 1169.4292 | -816.3871 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1429.3023 | 1429.3023 | 0 | 8.5 | 0 | 238.2171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1400.7163 | 280.1433 | 2.801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 07:00 | 8 | 8 | 7 | 220 | 5263 | 57.02 | 26.4255 | 1248.989 | 1248.989 | -1222.5636 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1526.5422 | 1526.5422 | 0 | 8.5 | 0 | 254.4237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1496.0113 | 299.2023 | 2.992% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 08:00 | 8 | 8 | 8 | 220 | 5264 | 57.02 | 0 | 4621.8845 | 4621.8845 | -4621.8845 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5648.97 | 5648.97 | 0 | 8.5 | 0 | 941.495 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5535.9906 | 1107.1981 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 09:00 | 8 | 8 | 9 | 220 | 5265 | 64.04 | 0 | 6048.4205 | 6048.4205 | -6048.4205 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7392.514 | 7392.514 | 0 | 8.5 | 0 | 1232.0857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7244.6637 | 1448.9327 | 14.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 10:00 | 8 | 8 | 10 | 220 | 5266 | 66.02 | 0 | 8459.4181 | 8459.4181 | -8459.4181 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10339.2888 | 10339.2888 | 0 | 8.5 | 0 | 1723.2148 | 34.46% | 1 | 68.93% | 0% | 0% | 0% | 34.6307 | 0 | 0 | 0 | 34.6307 | 0 | 10132.503 | 2026.5006 | 20.27% | 1 | 40.53% | 0% | 0% | 5.105 | 0 | 0 | 5.105 | 39.7358
2007-08-08 11:00 | 8 | 8 | 11 | 220 | 5267 | 66.02 | 0 | 10029.9771 | 10029.9771 | -10029.9771 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12258.8609 | 12258.8609 | 0 | 8.5 | 0 | 2043.1435 | 40.86% | 1 | 81.73% | 0% | 0% | 0% | 51.2352 | 0 | 0 | 0 | 51.2352 | 0 | 12013.6836 | 2402.7367 | 24.03% | 1 | 48.05% | 0% | 0% | 7.5528 | 0 | 0 | 7.5528 | 58.788
2007-08-08 12:00 | 8 | 8 | 12 | 220 | 5268 | 71.06 | 0 | 11142.5296 | 11142.5296 | -11142.5296 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13618.6473 | 13618.6473 | 0 | 8.5 | 0 | 2269.7745 | 45.4% | 1 | 90.79% | 0% | 0% | 0% | 65.2591 | 0 | 0 | 0 | 65.2591 | 0 | 13346.2743 | 2669.2549 | 26.69% | 1 | 53.39% | 0% | 0% | 9.6201 | 0 | 0 | 9.6201 | 74.8792
2007-08-08 13:00 | 8 | 8 | 13 | 220 | 5269 | 73.04 | 0 | 12555.9055 | 12555.9055 | -12555.9055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15346.1067 | 15346.1067 | 0 | 8.5 | 0 | 2557.6845 | 51.15% | 2 | 51.15% | 51.15% | 0% | 0% | 17.4405 | 17.4405 | 0 | 0 | 34.8811 | 0 | 15039.1846 | 3007.8369 | 30.08% | 1 | 60.16% | 0% | 0% | 12.661 | 0 | 0 | 12.661 | 47.5421
2007-08-08 14:00 | 8 | 8 | 14 | 220 | 5270 | 73.04 | 0 | 13883.421 | 13883.421 | -13883.421 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16968.6257 | 16968.6257 | 0 | 8.5 | 0 | 2828.1043 | 56.56% | 2 | 56.56% | 56.56% | 0% | 0% | 21.9761 | 21.9761 | 0 | 0 | 43.9523 | 0 | 16629.2532 | 3325.8506 | 33.26% | 1 | 33.26% | 33.26% | 0% | 3.2396 | 3.2396 | 0 | 6.4792 | 50.4315
2007-08-08 15:00 | 8 | 8 | 15 | 220 | 5271 | 73.94 | 0 | 14346.3807 | 14346.3807 | -14346.3807 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17534.4653 | 17534.4653 | 0 | 8.5 | 0 | 2922.4109 | 58.45% | 2 | 58.45% | 58.45% | 0% | 0% | 23.6983 | 23.6983 | 0 | 0 | 47.3966 | 0 | 17183.776 | 3436.7552 | 34.37% | 1 | 34.37% | 34.37% | 0% | 3.4935 | 3.4935 | 0 | 6.9869 | 54.3835
2007-08-08 16:00 | 8 | 8 | 16 | 220 | 5272 | 73.04 | 0 | 13982.4171 | 13982.4171 | -13982.4171 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17089.621 | 17089.621 | 0 | 8.5 | 0 | 2848.2702 | 56.97% | 2 | 56.97% | 56.97% | 0% | 0% | 22.3382 | 22.3382 | 0 | 0 | 44.6765 | 0 | 16747.8285 | 3349.5657 | 33.5% | 1 | 33.5% | 33.5% | 0% | 3.293 | 3.293 | 0 | 6.5859 | 51.2624
2007-08-08 17:00 | 8 | 8 | 17 | 220 | 5273 | 73.04 | 0 | 13434.0299 | 13434.0299 | -13434.0299 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16419.3698 | 16419.3698 | 0 | 8.5 | 0 | 2736.5616 | 54.73% | 2 | 54.73% | 54.73% | 0% | 0% | 20.3744 | 20.3744 | 0 | 0 | 40.7487 | 0 | 16090.9824 | 3218.1965 | 32.18% | 1 | 64.36% | 0% | 0% | 14.7908 | 0 | 0 | 14.7908 | 55.5395
2007-08-08 18:00 | 8 | 8 | 18 | 220 | 5274 | 71.06 | 0 | 9115.8568 | 9115.8568 | -9115.8568 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11141.6028 | 11141.6028 | 0 | 8.5 | 0 | 1856.9338 | 37.14% | 1 | 74.28% | 0% | 0% | 0% | 41.1257 | 0 | 0 | 0 | 41.1257 | 0 | 10918.7707 | 2183.7541 | 21.84% | 1 | 43.68% | 0% | 0% | 6.0625 | 0 | 0 | 6.0625 | 47.1881
2007-08-08 19:00 | 8 | 8 | 19 | 220 | 5275 | 69.08 | 0 | 7675.9643 | 7675.9643 | -7675.9643 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9381.7342 | 9381.7342 | 0 | 8.5 | 0 | 1563.6224 | 31.27% | 1 | 62.54% | 0% | 0% | 0% | 27.6939 | 0 | 0 | 0 | 27.6939 | 0 | 9194.0995 | 1838.8199 | 18.39% | 1 | 36.78% | 0% | 0% | 4.0825 | 0 | 0 | 4.0825 | 31.7764
2007-08-08 20:00 | 8 | 8 | 20 | 220 | 5276 | 69.08 | 0 | 5450.8515 | 5450.8515 | -5450.8515 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6662.1518 | 6662.1518 | 0 | 8.5 | 0 | 1110.3586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6528.9087 | 1305.7817 | 13.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 21:00 | 8 | 8 | 21 | 220 | 5277 | 66.02 | 0 | 2640.4532 | 2640.4532 | -2640.4532 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3227.2205 | 3227.2205 | 0 | 8.5 | 0 | 537.8701 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3162.6761 | 632.5352 | 6.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 22:00 | 8 | 8 | 22 | 220 | 5278 | 62.06 | 0 | 636.298 | 636.298 | -636.298 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 777.6975 | 777.6975 | 0 | 8.5 | 0 | 129.6163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 762.1436 | 152.4287 | 1.524% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-08 23:00 | 8 | 8 | 23 | 220 | 5279 | 62.06 | 0 | 296.9461 | 296.9461 | -296.9461 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 362.9341 | 362.9341 | 0 | 8.5 | 0 | 60.489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 355.6755 | 71.1351 | 0.7114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 | 8 | 9 | 0 | 221 | 5280 | 60.08 | 0 | 95.5718 | 95.5718 | -95.5718 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 116.81 | 116.81 | 0 | 8.5 | 0 | 19.4683 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 114.4738 | 22.8948 | 0.2289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 01:00 | 8 | 9 | 1 | 221 | 5281 | 60.98 | 0.46597 | 12.1937 | 12.1937 | -11.7278 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14.9034 | 14.9034 | 0 | 8.5 | 0 | 2.4839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 14.6054 | 2.9211 | 0.02921% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 02:00 | 8 | 9 | 2 | 221 | 5282 | 60.98 | 6.474 | 0 | 0 | 6.474 | Heating | 5.7123 | 8.5 | 5.7123 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.8289 | 0 | 1.1658 | 0.01166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 03:00 | 8 | 9 | 3 | 221 | 5283 | 62.06 | 11.4849 | 0 | 0 | 11.4849 | Heating | 10.1338 | 8.5 | 10.1338 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.3406 | 0 | 2.0681 | 0.02068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 04:00 | 8 | 9 | 4 | 221 | 5284 | 62.06 | 19.4221 | 0 | 0 | 19.4221 | Heating | 17.1371 | 8.5 | 17.1371 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.4274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.4869 | 0 | 3.4974 | 0.03497% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 05:00 | 8 | 9 | 5 | 221 | 5285 | 62.06 | 21.5549 | 0 | 0 | 21.5549 | Heating | 19.019 | 8.5 | 19.019 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.8038 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 19.4072 | 0 | 3.8814 | 0.03881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 06:00 | 8 | 9 | 6 | 221 | 5286 | 62.96 | 1533.1177 | 330.6184 | 330.6184 | 1202.4992 | Heating | 1061.0287 | 8.5 | 1061.0287 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.2057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1082.6824 | 0 | 216.5365 | 2.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 07:00 | 8 | 9 | 7 | 221 | 5287 | 64.04 | 696.1191 | 629.7435 | 629.7435 | 66.3756 | Heating | 58.5667 | 8.5 | 58.5667 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.7133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 59.762 | 0 | 11.9524 | 0.1195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 08:00 | 8 | 9 | 8 | 221 | 5288 | 64.04 | 3.3662 | 3650.0625 | 3650.0625 | -3646.6963 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4461.1875 | 4461.1875 | 0 | 8.5 | 0 | 743.5312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4371.9637 | 874.3927 | 8.744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 09:00 | 8 | 9 | 9 | 221 | 5289 | 66.92 | 0 | 5211.2602 | 5211.2602 | -5211.2602 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6369.318 | 6369.318 | 0 | 8.5 | 0 | 1061.553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6241.9317 | 1248.3863 | 12.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 10:00 | 8 | 9 | 10 | 221 | 5290 | 68 | 0 | 7656.0024 | 7656.0024 | -7656.0024 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9357.3363 | 9357.3363 | 0 | 8.5 | 0 | 1559.5561 | 31.19% | 1 | 62.38% | 0% | 0% | 0% | 27.5285 | 0 | 0 | 0 | 27.5285 | 0 | 9170.1896 | 1834.0379 | 18.34% | 1 | 36.68% | 0% | 0% | 4.0581 | 0 | 0 | 4.0581 | 31.5866
2007-08-09 11:00 | 8 | 9 | 11 | 221 | 5291 | 68 | 0 | 10222.2039 | 10222.2039 | -10222.2039 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12493.8048 | 12493.8048 | 0 | 8.5 | 0 | 2082.3008 | 41.65% | 1 | 83.29% | 0% | 0% | 0% | 53.5218 | 0 | 0 | 0 | 53.5218 | 0 | 12243.9287 | 2448.7857 | 24.49% | 1 | 48.98% | 0% | 0% | 7.8899 | 0 | 0 | 7.8899 | 61.4117
2007-08-09 12:00 | 8 | 9 | 12 | 221 | 5292 | 66.2 | 0 | 11611.4207 | 11611.4207 | -11611.4207 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14191.7364 | 14191.7364 | 0 | 8.5 | 0 | 2365.2894 | 47.31% | 1 | 94.61% | 0% | 0% | 0% | 71.7488 | 0 | 0 | 0 | 71.7488 | 0 | 13907.9017 | 2781.5803 | 27.82% | 1 | 55.63% | 0% | 0% | 10.5768 | 0 | 0 | 10.5768 | 82.3256
2007-08-09 13:00 | 8 | 9 | 13 | 221 | 5293 | 69.98 | 0 | 12502.1173 | 12502.1173 | -12502.1173 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15280.3656 | 15280.3656 | 0 | 8.5 | 0 | 2546.7276 | 50.93% | 2 | 50.93% | 50.93% | 0% | 0% | 17.2692 | 17.2692 | 0 | 0 | 34.5384 | 0 | 14974.7583 | 2994.9517 | 29.95% | 1 | 59.9% | 0% | 0% | 12.5366 | 0 | 0 | 12.5366 | 47.0749
2007-08-09 14:00 | 8 | 9 | 14 | 221 | 5294 | 69.98 | 0 | 13224.3374 | 13224.3374 | -13224.3374 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16163.0791 | 16163.0791 | 0 | 8.5 | 0 | 2693.8465 | 53.88% | 2 | 53.88% | 53.88% | 0% | 0% | 19.6503 | 19.6503 | 0 | 0 | 39.3006 | 0 | 15839.8175 | 3167.9635 | 31.68% | 1 | 63.36% | 0% | 0% | 14.2652 | 0 | 0 | 14.2652 | 53.5658
2007-08-09 15:00 | 8 | 9 | 15 | 221 | 5295 | 71.6 | 0 | 13088.5597 | 13088.5597 | -13088.5597 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15997.1285 | 15997.1285 | 0 | 8.5 | 0 | 2666.1881 | 53.32% | 2 | 53.32% | 53.32% | 0% | 0% | 19.1894 | 19.1894 | 0 | 0 | 38.3788 | 0 | 15677.1859 | 3135.4372 | 31.35% | 1 | 62.71% | 0% | 0% | 13.9305 | 0 | 0 | 13.9305 | 52.3093
2007-08-09 16:00 | 8 | 9 | 16 | 221 | 5296 | 71.6 | 0 | 12530.8518 | 12530.8518 | -12530.8518 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15315.4855 | 15315.4855 | 0 | 8.5 | 0 | 2552.5809 | 51.05% | 2 | 51.05% | 51.05% | 0% | 0% | 17.3606 | 17.3606 | 0 | 0 | 34.7212 | 0 | 15009.1758 | 3001.8352 | 30.02% | 1 | 60.04% | 0% | 0% | 12.6029 | 0 | 0 | 12.6029 | 47.3242
2007-08-09 17:00 | 8 | 9 | 17 | 221 | 5297 | 71.06 | 0 | 12000.0543 | 12000.0543 | -12000.0543 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14666.7331 | 14666.7331 | 0 | 8.5 | 0 | 2444.4555 | 48.89% | 1 | 97.78% | 0% | 0% | 0% | 77.3927 | 0 | 0 | 0 | 77.3927 | 0 | 14373.3984 | 2874.6797 | 28.75% | 1 | 57.49% | 0% | 0% | 11.4087 | 0 | 0 | 11.4087 | 88.8014
2007-08-09 18:00 | 8 | 9 | 18 | 221 | 5298 | 71.6 | 0 | 8045.5139 | 8045.5139 | -8045.5139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9833.4058 | 9833.4058 | 0 | 8.5 | 0 | 1638.901 | 32.78% | 1 | 65.56% | 0% | 0% | 0% | 30.8569 | 0 | 0 | 0 | 30.8569 | 0 | 9636.7377 | 1927.3475 | 19.27% | 1 | 38.55% | 0% | 0% | 4.5487 | 0 | 0 | 4.5487 | 35.4056
2007-08-09 19:00 | 8 | 9 | 19 | 221 | 5299 | 71.6 | 0 | 6891.1877 | 6891.1877 | -6891.1877 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8422.5628 | 8422.5628 | 0 | 8.5 | 0 | 1403.7605 | 30% | 1 | 56.15% | 0% | 0% | 0% | 21.61 | 0 | 0 | 0 | 21.61 | 0 | 8254.1115 | 1650.8223 | 16.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.8846
2007-08-09 20:00 | 8 | 9 | 20 | 221 | 5300 | 69.98 | 0 | 4878.9052 | 4878.9052 | -4878.9052 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5963.1063 | 5963.1063 | 0 | 8.5 | 0 | 993.8511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5843.8442 | 1168.7688 | 11.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 21:00 | 8 | 9 | 21 | 221 | 5301 | 69.98 | 0 | 2053.4579 | 2053.4579 | -2053.4579 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2509.7818 | 2509.7818 | 0 | 8.5 | 0 | 418.297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2459.5862 | 491.9172 | 4.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 22:00 | 8 | 9 | 22 | 221 | 5302 | 69.98 | 0 | 625.0974 | 625.0974 | -625.0974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 764.0079 | 764.0079 | 0 | 8.5 | 0 | 127.3346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 748.7277 | 149.7455 | 1.497% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-09 23:00 | 8 | 9 | 23 | 221 | 5303 | 69.98 | 0 | 349.9482 | 349.9482 | -349.9482 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 427.7144 | 427.7144 | 0 | 8.5 | 0 | 71.2857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 419.1601 | 83.832 | 0.8383% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 | 8 | 10 | 0 | 222 | 5304 | 69.98 | 0 | 114.3002 | 114.3002 | -114.3002 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 139.7003 | 139.7003 | 0 | 8.5 | 0 | 23.2834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 136.9063 | 27.3813 | 0.2738% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 01:00 | 8 | 10 | 1 | 222 | 5305 | 69.98 | 0 | 33.2258 | 33.2258 | -33.2258 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 40.6093 | 40.6093 | 0 | 8.5 | 0 | 6.7682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 39.7971 | 7.9594 | 0.07959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 02:00 | 8 | 10 | 2 | 222 | 5306 | 69.98 | 0.93061 | 3.2578 | 3.2578 | -2.3272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3.9817 | 3.9817 | 0 | 8.5 | 0 | 0.66362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3.9021 | 0.78042 | 0.007804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 03:00 | 8 | 10 | 3 | 222 | 5307 | 69.8 | 3.52 | 0 | 0 | 3.52 | Heating | 3.1059 | 8.5 | 3.1059 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.62118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.1693 | 0 | 0.63386 | 0.006339% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 04:00 | 8 | 10 | 4 | 222 | 5308 | 69.8 | 8.0574 | 0 | 0 | 8.0574 | Heating | 7.1094 | 8.5 | 7.1094 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.2545 | 0 | 1.4509 | 0.01451% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 05:00 | 8 | 10 | 5 | 222 | 5309 | 69.08 | 14.5326 | 0 | 0 | 14.5326 | Heating | 12.8229 | 8.5 | 12.8229 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.0846 | 0 | 2.6169 | 0.02617% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 06:00 | 8 | 10 | 6 | 222 | 5310 | 69.8 | 1331.7378 | 263.5509 | 263.5509 | 1068.1869 | Heating | 942.5178 | 8.5 | 942.5178 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.5036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 961.7529 | 0 | 192.3506 | 1.924% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 07:00 | 8 | 10 | 7 | 222 | 5311 | 69.8 | 696.1851 | 232.8263 | 232.8263 | 463.3588 | Heating | 408.846 | 8.5 | 408.846 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.7692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 417.1898 | 0 | 83.438 | 0.8344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 08:00 | 8 | 10 | 8 | 222 | 5312 | 69.08 | 33.5888 | 1108.903 | 1108.903 | -1075.3142 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1355.3259 | 1355.3259 | 0 | 8.5 | 0 | 225.8877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1328.2194 | 265.6439 | 2.656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 09:00 | 8 | 10 | 9 | 222 | 5313 | 73.4 | 0 | 1974.8116 | 1974.8116 | -1974.8116 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2413.6586 | 2413.6586 | 0 | 8.5 | 0 | 402.2764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2365.3855 | 473.0771 | 4.731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 10:00 | 8 | 10 | 10 | 222 | 5314 | 73.4 | 0 | 4827.9838 | 4827.9838 | -4827.9838 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5900.8691 | 5900.8691 | 0 | 8.5 | 0 | 983.4782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5782.8518 | 1156.5704 | 11.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 11:00 | 8 | 10 | 11 | 222 | 5315 | 75.02 | 0 | 6833.762 | 6833.762 | -6833.762 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8352.3758 | 8352.3758 | 0 | 8.5 | 0 | 1392.0626 | 30% | 1 | 55.68% | 0% | 0% | 0% | 21.1981 | 0 | 0 | 0 | 21.1981 | 0 | 8185.3283 | 1637.0657 | 16.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.4726
2007-08-10 12:00 | 8 | 10 | 12 | 222 | 5316 | 78.8 | 0 | 8530.7635 | 8530.7635 | -8530.7635 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10426.4887 | 10426.4887 | 0 | 8.5 | 0 | 1737.7481 | 34.75% | 1 | 69.51% | 0% | 0% | 0% | 35.3062 | 0 | 0 | 0 | 35.3062 | 0 | 10217.9589 | 2043.5918 | 20.44% | 1 | 40.87% | 0% | 0% | 5.2046 | 0 | 0 | 5.2046 | 40.5108
2007-08-10 13:00 | 8 | 10 | 13 | 222 | 5317 | 82.4 | 0 | 9109.4466 | 9109.4466 | -9109.4466 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11133.768 | 11133.768 | 0 | 8.5 | 0 | 1855.628 | 37.11% | 1 | 74.23% | 0% | 0% | 0% | 41.0592 | 0 | 0 | 0 | 41.0592 | 0 | 10911.0927 | 2182.2185 | 21.82% | 1 | 43.64% | 0% | 0% | 6.0527 | 0 | 0 | 6.0527 | 47.1119
2007-08-10 14:00 | 8 | 10 | 14 | 222 | 5318 | 84.02 | 0 | 8825.0541 | 8825.0541 | -8825.0541 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10786.1772 | 10786.1772 | 0 | 8.5 | 0 | 1797.6962 | 35.95% | 1 | 71.91% | 0% | 0% | 0% | 38.1706 | 0 | 0 | 0 | 38.1706 | 0 | 10570.4537 | 2114.0907 | 21.14% | 1 | 42.28% | 0% | 0% | 5.6269 | 0 | 0 | 5.6269 | 43.7974
2007-08-10 15:00 | 8 | 10 | 15 | 222 | 5319 | 84.92 | 0 | 8371.8511 | 8371.8511 | -8371.8511 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10232.2625 | 10232.2625 | 0 | 8.5 | 0 | 1705.3771 | 34.11% | 1 | 68.22% | 0% | 0% | 0% | 33.8118 | 0 | 0 | 0 | 33.8118 | 0 | 10027.6172 | 2005.5234 | 20.06% | 1 | 40.11% | 0% | 0% | 4.9843 | 0 | 0 | 4.9843 | 38.7961
2007-08-10 16:00 | 8 | 10 | 16 | 222 | 5320 | 84.92 | 0 | 8275.0799 | 8275.0799 | -8275.0799 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10113.9866 | 10113.9866 | 0 | 8.5 | 0 | 1685.6644 | 33.71% | 1 | 67.43% | 0% | 0% | 0% | 32.9196 | 0 | 0 | 0 | 32.9196 | 0 | 9911.7068 | 1982.3414 | 19.82% | 1 | 39.65% | 0% | 0% | 4.8528 | 0 | 0 | 4.8528 | 37.7724
2007-08-10 17:00 | 8 | 10 | 17 | 222 | 5321 | 84.92 | 0 | 8109.4699 | 8109.4699 | -8109.4699 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9911.5743 | 9911.5743 | 0 | 8.5 | 0 | 1651.9291 | 33.04% | 1 | 66.08% | 0% | 0% | 0% | 31.424 | 0 | 0 | 0 | 31.424 | 0 | 9713.3428 | 1942.6686 | 19.43% | 1 | 38.85% | 0% | 0% | 4.6323 | 0 | 0 | 4.6323 | 36.0563
2007-08-10 18:00 | 8 | 10 | 18 | 222 | 5322 | 80.96 | 0 | 5706.0014 | 5706.0014 | -5706.0014 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6974.0017 | 6974.0017 | 0 | 8.5 | 0 | 1162.3336 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6834.5217 | 1366.9043 | 13.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 19:00 | 8 | 10 | 19 | 222 | 5323 | 78.98 | 0 | 4879.725 | 4879.725 | -4879.725 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5964.1084 | 5964.1084 | 0 | 8.5 | 0 | 994.0181 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5844.8262 | 1168.9652 | 11.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 20:00 | 8 | 10 | 20 | 222 | 5324 | 78.98 | 0 | 3953.0745 | 3953.0745 | -3953.0745 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4831.5355 | 4831.5355 | 0 | 8.5 | 0 | 805.2559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4734.9047 | 946.9809 | 9.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 21:00 | 8 | 10 | 21 | 222 | 5325 | 77 | 0 | 2643.2325 | 2643.2325 | -2643.2325 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3230.6175 | 3230.6175 | 0 | 8.5 | 0 | 538.4362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3166.0051 | 633.201 | 6.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 22:00 | 8 | 10 | 22 | 222 | 5326 | 77 | 0 | 1197.7888 | 1197.7888 | -1197.7888 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1463.9641 | 1463.9641 | 0 | 8.5 | 0 | 243.994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1434.6848 | 286.937 | 2.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-10 23:00 | 8 | 10 | 23 | 222 | 5327 | 77 | 0 | 1036.8613 | 1036.8613 | -1036.8613 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1267.2749 | 1267.2749 | 0 | 8.5 | 0 | 211.2125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1241.9294 | 248.3859 | 2.484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 | 8 | 11 | 0 | 223 | 5328 | 75.02 | 0 | 847.5891 | 847.5891 | -847.5891 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1035.9423 | 1035.9423 | 0 | 8.5 | 0 | 172.657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1015.2234 | 203.0447 | 2.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 01:00 | 8 | 11 | 1 | 223 | 5329 | 73.04 | 0 | 755.9333 | 755.9333 | -755.9333 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 923.9185 | 923.9185 | 0 | 8.5 | 0 | 153.9864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 905.4401 | 181.088 | 1.811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 02:00 | 8 | 11 | 2 | 223 | 5330 | 73.04 | 0 | 613.2428 | 613.2428 | -613.2428 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 749.519 | 749.519 | 0 | 8.5 | 0 | 124.9198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 734.5286 | 146.9057 | 1.469% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 03:00 | 8 | 11 | 3 | 223 | 5331 | 71.96 | 0 | 501.5147 | 501.5147 | -501.5147 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 612.9624 | 612.9624 | 0 | 8.5 | 0 | 102.1604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 600.7032 | 120.1406 | 1.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 04:00 | 8 | 11 | 4 | 223 | 5332 | 69.98 | 0 | 343.8764 | 343.8764 | -343.8764 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 420.2933 | 420.2933 | 0 | 8.5 | 0 | 70.0489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 411.8875 | 82.3775 | 0.8238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 05:00 | 8 | 11 | 5 | 223 | 5333 | 69.98 | 0 | 294.5444 | 294.5444 | -294.5444 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 359.9988 | 359.9988 | 0 | 8.5 | 0 | 59.9998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 352.7988 | 70.5598 | 0.7056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 06:00 | 8 | 11 | 6 | 223 | 5334 | 71.06 | 0 | 289.9868 | 289.9868 | -289.9868 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 354.4283 | 354.4283 | 0 | 8.5 | 0 | 59.0714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 347.3397 | 69.4679 | 0.6947% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 07:00 | 8 | 11 | 7 | 223 | 5335 | 73.94 | 0 | 550.4287 | 550.4287 | -550.4287 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 672.7462 | 672.7462 | 0 | 8.5 | 0 | 112.1244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 659.2912 | 131.8582 | 1.319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 08:00 | 8 | 11 | 8 | 223 | 5336 | 73.94 | 28.9415 | 745.5402 | 745.5402 | -716.5987 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 911.2158 | 911.2158 | 0 | 8.5 | 0 | 151.8693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 892.9915 | 178.5983 | 1.786% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 09:00 | 8 | 11 | 9 | 223 | 5337 | 77 | 0 | 692.3749 | 692.3749 | -692.3749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 846.236 | 846.236 | 0 | 8.5 | 0 | 141.0393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 829.3113 | 165.8623 | 1.659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 10:00 | 8 | 11 | 10 | 223 | 5338 | 78.08 | 0 | 1707.2466 | 1707.2466 | -1707.2466 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2086.6347 | 2086.6347 | 0 | 8.5 | 0 | 347.7725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2044.902 | 408.9804 | 4.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 11:00 | 8 | 11 | 11 | 223 | 5339 | 78.08 | 0 | 3269.1727 | 3269.1727 | -3269.1727 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3995.6555 | 3995.6555 | 0 | 8.5 | 0 | 665.9426 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3915.7424 | 783.1485 | 7.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 12:00 | 8 | 11 | 12 | 223 | 5340 | 80.96 | 0 | 4855.8311 | 4855.8311 | -4855.8311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5934.9047 | 5934.9047 | 0 | 8.5 | 0 | 989.1508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5816.2066 | 1163.2413 | 11.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 13:00 | 8 | 11 | 13 | 223 | 5341 | 82.94 | 0 | 5338.2462 | 5338.2462 | -5338.2462 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6524.5232 | 6524.5232 | 0 | 8.5 | 0 | 1087.4205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6394.0327 | 1278.8065 | 12.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 14:00 | 8 | 11 | 14 | 223 | 5342 | 82.94 | 0 | 5852.5454 | 5852.5454 | -5852.5454 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7153.111 | 7153.111 | 0 | 8.5 | 0 | 1192.1852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7010.0488 | 1402.0098 | 14.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 15:00 | 8 | 11 | 15 | 223 | 5343 | 82.04 | 0 | 5475.6895 | 5475.6895 | -5475.6895 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6692.5093 | 6692.5093 | 0 | 8.5 | 0 | 1115.4182 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6558.6592 | 1311.7318 | 13.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 16:00 | 8 | 11 | 16 | 223 | 5344 | 82.04 | 0 | 6087.4976 | 6087.4976 | -6087.4976 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7440.2748 | 7440.2748 | 0 | 8.5 | 0 | 1240.0458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7291.4693 | 1458.2939 | 14.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 17:00 | 8 | 11 | 17 | 223 | 5345 | 82.04 | 0 | 6025.1523 | 6025.1523 | -6025.1523 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7364.075 | 7364.075 | 0 | 8.5 | 0 | 1227.3458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7216.7935 | 1443.3587 | 14.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 18:00 | 8 | 11 | 18 | 223 | 5346 | 78.08 | 0 | 4619.3913 | 4619.3913 | -4619.3913 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5645.9228 | 5645.9228 | 0 | 8.5 | 0 | 940.9871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5533.0043 | 1106.6009 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 19:00 | 8 | 11 | 19 | 223 | 5347 | 75.92 | 0 | 1827.3247 | 1827.3247 | -1827.3247 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2233.3968 | 2233.3968 | 0 | 8.5 | 0 | 372.2328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2188.7289 | 437.7458 | 4.377% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 20:00 | 8 | 11 | 20 | 223 | 5348 | 75.92 | 0 | 1387.8098 | 1387.8098 | -1387.8098 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1696.2119 | 1696.2119 | 0 | 8.5 | 0 | 282.702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1662.2877 | 332.4575 | 3.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 21:00 | 8 | 11 | 21 | 223 | 5349 | 73.94 | 0 | 1006.9034 | 1006.9034 | -1006.9034 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1230.6597 | 1230.6597 | 0 | 8.5 | 0 | 205.11 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1206.0465 | 241.2093 | 2.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 22:00 | 8 | 11 | 22 | 223 | 5350 | 71.96 | 0 | 790.8403 | 790.8403 | -790.8403 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 966.5826 | 966.5826 | 0 | 8.5 | 0 | 161.0971 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 947.2509 | 189.4502 | 1.895% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-11 23:00 | 8 | 11 | 23 | 223 | 5351 | 71.96 | 0 | 381.6285 | 381.6285 | -381.6285 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 466.4349 | 466.4349 | 0 | 8.5 | 0 | 77.7391 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 457.1062 | 91.4212 | 0.9142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 | 8 | 12 | 0 | 224 | 5352 | 69.08 | 0 | 217.3658 | 217.3658 | -217.3658 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 265.6693 | 265.6693 | 0 | 8.5 | 0 | 44.2782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 260.3559 | 52.0712 | 0.5207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 01:00 | 8 | 12 | 1 | 224 | 5353 | 68 | 0 | 91.1804 | 91.1804 | -91.1804 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 111.4428 | 111.4428 | 0 | 8.5 | 0 | 18.5738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 109.2139 | 21.8428 | 0.2184% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 02:00 | 8 | 12 | 2 | 224 | 5354 | 68 | 0 | 32.679 | 32.679 | -32.679 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 39.9411 | 39.9411 | 0 | 8.5 | 0 | 6.6568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 39.1422 | 7.8284 | 0.07828% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 03:00 | 8 | 12 | 3 | 224 | 5355 | 66.92 | 0 | 4.1166 | 4.1166 | -4.1166 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5.0314 | 5.0314 | 0 | 8.5 | 0 | 0.83857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4.9308 | 0.98616 | 0.009862% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 04:00 | 8 | 12 | 4 | 224 | 5356 | 66.92 | 0.34858 | 0 | 0 | 0.34858 | Heating | 0.30757 | 8.5 | 0.30757 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.061513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.31384 | 0 | 0.062769 | 0.0006277% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 05:00 | 8 | 12 | 5 | 224 | 5357 | 66.92 | 4.1127 | 0 | 0 | 4.1127 | Heating | 3.6289 | 8.5 | 3.6289 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.72578 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.7029 | 0 | 0.74059 | 0.007406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 06:00 | 8 | 12 | 6 | 224 | 5358 | 66.02 | 1187.4076 | 495.4339 | 495.4339 | 691.9737 | Heating | 610.5651 | 8.5 | 610.5651 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 623.0256 | 0 | 124.6051 | 1.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 07:00 | 8 | 12 | 7 | 224 | 5359 | 66.2 | 758.5279 | 513.8225 | 513.8225 | 244.7055 | Heating | 215.9166 | 8.5 | 215.9166 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.1833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 220.323 | 0 | 44.0646 | 0.4406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 08:00 | 8 | 12 | 8 | 224 | 5360 | 66.92 | 131.4117 | 2051.6834 | 2051.6834 | -1920.2717 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2507.613 | 2507.613 | 0 | 8.5 | 0 | 417.9355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2457.4608 | 491.4922 | 4.915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 09:00 | 8 | 12 | 9 | 224 | 5361 | 73.4 | 0 | 2866.5157 | 2866.5157 | -2866.5157 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3503.5192 | 3503.5192 | 0 | 8.5 | 0 | 583.9199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3433.4488 | 686.6898 | 6.867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 10:00 | 8 | 12 | 10 | 224 | 5362 | 75.02 | 0 | 3619.2099 | 3619.2099 | -3619.2099 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4423.4787 | 4423.4787 | 0 | 8.5 | 0 | 737.2465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4335.0091 | 867.0018 | 8.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 11:00 | 8 | 12 | 11 | 224 | 5363 | 75.02 | 0 | 5409.7274 | 5409.7274 | -5409.7274 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6611.8891 | 6611.8891 | 0 | 8.5 | 0 | 1101.9815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6479.6513 | 1295.9303 | 12.96% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 12:00 | 8 | 12 | 12 | 224 | 5364 | 78.08 | 0 | 6686.068 | 6686.068 | -6686.068 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8171.8609 | 8171.8609 | 0 | 8.5 | 0 | 1361.9768 | 30% | 1 | 54.48% | 0% | 0% | 0% | 20.1591 | 0 | 0 | 0 | 20.1591 | 0 | 8008.4237 | 1601.6847 | 16.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.4337
2007-08-12 13:00 | 8 | 12 | 13 | 224 | 5365 | 78.98 | 0 | 7666.2353 | 7666.2353 | -7666.2353 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9369.8431 | 9369.8431 | 0 | 8.5 | 0 | 1561.6405 | 31.23% | 1 | 62.47% | 0% | 0% | 0% | 27.6132 | 0 | 0 | 0 | 27.6132 | 0 | 9182.4463 | 1836.4893 | 18.36% | 1 | 36.73% | 0% | 0% | 4.0706 | 0 | 0 | 4.0706 | 31.6838
2007-08-12 14:00 | 8 | 12 | 14 | 224 | 5366 | 78.98 | 0 | 8304.531 | 8304.531 | -8304.531 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10149.9824 | 10149.9824 | 0 | 8.5 | 0 | 1691.6637 | 33.83% | 1 | 67.67% | 0% | 0% | 0% | 33.1897 | 0 | 0 | 0 | 33.1897 | 0 | 9946.9827 | 1989.3965 | 19.89% | 1 | 39.79% | 0% | 0% | 4.8926 | 0 | 0 | 4.8926 | 38.0823
2007-08-12 15:00 | 8 | 12 | 15 | 224 | 5367 | 80.06 | 0 | 8278.5635 | 8278.5635 | -8278.5635 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10118.2442 | 10118.2442 | 0 | 8.5 | 0 | 1686.374 | 33.73% | 1 | 67.45% | 0% | 0% | 0% | 32.9515 | 0 | 0 | 0 | 32.9515 | 0 | 9915.8793 | 1983.1759 | 19.83% | 1 | 39.66% | 0% | 0% | 4.8575 | 0 | 0 | 4.8575 | 37.809
2007-08-12 16:00 | 8 | 12 | 16 | 224 | 5368 | 78.08 | 0 | 7762.4729 | 7762.4729 | -7762.4729 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9487.4669 | 9487.4669 | 0 | 8.5 | 0 | 1581.2445 | 31.62% | 1 | 63.25% | 0% | 0% | 0% | 28.417 | 0 | 0 | 0 | 28.417 | 0 | 9297.7175 | 1859.5435 | 18.6% | 1 | 37.19% | 0% | 0% | 4.1891 | 0 | 0 | 4.1891 | 32.6061
2007-08-12 17:00 | 8 | 12 | 17 | 224 | 5369 | 78.08 | 0 | 7120.0471 | 7120.0471 | -7120.0471 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8702.2798 | 8702.2798 | 0 | 8.5 | 0 | 1450.38 | 30% | 1 | 58.02% | 0% | 0% | 0% | 23.2964 | 0 | 0 | 0 | 23.2964 | 0 | 8528.2342 | 1705.6468 | 17.06% | 1 | 34.11% | 0% | 0% | 3.4342 | 0 | 0 | 3.4342 | 26.7306
2007-08-12 18:00 | 8 | 12 | 18 | 224 | 5370 | 75.92 | 0 | 4295.6548 | 4295.6548 | -4295.6548 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5250.2448 | 5250.2448 | 0 | 8.5 | 0 | 875.0408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5145.2399 | 1029.048 | 10.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 19:00 | 8 | 12 | 19 | 224 | 5371 | 75.02 | 0 | 2843.8183 | 2843.8183 | -2843.8183 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3475.7779 | 3475.7779 | 0 | 8.5 | 0 | 579.2963 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3406.2624 | 681.2525 | 6.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 20:00 | 8 | 12 | 20 | 224 | 5372 | 75.02 | 0 | 862.6211 | 862.6211 | -862.6211 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1054.3147 | 1054.3147 | 0 | 8.5 | 0 | 175.7191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1033.2284 | 206.6457 | 2.066% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 21:00 | 8 | 12 | 21 | 224 | 5373 | 71.96 | 0 | 482.1231 | 482.1231 | -482.1231 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 589.2616 | 589.2616 | 0 | 8.5 | 0 | 98.2103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 577.4763 | 115.4953 | 1.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 22:00 | 8 | 12 | 22 | 224 | 5374 | 71.06 | 0 | 44.3178 | 44.3178 | -44.3178 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 54.1662 | 54.1662 | 0 | 8.5 | 0 | 9.0277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 53.0829 | 10.6166 | 0.1062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-12 23:00 | 8 | 12 | 23 | 224 | 5375 | 71.06 | 0.93152 | 7.9744 | 7.9744 | -7.0429 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9.7465 | 9.7465 | 0 | 8.5 | 0 | 1.6244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 9.5516 | 1.9103 | 0.0191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 | 8 | 13 | 0 | 225 | 5376 | 69.98 | 13.4929 | 0 | 0 | 13.4929 | Heating | 11.9055 | 8.5 | 11.9055 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.3811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.1485 | 0 | 2.4297 | 0.0243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 01:00 | 8 | 13 | 1 | 225 | 5377 | 69.98 | 28.0247 | 0 | 0 | 28.0247 | Heating | 24.7277 | 8.5 | 24.7277 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.9455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 25.2323 | 0 | 5.0465 | 0.05046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 02:00 | 8 | 13 | 2 | 225 | 5378 | 69.98 | 44.5892 | 0 | 0 | 44.5892 | Heating | 39.3434 | 8.5 | 39.3434 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.8687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.1463 | 0 | 8.0293 | 0.08029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 03:00 | 8 | 13 | 3 | 225 | 5379 | 66.92 | 67.8234 | 0 | 0 | 67.8234 | Heating | 59.8442 | 8.5 | 59.8442 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.9688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 61.0655 | 0 | 12.2131 | 0.1221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 04:00 | 8 | 13 | 4 | 225 | 5380 | 66.92 | 101.9541 | 0 | 0 | 101.9541 | Heating | 89.9595 | 8.5 | 89.9595 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.9919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 91.7954 | 0 | 18.3591 | 0.1836% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 05:00 | 8 | 13 | 5 | 225 | 5381 | 66.92 | 138.9301 | 0 | 0 | 138.9301 | Heating | 122.5854 | 8.5 | 122.5854 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.5171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 125.0871 | 0 | 25.0174 | 0.2502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 06:00 | 8 | 13 | 6 | 225 | 5382 | 68 | 3489.4049 | 120.6044 | 120.6044 | 3368.8005 | Heating | 2972.4711 | 8.5 | 2972.4711 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 594.4942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3033.1337 | 0 | 606.6267 | 6.066% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 07:00 | 8 | 13 | 7 | 225 | 5383 | 69.08 | 1936.7424 | 97.6561 | 97.6561 | 1839.0863 | Heating | 1622.7232 | 8.5 | 1622.7232 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.5446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1655.84 | 0 | 331.168 | 3.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 08:00 | 8 | 13 | 8 | 225 | 5384 | 69.08 | 745.6659 | 845.9687 | 845.9687 | -100.3028 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1033.9618 | 1033.9618 | 0 | 8.5 | 0 | 172.327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1013.2826 | 202.6565 | 2.027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 09:00 | 8 | 13 | 9 | 225 | 5385 | 71.96 | 2.9258 | 2263.2187 | 2263.2187 | -2260.2929 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2766.1562 | 2766.1562 | 0 | 8.5 | 0 | 461.026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2710.833 | 542.1666 | 5.422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 10:00 | 8 | 13 | 10 | 225 | 5386 | 71.6 | 0 | 3550.0966 | 3550.0966 | -3550.0966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4339.007 | 4339.007 | 0 | 8.5 | 0 | 723.1678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4252.2268 | 850.4454 | 8.504% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 11:00 | 8 | 13 | 11 | 225 | 5387 | 71.96 | 0 | 5493.8208 | 5493.8208 | -5493.8208 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6714.6699 | 6714.6699 | 0 | 8.5 | 0 | 1119.1117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6580.3765 | 1316.0753 | 13.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 12:00 | 8 | 13 | 12 | 225 | 5388 | 73.4 | 0 | 6974.833 | 6974.833 | -6974.833 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8524.7959 | 8524.7959 | 0 | 8.5 | 0 | 1420.7993 | 30% | 1 | 56.83% | 0% | 0% | 0% | 22.2181 | 0 | 0 | 0 | 22.2181 | 0 | 8354.2999 | 1670.86 | 16.71% | 1 | 33.42% | 0% | 0% | 3.2752 | 0 | 0 | 3.2752 | 25.4933
2007-08-13 13:00 | 8 | 13 | 13 | 225 | 5389 | 73.4 | 0 | 8652.3808 | 8652.3808 | -8652.3808 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10575.1321 | 10575.1321 | 0 | 8.5 | 0 | 1762.522 | 35.25% | 1 | 70.5% | 0% | 0% | 0% | 36.4746 | 0 | 0 | 0 | 36.4746 | 0 | 10363.6294 | 2072.7259 | 20.73% | 1 | 41.45% | 0% | 0% | 5.3769 | 0 | 0 | 5.3769 | 41.8515
2007-08-13 14:00 | 8 | 13 | 14 | 225 | 5390 | 73.94 | 0 | 10204.0887 | 10204.0887 | -10204.0887 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12471.6639 | 12471.6639 | 0 | 8.5 | 0 | 2078.6107 | 41.57% | 1 | 83.14% | 0% | 0% | 0% | 53.3039 | 0 | 0 | 0 | 53.3039 | 0 | 12222.2306 | 2444.4461 | 24.44% | 1 | 48.89% | 0% | 0% | 7.8577 | 0 | 0 | 7.8577 | 61.1617
2007-08-13 15:00 | 8 | 13 | 15 | 225 | 5391 | 75.92 | 0 | 10843.1244 | 10843.1244 | -10843.1244 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13252.7076 | 13252.7076 | 0 | 8.5 | 0 | 2208.7846 | 44.18% | 1 | 88.35% | 0% | 0% | 0% | 61.2962 | 0 | 0 | 0 | 61.2962 | 0 | 12987.6534 | 2597.5307 | 25.98% | 1 | 51.95% | 0% | 0% | 9.0359 | 0 | 0 | 9.0359 | 70.3321
2007-08-13 16:00 | 8 | 13 | 16 | 225 | 5392 | 77 | 0 | 10263.6666 | 10263.6666 | -10263.6666 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12544.4814 | 12544.4814 | 0 | 8.5 | 0 | 2090.7469 | 41.81% | 1 | 83.63% | 0% | 0% | 0% | 54.0225 | 0 | 0 | 0 | 54.0225 | 0 | 12293.5918 | 2458.7184 | 24.59% | 1 | 49.17% | 0% | 0% | 7.9637 | 0 | 0 | 7.9637 | 61.9861
2007-08-13 17:00 | 8 | 13 | 17 | 225 | 5393 | 77 | 0 | 9823.4526 | 9823.4526 | -9823.4526 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12006.4421 | 12006.4421 | 0 | 8.5 | 0 | 2001.0737 | 40.02% | 1 | 80.04% | 0% | 0% | 0% | 48.8412 | 0 | 0 | 0 | 48.8412 | 0 | 11766.3132 | 2353.2626 | 23.53% | 1 | 47.07% | 0% | 0% | 7.1999 | 0 | 0 | 7.1999 | 56.041
2007-08-13 18:00 | 8 | 13 | 18 | 225 | 5394 | 75.02 | 0 | 6600.6824 | 6600.6824 | -6600.6824 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8067.5007 | 8067.5007 | 0 | 8.5 | 0 | 1344.5835 | 30% | 1 | 53.78% | 0% | 0% | 0% | 19.5719 | 0 | 0 | 0 | 19.5719 | 0 | 7906.1507 | 1581.2301 | 15.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.8464
2007-08-13 19:00 | 8 | 13 | 19 | 225 | 5395 | 71.06 | 0 | 5911.3811 | 5911.3811 | -5911.3811 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7225.0214 | 7225.0214 | 0 | 8.5 | 0 | 1204.1702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7080.5209 | 1416.1042 | 14.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 20:00 | 8 | 13 | 20 | 225 | 5396 | 71.06 | 0 | 4763.9605 | 4763.9605 | -4763.9605 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5822.6184 | 5822.6184 | 0 | 8.5 | 0 | 970.4364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5706.1661 | 1141.2332 | 11.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 21:00 | 8 | 13 | 21 | 225 | 5397 | 69.98 | 0 | 2201.0473 | 2201.0473 | -2201.0473 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2690.169 | 2690.169 | 0 | 8.5 | 0 | 448.3615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2636.3656 | 527.2731 | 5.273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 22:00 | 8 | 13 | 22 | 225 | 5398 | 69.08 | 0 | 707.3883 | 707.3883 | -707.3883 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 864.5857 | 864.5857 | 0 | 8.5 | 0 | 144.0976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 847.294 | 169.4588 | 1.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-13 23:00 | 8 | 13 | 23 | 225 | 5399 | 69.08 | 0 | 754.3315 | 754.3315 | -754.3315 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 921.9607 | 921.9607 | 0 | 8.5 | 0 | 153.6601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 903.5215 | 180.7043 | 1.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 | 8 | 14 | 0 | 226 | 5400 | 64.94 | 0 | 717.8604 | 717.8604 | -717.8604 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 877.385 | 877.385 | 0 | 8.5 | 0 | 146.2308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 859.8373 | 171.9675 | 1.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 01:00 | 8 | 14 | 1 | 226 | 5401 | 64.94 | 0 | 637.0785 | 637.0785 | -637.0785 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 778.6516 | 778.6516 | 0 | 8.5 | 0 | 129.7753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 763.0785 | 152.6157 | 1.526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 02:00 | 8 | 14 | 2 | 226 | 5402 | 64.94 | 0 | 632.4571 | 632.4571 | -632.4571 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 773.0031 | 773.0031 | 0 | 8.5 | 0 | 128.8339 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 757.543 | 151.5086 | 1.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 03:00 | 8 | 14 | 3 | 226 | 5403 | 64.04 | 0 | 464.7968 | 464.7968 | -464.7968 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 568.085 | 568.085 | 0 | 8.5 | 0 | 94.6808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 556.7233 | 111.3447 | 1.113% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 04:00 | 8 | 14 | 4 | 226 | 5404 | 64.94 | 0 | 358.139 | 358.139 | -358.139 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 437.7254 | 437.7254 | 0 | 8.5 | 0 | 72.9542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 428.9709 | 85.7942 | 0.8579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 05:00 | 8 | 14 | 5 | 226 | 5405 | 64.94 | 0 | 386.8978 | 386.8978 | -386.8978 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 472.875 | 472.875 | 0 | 8.5 | 0 | 78.8125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 463.4175 | 92.6835 | 0.9268% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 06:00 | 8 | 14 | 6 | 226 | 5406 | 62.96 | 0 | 2954.4311 | 2954.4311 | -2954.4311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3610.9714 | 3610.9714 | 0 | 8.5 | 0 | 601.8286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3538.7519 | 707.7504 | 7.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 07:00 | 8 | 14 | 7 | 226 | 5407 | 64.4 | 0 | 3816.1974 | 3816.1974 | -3816.1974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4664.2412 | 4664.2412 | 0 | 8.5 | 0 | 777.3735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4570.9564 | 914.1913 | 9.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 08:00 | 8 | 14 | 8 | 226 | 5408 | 64.94 | 0 | 6722.1898 | 6722.1898 | -6722.1898 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8216.0097 | 8216.0097 | 0 | 8.5 | 0 | 1369.3349 | 30% | 1 | 54.77% | 0% | 0% | 0% | 20.4105 | 0 | 0 | 0 | 20.4105 | 0 | 8051.6895 | 1610.3379 | 16.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.685
2007-08-14 09:00 | 8 | 14 | 9 | 226 | 5409 | 71.6 | 0 | 10587.2583 | 10587.2583 | -10587.2583 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12939.9824 | 12939.9824 | 0 | 8.5 | 0 | 2156.6637 | 43.13% | 1 | 86.27% | 0% | 0% | 0% | 58.0204 | 0 | 0 | 0 | 58.0204 | 0 | 12681.1828 | 2536.2366 | 25.36% | 1 | 50.72% | 0% | 0% | 8.553 | 0 | 0 | 8.553 | 66.5734
2007-08-14 10:00 | 8 | 14 | 10 | 226 | 5410 | 73.04 | 0 | 12601.9964 | 12601.9964 | -12601.9964 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15402.44 | 15402.44 | 0 | 8.5 | 0 | 2567.0733 | 51.34% | 2 | 51.34% | 51.34% | 0% | 0% | 17.5881 | 17.5881 | 0 | 0 | 35.1763 | 0 | 15094.3912 | 3018.8782 | 30.19% | 1 | 60.38% | 0% | 0% | 12.7681 | 0 | 0 | 12.7681 | 47.9444
2007-08-14 11:00 | 8 | 14 | 11 | 226 | 5411 | 73.04 | 0 | 13518.6181 | 13518.6181 | -13518.6181 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16522.7554 | 16522.7554 | 0 | 8.5 | 0 | 2753.7926 | 55.08% | 2 | 55.08% | 55.08% | 0% | 0% | 20.6706 | 20.6706 | 0 | 0 | 41.3413 | 0 | 16192.3003 | 3238.4601 | 32.38% | 1 | 64.77% | 0% | 0% | 15.0059 | 0 | 0 | 15.0059 | 56.3471
2007-08-14 12:00 | 8 | 14 | 12 | 226 | 5412 | 80.06 | 0 | 14169.4612 | 14169.4612 | -14169.4612 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17318.2303 | 17318.2303 | 0 | 8.5 | 0 | 2886.3717 | 57.73% | 2 | 57.73% | 57.73% | 0% | 0% | 23.0315 | 23.0315 | 0 | 0 | 46.063 | 0 | 16971.8657 | 3394.3731 | 33.94% | 1 | 33.94% | 33.94% | 0% | 3.3952 | 3.3952 | 0 | 6.7903 | 52.8533
2007-08-14 13:00 | 8 | 14 | 13 | 226 | 5413 | 82.04 | 0 | 14602.0655 | 14602.0655 | -14602.0655 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17846.9689 | 17846.9689 | 0 | 8.5 | 0 | 2974.4948 | 59.49% | 2 | 59.49% | 59.49% | 0% | 0% | 24.681 | 24.681 | 0 | 0 | 49.362 | 0 | 17490.0296 | 3498.0059 | 34.98% | 1 | 34.98% | 34.98% | 0% | 3.6383 | 3.6383 | 0 | 7.2766 | 56.6386
2007-08-14 14:00 | 8 | 14 | 14 | 226 | 5414 | 82.04 | 0 | 14013.8935 | 14013.8935 | -14013.8935 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17128.0921 | 17128.0921 | 0 | 8.5 | 0 | 2854.682 | 57.09% | 2 | 57.09% | 57.09% | 0% | 0% | 22.4541 | 22.4541 | 0 | 0 | 44.9081 | 0 | 16785.5302 | 3357.106 | 33.57% | 1 | 33.57% | 33.57% | 0% | 3.31 | 3.31 | 0 | 6.6201 | 51.5282
2007-08-14 15:00 | 8 | 14 | 15 | 226 | 5415 | 84.02 | 0 | 13488.5956 | 13488.5956 | -13488.5956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16486.0613 | 16486.0613 | 0 | 8.5 | 0 | 2747.6769 | 54.95% | 2 | 54.95% | 54.95% | 0% | 0% | 20.5652 | 20.5652 | 0 | 0 | 41.1304 | 0 | 16156.3401 | 3231.268 | 32.31% | 1 | 64.63% | 0% | 0% | 14.9293 | 0 | 0 | 14.9293 | 56.0597
2007-08-14 16:00 | 8 | 14 | 16 | 226 | 5416 | 84.02 | 0 | 13972.3387 | 13972.3387 | -13972.3387 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17077.3028 | 17077.3028 | 0 | 8.5 | 0 | 2846.2171 | 56.92% | 2 | 56.92% | 56.92% | 0% | 0% | 22.3012 | 22.3012 | 0 | 0 | 44.6024 | 0 | 16735.7567 | 3347.1513 | 33.47% | 1 | 33.47% | 33.47% | 0% | 3.2875 | 3.2875 | 0 | 6.575 | 51.1774
2007-08-14 17:00 | 8 | 14 | 17 | 226 | 5417 | 84.02 | 0 | 13668.4438 | 13668.4438 | -13668.4438 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16705.8757 | 16705.8757 | 0 | 8.5 | 0 | 2784.3126 | 55.69% | 2 | 55.69% | 55.69% | 0% | 0% | 21.2013 | 21.2013 | 0 | 0 | 42.4027 | 0 | 16371.7582 | 3274.3516 | 32.74% | 1 | 65.49% | 0% | 0% | 15.3911 | 0 | 0 | 15.3911 | 57.7938
2007-08-14 18:00 | 8 | 14 | 18 | 226 | 5418 | 82.94 | 0 | 9012.3045 | 9012.3045 | -9012.3045 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11015.0388 | 11015.0388 | 0 | 8.5 | 0 | 1835.8398 | 36.72% | 1 | 73.43% | 0% | 0% | 0% | 40.0591 | 0 | 0 | 0 | 40.0591 | 0 | 10794.7381 | 2158.9476 | 21.59% | 1 | 43.18% | 0% | 0% | 5.9053 | 0 | 0 | 5.9053 | 45.9643
2007-08-14 19:00 | 8 | 14 | 19 | 226 | 5419 | 78.08 | 0 | 8665.7992 | 8665.7992 | -8665.7992 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10591.5324 | 10591.5324 | 0 | 8.5 | 0 | 1765.2554 | 35.31% | 1 | 70.61% | 0% | 0% | 0% | 36.6048 | 0 | 0 | 0 | 36.6048 | 0 | 10379.7018 | 2075.9404 | 20.76% | 1 | 41.52% | 0% | 0% | 5.3961 | 0 | 0 | 5.3961 | 42.0009
2007-08-14 20:00 | 8 | 14 | 20 | 226 | 5420 | 78.08 | 0 | 8938.6529 | 8938.6529 | -8938.6529 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10925.0202 | 10925.0202 | 0 | 8.5 | 0 | 1820.8367 | 36.42% | 1 | 72.83% | 0% | 0% | 0% | 39.3101 | 0 | 0 | 0 | 39.3101 | 0 | 10706.5198 | 2141.304 | 21.41% | 1 | 42.83% | 0% | 0% | 5.7948 | 0 | 0 | 5.7948 | 45.105
2007-08-14 21:00 | 8 | 14 | 21 | 226 | 5421 | 71.06 | 0 | 3976.4685 | 3976.4685 | -3976.4685 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4860.1281 | 4860.1281 | 0 | 8.5 | 0 | 810.0214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4762.9256 | 952.5851 | 9.526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 22:00 | 8 | 14 | 22 | 226 | 5422 | 69.98 | 0 | 1790.7932 | 1790.7932 | -1790.7932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2188.7472 | 2188.7472 | 0 | 8.5 | 0 | 364.7912 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2144.9722 | 428.9944 | 4.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-14 23:00 | 8 | 14 | 23 | 226 | 5423 | 69.98 | 0 | 2001.9388 | 2001.9388 | -2001.9388 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2446.814 | 2446.814 | 0 | 8.5 | 0 | 407.8023 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2397.8778 | 479.5756 | 4.796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 | 8 | 15 | 0 | 227 | 5424 | 64.94 | 0 | 1551.8147 | 1551.8147 | -1551.8147 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1896.6624 | 1896.6624 | 0 | 8.5 | 0 | 316.1104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1858.7292 | 371.7458 | 3.717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 01:00 | 8 | 15 | 1 | 227 | 5425 | 66.02 | 0 | 1314.3246 | 1314.3246 | -1314.3246 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1606.3967 | 1606.3967 | 0 | 8.5 | 0 | 267.7328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1574.2688 | 314.8538 | 3.149% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 02:00 | 8 | 15 | 2 | 227 | 5426 | 66.02 | 0 | 1304.2589 | 1304.2589 | -1304.2589 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1594.0942 | 1594.0942 | 0 | 8.5 | 0 | 265.6824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1562.2123 | 312.4425 | 3.124% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 03:00 | 8 | 15 | 3 | 227 | 5427 | 64.04 | 0 | 1190.6838 | 1190.6838 | -1190.6838 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1455.2802 | 1455.2802 | 0 | 8.5 | 0 | 242.5467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1426.1746 | 285.2349 | 2.852% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 04:00 | 8 | 15 | 4 | 227 | 5428 | 62.96 | 0 | 911.6048 | 911.6048 | -911.6048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1114.1837 | 1114.1837 | 0 | 8.5 | 0 | 185.6973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1091.9 | 218.38 | 2.184% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 05:00 | 8 | 15 | 5 | 227 | 5429 | 62.96 | 0 | 953.9911 | 953.9911 | -953.9911 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1165.9891 | 1165.9891 | 0 | 8.5 | 0 | 194.3315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1142.6693 | 228.5339 | 2.285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 06:00 | 8 | 15 | 6 | 227 | 5430 | 64.4 | 0 | 5283.7926 | 5283.7926 | -5283.7926 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6457.9687 | 6457.9687 | 0 | 8.5 | 0 | 1076.3281 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6328.8093 | 1265.7619 | 12.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 07:00 | 8 | 15 | 7 | 227 | 5431 | 64.4 | 0 | 5583.1055 | 5583.1055 | -5583.1055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6823.7956 | 6823.7956 | 0 | 8.5 | 0 | 1137.2993 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6687.3197 | 1337.4639 | 13.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 08:00 | 8 | 15 | 8 | 227 | 5432 | 66.02 | 0 | 7651.5548 | 7651.5548 | -7651.5548 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9351.9003 | 9351.9003 | 0 | 8.5 | 0 | 1558.6501 | 31.17% | 1 | 62.35% | 0% | 0% | 0% | 27.4918 | 0 | 0 | 0 | 27.4918 | 0 | 9164.8623 | 1832.9725 | 18.33% | 1 | 36.66% | 0% | 0% | 4.0527 | 0 | 0 | 4.0527 | 31.5444
2007-08-15 09:00 | 8 | 15 | 9 | 227 | 5433 | 75.02 | 0 | 11071.991 | 11071.991 | -11071.991 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13532.4334 | 13532.4334 | 0 | 8.5 | 0 | 2255.4056 | 45.11% | 1 | 90.22% | 0% | 0% | 0% | 64.3128 | 0 | 0 | 0 | 64.3128 | 0 | 13261.7848 | 2652.357 | 26.52% | 1 | 53.05% | 0% | 0% | 9.4806 | 0 | 0 | 9.4806 | 73.7934
2007-08-15 10:00 | 8 | 15 | 10 | 227 | 5434 | 78.98 | 0 | 12961.8621 | 12961.8621 | -12961.8621 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15842.2759 | 15842.2759 | 0 | 8.5 | 0 | 2640.3793 | 52.81% | 2 | 52.81% | 52.81% | 0% | 0% | 18.7648 | 18.7648 | 0 | 0 | 37.5297 | 0 | 15525.4304 | 3105.0861 | 31.05% | 1 | 62.1% | 0% | 0% | 13.6223 | 0 | 0 | 13.6223 | 51.152
2007-08-15 11:00 | 8 | 15 | 11 | 227 | 5435 | 78.98 | 0 | 14936.7155 | 14936.7155 | -14936.7155 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 18255.9856 | 18255.9856 | 0 | 8.5 | 0 | 3042.6643 | 60.85% | 2 | 60.85% | 60.85% | 0% | 0% | 26.0014 | 26.0014 | 0 | 0 | 52.0028 | 0 | 17890.8659 | 3578.1732 | 35.78% | 1 | 35.78% | 35.78% | 0% | 3.833 | 3.833 | 0 | 7.6659 | 59.6687
2007-08-15 12:00 | 8 | 15 | 12 | 227 | 5436 | 84.92 | 0 | 16257.1701 | 16257.1701 | -16257.1701 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 19869.8746 | 19869.8746 | 0 | 8.5 | 0 | 3311.6458 | 66.23% | 2 | 66.23% | 66.23% | 0% | 0% | 31.5946 | 31.5946 | 0 | 0 | 63.1892 | 0 | 19472.4771 | 3894.4954 | 38.94% | 1 | 38.94% | 38.94% | 0% | 4.6575 | 4.6575 | 0 | 9.315 | 72.5042
2007-08-15 13:00 | 8 | 15 | 13 | 227 | 5437 | 86 | 0 | 17544.33 | 17544.33 | -17544.33 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 21443.07 | 21443.07 | 0 | 8.5 | 0 | 3573.845 | 71.48% | 2 | 71.48% | 71.48% | 0% | 0% | 37.6465 | 37.6465 | 0 | 0 | 75.2929 | 0 | 21014.2086 | 4202.8417 | 42.03% | 1 | 42.03% | 42.03% | 0% | 5.5496 | 5.5496 | 0 | 11.0992 | 86.3921
2007-08-15 14:00 | 8 | 15 | 14 | 227 | 5438 | 86 | 0 | 18460.3406 | 18460.3406 | -18460.3406 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 22562.6386 | 22562.6386 | 0 | 8.5 | 0 | 3760.4398 | 75.21% | 2 | 75.21% | 75.21% | 0% | 0% | 42.3215 | 42.3215 | 0 | 0 | 84.643 | 0 | 22111.3858 | 4422.2772 | 44.22% | 1 | 44.22% | 44.22% | 0% | 6.2388 | 6.2388 | 0 | 12.4775 | 97.1205
2007-08-15 15:00 | 8 | 15 | 15 | 227 | 5439 | 89.06 | 0 | 17645.1644 | 17645.1644 | -17645.1644 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 21566.3121 | 21566.3121 | 0 | 8.5 | 0 | 3594.3853 | 71.89% | 2 | 71.89% | 71.89% | 0% | 0% | 38.146 | 38.146 | 0 | 0 | 76.2919 | 0 | 21134.9858 | 4226.9972 | 42.27% | 1 | 42.27% | 42.27% | 0% | 5.6232 | 5.6232 | 0 | 11.2465 | 87.5384
2007-08-15 16:00 | 8 | 15 | 16 | 227 | 5440 | 87.08 | 0 | 17927.4435 | 17927.4435 | -17927.4435 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 21911.3199 | 21911.3199 | 0 | 8.5 | 0 | 3651.8866 | 73.04% | 2 | 73.04% | 73.04% | 0% | 0% | 39.5641 | 39.5641 | 0 | 0 | 79.1283 | 0 | 21473.0935 | 4294.6187 | 42.95% | 1 | 42.95% | 42.95% | 0% | 5.8323 | 5.8323 | 0 | 11.6646 | 90.7929
2007-08-15 17:00 | 8 | 15 | 17 | 227 | 5441 | 87.08 | 0 | 17847.0444 | 17847.0444 | -17847.0444 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 21813.0543 | 21813.0543 | 0 | 8.5 | 0 | 3635.509 | 72.71% | 2 | 72.71% | 72.71% | 0% | 0% | 39.1572 | 39.1572 | 0 | 0 | 78.3145 | 0 | 21376.7932 | 4275.3586 | 42.75% | 1 | 42.75% | 42.75% | 0% | 5.7723 | 5.7723 | 0 | 11.5446 | 89.8591
2007-08-15 18:00 | 8 | 15 | 18 | 227 | 5442 | 82.94 | 0 | 10572.8479 | 10572.8479 | -10572.8479 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12922.3697 | 12922.3697 | 0 | 8.5 | 0 | 2153.7283 | 43.07% | 1 | 86.15% | 0% | 0% | 0% | 57.8389 | 0 | 0 | 0 | 57.8389 | 0 | 12663.9223 | 2532.7845 | 25.33% | 1 | 50.66% | 0% | 0% | 8.5262 | 0 | 0 | 8.5262 | 66.3652
2007-08-15 19:00 | 8 | 15 | 19 | 227 | 5443 | 80.06 | 0 | 7889.7848 | 7889.7848 | -7889.7848 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9643.0704 | 9643.0704 | 0 | 8.5 | 0 | 1607.1784 | 32.14% | 1 | 64.29% | 0% | 0% | 0% | 29.5004 | 0 | 0 | 0 | 29.5004 | 0 | 9450.209 | 1890.0418 | 18.9% | 1 | 37.8% | 0% | 0% | 4.3488 | 0 | 0 | 4.3488 | 33.8492
2007-08-15 20:00 | 8 | 15 | 20 | 227 | 5444 | 80.06 | 0 | 6604.3525 | 6604.3525 | -6604.3525 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8071.9864 | 8071.9864 | 0 | 8.5 | 0 | 1345.3311 | 30% | 1 | 53.81% | 0% | 0% | 0% | 19.5969 | 0 | 0 | 0 | 19.5969 | 0 | 7910.5467 | 1582.1093 | 15.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.8715
2007-08-15 21:00 | 8 | 15 | 21 | 227 | 5445 | 75.92 | 0 | 3288.1017 | 3288.1017 | -3288.1017 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4018.791 | 4018.791 | 0 | 8.5 | 0 | 669.7985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3938.4151 | 787.683 | 7.877% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 22:00 | 8 | 15 | 22 | 227 | 5446 | 71.96 | 0 | 1471.9269 | 1471.9269 | -1471.9269 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1799.0218 | 1799.0218 | 0 | 8.5 | 0 | 299.837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1763.0414 | 352.6083 | 3.526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-15 23:00 | 8 | 15 | 23 | 227 | 5447 | 71.96 | 0 | 1256.7242 | 1256.7242 | -1256.7242 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1535.9963 | 1535.9963 | 0 | 8.5 | 0 | 255.9994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1505.2764 | 301.0553 | 3.011% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 | 8 | 16 | 0 | 228 | 5448 | 69.08 | 0 | 1207.0382 | 1207.0382 | -1207.0382 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1475.2689 | 1475.2689 | 0 | 8.5 | 0 | 245.8782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1445.7635 | 289.1527 | 2.892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 01:00 | 8 | 16 | 1 | 228 | 5449 | 69.08 | 0 | 1128.9992 | 1128.9992 | -1128.9992 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1379.8879 | 1379.8879 | 0 | 8.5 | 0 | 229.9813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1352.2901 | 270.458 | 2.705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 02:00 | 8 | 16 | 2 | 228 | 5450 | 69.08 | 0 | 920.9188 | 920.9188 | -920.9188 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1125.5674 | 1125.5674 | 0 | 8.5 | 0 | 187.5946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1103.0561 | 220.6112 | 2.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 03:00 | 8 | 16 | 3 | 228 | 5451 | 68 | 0 | 883.4823 | 883.4823 | -883.4823 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1079.8117 | 1079.8117 | 0 | 8.5 | 0 | 179.9686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1058.2154 | 211.6431 | 2.116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 04:00 | 8 | 16 | 4 | 228 | 5452 | 66.92 | 0 | 643.5283 | 643.5283 | -643.5283 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 786.5346 | 786.5346 | 0 | 8.5 | 0 | 131.0891 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 770.8039 | 154.1608 | 1.542% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 05:00 | 8 | 16 | 5 | 228 | 5453 | 66.92 | 0 | 321.1914 | 321.1914 | -321.1914 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 392.5673 | 392.5673 | 0 | 8.5 | 0 | 65.4279 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 384.716 | 76.9432 | 0.7694% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 06:00 | 8 | 16 | 6 | 228 | 5454 | 66.92 | 64.231 | 2998.5136 | 2998.5136 | -2934.2826 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3664.8499 | 3664.8499 | 0 | 8.5 | 0 | 610.8083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3591.553 | 718.3106 | 7.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 07:00 | 8 | 16 | 7 | 228 | 5455 | 71.06 | 0 | 2994.1598 | 2994.1598 | -2994.1598 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3659.5286 | 3659.5286 | 0 | 8.5 | 0 | 609.9214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3586.338 | 717.2676 | 7.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 08:00 | 8 | 16 | 8 | 228 | 5456 | 71.06 | 0 | 4619.3479 | 4619.3479 | -4619.3479 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5645.8697 | 5645.8697 | 0 | 8.5 | 0 | 940.9783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5532.9523 | 1106.5905 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 09:00 | 8 | 16 | 9 | 228 | 5457 | 77 | 0 | 5028.5905 | 5028.5905 | -5028.5905 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6146.0551 | 6146.0551 | 0 | 8.5 | 0 | 1024.3425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6023.134 | 1204.6268 | 12.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 10:00 | 8 | 16 | 10 | 228 | 5458 | 80.96 | 0 | 5779.7142 | 5779.7142 | -5779.7142 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7064.0951 | 7064.0951 | 0 | 8.5 | 0 | 1177.3492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6922.8132 | 1384.5626 | 13.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 11:00 | 8 | 16 | 11 | 228 | 5459 | 80.96 | 0 | 7060.3625 | 7060.3625 | -7060.3625 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8629.332 | 8629.332 | 0 | 8.5 | 0 | 1438.222 | 30% | 1 | 57.53% | 0% | 0% | 0% | 22.8497 | 0 | 0 | 0 | 22.8497 | 0 | 8456.7453 | 1691.3491 | 16.91% | 1 | 33.83% | 0% | 0% | 3.3684 | 0 | 0 | 3.3684 | 26.2181
2007-08-16 12:00 | 8 | 16 | 12 | 228 | 5460 | 87.08 | 0 | 7432.5337 | 7432.5337 | -7432.5337 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9084.2079 | 9084.2079 | 0 | 8.5 | 0 | 1514.0346 | 30.28% | 1 | 60.56% | 0% | 0% | 0% | 25.7154 | 0 | 0 | 0 | 25.7154 | 0 | 8902.5237 | 1780.5047 | 17.81% | 1 | 35.61% | 0% | 0% | 3.7908 | 0 | 0 | 3.7908 | 29.5062
2007-08-16 13:00 | 8 | 16 | 13 | 228 | 5461 | 87.98 | 0 | 8298.9842 | 8298.9842 | -8298.9842 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10143.2029 | 10143.2029 | 0 | 8.5 | 0 | 1690.5338 | 33.81% | 1 | 67.62% | 0% | 0% | 0% | 33.1387 | 0 | 0 | 0 | 33.1387 | 0 | 9940.3388 | 1988.0678 | 19.88% | 1 | 39.76% | 0% | 0% | 4.8851 | 0 | 0 | 4.8851 | 38.0238
2007-08-16 14:00 | 8 | 16 | 14 | 228 | 5462 | 87.98 | 0 | 8826.6093 | 8826.6093 | -8826.6093 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10788.078 | 10788.078 | 0 | 8.5 | 0 | 1798.013 | 35.96% | 1 | 71.92% | 0% | 0% | 0% | 38.186 | 0 | 0 | 0 | 38.186 | 0 | 10572.3165 | 2114.4633 | 21.14% | 1 | 42.29% | 0% | 0% | 5.6291 | 0 | 0 | 5.6291 | 43.8152
2007-08-16 15:00 | 8 | 16 | 15 | 228 | 5463 | 86 | 0 | 9010.8996 | 9010.8996 | -9010.8996 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11013.3217 | 11013.3217 | 0 | 8.5 | 0 | 1835.5536 | 36.71% | 1 | 73.42% | 0% | 0% | 0% | 40.0447 | 0 | 0 | 0 | 40.0447 | 0 | 10793.0553 | 2158.6111 | 21.59% | 1 | 43.17% | 0% | 0% | 5.9031 | 0 | 0 | 5.9031 | 45.9479
2007-08-16 16:00 | 8 | 16 | 16 | 228 | 5464 | 87.08 | 0 | 8621.7441 | 8621.7441 | -8621.7441 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10537.6873 | 10537.6873 | 0 | 8.5 | 0 | 1756.2812 | 35.13% | 1 | 70.25% | 0% | 0% | 0% | 36.1782 | 0 | 0 | 0 | 36.1782 | 0 | 10326.9335 | 2065.3867 | 20.65% | 1 | 41.31% | 0% | 0% | 5.3332 | 0 | 0 | 5.3332 | 41.5114
2007-08-16 17:00 | 8 | 16 | 17 | 228 | 5465 | 87.08 | 0 | 7879.7828 | 7879.7828 | -7879.7828 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9630.8456 | 9630.8456 | 0 | 8.5 | 0 | 1605.1409 | 32.1% | 1 | 64.21% | 0% | 0% | 0% | 29.4145 | 0 | 0 | 0 | 29.4145 | 0 | 9438.2287 | 1887.6457 | 18.88% | 1 | 37.75% | 0% | 0% | 4.3361 | 0 | 0 | 4.3361 | 33.7506
2007-08-16 18:00 | 8 | 16 | 18 | 228 | 5466 | 80.96 | 0 | 4893.0201 | 4893.0201 | -4893.0201 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5980.3579 | 5980.3579 | 0 | 8.5 | 0 | 996.7263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5860.7507 | 1172.1501 | 11.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 19:00 | 8 | 16 | 19 | 228 | 5467 | 78.98 | 0 | 3871.2434 | 3871.2434 | -3871.2434 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4731.5198 | 4731.5198 | 0 | 8.5 | 0 | 788.5866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4636.8894 | 927.3779 | 9.274% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 20:00 | 8 | 16 | 20 | 228 | 5468 | 78.98 | 0 | 2448.7884 | 2448.7884 | -2448.7884 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2992.9636 | 2992.9636 | 0 | 8.5 | 0 | 498.8273 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2933.1043 | 586.6209 | 5.866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 21:00 | 8 | 16 | 21 | 228 | 5469 | 73.94 | 0 | 1116.4941 | 1116.4941 | -1116.4941 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1364.6039 | 1364.6039 | 0 | 8.5 | 0 | 227.434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1337.3118 | 267.4624 | 2.675% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 22:00 | 8 | 16 | 22 | 228 | 5470 | 73.94 | 0 | 206.9333 | 206.9333 | -206.9333 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 252.9185 | 252.9185 | 0 | 8.5 | 0 | 42.1531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 247.8601 | 49.572 | 0.4957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-16 23:00 | 8 | 16 | 23 | 228 | 5471 | 73.94 | 0 | 67.7432 | 67.7432 | -67.7432 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 82.7973 | 82.7973 | 0 | 8.5 | 0 | 13.7995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 81.1413 | 16.2283 | 0.1623% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 | 8 | 17 | 0 | 229 | 5472 | 73.04 | 0.17704 | 6.3641 | 6.3641 | -6.1871 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7.7784 | 7.7784 | 0 | 8.5 | 0 | 1.2964 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7.6228 | 1.5246 | 0.01525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 01:00 | 8 | 17 | 1 | 229 | 5473 | 71.06 | 6.6701 | 0 | 0 | 6.6701 | Heating | 5.8854 | 8.5 | 5.8854 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.0055 | 0 | 1.2011 | 0.01201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 02:00 | 8 | 17 | 2 | 229 | 5474 | 71.06 | 23.3219 | 0 | 0 | 23.3219 | Heating | 20.5782 | 8.5 | 20.5782 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.1156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.9981 | 0 | 4.1996 | 0.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 03:00 | 8 | 17 | 3 | 229 | 5475 | 69.08 | 35.7202 | 0 | 0 | 35.7202 | Heating | 31.5178 | 8.5 | 31.5178 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.3036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 32.161 | 0 | 6.4322 | 0.06432% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 04:00 | 8 | 17 | 4 | 229 | 5476 | 68 | 45.5884 | 0 | 0 | 45.5884 | Heating | 40.225 | 8.5 | 40.225 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.045 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 41.0459 | 0 | 8.2092 | 0.08209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 05:00 | 8 | 17 | 5 | 229 | 5477 | 68 | 59.8804 | 0 | 0 | 59.8804 | Heating | 52.8356 | 8.5 | 52.8356 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.5671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 53.9139 | 0 | 10.7828 | 0.1078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 06:00 | 8 | 17 | 6 | 229 | 5478 | 66.2 | 2834.3394 | 89.2366 | 89.2366 | 2745.1027 | Heating | 2422.1495 | 8.5 | 2422.1495 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 484.4299 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2471.5811 | 0 | 494.3162 | 4.943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 07:00 | 8 | 17 | 7 | 229 | 5479 | 71.96 | 1511.5715 | 80.4339 | 80.4339 | 1431.1376 | Heating | 1262.7685 | 8.5 | 1262.7685 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.5537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1288.5393 | 0 | 257.7079 | 2.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 08:00 | 8 | 17 | 8 | 229 | 5480 | 71.96 | 524.2609 | 266.1039 | 266.1039 | 258.157 | Heating | 227.7856 | 8.5 | 227.7856 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.5571 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 232.4343 | 0 | 46.4869 | 0.4649% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 09:00 | 8 | 17 | 9 | 229 | 5481 | 78.08 | 0 | 908.7717 | 908.7717 | -908.7717 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1110.721 | 1110.721 | 0 | 8.5 | 0 | 185.1202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1088.5065 | 217.7013 | 2.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 10:00 | 8 | 17 | 10 | 229 | 5482 | 82.94 | 0 | 1798.1689 | 1798.1689 | -1798.1689 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2197.762 | 2197.762 | 0 | 8.5 | 0 | 366.2937 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2153.8068 | 430.7614 | 4.308% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 11:00 | 8 | 17 | 11 | 229 | 5483 | 82.94 | 0 | 3668.8998 | 3668.8998 | -3668.8998 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4484.2109 | 4484.2109 | 0 | 8.5 | 0 | 747.3685 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4394.5267 | 878.9053 | 8.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 12:00 | 8 | 17 | 12 | 229 | 5484 | 87.08 | 0 | 4942.4504 | 4942.4504 | -4942.4504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6040.7727 | 6040.7727 | 0 | 8.5 | 0 | 1006.7954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5919.9572 | 1183.9914 | 11.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 13:00 | 8 | 17 | 13 | 229 | 5485 | 89.96 | 0 | 5572.0127 | 5572.0127 | -5572.0127 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6810.2378 | 6810.2378 | 0 | 8.5 | 0 | 1135.0396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6674.033 | 1334.8066 | 13.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 14:00 | 8 | 17 | 14 | 229 | 5486 | 89.96 | 0 | 5819.6225 | 5819.6225 | -5819.6225 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7112.872 | 7112.872 | 0 | 8.5 | 0 | 1185.4787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6970.6145 | 1394.1229 | 13.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 15:00 | 8 | 17 | 15 | 229 | 5487 | 91.04 | 0 | 6069.4727 | 6069.4727 | -6069.4727 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7418.2444 | 7418.2444 | 0 | 8.5 | 0 | 1236.3741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7269.8795 | 1453.9759 | 14.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 16:00 | 8 | 17 | 16 | 229 | 5488 | 91.04 | 0 | 6376.6486 | 6376.6486 | -6376.6486 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7793.6817 | 7793.6817 | 0 | 8.5 | 0 | 1298.9469 | 30% | 1 | 51.96% | 0% | 0% | 0% | 18.0776 | 0 | 0 | 0 | 18.0776 | 0 | 7637.808 | 1527.5616 | 15.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.3522
2007-08-17 17:00 | 8 | 17 | 17 | 229 | 5489 | 91.04 | 0 | 6156.1566 | 6156.1566 | -6156.1566 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7524.1914 | 7524.1914 | 0 | 8.5 | 0 | 1254.0319 | 30% | 1 | 50.16% | 0% | 0% | 0% | 16.6721 | 0 | 0 | 0 | 16.6721 | 0 | 7373.7076 | 1474.7415 | 14.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9467
2007-08-17 18:00 | 8 | 17 | 18 | 229 | 5490 | 86 | 0 | 3828.908 | 3828.908 | -3828.908 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4679.7764 | 4679.7764 | 0 | 8.5 | 0 | 779.9627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4586.1809 | 917.2362 | 9.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 19:00 | 8 | 17 | 19 | 229 | 5491 | 84.02 | 0 | 2673.6647 | 2673.6647 | -2673.6647 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3267.8124 | 3267.8124 | 0 | 8.5 | 0 | 544.6354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3202.4561 | 640.4912 | 6.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 20:00 | 8 | 17 | 20 | 229 | 5492 | 84.02 | 0 | 998.8343 | 998.8343 | -998.8343 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1220.7975 | 1220.7975 | 0 | 8.5 | 0 | 203.4663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1196.3816 | 239.2763 | 2.393% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 21:00 | 8 | 17 | 21 | 229 | 5493 | 78.98 | 0 | 249.8505 | 249.8505 | -249.8505 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 305.3729 | 305.3729 | 0 | 8.5 | 0 | 50.8955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 299.2654 | 59.8531 | 0.5985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 22:00 | 8 | 17 | 22 | 229 | 5494 | 77 | 0 | 89.6028 | 89.6028 | -89.6028 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 109.5145 | 109.5145 | 0 | 8.5 | 0 | 18.2524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 107.3243 | 21.4649 | 0.2146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-17 23:00 | 8 | 17 | 23 | 229 | 5495 | 77 | 0.19478 | 13.0226 | 13.0226 | -12.8278 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15.9165 | 15.9165 | 0 | 8.5 | 0 | 2.6527 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 15.5982 | 3.1196 | 0.0312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 | 8 | 18 | 0 | 230 | 5496 | 73.94 | 7.5477 | 0 | 0 | 7.5477 | Heating | 6.6597 | 8.5 | 6.6597 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.7957 | 0 | 1.3591 | 0.01359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 01:00 | 8 | 18 | 1 | 230 | 5497 | 73.04 | 19.3854 | 0 | 0 | 19.3854 | Heating | 17.1048 | 8.5 | 17.1048 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.421 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.4539 | 0 | 3.4908 | 0.03491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 02:00 | 8 | 18 | 2 | 230 | 5498 | 73.04 | 31.7388 | 0 | 0 | 31.7388 | Heating | 28.0048 | 8.5 | 28.0048 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 28.5764 | 0 | 5.7153 | 0.05715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 03:00 | 8 | 18 | 3 | 230 | 5499 | 73.94 | 43.5646 | 0 | 0 | 43.5646 | Heating | 38.4394 | 8.5 | 38.4394 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.6879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 39.2238 | 0 | 7.8448 | 0.07845% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 04:00 | 8 | 18 | 4 | 230 | 5500 | 71.96 | 58.2001 | 0 | 0 | 58.2001 | Heating | 51.353 | 8.5 | 51.353 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.2706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 52.401 | 0 | 10.4802 | 0.1048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 05:00 | 8 | 18 | 5 | 230 | 5501 | 71.96 | 74.1103 | 0 | 0 | 74.1103 | Heating | 65.3915 | 8.5 | 65.3915 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.0783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 66.726 | 0 | 13.3452 | 0.1335% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 06:00 | 8 | 18 | 6 | 230 | 5502 | 71.96 | 79.8744 | 0 | 0 | 79.8744 | Heating | 70.4774 | 8.5 | 70.4774 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.0955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 71.9157 | 0 | 14.3831 | 0.1438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 07:00 | 8 | 18 | 7 | 230 | 5503 | 73.94 | 49.1175 | 0 | 0 | 49.1175 | Heating | 43.3389 | 8.5 | 43.3389 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.6678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.2234 | 0 | 8.8447 | 0.08845% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 08:00 | 8 | 18 | 8 | 230 | 5504 | 73.94 | 2014.2541 | 0 | 0 | 2014.2541 | Heating | 1777.2831 | 8.5 | 1777.2831 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 355.4566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1813.5541 | 0 | 362.7108 | 3.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 09:00 | 8 | 18 | 9 | 230 | 5505 | 78.98 | 544.7988 | 0.36087 | 0.36087 | 544.4379 | Heating | 480.3864 | 8.5 | 480.3864 | 0 | 8.9059 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.0773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 490.1902 | 0 | 98.038 | 0.9804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 10:00 | 8 | 18 | 10 | 230 | 5506 | 82.04 | 0 | 270.573 | 270.573 | -270.573 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 330.7003 | 330.7003 | 0 | 8.5 | 0 | 55.1167 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 324.0863 | 64.8173 | 0.6482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 11:00 | 8 | 18 | 11 | 230 | 5507 | 82.04 | 0 | 645.3489 | 645.3489 | -645.3489 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 788.7597 | 788.7597 | 0 | 8.5 | 0 | 131.46 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 772.9846 | 154.5969 | 1.546% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 12:00 | 8 | 18 | 12 | 230 | 5508 | 86 | 0 | 2674.691 | 2674.691 | -2674.691 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3269.0668 | 3269.0668 | 0 | 8.5 | 0 | 544.8445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3203.6855 | 640.7371 | 6.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 13:00 | 8 | 18 | 13 | 230 | 5509 | 89.06 | 0 | 3548.9991 | 3548.9991 | -3548.9991 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4337.6656 | 4337.6656 | 0 | 8.5 | 0 | 722.9443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4250.9123 | 850.1825 | 8.502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 14:00 | 8 | 18 | 14 | 230 | 5510 | 89.06 | 0 | 3880.6554 | 3880.6554 | -3880.6554 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4743.0233 | 4743.0233 | 0 | 8.5 | 0 | 790.5039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4648.1628 | 929.6326 | 9.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 15:00 | 8 | 18 | 15 | 230 | 5511 | 89.96 | 0 | 3897.7003 | 3897.7003 | -3897.7003 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4763.8559 | 4763.8559 | 0 | 8.5 | 0 | 793.976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4668.5788 | 933.7158 | 9.337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 16:00 | 8 | 18 | 16 | 230 | 5512 | 89.6 | 0 | 3774.739 | 3774.739 | -3774.739 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4613.5699 | 4613.5699 | 0 | 8.5 | 0 | 768.9283 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4521.2985 | 904.2597 | 9.043% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 17:00 | 8 | 18 | 17 | 230 | 5513 | 87.98 | 0 | 3006.6039 | 3006.6039 | -3006.6039 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3674.7381 | 3674.7381 | 0 | 8.5 | 0 | 612.4564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3601.2433 | 720.2487 | 7.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 18:00 | 8 | 18 | 18 | 230 | 5514 | 87.8 | 0 | 1926.8929 | 1926.8929 | -1926.8929 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2355.0913 | 2355.0913 | 0 | 8.5 | 0 | 392.5152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2307.9895 | 461.5979 | 4.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 19:00 | 8 | 18 | 19 | 230 | 5515 | 80.96 | 0 | 828.0247 | 828.0247 | -828.0247 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1012.0302 | 1012.0302 | 0 | 8.5 | 0 | 168.6717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 991.7895 | 198.3579 | 1.984% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 20:00 | 8 | 18 | 20 | 230 | 5516 | 80.96 | 0 | 609.6325 | 609.6325 | -609.6325 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 745.1064 | 745.1064 | 0 | 8.5 | 0 | 124.1844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 730.2043 | 146.0409 | 1.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 21:00 | 8 | 18 | 21 | 230 | 5517 | 71.06 | 0 | 347.3959 | 347.3959 | -347.3959 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 424.595 | 424.595 | 0 | 8.5 | 0 | 70.7658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 416.1031 | 83.2206 | 0.8322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 22:00 | 8 | 18 | 22 | 230 | 5518 | 71.06 | 0 | 173.9876 | 173.9876 | -173.9876 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 212.6515 | 212.6515 | 0 | 8.5 | 0 | 35.4419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 208.3985 | 41.6797 | 0.4168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-18 23:00 | 8 | 18 | 23 | 230 | 5519 | 71.06 | 0 | 56.3156 | 56.3156 | -56.3156 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 68.8302 | 68.8302 | 0 | 8.5 | 0 | 11.4717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 67.4536 | 13.4907 | 0.1349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 | 8 | 19 | 0 | 231 | 5520 | 69.98 | 0 | 6.3609 | 6.3609 | -6.3609 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7.7744 | 7.7744 | 0 | 8.5 | 0 | 1.2957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7.6189 | 1.5238 | 0.01524% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 01:00 | 8 | 19 | 1 | 231 | 5521 | 69.98 | 4.1525 | 0 | 0 | 4.1525 | Heating | 3.664 | 8.5 | 3.664 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.7328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.7388 | 0 | 0.74775 | 0.007478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 02:00 | 8 | 19 | 2 | 231 | 5522 | 69.98 | 18.4718 | 0 | 0 | 18.4718 | Heating | 16.2987 | 8.5 | 16.2987 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.2597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.6313 | 0 | 3.3263 | 0.03326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 03:00 | 8 | 19 | 3 | 231 | 5523 | 68 | 33.4102 | 0 | 0 | 33.4102 | Heating | 29.4796 | 8.5 | 29.4796 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.8959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.0812 | 0 | 6.0162 | 0.06016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 04:00 | 8 | 19 | 4 | 231 | 5524 | 69.98 | 40.5839 | 0 | 0 | 40.5839 | Heating | 35.8093 | 8.5 | 35.8093 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.1619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 36.5401 | 0 | 7.308 | 0.07308% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 05:00 | 8 | 19 | 5 | 231 | 5525 | 69.98 | 34.6259 | 0 | 0 | 34.6259 | Heating | 30.5522 | 8.5 | 30.5522 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.1104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 31.1758 | 0 | 6.2352 | 0.06235% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 06:00 | 8 | 19 | 6 | 231 | 5526 | 68 | 1646.4346 | 250.1585 | 250.1585 | 1396.2761 | Heating | 1232.0083 | 8.5 | 1232.0083 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 246.4017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1257.1514 | 0 | 251.4303 | 2.514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 07:00 | 8 | 19 | 7 | 231 | 5527 | 71.06 | 1069.5943 | 165.9006 | 165.9006 | 903.6936 | Heating | 797.3767 | 8.5 | 797.3767 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 159.4753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 813.6497 | 0 | 162.7299 | 1.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 08:00 | 8 | 19 | 8 | 231 | 5528 | 71.06 | 158.2476 | 1810.742 | 1810.742 | -1652.4943 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2213.1291 | 2213.1291 | 0 | 8.5 | 0 | 368.8548 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2168.8665 | 433.7733 | 4.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 09:00 | 8 | 19 | 9 | 231 | 5529 | 75.2 | 0 | 3178.2763 | 3178.2763 | -3178.2763 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3884.5599 | 3884.5599 | 0 | 8.5 | 0 | 647.4267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3806.8687 | 761.3737 | 7.614% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 10:00 | 8 | 19 | 10 | 231 | 5530 | 77 | 0 | 3933.4207 | 3933.4207 | -3933.4207 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4807.5142 | 4807.5142 | 0 | 8.5 | 0 | 801.2524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4711.3639 | 942.2728 | 9.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 11:00 | 8 | 19 | 11 | 231 | 5531 | 77 | 0 | 6159.5486 | 6159.5486 | -6159.5486 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7528.3372 | 7528.3372 | 0 | 8.5 | 0 | 1254.7229 | 30% | 1 | 50.19% | 0% | 0% | 0% | 16.6933 | 0 | 0 | 0 | 16.6933 | 0 | 7377.7704 | 1475.5541 | 14.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9678
2007-08-19 12:00 | 8 | 19 | 12 | 231 | 5532 | 82.94 | 0 | 7445.2111 | 7445.2111 | -7445.2111 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9099.7024 | 9099.7024 | 0 | 8.5 | 0 | 1516.6171 | 30.33% | 1 | 60.66% | 0% | 0% | 0% | 25.8164 | 0 | 0 | 0 | 25.8164 | 0 | 8917.7084 | 1783.5417 | 17.84% | 1 | 35.67% | 0% | 0% | 3.8057 | 0 | 0 | 3.8057 | 29.6221
2007-08-19 13:00 | 8 | 19 | 13 | 231 | 5533 | 82.94 | 0 | 8831.3699 | 8831.3699 | -8831.3699 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10793.8965 | 10793.8965 | 0 | 8.5 | 0 | 1798.9828 | 35.98% | 1 | 71.96% | 0% | 0% | 0% | 38.2334 | 0 | 0 | 0 | 38.2334 | 0 | 10578.0186 | 2115.6037 | 21.16% | 1 | 42.31% | 0% | 0% | 5.6361 | 0 | 0 | 5.6361 | 43.8695
2007-08-19 14:00 | 8 | 19 | 14 | 231 | 5534 | 82.94 | 0 | 9834.8756 | 9834.8756 | -9834.8756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12020.4035 | 12020.4035 | 0 | 8.5 | 0 | 2003.4006 | 40.07% | 1 | 80.14% | 0% | 0% | 0% | 48.9719 | 0 | 0 | 0 | 48.9719 | 0 | 11779.9954 | 2355.9991 | 23.56% | 1 | 47.12% | 0% | 0% | 7.2191 | 0 | 0 | 7.2191 | 56.191
2007-08-19 15:00 | 8 | 19 | 15 | 231 | 5535 | 75.2 | 0 | 9516.3728 | 9516.3728 | -9516.3728 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11631.1223 | 11631.1223 | 0 | 8.5 | 0 | 1938.5204 | 38.77% | 1 | 77.54% | 0% | 0% | 0% | 45.4007 | 0 | 0 | 0 | 45.4007 | 0 | 11398.4999 | 2279.7 | 22.8% | 1 | 45.59% | 0% | 0% | 6.6927 | 0 | 0 | 6.6927 | 52.0934
2007-08-19 16:00 | 8 | 19 | 16 | 231 | 5536 | 75.2 | 0 | 8991.7695 | 8991.7695 | -8991.7695 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10989.9404 | 10989.9404 | 0 | 8.5 | 0 | 1831.6567 | 36.63% | 1 | 73.27% | 0% | 0% | 0% | 39.8495 | 0 | 0 | 0 | 39.8495 | 0 | 10770.1416 | 2154.0283 | 21.54% | 1 | 43.08% | 0% | 0% | 5.8744 | 0 | 0 | 5.8744 | 45.7238
2007-08-19 17:00 | 8 | 19 | 17 | 231 | 5537 | 78.08 | 0 | 8550.5565 | 8550.5565 | -8550.5565 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10450.6802 | 10450.6802 | 0 | 8.5 | 0 | 1741.78 | 34.84% | 1 | 69.67% | 0% | 0% | 0% | 35.4949 | 0 | 0 | 0 | 35.4949 | 0 | 10241.6666 | 2048.3333 | 20.48% | 1 | 40.97% | 0% | 0% | 5.2324 | 0 | 0 | 5.2324 | 40.7273
2007-08-19 18:00 | 8 | 19 | 18 | 231 | 5538 | 80.06 | 0 | 5565.4433 | 5565.4433 | -5565.4433 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6802.2084 | 6802.2084 | 0 | 8.5 | 0 | 1133.7014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6666.1643 | 1333.2329 | 13.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 19:00 | 8 | 19 | 19 | 231 | 5539 | 73.94 | 0 | 4558.6564 | 4558.6564 | -4558.6564 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5571.6912 | 5571.6912 | 0 | 8.5 | 0 | 928.6152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5460.2573 | 1092.0515 | 10.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 20:00 | 8 | 19 | 20 | 231 | 5540 | 73.94 | 0 | 3068.9467 | 3068.9467 | -3068.9467 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3750.9348 | 3750.9348 | 0 | 8.5 | 0 | 625.1558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3675.9161 | 735.1832 | 7.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 21:00 | 8 | 19 | 21 | 231 | 5541 | 71.06 | 0 | 1545.5383 | 1545.5383 | -1545.5383 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1888.9913 | 1888.9913 | 0 | 8.5 | 0 | 314.8319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1851.2115 | 370.2423 | 3.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 22:00 | 8 | 19 | 22 | 231 | 5542 | 69.98 | 0 | 320.8342 | 320.8342 | -320.8342 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 392.1307 | 392.1307 | 0 | 8.5 | 0 | 65.3551 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 384.2881 | 76.8576 | 0.7686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-19 23:00 | 8 | 19 | 23 | 231 | 5543 | 69.98 | 0 | 241.0418 | 241.0418 | -241.0418 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 294.6066 | 294.6066 | 0 | 8.5 | 0 | 49.1011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 288.7145 | 57.7429 | 0.5774% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 | 8 | 20 | 0 | 232 | 5544 | 68 | 0 | 144.4631 | 144.4631 | -144.4631 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 176.566 | 176.566 | 0 | 8.5 | 0 | 29.4277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 173.0347 | 34.6069 | 0.3461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 01:00 | 8 | 20 | 1 | 232 | 5545 | 66.02 | 0 | 95.8372 | 95.8372 | -95.8372 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 117.1344 | 117.1344 | 0 | 8.5 | 0 | 19.5224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 114.7917 | 22.9583 | 0.2296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 02:00 | 8 | 20 | 2 | 232 | 5546 | 66.02 | 0 | 55.0655 | 55.0655 | -55.0655 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 67.3023 | 67.3023 | 0 | 8.5 | 0 | 11.217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 65.9562 | 13.1912 | 0.1319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 03:00 | 8 | 20 | 3 | 232 | 5547 | 64.4 | 0 | 13.7359 | 13.7359 | -13.7359 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16.7884 | 16.7884 | 0 | 8.5 | 0 | 2.7981 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 16.4526 | 3.2905 | 0.03291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 04:00 | 8 | 20 | 4 | 232 | 5548 | 64.4 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-20 05:00 | 8 | 20 | 5 | 232 | 5549 | 64.04 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-20 06:00 | 8 | 20 | 6 | 232 | 5550 | 62.6 | 630.1852 | 528.1643 | 528.1643 | 102.0209 | Heating | 90.0185 | 8.5 | 90.0185 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.0037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 91.8556 | 0 | 18.3711 | 0.1837% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 07:00 | 8 | 20 | 7 | 232 | 5551 | 64.94 | 285.0181 | 492.768 | 492.768 | -207.75 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 602.272 | 602.272 | 0 | 8.5 | 0 | 100.3787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 590.2266 | 118.0453 | 1.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 08:00 | 8 | 20 | 8 | 232 | 5552 | 64.94 | 0 | 2589.6108 | 2589.6108 | -2589.6108 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3165.0799 | 3165.0799 | 0 | 8.5 | 0 | 527.5133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3101.7783 | 620.3557 | 6.204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 09:00 | 8 | 20 | 9 | 232 | 5553 | 73.04 | 0 | 3593.5055 | 3593.5055 | -3593.5055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4392.0623 | 4392.0623 | 0 | 8.5 | 0 | 732.0104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4304.2211 | 860.8442 | 8.608% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 10:00 | 8 | 20 | 10 | 232 | 5554 | 77 | 0 | 4870.5878 | 4870.5878 | -4870.5878 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5952.9407 | 5952.9407 | 0 | 8.5 | 0 | 992.1568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5833.8819 | 1166.7764 | 11.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 11:00 | 8 | 20 | 11 | 232 | 5555 | 77 | 0 | 6297.6482 | 6297.6482 | -6297.6482 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7697.1256 | 7697.1256 | 0 | 8.5 | 0 | 1282.8543 | 30% | 1 | 51.31% | 0% | 0% | 0% | 17.5666 | 0 | 0 | 0 | 17.5666 | 0 | 7543.1831 | 1508.6366 | 15.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.8412
2007-08-20 12:00 | 8 | 20 | 12 | 232 | 5556 | 82.94 | 0 | 7218.2723 | 7218.2723 | -7218.2723 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8822.3328 | 8822.3328 | 0 | 8.5 | 0 | 1470.3888 | 30% | 1 | 58.82% | 0% | 0% | 0% | 24.0422 | 0 | 0 | 0 | 24.0422 | 0 | 8645.8861 | 1729.1772 | 17.29% | 1 | 34.58% | 0% | 0% | 3.5442 | 0 | 0 | 3.5442 | 27.5864
2007-08-20 13:00 | 8 | 20 | 13 | 232 | 5557 | 82.94 | 0 | 7983.705 | 7983.705 | -7983.705 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9757.8617 | 9757.8617 | 0 | 8.5 | 0 | 1626.3103 | 32.53% | 1 | 65.05% | 0% | 0% | 0% | 30.3144 | 0 | 0 | 0 | 30.3144 | 0 | 9562.7045 | 1912.5409 | 19.13% | 1 | 38.25% | 0% | 0% | 4.4688 | 0 | 0 | 4.4688 | 34.7831
2007-08-20 14:00 | 8 | 20 | 14 | 232 | 5558 | 82.94 | 0 | 9104.0286 | 9104.0286 | -9104.0286 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11127.1461 | 11127.1461 | 0 | 8.5 | 0 | 1854.5243 | 37.09% | 1 | 74.18% | 0% | 0% | 0% | 41.003 | 0 | 0 | 0 | 41.003 | 0 | 10904.6032 | 2180.9206 | 21.81% | 1 | 43.62% | 0% | 0% | 6.0444 | 0 | 0 | 6.0444 | 47.0474
2007-08-20 15:00 | 8 | 20 | 15 | 232 | 5559 | 84.92 | 0 | 9499.8836 | 9499.8836 | -9499.8836 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11610.9688 | 11610.9688 | 0 | 8.5 | 0 | 1935.1615 | 38.7% | 1 | 77.41% | 0% | 0% | 0% | 45.22 | 0 | 0 | 0 | 45.22 | 0 | 11378.7495 | 2275.7499 | 22.76% | 1 | 45.51% | 0% | 0% | 6.666 | 0 | 0 | 6.666 | 51.8861
2007-08-20 16:00 | 8 | 20 | 16 | 232 | 5560 | 84.92 | 0 | 8797.8095 | 8797.8095 | -8797.8095 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10752.8783 | 10752.8783 | 0 | 8.5 | 0 | 1792.1464 | 35.84% | 1 | 71.69% | 0% | 0% | 0% | 37.9001 | 0 | 0 | 0 | 37.9001 | 0 | 10537.8207 | 2107.5641 | 21.08% | 1 | 42.15% | 0% | 0% | 5.587 | 0 | 0 | 5.587 | 43.4871
2007-08-20 17:00 | 8 | 20 | 17 | 232 | 5561 | 84.92 | 0 | 8088.9895 | 8088.9895 | -8088.9895 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9886.5428 | 9886.5428 | 0 | 8.5 | 0 | 1647.7571 | 32.96% | 1 | 65.91% | 0% | 0% | 0% | 31.2418 | 0 | 0 | 0 | 31.2418 | 0 | 9688.8119 | 1937.7624 | 19.38% | 1 | 38.76% | 0% | 0% | 4.6055 | 0 | 0 | 4.6055 | 35.8472
2007-08-20 18:00 | 8 | 20 | 18 | 232 | 5562 | 82.94 | 0 | 4787.5684 | 4787.5684 | -4787.5684 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5851.4724 | 5851.4724 | 0 | 8.5 | 0 | 975.2454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5734.443 | 1146.8886 | 11.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 19:00 | 8 | 20 | 19 | 232 | 5563 | 82.04 | 0 | 3697.5056 | 3697.5056 | -3697.5056 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4519.1735 | 4519.1735 | 0 | 8.5 | 0 | 753.1956 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4428.79 | 885.758 | 8.858% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 20:00 | 8 | 20 | 20 | 232 | 5564 | 82.04 | 0 | 2598.2635 | 2598.2635 | -2598.2635 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3175.6554 | 3175.6554 | 0 | 8.5 | 0 | 529.2759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3112.1423 | 622.4285 | 6.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 21:00 | 8 | 20 | 21 | 232 | 5565 | 80.96 | 0 | 841.6373 | 841.6373 | -841.6373 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1028.6679 | 1028.6679 | 0 | 8.5 | 0 | 171.4446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1008.0945 | 201.6189 | 2.016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 22:00 | 8 | 20 | 22 | 232 | 5566 | 78.98 | 0 | 119.0776 | 119.0776 | -119.0776 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 145.5392 | 145.5392 | 0 | 8.5 | 0 | 24.2565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 142.6285 | 28.5257 | 0.2853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-20 23:00 | 8 | 20 | 23 | 232 | 5567 | 78.98 | 0 | 59.9494 | 59.9494 | -59.9494 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 73.2715 | 73.2715 | 0 | 8.5 | 0 | 12.2119 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 71.806 | 14.3612 | 0.1436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 | 8 | 21 | 0 | 233 | 5568 | 78.08 | 0.28356 | 10.9317 | 10.9317 | -10.6481 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13.3609 | 13.3609 | 0 | 8.5 | 0 | 2.2268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.0937 | 2.6187 | 0.02619% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 01:00 | 8 | 21 | 1 | 233 | 5569 | 77 | 2.7905 | 0 | 0 | 2.7905 | Heating | 2.4622 | 8.5 | 2.4622 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.49245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.5125 | 0 | 0.5025 | 0.005025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 02:00 | 8 | 21 | 2 | 233 | 5570 | 77 | 4.8437 | 0 | 0 | 4.8437 | Heating | 4.2739 | 8.5 | 4.2739 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.85478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.3611 | 0 | 0.87222 | 0.008722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 03:00 | 8 | 21 | 3 | 233 | 5571 | 77 | 7.1917 | 0 | 0 | 7.1917 | Heating | 6.3456 | 8.5 | 6.3456 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.4751 | 0 | 1.295 | 0.01295% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 04:00 | 8 | 21 | 4 | 233 | 5572 | 77 | 7.0062 | 0 | 0 | 7.0062 | Heating | 6.1819 | 8.5 | 6.1819 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.3081 | 0 | 1.2616 | 0.01262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 05:00 | 8 | 21 | 5 | 233 | 5573 | 77 | 7.5582 | 0 | 0 | 7.5582 | Heating | 6.669 | 8.5 | 6.669 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.8051 | 0 | 1.361 | 0.01361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 06:00 | 8 | 21 | 6 | 233 | 5574 | 77 | 1184.1499 | 374.7042 | 374.7042 | 809.4457 | Heating | 714.2168 | 8.5 | 714.2168 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 142.8434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 728.7926 | 0 | 145.7585 | 1.458% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 07:00 | 8 | 21 | 7 | 233 | 5575 | 77 | 726.4262 | 368.9758 | 368.9758 | 357.4504 | Heating | 315.3974 | 8.5 | 315.3974 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.0795 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 321.8341 | 0 | 64.3668 | 0.6437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 08:00 | 8 | 21 | 8 | 233 | 5576 | 77 | 84.9422 | 2045.8097 | 2045.8097 | -1960.8675 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2500.4341 | 2500.4341 | 0 | 8.5 | 0 | 416.739 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2450.4255 | 490.0851 | 4.901% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 09:00 | 8 | 21 | 9 | 233 | 5577 | 78.08 | 0 | 3352.7742 | 3352.7742 | -3352.7742 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4097.8351 | 4097.8351 | 0 | 8.5 | 0 | 682.9725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4015.8784 | 803.1757 | 8.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 10:00 | 8 | 21 | 10 | 233 | 5578 | 80.06 | 0 | 4128.9408 | 4128.9408 | -4128.9408 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5046.4832 | 5046.4832 | 0 | 8.5 | 0 | 841.0805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4945.5535 | 989.1107 | 9.891% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 11:00 | 8 | 21 | 11 | 233 | 5579 | 80.06 | 0 | 5936.0352 | 5936.0352 | -5936.0352 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7255.1541 | 7255.1541 | 0 | 8.5 | 0 | 1209.1923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7110.051 | 1422.0102 | 14.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 12:00 | 8 | 21 | 12 | 233 | 5580 | 82.4 | 0 | 6709.6928 | 6709.6928 | -6709.6928 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8200.7356 | 8200.7356 | 0 | 8.5 | 0 | 1366.7893 | 30% | 1 | 54.67% | 0% | 0% | 0% | 20.3233 | 0 | 0 | 0 | 20.3233 | 0 | 8036.7209 | 1607.3442 | 16.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.5979
2007-08-21 13:00 | 8 | 21 | 13 | 233 | 5581 | 69.8 | 0 | 7348.2602 | 7348.2602 | -7348.2602 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8981.2069 | 8981.2069 | 0 | 8.5 | 0 | 1496.8678 | 30% | 1 | 59.87% | 0% | 0% | 0% | 25.0497 | 0 | 0 | 0 | 25.0497 | 0 | 8801.5828 | 1760.3166 | 17.6% | 1 | 35.21% | 0% | 0% | 3.6927 | 0 | 0 | 3.6927 | 28.7424
2007-08-21 14:00 | 8 | 21 | 14 | 233 | 5582 | 71.06 | 0 | 7646.6199 | 7646.6199 | -7646.6199 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9345.8687 | 9345.8687 | 0 | 8.5 | 0 | 1557.6448 | 31.15% | 1 | 62.31% | 0% | 0% | 0% | 27.451 | 0 | 0 | 0 | 27.451 | 0 | 9158.9513 | 1831.7903 | 18.32% | 1 | 36.64% | 0% | 0% | 4.0467 | 0 | 0 | 4.0467 | 31.4977
2007-08-21 15:00 | 8 | 21 | 15 | 233 | 5583 | 71.96 | 0 | 7330.608 | 7330.608 | -7330.608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8959.632 | 8959.632 | 0 | 8.5 | 0 | 1493.272 | 30% | 1 | 59.73% | 0% | 0% | 0% | 24.9115 | 0 | 0 | 0 | 24.9115 | 0 | 8780.4394 | 1756.0879 | 17.56% | 1 | 35.12% | 0% | 0% | 3.6723 | 0 | 0 | 3.6723 | 28.5838
2007-08-21 16:00 | 8 | 21 | 16 | 233 | 5584 | 71.96 | 0 | 6920.3778 | 6920.3778 | -6920.3778 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8458.2395 | 8458.2395 | 0 | 8.5 | 0 | 1409.7066 | 30% | 1 | 56.39% | 0% | 0% | 0% | 21.8211 | 0 | 0 | 0 | 21.8211 | 0 | 8289.0747 | 1657.8149 | 16.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.0957
2007-08-21 17:00 | 8 | 21 | 17 | 233 | 5585 | 71.96 | 0 | 6288.4859 | 6288.4859 | -6288.4859 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7685.9272 | 7685.9272 | 0 | 8.5 | 0 | 1280.9879 | 30% | 1 | 51.24% | 0% | 0% | 0% | 17.5079 | 0 | 0 | 0 | 17.5079 | 0 | 7532.2087 | 1506.4417 | 15.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7825
2007-08-21 18:00 | 8 | 21 | 18 | 233 | 5586 | 73.04 | 0 | 3743.7917 | 3743.7917 | -3743.7917 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4575.7455 | 4575.7455 | 0 | 8.5 | 0 | 762.6242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4484.2306 | 896.8461 | 8.968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 19:00 | 8 | 21 | 19 | 233 | 5587 | 73.04 | 0 | 2738.4078 | 2738.4078 | -2738.4078 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3346.9429 | 3346.9429 | 0 | 8.5 | 0 | 557.8238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3280.004 | 656.0008 | 6.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 20:00 | 8 | 21 | 20 | 233 | 5588 | 73.04 | 0 | 1572.2431 | 1572.2431 | -1572.2431 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1921.6305 | 1921.6305 | 0 | 8.5 | 0 | 320.2717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1883.1979 | 376.6396 | 3.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 21:00 | 8 | 21 | 21 | 233 | 5589 | 71.6 | 0 | 839.31 | 839.31 | -839.31 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1025.8233 | 1025.8233 | 0 | 8.5 | 0 | 170.9706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1005.3069 | 201.0614 | 2.011% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 22:00 | 8 | 21 | 22 | 233 | 5590 | 73.4 | 0 | 129.7608 | 129.7608 | -129.7608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 158.5966 | 158.5966 | 0 | 8.5 | 0 | 26.4328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 155.4246 | 31.0849 | 0.3108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-21 23:00 | 8 | 21 | 23 | 233 | 5591 | 71.96 | 0 | 43.8227 | 43.8227 | -43.8227 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 53.5611 | 53.5611 | 0 | 8.5 | 0 | 8.9269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 52.4899 | 10.498 | 0.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 | 8 | 22 | 0 | 234 | 5592 | 71.6 | 0 | 9.2811 | 9.2811 | -9.2811 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11.3435 | 11.3435 | 0 | 8.5 | 0 | 1.8906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 11.1167 | 2.2233 | 0.02223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 01:00 | 8 | 22 | 1 | 234 | 5593 | 71.6 | 0 | 0.67821 | 0.67821 | -0.67821 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.82892 | 0.82892 | 0 | 8.5 | 0 | 0.13815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.81234 | 0.16247 | 0.001625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 02:00 | 8 | 22 | 2 | 234 | 5594 | 71.96 | 0.4619 | 0 | 0 | 0.4619 | Heating | 0.40756 | 8.5 | 0.40756 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.081511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.41587 | 0 | 0.083175 | 0.0008317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 03:00 | 8 | 22 | 3 | 234 | 5595 | 71.6 | 3.7238 | 0 | 0 | 3.7238 | Heating | 3.2857 | 8.5 | 3.2857 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.65714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.3528 | 0 | 0.67055 | 0.006706% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 04:00 | 8 | 22 | 4 | 234 | 5596 | 71.6 | 5.9112 | 0 | 0 | 5.9112 | Heating | 5.2158 | 8.5 | 5.2158 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.0432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.3222 | 0 | 1.0644 | 0.01064% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 05:00 | 8 | 22 | 5 | 234 | 5597 | 71.06 | 6.2247 | 0 | 0 | 6.2247 | Heating | 5.4923 | 8.5 | 5.4923 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.0985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.6044 | 0 | 1.1209 | 0.01121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 06:00 | 8 | 22 | 6 | 234 | 5598 | 69.8 | 1004.8876 | 332.3253 | 332.3253 | 672.5623 | Heating | 593.4373 | 8.5 | 593.4373 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.6875 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 605.5483 | 0 | 121.1097 | 1.211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 07:00 | 8 | 22 | 7 | 234 | 5599 | 71.06 | 618.0049 | 247.3446 | 247.3446 | 370.6603 | Heating | 327.0532 | 8.5 | 327.0532 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.4106 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 333.7278 | 0 | 66.7456 | 0.6675% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 08:00 | 8 | 22 | 8 | 234 | 5600 | 71.06 | 95.7833 | 1670.2316 | 1670.2316 | -1574.4484 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2041.3942 | 2041.3942 | 0 | 8.5 | 0 | 340.2324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2000.5663 | 400.1133 | 4.001% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 09:00 | 8 | 22 | 9 | 234 | 5601 | 71.96 | 0.13888 | 2555.0631 | 2555.0631 | -2554.9242 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3122.8549 | 3122.8549 | 0 | 8.5 | 0 | 520.4758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3060.3978 | 612.0796 | 6.121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 10:00 | 8 | 22 | 10 | 234 | 5602 | 73.04 | 0 | 3192.719 | 3192.719 | -3192.719 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3902.2122 | 3902.2122 | 0 | 8.5 | 0 | 650.3687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3824.1679 | 764.8336 | 7.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 11:00 | 8 | 22 | 11 | 234 | 5603 | 73.04 | 0 | 4681.9504 | 4681.9504 | -4681.9504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5722.3838 | 5722.3838 | 0 | 8.5 | 0 | 953.7306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5607.9361 | 1121.5872 | 11.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 12:00 | 8 | 22 | 12 | 234 | 5604 | 73.04 | 0 | 6293.1011 | 6293.1011 | -6293.1011 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7691.5681 | 7691.5681 | 0 | 8.5 | 0 | 1281.928 | 30% | 1 | 51.28% | 0% | 0% | 0% | 17.5375 | 0 | 0 | 0 | 17.5375 | 0 | 7537.7367 | 1507.5473 | 15.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.812
2007-08-22 13:00 | 8 | 22 | 13 | 234 | 5605 | 73.4 | 0 | 6614.231 | 6614.231 | -6614.231 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8084.0602 | 8084.0602 | 0 | 8.5 | 0 | 1347.3434 | 30% | 1 | 53.89% | 0% | 0% | 0% | 19.6644 | 0 | 0 | 0 | 19.6644 | 0 | 7922.379 | 1584.4758 | 15.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.939
2007-08-22 14:00 | 8 | 22 | 14 | 234 | 5606 | 73.94 | 0 | 6899.7436 | 6899.7436 | -6899.7436 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8433.0199 | 8433.0199 | 0 | 8.5 | 0 | 1405.5033 | 30% | 1 | 56.22% | 0% | 0% | 0% | 21.6718 | 0 | 0 | 0 | 21.6718 | 0 | 8264.3595 | 1652.8719 | 16.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.9463
2007-08-22 15:00 | 8 | 22 | 15 | 234 | 5607 | 78.98 | 0 | 6675.603 | 6675.603 | -6675.603 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8159.0703 | 8159.0703 | 0 | 8.5 | 0 | 1359.8451 | 30% | 1 | 54.39% | 0% | 0% | 0% | 20.0866 | 0 | 0 | 0 | 20.0866 | 0 | 7995.8889 | 1599.1778 | 15.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.3612
2007-08-22 16:00 | 8 | 22 | 16 | 234 | 5608 | 78.8 | 0 | 6236.7176 | 6236.7176 | -6236.7176 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7622.6549 | 7622.6549 | 0 | 8.5 | 0 | 1270.4425 | 30% | 1 | 50.82% | 0% | 0% | 0% | 17.1782 | 0 | 0 | 0 | 17.1782 | 0 | 7470.2018 | 1494.0404 | 14.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.4527
2007-08-22 17:00 | 8 | 22 | 17 | 234 | 5609 | 78.08 | 0 | 5822.2787 | 5822.2787 | -5822.2787 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7116.1184 | 7116.1184 | 0 | 8.5 | 0 | 1186.0197 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6973.7961 | 1394.7592 | 13.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 18:00 | 8 | 22 | 18 | 234 | 5610 | 78.08 | 0 | 3445.2544 | 3445.2544 | -3445.2544 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4210.8665 | 4210.8665 | 0 | 8.5 | 0 | 701.8111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4126.6492 | 825.3298 | 8.253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 19:00 | 8 | 22 | 19 | 234 | 5611 | 77 | 0 | 2200.644 | 2200.644 | -2200.644 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2689.676 | 2689.676 | 0 | 8.5 | 0 | 448.2793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2635.8825 | 527.1765 | 5.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 20:00 | 8 | 22 | 20 | 234 | 5612 | 73.04 | 0 | 1095.9809 | 1095.9809 | -1095.9809 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1339.5322 | 1339.5322 | 0 | 8.5 | 0 | 223.2554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1312.7415 | 262.5483 | 2.625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 21:00 | 8 | 22 | 21 | 234 | 5613 | 71.96 | 0 | 474.5358 | 474.5358 | -474.5358 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 579.9882 | 579.9882 | 0 | 8.5 | 0 | 96.6647 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 568.3885 | 113.6777 | 1.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 22:00 | 8 | 22 | 22 | 234 | 5614 | 71.06 | 0 | 65.328 | 65.328 | -65.328 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 79.8454 | 79.8454 | 0 | 8.5 | 0 | 13.3076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 78.2485 | 15.6497 | 0.1565% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-22 23:00 | 8 | 22 | 23 | 234 | 5615 | 71.06 | 0 | 25.9251 | 25.9251 | -25.9251 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 31.6862 | 31.6862 | 0 | 8.5 | 0 | 5.281 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 31.0525 | 6.2105 | 0.06211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 | 8 | 23 | 0 | 235 | 5616 | 71.6 | 0.13627 | 2.0844 | 2.0844 | -1.9482 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.5476 | 2.5476 | 0 | 8.5 | 0 | 0.42461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.4967 | 0.49934 | 0.004993% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 01:00 | 8 | 23 | 1 | 235 | 5617 | 71.6 | 6.9734 | 0 | 0 | 6.9734 | Heating | 6.153 | 8.5 | 6.153 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.2785 | 0 | 1.2557 | 0.01256% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 02:00 | 8 | 23 | 2 | 235 | 5618 | 71.06 | 20.0966 | 0 | 0 | 20.0966 | Heating | 17.7323 | 8.5 | 17.7323 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.5465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.0942 | 0 | 3.6188 | 0.03619% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 03:00 | 8 | 23 | 3 | 235 | 5619 | 71.6 | 38.6255 | 0 | 0 | 38.6255 | Heating | 34.0813 | 8.5 | 34.0813 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.8163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.7768 | 0 | 6.9554 | 0.06955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 04:00 | 8 | 23 | 4 | 235 | 5620 | 71.6 | 62.7866 | 0 | 0 | 62.7866 | Heating | 55.3999 | 8.5 | 55.3999 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.08 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.5305 | 0 | 11.3061 | 0.1131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 05:00 | 8 | 23 | 5 | 235 | 5621 | 71.06 | 110.0054 | 0 | 0 | 110.0054 | Heating | 97.0636 | 8.5 | 97.0636 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.4127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 99.0444 | 0 | 19.8089 | 0.1981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 06:00 | 8 | 23 | 6 | 235 | 5622 | 71.06 | 3404.0357 | 147.989 | 147.989 | 3256.0467 | Heating | 2872.9824 | 8.5 | 2872.9824 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 574.5965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2931.6146 | 0 | 586.3229 | 5.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 07:00 | 8 | 23 | 7 | 235 | 5623 | 71.6 | 1842.1369 | 89.3002 | 89.3002 | 1752.8367 | Heating | 1546.6206 | 8.5 | 1546.6206 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 309.3241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1578.1843 | 0 | 315.6369 | 3.156% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 08:00 | 8 | 23 | 8 | 235 | 5624 | 69.98 | 697.9031 | 813.2884 | 813.2884 | -115.3853 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 994.0192 | 994.0192 | 0 | 8.5 | 0 | 165.6699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 974.1388 | 194.8278 | 1.948% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 09:00 | 8 | 23 | 9 | 235 | 5625 | 71.96 | 5.9411 | 1957.9994 | 1957.9994 | -1952.0583 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2393.1103 | 2393.1103 | 0 | 8.5 | 0 | 398.8517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2345.2481 | 469.0496 | 4.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 10:00 | 8 | 23 | 10 | 235 | 5626 | 75.02 | 0.022232 | 3197.7223 | 3197.7223 | -3197.7001 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3908.3273 | 3908.3273 | 0 | 8.5 | 0 | 651.3879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3830.1607 | 766.0321 | 7.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 11:00 | 8 | 23 | 11 | 235 | 5627 | 75.02 | 0 | 5238.6168 | 5238.6168 | -5238.6168 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6402.7539 | 6402.7539 | 0 | 8.5 | 0 | 1067.1257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6274.6988 | 1254.9398 | 12.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 12:00 | 8 | 23 | 12 | 235 | 5628 | 75.92 | 0 | 6198.9346 | 6198.9346 | -6198.9346 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7576.4756 | 7576.4756 | 0 | 8.5 | 0 | 1262.7459 | 30% | 1 | 50.51% | 0% | 0% | 0% | 16.9398 | 0 | 0 | 0 | 16.9398 | 0 | 7424.9461 | 1484.9892 | 14.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.2143
2007-08-23 13:00 | 8 | 23 | 13 | 235 | 5629 | 77 | 0 | 7088.2693 | 7088.2693 | -7088.2693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8663.4402 | 8663.4402 | 0 | 8.5 | 0 | 1443.9067 | 30% | 1 | 57.76% | 0% | 0% | 0% | 23.058 | 0 | 0 | 0 | 23.058 | 0 | 8490.1714 | 1698.0343 | 16.98% | 1 | 33.96% | 0% | 0% | 3.3991 | 0 | 0 | 3.3991 | 26.457
2007-08-23 14:00 | 8 | 23 | 14 | 235 | 5630 | 77 | 0 | 7797.384 | 7797.384 | -7797.384 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9530.136 | 9530.136 | 0 | 8.5 | 0 | 1588.356 | 31.77% | 1 | 63.53% | 0% | 0% | 0% | 28.7118 | 0 | 0 | 0 | 28.7118 | 0 | 9339.5333 | 1867.9067 | 18.68% | 1 | 37.36% | 0% | 0% | 4.2325 | 0 | 0 | 4.2325 | 32.9444
2007-08-23 15:00 | 8 | 23 | 15 | 235 | 5631 | 80.6 | 0 | 8067.251 | 8067.251 | -8067.251 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9859.9735 | 9859.9735 | 0 | 8.5 | 0 | 1643.3289 | 32.87% | 1 | 65.73% | 0% | 0% | 0% | 31.049 | 0 | 0 | 0 | 31.049 | 0 | 9662.774 | 1932.5548 | 19.33% | 1 | 38.65% | 0% | 0% | 4.577 | 0 | 0 | 4.577 | 35.626
2007-08-23 16:00 | 8 | 23 | 16 | 235 | 5632 | 78.98 | 0 | 7527.0693 | 7527.0693 | -7527.0693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9199.7513 | 9199.7513 | 0 | 8.5 | 0 | 1533.2919 | 30.67% | 1 | 61.33% | 0% | 0% | 0% | 26.4739 | 0 | 0 | 0 | 26.4739 | 0 | 9015.7563 | 1803.1513 | 18.03% | 1 | 36.06% | 0% | 0% | 3.9026 | 0 | 0 | 3.9026 | 30.3765
2007-08-23 17:00 | 8 | 23 | 17 | 235 | 5633 | 78.98 | 0 | 6621.8178 | 6621.8178 | -6621.8178 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8093.3329 | 8093.3329 | 0 | 8.5 | 0 | 1348.8888 | 30% | 1 | 53.96% | 0% | 0% | 0% | 19.7163 | 0 | 0 | 0 | 19.7163 | 0 | 7931.4662 | 1586.2932 | 15.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.9909
2007-08-23 18:00 | 8 | 23 | 18 | 235 | 5634 | 77 | 0 | 4078.7479 | 4078.7479 | -4078.7479 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4985.1364 | 4985.1364 | 0 | 8.5 | 0 | 830.8561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4885.4336 | 977.0867 | 9.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 19:00 | 8 | 23 | 19 | 235 | 5635 | 71.06 | 0 | 2392.8213 | 2392.8213 | -2392.8213 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2924.5594 | 2924.5594 | 0 | 8.5 | 0 | 487.4266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2866.0682 | 573.2136 | 5.732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 20:00 | 8 | 23 | 20 | 235 | 5636 | 71.06 | 0 | 644.9124 | 644.9124 | -644.9124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 788.2263 | 788.2263 | 0 | 8.5 | 0 | 131.3711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 772.4618 | 154.4924 | 1.545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 21:00 | 8 | 23 | 21 | 235 | 5637 | 69.8 | 0 | 377.0997 | 377.0997 | -377.0997 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 460.8997 | 460.8997 | 0 | 8.5 | 0 | 76.8166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 451.6817 | 90.3363 | 0.9034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 22:00 | 8 | 23 | 22 | 235 | 5638 | 68 | 2.3308 | 1.5351 | 1.5351 | 0.79572 | Heating | 0.70211 | 8.5 | 0.70211 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.14042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.71644 | 0 | 0.14329 | 0.001433% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-23 23:00 | 8 | 23 | 23 | 235 | 5639 | 68 | 13.6196 | 0 | 0 | 13.6196 | Heating | 12.0173 | 8.5 | 12.0173 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.4035 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.2626 | 0 | 2.4525 | 0.02453% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 | 8 | 24 | 0 | 236 | 5640 | 66.2 | 29.3716 | 0 | 0 | 29.3716 | Heating | 25.9161 | 8.5 | 25.9161 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.1832 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 26.445 | 0 | 5.289 | 0.05289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 01:00 | 8 | 24 | 1 | 236 | 5641 | 66.2 | 45.4138 | 0 | 0 | 45.4138 | Heating | 40.071 | 8.5 | 40.071 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.0142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.8887 | 0 | 8.1777 | 0.08178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 02:00 | 8 | 24 | 2 | 236 | 5642 | 66.02 | 66.3318 | 0 | 0 | 66.3318 | Heating | 58.5281 | 8.5 | 58.5281 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.7056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 59.7225 | 0 | 11.9445 | 0.1194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 03:00 | 8 | 24 | 3 | 236 | 5643 | 66.2 | 93.1912 | 0 | 0 | 93.1912 | Heating | 82.2275 | 8.5 | 82.2275 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.4455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.9057 | 0 | 16.7811 | 0.1678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 04:00 | 8 | 24 | 4 | 236 | 5644 | 66.2 | 116.668 | 0 | 0 | 116.668 | Heating | 102.9423 | 8.5 | 102.9423 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.5885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 105.0432 | 0 | 21.0086 | 0.2101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 05:00 | 8 | 24 | 5 | 236 | 5645 | 64.94 | 164.0572 | 0 | 0 | 164.0572 | Heating | 144.7564 | 8.5 | 144.7564 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.9513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 147.7106 | 0 | 29.5421 | 0.2954% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 06:00 | 8 | 24 | 6 | 236 | 5646 | 66.2 | 3504.8118 | 64.2617 | 64.2617 | 3440.5501 | Heating | 3035.7795 | 8.5 | 3035.7795 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 607.1559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3097.7342 | 0 | 619.5468 | 6.195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 07:00 | 8 | 24 | 7 | 236 | 5647 | 66.2 | 2034.7219 | 1.5561 | 1.5561 | 2033.1657 | Heating | 1793.9697 | 8.5 | 1793.9697 | 0 | 6.5112 | 0 | 0 | 0 | 0 | 8.5 | 0 | 358.7939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1830.5814 | 0 | 366.1163 | 3.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 08:00 | 8 | 24 | 8 | 236 | 5648 | 69.08 | 1033.7144 | 70.8499 | 70.8499 | 962.8645 | Heating | 849.5864 | 8.5 | 849.5864 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.9173 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 866.9249 | 0 | 173.385 | 1.734% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 09:00 | 8 | 24 | 9 | 236 | 5649 | 71.6 | 80.0763 | 134.274 | 134.274 | -54.1978 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 164.1127 | 164.1127 | 0 | 8.5 | 0 | 27.3521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 160.8305 | 32.1661 | 0.3217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 10:00 | 8 | 24 | 10 | 236 | 5650 | 73.4 | 1.1179 | 323.2737 | 323.2737 | -322.1558 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 395.1123 | 395.1123 | 0 | 8.5 | 0 | 65.8521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 387.2101 | 77.442 | 0.7744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 11:00 | 8 | 24 | 11 | 236 | 5651 | 75.02 | 0 | 639.5029 | 639.5029 | -639.5029 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 781.6147 | 781.6147 | 0 | 8.5 | 0 | 130.2691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 765.9824 | 153.1965 | 1.532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 12:00 | 8 | 24 | 12 | 236 | 5652 | 78.08 | 0 | 1484.7807 | 1484.7807 | -1484.7807 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1814.7319 | 1814.7319 | 0 | 8.5 | 0 | 302.4553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1778.4373 | 355.6875 | 3.557% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 13:00 | 8 | 24 | 13 | 236 | 5653 | 78.98 | 0 | 2545.9844 | 2545.9844 | -2545.9844 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3111.7587 | 3111.7587 | 0 | 8.5 | 0 | 518.6265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3049.5236 | 609.9047 | 6.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 14:00 | 8 | 24 | 14 | 236 | 5654 | 78.98 | 0 | 2870.3166 | 2870.3166 | -2870.3166 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3508.1648 | 3508.1648 | 0 | 8.5 | 0 | 584.6941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3438.0015 | 687.6003 | 6.876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 15:00 | 8 | 24 | 15 | 236 | 5655 | 80.96 | 0 | 3159.0414 | 3159.0414 | -3159.0414 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3861.0507 | 3861.0507 | 0 | 8.5 | 0 | 643.5084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3783.8296 | 756.7659 | 7.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 16:00 | 8 | 24 | 16 | 236 | 5656 | 80.06 | 0 | 3345.681 | 3345.681 | -3345.681 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4089.1657 | 4089.1657 | 0 | 8.5 | 0 | 681.5276 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4007.3824 | 801.4765 | 8.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 17:00 | 8 | 24 | 17 | 236 | 5657 | 80.06 | 0 | 2392.0955 | 2392.0955 | -2392.0955 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2923.6723 | 2923.6723 | 0 | 8.5 | 0 | 487.2787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2865.1989 | 573.0398 | 5.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 18:00 | 8 | 24 | 18 | 236 | 5658 | 75.92 | 0 | 501.1962 | 501.1962 | -501.1962 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 612.5731 | 612.5731 | 0 | 8.5 | 0 | 102.0955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 600.3217 | 120.0643 | 1.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 19:00 | 8 | 24 | 19 | 236 | 5659 | 71.96 | 0 | 22.8027 | 22.8027 | -22.8027 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 27.8699 | 27.8699 | 0 | 8.5 | 0 | 4.645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 27.3125 | 5.4625 | 0.05463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 20:00 | 8 | 24 | 20 | 236 | 5660 | 71.96 | 0 | 3.7454 | 3.7454 | -3.7454 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4.5777 | 4.5777 | 0 | 8.5 | 0 | 0.76295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4.4861 | 0.89722 | 0.008972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 21:00 | 8 | 24 | 21 | 236 | 5661 | 69.98 | 0 | 12.7261 | 12.7261 | -12.7261 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15.5542 | 15.5542 | 0 | 8.5 | 0 | 2.5924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 15.2431 | 3.0486 | 0.03049% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 22:00 | 8 | 24 | 22 | 236 | 5662 | 69.08 | 0 | 21.7227 | 21.7227 | -21.7227 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 26.5499 | 26.5499 | 0 | 8.5 | 0 | 4.425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 26.0189 | 5.2038 | 0.05204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-24 23:00 | 8 | 24 | 23 | 236 | 5663 | 69.08 | 0 | 11.683 | 11.683 | -11.683 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14.2793 | 14.2793 | 0 | 8.5 | 0 | 2.3799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.9937 | 2.7987 | 0.02799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 | 8 | 25 | 0 | 237 | 5664 | 66.92 | 0 | 0.49135 | 0.49135 | -0.49135 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.60054 | 0.60054 | 0 | 8.5 | 0 | 0.10009 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.58853 | 0.11771 | 0.001177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 01:00 | 8 | 25 | 1 | 237 | 5665 | 68 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-25 02:00 | 8 | 25 | 2 | 237 | 5666 | 68 | 3.9303 | 0 | 0 | 3.9303 | Heating | 3.4679 | 8.5 | 3.4679 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.69359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.5387 | 0 | 0.70774 | 0.007077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 03:00 | 8 | 25 | 3 | 237 | 5667 | 66.02 | 6.5884 | 0 | 0 | 6.5884 | Heating | 5.8133 | 8.5 | 5.8133 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.1627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.9319 | 0 | 1.1864 | 0.01186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 04:00 | 8 | 25 | 4 | 237 | 5668 | 64.94 | 8.0259 | 0 | 0 | 8.0259 | Heating | 7.0817 | 8.5 | 7.0817 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.2262 | 0 | 1.4452 | 0.01445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 05:00 | 8 | 25 | 5 | 237 | 5669 | 64.94 | 7.7442 | 0 | 0 | 7.7442 | Heating | 6.8331 | 8.5 | 6.8331 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.3666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.9725 | 0 | 1.3945 | 0.01395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 06:00 | 8 | 25 | 6 | 237 | 5670 | 64.04 | 10.9921 | 0 | 0 | 10.9921 | Heating | 9.6989 | 8.5 | 9.6989 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.9398 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.8968 | 0 | 1.9794 | 0.01979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 07:00 | 8 | 25 | 7 | 237 | 5671 | 66.02 | 14.6065 | 0 | 0 | 14.6065 | Heating | 12.8881 | 8.5 | 12.8881 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.1512 | 0 | 2.6302 | 0.0263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 08:00 | 8 | 25 | 8 | 237 | 5672 | 66.02 | 1425.385 | 0 | 0 | 1425.385 | Heating | 1257.6926 | 8.5 | 1257.6926 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.5385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1283.3598 | 0 | 256.672 | 2.567% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 09:00 | 8 | 25 | 9 | 237 | 5673 | 69.98 | 814.8872 | 0 | 0 | 814.8872 | Heating | 719.0181 | 8.5 | 719.0181 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 143.8036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 733.692 | 0 | 146.7384 | 1.467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 10:00 | 8 | 25 | 10 | 237 | 5674 | 73.04 | 330.1649 | 0 | 0 | 330.1649 | Heating | 291.322 | 8.5 | 291.322 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.2644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 297.2673 | 0 | 59.4535 | 0.5945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 11:00 | 8 | 25 | 11 | 237 | 5675 | 73.04 | 39.5939 | 0 | 0 | 39.5939 | Heating | 34.9358 | 8.5 | 34.9358 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.9872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.6488 | 0 | 7.1298 | 0.0713% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 12:00 | 8 | 25 | 12 | 237 | 5676 | 75.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-25 13:00 | 8 | 25 | 13 | 237 | 5677 | 78.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-25 14:00 | 8 | 25 | 14 | 237 | 5678 | 78.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-25 15:00 | 8 | 25 | 15 | 237 | 5679 | 80.06 | 0 | 122.7328 | 122.7328 | -122.7328 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 150.0067 | 150.0067 | 0 | 8.5 | 0 | 25.0011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 147.0066 | 29.4013 | 0.294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 16:00 | 8 | 25 | 16 | 237 | 5680 | 80.06 | 0 | 1001.3126 | 1001.3126 | -1001.3126 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1223.8266 | 1223.8266 | 0 | 8.5 | 0 | 203.9711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1199.35 | 239.87 | 2.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 17:00 | 8 | 25 | 17 | 237 | 5681 | 80.06 | 0 | 234.2973 | 234.2973 | -234.2973 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 286.3634 | 286.3634 | 0 | 8.5 | 0 | 47.7272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 280.6361 | 56.1272 | 0.5613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 18:00 | 8 | 25 | 18 | 237 | 5682 | 77 | 0 | 143.8576 | 143.8576 | -143.8576 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 175.826 | 175.826 | 0 | 8.5 | 0 | 29.3043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 172.3095 | 34.4619 | 0.3446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 19:00 | 8 | 25 | 19 | 237 | 5683 | 75.02 | 0 | 98.6048 | 98.6048 | -98.6048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 120.517 | 120.517 | 0 | 8.5 | 0 | 20.0862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 118.1067 | 23.6213 | 0.2362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 20:00 | 8 | 25 | 20 | 237 | 5684 | 75.02 | 0 | 71.7812 | 71.7812 | -71.7812 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 87.7326 | 87.7326 | 0 | 8.5 | 0 | 14.6221 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 85.978 | 17.1956 | 0.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 21:00 | 8 | 25 | 21 | 237 | 5685 | 69.98 | 0 | 59.5235 | 59.5235 | -59.5235 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 72.7509 | 72.7509 | 0 | 8.5 | 0 | 12.1251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 71.2959 | 14.2592 | 0.1426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 22:00 | 8 | 25 | 22 | 237 | 5686 | 68 | 0 | 21.4603 | 21.4603 | -21.4603 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 26.2293 | 26.2293 | 0 | 8.5 | 0 | 4.3716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 25.7047 | 5.1409 | 0.05141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-25 23:00 | 8 | 25 | 23 | 237 | 5687 | 68 | 0 | 1.2229 | 1.2229 | -1.2229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.4946 | 1.4946 | 0 | 8.5 | 0 | 0.24911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.4647 | 0.29295 | 0.002929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 | 8 | 26 | 0 | 238 | 5688 | 66.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-26 01:00 | 8 | 26 | 1 | 238 | 5689 | 68 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-08-26 02:00 | 8 | 26 | 2 | 238 | 5690 | 68 | 0.37072 | 0 | 0 | 0.37072 | Heating | 0.32711 | 8.5 | 0.32711 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.065422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.33379 | 0 | 0.066757 | 0.0006676% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 03:00 | 8 | 26 | 3 | 238 | 5691 | 64.94 | 1.5011 | 0 | 0 | 1.5011 | Heating | 1.3245 | 8.5 | 1.3245 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.2649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.3515 | 0 | 0.27031 | 0.002703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 04:00 | 8 | 26 | 4 | 238 | 5692 | 64.94 | 2.0864 | 0 | 0 | 2.0864 | Heating | 1.8409 | 8.5 | 1.8409 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.36818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.8785 | 0 | 0.3757 | 0.003757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 05:00 | 8 | 26 | 5 | 238 | 5693 | 64.94 | 1.6828 | 0 | 0 | 1.6828 | Heating | 1.4849 | 8.5 | 1.4849 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.29697 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.5152 | 0 | 0.30303 | 0.00303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 06:00 | 8 | 26 | 6 | 238 | 5694 | 64.04 | 740.4839 | 387.2192 | 387.2192 | 353.2648 | Heating | 311.7042 | 8.5 | 311.7042 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.3408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 318.0655 | 0 | 63.6131 | 0.6361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 07:00 | 8 | 26 | 7 | 238 | 5695 | 66.92 | 336.618 | 173.1443 | 173.1443 | 163.4736 | Heating | 144.2414 | 8.5 | 144.2414 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.8483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 147.1851 | 0 | 29.437 | 0.2944% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 08:00 | 8 | 26 | 8 | 238 | 5696 | 66.92 | 0.40787 | 1674.7045 | 1674.7045 | -1674.2967 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2046.8611 | 2046.8611 | 0 | 8.5 | 0 | 341.1435 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2005.9239 | 401.1848 | 4.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 09:00 | 8 | 26 | 9 | 238 | 5697 | 75.02 | 0 | 2771.6159 | 2771.6159 | -2771.6159 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3387.5306 | 3387.5306 | 0 | 8.5 | 0 | 564.5884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3319.78 | 663.956 | 6.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 10:00 | 8 | 26 | 10 | 238 | 5698 | 75.92 | 0 | 3559.0946 | 3559.0946 | -3559.0946 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4350.0045 | 4350.0045 | 0 | 8.5 | 0 | 725.0008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4263.0044 | 852.6009 | 8.526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 11:00 | 8 | 26 | 11 | 238 | 5699 | 75.92 | 0 | 4837.7119 | 4837.7119 | -4837.7119 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5912.759 | 5912.759 | 0 | 8.5 | 0 | 985.4598 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5794.5038 | 1158.9008 | 11.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 12:00 | 8 | 26 | 12 | 238 | 5700 | 78.08 | 0 | 7023.1881 | 7023.1881 | -7023.1881 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8583.8965 | 8583.8965 | 0 | 8.5 | 0 | 1430.6494 | 30% | 1 | 57.23% | 0% | 0% | 0% | 22.5739 | 0 | 0 | 0 | 22.5739 | 0 | 8412.2186 | 1682.4437 | 16.82% | 1 | 33.65% | 0% | 0% | 3.3277 | 0 | 0 | 3.3277 | 25.9017
2007-08-26 13:00 | 8 | 26 | 13 | 238 | 5701 | 77 | 0 | 8525.8503 | 8525.8503 | -8525.8503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10420.4837 | 10420.4837 | 0 | 8.5 | 0 | 1736.7473 | 34.73% | 1 | 69.47% | 0% | 0% | 0% | 35.2594 | 0 | 0 | 0 | 35.2594 | 0 | 10212.0741 | 2042.4148 | 20.42% | 1 | 40.85% | 0% | 0% | 5.1977 | 0 | 0 | 5.1977 | 40.4572
2007-08-26 14:00 | 8 | 26 | 14 | 238 | 5702 | 77 | 0 | 10228.5506 | 10228.5506 | -10228.5506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12501.5619 | 12501.5619 | 0 | 8.5 | 0 | 2083.5936 | 41.67% | 1 | 83.34% | 0% | 0% | 0% | 53.5983 | 0 | 0 | 0 | 53.5983 | 0 | 12251.5306 | 2450.3061 | 24.5% | 1 | 49.01% | 0% | 0% | 7.9011 | 0 | 0 | 7.9011 | 61.4994
2007-08-26 15:00 | 8 | 26 | 15 | 238 | 5703 | 73.94 | 0 | 11801.9348 | 11801.9348 | -11801.9348 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14424.587 | 14424.587 | 0 | 8.5 | 0 | 2404.0978 | 48.08% | 1 | 96.16% | 0% | 0% | 0% | 74.4854 | 0 | 0 | 0 | 74.4854 | 0 | 14136.0952 | 2827.219 | 28.27% | 1 | 56.54% | 0% | 0% | 10.9802 | 0 | 0 | 10.9802 | 85.4655
2007-08-26 16:00 | 8 | 26 | 16 | 238 | 5704 | 73.04 | 0 | 12573.2503 | 12573.2503 | -12573.2503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15367.306 | 15367.306 | 0 | 8.5 | 0 | 2561.2177 | 51.22% | 2 | 51.22% | 51.22% | 0% | 0% | 17.496 | 17.496 | 0 | 0 | 34.992 | 0 | 15059.9599 | 3011.992 | 30.12% | 1 | 60.24% | 0% | 0% | 12.7012 | 0 | 0 | 12.7012 | 47.6932
2007-08-26 17:00 | 8 | 26 | 17 | 238 | 5705 | 73.04 | 0 | 12433.9474 | 12433.9474 | -12433.9474 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15197.0468 | 15197.0468 | 0 | 8.5 | 0 | 2532.8411 | 50.66% | 2 | 50.66% | 50.66% | 0% | 0% | 17.0534 | 17.0534 | 0 | 0 | 34.1067 | 0 | 14893.1059 | 2978.6212 | 29.79% | 1 | 59.57% | 0% | 0% | 12.3799 | 0 | 0 | 12.3799 | 46.4866
2007-08-26 18:00 | 8 | 26 | 18 | 238 | 5706 | 71.06 | 0 | 8497.3114 | 8497.3114 | -8497.3114 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10385.6028 | 10385.6028 | 0 | 8.5 | 0 | 1730.9338 | 34.62% | 1 | 69.24% | 0% | 0% | 0% | 34.9886 | 0 | 0 | 0 | 34.9886 | 0 | 10177.8908 | 2035.5782 | 20.36% | 1 | 40.71% | 0% | 0% | 5.1578 | 0 | 0 | 5.1578 | 40.1464
2007-08-26 19:00 | 8 | 26 | 19 | 238 | 5707 | 68 | 0 | 6887.5327 | 6887.5327 | -6887.5327 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8418.0955 | 8418.0955 | 0 | 8.5 | 0 | 1403.0159 | 30% | 1 | 56.12% | 0% | 0% | 0% | 21.5837 | 0 | 0 | 0 | 21.5837 | 0 | 8249.7336 | 1649.9467 | 16.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.8582
2007-08-26 20:00 | 8 | 26 | 20 | 238 | 5708 | 68 | 0 | 4817.0901 | 4817.0901 | -4817.0901 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5887.5546 | 5887.5546 | 0 | 8.5 | 0 | 981.2591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5769.8035 | 1153.9607 | 11.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 21:00 | 8 | 26 | 21 | 238 | 5709 | 66.02 | 0 | 2125.6042 | 2125.6042 | -2125.6042 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2597.9607 | 2597.9607 | 0 | 8.5 | 0 | 432.9935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2546.0015 | 509.2003 | 5.092% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 22:00 | 8 | 26 | 22 | 238 | 5710 | 64.04 | 0 | 465.3966 | 465.3966 | -465.3966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 568.8181 | 568.8181 | 0 | 8.5 | 0 | 94.803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 557.4418 | 111.4884 | 1.115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-26 23:00 | 8 | 26 | 23 | 238 | 5711 | 64.04 | 0 | 683.3288 | 683.3288 | -683.3288 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 835.1797 | 835.1797 | 0 | 8.5 | 0 | 139.1966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 818.4761 | 163.6952 | 1.637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 | 8 | 27 | 0 | 239 | 5712 | 60.08 | 0 | 810.6786 | 810.6786 | -810.6786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 990.8294 | 990.8294 | 0 | 8.5 | 0 | 165.1382 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 971.0128 | 194.2026 | 1.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 01:00 | 8 | 27 | 1 | 239 | 5713 | 57.92 | 0 | 722.7389 | 722.7389 | -722.7389 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 883.3476 | 883.3476 | 0 | 8.5 | 0 | 147.2246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 865.6806 | 173.1361 | 1.731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 02:00 | 8 | 27 | 2 | 239 | 5714 | 57.92 | 0 | 722.1609 | 722.1609 | -722.1609 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 882.6411 | 882.6411 | 0 | 8.5 | 0 | 147.1068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 864.9883 | 172.9977 | 1.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 03:00 | 8 | 27 | 3 | 239 | 5715 | 55.94 | 0 | 588.2966 | 588.2966 | -588.2966 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 719.0292 | 719.0292 | 0 | 8.5 | 0 | 119.8382 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 704.6486 | 140.9297 | 1.409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 04:00 | 8 | 27 | 4 | 239 | 5716 | 55.04 | 0 | 581.865 | 581.865 | -581.865 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 711.1684 | 711.1684 | 0 | 8.5 | 0 | 118.5281 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 696.945 | 139.389 | 1.394% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 05:00 | 8 | 27 | 5 | 239 | 5717 | 55.04 | 0 | 493.6567 | 493.6567 | -493.6567 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 603.3582 | 603.3582 | 0 | 8.5 | 0 | 100.5597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 591.2911 | 118.2582 | 1.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 06:00 | 8 | 27 | 6 | 239 | 5718 | 53.96 | 8.3327 | 1575.6829 | 1575.6829 | -1567.3503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1925.8347 | 1925.8347 | 0 | 8.5 | 0 | 320.9725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1887.318 | 377.4636 | 3.775% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 07:00 | 8 | 27 | 7 | 239 | 5719 | 57.92 | 0 | 2471.2878 | 2471.2878 | -2471.2878 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3020.4629 | 3020.4629 | 0 | 8.5 | 0 | 503.4105 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2960.0536 | 592.0107 | 5.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 08:00 | 8 | 27 | 8 | 239 | 5720 | 57.92 | 0 | 5335.4888 | 5335.4888 | -5335.4888 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6521.153 | 6521.153 | 0 | 8.5 | 0 | 1086.8588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6390.7299 | 1278.146 | 12.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 09:00 | 8 | 27 | 9 | 239 | 5721 | 60.98 | 0 | 6816.8603 | 6816.8603 | -6816.8603 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8331.7182 | 8331.7182 | 0 | 8.5 | 0 | 1388.6197 | 30% | 1 | 55.54% | 0% | 0% | 0% | 21.0777 | 0 | 0 | 0 | 21.0777 | 0 | 8165.0838 | 1633.0168 | 16.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.3522
2007-08-27 10:00 | 8 | 27 | 10 | 239 | 5722 | 62.96 | 0 | 8062.2742 | 8062.2742 | -8062.2742 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9853.8907 | 9853.8907 | 0 | 8.5 | 0 | 1642.3151 | 32.85% | 1 | 65.69% | 0% | 0% | 0% | 31.0049 | 0 | 0 | 0 | 31.0049 | 0 | 9656.8129 | 1931.3626 | 19.31% | 1 | 38.63% | 0% | 0% | 4.5706 | 0 | 0 | 4.5706 | 35.5755
2007-08-27 11:00 | 8 | 27 | 11 | 239 | 5723 | 62.96 | 0 | 9111.0132 | 9111.0132 | -9111.0132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11135.6827 | 11135.6827 | 0 | 8.5 | 0 | 1855.9471 | 37.12% | 1 | 74.24% | 0% | 0% | 0% | 41.0754 | 0 | 0 | 0 | 41.0754 | 0 | 10912.9691 | 2182.5938 | 21.83% | 1 | 43.65% | 0% | 0% | 6.0551 | 0 | 0 | 6.0551 | 47.1305
2007-08-27 12:00 | 8 | 27 | 12 | 239 | 5724 | 68 | 0 | 9400.3292 | 9400.3292 | -9400.3292 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11489.2913 | 11489.2913 | 0 | 8.5 | 0 | 1914.8819 | 38.3% | 1 | 76.6% | 0% | 0% | 0% | 44.1375 | 0 | 0 | 0 | 44.1375 | 0 | 11259.5054 | 2251.9011 | 22.52% | 1 | 45.04% | 0% | 0% | 6.5065 | 0 | 0 | 6.5065 | 50.644
2007-08-27 13:00 | 8 | 27 | 13 | 239 | 5725 | 69.98 | 0 | 9654.3963 | 9654.3963 | -9654.3963 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11799.8177 | 11799.8177 | 0 | 8.5 | 0 | 1966.6363 | 39.33% | 1 | 78.67% | 0% | 0% | 0% | 46.9295 | 0 | 0 | 0 | 46.9295 | 0 | 11563.8213 | 2312.7643 | 23.13% | 1 | 46.26% | 0% | 0% | 6.9181 | 0 | 0 | 6.9181 | 53.8476
2007-08-27 14:00 | 8 | 27 | 14 | 239 | 5726 | 69.98 | 0 | 10057.3958 | 10057.3958 | -10057.3958 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12292.3727 | 12292.3727 | 0 | 8.5 | 0 | 2048.7288 | 40.97% | 1 | 81.95% | 0% | 0% | 0% | 51.5579 | 0 | 0 | 0 | 51.5579 | 0 | 12046.5252 | 2409.305 | 24.09% | 1 | 48.19% | 0% | 0% | 7.6003 | 0 | 0 | 7.6003 | 59.1583
2007-08-27 15:00 | 8 | 27 | 15 | 239 | 5727 | 71.96 | 0 | 10401.0655 | 10401.0655 | -10401.0655 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12712.4134 | 12712.4134 | 0 | 8.5 | 0 | 2118.7356 | 42.37% | 1 | 84.75% | 0% | 0% | 0% | 55.7003 | 0 | 0 | 0 | 55.7003 | 0 | 12458.1651 | 2491.633 | 24.92% | 1 | 49.83% | 0% | 0% | 8.211 | 0 | 0 | 8.211 | 63.9113
2007-08-27 16:00 | 8 | 27 | 16 | 239 | 5728 | 71.06 | 0 | 10388.9404 | 10388.9404 | -10388.9404 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12697.5938 | 12697.5938 | 0 | 8.5 | 0 | 2116.2656 | 42.33% | 1 | 84.65% | 0% | 0% | 0% | 55.5511 | 0 | 0 | 0 | 55.5511 | 0 | 12443.642 | 2488.7284 | 24.89% | 1 | 49.77% | 0% | 0% | 8.189 | 0 | 0 | 8.189 | 63.7401
2007-08-27 17:00 | 8 | 27 | 17 | 239 | 5729 | 71.06 | 0 | 9562.2941 | 9562.2941 | -9562.2941 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11687.2483 | 11687.2483 | 0 | 8.5 | 0 | 1947.8747 | 38.96% | 1 | 77.91% | 0% | 0% | 0% | 45.9062 | 0 | 0 | 0 | 45.9062 | 0 | 11453.5034 | 2290.7007 | 22.91% | 1 | 45.81% | 0% | 0% | 6.7672 | 0 | 0 | 6.7672 | 52.6734
2007-08-27 18:00 | 8 | 27 | 18 | 239 | 5730 | 66.92 | 0 | 5887.1786 | 5887.1786 | -5887.1786 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7195.4405 | 7195.4405 | 0 | 8.5 | 0 | 1199.2401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7051.5317 | 1410.3063 | 14.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 19:00 | 8 | 27 | 19 | 239 | 5731 | 66.92 | 0 | 4763.5348 | 4763.5348 | -4763.5348 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5822.0981 | 5822.0981 | 0 | 8.5 | 0 | 970.3497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5705.6562 | 1141.1312 | 11.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 20:00 | 8 | 27 | 20 | 239 | 5732 | 66.92 | 0 | 3559.3979 | 3559.3979 | -3559.3979 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4350.3752 | 4350.3752 | 0 | 8.5 | 0 | 725.0625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4263.3677 | 852.6735 | 8.527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 21:00 | 8 | 27 | 21 | 239 | 5733 | 62.06 | 0 | 1747.5035 | 1747.5035 | -1747.5035 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2135.8376 | 2135.8376 | 0 | 8.5 | 0 | 355.9729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2093.1209 | 418.6242 | 4.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 22:00 | 8 | 27 | 22 | 239 | 5734 | 62.06 | 0 | 427.1844 | 427.1844 | -427.1844 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 522.1143 | 522.1143 | 0 | 8.5 | 0 | 87.019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 511.672 | 102.3344 | 1.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-27 23:00 | 8 | 27 | 23 | 239 | 5735 | 62.06 | 0 | 214.2895 | 214.2895 | -214.2895 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 261.9094 | 261.9094 | 0 | 8.5 | 0 | 43.6516 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 256.6712 | 51.3342 | 0.5133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 | 8 | 28 | 0 | 240 | 5736 | 60.08 | 0 | 116.2453 | 116.2453 | -116.2453 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 142.0775 | 142.0775 | 0 | 8.5 | 0 | 23.6796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 139.236 | 27.8472 | 0.2785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 01:00 | 8 | 28 | 1 | 240 | 5737 | 59 | 0.12074 | 21.8009 | 21.8009 | -21.6801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 26.6455 | 26.6455 | 0 | 8.5 | 0 | 4.4409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 26.1126 | 5.2225 | 0.05223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 02:00 | 8 | 28 | 2 | 240 | 5738 | 59 | 4.7676 | 0 | 0 | 4.7676 | Heating | 4.2067 | 8.5 | 4.2067 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.84134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.2926 | 0 | 0.85851 | 0.008585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 03:00 | 8 | 28 | 3 | 240 | 5739 | 57.02 | 6.239 | 0 | 0 | 6.239 | Heating | 5.505 | 8.5 | 5.505 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5.6173 | 0 | 1.1235 | 0.01123% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 04:00 | 8 | 28 | 4 | 240 | 5740 | 57.02 | 2.4212 | 0 | 0 | 2.4212 | Heating | 2.1364 | 8.5 | 2.1364 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.42727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.18 | 0 | 0.43599 | 0.00436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 05:00 | 8 | 28 | 5 | 240 | 5741 | 57.02 | 0.29058 | 0 | 0 | 0.29058 | Heating | 0.25639 | 8.5 | 0.25639 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.051279 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.26163 | 0 | 0.052325 | 0.0005233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 06:00 | 8 | 28 | 6 | 240 | 5742 | 55.94 | 784.2022 | 502.9464 | 502.9464 | 281.2557 | Heating | 248.1668 | 8.5 | 248.1668 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.6334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 253.2315 | 0 | 50.6463 | 0.5065% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 07:00 | 8 | 28 | 7 | 240 | 5743 | 57.02 | 303.3599 | 579.3761 | 579.3761 | -276.0162 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 708.1264 | 708.1264 | 0 | 8.5 | 0 | 118.0211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 693.9638 | 138.7928 | 1.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 08:00 | 8 | 28 | 8 | 240 | 5744 | 57.02 | 0 | 3517.5169 | 3517.5169 | -3517.5169 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4299.1873 | 4299.1873 | 0 | 8.5 | 0 | 716.5312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4213.2036 | 842.6407 | 8.426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 09:00 | 8 | 28 | 9 | 240 | 5745 | 62.96 | 0 | 4566.1533 | 4566.1533 | -4566.1533 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5580.854 | 5580.854 | 0 | 8.5 | 0 | 930.1423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5469.2369 | 1093.8474 | 10.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 10:00 | 8 | 28 | 10 | 240 | 5746 | 64.94 | 0 | 6067.1774 | 6067.1774 | -6067.1774 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7415.4391 | 7415.4391 | 0 | 8.5 | 0 | 1235.9065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7267.1303 | 1453.4261 | 14.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 11:00 | 8 | 28 | 11 | 240 | 5747 | 64.94 | 0 | 7414.102 | 7414.102 | -7414.102 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9061.6802 | 9061.6802 | 0 | 8.5 | 0 | 1510.28 | 30.21% | 1 | 60.41% | 0% | 0% | 0% | 25.569 | 0 | 0 | 0 | 25.569 | 0 | 8880.4466 | 1776.0893 | 17.76% | 1 | 35.52% | 0% | 0% | 3.7692 | 0 | 0 | 3.7692 | 29.3382
2007-08-28 12:00 | 8 | 28 | 12 | 240 | 5748 | 69.08 | 0 | 7807.0522 | 7807.0522 | -7807.0522 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9541.9527 | 9541.9527 | 0 | 8.5 | 0 | 1590.3254 | 31.81% | 1 | 63.61% | 0% | 0% | 0% | 28.7938 | 0 | 0 | 0 | 28.7938 | 0 | 9351.1136 | 1870.2227 | 18.7% | 1 | 37.4% | 0% | 0% | 4.2446 | 0 | 0 | 4.2446 | 33.0384
2007-08-28 13:00 | 8 | 28 | 13 | 240 | 5749 | 69.98 | 0 | 8943.9885 | 8943.9885 | -8943.9885 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10931.5416 | 10931.5416 | 0 | 8.5 | 0 | 1821.9236 | 36.44% | 1 | 72.88% | 0% | 0% | 0% | 39.3641 | 0 | 0 | 0 | 39.3641 | 0 | 10712.9107 | 2142.5821 | 21.43% | 1 | 42.85% | 0% | 0% | 5.8028 | 0 | 0 | 5.8028 | 45.1669
2007-08-28 14:00 | 8 | 28 | 14 | 240 | 5750 | 69.98 | 0 | 9978.6953 | 9978.6953 | -9978.6953 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12196.1831 | 12196.1831 | 0 | 8.5 | 0 | 2032.6972 | 40.65% | 1 | 81.31% | 0% | 0% | 0% | 50.6347 | 0 | 0 | 0 | 50.6347 | 0 | 11952.2595 | 2390.4519 | 23.9% | 1 | 47.81% | 0% | 0% | 7.4642 | 0 | 0 | 7.4642 | 58.0989
2007-08-28 15:00 | 8 | 28 | 15 | 240 | 5751 | 71.06 | 0 | 10428.4365 | 10428.4365 | -10428.4365 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12745.8669 | 12745.8669 | 0 | 8.5 | 0 | 2124.3111 | 42.49% | 1 | 84.97% | 0% | 0% | 0% | 56.038 | 0 | 0 | 0 | 56.038 | 0 | 12490.9495 | 2498.1899 | 24.98% | 1 | 49.96% | 0% | 0% | 8.2608 | 0 | 0 | 8.2608 | 64.2988
2007-08-28 16:00 | 8 | 28 | 16 | 240 | 5752 | 68 | 0 | 9960.0031 | 9960.0031 | -9960.0031 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12173.3372 | 12173.3372 | 0 | 8.5 | 0 | 2028.8895 | 40.58% | 1 | 81.16% | 0% | 0% | 0% | 50.4168 | 0 | 0 | 0 | 50.4168 | 0 | 11929.8704 | 2385.9741 | 23.86% | 1 | 47.72% | 0% | 0% | 7.4321 | 0 | 0 | 7.4321 | 57.8489
2007-08-28 17:00 | 8 | 28 | 17 | 240 | 5753 | 68 | 0 | 9250.5718 | 9250.5718 | -9250.5718 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11306.2544 | 11306.2544 | 0 | 8.5 | 0 | 1884.3757 | 37.69% | 1 | 75.38% | 0% | 0% | 0% | 42.5369 | 0 | 0 | 0 | 42.5369 | 0 | 11080.1293 | 2216.0259 | 22.16% | 1 | 44.32% | 0% | 0% | 6.2705 | 0 | 0 | 6.2705 | 48.8075
2007-08-28 18:00 | 8 | 28 | 18 | 240 | 5754 | 62.06 | 0 | 5585.7362 | 5585.7362 | -5585.7362 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6827.0109 | 6827.0109 | 0 | 8.5 | 0 | 1137.8351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6690.4707 | 1338.0941 | 13.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 19:00 | 8 | 28 | 19 | 240 | 5755 | 60.98 | 0 | 4202.2765 | 4202.2765 | -4202.2765 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5136.1158 | 5136.1158 | 0 | 8.5 | 0 | 856.0193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5033.3935 | 1006.6787 | 10.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 20:00 | 8 | 28 | 20 | 240 | 5756 | 60.98 | 0 | 2994.1265 | 2994.1265 | -2994.1265 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3659.488 | 3659.488 | 0 | 8.5 | 0 | 609.9147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3586.2982 | 717.2596 | 7.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 21:00 | 8 | 28 | 21 | 240 | 5757 | 60.8 | 0 | 1240.9257 | 1240.9257 | -1240.9257 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1516.687 | 1516.687 | 0 | 8.5 | 0 | 252.7812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1486.3533 | 297.2707 | 2.973% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 22:00 | 8 | 28 | 22 | 240 | 5758 | 60.8 | 0 | 259.125 | 259.125 | -259.125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 316.7084 | 316.7084 | 0 | 8.5 | 0 | 52.7847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 310.3742 | 62.0748 | 0.6207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-28 23:00 | 8 | 28 | 23 | 240 | 5759 | 60.98 | 0 | 84.1808 | 84.1808 | -84.1808 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 102.8876 | 102.8876 | 0 | 8.5 | 0 | 17.1479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 100.8298 | 20.166 | 0.2017% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 | 8 | 29 | 0 | 241 | 5760 | 59 | 0 | 50.4803 | 50.4803 | -50.4803 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 61.6981 | 61.6981 | 0 | 8.5 | 0 | 10.283 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 60.4642 | 12.0928 | 0.1209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 01:00 | 8 | 29 | 1 | 241 | 5761 | 59 | 0 | 23.7165 | 23.7165 | -23.7165 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 28.9868 | 28.9868 | 0 | 8.5 | 0 | 4.8311 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 28.4071 | 5.6814 | 0.05681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 02:00 | 8 | 29 | 2 | 241 | 5762 | 59 | 0.17082 | 0.039411 | 0.039411 | 0.13141 | Heating | 0.11595 | 8.5 | 0.11595 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.02319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.11831 | 0 | 0.023663 | 0.0002366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 03:00 | 8 | 29 | 3 | 241 | 5763 | 57.02 | 2.6984 | 0 | 0 | 2.6984 | Heating | 2.381 | 8.5 | 2.381 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.47619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.4295 | 0 | 0.48591 | 0.004859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 04:00 | 8 | 29 | 4 | 241 | 5764 | 57.2 | 4.407 | 0 | 0 | 4.407 | Heating | 3.8886 | 8.5 | 3.8886 | 0 | 5.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.77771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.9679 | 0 | 0.79358 | 0.007936% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 05:00 | 8 | 29 | 5 | 241 | 5765 | 57.92 | 9.707 | 0 | 0 | 9.707 | Heating | 8.565 | 8.5 | 8.565 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.7398 | 0 | 1.748 | 0.01748% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 06:00 | 8 | 29 | 6 | 241 | 5766 | 59 | 1349.7759 | 318.3193 | 318.3193 | 1031.4567 | Heating | 910.1088 | 8.5 | 910.1088 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.0218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 928.6825 | 0 | 185.7365 | 1.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 07:00 | 8 | 29 | 7 | 241 | 5767 | 57.2 | 965.9113 | 259.6408 | 259.6408 | 706.2705 | Heating | 623.1798 | 8.5 | 623.1798 | 0 | 5.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 635.8978 | 0 | 127.1796 | 1.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 08:00 | 8 | 29 | 8 | 241 | 5768 | 57.92 | 398.8944 | 1123.0731 | 1123.0731 | -724.1787 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1372.6449 | 1372.6449 | 0 | 8.5 | 0 | 228.7742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1345.192 | 269.0384 | 2.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 09:00 | 8 | 29 | 9 | 241 | 5769 | 59 | 3.3519 | 1832.8705 | 1832.8705 | -1829.5186 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2240.1751 | 2240.1751 | 0 | 8.5 | 0 | 373.3625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2195.3716 | 439.0743 | 4.391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 10:00 | 8 | 29 | 10 | 241 | 5770 | 59 | 0.47979 | 2500.7732 | 2500.7732 | -2500.2934 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3056.5006 | 3056.5006 | 0 | 8.5 | 0 | 509.4168 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2995.3706 | 599.0741 | 5.991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 11:00 | 8 | 29 | 11 | 241 | 5771 | 59 | 0 | 2630.5932 | 2630.5932 | -2630.5932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3215.1694 | 3215.1694 | 0 | 8.5 | 0 | 535.8616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3150.866 | 630.1732 | 6.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 12:00 | 8 | 29 | 12 | 241 | 5772 | 60.98 | 0 | 3120.1053 | 3120.1053 | -3120.1053 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3813.4621 | 3813.4621 | 0 | 8.5 | 0 | 635.577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3737.1928 | 747.4386 | 7.474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 13:00 | 8 | 29 | 13 | 241 | 5773 | 60.8 | 0 | 3845.4389 | 3845.4389 | -3845.4389 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4699.9808 | 4699.9808 | 0 | 8.5 | 0 | 783.3301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4605.9812 | 921.1962 | 9.212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 14:00 | 8 | 29 | 14 | 241 | 5774 | 60.98 | 0 | 4460.87 | 4460.87 | -4460.87 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5452.1745 | 5452.1745 | 0 | 8.5 | 0 | 908.6957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5343.131 | 1068.6262 | 10.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 15:00 | 8 | 29 | 15 | 241 | 5775 | 62.6 | 0 | 4432.7931 | 4432.7931 | -4432.7931 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5417.8582 | 5417.8582 | 0 | 8.5 | 0 | 902.9764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5309.5011 | 1061.9002 | 10.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 16:00 | 8 | 29 | 16 | 241 | 5776 | 62.6 | 0 | 3936.5214 | 3936.5214 | -3936.5214 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4811.3039 | 4811.3039 | 0 | 8.5 | 0 | 801.884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4715.0779 | 943.0156 | 9.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 17:00 | 8 | 29 | 17 | 241 | 5777 | 62.96 | 0 | 2997.7398 | 2997.7398 | -2997.7398 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3663.9042 | 3663.9042 | 0 | 8.5 | 0 | 610.6507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3590.6261 | 718.1252 | 7.181% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 18:00 | 8 | 29 | 18 | 241 | 5778 | 64.4 | 0 | 1186.1386 | 1186.1386 | -1186.1386 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1449.7249 | 1449.7249 | 0 | 8.5 | 0 | 241.6208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1420.7304 | 284.1461 | 2.841% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 19:00 | 8 | 29 | 19 | 241 | 5779 | 64.04 | 0 | 495.6702 | 495.6702 | -495.6702 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 605.8192 | 605.8192 | 0 | 8.5 | 0 | 100.9699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 593.7028 | 118.7406 | 1.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 20:00 | 8 | 29 | 20 | 241 | 5780 | 64.04 | 0 | 366.1109 | 366.1109 | -366.1109 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 447.4689 | 447.4689 | 0 | 8.5 | 0 | 74.5782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 438.5195 | 87.7039 | 0.877% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 21:00 | 8 | 29 | 21 | 241 | 5781 | 62.06 | 0 | 307.1761 | 307.1761 | -307.1761 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 375.4374 | 375.4374 | 0 | 8.5 | 0 | 62.5729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 367.9287 | 73.5857 | 0.7359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 22:00 | 8 | 29 | 22 | 241 | 5782 | 60.8 | 0.50191 | 0 | 0 | 0.50191 | Heating | 0.44286 | 8.5 | 0.44286 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.088573 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.4519 | 0 | 0.090381 | 0.0009038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-29 23:00 | 8 | 29 | 23 | 241 | 5783 | 60.8 | 5.3267 | 0 | 0 | 5.3267 | Heating | 4.7 | 8.5 | 4.7 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.94 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.7959 | 0 | 0.95919 | 0.009592% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 | 8 | 30 | 0 | 242 | 5784 | 60.8 | 11.6663 | 0 | 0 | 11.6663 | Heating | 10.2938 | 8.5 | 10.2938 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.5039 | 0 | 2.1008 | 0.02101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 01:00 | 8 | 30 | 1 | 242 | 5785 | 62.6 | 16.0075 | 0 | 0 | 16.0075 | Heating | 14.1242 | 8.5 | 14.1242 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.8248 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 14.4125 | 0 | 2.8825 | 0.02882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 02:00 | 8 | 30 | 2 | 242 | 5786 | 62.06 | 25.7546 | 0 | 0 | 25.7546 | Heating | 22.7246 | 8.5 | 22.7246 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.5449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.1884 | 0 | 4.6377 | 0.04638% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 03:00 | 8 | 30 | 3 | 242 | 5787 | 60.8 | 33.5457 | 0 | 0 | 33.5457 | Heating | 29.5991 | 8.5 | 29.5991 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.9198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.2032 | 0 | 6.0406 | 0.06041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 04:00 | 8 | 30 | 4 | 242 | 5788 | 60.8 | 41.2107 | 0 | 0 | 41.2107 | Heating | 36.3624 | 8.5 | 36.3624 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.2725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 37.1045 | 0 | 7.4209 | 0.07421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 05:00 | 8 | 30 | 5 | 242 | 5789 | 60.98 | 46.5138 | 0 | 0 | 46.5138 | Heating | 41.0416 | 8.5 | 41.0416 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.2083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 41.8792 | 0 | 8.3758 | 0.08376% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 06:00 | 8 | 30 | 6 | 242 | 5790 | 60.8 | 1829.9014 | 148.4793 | 148.4793 | 1681.4222 | Heating | 1483.6078 | 8.5 | 1483.6078 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.7216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1513.8855 | 0 | 302.7771 | 3.028% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 07:00 | 8 | 30 | 7 | 242 | 5791 | 62.96 | 1371.0408 | 32.8837 | 32.8837 | 1338.1571 | Heating | 1180.7269 | 8.5 | 1180.7269 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 236.1454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1204.8234 | 0 | 240.9647 | 2.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 08:00 | 8 | 30 | 8 | 242 | 5792 | 62.96 | 687.0604 | 712.5474 | 712.5474 | -25.487 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 870.8912 | 870.8912 | 0 | 8.5 | 0 | 145.1485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 853.4734 | 170.6947 | 1.707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 09:00 | 8 | 30 | 9 | 242 | 5793 | 66.2 | 20.0493 | 1107.34 | 1107.34 | -1087.2907 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1353.4155 | 1353.4155 | 0 | 8.5 | 0 | 225.5693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1326.3472 | 265.2694 | 2.653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 10:00 | 8 | 30 | 10 | 242 | 5794 | 69.8 | 4.0923 | 2500.2416 | 2500.2416 | -2496.1494 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3055.8509 | 3055.8509 | 0 | 8.5 | 0 | 509.3085 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2994.7339 | 598.9468 | 5.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 11:00 | 8 | 30 | 11 | 242 | 5795 | 69.98 | 0 | 3266.4904 | 3266.4904 | -3266.4904 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3992.3771 | 3992.3771 | 0 | 8.5 | 0 | 665.3962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3912.5296 | 782.5059 | 7.825% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 12:00 | 8 | 30 | 12 | 242 | 5796 | 75.02 | 0 | 4357.0138 | 4357.0138 | -4357.0138 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5325.2391 | 5325.2391 | 0 | 8.5 | 0 | 887.5398 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5218.7343 | 1043.7469 | 10.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 13:00 | 8 | 30 | 13 | 242 | 5797 | 73.94 | 0 | 5039.8627 | 5039.8627 | -5039.8627 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6159.8322 | 6159.8322 | 0 | 8.5 | 0 | 1026.6387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6036.6356 | 1207.3271 | 12.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 14:00 | 8 | 30 | 14 | 242 | 5798 | 73.94 | 0 | 5621.3363 | 5621.3363 | -5621.3363 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6870.5222 | 6870.5222 | 0 | 8.5 | 0 | 1145.087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6733.1117 | 1346.6223 | 13.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 15:00 | 8 | 30 | 15 | 242 | 5799 | 77 | 0 | 5572.5279 | 5572.5279 | -5572.5279 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6810.8675 | 6810.8675 | 0 | 8.5 | 0 | 1135.1446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6674.6501 | 1334.93 | 13.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 16:00 | 8 | 30 | 16 | 242 | 5800 | 75.92 | 0 | 4894.0438 | 4894.0438 | -4894.0438 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5981.6091 | 5981.6091 | 0 | 8.5 | 0 | 996.9348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5861.9769 | 1172.3954 | 11.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 17:00 | 8 | 30 | 17 | 242 | 5801 | 75.92 | 0 | 2655.3451 | 2655.3451 | -2655.3451 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3245.4218 | 3245.4218 | 0 | 8.5 | 0 | 540.9036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3180.5133 | 636.1027 | 6.361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 18:00 | 8 | 30 | 18 | 242 | 5802 | 69.98 | 0 | 409.3551 | 409.3551 | -409.3551 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 500.3229 | 500.3229 | 0 | 8.5 | 0 | 83.3871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 490.3164 | 98.0633 | 0.9806% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 19:00 | 8 | 30 | 19 | 242 | 5803 | 66.02 | 1.5516 | 353.6665 | 353.6665 | -352.1148 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 432.259 | 432.259 | 0 | 8.5 | 0 | 72.0432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 423.6139 | 84.7228 | 0.8472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 20:00 | 8 | 30 | 20 | 242 | 5804 | 66.02 | 5.6631 | 230.4402 | 230.4402 | -224.7771 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 281.6492 | 281.6492 | 0 | 8.5 | 0 | 46.9415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 276.0162 | 55.2032 | 0.552% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 21:00 | 8 | 30 | 21 | 242 | 5805 | 62.96 | 8.1328 | 190.8915 | 190.8915 | -182.7587 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 233.3119 | 233.3119 | 0 | 8.5 | 0 | 38.8853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 228.6456 | 45.7291 | 0.4573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 22:00 | 8 | 30 | 22 | 242 | 5806 | 62.06 | 12.6116 | 0 | 0 | 12.6116 | Heating | 11.1279 | 8.5 | 11.1279 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.2256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.355 | 0 | 2.271 | 0.02271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-30 23:00 | 8 | 30 | 23 | 242 | 5807 | 62.06 | 22.5844 | 0 | 0 | 22.5844 | Heating | 19.9274 | 8.5 | 19.9274 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.9855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.334 | 0 | 4.0668 | 0.04067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 | 8 | 31 | 0 | 243 | 5808 | 59 | 38.2205 | 0 | 0 | 38.2205 | Heating | 33.724 | 8.5 | 33.724 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.4122 | 0 | 6.8824 | 0.06882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 01:00 | 8 | 31 | 1 | 243 | 5809 | 57.92 | 49.9133 | 0 | 0 | 49.9133 | Heating | 44.0411 | 8.5 | 44.0411 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.8082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.9399 | 0 | 8.988 | 0.08988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 02:00 | 8 | 31 | 2 | 243 | 5810 | 57.92 | 63.1084 | 0 | 0 | 63.1084 | Heating | 55.6839 | 8.5 | 55.6839 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.1368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.8203 | 0 | 11.3641 | 0.1136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 03:00 | 8 | 31 | 3 | 243 | 5811 | 57.02 | 82.6111 | 0 | 0 | 82.6111 | Heating | 72.8921 | 8.5 | 72.8921 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.5784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 74.3797 | 0 | 14.8759 | 0.1488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 04:00 | 8 | 31 | 4 | 243 | 5812 | 55.94 | 97.322 | 0 | 0 | 97.322 | Heating | 85.8724 | 8.5 | 85.8724 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.1745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 87.6249 | 0 | 17.525 | 0.1752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 05:00 | 8 | 31 | 5 | 243 | 5813 | 55.94 | 110.5965 | 0 | 0 | 110.5965 | Heating | 97.5852 | 8.5 | 97.5852 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 99.5767 | 0 | 19.9153 | 0.1992% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 06:00 | 8 | 31 | 6 | 243 | 5814 | 55.04 | 2594.6963 | 108.6033 | 108.6033 | 2486.093 | Heating | 2193.6114 | 8.5 | 2193.6114 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.7223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2238.379 | 0 | 447.6758 | 4.477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 07:00 | 8 | 31 | 7 | 243 | 5815 | 55.04 | 1864.9332 | 0 | 0 | 1864.9332 | Heating | 1645.5293 | 8.5 | 1645.5293 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.1059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1679.1115 | 0 | 335.8223 | 3.358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 08:00 | 8 | 31 | 8 | 243 | 5816 | 55.04 | 1490.5881 | 17.814 | 17.814 | 1472.774 | Heating | 1299.5065 | 8.5 | 1299.5065 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 259.9013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1326.027 | 0 | 265.2054 | 2.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 09:00 | 8 | 31 | 9 | 243 | 5817 | 59 | 777.726 | 46.7932 | 46.7932 | 730.9328 | Heating | 644.9407 | 8.5 | 644.9407 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.9881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 658.1027 | 0 | 131.6205 | 1.316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 10:00 | 8 | 31 | 10 | 243 | 5818 | 60.98 | 173.3616 | 104.9275 | 104.9275 | 68.4341 | Heating | 60.383 | 8.5 | 60.383 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.0766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 61.6153 | 0 | 12.3231 | 0.1232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 11:00 | 8 | 31 | 11 | 243 | 5819 | 60.98 | 51.9969 | 160.9406 | 160.9406 | -108.9438 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 196.7052 | 196.7052 | 0 | 8.5 | 0 | 32.7842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 192.7711 | 38.5542 | 0.3855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 12:00 | 8 | 31 | 12 | 243 | 5820 | 64.94 | 32.2876 | 199.6139 | 199.6139 | -167.3263 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 243.9725 | 243.9725 | 0 | 8.5 | 0 | 40.6621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 239.0931 | 47.8186 | 0.4782% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 13:00 | 8 | 31 | 13 | 243 | 5821 | 64.94 | 27.5501 | 233.0633 | 233.0633 | -205.5131 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 284.8551 | 284.8551 | 0 | 8.5 | 0 | 47.4758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 279.158 | 55.8316 | 0.5583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 14:00 | 8 | 31 | 14 | 243 | 5822 | 64.94 | 29.9765 | 142.1944 | 142.1944 | -112.2179 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 173.7932 | 173.7932 | 0 | 8.5 | 0 | 28.9655 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 170.3173 | 34.0635 | 0.3406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 15:00 | 8 | 31 | 15 | 243 | 5823 | 69.08 | 31.6012 | 140.1039 | 140.1039 | -108.5027 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 171.2381 | 171.2381 | 0 | 8.5 | 0 | 28.5397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 167.8133 | 33.5627 | 0.3356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 16:00 | 8 | 31 | 16 | 243 | 5824 | 68 | 21.4269 | 134.2416 | 134.2416 | -112.8148 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 164.0731 | 164.0731 | 0 | 8.5 | 0 | 27.3455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 160.7917 | 32.1583 | 0.3216% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 17:00 | 8 | 31 | 17 | 243 | 5825 | 68 | 13.7282 | 81.9846 | 81.9846 | -68.2564 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 100.2034 | 100.2034 | 0 | 8.5 | 0 | 16.7006 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 98.1993 | 19.6399 | 0.1964% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 18:00 | 8 | 31 | 18 | 243 | 5826 | 64.94 | 14.837 | 0 | 0 | 14.837 | Heating | 13.0914 | 8.5 | 13.0914 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.6183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 13.3586 | 0 | 2.6717 | 0.02672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 19:00 | 8 | 31 | 19 | 243 | 5827 | 58.64 | 72.2525 | 0 | 0 | 72.2525 | Heating | 63.7522 | 8.5 | 63.7522 | 0 | 5.4502 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.7504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.0533 | 0 | 13.0107 | 0.1301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 20:00 | 8 | 31 | 20 | 243 | 5828 | 57.38 | 272.8468 | 0 | 0 | 272.8468 | Heating | 240.7472 | 8.5 | 240.7472 | 0 | 5.2962 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.1494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 245.6604 | 0 | 49.1321 | 0.4913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 21:00 | 8 | 31 | 21 | 243 | 5829 | 55.76 | 727.0869 | 0 | 0 | 727.0869 | Heating | 641.5473 | 8.5 | 641.5473 | 0 | 5.1073 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.3095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 654.6401 | 0 | 130.928 | 1.309% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 22:00 | 8 | 31 | 22 | 243 | 5830 | 55.76 | 86.1759 | 0 | 0 | 86.1759 | Heating | 76.0376 | 8.5 | 76.0376 | 0 | 5.1073 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.2075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.5894 | 0 | 15.5179 | 0.1552% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-08-31 23:00 | 8 | 31 | 23 | 243 | 5831 | 55.94 | 117.4983 | 0 | 0 | 117.4983 | Heating | 103.675 | 8.5 | 103.675 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 105.7908 | 0 | 21.1582 | 0.2116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 | 9 | 1 | 0 | 244 | 5832 | 55.76 | 153.7609 | 0 | 0 | 153.7609 | Heating | 135.6714 | 8.5 | 135.6714 | 0 | 5.1073 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.1343 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 138.4402 | 0 | 27.688 | 0.2769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 01:00 | 9 | 1 | 1 | 244 | 5833 | 55.76 | 190.2507 | 0 | 0 | 190.2507 | Heating | 167.8683 | 8.5 | 167.8683 | 0 | 5.1073 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.5737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 171.2942 | 0 | 34.2588 | 0.3426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 02:00 | 9 | 1 | 2 | 244 | 5834 | 55.04 | 225.1553 | 0 | 0 | 225.1553 | Heating | 198.6665 | 8.5 | 198.6665 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.7333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 202.7209 | 0 | 40.5442 | 0.4054% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 03:00 | 9 | 1 | 3 | 244 | 5835 | 53.96 | 256.1161 | 0 | 0 | 256.1161 | Heating | 225.9848 | 8.5 | 225.9848 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.197 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 230.5967 | 0 | 46.1193 | 0.4612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 04:00 | 9 | 1 | 4 | 244 | 5836 | 55.04 | 283.5925 | 0 | 0 | 283.5925 | Heating | 250.2287 | 8.5 | 250.2287 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.0457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 255.3354 | 0 | 51.0671 | 0.5107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 05:00 | 9 | 1 | 5 | 244 | 5837 | 56.3 | 310.1439 | 0 | 0 | 310.1439 | Heating | 273.6564 | 8.5 | 273.6564 | 0 | 5.1692 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.7313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 279.2412 | 0 | 55.8482 | 0.5585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 06:00 | 9 | 1 | 6 | 244 | 5838 | 58.46 | 318.7203 | 0 | 0 | 318.7203 | Heating | 281.2238 | 8.5 | 281.2238 | 0 | 5.4278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 56.2448 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 286.9631 | 0 | 57.3926 | 0.5739% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 07:00 | 9 | 1 | 7 | 244 | 5839 | 59 | 229.6894 | 0 | 0 | 229.6894 | Heating | 202.6671 | 8.5 | 202.6671 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.5334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 206.8032 | 0 | 41.3606 | 0.4136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 08:00 | 9 | 1 | 8 | 244 | 5840 | 59 | 2485.5569 | 0 | 0 | 2485.5569 | Heating | 2193.1384 | 8.5 | 2193.1384 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.6277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2237.8963 | 0 | 447.5793 | 4.476% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 09:00 | 9 | 1 | 9 | 244 | 5841 | 62.96 | 927.2418 | 0 | 0 | 927.2418 | Heating | 818.1545 | 8.5 | 818.1545 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.6309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 834.8516 | 0 | 166.9703 | 1.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 10:00 | 9 | 1 | 10 | 244 | 5842 | 66.92 | 33.5659 | 0 | 0 | 33.5659 | Heating | 29.617 | 8.5 | 29.617 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.9234 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.2214 | 0 | 6.0443 | 0.06044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 11:00 | 9 | 1 | 11 | 244 | 5843 | 66.92 | 0 | 0.21004 | 0.21004 | -0.21004 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.25672 | 0.25672 | 0 | 8.5 | 0 | 0.042786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.25158 | 0.050316 | 0.0005032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 12:00 | 9 | 1 | 12 | 244 | 5844 | 69.08 | 0 | 825.5511 | 825.5511 | -825.5511 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1009.0069 | 1009.0069 | 0 | 8.5 | 0 | 168.1678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 988.8267 | 197.7653 | 1.978% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 13:00 | 9 | 1 | 13 | 244 | 5845 | 71.96 | 0 | 2240.6553 | 2240.6553 | -2240.6553 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2738.5787 | 2738.5787 | 0 | 8.5 | 0 | 456.4298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2683.8071 | 536.7614 | 5.368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 14:00 | 9 | 1 | 14 | 244 | 5846 | 71.96 | 0 | 3159.5946 | 3159.5946 | -3159.5946 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3861.7267 | 3861.7267 | 0 | 8.5 | 0 | 643.6211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3784.4922 | 756.8984 | 7.569% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 15:00 | 9 | 1 | 15 | 244 | 5847 | 73.04 | 0 | 3663.6571 | 3663.6571 | -3663.6571 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4477.8032 | 4477.8032 | 0 | 8.5 | 0 | 746.3005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4388.2471 | 877.6494 | 8.776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 16:00 | 9 | 1 | 16 | 244 | 5848 | 73.04 | 0 | 3843.2698 | 3843.2698 | -3843.2698 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4697.3298 | 4697.3298 | 0 | 8.5 | 0 | 782.8883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4603.3832 | 920.6766 | 9.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 17:00 | 9 | 1 | 17 | 244 | 5849 | 73.04 | 0 | 3483.846 | 3483.846 | -3483.846 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4258.034 | 4258.034 | 0 | 8.5 | 0 | 709.6723 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4172.8734 | 834.5747 | 8.346% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 18:00 | 9 | 1 | 18 | 244 | 5850 | 69.98 | 0 | 2545.6202 | 2545.6202 | -2545.6202 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3111.3136 | 3111.3136 | 0 | 8.5 | 0 | 518.5523 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3049.0873 | 609.8175 | 6.098% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 19:00 | 9 | 1 | 19 | 244 | 5851 | 66.02 | 0 | 726.4237 | 726.4237 | -726.4237 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 887.8512 | 887.8512 | 0 | 8.5 | 0 | 147.9752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 870.0942 | 174.0188 | 1.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 20:00 | 9 | 1 | 20 | 244 | 5852 | 66.02 | 0 | 564.4714 | 564.4714 | -564.4714 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 689.9095 | 689.9095 | 0 | 8.5 | 0 | 114.9849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 676.1113 | 135.2223 | 1.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 21:00 | 9 | 1 | 21 | 244 | 5853 | 60.08 | 0 | 511.8142 | 511.8142 | -511.8142 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 625.5506 | 625.5506 | 0 | 8.5 | 0 | 104.2584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 613.0396 | 122.6079 | 1.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 22:00 | 9 | 1 | 22 | 244 | 5854 | 57.02 | 0 | 408.5143 | 408.5143 | -408.5143 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 499.2952 | 499.2952 | 0 | 8.5 | 0 | 83.2159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 489.3093 | 97.8619 | 0.9786% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-01 23:00 | 9 | 1 | 23 | 244 | 5855 | 57.02 | 0 | 94.3843 | 94.3843 | -94.3843 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 115.3586 | 115.3586 | 0 | 8.5 | 0 | 19.2264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 113.0514 | 22.6103 | 0.2261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 | 9 | 2 | 0 | 245 | 5856 | 55.94 | 0 | 46.4326 | 46.4326 | -46.4326 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 56.751 | 56.751 | 0 | 8.5 | 0 | 9.4585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 55.616 | 11.1232 | 0.1112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 01:00 | 9 | 2 | 1 | 245 | 5857 | 53.96 | 0 | 24.6256 | 24.6256 | -24.6256 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 30.098 | 30.098 | 0 | 8.5 | 0 | 5.0163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 29.496 | 5.8992 | 0.05899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 02:00 | 9 | 2 | 2 | 245 | 5858 | 53.96 | 0 | 11.3775 | 11.3775 | -11.3775 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13.9058 | 13.9058 | 0 | 8.5 | 0 | 2.3176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.6277 | 2.7255 | 0.02726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 03:00 | 9 | 2 | 3 | 245 | 5859 | 48.92 | 0 | 2.5569 | 2.5569 | -2.5569 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3.125 | 3.125 | 0 | 8.5 | 0 | 0.52084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3.0625 | 0.61251 | 0.006125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 04:00 | 9 | 2 | 4 | 245 | 5860 | 48.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-09-02 05:00 | 9 | 2 | 5 | 245 | 5861 | 48.02 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-09-02 06:00 | 9 | 2 | 6 | 245 | 5862 | 46.94 | 487.7828 | 526.2817 | 526.2817 | -38.4989 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 643.2332 | 643.2332 | 0 | 8.5 | 0 | 107.2055 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 630.3685 | 126.0737 | 1.261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 07:00 | 9 | 2 | 7 | 245 | 5863 | 53.06 | 46.3603 | 635.5677 | 635.5677 | -589.2074 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 776.805 | 776.805 | 0 | 8.5 | 0 | 129.4675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 761.2689 | 152.2538 | 1.523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 08:00 | 9 | 2 | 8 | 245 | 5864 | 53.06 | 0 | 2160.7979 | 2160.7979 | -2160.7979 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2640.9752 | 2640.9752 | 0 | 8.5 | 0 | 440.1625 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2588.1557 | 517.6311 | 5.176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 09:00 | 9 | 2 | 9 | 245 | 5865 | 60.98 | 0 | 3785.4938 | 3785.4938 | -3785.4938 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4626.7146 | 4626.7146 | 0 | 8.5 | 0 | 771.1191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4534.1803 | 906.8361 | 9.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 10:00 | 9 | 2 | 10 | 245 | 5866 | 66.02 | 0 | 7179.9918 | 7179.9918 | -7179.9918 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8775.5456 | 8775.5456 | 0 | 8.5 | 0 | 1462.5909 | 30% | 1 | 58.5% | 0% | 0% | 0% | 23.75 | 0 | 0 | 0 | 23.75 | 0 | 8600.0347 | 1720.0069 | 17.2% | 1 | 34.4% | 0% | 0% | 3.5011 | 0 | 0 | 3.5011 | 27.2511
2007-09-02 11:00 | 9 | 2 | 11 | 245 | 5867 | 66.02 | 0 | 9903.3305 | 9903.3305 | -9903.3305 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12104.0707 | 12104.0707 | 0 | 8.5 | 0 | 2017.3451 | 40.35% | 1 | 80.69% | 0% | 0% | 0% | 49.7594 | 0 | 0 | 0 | 49.7594 | 0 | 11861.9893 | 2372.3979 | 23.72% | 1 | 47.45% | 0% | 0% | 7.3352 | 0 | 0 | 7.3352 | 57.0947
2007-09-02 12:00 | 9 | 2 | 12 | 245 | 5868 | 69.98 | 0 | 11316.6646 | 11316.6646 | -11316.6646 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13831.479 | 13831.479 | 0 | 8.5 | 0 | 2305.2465 | 46.1% | 1 | 92.21% | 0% | 0% | 0% | 67.6287 | 0 | 0 | 0 | 67.6287 | 0 | 13554.8494 | 2710.9699 | 27.11% | 1 | 54.22% | 0% | 0% | 9.9694 | 0 | 0 | 9.9694 | 77.5981
2007-09-02 13:00 | 9 | 2 | 13 | 245 | 5869 | 73.04 | 0 | 12689.4147 | 12689.4147 | -12689.4147 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15509.2847 | 15509.2847 | 0 | 8.5 | 0 | 2584.8808 | 51.7% | 2 | 51.7% | 51.7% | 0% | 0% | 17.87 | 17.87 | 0 | 0 | 35.7401 | 0 | 15199.099 | 3039.8198 | 30.4% | 1 | 60.8% | 0% | 0% | 12.9728 | 0 | 0 | 12.9728 | 48.7128
2007-09-02 14:00 | 9 | 2 | 14 | 245 | 5870 | 73.04 | 0 | 14003.8478 | 14003.8478 | -14003.8478 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17115.814 | 17115.814 | 0 | 8.5 | 0 | 2852.6357 | 57.05% | 2 | 57.05% | 57.05% | 0% | 0% | 22.4171 | 22.4171 | 0 | 0 | 44.8341 | 0 | 16773.4977 | 3354.6995 | 33.55% | 1 | 33.55% | 33.55% | 0% | 3.3046 | 3.3046 | 0 | 6.6092 | 51.4433
2007-09-02 15:00 | 9 | 2 | 15 | 245 | 5871 | 75.92 | 0 | 13920.5598 | 13920.5598 | -13920.5598 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 17014.0175 | 17014.0175 | 0 | 8.5 | 0 | 2835.6696 | 56.71% | 2 | 56.71% | 56.71% | 0% | 0% | 22.1116 | 22.1116 | 0 | 0 | 44.2232 | 0 | 16673.7371 | 3334.7474 | 33.35% | 1 | 33.35% | 33.35% | 0% | 3.2596 | 3.2596 | 0 | 6.5191 | 50.7423
2007-09-02 16:00 | 9 | 2 | 16 | 245 | 5872 | 75.92 | 0 | 13002.653 | 13002.653 | -13002.653 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15892.1315 | 15892.1315 | 0 | 8.5 | 0 | 2648.6886 | 52.97% | 2 | 52.97% | 52.97% | 0% | 0% | 18.9009 | 18.9009 | 0 | 0 | 37.8019 | 0 | 15574.2889 | 3114.8578 | 31.15% | 1 | 62.3% | 0% | 0% | 13.7211 | 0 | 0 | 13.7211 | 51.523
2007-09-02 17:00 | 9 | 2 | 17 | 245 | 5873 | 75.92 | 0 | 11789.5236 | 11789.5236 | -11789.5236 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14409.4177 | 14409.4177 | 0 | 8.5 | 0 | 2401.5696 | 48.03% | 1 | 96.06% | 0% | 0% | 0% | 74.3053 | 0 | 0 | 0 | 74.3053 | 0 | 14121.2294 | 2824.2459 | 28.24% | 1 | 56.48% | 0% | 0% | 10.9536 | 0 | 0 | 10.9536 | 85.2589
2007-09-02 18:00 | 9 | 2 | 18 | 245 | 5874 | 71.96 | 0 | 7955.179 | 7955.179 | -7955.179 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9722.9965 | 9722.9965 | 0 | 8.5 | 0 | 1620.4994 | 32.41% | 1 | 64.82% | 0% | 0% | 0% | 30.0658 | 0 | 0 | 0 | 30.0658 | 0 | 9528.5366 | 1905.7073 | 19.06% | 1 | 38.11% | 0% | 0% | 4.4321 | 0 | 0 | 4.4321 | 34.498
2007-09-02 19:00 | 9 | 2 | 19 | 245 | 5875 | 69.98 | 0 | 6139.1722 | 6139.1722 | -6139.1722 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7503.4326 | 7503.4326 | 0 | 8.5 | 0 | 1250.5721 | 30% | 1 | 50.02% | 0% | 0% | 0% | 16.5665 | 0 | 0 | 0 | 16.5665 | 0 | 7353.364 | 1470.6728 | 14.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8411
2007-09-02 20:00 | 9 | 2 | 20 | 245 | 5876 | 69.98 | 0 | 4045.5414 | 4045.5414 | -4045.5414 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4944.5505 | 4944.5505 | 0 | 8.5 | 0 | 824.0918 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4845.6595 | 969.1319 | 9.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 21:00 | 9 | 2 | 21 | 245 | 5877 | 62.96 | 0 | 1847.4529 | 1847.4529 | -1847.4529 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2257.998 | 2257.998 | 0 | 8.5 | 0 | 376.333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2212.8381 | 442.5676 | 4.426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 22:00 | 9 | 2 | 22 | 245 | 5878 | 62.96 | 0 | 551.8596 | 551.8596 | -551.8596 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 674.4951 | 674.4951 | 0 | 8.5 | 0 | 112.4158 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 661.0052 | 132.201 | 1.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-02 23:00 | 9 | 2 | 23 | 245 | 5879 | 62.96 | 0 | 395.326 | 395.326 | -395.326 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 483.1763 | 483.1763 | 0 | 8.5 | 0 | 80.5294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 473.5128 | 94.7026 | 0.947% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 | 9 | 3 | 0 | 246 | 5880 | 59 | 0 | 260.4976 | 260.4976 | -260.4976 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 318.386 | 318.386 | 0 | 8.5 | 0 | 53.0643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 312.0182 | 62.4036 | 0.624% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 01:00 | 9 | 3 | 1 | 246 | 5881 | 60.08 | 0 | 142.7368 | 142.7368 | -142.7368 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 174.4561 | 174.4561 | 0 | 8.5 | 0 | 29.076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 170.967 | 34.1934 | 0.3419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 02:00 | 9 | 3 | 2 | 246 | 5882 | 60.08 | 0 | 43.6835 | 43.6835 | -43.6835 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 53.3909 | 53.3909 | 0 | 8.5 | 0 | 8.8985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 52.3231 | 10.4646 | 0.1046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 03:00 | 9 | 3 | 3 | 246 | 5883 | 60.08 | 0 | 5.6617 | 5.6617 | -5.6617 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6.9198 | 6.9198 | 0 | 8.5 | 0 | 1.1533 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6.7814 | 1.3563 | 0.01356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 04:00 | 9 | 3 | 4 | 246 | 5884 | 59 | 4.6169 | 0 | 0 | 4.6169 | Heating | 4.0738 | 8.5 | 4.0738 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.81476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.1569 | 0 | 0.83138 | 0.008314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 05:00 | 9 | 3 | 5 | 246 | 5885 | 59 | 11.4351 | 0 | 0 | 11.4351 | Heating | 10.0898 | 8.5 | 10.0898 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.2957 | 0 | 2.0591 | 0.02059% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 06:00 | 9 | 3 | 6 | 246 | 5886 | 57.92 | 1339.067 | 188.3438 | 188.3438 | 1150.7232 | Heating | 1015.344 | 8.5 | 1015.344 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 203.0688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1036.0653 | 0 | 207.2131 | 2.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 07:00 | 9 | 3 | 7 | 246 | 5887 | 60.98 | 1051.2799 | 73.5627 | 73.5627 | 977.7172 | Heating | 862.6917 | 8.5 | 862.6917 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.5383 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 880.2976 | 0 | 176.0595 | 1.761% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 08:00 | 9 | 3 | 8 | 246 | 5888 | 60.98 | 697.4408 | 634.5656 | 634.5656 | 62.8751 | Heating | 55.4781 | 8.5 | 55.4781 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.0956 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.6103 | 0 | 11.3221 | 0.1132% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 09:00 | 9 | 3 | 9 | 246 | 5889 | 66.92 | 35.8965 | 1199.397 | 1199.397 | -1163.5005 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1465.9297 | 1465.9297 | 0 | 8.5 | 0 | 244.3216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1436.6111 | 287.3222 | 2.873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 10:00 | 9 | 3 | 10 | 246 | 5890 | 71.06 | 1.2614 | 1916.9743 | 1916.9743 | -1915.7129 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2342.9686 | 2342.9686 | 0 | 8.5 | 0 | 390.4948 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2296.1092 | 459.2218 | 4.592% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 11:00 | 9 | 3 | 11 | 246 | 5891 | 71.06 | 0.058509 | 2650.5688 | 2650.5688 | -2650.5103 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3239.5841 | 3239.5841 | 0 | 8.5 | 0 | 539.9307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3174.7924 | 634.9585 | 6.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 12:00 | 9 | 3 | 12 | 246 | 5892 | 78.98 | 0 | 3866.2534 | 3866.2534 | -3866.2534 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4725.4208 | 4725.4208 | 0 | 8.5 | 0 | 787.5701 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4630.9124 | 926.1825 | 9.262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 13:00 | 9 | 3 | 13 | 246 | 5893 | 80.06 | 0 | 5118.06 | 5118.06 | -5118.06 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6255.4067 | 6255.4067 | 0 | 8.5 | 0 | 1042.5678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6130.2985 | 1226.0597 | 12.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 14:00 | 9 | 3 | 14 | 246 | 5894 | 80.06 | 0 | 6428.253 | 6428.253 | -6428.253 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7856.7537 | 7856.7537 | 0 | 8.5 | 0 | 1309.459 | 30% | 1 | 52.38% | 0% | 0% | 0% | 18.4159 | 0 | 0 | 0 | 18.4159 | 0 | 7699.6186 | 1539.9237 | 15.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.6904
2007-09-03 15:00 | 9 | 3 | 15 | 246 | 5895 | 82.04 | 0 | 6851.4163 | 6851.4163 | -6851.4163 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8373.9533 | 8373.9533 | 0 | 8.5 | 0 | 1395.6589 | 30% | 1 | 55.83% | 0% | 0% | 0% | 21.3242 | 0 | 0 | 0 | 21.3242 | 0 | 8206.4742 | 1641.2948 | 16.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.5988
2007-09-03 16:00 | 9 | 3 | 16 | 246 | 5896 | 82.04 | 0 | 6763.8813 | 6763.8813 | -6763.8813 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8266.966 | 8266.966 | 0 | 8.5 | 0 | 1377.8277 | 30% | 1 | 55.11% | 0% | 0% | 0% | 20.7028 | 0 | 0 | 0 | 20.7028 | 0 | 8101.6267 | 1620.3253 | 16.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.9774
2007-09-03 17:00 | 9 | 3 | 17 | 246 | 5897 | 82.04 | 0 | 6128.9801 | 6128.9801 | -6128.9801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7490.9756 | 7490.9756 | 0 | 8.5 | 0 | 1248.4959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7341.1561 | 1468.2312 | 14.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 18:00 | 9 | 3 | 18 | 246 | 5898 | 78.98 | 0 | 3490.6608 | 3490.6608 | -3490.6608 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4266.3632 | 4266.3632 | 0 | 8.5 | 0 | 711.0605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4181.0359 | 836.2072 | 8.362% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 19:00 | 9 | 3 | 19 | 246 | 5899 | 73.04 | 0 | 1316.5632 | 1316.5632 | -1316.5632 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1609.1328 | 1609.1328 | 0 | 8.5 | 0 | 268.1888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1576.9502 | 315.39 | 3.154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 20:00 | 9 | 3 | 20 | 246 | 5900 | 73.04 | 0 | 436.8821 | 436.8821 | -436.8821 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 533.967 | 533.967 | 0 | 8.5 | 0 | 88.9945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 523.2877 | 104.6575 | 1.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 21:00 | 9 | 3 | 21 | 246 | 5901 | 69.08 | 3.0155 | 306.8525 | 306.8525 | -303.837 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 375.0419 | 375.0419 | 0 | 8.5 | 0 | 62.507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 367.5411 | 73.5082 | 0.7351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 22:00 | 9 | 3 | 22 | 246 | 5902 | 66.02 | 8.8648 | 0 | 0 | 8.8648 | Heating | 7.8219 | 8.5 | 7.8219 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.9815 | 0 | 1.5963 | 0.01596% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-03 23:00 | 9 | 3 | 23 | 246 | 5903 | 66.02 | 19.4778 | 0 | 0 | 19.4778 | Heating | 17.1863 | 8.5 | 17.1863 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.4373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.537 | 0 | 3.5074 | 0.03507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 | 9 | 4 | 0 | 247 | 5904 | 62.06 | 33.3217 | 0 | 0 | 33.3217 | Heating | 29.4015 | 8.5 | 29.4015 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.8803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 30.0015 | 0 | 6.0003 | 0.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 01:00 | 9 | 4 | 1 | 247 | 5905 | 62.06 | 52.0998 | 0 | 0 | 52.0998 | Heating | 45.9704 | 8.5 | 45.9704 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.1941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 46.9086 | 0 | 9.3817 | 0.09382% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 02:00 | 9 | 4 | 2 | 247 | 5906 | 62.06 | 86.7994 | 0 | 0 | 86.7994 | Heating | 76.5877 | 8.5 | 76.5877 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.3175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 78.1507 | 0 | 15.6301 | 0.1563% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 03:00 | 9 | 4 | 3 | 247 | 5907 | 64.94 | 121.671 | 0 | 0 | 121.671 | Heating | 107.3567 | 8.5 | 107.3567 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.4713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 109.5477 | 0 | 21.9095 | 0.2191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 04:00 | 9 | 4 | 4 | 247 | 5908 | 62.96 | 159.8104 | 0 | 0 | 159.8104 | Heating | 141.0092 | 8.5 | 141.0092 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.2018 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 143.8869 | 0 | 28.7774 | 0.2878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 05:00 | 9 | 4 | 5 | 247 | 5909 | 62.96 | 199.7712 | 0 | 0 | 199.7712 | Heating | 176.2687 | 8.5 | 176.2687 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.2537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 179.866 | 0 | 35.9732 | 0.3597% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 06:00 | 9 | 4 | 6 | 247 | 5910 | 60.98 | 4020.79 | 84.5398 | 84.5398 | 3936.2502 | Heating | 3473.1619 | 8.5 | 3473.1619 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 694.6324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3544.0428 | 0 | 708.8086 | 7.088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 07:00 | 9 | 4 | 7 | 247 | 5911 | 62.06 | 2556.2865 | 4.0321 | 4.0321 | 2552.2544 | Heating | 2251.9892 | 8.5 | 2251.9892 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 450.3978 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2297.9482 | 0 | 459.5896 | 4.596% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 08:00 | 9 | 4 | 8 | 247 | 5912 | 62.06 | 1578.5089 | 356.5214 | 356.5214 | 1221.9875 | Heating | 1078.2243 | 8.5 | 1078.2243 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.6449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1100.2288 | 0 | 220.0458 | 2.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 09:00 | 9 | 4 | 9 | 247 | 5913 | 66.02 | 199.895 | 1044.3749 | 1044.3749 | -844.4799 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1276.4582 | 1276.4582 | 0 | 8.5 | 0 | 212.743 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1250.9291 | 250.1858 | 2.502% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 10:00 | 9 | 4 | 10 | 247 | 5914 | 66.92 | 1.713 | 2656.0881 | 2656.0881 | -2654.3752 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3246.3299 | 3246.3299 | 0 | 8.5 | 0 | 541.055 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3181.4033 | 636.2807 | 6.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 11:00 | 9 | 4 | 11 | 247 | 5915 | 69.08 | 0 | 4514.6185 | 4514.6185 | -4514.6185 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5517.867 | 5517.867 | 0 | 8.5 | 0 | 919.6445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5407.5097 | 1081.5019 | 10.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 12:00 | 9 | 4 | 12 | 247 | 5916 | 71.96 | 0 | 5480.7661 | 5480.7661 | -5480.7661 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6698.7141 | 6698.7141 | 0 | 8.5 | 0 | 1116.4523 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6564.7398 | 1312.948 | 13.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 13:00 | 9 | 4 | 13 | 247 | 5917 | 73.04 | 0 | 6447.0174 | 6447.0174 | -6447.0174 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7879.6879 | 7879.6879 | 0 | 8.5 | 0 | 1313.2813 | 30% | 1 | 52.53% | 0% | 0% | 0% | 18.5398 | 0 | 0 | 0 | 18.5398 | 0 | 7722.0942 | 1544.4188 | 15.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.8143
2007-09-04 14:00 | 9 | 4 | 14 | 247 | 5918 | 73.04 | 0 | 7249.2956 | 7249.2956 | -7249.2956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8860.2502 | 8860.2502 | 0 | 8.5 | 0 | 1476.7084 | 30% | 1 | 59.07% | 0% | 0% | 0% | 24.2806 | 0 | 0 | 0 | 24.2806 | 0 | 8683.0452 | 1736.609 | 17.37% | 1 | 34.73% | 0% | 0% | 3.5793 | 0 | 0 | 3.5793 | 27.8599
2007-09-04 15:00 | 9 | 4 | 15 | 247 | 5919 | 73.94 | 0 | 7365.9827 | 7365.9827 | -7365.9827 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9002.8677 | 9002.8677 | 0 | 8.5 | 0 | 1500.478 | 30.01% | 1 | 60.02% | 0% | 0% | 0% | 25.1889 | 0 | 0 | 0 | 25.1889 | 0 | 8822.8104 | 1764.5621 | 17.65% | 1 | 35.29% | 0% | 0% | 3.7132 | 0 | 0 | 3.7132 | 28.9021
2007-09-04 16:00 | 9 | 4 | 16 | 247 | 5920 | 73.94 | 0 | 7169.0983 | 7169.0983 | -7169.0983 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8762.2312 | 8762.2312 | 0 | 8.5 | 0 | 1460.3719 | 30% | 1 | 58.41% | 0% | 0% | 0% | 23.6672 | 0 | 0 | 0 | 23.6672 | 0 | 8586.9866 | 1717.3973 | 17.17% | 1 | 34.35% | 0% | 0% | 3.4889 | 0 | 0 | 3.4889 | 27.1561
2007-09-04 17:00 | 9 | 4 | 17 | 247 | 5921 | 73.94 | 0 | 6629.9237 | 6629.9237 | -6629.9237 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8103.24 | 8103.24 | 0 | 8.5 | 0 | 1350.54 | 30% | 1 | 54.02% | 0% | 0% | 0% | 19.7719 | 0 | 0 | 0 | 19.7719 | 0 | 7941.1752 | 1588.235 | 15.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.0464
2007-09-04 18:00 | 9 | 4 | 18 | 247 | 5922 | 69.08 | 0 | 3838.1116 | 3838.1116 | -3838.1116 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4691.0253 | 4691.0253 | 0 | 8.5 | 0 | 781.8376 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4597.2048 | 919.441 | 9.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 19:00 | 9 | 4 | 19 | 247 | 5923 | 66.92 | 0 | 2378.5429 | 2378.5429 | -2378.5429 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2907.108 | 2907.108 | 0 | 8.5 | 0 | 484.518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2848.9659 | 569.7932 | 5.698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 20:00 | 9 | 4 | 20 | 247 | 5924 | 66.92 | 0 | 1096.124 | 1096.124 | -1096.124 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1339.7072 | 1339.7072 | 0 | 8.5 | 0 | 223.2845 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1312.913 | 262.5826 | 2.626% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 21:00 | 9 | 4 | 21 | 247 | 5925 | 64.94 | 0 | 443.6128 | 443.6128 | -443.6128 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 542.1935 | 542.1935 | 0 | 8.5 | 0 | 90.3656 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 531.3496 | 106.2699 | 1.063% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 22:00 | 9 | 4 | 22 | 247 | 5926 | 64.04 | 0 | 28.5959 | 28.5959 | -28.5959 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 34.9506 | 34.9506 | 0 | 8.5 | 0 | 5.8251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 34.2515 | 6.8503 | 0.0685% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-04 23:00 | 9 | 4 | 23 | 247 | 5927 | 64.04 | 0 | 12.5694 | 12.5694 | -12.5694 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15.3625 | 15.3625 | 0 | 8.5 | 0 | 2.5604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 15.0553 | 3.0111 | 0.03011% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 | 9 | 5 | 0 | 248 | 5928 | 57.92 | 0 | 0.49713 | 0.49713 | -0.49713 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0.6076 | 0.6076 | 0 | 8.5 | 0 | 0.10127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 0.59545 | 0.11909 | 0.001191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 01:00 | 9 | 5 | 1 | 248 | 5929 | 55.04 | 0.584 | 0 | 0 | 0.584 | Heating | 0.51529 | 8.5 | 0.51529 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.10306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.52581 | 0 | 0.10516 | 0.001052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 02:00 | 9 | 5 | 2 | 248 | 5930 | 55.04 | 2.6455 | 0 | 0 | 2.6455 | Heating | 2.3343 | 8.5 | 2.3343 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.46686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.3819 | 0 | 0.47639 | 0.004764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 03:00 | 9 | 5 | 3 | 248 | 5931 | 51.98 | 5.2569 | 0 | 0 | 5.2569 | Heating | 4.6384 | 8.5 | 4.6384 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.92769 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4.7331 | 0 | 0.94662 | 0.009466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 04:00 | 9 | 5 | 4 | 248 | 5932 | 50 | 8.5529 | 0 | 0 | 8.5529 | Heating | 7.5467 | 8.5 | 7.5467 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.7007 | 0 | 1.5401 | 0.0154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 05:00 | 9 | 5 | 5 | 248 | 5933 | 50 | 12.1612 | 0 | 0 | 12.1612 | Heating | 10.7305 | 8.5 | 10.7305 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.1461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.9495 | 0 | 2.1899 | 0.0219% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 06:00 | 9 | 5 | 6 | 248 | 5934 | 48.92 | 1147.3596 | 207.8781 | 207.8781 | 939.4815 | Heating | 828.9543 | 8.5 | 828.9543 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.7909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 845.8717 | 0 | 169.1743 | 1.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 07:00 | 9 | 5 | 7 | 248 | 5935 | 53.96 | 699.9698 | 201.1527 | 201.1527 | 498.8171 | Heating | 440.1327 | 8.5 | 440.1327 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.0265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 449.115 | 0 | 89.823 | 0.8982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 08:00 | 9 | 5 | 8 | 248 | 5936 | 53.96 | 167.1299 | 1374.9768 | 1374.9768 | -1207.8469 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1680.5272 | 1680.5272 | 0 | 8.5 | 0 | 280.0879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1646.9166 | 329.3833 | 3.294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 09:00 | 9 | 5 | 9 | 248 | 5937 | 62.06 | 3.5735 | 2173.444 | 2173.444 | -2169.8704 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2656.4315 | 2656.4315 | 0 | 8.5 | 0 | 442.7386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2603.3029 | 520.6606 | 5.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 10:00 | 9 | 5 | 10 | 248 | 5938 | 64.04 | 0.50324 | 2607.3225 | 2607.3225 | -2606.8193 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3186.7276 | 3186.7276 | 0 | 8.5 | 0 | 531.1213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3122.993 | 624.5986 | 6.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 11:00 | 9 | 5 | 11 | 248 | 5939 | 66.92 | 0 | 3681.1636 | 3681.1636 | -3681.1636 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4499.2 | 4499.2 | 0 | 8.5 | 0 | 749.8667 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4409.216 | 881.8432 | 8.818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 12:00 | 9 | 5 | 12 | 248 | 5940 | 68 | 0 | 4846.9238 | 4846.9238 | -4846.9238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5924.018 | 5924.018 | 0 | 8.5 | 0 | 987.3363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5805.5376 | 1161.1075 | 11.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 13:00 | 9 | 5 | 13 | 248 | 5941 | 69.98 | 0 | 5516.1456 | 5516.1456 | -5516.1456 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6741.9558 | 6741.9558 | 0 | 8.5 | 0 | 1123.6593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6607.1167 | 1321.4233 | 13.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 14:00 | 9 | 5 | 14 | 248 | 5942 | 71.96 | 0 | 6458.4586 | 6458.4586 | -6458.4586 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7893.6716 | 7893.6716 | 0 | 8.5 | 0 | 1315.6119 | 30% | 1 | 52.62% | 0% | 0% | 0% | 18.6155 | 0 | 0 | 0 | 18.6155 | 0 | 7735.7981 | 1547.1596 | 15.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.8901
2007-09-05 15:00 | 9 | 5 | 15 | 248 | 5943 | 73.04 | 0 | 7332.4071 | 7332.4071 | -7332.4071 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8961.8309 | 8961.8309 | 0 | 8.5 | 0 | 1493.6385 | 30% | 1 | 59.75% | 0% | 0% | 0% | 24.9256 | 0 | 0 | 0 | 24.9256 | 0 | 8782.5943 | 1756.5189 | 17.57% | 1 | 35.13% | 0% | 0% | 3.6744 | 0 | 0 | 3.6744 | 28.6
2007-09-05 16:00 | 9 | 5 | 16 | 248 | 5944 | 73.04 | 0 | 7885.1283 | 7885.1283 | -7885.1283 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9637.3791 | 9637.3791 | 0 | 8.5 | 0 | 1606.2298 | 32.12% | 1 | 64.25% | 0% | 0% | 0% | 29.4604 | 0 | 0 | 0 | 29.4604 | 0 | 9444.6315 | 1888.9263 | 18.89% | 1 | 37.78% | 0% | 0% | 4.3429 | 0 | 0 | 4.3429 | 33.8033
2007-09-05 17:00 | 9 | 5 | 17 | 248 | 5945 | 73.04 | 0 | 7676.769 | 7676.769 | -7676.769 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9382.7177 | 9382.7177 | 0 | 8.5 | 0 | 1563.7863 | 31.28% | 1 | 62.55% | 0% | 0% | 0% | 27.7006 | 0 | 0 | 0 | 27.7006 | 0 | 9195.0633 | 1839.0127 | 18.39% | 1 | 36.78% | 0% | 0% | 4.0834 | 0 | 0 | 4.0834 | 31.784
2007-09-05 18:00 | 9 | 5 | 18 | 248 | 5946 | 69.98 | 0 | 4812.712 | 4812.712 | -4812.712 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5882.2035 | 5882.2035 | 0 | 8.5 | 0 | 980.3673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5764.5594 | 1152.9119 | 11.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 19:00 | 9 | 5 | 19 | 248 | 5947 | 64.94 | 0 | 3869.2387 | 3869.2387 | -3869.2387 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4729.0696 | 4729.0696 | 0 | 8.5 | 0 | 788.1783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4634.4882 | 926.8976 | 9.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 20:00 | 9 | 5 | 20 | 248 | 5948 | 64.94 | 0 | 3059.9423 | 3059.9423 | -3059.9423 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3739.9295 | 3739.9295 | 0 | 8.5 | 0 | 623.3216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3665.1309 | 733.0262 | 7.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 21:00 | 9 | 5 | 21 | 248 | 5949 | 60.08 | 0 | 1590.1849 | 1590.1849 | -1590.1849 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1943.5594 | 1943.5594 | 0 | 8.5 | 0 | 323.9266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1904.6882 | 380.9376 | 3.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 22:00 | 9 | 5 | 22 | 248 | 5950 | 59 | 0 | 248.4177 | 248.4177 | -248.4177 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 303.6216 | 303.6216 | 0 | 8.5 | 0 | 50.6036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 297.5492 | 59.5098 | 0.5951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-05 23:00 | 9 | 5 | 23 | 248 | 5951 | 59 | 0 | 107.377 | 107.377 | -107.377 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 131.2385 | 131.2385 | 0 | 8.5 | 0 | 21.8731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 128.6138 | 25.7228 | 0.2572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 | 9 | 6 | 0 | 249 | 5952 | 60.98 | 0 | 26.1152 | 26.1152 | -26.1152 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 31.9186 | 31.9186 | 0 | 8.5 | 0 | 5.3198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 31.2803 | 6.2561 | 0.06256% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 01:00 | 9 | 6 | 1 | 249 | 5953 | 60.08 | 0 | 2.2719 | 2.2719 | -2.2719 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.7768 | 2.7768 | 0 | 8.5 | 0 | 0.4628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.7212 | 0.54425 | 0.005442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 02:00 | 9 | 6 | 2 | 249 | 5954 | 59 | 0.42276 | 0 | 0 | 0.42276 | Heating | 0.37303 | 8.5 | 0.37303 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.074606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.38064 | 0 | 0.076128 | 0.0007613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 03:00 | 9 | 6 | 3 | 249 | 5955 | 57.92 | 2.3668 | 0 | 0 | 2.3668 | Heating | 2.0883 | 8.5 | 2.0883 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.41767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.1309 | 0 | 0.42619 | 0.004262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 04:00 | 9 | 6 | 4 | 249 | 5956 | 57.92 | 2.1583 | 0 | 0 | 2.1583 | Heating | 1.9044 | 8.5 | 1.9044 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.38087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.9432 | 0 | 0.38865 | 0.003886% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 05:00 | 9 | 6 | 5 | 249 | 5957 | 57.92 | 0.38924 | 0 | 0 | 0.38924 | Heating | 0.34345 | 8.5 | 0.34345 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.06869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.35046 | 0 | 0.070092 | 0.0007009% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 06:00 | 9 | 6 | 6 | 249 | 5958 | 59 | 751.6946 | 514.302 | 514.302 | 237.3926 | Heating | 209.4641 | 8.5 | 209.4641 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.8928 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 213.7389 | 0 | 42.7478 | 0.4275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 07:00 | 9 | 6 | 7 | 249 | 5959 | 62.96 | 304.3989 | 493.347 | 493.347 | -188.9481 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 602.9796 | 602.9796 | 0 | 8.5 | 0 | 100.4966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 590.92 | 118.184 | 1.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 08:00 | 9 | 6 | 8 | 249 | 5960 | 62.96 | 0 | 3182.8125 | 3182.8125 | -3182.8125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3890.1042 | 3890.1042 | 0 | 8.5 | 0 | 648.3507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3812.3021 | 762.4604 | 7.625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 09:00 | 9 | 6 | 9 | 249 | 5961 | 69.08 | 0 | 4703.0477 | 4703.0477 | -4703.0477 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5748.1694 | 5748.1694 | 0 | 8.5 | 0 | 958.0282 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5633.206 | 1126.6412 | 11.27% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 10:00 | 9 | 6 | 10 | 249 | 5962 | 73.94 | 0 | 6738.5243 | 6738.5243 | -6738.5243 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8235.9741 | 8235.9741 | 0 | 8.5 | 0 | 1372.6624 | 30% | 1 | 54.91% | 0% | 0% | 0% | 20.5247 | 0 | 0 | 0 | 20.5247 | 0 | 8071.2547 | 1614.2509 | 16.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.7993
2007-09-06 11:00 | 9 | 6 | 11 | 249 | 5963 | 73.94 | 0 | 9183.3056 | 9183.3056 | -9183.3056 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11224.0402 | 11224.0402 | 0 | 8.5 | 0 | 1870.6734 | 37.41% | 1 | 74.83% | 0% | 0% | 0% | 41.8289 | 0 | 0 | 0 | 41.8289 | 0 | 10999.5594 | 2199.9119 | 22% | 1 | 44% | 0% | 0% | 6.1662 | 0 | 0 | 6.1662 | 47.995
2007-09-06 12:00 | 9 | 6 | 12 | 249 | 5964 | 78.08 | 0 | 10797.4025 | 10797.4025 | -10797.4025 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13196.8252 | 13196.8252 | 0 | 8.5 | 0 | 2199.4709 | 43.99% | 1 | 87.98% | 0% | 0% | 0% | 60.7034 | 0 | 0 | 0 | 60.7034 | 0 | 12932.8887 | 2586.5777 | 25.87% | 1 | 51.73% | 0% | 0% | 8.9485 | 0 | 0 | 8.9485 | 69.6519
2007-09-06 13:00 | 9 | 6 | 13 | 249 | 5965 | 80.06 | 0 | 12127.3633 | 12127.3633 | -12127.3633 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14822.3329 | 14822.3329 | 0 | 8.5 | 0 | 2470.3888 | 49.41% | 1 | 98.82% | 0% | 0% | 0% | 79.2942 | 0 | 0 | 0 | 79.2942 | 0 | 14525.8863 | 2905.1773 | 29.05% | 1 | 58.1% | 0% | 0% | 11.689 | 0 | 0 | 11.689 | 90.9832
2007-09-06 14:00 | 9 | 6 | 14 | 249 | 5966 | 80.06 | 0 | 12555.0097 | 12555.0097 | -12555.0097 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15345.0118 | 15345.0118 | 0 | 8.5 | 0 | 2557.502 | 51.15% | 2 | 51.15% | 51.15% | 0% | 0% | 17.4377 | 17.4377 | 0 | 0 | 34.8754 | 0 | 15038.1116 | 3007.6223 | 30.08% | 1 | 60.15% | 0% | 0% | 12.6589 | 0 | 0 | 12.6589 | 47.5343
2007-09-06 15:00 | 9 | 6 | 15 | 249 | 5967 | 80.96 | 0 | 13044.9885 | 13044.9885 | -13044.9885 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15943.8748 | 15943.8748 | 0 | 8.5 | 0 | 2657.3125 | 53.15% | 2 | 53.15% | 53.15% | 0% | 0% | 19.0428 | 19.0428 | 0 | 0 | 38.0855 | 0 | 15624.9973 | 3124.9995 | 31.25% | 1 | 62.5% | 0% | 0% | 13.8241 | 0 | 0 | 13.8241 | 51.9096
2007-09-06 16:00 | 9 | 6 | 16 | 249 | 5968 | 80.96 | 0 | 12628.8828 | 12628.8828 | -12628.8828 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15435.3013 | 15435.3013 | 0 | 8.5 | 0 | 2572.5502 | 51.45% | 2 | 51.45% | 51.45% | 0% | 0% | 17.6746 | 17.6746 | 0 | 0 | 35.3491 | 0 | 15126.5952 | 3025.319 | 30.25% | 1 | 60.51% | 0% | 0% | 12.8309 | 0 | 0 | 12.8309 | 48.18
2007-09-06 17:00 | 9 | 6 | 17 | 249 | 5969 | 80.96 | 0 | 11345.664 | 11345.664 | -11345.664 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13866.9226 | 13866.9226 | 0 | 8.5 | 0 | 2311.1538 | 46.22% | 1 | 92.45% | 0% | 0% | 0% | 68.0279 | 0 | 0 | 0 | 68.0279 | 0 | 13589.5842 | 2717.9168 | 27.18% | 1 | 54.36% | 0% | 0% | 10.0283 | 0 | 0 | 10.0283 | 78.0562
2007-09-06 18:00 | 9 | 6 | 18 | 249 | 5970 | 78.98 | 0 | 6925.7211 | 6925.7211 | -6925.7211 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8464.7702 | 8464.7702 | 0 | 8.5 | 0 | 1410.795 | 30% | 1 | 56.43% | 0% | 0% | 0% | 21.8599 | 0 | 0 | 0 | 21.8599 | 0 | 8295.4748 | 1659.095 | 16.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.1344
2007-09-06 19:00 | 9 | 6 | 19 | 249 | 5971 | 77 | 0 | 5617.6835 | 5617.6835 | -5617.6835 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6866.0577 | 6866.0577 | 0 | 8.5 | 0 | 1144.3429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6728.7365 | 1345.7473 | 13.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 20:00 | 9 | 6 | 20 | 249 | 5972 | 77 | 0 | 4191.1445 | 4191.1445 | -4191.1445 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5122.51 | 5122.51 | 0 | 8.5 | 0 | 853.7517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5020.0598 | 1004.012 | 10.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 21:00 | 9 | 6 | 21 | 249 | 5973 | 73.04 | 0 | 2140.6005 | 2140.6005 | -2140.6005 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2616.2895 | 2616.2895 | 0 | 8.5 | 0 | 436.0482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2563.9637 | 512.7927 | 5.128% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 22:00 | 9 | 6 | 22 | 249 | 5974 | 71.96 | 0 | 644.1325 | 644.1325 | -644.1325 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 787.273 | 787.273 | 0 | 8.5 | 0 | 131.2122 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 771.5276 | 154.3055 | 1.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-06 23:00 | 9 | 6 | 23 | 249 | 5975 | 71.96 | 0 | 723.0787 | 723.0787 | -723.0787 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 883.7629 | 883.7629 | 0 | 8.5 | 0 | 147.2938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 866.0876 | 173.2175 | 1.732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 | 9 | 7 | 0 | 250 | 5976 | 69.98 | 0 | 585.7362 | 585.7362 | -585.7362 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 715.8998 | 715.8998 | 0 | 8.5 | 0 | 119.3166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 701.5818 | 140.3164 | 1.403% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 01:00 | 9 | 7 | 1 | 250 | 5977 | 69.08 | 0 | 525.5203 | 525.5203 | -525.5203 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 642.3026 | 642.3026 | 0 | 8.5 | 0 | 107.0504 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 629.4566 | 125.8913 | 1.259% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 02:00 | 9 | 7 | 2 | 250 | 5978 | 69.08 | 0 | 282.4643 | 282.4643 | -282.4643 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 345.2341 | 345.2341 | 0 | 8.5 | 0 | 57.539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 338.3294 | 67.6659 | 0.6767% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 03:00 | 9 | 7 | 3 | 250 | 5979 | 68 | 0 | 427.3206 | 427.3206 | -427.3206 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 522.2808 | 522.2808 | 0 | 8.5 | 0 | 87.0468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 511.8352 | 102.367 | 1.024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 04:00 | 9 | 7 | 4 | 250 | 5980 | 66.92 | 0 | 501.6169 | 501.6169 | -501.6169 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 613.0874 | 613.0874 | 0 | 8.5 | 0 | 102.1812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 600.8256 | 120.1651 | 1.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 05:00 | 9 | 7 | 5 | 250 | 5981 | 66.92 | 0 | 340.395 | 340.395 | -340.395 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 416.0383 | 416.0383 | 0 | 8.5 | 0 | 69.3397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 407.7176 | 81.5435 | 0.8154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 06:00 | 9 | 7 | 6 | 250 | 5982 | 66.92 | 13.0899 | 1431.0249 | 1431.0249 | -1417.935 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1749.0304 | 1749.0304 | 0 | 8.5 | 0 | 291.5051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1714.0498 | 342.81 | 3.428% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 07:00 | 9 | 7 | 7 | 250 | 5983 | 69.08 | 0 | 1054.4264 | 1054.4264 | -1054.4264 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1288.7434 | 1288.7434 | 0 | 8.5 | 0 | 214.7906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1262.9685 | 252.5937 | 2.526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 08:00 | 9 | 7 | 8 | 250 | 5984 | 69.08 | 0 | 1482.1798 | 1482.1798 | -1482.1798 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1811.553 | 1811.553 | 0 | 8.5 | 0 | 301.9255 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1775.322 | 355.0644 | 3.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 09:00 | 9 | 7 | 9 | 250 | 5985 | 73.04 | 0 | 1919.479 | 1919.479 | -1919.479 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2346.0299 | 2346.0299 | 0 | 8.5 | 0 | 391.005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2299.1093 | 459.8219 | 4.598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 10:00 | 9 | 7 | 10 | 250 | 5986 | 77 | 0 | 2504.1105 | 2504.1105 | -2504.1105 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3060.5796 | 3060.5796 | 0 | 8.5 | 0 | 510.0966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2999.368 | 599.8736 | 5.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 11:00 | 9 | 7 | 11 | 250 | 5987 | 77 | 0 | 3468.3971 | 3468.3971 | -3468.3971 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4239.152 | 4239.152 | 0 | 8.5 | 0 | 706.5253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4154.369 | 830.8738 | 8.309% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 12:00 | 9 | 7 | 12 | 250 | 5988 | 84.02 | 0 | 4212.3907 | 4212.3907 | -4212.3907 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5148.4775 | 5148.4775 | 0 | 8.5 | 0 | 858.0796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5045.5079 | 1009.1016 | 10.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 13:00 | 9 | 7 | 13 | 250 | 5989 | 87.08 | 0 | 5132.2985 | 5132.2985 | -5132.2985 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6272.8092 | 6272.8092 | 0 | 8.5 | 0 | 1045.4682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6147.353 | 1229.4706 | 12.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 14:00 | 9 | 7 | 14 | 250 | 5990 | 87.08 | 0 | 5293.8233 | 5293.8233 | -5293.8233 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6470.2285 | 6470.2285 | 0 | 8.5 | 0 | 1078.3714 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6340.8239 | 1268.1648 | 12.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 15:00 | 9 | 7 | 15 | 250 | 5991 | 89.06 | 0 | 5348.9755 | 5348.9755 | -5348.9755 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6537.6367 | 6537.6367 | 0 | 8.5 | 0 | 1089.6061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6406.8839 | 1281.3768 | 12.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 16:00 | 9 | 7 | 16 | 250 | 5992 | 87.98 | 0 | 5876.1296 | 5876.1296 | -5876.1296 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7181.9361 | 7181.9361 | 0 | 8.5 | 0 | 1196.9894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7038.2974 | 1407.6595 | 14.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 17:00 | 9 | 7 | 17 | 250 | 5993 | 87.98 | 0 | 6082.61 | 6082.61 | -6082.61 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7434.3011 | 7434.3011 | 0 | 8.5 | 0 | 1239.0502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7285.615 | 1457.123 | 14.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 18:00 | 9 | 7 | 18 | 250 | 5994 | 84.02 | 0 | 1702.3928 | 1702.3928 | -1702.3928 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2080.7023 | 2080.7023 | 0 | 8.5 | 0 | 346.7837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2039.0882 | 407.8176 | 4.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 19:00 | 9 | 7 | 19 | 250 | 5995 | 82.94 | 0 | 283.462 | 283.462 | -283.462 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 346.4536 | 346.4536 | 0 | 8.5 | 0 | 57.7423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 339.5245 | 67.9049 | 0.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 20:00 | 9 | 7 | 20 | 250 | 5996 | 82.94 | 0 | 138.639 | 138.639 | -138.639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 169.4477 | 169.4477 | 0 | 8.5 | 0 | 28.2413 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 166.0587 | 33.2117 | 0.3321% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 21:00 | 9 | 7 | 21 | 250 | 5997 | 80.06 | 42.7088 | 50.8041 | 50.8041 | -8.0953 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 62.0939 | 62.0939 | 0 | 8.5 | 0 | 10.349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 60.852 | 12.1704 | 0.1217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 22:00 | 9 | 7 | 22 | 250 | 5998 | 78.08 | 1.5613 | 2.2307 | 2.2307 | -0.66939 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2.7264 | 2.7264 | 0 | 8.5 | 0 | 0.45439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2.6718 | 0.53437 | 0.005344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-07 23:00 | 9 | 7 | 23 | 250 | 5999 | 78.08 | 9.3999 | 0 | 0 | 9.3999 | Heating | 8.294 | 8.5 | 8.294 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.6588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 8.4633 | 0 | 1.6927 | 0.01693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 | 9 | 8 | 0 | 251 | 6000 | 75.02 | 18.1439 | 0 | 0 | 18.1439 | Heating | 16.0093 | 8.5 | 16.0093 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.2019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.336 | 0 | 3.2672 | 0.03267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 01:00 | 9 | 8 | 1 | 251 | 6001 | 75.02 | 30.9814 | 0 | 0 | 30.9814 | Heating | 27.3366 | 8.5 | 27.3366 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.4673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 27.8944 | 0 | 5.5789 | 0.05579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 02:01 | 9 | 8 | 2 | 251 | 6002 | 75.02 | 48.0814 | 0 | 0 | 48.0814 | Heating | 42.4248 | 8.5 | 42.4248 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.2906 | 0 | 8.6581 | 0.08658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 03:01 | 9 | 8 | 3 | 251 | 6003 | 75.02 | 89.1218 | 0 | 0 | 89.1218 | Heating | 78.6369 | 8.5 | 78.6369 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.7274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 80.2417 | 0 | 16.0483 | 0.1605% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 04:01 | 9 | 8 | 4 | 251 | 6004 | 73.94 | 132.4451 | 0 | 0 | 132.4451 | Heating | 116.8633 | 8.5 | 116.8633 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.3727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 119.2483 | 0 | 23.8497 | 0.2385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 05:01 | 9 | 8 | 5 | 251 | 6005 | 73.94 | 182.4196 | 0 | 0 | 182.4196 | Heating | 160.9585 | 8.5 | 160.9585 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.1917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 164.2434 | 0 | 32.8487 | 0.3285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 06:01 | 9 | 8 | 6 | 251 | 6006 | 73.04 | 212.8986 | 0 | 0 | 212.8986 | Heating | 187.8517 | 8.5 | 187.8517 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 37.5703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 191.6854 | 0 | 38.3371 | 0.3834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 07:01 | 9 | 8 | 7 | 251 | 6007 | 75.02 | 186.5224 | 0 | 0 | 186.5224 | Heating | 164.5786 | 8.5 | 164.5786 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.9157 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 167.9374 | 0 | 33.5875 | 0.3359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 08:01 | 9 | 8 | 8 | 251 | 6008 | 75.02 | 3656.4597 | 0 | 0 | 3656.4597 | Heating | 3226.288 | 8.5 | 3226.288 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 645.2576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3292.1306 | 0 | 658.4261 | 6.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 09:01 | 9 | 8 | 9 | 251 | 6009 | 77 | 2113.1161 | 0 | 0 | 2113.1161 | Heating | 1864.5142 | 8.5 | 1864.5142 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.9028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1902.5655 | 0 | 380.5131 | 3.805% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 10:01 | 9 | 8 | 10 | 251 | 6010 | 78.08 | 1263.7858 | 0 | 0 | 1263.7858 | Heating | 1115.1051 | 8.5 | 1115.1051 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1137.8624 | 0 | 227.5725 | 2.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 11:01 | 9 | 8 | 11 | 251 | 6011 | 78.08 | 647.7117 | 0 | 0 | 647.7117 | Heating | 571.5103 | 8.5 | 571.5103 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.3021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 583.1738 | 0 | 116.6348 | 1.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 12:01 | 9 | 8 | 12 | 251 | 6012 | 82.04 | 42.1383 | 0 | 0 | 42.1383 | Heating | 37.1809 | 8.5 | 37.1809 | 0 | 9.6047 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.4362 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 37.9397 | 0 | 7.5879 | 0.07588% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 13:01 | 9 | 8 | 13 | 251 | 6013 | 84.02 | 8.2557 | 0 | 0 | 8.2557 | Heating | 7.2845 | 8.5 | 7.2845 | 0 | 10.0848 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4569 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.4331 | 0 | 1.4866 | 0.01487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 14:01 | 9 | 8 | 14 | 251 | 6014 | 84.02 | 1.1733 | 3.5113 | 3.5113 | -2.3379 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4.2916 | 4.2916 | 0 | 8.5 | 0 | 0.71526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4.2057 | 0.84115 | 0.008411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 15:01 | 9 | 8 | 15 | 251 | 6015 | 84.02 | 0 | 18.757 | 18.757 | -18.757 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 22.9252 | 22.9252 | 0 | 8.5 | 0 | 3.8209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 22.4667 | 4.4933 | 0.04493% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 16:01 | 9 | 8 | 16 | 251 | 6016 | 80.96 | 0 | 113.4783 | 113.4783 | -113.4783 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 138.6956 | 138.6956 | 0 | 8.5 | 0 | 23.1159 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 135.9217 | 27.1843 | 0.2718% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 17:01 | 9 | 8 | 17 | 251 | 6017 | 80.96 | 0 | 97.5198 | 97.5198 | -97.5198 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 119.1909 | 119.1909 | 0 | 8.5 | 0 | 19.8651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 116.8071 | 23.3614 | 0.2336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 18:01 | 9 | 8 | 18 | 251 | 6018 | 78.08 | 0 | 75.0519 | 75.0519 | -75.0519 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 91.7302 | 91.7302 | 0 | 8.5 | 0 | 15.2884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 89.8955 | 17.9791 | 0.1798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 19:01 | 9 | 8 | 19 | 251 | 6019 | 77 | 6.7734 | 5.8803 | 5.8803 | 0.89312 | Heating | 0.78805 | 8.5 | 0.78805 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.15761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.80413 | 0 | 0.16083 | 0.001608% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 20:01 | 9 | 8 | 20 | 251 | 6020 | 77 | 23.2661 | 0 | 0 | 23.2661 | Heating | 20.5289 | 8.5 | 20.5289 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.1058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.9479 | 0 | 4.1896 | 0.0419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 21:01 | 9 | 8 | 21 | 251 | 6021 | 73.4 | 52.6269 | 0 | 0 | 52.6269 | Heating | 46.4355 | 8.5 | 46.4355 | 0 | 7.7605 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.2871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.3831 | 0 | 9.4766 | 0.09477% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 22:01 | 9 | 8 | 22 | 251 | 6022 | 73.04 | 100.7948 | 0 | 0 | 100.7948 | Heating | 88.9365 | 8.5 | 88.9365 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.7873 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 90.7516 | 0 | 18.1503 | 0.1815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-08 23:01 | 9 | 8 | 23 | 251 | 6023 | 73.04 | 159.0225 | 0 | 0 | 159.0225 | Heating | 140.314 | 8.5 | 140.314 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.0628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 143.1775 | 0 | 28.6355 | 0.2864% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 00:01 | 9 | 9 | 0 | 252 | 6024 | 71.6 | 251.5173 | 0 | 0 | 251.5173 | Heating | 221.927 | 8.5 | 221.927 | 0 | 7.4249 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.3854 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 226.4562 | 0 | 45.2912 | 0.4529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 01:01 | 9 | 9 | 1 | 252 | 6025 | 69.8 | 310.8832 | 0 | 0 | 310.8832 | Heating | 274.3087 | 8.5 | 274.3087 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.8617 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 279.9068 | 0 | 55.9814 | 0.5598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 02:01 | 9 | 9 | 2 | 252 | 6026 | 68 | 362.548 | 0 | 0 | 362.548 | Heating | 319.8953 | 8.5 | 319.8953 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.9791 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 326.4238 | 0 | 65.2848 | 0.6528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 03:01 | 9 | 9 | 3 | 252 | 6027 | 66.92 | 427.4781 | 0 | 0 | 427.4781 | Heating | 377.1865 | 8.5 | 377.1865 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.4373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 384.8842 | 0 | 76.9768 | 0.7698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 04:01 | 9 | 9 | 4 | 252 | 6028 | 66.92 | 484.6347 | 0 | 0 | 484.6347 | Heating | 427.6188 | 8.5 | 427.6188 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.5238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 436.3458 | 0 | 87.2692 | 0.8727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 05:01 | 9 | 9 | 5 | 252 | 6029 | 66.92 | 542.1278 | 0 | 0 | 542.1278 | Heating | 478.3481 | 8.5 | 478.3481 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.6696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 488.1103 | 0 | 97.6221 | 0.9762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 06:01 | 9 | 9 | 6 | 252 | 6030 | 64.4 | 6109.1826 | 0 | 0 | 6109.1826 | Heating | 5390.4552 | 8.5 | 5390.4552 | 0 | 6.2364 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1078.091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5500.4645 | 0 | 1100.0929 | 11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 07:01 | 9 | 9 | 7 | 252 | 6031 | 62.6 | 3776.7948 | 0 | 0 | 3776.7948 | Heating | 3332.466 | 8.5 | 3332.466 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 666.4932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3400.4755 | 0 | 680.0951 | 6.801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 08:01 | 9 | 9 | 8 | 252 | 6032 | 62.96 | 2291.9286 | 24.0423 | 24.0423 | 2267.8863 | Heating | 2001.0761 | 8.5 | 2001.0761 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 400.2152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2041.9144 | 0 | 408.3829 | 4.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 09:01 | 9 | 9 | 9 | 252 | 6033 | 64.04 | 687.1634 | 145.8297 | 145.8297 | 541.3337 | Heating | 477.6474 | 8.5 | 477.6474 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.5295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 487.3953 | 0 | 97.4791 | 0.9748% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 10:01 | 9 | 9 | 10 | 252 | 6034 | 64.4 | 57.8968 | 431.6561 | 431.6561 | -373.7593 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 527.5797 | 527.5797 | 0 | 8.5 | 0 | 87.9299 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 517.0281 | 103.4056 | 1.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 11:01 | 9 | 9 | 11 | 252 | 6035 | 64.04 | 11.4728 | 928.65 | 928.65 | -917.1772 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1135.0167 | 1135.0167 | 0 | 8.5 | 0 | 189.1695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1112.3164 | 222.4633 | 2.225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 12:01 | 9 | 9 | 12 | 252 | 6036 | 62.06 | 1.4925 | 1606.7235 | 1606.7235 | -1605.231 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1963.7731 | 1963.7731 | 0 | 8.5 | 0 | 327.2955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1924.4977 | 384.8995 | 3.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 13:01 | 9 | 9 | 13 | 252 | 6037 | 60.8 | 0 | 2552.3481 | 2552.3481 | -2552.3481 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3119.5366 | 3119.5366 | 0 | 8.5 | 0 | 519.9228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3057.1458 | 611.4292 | 6.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 14:01 | 9 | 9 | 14 | 252 | 6038 | 62.6 | 1.8978 | 2305.1038 | 2305.1038 | -2303.206 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2817.3491 | 2817.3491 | 0 | 8.5 | 0 | 469.5582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2761.0021 | 552.2004 | 5.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 15:01 | 9 | 9 | 15 | 252 | 6039 | 62.96 | 14.4863 | 1190.5522 | 1190.5522 | -1176.0659 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1455.1193 | 1455.1193 | 0 | 8.5 | 0 | 242.5199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1426.0169 | 285.2034 | 2.852% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 16:01 | 9 | 9 | 16 | 252 | 6040 | 62.6 | 38.2038 | 565.8568 | 565.8568 | -527.653 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 691.6027 | 691.6027 | 0 | 8.5 | 0 | 115.2671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 677.7706 | 135.5541 | 1.356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 17:01 | 9 | 9 | 17 | 252 | 6041 | 62.96 | 68.8028 | 361.573 | 361.573 | -292.7702 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 441.9226 | 441.9226 | 0 | 8.5 | 0 | 73.6538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 433.0841 | 86.6168 | 0.8662% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 18:01 | 9 | 9 | 18 | 252 | 6042 | 62.6 | 72.2907 | 188.0639 | 188.0639 | -115.7733 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 229.8559 | 229.8559 | 0 | 8.5 | 0 | 38.3093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 225.2588 | 45.0518 | 0.4505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 19:01 | 9 | 9 | 19 | 252 | 6043 | 62.6 | 136.6917 | 163.3314 | 163.3314 | -26.6397 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 199.6273 | 199.6273 | 0 | 8.5 | 0 | 33.2712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 195.6347 | 39.1269 | 0.3913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 20:01 | 9 | 9 | 20 | 252 | 6044 | 62.06 | 202.8182 | 96.3186 | 96.3186 | 106.4996 | Heating | 93.9702 | 8.5 | 93.9702 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 95.888 | 0 | 19.1776 | 0.1918% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 21:01 | 9 | 9 | 21 | 252 | 6045 | 62.6 | 82.8829 | 84.129 | 84.129 | -1.2462 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 102.8244 | 102.8244 | 0 | 8.5 | 0 | 17.1374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 100.7679 | 20.1536 | 0.2015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 22:01 | 9 | 9 | 22 | 252 | 6046 | 62.06 | 98.2836 | 0 | 0 | 98.2836 | Heating | 86.7208 | 8.5 | 86.7208 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.3442 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 88.4907 | 0 | 17.6981 | 0.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-09 23:01 | 9 | 9 | 23 | 252 | 6047 | 62.06 | 129.0287 | 0 | 0 | 129.0287 | Heating | 113.8488 | 8.5 | 113.8488 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.7698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.1723 | 0 | 23.2345 | 0.2323% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 00:01 | 9 | 10 | 0 | 253 | 6048 | 62.6 | 175.1818 | 0 | 0 | 175.1818 | Heating | 154.5722 | 8.5 | 154.5722 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.9144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 157.7267 | 0 | 31.5453 | 0.3155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 01:01 | 9 | 10 | 1 | 253 | 6049 | 62.06 | 191.2152 | 0 | 0 | 191.2152 | Heating | 168.7193 | 8.5 | 168.7193 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.7439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 172.1625 | 0 | 34.4325 | 0.3443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 02:01 | 9 | 10 | 2 | 253 | 6050 | 62.06 | 199.3025 | 0 | 0 | 199.3025 | Heating | 175.8551 | 8.5 | 175.8551 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 179.444 | 0 | 35.8888 | 0.3589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 03:01 | 9 | 10 | 3 | 253 | 6051 | 62.6 | 197.7594 | 0 | 0 | 197.7594 | Heating | 174.4936 | 8.5 | 174.4936 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.8987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 178.0546 | 0 | 35.6109 | 0.3561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 04:01 | 9 | 10 | 4 | 253 | 6052 | 62.6 | 193.1198 | 0 | 0 | 193.1198 | Heating | 170.3998 | 8.5 | 170.3998 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.08 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 173.8774 | 0 | 34.7755 | 0.3478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 05:01 | 9 | 10 | 5 | 253 | 6053 | 62.06 | 188.3675 | 0 | 0 | 188.3675 | Heating | 166.2066 | 8.5 | 166.2066 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.2413 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 169.5986 | 0 | 33.9197 | 0.3392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 06:01 | 9 | 10 | 6 | 253 | 6054 | 62.06 | 2677.7316 | 83.0277 | 83.0277 | 2594.7039 | Heating | 2289.4446 | 8.5 | 2289.4446 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 457.8889 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2336.168 | 0 | 467.2336 | 4.672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 07:01 | 9 | 10 | 7 | 253 | 6055 | 62.06 | 1775.8438 | 0.76996 | 0.76996 | 1775.0738 | Heating | 1566.2416 | 8.5 | 1566.2416 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.2483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1598.2057 | 0 | 319.6411 | 3.196% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 08:01 | 9 | 10 | 8 | 253 | 6056 | 62.06 | 1019.3046 | 208.6226 | 208.6226 | 810.682 | Heating | 715.3077 | 8.5 | 715.3077 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 143.0615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 729.9058 | 0 | 145.9812 | 1.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 09:01 | 9 | 10 | 9 | 253 | 6057 | 62.6 | 131.959 | 473.9655 | 473.9655 | -342.0065 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 579.2912 | 579.2912 | 0 | 8.5 | 0 | 96.5485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 567.7054 | 113.5411 | 1.135% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 10:01 | 9 | 10 | 10 | 253 | 6058 | 62.6 | 38.959 | 1016.1685 | 1016.1685 | -977.2096 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1241.9838 | 1241.9838 | 0 | 8.5 | 0 | 206.9973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1217.1441 | 243.4288 | 2.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 11:01 | 9 | 10 | 11 | 253 | 6059 | 62.06 | 8.6307 | 1650.6192 | 1650.6192 | -1641.9885 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2017.4235 | 2017.4235 | 0 | 8.5 | 0 | 336.2372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1977.075 | 395.415 | 3.954% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 12:01 | 9 | 10 | 12 | 253 | 6060 | 62.96 | 0.49421 | 2965.9788 | 2965.9788 | -2965.4845 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3625.0852 | 3625.0852 | 0 | 8.5 | 0 | 604.1809 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3552.5834 | 710.5167 | 7.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 13:01 | 9 | 10 | 13 | 253 | 6061 | 64.04 | 0 | 5250.9282 | 5250.9282 | -5250.9282 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6417.8012 | 6417.8012 | 0 | 8.5 | 0 | 1069.6335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6289.4451 | 1257.889 | 12.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 14:01 | 9 | 10 | 14 | 253 | 6062 | 64.04 | 0 | 6835.0458 | 6835.0458 | -6835.0458 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8353.9449 | 8353.9449 | 0 | 8.5 | 0 | 1392.3241 | 30% | 1 | 55.69% | 0% | 0% | 0% | 21.2072 | 0 | 0 | 0 | 21.2072 | 0 | 8186.866 | 1637.3732 | 16.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.4818
2007-09-10 15:01 | 9 | 10 | 15 | 253 | 6063 | 64.4 | 0 | 7355.975 | 7355.975 | -7355.975 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8990.6361 | 8990.6361 | 0 | 8.5 | 0 | 1498.4394 | 30% | 1 | 59.94% | 0% | 0% | 0% | 25.1103 | 0 | 0 | 0 | 25.1103 | 0 | 8810.8234 | 1762.1647 | 17.62% | 1 | 35.24% | 0% | 0% | 3.7016 | 0 | 0 | 3.7016 | 28.8119
2007-09-10 16:01 | 9 | 10 | 16 | 253 | 6064 | 66.2 | 0 | 7532.882 | 7532.882 | -7532.882 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9206.8558 | 9206.8558 | 0 | 8.5 | 0 | 1534.476 | 30.69% | 1 | 61.38% | 0% | 0% | 0% | 26.521 | 0 | 0 | 0 | 26.521 | 0 | 9022.7187 | 1804.5437 | 18.05% | 1 | 36.09% | 0% | 0% | 3.9096 | 0 | 0 | 3.9096 | 30.4305
2007-09-10 17:01 | 9 | 10 | 17 | 253 | 6065 | 66.92 | 0 | 7358.0164 | 7358.0164 | -7358.0164 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8993.1312 | 8993.1312 | 0 | 8.5 | 0 | 1498.8552 | 30% | 1 | 59.95% | 0% | 0% | 0% | 25.1263 | 0 | 0 | 0 | 25.1263 | 0 | 8813.2685 | 1762.6537 | 17.63% | 1 | 35.25% | 0% | 0% | 3.704 | 0 | 0 | 3.704 | 28.8302
2007-09-10 18:01 | 9 | 10 | 18 | 253 | 6066 | 66.2 | 0 | 4359.5101 | 4359.5101 | -4359.5101 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5328.2902 | 5328.2902 | 0 | 8.5 | 0 | 888.0484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5221.7244 | 1044.3449 | 10.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 19:01 | 9 | 10 | 19 | 253 | 6067 | 64.94 | 0 | 2351.5111 | 2351.5111 | -2351.5111 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2874.0691 | 2874.0691 | 0 | 8.5 | 0 | 479.0115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2816.5877 | 563.3175 | 5.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 20:01 | 9 | 10 | 20 | 253 | 6068 | 64.94 | 0 | 803.9574 | 803.9574 | -803.9574 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 982.6146 | 982.6146 | 0 | 8.5 | 0 | 163.7691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 962.9623 | 192.5925 | 1.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 21:01 | 9 | 10 | 21 | 253 | 6069 | 62.96 | 0 | 355.3719 | 355.3719 | -355.3719 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 434.3435 | 434.3435 | 0 | 8.5 | 0 | 72.3906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 425.6566 | 85.1313 | 0.8513% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-10 22:01 | 9 | 10 | 22 | 253 | 6070 | 60.08 | 0 | 0 | 0 | 0 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 30% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 8.2745
2007-09-10 23:01 | 9 | 10 | 23 | 253 | 6071 | 60.08 | 1.5628 | 0 | 0 | 1.5628 | Heating | 1.3789 | 8.5 | 1.3789 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.27579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.4071 | 0 | 0.28142 | 0.002814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 00:01 | 9 | 11 | 0 | 254 | 6072 | 60.8 | 7.5595 | 0 | 0 | 7.5595 | Heating | 6.6702 | 8.5 | 6.6702 | 0 | 5.7289 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.8063 | 0 | 1.3613 | 0.01361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 01:01 | 9 | 11 | 1 | 254 | 6073 | 62.06 | 12.5933 | 0 | 0 | 12.5933 | Heating | 11.1117 | 8.5 | 11.1117 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.2223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.3385 | 0 | 2.2677 | 0.02268% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 02:01 | 9 | 11 | 2 | 254 | 6074 | 62.06 | 13.1106 | 0 | 0 | 13.1106 | Heating | 11.5681 | 8.5 | 11.5681 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.3136 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.8042 | 0 | 2.3608 | 0.02361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 03:01 | 9 | 11 | 3 | 254 | 6075 | 62.06 | 10.8888 | 0 | 0 | 10.8888 | Heating | 9.6078 | 8.5 | 9.6078 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.9216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.8039 | 0 | 1.9608 | 0.01961% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 04:01 | 9 | 11 | 4 | 254 | 6076 | 62.6 | 12.5545 | 0 | 0 | 12.5545 | Heating | 11.0775 | 8.5 | 11.0775 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.2155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.3036 | 0 | 2.2607 | 0.02261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 05:01 | 9 | 11 | 5 | 254 | 6077 | 62.06 | 19.255 | 0 | 0 | 19.255 | Heating | 16.9897 | 8.5 | 16.9897 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.3979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 17.3365 | 0 | 3.4673 | 0.03467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 06:01 | 9 | 11 | 6 | 254 | 6078 | 62.06 | 1280.2875 | 286.8911 | 286.8911 | 993.3963 | Heating | 876.5262 | 8.5 | 876.5262 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.3052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 894.4145 | 0 | 178.8829 | 1.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 07:01 | 9 | 11 | 7 | 254 | 6079 | 62.6 | 751.6699 | 174.3947 | 174.3947 | 577.2752 | Heating | 509.3604 | 8.5 | 509.3604 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.8721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 519.7556 | 0 | 103.9511 | 1.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 08:01 | 9 | 11 | 8 | 254 | 6080 | 62.06 | 38.9524 | 2540.0318 | 2540.0318 | -2501.0794 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3104.4833 | 3104.4833 | 0 | 8.5 | 0 | 517.4139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3042.3937 | 608.4787 | 6.085% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 09:01 | 9 | 11 | 9 | 254 | 6081 | 62.6 | 0 | 4424.7503 | 4424.7503 | -4424.7503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5408.0282 | 5408.0282 | 0 | 8.5 | 0 | 901.338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5299.8676 | 1059.9735 | 10.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 10:01 | 9 | 11 | 10 | 254 | 6082 | 62.6 | 0 | 6886.6931 | 6886.6931 | -6886.6931 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8417.0693 | 8417.0693 | 0 | 8.5 | 0 | 1402.8449 | 30% | 1 | 56.11% | 0% | 0% | 0% | 21.5776 | 0 | 0 | 0 | 21.5776 | 0 | 8248.728 | 1649.7456 | 16.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.8521
2007-09-11 11:01 | 9 | 11 | 11 | 254 | 6083 | 62.06 | 0 | 9038.5818 | 9038.5818 | -9038.5818 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11047.1555 | 11047.1555 | 0 | 8.5 | 0 | 1841.1926 | 36.82% | 1 | 73.65% | 0% | 0% | 0% | 40.3282 | 0 | 0 | 0 | 40.3282 | 0 | 10826.2124 | 2165.2425 | 21.65% | 1 | 43.3% | 0% | 0% | 5.9449 | 0 | 0 | 5.9449 | 46.2732
2007-09-11 12:01 | 9 | 11 | 12 | 254 | 6084 | 66.2 | 0 | 10233.839 | 10233.839 | -10233.839 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12508.0255 | 12508.0255 | 0 | 8.5 | 0 | 2084.6709 | 41.69% | 1 | 83.39% | 0% | 0% | 0% | 53.6621 | 0 | 0 | 0 | 53.6621 | 0 | 12257.865 | 2451.573 | 24.52% | 1 | 49.03% | 0% | 0% | 7.9105 | 0 | 0 | 7.9105 | 61.5726
2007-09-11 13:01 | 9 | 11 | 13 | 254 | 6085 | 66.2 | 0 | 11433.5111 | 11433.5111 | -11433.5111 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13974.2913 | 13974.2913 | 0 | 8.5 | 0 | 2329.0486 | 46.58% | 1 | 93.16% | 0% | 0% | 0% | 69.2455 | 0 | 0 | 0 | 69.2455 | 0 | 13694.8055 | 2738.9611 | 27.39% | 1 | 54.78% | 0% | 0% | 10.2077 | 0 | 0 | 10.2077 | 79.4533
2007-09-11 14:01 | 9 | 11 | 14 | 254 | 6086 | 66.92 | 0 | 11776.1257 | 11776.1257 | -11776.1257 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14393.0425 | 14393.0425 | 0 | 8.5 | 0 | 2398.8404 | 47.98% | 1 | 95.95% | 0% | 0% | 0% | 74.1113 | 0 | 0 | 0 | 74.1113 | 0 | 14105.1816 | 2821.0363 | 28.21% | 1 | 56.42% | 0% | 0% | 10.925 | 0 | 0 | 10.925 | 85.0363
2007-09-11 15:01 | 9 | 11 | 15 | 254 | 6087 | 66.2 | 0 | 10794.9148 | 10794.9148 | -10794.9148 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13193.7848 | 13193.7848 | 0 | 8.5 | 0 | 2198.9641 | 43.98% | 1 | 87.96% | 0% | 0% | 0% | 60.6712 | 0 | 0 | 0 | 60.6712 | 0 | 12929.9091 | 2585.9818 | 25.86% | 1 | 51.72% | 0% | 0% | 8.9438 | 0 | 0 | 8.9438 | 69.615
2007-09-11 16:01 | 9 | 11 | 16 | 254 | 6088 | 68 | 0 | 10078.4024 | 10078.4024 | -10078.4024 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12318.0474 | 12318.0474 | 0 | 8.5 | 0 | 2053.0079 | 41.06% | 1 | 82.12% | 0% | 0% | 0% | 51.8059 | 0 | 0 | 0 | 51.8059 | 0 | 12071.6865 | 2414.3373 | 24.14% | 1 | 48.29% | 0% | 0% | 7.6369 | 0 | 0 | 7.6369 | 59.4428
2007-09-11 17:01 | 9 | 11 | 17 | 254 | 6089 | 68 | 0 | 9490.4424 | 9490.4424 | -9490.4424 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11599.4296 | 11599.4296 | 0 | 8.5 | 0 | 1933.2383 | 38.66% | 1 | 77.33% | 0% | 0% | 0% | 45.1167 | 0 | 0 | 0 | 45.1167 | 0 | 11367.441 | 2273.4882 | 22.73% | 1 | 45.47% | 0% | 0% | 6.6508 | 0 | 0 | 6.6508 | 51.7675
2007-09-11 18:01 | 9 | 11 | 18 | 254 | 6090 | 66.92 | 0 | 5576.6872 | 5576.6872 | -5576.6872 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6815.951 | 6815.951 | 0 | 8.5 | 0 | 1135.9918 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6679.632 | 1335.9264 | 13.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 19:01 | 9 | 11 | 19 | 254 | 6091 | 68 | 0 | 3873.5401 | 3873.5401 | -3873.5401 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4734.3267 | 4734.3267 | 0 | 8.5 | 0 | 789.0545 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4639.6402 | 927.928 | 9.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 20:01 | 9 | 11 | 20 | 254 | 6092 | 68 | 0 | 1771.7807 | 1771.7807 | -1771.7807 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2165.5098 | 2165.5098 | 0 | 8.5 | 0 | 360.9183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2122.1996 | 424.4399 | 4.244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 21:01 | 9 | 11 | 21 | 254 | 6093 | 64.04 | 0 | 623.9695 | 623.9695 | -623.9695 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 762.6294 | 762.6294 | 0 | 8.5 | 0 | 127.1049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 747.3769 | 149.4754 | 1.495% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 22:01 | 9 | 11 | 22 | 254 | 6094 | 64.04 | 0 | 80.0066 | 80.0066 | -80.0066 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 97.7859 | 97.7859 | 0 | 8.5 | 0 | 16.2976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 95.8302 | 19.166 | 0.1917% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-11 23:01 | 9 | 11 | 23 | 254 | 6095 | 64.04 | 0 | 20.0371 | 20.0371 | -20.0371 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 24.4898 | 24.4898 | 0 | 8.5 | 0 | 4.0816 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 24 | 4.8 | 0.048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 00:01 | 9 | 12 | 0 | 255 | 6096 | 62.96 | 0.51276 | 1.5546 | 1.5546 | -1.0419 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1.9001 | 1.9001 | 0 | 8.5 | 0 | 0.31668 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1.8621 | 0.37242 | 0.003724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 01:01 | 9 | 12 | 1 | 255 | 6097 | 60.98 | 6.9196 | 0 | 0 | 6.9196 | Heating | 6.1055 | 8.5 | 6.1055 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.2301 | 0 | 1.246 | 0.01246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 02:01 | 9 | 12 | 2 | 255 | 6098 | 60.98 | 17.5476 | 0 | 0 | 17.5476 | Heating | 15.4831 | 8.5 | 15.4831 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.0966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.7991 | 0 | 3.1598 | 0.0316% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 03:01 | 9 | 12 | 3 | 255 | 6099 | 59 | 27.7622 | 0 | 0 | 27.7622 | Heating | 24.4961 | 8.5 | 24.4961 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.8992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.996 | 0 | 4.9992 | 0.04999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 04:01 | 9 | 12 | 4 | 255 | 6100 | 57.92 | 36.9381 | 0 | 0 | 36.9381 | Heating | 32.5925 | 8.5 | 32.5925 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.5185 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 33.2576 | 0 | 6.6515 | 0.06652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 05:01 | 9 | 12 | 5 | 255 | 6101 | 57.92 | 38.0066 | 0 | 0 | 38.0066 | Heating | 33.5352 | 8.5 | 33.5352 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.2196 | 0 | 6.8439 | 0.06844% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 06:01 | 9 | 12 | 6 | 255 | 6102 | 57.02 | 1784.1285 | 177.4706 | 177.4706 | 1606.6579 | Heating | 1417.6394 | 8.5 | 1417.6394 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 283.5279 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1446.5708 | 0 | 289.3142 | 2.893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 07:01 | 9 | 12 | 7 | 255 | 6103 | 57.92 | 1206.0664 | 100.9899 | 100.9899 | 1105.0765 | Heating | 975.0675 | 8.5 | 975.0675 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.0135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 994.9669 | 0 | 198.9934 | 1.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 08:01 | 9 | 12 | 8 | 255 | 6104 | 57.92 | 449.715 | 1021.4937 | 1021.4937 | -571.7787 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1248.4924 | 1248.4924 | 0 | 8.5 | 0 | 208.0821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1223.5225 | 244.7045 | 2.447% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 09:01 | 9 | 12 | 9 | 255 | 6105 | 60.98 | 2.4162 | 2519.6912 | 2519.6912 | -2517.275 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3079.6226 | 3079.6226 | 0 | 8.5 | 0 | 513.2704 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3018.0302 | 603.606 | 6.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 10:01 | 9 | 12 | 10 | 255 | 6106 | 62.06 | 0 | 4783.1411 | 4783.1411 | -4783.1411 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5846.0614 | 5846.0614 | 0 | 8.5 | 0 | 974.3436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5729.1402 | 1145.828 | 11.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 11:01 | 9 | 12 | 11 | 255 | 6107 | 62.06 | 0 | 7634.5368 | 7634.5368 | -7634.5368 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 9331.1006 | 9331.1006 | 0 | 8.5 | 0 | 1555.1834 | 31.1% | 1 | 62.21% | 0% | 0% | 0% | 27.3513 | 0 | 0 | 0 | 27.3513 | 0 | 9144.4786 | 1828.8957 | 18.29% | 1 | 36.58% | 0% | 0% | 4.032 | 0 | 0 | 4.032 | 31.3833
2007-09-12 12:01 | 9 | 12 | 12 | 255 | 6108 | 62.96 | 0 | 9795.2888 | 9795.2888 | -9795.2888 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 11972.0197 | 11972.0197 | 0 | 8.5 | 0 | 1995.3366 | 39.91% | 1 | 79.81% | 0% | 0% | 0% | 48.5197 | 0 | 0 | 0 | 48.5197 | 0 | 11732.5793 | 2346.5159 | 23.47% | 1 | 46.93% | 0% | 0% | 7.1525 | 0 | 0 | 7.1525 | 55.6722
2007-09-12 13:01 | 9 | 12 | 13 | 255 | 6109 | 64.04 | 0 | 11651.8755 | 11651.8755 | -11651.8755 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14241.1811 | 14241.1811 | 0 | 8.5 | 0 | 2373.5302 | 47.47% | 1 | 94.94% | 0% | 0% | 0% | 72.3251 | 0 | 0 | 0 | 72.3251 | 0 | 13956.3575 | 2791.2715 | 27.91% | 1 | 55.83% | 0% | 0% | 10.6617 | 0 | 0 | 10.6617 | 82.9868
2007-09-12 14:01 | 9 | 12 | 14 | 255 | 6110 | 64.04 | 0 | 12503.3171 | 12503.3171 | -12503.3171 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15281.832 | 15281.832 | 0 | 8.5 | 0 | 2546.972 | 50.94% | 2 | 50.94% | 50.94% | 0% | 0% | 17.273 | 17.273 | 0 | 0 | 34.546 | 0 | 14976.1954 | 2995.2391 | 29.95% | 1 | 59.9% | 0% | 0% | 12.5393 | 0 | 0 | 12.5393 | 47.0853
2007-09-12 15:01 | 9 | 12 | 15 | 255 | 6111 | 69.98 | 0 | 13010.5167 | 13010.5167 | -13010.5167 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15901.7426 | 15901.7426 | 0 | 8.5 | 0 | 2650.2904 | 53.01% | 2 | 53.01% | 53.01% | 0% | 0% | 18.9272 | 18.9272 | 0 | 0 | 37.8545 | 0 | 15583.7077 | 3116.7415 | 31.17% | 1 | 62.33% | 0% | 0% | 13.7402 | 0 | 0 | 13.7402 | 51.5947
2007-09-12 16:01 | 9 | 12 | 16 | 255 | 6112 | 69.08 | 0 | 12078.4671 | 12078.4671 | -12078.4671 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14762.5709 | 14762.5709 | 0 | 8.5 | 0 | 2460.4285 | 49.21% | 1 | 98.42% | 0% | 0% | 0% | 78.5608 | 0 | 0 | 0 | 78.5608 | 0 | 14467.3195 | 2893.4639 | 28.93% | 1 | 57.87% | 0% | 0% | 11.5809 | 0 | 0 | 11.5809 | 90.1417
2007-09-12 17:01 | 9 | 12 | 17 | 255 | 6113 | 66.92 | 0 | 10919.3229 | 10919.3229 | -10919.3229 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 13345.8391 | 13345.8391 | 0 | 8.5 | 0 | 2224.3065 | 44.49% | 1 | 88.97% | 0% | 0% | 0% | 62.2915 | 0 | 0 | 0 | 62.2915 | 0 | 13078.9223 | 2615.7845 | 26.16% | 1 | 52.32% | 0% | 0% | 9.1826 | 0 | 0 | 9.1826 | 71.4741
2007-09-12 18:01 | 9 | 12 | 18 | 255 | 6114 | 64.04 | 0 | 6911.8092 | 6911.8092 | -6911.8092 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8447.7667 | 8447.7667 | 0 | 8.5 | 0 | 1407.9611 | 30% | 1 | 56.32% | 0% | 0% | 0% | 21.759 | 0 | 0 | 0 | 21.759 | 0 | 8278.8114 | 1655.7623 | 16.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.0336
2007-09-12 19:01 | 9 | 12 | 19 | 255 | 6115 | 60.98 | 0 | 5472.4384 | 5472.4384 | -5472.4384 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6688.5358 | 6688.5358 | 0 | 8.5 | 0 | 1114.756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6554.7651 | 1310.953 | 13.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 20:01 | 9 | 12 | 20 | 255 | 6116 | 60.98 | 0 | 3880.248 | 3880.248 | -3880.248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4742.5253 | 4742.5253 | 0 | 8.5 | 0 | 790.4209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4647.6748 | 929.535 | 9.295% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 21:01 | 9 | 12 | 21 | 255 | 6117 | 55.94 | 0 | 1786.397 | 1786.397 | -1786.397 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2183.3741 | 2183.3741 | 0 | 8.5 | 0 | 363.8957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2139.7067 | 427.9413 | 4.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 22:01 | 9 | 12 | 22 | 255 | 6118 | 53.06 | 0 | 342.3238 | 342.3238 | -342.3238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 418.3958 | 418.3958 | 0 | 8.5 | 0 | 69.7326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 410.0279 | 82.0056 | 0.8201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-12 23:01 | 9 | 12 | 23 | 255 | 6119 | 53.06 | 0 | 166.385 | 166.385 | -166.385 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 203.3594 | 203.3594 | 0 | 8.5 | 0 | 33.8932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 199.2922 | 39.8584 | 0.3986% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 00:01 | 9 | 13 | 0 | 256 | 6120 | 50 | 0 | 41.2648 | 41.2648 | -41.2648 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 50.4348 | 50.4348 | 0 | 8.5 | 0 | 8.4058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 49.4261 | 9.8852 | 0.09885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 01:01 | 9 | 13 | 1 | 256 | 6121 | 50 | 0 | 4.5461 | 4.5461 | -4.5461 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5.5564 | 5.5564 | 0 | 8.5 | 0 | 0.92606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5.4452 | 1.089 | 0.01089% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 02:01 | 9 | 13 | 2 | 256 | 6122 | 50 | 4.3508 | 0 | 0 | 4.3508 | Heating | 3.8389 | 8.5 | 3.8389 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.76779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3.9173 | 0 | 0.78346 | 0.007835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 03:01 | 9 | 13 | 3 | 256 | 6123 | 48.92 | 11.8679 | 0 | 0 | 11.8679 | Heating | 10.4717 | 8.5 | 10.4717 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.0943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 10.6854 | 0 | 2.1371 | 0.02137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 04:01 | 9 | 13 | 4 | 256 | 6124 | 46.94 | 20.6893 | 0 | 0 | 20.6893 | Heating | 18.2553 | 8.5 | 18.2553 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.6511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.6279 | 0 | 3.7256 | 0.03726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 05:01 | 9 | 13 | 5 | 256 | 6125 | 46.94 | 22.3116 | 0 | 0 | 22.3116 | Heating | 19.6867 | 8.5 | 19.6867 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.9373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.0885 | 0 | 4.0177 | 0.04018% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 06:01 | 9 | 13 | 6 | 256 | 6126 | 48.92 | 1529.2332 | 329.1438 | 329.1438 | 1200.0895 | Heating | 1058.9025 | 8.5 | 1058.9025 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.7805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1080.5127 | 0 | 216.1025 | 2.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 07:01 | 9 | 13 | 7 | 256 | 6127 | 51.98 | 1040.715 | 293.0056 | 293.0056 | 747.7094 | Heating | 659.7436 | 8.5 | 659.7436 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.9487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 673.2077 | 0 | 134.6415 | 1.346% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 08:01 | 9 | 13 | 8 | 256 | 6128 | 51.98 | 128.7583 | 2517.9498 | 2517.9498 | -2389.1915 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3077.4942 | 3077.4942 | 0 | 8.5 | 0 | 512.9157 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3015.9443 | 603.1889 | 6.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 09:01 | 9 | 13 | 9 | 256 | 6129 | 60.08 | 0 | 4595.2795 | 4595.2795 | -4595.2795 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5616.4527 | 5616.4527 | 0 | 8.5 | 0 | 936.0755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5504.1237 | 1100.8247 | 11.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 10:01 | 9 | 13 | 10 | 256 | 6130 | 62.06 | 0 | 6945.8614 | 6945.8614 | -6945.8614 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8489.3861 | 8489.3861 | 0 | 8.5 | 0 | 1414.8977 | 30% | 1 | 56.6% | 0% | 0% | 0% | 22.0064 | 0 | 0 | 0 | 22.0064 | 0 | 8319.5984 | 1663.9197 | 16.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.2809
2007-09-13 11:01 | 9 | 13 | 11 | 256 | 6131 | 62.06 | 0 | 8826.7417 | 8826.7417 | -8826.7417 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10788.2399 | 10788.2399 | 0 | 8.5 | 0 | 1798.04 | 35.96% | 1 | 71.92% | 0% | 0% | 0% | 38.1874 | 0 | 0 | 0 | 38.1874 | 0 | 10572.4751 | 2114.495 | 21.14% | 1 | 42.29% | 0% | 0% | 5.6293 | 0 | 0 | 5.6293 | 43.8167
2007-09-13 12:01 | 9 | 13 | 12 | 256 | 6132 | 66.2 | 0 | 10510.086 | 10510.086 | -10510.086 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12845.6607 | 12845.6607 | 0 | 8.5 | 0 | 2140.9435 | 42.82% | 1 | 85.64% | 0% | 0% | 0% | 57.0523 | 0 | 0 | 0 | 57.0523 | 0 | 12588.7475 | 2517.7495 | 25.18% | 1 | 50.35% | 0% | 0% | 8.4103 | 0 | 0 | 8.4103 | 65.4626
2007-09-13 13:01 | 9 | 13 | 13 | 256 | 6133 | 69.98 | 0 | 12156.0916 | 12156.0916 | -12156.0916 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14857.4453 | 14857.4453 | 0 | 8.5 | 0 | 2476.2409 | 49.52% | 1 | 99.05% | 0% | 0% | 0% | 79.7269 | 0 | 0 | 0 | 79.7269 | 0 | 14560.2964 | 2912.0593 | 29.12% | 1 | 58.24% | 0% | 0% | 11.7528 | 0 | 0 | 11.7528 | 91.4797
2007-09-13 14:01 | 9 | 13 | 14 | 256 | 6134 | 69.98 | 0 | 12920.0245 | 12920.0245 | -12920.0245 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15791.141 | 15791.141 | 0 | 8.5 | 0 | 2631.8568 | 52.64% | 2 | 52.64% | 52.64% | 0% | 0% | 18.6258 | 18.6258 | 0 | 0 | 37.2516 | 0 | 15475.3182 | 3095.0636 | 30.95% | 1 | 61.9% | 0% | 0% | 13.5214 | 0 | 0 | 13.5214 | 50.773
2007-09-13 15:01 | 9 | 13 | 15 | 256 | 6135 | 71.06 | 0 | 13173.511 | 13173.511 | -13173.511 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 16100.9579 | 16100.9579 | 0 | 8.5 | 0 | 2683.493 | 53.67% | 2 | 53.67% | 53.67% | 0% | 0% | 19.477 | 19.477 | 0 | 0 | 38.9541 | 0 | 15778.9387 | 3155.7877 | 31.56% | 1 | 63.12% | 0% | 0% | 14.1394 | 0 | 0 | 14.1394 | 53.0935
2007-09-13 16:01 | 9 | 13 | 16 | 256 | 6136 | 71.06 | 0 | 12711.6997 | 12711.6997 | -12711.6997 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 15536.5219 | 15536.5219 | 0 | 8.5 | 0 | 2589.4203 | 51.79% | 2 | 51.79% | 51.79% | 0% | 0% | 17.9423 | 17.9423 | 0 | 0 | 35.8846 | 0 | 15225.7914 | 3045.1583 | 30.45% | 1 | 60.9% | 0% | 0% | 13.0252 | 0 | 0 | 13.0252 | 48.9098
2007-09-13 17:01 | 9 | 13 | 17 | 256 | 6137 | 71.06 | 0 | 11734.3355 | 11734.3355 | -11734.3355 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14341.9657 | 14341.9657 | 0 | 8.5 | 0 | 2390.3276 | 47.81% | 1 | 95.61% | 0% | 0% | 0% | 73.5077 | 0 | 0 | 0 | 73.5077 | 0 | 14055.1263 | 2811.0253 | 28.11% | 1 | 56.22% | 0% | 0% | 10.836 | 0 | 0 | 10.836 | 84.3438
2007-09-13 18:01 | 9 | 13 | 18 | 256 | 6138 | 68 | 0 | 7193.6948 | 7193.6948 | -7193.6948 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8792.2936 | 8792.2936 | 0 | 8.5 | 0 | 1465.3823 | 30% | 1 | 58.62% | 0% | 0% | 0% | 23.8544 | 0 | 0 | 0 | 23.8544 | 0 | 8616.4478 | 1723.2896 | 17.23% | 1 | 34.47% | 0% | 0% | 3.5165 | 0 | 0 | 3.5165 | 27.3708
2007-09-13 19:01 | 9 | 13 | 19 | 256 | 6139 | 60.98 | 0 | 5218.9402 | 5218.9402 | -5218.9402 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6378.7046 | 6378.7046 | 0 | 8.5 | 0 | 1063.1174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6251.1305 | 1250.2261 | 12.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 20:01 | 9 | 13 | 20 | 256 | 6140 | 60.98 | 0 | 3187.8403 | 3187.8403 | -3187.8403 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3896.2492 | 3896.2492 | 0 | 8.5 | 0 | 649.3749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3818.3243 | 763.6649 | 7.637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 21:01 | 9 | 13 | 21 | 256 | 6141 | 57.92 | 0 | 1405.2075 | 1405.2075 | -1405.2075 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1717.4758 | 1717.4758 | 0 | 8.5 | 0 | 286.246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1683.1263 | 336.6253 | 3.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 22:01 | 9 | 13 | 22 | 256 | 6142 | 55.04 | 0 | 312.5538 | 312.5538 | -312.5538 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 382.0103 | 382.0103 | 0 | 8.5 | 0 | 63.6684 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 374.37 | 74.874 | 0.7487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-13 23:01 | 9 | 13 | 23 | 256 | 6143 | 55.04 | 0 | 269.4114 | 269.4114 | -269.4114 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 329.2806 | 329.2806 | 0 | 8.5 | 0 | 54.8801 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 322.6949 | 64.539 | 0.6454% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 00:01 | 9 | 14 | 0 | 257 | 6144 | 57.92 | 0 | 217.1442 | 217.1442 | -217.1442 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 265.3984 | 265.3984 | 0 | 8.5 | 0 | 44.2331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 260.0905 | 52.0181 | 0.5202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 01:01 | 9 | 14 | 1 | 257 | 6145 | 57.92 | 0 | 113.1199 | 113.1199 | -113.1199 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 138.2577 | 138.2577 | 0 | 8.5 | 0 | 23.043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 135.4926 | 27.0985 | 0.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 02:01 | 9 | 14 | 2 | 257 | 6146 | 57.92 | 0 | 48.4553 | 48.4553 | -48.4553 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 59.2232 | 59.2232 | 0 | 8.5 | 0 | 9.8705 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 58.0387 | 11.6077 | 0.1161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 03:01 | 9 | 14 | 3 | 257 | 6147 | 57.02 | 0 | 19.3724 | 19.3724 | -19.3724 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23.6774 | 23.6774 | 0 | 8.5 | 0 | 3.9462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 23.2039 | 4.6408 | 0.04641% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 04:01 | 9 | 14 | 4 | 257 | 6148 | 55.94 | 0 | 8.3177 | 8.3177 | -8.3177 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 10.166 | 10.166 | 0 | 8.5 | 0 | 1.6943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 9.9627 | 1.9925 | 0.01993% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 05:01 | 9 | 14 | 5 | 257 | 6149 | 55.94 | 0 | 10.2249 | 10.2249 | -10.2249 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 12.4971 | 12.4971 | 0 | 8.5 | 0 | 2.0828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 12.2471 | 2.4494 | 0.02449% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 06:01 | 9 | 14 | 6 | 257 | 6150 | 55.94 | 481.1041 | 494.3466 | 494.3466 | -13.2425 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 604.2014 | 604.2014 | 0 | 8.5 | 0 | 100.7002 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 592.1173 | 118.4235 | 1.184% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 07:01 | 9 | 14 | 7 | 257 | 6151 | 60.98 | 159.1702 | 251.5405 | 251.5405 | -92.3703 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 307.4383 | 307.4383 | 0 | 8.5 | 0 | 51.2397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 301.2896 | 60.2579 | 0.6026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 08:01 | 9 | 14 | 8 | 257 | 6152 | 60.98 | 0 | 920.1092 | 920.1092 | -920.1092 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1124.5779 | 1124.5779 | 0 | 8.5 | 0 | 187.4297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1102.0864 | 220.4173 | 2.204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 09:01 | 9 | 14 | 9 | 257 | 6153 | 66.92 | 0 | 1573.4346 | 1573.4346 | -1573.4346 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1923.0867 | 1923.0867 | 0 | 8.5 | 0 | 320.5144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1884.625 | 376.925 | 3.769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 10:01 | 9 | 14 | 10 | 257 | 6154 | 66.92 | 0 | 2951.3253 | 2951.3253 | -2951.3253 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3607.1753 | 3607.1753 | 0 | 8.5 | 0 | 601.1959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3535.0318 | 707.0064 | 7.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 11:01 | 9 | 14 | 11 | 257 | 6155 | 66.92 | 0 | 4619.0225 | 4619.0225 | -4619.0225 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5645.472 | 5645.472 | 0 | 8.5 | 0 | 940.912 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5532.5625 | 1106.5125 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 12:01 | 9 | 14 | 12 | 257 | 6156 | 71.06 | 0 | 5469.2199 | 5469.2199 | -5469.2199 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6684.6021 | 6684.6021 | 0 | 8.5 | 0 | 1114.1003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6550.91 | 1310.182 | 13.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 13:01 | 9 | 14 | 13 | 257 | 6157 | 71.96 | 0 | 6158.2979 | 6158.2979 | -6158.2979 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7526.8086 | 7526.8086 | 0 | 8.5 | 0 | 1254.4681 | 30% | 1 | 50.18% | 0% | 0% | 0% | 16.6855 | 0 | 0 | 0 | 16.6855 | 0 | 7376.2724 | 1475.2545 | 14.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.96
2007-09-14 14:01 | 9 | 14 | 14 | 257 | 6158 | 71.96 | 0 | 6384.6159 | 6384.6159 | -6384.6159 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7803.4194 | 7803.4194 | 0 | 8.5 | 0 | 1300.5699 | 30% | 1 | 52.02% | 0% | 0% | 0% | 18.1296 | 0 | 0 | 0 | 18.1296 | 0 | 7647.351 | 1529.4702 | 15.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.4042
2007-09-14 15:01 | 9 | 14 | 15 | 257 | 6159 | 71.96 | 0 | 6621.909 | 6621.909 | -6621.909 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8093.4444 | 8093.4444 | 0 | 8.5 | 0 | 1348.9074 | 30% | 1 | 53.96% | 0% | 0% | 0% | 19.717 | 0 | 0 | 0 | 19.717 | 0 | 7931.5755 | 1586.3151 | 15.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.9915
2007-09-14 16:01 | 9 | 14 | 16 | 257 | 6160 | 71.06 | 0 | 6602.5035 | 6602.5035 | -6602.5035 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8069.7265 | 8069.7265 | 0 | 8.5 | 0 | 1344.9544 | 30% | 1 | 53.8% | 0% | 0% | 0% | 19.5843 | 0 | 0 | 0 | 19.5843 | 0 | 7908.332 | 1581.6664 | 15.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.8589
2007-09-14 17:01 | 9 | 14 | 17 | 257 | 6161 | 71.06 | 0 | 6077.1206 | 6077.1206 | -6077.1206 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7427.5918 | 7427.5918 | 0 | 8.5 | 0 | 1237.932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7279.04 | 1455.808 | 14.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 18:01 | 9 | 14 | 18 | 257 | 6162 | 69.08 | 0 | 3426.6693 | 3426.6693 | -3426.6693 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4188.1513 | 4188.1513 | 0 | 8.5 | 0 | 698.0252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4104.3883 | 820.8777 | 8.209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 19:01 | 9 | 14 | 19 | 257 | 6163 | 68 | 0 | 2403.1098 | 2403.1098 | -2403.1098 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2937.1341 | 2937.1341 | 0 | 8.5 | 0 | 489.5224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2878.3915 | 575.6783 | 5.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 20:01 | 9 | 14 | 20 | 257 | 6164 | 68 | 0 | 1590.1407 | 1590.1407 | -1590.1407 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1943.5053 | 1943.5053 | 0 | 8.5 | 0 | 323.9175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1904.6352 | 380.927 | 3.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 21:01 | 9 | 14 | 21 | 257 | 6165 | 66.92 | 0 | 875.7151 | 875.7151 | -875.7151 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1070.3184 | 1070.3184 | 0 | 8.5 | 0 | 178.3864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1048.912 | 209.7824 | 2.098% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 22:01 | 9 | 14 | 22 | 257 | 6166 | 66.92 | 0 | 688.2416 | 688.2416 | -688.2416 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 841.1842 | 841.1842 | 0 | 8.5 | 0 | 140.1974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 824.3605 | 164.8721 | 1.649% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-14 23:01 | 9 | 14 | 23 | 257 | 6167 | 66.92 | 0 | 537.7274 | 537.7274 | -537.7274 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 657.2224 | 657.2224 | 0 | 8.5 | 0 | 109.5371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 644.0779 | 128.8156 | 1.288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 00:01 | 9 | 15 | 0 | 258 | 6168 | 66.02 | 0 | 513.0323 | 513.0323 | -513.0323 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 627.0395 | 627.0395 | 0 | 8.5 | 0 | 104.5066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 614.4987 | 122.8997 | 1.229% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 01:01 | 9 | 15 | 1 | 258 | 6169 | 66.02 | 0 | 265.6721 | 265.6721 | -265.6721 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 324.7104 | 324.7104 | 0 | 8.5 | 0 | 54.1184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 318.2162 | 63.6432 | 0.6364% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 02:01 | 9 | 15 | 2 | 258 | 6170 | 66.02 | 0 | 461.9643 | 461.9643 | -461.9643 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 564.623 | 564.623 | 0 | 8.5 | 0 | 94.1038 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 553.3305 | 110.6661 | 1.107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 03:01 | 9 | 15 | 3 | 258 | 6171 | 64.94 | 0 | 373.9462 | 373.9462 | -373.9462 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 457.0453 | 457.0453 | 0 | 8.5 | 0 | 76.1742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 447.9044 | 89.5809 | 0.8958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 04:01 | 9 | 15 | 4 | 258 | 6172 | 64.4 | 0 | 256.3575 | 256.3575 | -256.3575 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 313.3258 | 313.3258 | 0 | 8.5 | 0 | 52.221 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 307.0593 | 61.4119 | 0.6141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 05:01 | 9 | 15 | 5 | 258 | 6173 | 59 | 0 | 93.0709 | 93.0709 | -93.0709 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 113.7533 | 113.7533 | 0 | 8.5 | 0 | 18.9589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 111.4783 | 22.2957 | 0.223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 06:01 | 9 | 15 | 6 | 258 | 6174 | 57.2 | 0 | 57.9704 | 57.9704 | -57.9704 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 70.8527 | 70.8527 | 0 | 8.5 | 0 | 11.8088 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 69.4356 | 13.8871 | 0.1389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 07:01 | 9 | 15 | 7 | 258 | 6175 | 55.4 | 0 | 38.1008 | 38.1008 | -38.1008 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 46.5677 | 46.5677 | 0 | 8.5 | 0 | 7.7613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 45.6363 | 9.1273 | 0.09127% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 08:01 | 9 | 15 | 8 | 258 | 6176 | 53.96 | 549.6752 | 5.5956 | 5.5956 | 544.0796 | Heating | 480.0702 | 8.5 | 480.0702 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 489.8676 | 0 | 97.9735 | 0.9797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 09:01 | 9 | 15 | 9 | 258 | 6177 | 53.96 | 153.3653 | 15.1323 | 15.1323 | 138.233 | Heating | 121.9703 | 8.5 | 121.9703 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.3941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 124.4595 | 0 | 24.8919 | 0.2489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 10:01 | 9 | 15 | 10 | 258 | 6178 | 55.04 | 0 | 120.037 | 120.037 | -120.037 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 146.7119 | 146.7119 | 0 | 8.5 | 0 | 24.452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 143.7776 | 28.7555 | 0.2876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 11:01 | 9 | 15 | 11 | 258 | 6179 | 55.04 | 0 | 82.9448 | 82.9448 | -82.9448 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 101.3769 | 101.3769 | 0 | 8.5 | 0 | 16.8962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 99.3494 | 19.8699 | 0.1987% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 12:01 | 9 | 15 | 12 | 258 | 6180 | 57.92 | 0 | 66.0681 | 66.0681 | -66.0681 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 80.7499 | 80.7499 | 0 | 8.5 | 0 | 13.4583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 79.1349 | 15.827 | 0.1583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 13:01 | 9 | 15 | 13 | 258 | 6181 | 60.08 | 0 | 75.0743 | 75.0743 | -75.0743 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 91.7575 | 91.7575 | 0 | 8.5 | 0 | 15.2929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 89.9224 | 17.9845 | 0.1798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 14:01 | 9 | 15 | 14 | 258 | 6182 | 60.08 | 0 | 61.3817 | 61.3817 | -61.3817 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 75.022 | 75.022 | 0 | 8.5 | 0 | 12.5037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 73.5216 | 14.7043 | 0.147% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 15:01 | 9 | 15 | 15 | 258 | 6183 | 60.98 | 0 | 67.5925 | 67.5925 | -67.5925 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 82.6131 | 82.6131 | 0 | 8.5 | 0 | 13.7689 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 80.9608 | 16.1922 | 0.1619% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 16:01 | 9 | 15 | 16 | 258 | 6184 | 62.06 | 0 | 87.6159 | 87.6159 | -87.6159 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 107.0861 | 107.0861 | 0 | 8.5 | 0 | 17.8477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 104.9444 | 20.9889 | 0.2099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 17:01 | 9 | 15 | 17 | 258 | 6185 | 62.06 | 0 | 115.5897 | 115.5897 | -115.5897 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 141.2763 | 141.2763 | 0 | 8.5 | 0 | 23.5461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 138.4508 | 27.6902 | 0.2769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 18:01 | 9 | 15 | 18 | 258 | 6186 | 57.92 | 46.4345 | 78.8628 | 78.8628 | -32.4282 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 96.3879 | 96.3879 | 0 | 8.5 | 0 | 16.0646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 94.4601 | 18.892 | 0.1889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 19:01 | 9 | 15 | 19 | 258 | 6187 | 53.96 | 0 | 23.7669 | 23.7669 | -23.7669 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 29.0485 | 29.0485 | 0 | 8.5 | 0 | 4.8414 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 28.4675 | 5.6935 | 0.05693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 20:01 | 9 | 15 | 20 | 258 | 6188 | 53.96 | 1.1295 | 5.0934 | 5.0934 | -3.9638 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6.2252 | 6.2252 | 0 | 8.5 | 0 | 1.0375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6.1007 | 1.2201 | 0.0122% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 21:01 | 9 | 15 | 21 | 258 | 6189 | 51.98 | 3.3195 | 0 | 0 | 3.3195 | Heating | 2.9289 | 8.5 | 2.9289 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.58579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.9887 | 0 | 0.59774 | 0.005977% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 22:01 | 9 | 15 | 22 | 258 | 6190 | 51.98 | 8.8438 | 0 | 0 | 8.8438 | Heating | 7.8034 | 8.5 | 7.8034 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.9626 | 0 | 1.5925 | 0.01593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-15 23:01 | 9 | 15 | 23 | 258 | 6191 | 51.98 | 18.4186 | 0 | 0 | 18.4186 | Heating | 16.2517 | 8.5 | 16.2517 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.2503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 16.5834 | 0 | 3.3167 | 0.03317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 00:01 | 9 | 16 | 0 | 259 | 6192 | 48.92 | 31.2188 | 0 | 0 | 31.2188 | Heating | 27.546 | 8.5 | 27.546 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.5092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 28.1082 | 0 | 5.6216 | 0.05622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 01:01 | 9 | 16 | 1 | 259 | 6193 | 48.92 | 43.2724 | 0 | 0 | 43.2724 | Heating | 38.1815 | 8.5 | 38.1815 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.6363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 38.9608 | 0 | 7.7922 | 0.07792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 02:01 | 9 | 16 | 2 | 259 | 6194 | 48.92 | 61.3377 | 0 | 0 | 61.3377 | Heating | 54.1215 | 8.5 | 54.1215 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.8243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 55.226 | 0 | 11.0452 | 0.1105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 03:01 | 9 | 16 | 3 | 259 | 6195 | 46.04 | 107.5658 | 0 | 0 | 107.5658 | Heating | 94.911 | 8.5 | 94.911 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.9822 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 96.848 | 0 | 19.3696 | 0.1937% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 04:01 | 9 | 16 | 4 | 259 | 6196 | 42.98 | 192.9817 | 0 | 0 | 192.9817 | Heating | 170.278 | 8.5 | 170.278 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.0556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 173.753 | 0 | 34.7506 | 0.3475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 05:01 | 9 | 16 | 5 | 259 | 6197 | 42.98 | 246.3682 | 0 | 0 | 246.3682 | Heating | 217.3837 | 8.5 | 217.3837 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.4767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 221.8201 | 0 | 44.364 | 0.4436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 06:01 | 9 | 16 | 6 | 259 | 6198 | 44.06 | 4315.5162 | 42.4901 | 42.4901 | 4273.0261 | Heating | 3770.3171 | 8.5 | 3770.3171 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 754.0634 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3847.2624 | 0 | 769.4525 | 7.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 07:01 | 9 | 16 | 7 | 259 | 6199 | 46.94 | 2643.0031 | 2.7149 | 2.7149 | 2640.2882 | Heating | 2329.666 | 8.5 | 2329.666 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 465.9332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2377.2102 | 0 | 475.442 | 4.754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 08:01 | 9 | 16 | 8 | 259 | 6200 | 46.94 | 1703.4746 | 86.3035 | 86.3035 | 1617.1712 | Heating | 1426.9157 | 8.5 | 1426.9157 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 285.3831 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1456.0365 | 0 | 291.2073 | 2.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 09:01 | 9 | 16 | 9 | 259 | 6201 | 53.06 | 707.2529 | 258.9627 | 258.9627 | 448.2902 | Heating | 395.5502 | 8.5 | 395.5502 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.11 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 403.6226 | 0 | 80.7245 | 0.8072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 10:01 | 9 | 16 | 10 | 259 | 6202 | 57.02 | 214.509 | 547.614 | 547.614 | -333.105 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 669.306 | 669.306 | 0 | 8.5 | 0 | 111.551 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 655.9199 | 131.184 | 1.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 11:01 | 9 | 16 | 11 | 259 | 6203 | 57.02 | 42.1901 | 738.9889 | 738.9889 | -696.7988 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 903.2087 | 903.2087 | 0 | 8.5 | 0 | 150.5348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 885.1445 | 177.0289 | 1.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 12:01 | 9 | 16 | 12 | 259 | 6204 | 60.08 | 27.9502 | 927.6716 | 927.6716 | -899.7214 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1133.8209 | 1133.8209 | 0 | 8.5 | 0 | 188.9702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1111.1445 | 222.2289 | 2.222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 13:01 | 9 | 16 | 13 | 259 | 6205 | 60.08 | 15.935 | 1262.159 | 1262.159 | -1246.224 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1542.6388 | 1542.6388 | 0 | 8.5 | 0 | 257.1065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1511.786 | 302.3572 | 3.024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 14:01 | 9 | 16 | 14 | 259 | 6206 | 60.08 | 13.7841 | 1228.3609 | 1228.3609 | -1214.5768 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1501.33 | 1501.33 | 0 | 8.5 | 0 | 250.2217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1471.3034 | 294.2607 | 2.943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 15:01 | 9 | 16 | 15 | 259 | 6207 | 59 | 10.5954 | 1300.846 | 1300.846 | -1290.2507 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1589.9229 | 1589.9229 | 0 | 8.5 | 0 | 264.9872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1558.1245 | 311.6249 | 3.116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 16:01 | 9 | 16 | 16 | 259 | 6208 | 60.98 | 11.3924 | 996.7386 | 996.7386 | -985.3463 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1218.2361 | 1218.2361 | 0 | 8.5 | 0 | 203.0393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1193.8714 | 238.7743 | 2.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 17:01 | 9 | 16 | 17 | 259 | 6209 | 60.98 | 16.4186 | 586.7707 | 586.7707 | -570.352 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 717.1641 | 717.1641 | 0 | 8.5 | 0 | 119.5274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 702.8208 | 140.5642 | 1.406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 18:01 | 9 | 16 | 18 | 259 | 6210 | 55.04 | 26.7866 | 266.181 | 266.181 | -239.3944 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 325.3324 | 325.3324 | 0 | 8.5 | 0 | 54.2221 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 318.8257 | 63.7651 | 0.6377% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 19:01 | 9 | 16 | 19 | 259 | 6211 | 50 | 77.8239 | 211.9267 | 211.9267 | -134.1028 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 259.0215 | 259.0215 | 0 | 8.5 | 0 | 43.1703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 253.8411 | 50.7682 | 0.5077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 20:01 | 9 | 16 | 20 | 259 | 6212 | 50 | 377.1328 | 105.0658 | 105.0658 | 272.0671 | Heating | 240.0592 | 8.5 | 240.0592 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.0118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 244.9583 | 0 | 48.9917 | 0.4899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 21:01 | 9 | 16 | 21 | 259 | 6213 | 46.94 | 121.2071 | 57.3609 | 57.3609 | 63.8462 | Heating | 56.3349 | 8.5 | 56.3349 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 57.4846 | 0 | 11.4969 | 0.115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 22:01 | 9 | 16 | 22 | 259 | 6214 | 46.04 | 147.2953 | 0 | 0 | 147.2953 | Heating | 129.9664 | 8.5 | 129.9664 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.9933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 132.6188 | 0 | 26.5238 | 0.2652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-16 23:01 | 9 | 16 | 23 | 259 | 6215 | 46.04 | 187.4123 | 0 | 0 | 187.4123 | Heating | 165.3638 | 8.5 | 165.3638 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.0728 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 168.7385 | 0 | 33.7477 | 0.3375% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 00:01 | 9 | 17 | 0 | 260 | 6216 | 44.06 | 231.8848 | 0 | 0 | 231.8848 | Heating | 204.6042 | 8.5 | 204.6042 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.9208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 208.7798 | 0 | 41.756 | 0.4176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 01:01 | 9 | 17 | 1 | 260 | 6217 | 42.98 | 282.7773 | 0 | 0 | 282.7773 | Heating | 249.5094 | 8.5 | 249.5094 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.9019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 254.6014 | 0 | 50.9203 | 0.5092% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 02:01 | 9 | 17 | 2 | 260 | 6218 | 42.98 | 337.4411 | 0 | 0 | 337.4411 | Heating | 297.7421 | 8.5 | 297.7421 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.5484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 303.8185 | 0 | 60.7637 | 0.6076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 03:01 | 9 | 17 | 3 | 260 | 6219 | 42.08 | 425.2794 | 0 | 0 | 425.2794 | Heating | 375.2466 | 8.5 | 375.2466 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.0493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 382.9047 | 0 | 76.5809 | 0.7658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 04:01 | 9 | 17 | 4 | 260 | 6220 | 41 | 473.0582 | 0 | 0 | 473.0582 | Heating | 417.4043 | 8.5 | 417.4043 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.4809 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 425.9227 | 0 | 85.1845 | 0.8518% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 05:01 | 9 | 17 | 5 | 260 | 6221 | 41 | 502.9638 | 0 | 0 | 502.9638 | Heating | 443.7915 | 8.5 | 443.7915 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.7583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 452.8485 | 0 | 90.5697 | 0.9057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 06:01 | 9 | 17 | 6 | 260 | 6222 | 42.8 | 5516.1723 | 0 | 0 | 5516.1723 | Heating | 4867.2108 | 8.5 | 4867.2108 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 973.4422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4966.5416 | 0 | 993.3083 | 9.933% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 07:01 | 9 | 17 | 7 | 260 | 6223 | 41 | 3801.4495 | 0 | 0 | 3801.4495 | Heating | 3354.2202 | 8.5 | 3354.2202 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 670.844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3422.6736 | 0 | 684.5347 | 6.845% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 08:01 | 9 | 17 | 8 | 260 | 6224 | 42.98 | 2714.2639 | 30.7204 | 30.7204 | 2683.5435 | Heating | 2367.8325 | 8.5 | 2367.8325 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 473.5665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2416.1556 | 0 | 483.2311 | 4.832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 09:01 | 9 | 17 | 9 | 260 | 6225 | 51.08 | 1527.29 | 123.1268 | 123.1268 | 1404.1632 | Heating | 1238.9675 | 8.5 | 1238.9675 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.7935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1264.2526 | 0 | 252.8505 | 2.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 10:01 | 9 | 17 | 10 | 260 | 6226 | 55.04 | 807.1054 | 271.3349 | 271.3349 | 535.7705 | Heating | 472.7387 | 8.5 | 472.7387 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.5477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 482.3864 | 0 | 96.4773 | 0.9648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 11:01 | 9 | 17 | 11 | 260 | 6227 | 55.04 | 424.4606 | 320.26 | 320.26 | 104.2006 | Heating | 91.9417 | 8.5 | 91.9417 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.3883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 93.8181 | 0 | 18.7636 | 0.1876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 12:01 | 9 | 17 | 12 | 260 | 6228 | 62.06 | 256.6832 | 377.5425 | 377.5425 | -120.8594 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 461.4409 | 461.4409 | 0 | 8.5 | 0 | 76.9068 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 452.2121 | 90.4424 | 0.9044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 13:01 | 9 | 17 | 13 | 260 | 6229 | 64.94 | 203.4734 | 538.8722 | 538.8722 | -335.3988 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 658.6215 | 658.6215 | 0 | 8.5 | 0 | 109.7703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 645.4491 | 129.0898 | 1.291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 14:01 | 9 | 17 | 14 | 260 | 6230 | 64.94 | 173.991 | 729.4515 | 729.4515 | -555.4605 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 891.5519 | 891.5519 | 0 | 8.5 | 0 | 148.592 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 873.7208 | 174.7442 | 1.747% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 15:01 | 9 | 17 | 15 | 260 | 6231 | 66.02 | 162.675 | 643.4155 | 643.4155 | -480.7405 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 786.3967 | 786.3967 | 0 | 8.5 | 0 | 131.0661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 770.6688 | 154.1338 | 1.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 16:01 | 9 | 17 | 16 | 260 | 6232 | 66.92 | 158.4722 | 469.6097 | 469.6097 | -311.1375 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 573.9674 | 573.9674 | 0 | 8.5 | 0 | 95.6612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 562.4881 | 112.4976 | 1.125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 17:01 | 9 | 17 | 17 | 260 | 6233 | 66.92 | 163.6782 | 357.0765 | 357.0765 | -193.3983 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 436.4268 | 436.4268 | 0 | 8.5 | 0 | 72.7378 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 427.6983 | 85.5397 | 0.8554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 18:01 | 9 | 17 | 18 | 260 | 6234 | 62.06 | 300.6769 | 152.3976 | 152.3976 | 148.2793 | Heating | 130.8347 | 8.5 | 130.8347 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.1669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 133.5048 | 0 | 26.701 | 0.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 19:01 | 9 | 17 | 19 | 260 | 6235 | 55.94 | 811.3558 | 86.8665 | 86.8665 | 724.4893 | Heating | 639.2553 | 8.5 | 639.2553 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.8511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 652.3013 | 0 | 130.4603 | 1.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 20:01 | 9 | 17 | 20 | 260 | 6236 | 55.94 | 1279.1586 | 20.3081 | 20.3081 | 1258.8505 | Heating | 1110.7505 | 8.5 | 1110.7505 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.1501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1133.4189 | 0 | 226.6838 | 2.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 21:01 | 9 | 17 | 21 | 260 | 6237 | 51.08 | 347.5271 | 2.5821 | 2.5821 | 344.945 | Heating | 304.3632 | 8.5 | 304.3632 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.8726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 310.5747 | 0 | 62.1149 | 0.6211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 22:01 | 9 | 17 | 22 | 260 | 6238 | 50 | 437.2266 | 0 | 0 | 437.2266 | Heating | 385.7881 | 8.5 | 385.7881 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.1576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 393.6614 | 0 | 78.7323 | 0.7873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-17 23:01 | 9 | 17 | 23 | 260 | 6239 | 50 | 496.3622 | 0 | 0 | 496.3622 | Heating | 437.9666 | 8.5 | 437.9666 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.5933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 446.9047 | 0 | 89.3809 | 0.8938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 00:01 | 9 | 18 | 0 | 261 | 6240 | 48.02 | 556.4579 | 0 | 0 | 556.4579 | Heating | 490.9923 | 8.5 | 490.9923 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.1985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 501.0125 | 0 | 100.2025 | 1.002% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 01:01 | 9 | 18 | 1 | 261 | 6241 | 46.4 | 614.1085 | 0 | 0 | 614.1085 | Heating | 541.8605 | 8.5 | 541.8605 | 0 | 4.1996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.3721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 552.9189 | 0 | 110.5838 | 1.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 02:01 | 9 | 18 | 2 | 261 | 6242 | 46.04 | 648.0322 | 0 | 0 | 648.0322 | Heating | 571.7931 | 8.5 | 571.7931 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.3586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 583.4624 | 0 | 116.6925 | 1.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 03:01 | 9 | 18 | 3 | 261 | 6243 | 44.6 | 684.6157 | 0 | 0 | 684.6157 | Heating | 604.0726 | 8.5 | 604.0726 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.8145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 616.4006 | 0 | 123.2801 | 1.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 04:01 | 9 | 18 | 4 | 261 | 6244 | 44.6 | 723.7444 | 0 | 0 | 723.7444 | Heating | 638.598 | 8.5 | 638.598 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.7196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 651.6306 | 0 | 130.3261 | 1.303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 05:01 | 9 | 18 | 5 | 261 | 6245 | 44.06 | 766.2068 | 0 | 0 | 766.2068 | Heating | 676.0649 | 8.5 | 676.0649 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 689.8621 | 0 | 137.9724 | 1.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 06:01 | 9 | 18 | 6 | 261 | 6246 | 44.6 | 7428.9658 | 0 | 0 | 7428.9658 | Heating | 6554.9698 | 8.5 | 6554.9698 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1310.994 | 30% | 1 | 52.44% | 0% | 0% | 0% | 18.4656 | 0 | 0 | 0 | 18.4656 | 6688.7447 | 0 | 1337.7489 | 13.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.7401
2007-09-18 07:01 | 9 | 18 | 7 | 261 | 6247 | 42.8 | 5028.1387 | 0 | 0 | 5028.1387 | Heating | 4436.593 | 8.5 | 4436.593 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 887.3186 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4527.1357 | 0 | 905.4271 | 9.054% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 08:01 | 9 | 18 | 8 | 261 | 6248 | 44.96 | 3352.6206 | 8.6164 | 8.6164 | 3344.0042 | Heating | 2950.5919 | 8.5 | 2950.5919 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 590.1184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3010.8081 | 0 | 602.1616 | 6.022% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 09:01 | 9 | 18 | 9 | 261 | 6249 | 53.96 | 1881.688 | 47.58 | 47.58 | 1834.108 | Heating | 1618.3306 | 8.5 | 1618.3306 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.6661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1651.3578 | 0 | 330.2716 | 3.303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 10:01 | 9 | 18 | 10 | 261 | 6250 | 57.92 | 1113.4394 | 140.6316 | 140.6316 | 972.8078 | Heating | 858.3598 | 8.5 | 858.3598 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 875.8773 | 0 | 175.1755 | 1.752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 11:01 | 9 | 18 | 11 | 261 | 6251 | 57.92 | 498.7231 | 292.3475 | 292.3475 | 206.3756 | Heating | 182.0961 | 8.5 | 182.0961 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.4192 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 185.8124 | 0 | 37.1625 | 0.3716% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 12:01 | 9 | 18 | 12 | 261 | 6252 | 66.02 | 221.1167 | 441.0557 | 441.0557 | -219.939 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 539.0681 | 539.0681 | 0 | 8.5 | 0 | 89.8447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 528.2867 | 105.6573 | 1.057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 13:01 | 9 | 18 | 13 | 261 | 6253 | 68 | 143.5775 | 633.4323 | 633.4323 | -489.8549 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 774.1951 | 774.1951 | 0 | 8.5 | 0 | 129.0325 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 758.7112 | 151.7422 | 1.517% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 14:01 | 9 | 18 | 14 | 261 | 6254 | 68 | 94.3952 | 858.2303 | 858.2303 | -763.8351 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1048.9481 | 1048.9481 | 0 | 8.5 | 0 | 174.8247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1027.9692 | 205.5938 | 2.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 15:01 | 9 | 18 | 15 | 261 | 6255 | 69.98 | 71.1947 | 863.9289 | 863.9289 | -792.7342 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1055.9131 | 1055.9131 | 0 | 8.5 | 0 | 175.9855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1034.7948 | 206.959 | 2.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 16:01 | 9 | 18 | 16 | 261 | 6256 | 69.98 | 53.3281 | 778.7627 | 778.7627 | -725.4347 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 951.8211 | 951.8211 | 0 | 8.5 | 0 | 158.6369 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 932.7847 | 186.5569 | 1.866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 17:01 | 9 | 18 | 17 | 261 | 6257 | 69.98 | 40.8796 | 641.1303 | 641.1303 | -600.2507 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 783.6037 | 783.6037 | 0 | 8.5 | 0 | 130.6006 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 767.9317 | 153.5863 | 1.536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 18:01 | 9 | 18 | 18 | 261 | 6258 | 64.94 | 61.2385 | 251.1929 | 251.1929 | -189.9544 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 307.0136 | 307.0136 | 0 | 8.5 | 0 | 51.1689 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 300.8733 | 60.1747 | 0.6017% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 19:01 | 9 | 18 | 19 | 261 | 6259 | 59 | 172.7931 | 176.0382 | 176.0382 | -3.2451 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 215.1578 | 215.1578 | 0 | 8.5 | 0 | 35.8596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 210.8547 | 42.1709 | 0.4217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 20:01 | 9 | 18 | 20 | 261 | 6260 | 59 | 594.5602 | 89.7604 | 89.7604 | 504.7997 | Heating | 445.4115 | 8.5 | 445.4115 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 89.0823 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 454.5016 | 0 | 90.9003 | 0.909% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 21:01 | 9 | 18 | 21 | 261 | 6261 | 53.96 | 254.7212 | 44.3069 | 44.3069 | 210.4143 | Heating | 185.6597 | 8.5 | 185.6597 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 37.1319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 189.4486 | 0 | 37.8897 | 0.3789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 22:01 | 9 | 18 | 22 | 261 | 6262 | 53.96 | 350.8679 | 0 | 0 | 350.8679 | Heating | 309.5893 | 8.5 | 309.5893 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.9179 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 315.9075 | 0 | 63.1815 | 0.6318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-18 23:01 | 9 | 18 | 23 | 261 | 6263 | 53.96 | 467.763 | 0 | 0 | 467.763 | Heating | 412.732 | 8.5 | 412.732 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.5464 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 421.1551 | 0 | 84.231 | 0.8423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 00:01 | 9 | 19 | 0 | 262 | 6264 | 50 | 587.8082 | 0 | 0 | 587.8082 | Heating | 518.6543 | 8.5 | 518.6543 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 103.7309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 529.2391 | 0 | 105.8478 | 1.058% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 01:01 | 9 | 19 | 1 | 262 | 6265 | 48.02 | 659.1678 | 0 | 0 | 659.1678 | Heating | 581.6187 | 8.5 | 581.6187 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.3237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 593.4884 | 0 | 118.6977 | 1.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 02:01 | 9 | 19 | 2 | 262 | 6266 | 48.02 | 718.2381 | 0 | 0 | 718.2381 | Heating | 633.7395 | 8.5 | 633.7395 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.7479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 646.673 | 0 | 129.3346 | 1.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 03:01 | 9 | 19 | 3 | 262 | 6267 | 46.94 | 788.2792 | 0 | 0 | 788.2792 | Heating | 695.5404 | 8.5 | 695.5404 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.1081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 709.7352 | 0 | 141.947 | 1.419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 04:01 | 9 | 19 | 4 | 262 | 6268 | 46.04 | 801.4624 | 0 | 0 | 801.4624 | Heating | 707.1727 | 8.5 | 707.1727 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.4345 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 721.6048 | 0 | 144.321 | 1.443% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 05:01 | 9 | 19 | 5 | 262 | 6269 | 44.6 | 791.9879 | 0 | 0 | 791.9879 | Heating | 698.8129 | 8.5 | 698.8129 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.7626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 713.0744 | 0 | 142.6149 | 1.426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 06:01 | 9 | 19 | 6 | 262 | 6270 | 44.6 | 7402.2432 | 0 | 0 | 7402.2432 | Heating | 6531.3911 | 8.5 | 6531.3911 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1306.2782 | 30% | 1 | 52.25% | 0% | 0% | 0% | 18.3132 | 0 | 0 | 0 | 18.3132 | 6664.6848 | 0 | 1332.937 | 13.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.5877
2007-09-19 07:01 | 9 | 19 | 7 | 262 | 6271 | 46.4 | 5052.857 | 0 | 0 | 5052.857 | Heating | 4458.4032 | 8.5 | 4458.4032 | 0 | 4.1996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 891.6806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4549.391 | 0 | 909.8782 | 9.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 08:01 | 9 | 19 | 8 | 262 | 6272 | 46.94 | 3542.7009 | 0 | 0 | 3542.7009 | Heating | 3125.9126 | 8.5 | 3125.9126 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 625.1825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3189.7067 | 0 | 637.9413 | 6.379% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 09:01 | 9 | 19 | 9 | 262 | 6273 | 57.02 | 2076.5238 | 1.8946 | 1.8946 | 2074.6292 | Heating | 1830.5552 | 8.5 | 1830.5552 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 366.111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1867.9135 | 0 | 373.5827 | 3.736% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 10:01 | 9 | 19 | 10 | 262 | 6274 | 60.98 | 1107.1328 | 41.1783 | 41.1783 | 1065.9544 | Heating | 940.548 | 8.5 | 940.548 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.1096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 959.7429 | 0 | 191.9486 | 1.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 11:01 | 9 | 19 | 11 | 262 | 6275 | 60.98 | 302.4141 | 207.2383 | 207.2383 | 95.1758 | Heating | 83.9786 | 8.5 | 83.9786 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.7957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 85.6925 | 0 | 17.1385 | 0.1714% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 12:01 | 9 | 19 | 12 | 262 | 6276 | 68 | 175.314 | 301.5931 | 301.5931 | -126.2791 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 368.6138 | 368.6138 | 0 | 8.5 | 0 | 61.4356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 361.2415 | 72.2483 | 0.7225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 13:01 | 9 | 19 | 13 | 262 | 6277 | 71.96 | 179.1476 | 386.1127 | 386.1127 | -206.9651 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 471.9155 | 471.9155 | 0 | 8.5 | 0 | 78.6526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 462.4772 | 92.4954 | 0.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 14:01 | 9 | 19 | 14 | 262 | 6278 | 71.96 | 183.5908 | 473.618 | 473.618 | -290.0272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 578.8664 | 578.8664 | 0 | 8.5 | 0 | 96.4777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 567.2891 | 113.4578 | 1.135% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 15:01 | 9 | 19 | 15 | 262 | 6279 | 73.04 | 174.3229 | 362.7665 | 362.7665 | -188.4436 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 443.3813 | 443.3813 | 0 | 8.5 | 0 | 73.8969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 434.5137 | 86.9027 | 0.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 16:01 | 9 | 19 | 16 | 262 | 6280 | 73.04 | 164.8331 | 247.6286 | 247.6286 | -82.7955 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 302.6572 | 302.6572 | 0 | 8.5 | 0 | 50.4429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 296.604 | 59.3208 | 0.5932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 17:01 | 9 | 19 | 17 | 262 | 6281 | 73.04 | 214.3634 | 148.2982 | 148.2982 | 66.0652 | Heating | 58.2929 | 8.5 | 58.2929 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.6586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 59.4825 | 0 | 11.8965 | 0.119% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 18:01 | 9 | 19 | 18 | 262 | 6282 | 68 | 433.0144 | 59.2375 | 59.2375 | 373.7769 | Heating | 329.8032 | 8.5 | 329.8032 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.9606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 336.5339 | 0 | 67.3068 | 0.6731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 19:01 | 9 | 19 | 19 | 262 | 6283 | 62.06 | 766.7871 | 40.2851 | 40.2851 | 726.502 | Heating | 641.0311 | 8.5 | 641.0311 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.2062 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 654.1134 | 0 | 130.8227 | 1.308% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 20:01 | 9 | 19 | 20 | 262 | 6284 | 62.06 | 897.1302 | 6.66 | 6.66 | 890.4702 | Heating | 785.709 | 8.5 | 785.709 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.1418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 801.7439 | 0 | 160.3488 | 1.603% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 21:01 | 9 | 19 | 21 | 262 | 6285 | 57.92 | 244.9527 | 2.2589 | 2.2589 | 242.6938 | Heating | 214.1416 | 8.5 | 214.1416 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 42.8283 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 218.5118 | 0 | 43.7024 | 0.437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 22:01 | 9 | 19 | 22 | 262 | 6286 | 60.08 | 272.3394 | 0 | 0 | 272.3394 | Heating | 240.2995 | 8.5 | 240.2995 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.0599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 245.2036 | 0 | 49.0407 | 0.4904% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-19 23:01 | 9 | 19 | 23 | 262 | 6287 | 57.02 | 288.4065 | 0 | 0 | 288.4065 | Heating | 254.4763 | 8.5 | 254.4763 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.8953 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 259.6697 | 0 | 51.9339 | 0.5193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 00:01 | 9 | 20 | 0 | 263 | 6288 | 55.94 | 303.9213 | 0 | 0 | 303.9213 | Heating | 268.1658 | 8.5 | 268.1658 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.6332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 273.6386 | 0 | 54.7277 | 0.5473% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 01:01 | 9 | 20 | 1 | 263 | 6289 | 55.94 | 315.618 | 0 | 0 | 315.618 | Heating | 278.4864 | 8.5 | 278.4864 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.6973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 284.1698 | 0 | 56.834 | 0.5683% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 02:01 | 9 | 20 | 2 | 263 | 6290 | 55.94 | 325.1448 | 0 | 0 | 325.1448 | Heating | 286.8925 | 8.5 | 286.8925 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.3785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 292.7475 | 0 | 58.5495 | 0.5855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 03:01 | 9 | 20 | 3 | 263 | 6291 | 51.08 | 333.5284 | 0 | 0 | 333.5284 | Heating | 294.2897 | 8.5 | 294.2897 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.8579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 300.2957 | 0 | 60.0591 | 0.6006% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 04:01 | 9 | 20 | 4 | 263 | 6292 | 51.08 | 337.0251 | 0 | 0 | 337.0251 | Heating | 297.3751 | 8.5 | 297.3751 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 303.4439 | 0 | 60.6888 | 0.6069% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 05:01 | 9 | 20 | 5 | 263 | 6293 | 51.08 | 342.5715 | 0 | 0 | 342.5715 | Heating | 302.269 | 8.5 | 302.269 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.4538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 308.4378 | 0 | 61.6876 | 0.6169% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 06:01 | 9 | 20 | 6 | 263 | 6294 | 50 | 3732.181 | 50.7474 | 50.7474 | 3681.4336 | Heating | 3248.3238 | 8.5 | 3248.3238 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 649.6648 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3314.6161 | 0 | 662.9232 | 6.629% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 07:01 | 9 | 20 | 7 | 263 | 6295 | 55.04 | 2432.2546 | 0 | 0 | 2432.2546 | Heating | 2146.107 | 8.5 | 2146.107 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 429.2214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2189.9051 | 0 | 437.981 | 4.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 08:01 | 9 | 20 | 8 | 263 | 6296 | 55.04 | 1414.5198 | 36.0647 | 36.0647 | 1378.4551 | Heating | 1216.2839 | 8.5 | 1216.2839 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 243.2568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1241.106 | 0 | 248.2212 | 2.482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 09:01 | 9 | 20 | 9 | 263 | 6297 | 62.96 | 457.3365 | 144.5647 | 144.5647 | 312.7718 | Heating | 275.9751 | 8.5 | 275.9751 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 281.6072 | 0 | 56.3214 | 0.5632% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 10:01 | 9 | 20 | 10 | 263 | 6298 | 66.92 | 123.6711 | 401.1087 | 401.1087 | -277.4376 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 490.244 | 490.244 | 0 | 8.5 | 0 | 81.7073 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 480.4391 | 96.0878 | 0.9609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 11:01 | 9 | 20 | 11 | 263 | 6299 | 66.92 | 72.002 | 583.7346 | 583.7346 | -511.7326 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 713.4534 | 713.4534 | 0 | 8.5 | 0 | 118.9089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 699.1843 | 139.8369 | 1.398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 12:01 | 9 | 20 | 12 | 263 | 6300 | 75.02 | 61.5382 | 750.6102 | 750.6102 | -689.072 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 917.4124 | 917.4124 | 0 | 8.5 | 0 | 152.9021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 899.0642 | 179.8128 | 1.798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 13:01 | 9 | 20 | 13 | 263 | 6301 | 77 | 31.2703 | 1244.9724 | 1244.9724 | -1213.7021 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1521.6329 | 1521.6329 | 0 | 8.5 | 0 | 253.6055 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1491.2002 | 298.24 | 2.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 14:01 | 9 | 20 | 14 | 263 | 6302 | 77 | 12.662 | 1753.9715 | 1753.9715 | -1741.3096 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2143.743 | 2143.743 | 0 | 8.5 | 0 | 357.2905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2100.8681 | 420.1736 | 4.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 15:01 | 9 | 20 | 15 | 263 | 6303 | 80.06 | 11.3408 | 1711.0659 | 1711.0659 | -1699.7252 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2091.3028 | 2091.3028 | 0 | 8.5 | 0 | 348.5505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2049.4768 | 409.8954 | 4.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 16:01 | 9 | 20 | 16 | 263 | 6304 | 80.06 | 5.3743 | 1641.9591 | 1641.9591 | -1636.5848 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2006.8389 | 2006.8389 | 0 | 8.5 | 0 | 334.4732 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1966.7021 | 393.3404 | 3.933% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 17:01 | 9 | 20 | 17 | 263 | 6305 | 80.06 | 3.5718 | 1088.6235 | 1088.6235 | -1085.0516 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1330.5398 | 1330.5398 | 0 | 8.5 | 0 | 221.7566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1303.929 | 260.7858 | 2.608% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 18:01 | 9 | 20 | 18 | 263 | 6306 | 75.02 | 11.1787 | 305.5177 | 305.5177 | -294.3389 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 373.4105 | 373.4105 | 0 | 8.5 | 0 | 62.2351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 365.9423 | 73.1885 | 0.7319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 19:01 | 9 | 20 | 19 | 263 | 6307 | 69.98 | 40.2515 | 238.1702 | 238.1702 | -197.9187 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 291.0969 | 291.0969 | 0 | 8.5 | 0 | 48.5162 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 285.275 | 57.055 | 0.5705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 20:01 | 9 | 20 | 20 | 263 | 6308 | 69.98 | 76.7993 | 144.0067 | 144.0067 | -67.2074 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 176.0081 | 176.0081 | 0 | 8.5 | 0 | 29.3347 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 172.488 | 34.4976 | 0.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 21:01 | 9 | 20 | 21 | 263 | 6309 | 64.94 | 102.7437 | 88.3154 | 88.3154 | 14.4283 | Heating | 12.7308 | 8.5 | 12.7308 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.9907 | 0 | 2.5981 | 0.02598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 22:01 | 9 | 20 | 22 | 263 | 6310 | 64.04 | 183.5291 | 0 | 0 | 183.5291 | Heating | 161.9374 | 8.5 | 161.9374 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.3875 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 165.2423 | 0 | 33.0485 | 0.3305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-20 23:01 | 9 | 20 | 23 | 263 | 6311 | 64.04 | 268.6245 | 0 | 0 | 268.6245 | Heating | 237.0216 | 8.5 | 237.0216 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.4043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 241.8588 | 0 | 48.3718 | 0.4837% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 00:01 | 9 | 21 | 0 | 264 | 6312 | 62.96 | 354.3693 | 0 | 0 | 354.3693 | Heating | 312.6788 | 8.5 | 312.6788 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.5358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 319.06 | 0 | 63.812 | 0.6381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 01:01 | 9 | 21 | 1 | 264 | 6313 | 62.06 | 430.0956 | 0 | 0 | 430.0956 | Heating | 379.4962 | 8.5 | 379.4962 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.8992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 387.241 | 0 | 77.4482 | 0.7745% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 02:01 | 9 | 21 | 2 | 264 | 6314 | 62.06 | 502.4726 | 0 | 0 | 502.4726 | Heating | 443.3581 | 8.5 | 443.3581 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.6716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 452.4063 | 0 | 90.4813 | 0.9048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 03:01 | 9 | 21 | 3 | 264 | 6315 | 59 | 562.9178 | 0 | 0 | 562.9178 | Heating | 496.6922 | 8.5 | 496.6922 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.3384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 506.8287 | 0 | 101.3657 | 1.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 04:01 | 9 | 21 | 4 | 264 | 6316 | 57.2 | 578.3735 | 0 | 0 | 578.3735 | Heating | 510.3296 | 8.5 | 510.3296 | 0 | 5.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.0659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 520.7445 | 0 | 104.1489 | 1.041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 05:01 | 9 | 21 | 5 | 264 | 6317 | 57.02 | 603.0082 | 0 | 0 | 603.0082 | Heating | 532.0661 | 8.5 | 532.0661 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.4132 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.9246 | 0 | 108.5849 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 06:01 | 9 | 21 | 6 | 264 | 6318 | 55.4 | 6137.5903 | 0 | 0 | 6137.5903 | Heating | 5415.5208 | 8.5 | 5415.5208 | 0 | 5.0667 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1083.1042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5526.0417 | 0 | 1105.2083 | 11.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 07:01 | 9 | 21 | 7 | 264 | 6319 | 55.4 | 4276.8248 | 0 | 0 | 4276.8248 | Heating | 3773.6689 | 8.5 | 3773.6689 | 0 | 5.0667 | 0 | 0 | 0 | 0 | 8.5 | 0 | 754.7338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3850.6826 | 0 | 770.1365 | 7.701% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 08:01 | 9 | 21 | 8 | 264 | 6320 | 57.02 | 3041.1363 | 10.1582 | 10.1582 | 3030.9781 | Heating | 2674.3924 | 8.5 | 2674.3924 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 534.8785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2728.9719 | 0 | 545.7944 | 5.458% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 09:01 | 9 | 21 | 9 | 264 | 6321 | 62.6 | 1592.5717 | 36.8883 | 36.8883 | 1555.6834 | Heating | 1372.6618 | 8.5 | 1372.6618 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.5324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1400.6753 | 0 | 280.1351 | 2.801% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 10:01 | 9 | 21 | 10 | 264 | 6322 | 68 | 460.8349 | 77.0525 | 77.0525 | 383.7823 | Heating | 338.6315 | 8.5 | 338.6315 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 67.7263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 345.5423 | 0 | 69.1085 | 0.6911% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 11:01 | 9 | 21 | 11 | 264 | 6323 | 68 | 88.1628 | 129.8507 | 129.8507 | -41.6879 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 158.7064 | 158.7064 | 0 | 8.5 | 0 | 26.4511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 155.5323 | 31.1065 | 0.3111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 12:01 | 9 | 21 | 12 | 264 | 6324 | 75.92 | 28.9481 | 183.7441 | 183.7441 | -154.796 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 224.5762 | 224.5762 | 0 | 8.5 | 0 | 37.4294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 220.0846 | 44.0169 | 0.4402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 13:01 | 9 | 21 | 13 | 264 | 6325 | 78.98 | 10.0998 | 683.4291 | 683.4291 | -673.3293 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 835.3022 | 835.3022 | 0 | 8.5 | 0 | 139.217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 818.5962 | 163.7192 | 1.637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 14:01 | 9 | 21 | 14 | 264 | 6326 | 78.98 | 5.3831 | 968.4859 | 968.4859 | -963.1028 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1183.705 | 1183.705 | 0 | 8.5 | 0 | 197.2842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1160.0309 | 232.0062 | 2.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 15:01 | 9 | 21 | 15 | 264 | 6327 | 80.96 | 3.9764 | 1090.2484 | 1090.2484 | -1086.272 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1332.5258 | 1332.5258 | 0 | 8.5 | 0 | 222.0876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1305.8753 | 261.1751 | 2.612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 16:01 | 9 | 21 | 16 | 264 | 6328 | 80.96 | 1.2784 | 1262.4107 | 1262.4107 | -1261.1323 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1542.9464 | 1542.9464 | 0 | 8.5 | 0 | 257.1577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1512.0875 | 302.4175 | 3.024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 17:01 | 9 | 21 | 17 | 264 | 6329 | 80.96 | 1.6227 | 787.7791 | 787.7791 | -786.1565 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 962.8412 | 962.8412 | 0 | 8.5 | 0 | 160.4735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 943.5843 | 188.7169 | 1.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 18:01 | 9 | 21 | 18 | 264 | 6330 | 75.92 | 10.6369 | 0 | 0 | 10.6369 | Heating | 9.3855 | 8.5 | 9.3855 | 0 | 8.2577 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.8771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 9.5771 | 0 | 1.9154 | 0.01915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 19:01 | 9 | 21 | 19 | 264 | 6331 | 73.94 | 71.0075 | 0 | 0 | 71.0075 | Heating | 62.6537 | 8.5 | 62.6537 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.5307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 63.9323 | 0 | 12.7865 | 0.1279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 20:01 | 9 | 21 | 20 | 264 | 6332 | 73.94 | 500.2419 | 0 | 0 | 500.2419 | Heating | 441.3899 | 8.5 | 441.3899 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 450.3979 | 0 | 90.0796 | 0.9008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 21:01 | 9 | 21 | 21 | 264 | 6333 | 71.06 | 1207.3563 | 0 | 0 | 1207.3563 | Heating | 1065.3144 | 8.5 | 1065.3144 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 213.0629 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1087.0555 | 0 | 217.4111 | 2.174% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 22:01 | 9 | 21 | 22 | 264 | 6334 | 69.98 | 164.454 | 0 | 0 | 164.454 | Heating | 145.1065 | 8.5 | 145.1065 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.0213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 148.0678 | 0 | 29.6136 | 0.2961% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-21 23:01 | 9 | 21 | 23 | 264 | 6335 | 69.98 | 163.5683 | 0 | 0 | 163.5683 | Heating | 144.3249 | 8.5 | 144.3249 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 147.2703 | 0 | 29.4541 | 0.2945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 00:01 | 9 | 22 | 0 | 265 | 6336 | 66.92 | 167.3795 | 0 | 0 | 167.3795 | Heating | 147.6878 | 8.5 | 147.6878 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.5376 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 150.7019 | 0 | 30.1404 | 0.3014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 01:01 | 9 | 22 | 1 | 265 | 6337 | 64.04 | 186.2138 | 0 | 0 | 186.2138 | Heating | 164.3063 | 8.5 | 164.3063 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.8613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 167.6595 | 0 | 33.5319 | 0.3353% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 02:01 | 9 | 22 | 2 | 265 | 6338 | 64.04 | 214.6788 | 0 | 0 | 214.6788 | Heating | 189.4224 | 8.5 | 189.4224 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 37.8845 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 193.2882 | 0 | 38.6576 | 0.3866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 03:01 | 9 | 22 | 3 | 265 | 6339 | 62.06 | 215.5983 | 0 | 0 | 215.5983 | Heating | 190.2338 | 8.5 | 190.2338 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.0468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 194.1161 | 0 | 38.8232 | 0.3882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 04:01 | 9 | 22 | 4 | 265 | 6340 | 62.96 | 195.3992 | 0 | 0 | 195.3992 | Heating | 172.411 | 8.5 | 172.411 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.4822 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 175.9296 | 0 | 35.1859 | 0.3519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 05:01 | 9 | 22 | 5 | 265 | 6341 | 62.96 | 207.8867 | 0 | 0 | 207.8867 | Heating | 183.4295 | 8.5 | 183.4295 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.6859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 187.1729 | 0 | 37.4346 | 0.3743% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 06:01 | 9 | 22 | 6 | 265 | 6342 | 60.98 | 193.7163 | 0 | 0 | 193.7163 | Heating | 170.9261 | 8.5 | 170.9261 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.1852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 174.4144 | 0 | 34.8829 | 0.3488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 07:01 | 9 | 22 | 7 | 265 | 6343 | 62.96 | 174.9602 | 0 | 0 | 174.9602 | Heating | 154.3767 | 8.5 | 154.3767 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.8753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 157.5272 | 0 | 31.5054 | 0.3151% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 08:01 | 9 | 22 | 8 | 265 | 6344 | 62.96 | 2714.1699 | 0 | 0 | 2714.1699 | Heating | 2394.8558 | 8.5 | 2394.8558 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 478.9712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2443.7304 | 0 | 488.7461 | 4.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 09:01 | 9 | 22 | 9 | 265 | 6345 | 69.08 | 1799.7614 | 0 | 0 | 1799.7614 | Heating | 1588.0248 | 8.5 | 1588.0248 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1620.4335 | 0 | 324.0867 | 3.241% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 10:01 | 9 | 22 | 10 | 265 | 6346 | 71.96 | 1145.3706 | 0 | 0 | 1145.3706 | Heating | 1010.6212 | 8.5 | 1010.6212 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.1242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1031.2461 | 0 | 206.2492 | 2.062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 11:01 | 9 | 22 | 11 | 265 | 6347 | 71.96 | 763.7924 | 0 | 0 | 763.7924 | Heating | 673.9345 | 8.5 | 673.9345 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 134.7869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 687.6883 | 0 | 137.5377 | 1.375% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 12:01 | 9 | 22 | 12 | 265 | 6348 | 73.94 | 398.3499 | 0 | 0 | 398.3499 | Heating | 351.4852 | 8.5 | 351.4852 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 358.6584 | 0 | 71.7317 | 0.7173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 13:01 | 9 | 22 | 13 | 265 | 6349 | 77 | 339.9431 | 0 | 0 | 339.9431 | Heating | 299.9498 | 8.5 | 299.9498 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.99 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 306.0712 | 0 | 61.2142 | 0.6121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 14:01 | 9 | 22 | 14 | 265 | 6350 | 77 | 257.6972 | 0 | 0 | 257.6972 | Heating | 227.3798 | 8.5 | 227.3798 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 232.0202 | 0 | 46.404 | 0.464% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 15:01 | 9 | 22 | 15 | 265 | 6351 | 78.08 | 130.6119 | 0 | 0 | 130.6119 | Heating | 115.2458 | 8.5 | 115.2458 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.0492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 117.5978 | 0 | 23.5196 | 0.2352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 16:01 | 9 | 22 | 16 | 265 | 6352 | 78.08 | 72.1542 | 0 | 0 | 72.1542 | Heating | 63.6654 | 8.5 | 63.6654 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.7331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 64.9647 | 0 | 12.9929 | 0.1299% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 17:01 | 9 | 22 | 17 | 265 | 6353 | 78.08 | 502.7172 | 0 | 0 | 502.7172 | Heating | 443.574 | 8.5 | 443.574 | 0 | 8.7101 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.7148 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 452.6266 | 0 | 90.5253 | 0.9053% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 18:01 | 9 | 22 | 18 | 265 | 6354 | 75.2 | 780.2206 | 0 | 0 | 780.2206 | Heating | 688.4299 | 8.5 | 688.4299 | 0 | 8.1123 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 702.4795 | 0 | 140.4959 | 1.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 19:01 | 9 | 22 | 19 | 265 | 6355 | 71.96 | 38.4682 | 0 | 0 | 38.4682 | Heating | 33.9425 | 8.5 | 33.9425 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.6352 | 0 | 6.927 | 0.06927% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 20:01 | 9 | 22 | 20 | 265 | 6356 | 71.96 | 41.4165 | 0 | 0 | 41.4165 | Heating | 36.544 | 8.5 | 36.544 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.3088 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 37.2898 | 0 | 7.458 | 0.07458% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 21:01 | 9 | 22 | 21 | 265 | 6357 | 68 | 53.7075 | 0 | 0 | 53.7075 | Heating | 47.389 | 8.5 | 47.389 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.4778 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 48.3561 | 0 | 9.6712 | 0.09671% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 22:01 | 9 | 22 | 22 | 265 | 6358 | 68 | 69.0787 | 0 | 0 | 69.0787 | Heating | 60.9518 | 8.5 | 60.9518 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.1904 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 62.1957 | 0 | 12.4391 | 0.1244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-22 23:01 | 9 | 22 | 23 | 265 | 6359 | 68 | 152.5143 | 0 | 0 | 152.5143 | Heating | 134.5714 | 8.5 | 134.5714 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.9143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 137.3178 | 0 | 27.4636 | 0.2746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 00:01 | 9 | 23 | 0 | 266 | 6360 | 62.06 | 270.2567 | 0 | 0 | 270.2567 | Heating | 238.4618 | 8.5 | 238.4618 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.6924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 243.3284 | 0 | 48.6657 | 0.4867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 01:01 | 9 | 23 | 1 | 266 | 6361 | 60.98 | 348.6131 | 0 | 0 | 348.6131 | Heating | 307.5998 | 8.5 | 307.5998 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.52 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 313.8773 | 0 | 62.7755 | 0.6278% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 02:01 | 9 | 23 | 2 | 266 | 6362 | 60.98 | 429.6487 | 0 | 0 | 429.6487 | Heating | 379.1018 | 8.5 | 379.1018 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.8204 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 386.8386 | 0 | 77.3677 | 0.7737% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 03:01 | 9 | 23 | 3 | 266 | 6363 | 55.04 | 507.0813 | 0 | 0 | 507.0813 | Heating | 447.4247 | 8.5 | 447.4247 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 89.4849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 456.5558 | 0 | 91.3112 | 0.9131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 04:01 | 9 | 23 | 4 | 266 | 6364 | 53.96 | 521.9022 | 0 | 0 | 521.9022 | Heating | 460.5019 | 8.5 | 460.5019 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.1004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 469.8999 | 0 | 93.98 | 0.9398% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 05:01 | 9 | 23 | 5 | 266 | 6365 | 53.96 | 514.6693 | 0 | 0 | 514.6693 | Heating | 454.12 | 8.5 | 454.12 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 90.824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 463.3878 | 0 | 92.6776 | 0.9268% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 06:01 | 9 | 23 | 6 | 266 | 6366 | 51.08 | 5751.002 | 20.6965 | 20.6965 | 5730.3055 | Heating | 5056.1519 | 8.5 | 5056.1519 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1011.2304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5159.3387 | 0 | 1031.8677 | 10.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 07:01 | 9 | 23 | 7 | 266 | 6367 | 55.94 | 3962.0998 | 0 | 0 | 3962.0998 | Heating | 3495.9704 | 8.5 | 3495.9704 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 699.1941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3567.3167 | 0 | 713.4633 | 7.135% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 08:01 | 9 | 23 | 8 | 266 | 6368 | 55.94 | 2394.8143 | 1.0688 | 1.0688 | 2393.7455 | Heating | 2112.1284 | 8.5 | 2112.1284 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 422.4257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2155.233 | 0 | 431.0466 | 4.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 09:01 | 9 | 23 | 9 | 266 | 6369 | 62.96 | 817.272 | 31.3411 | 31.3411 | 785.9309 | Heating | 693.4684 | 8.5 | 693.4684 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.6937 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 707.6208 | 0 | 141.5242 | 1.415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 10:01 | 9 | 23 | 10 | 266 | 6370 | 66.02 | 152.3836 | 87.0279 | 87.0279 | 65.3557 | Heating | 57.6668 | 8.5 | 57.6668 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.5334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 58.8437 | 0 | 11.7687 | 0.1177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 11:01 | 9 | 23 | 11 | 266 | 6371 | 66.02 | 85.7868 | 147.5332 | 147.5332 | -61.7464 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 180.3183 | 180.3183 | 0 | 8.5 | 0 | 30.0531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 176.712 | 35.3424 | 0.3534% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 12:01 | 9 | 23 | 12 | 266 | 6372 | 69.08 | 105.0991 | 186.5044 | 186.5044 | -81.4053 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 227.9498 | 227.9498 | 0 | 8.5 | 0 | 37.9916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 223.3908 | 44.6782 | 0.4468% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 13:01 | 9 | 23 | 13 | 266 | 6373 | 71.96 | 142.7965 | 288.1883 | 288.1883 | -145.3918 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 352.2302 | 352.2302 | 0 | 8.5 | 0 | 58.705 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 345.1856 | 69.0371 | 0.6904% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 14:01 | 9 | 23 | 14 | 266 | 6374 | 71.96 | 109.0771 | 474.1112 | 474.1112 | -365.0342 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 579.4693 | 579.4693 | 0 | 8.5 | 0 | 96.5782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 567.8799 | 113.576 | 1.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 15:01 | 9 | 23 | 15 | 266 | 6375 | 75.02 | 98.7741 | 357.1572 | 357.1572 | -258.3831 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 436.5255 | 436.5255 | 0 | 8.5 | 0 | 72.7543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 427.795 | 85.559 | 0.8556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 16:01 | 9 | 23 | 16 | 266 | 6376 | 75.02 | 92.9102 | 318.1735 | 318.1735 | -225.2633 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 388.8787 | 388.8787 | 0 | 8.5 | 0 | 64.8131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 381.1012 | 76.2202 | 0.7622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 17:01 | 9 | 23 | 17 | 266 | 6377 | 75.02 | 63.8516 | 251.4661 | 251.4661 | -187.6145 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 307.3474 | 307.3474 | 0 | 8.5 | 0 | 51.2246 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 301.2005 | 60.2401 | 0.6024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 18:01 | 9 | 23 | 18 | 266 | 6378 | 66.02 | 76.795 | 121.0265 | 121.0265 | -44.2315 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 147.9213 | 147.9213 | 0 | 8.5 | 0 | 24.6535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 144.9628 | 28.9926 | 0.2899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 19:01 | 9 | 23 | 19 | 266 | 6379 | 64.94 | 285.2868 | 69.0627 | 69.0627 | 216.2241 | Heating | 190.786 | 8.5 | 190.786 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.1572 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 194.6796 | 0 | 38.9359 | 0.3894% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 20:01 | 9 | 23 | 20 | 266 | 6380 | 64.94 | 874.9267 | 5.0377 | 5.0377 | 869.889 | Heating | 767.5491 | 8.5 | 767.5491 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 153.5098 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 783.2134 | 0 | 156.6427 | 1.566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 21:01 | 9 | 23 | 21 | 266 | 6381 | 64.04 | 263.2483 | 0 | 0 | 263.2483 | Heating | 232.2779 | 8.5 | 232.2779 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 46.4556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 237.0183 | 0 | 47.4037 | 0.474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 22:01 | 9 | 23 | 22 | 266 | 6382 | 60.08 | 292.6942 | 0 | 0 | 292.6942 | Heating | 258.2596 | 8.5 | 258.2596 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.6519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 263.5302 | 0 | 52.706 | 0.5271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-23 23:01 | 9 | 23 | 23 | 266 | 6383 | 60.08 | 365.4361 | 0 | 0 | 365.4361 | Heating | 322.4436 | 8.5 | 322.4436 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.4887 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 329.0241 | 0 | 65.8048 | 0.658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 00:01 | 9 | 24 | 0 | 267 | 6384 | 57.92 | 424.0997 | 0 | 0 | 424.0997 | Heating | 374.2057 | 8.5 | 374.2057 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.8411 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 381.8425 | 0 | 76.3685 | 0.7637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 01:01 | 9 | 24 | 1 | 267 | 6385 | 57.02 | 434.3451 | 0 | 0 | 434.3451 | Heating | 383.2457 | 8.5 | 383.2457 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.6491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 391.067 | 0 | 78.2134 | 0.7821% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 02:01 | 9 | 24 | 2 | 267 | 6386 | 57.02 | 428.9395 | 0 | 0 | 428.9395 | Heating | 378.476 | 8.5 | 378.476 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.6952 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 386.2 | 0 | 77.24 | 0.7724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 03:01 | 9 | 24 | 3 | 267 | 6387 | 53.06 | 430.2166 | 0 | 0 | 430.2166 | Heating | 379.6029 | 8.5 | 379.6029 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.9206 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 387.3499 | 0 | 77.47 | 0.7747% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 04:01 | 9 | 24 | 4 | 267 | 6388 | 51.08 | 448.6464 | 0 | 0 | 448.6464 | Heating | 395.8644 | 8.5 | 395.8644 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.1729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 403.9433 | 0 | 80.7887 | 0.8079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 05:01 | 9 | 24 | 5 | 267 | 6389 | 51.08 | 441.4639 | 0 | 0 | 441.4639 | Heating | 389.527 | 8.5 | 389.527 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.9054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 397.4765 | 0 | 79.4953 | 0.795% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 06:01 | 9 | 24 | 6 | 267 | 6390 | 50 | 4716.1386 | 46.4427 | 46.4427 | 4669.696 | Heating | 4120.32 | 8.5 | 4120.32 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 824.064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4204.4081 | 0 | 840.8816 | 8.409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 07:01 | 9 | 24 | 7 | 267 | 6391 | 53.06 | 3301.9613 | 0 | 0 | 3301.9613 | Heating | 2913.4952 | 8.5 | 2913.4952 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 582.699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2972.9543 | 0 | 594.5909 | 5.946% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 08:01 | 9 | 24 | 8 | 267 | 6392 | 53.06 | 2502.3195 | 0 | 0 | 2502.3195 | Heating | 2207.929 | 8.5 | 2207.929 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 441.5858 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2252.9888 | 0 | 450.5978 | 4.506% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 09:01 | 9 | 24 | 9 | 267 | 6393 | 62.96 | 1588.7718 | 2.8694 | 2.8694 | 1585.9024 | Heating | 1399.3256 | 8.5 | 1399.3256 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.8651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1427.8833 | 0 | 285.5767 | 2.856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 10:01 | 9 | 24 | 10 | 267 | 6394 | 66.02 | 1195.4358 | 7.2128 | 7.2128 | 1188.223 | Heating | 1048.4321 | 8.5 | 1048.4321 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.6864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1069.8287 | 0 | 213.9657 | 2.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 11:01 | 9 | 24 | 11 | 267 | 6395 | 66.02 | 803.5649 | 31.1205 | 31.1205 | 772.4444 | Heating | 681.5686 | 8.5 | 681.5686 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.3137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 695.4781 | 0 | 139.0956 | 1.391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 12:01 | 9 | 24 | 12 | 267 | 6396 | 73.94 | 529.3372 | 54.959 | 54.959 | 474.3781 | Heating | 418.5689 | 8.5 | 418.5689 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.7138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 427.1112 | 0 | 85.4222 | 0.8542% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 13:01 | 9 | 24 | 13 | 267 | 6397 | 77 | 252.6841 | 294.1734 | 294.1734 | -41.4893 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 359.5453 | 359.5453 | 0 | 8.5 | 0 | 59.9242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 352.3544 | 70.4709 | 0.7047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 14:01 | 9 | 24 | 14 | 267 | 6398 | 77 | 184.0616 | 528.4623 | 528.4623 | -344.4007 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 645.8983 | 645.8983 | 0 | 8.5 | 0 | 107.6497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 632.9804 | 126.5961 | 1.266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 15:01 | 9 | 24 | 15 | 267 | 6399 | 77 | 135.714 | 474.8889 | 474.8889 | -339.1748 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 580.4197 | 580.4197 | 0 | 8.5 | 0 | 96.7366 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 568.8113 | 113.7623 | 1.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 16:01 | 9 | 24 | 16 | 267 | 6400 | 77 | 61.3394 | 488.989 | 488.989 | -427.6496 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 597.6532 | 597.6532 | 0 | 8.5 | 0 | 99.6089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 585.7002 | 117.14 | 1.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 17:01 | 9 | 24 | 17 | 267 | 6401 | 77 | 22.2622 | 456.687 | 456.687 | -434.4248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 558.173 | 558.173 | 0 | 8.5 | 0 | 93.0288 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 547.0096 | 109.4019 | 1.094% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 18:01 | 9 | 24 | 18 | 267 | 6402 | 69.98 | 90.3634 | 198.7221 | 198.7221 | -108.3587 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 242.8826 | 242.8826 | 0 | 8.5 | 0 | 40.4804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 238.0249 | 47.605 | 0.476% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 19:01 | 9 | 24 | 19 | 267 | 6403 | 66.02 | 757.1865 | 106.9564 | 106.9564 | 650.2301 | Heating | 573.7325 | 8.5 | 573.7325 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.7465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 585.4413 | 0 | 117.0883 | 1.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 20:01 | 9 | 24 | 20 | 267 | 6404 | 66.02 | 1436.1507 | 21.6259 | 21.6259 | 1414.5248 | Heating | 1248.1102 | 8.5 | 1248.1102 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.622 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1273.5818 | 0 | 254.7164 | 2.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 21:01 | 9 | 24 | 21 | 267 | 6405 | 60.98 | 322.4646 | 6.0558 | 6.0558 | 316.4088 | Heating | 279.1843 | 8.5 | 279.1843 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.8369 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 284.8819 | 0 | 56.9764 | 0.5698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 22:01 | 9 | 24 | 22 | 267 | 6406 | 60.08 | 358.3598 | 0 | 0 | 358.3598 | Heating | 316.1999 | 8.5 | 316.1999 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.24 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 322.6529 | 0 | 64.5306 | 0.6453% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-24 23:01 | 9 | 24 | 23 | 267 | 6407 | 60.08 | 465.7742 | 0 | 0 | 465.7742 | Heating | 410.9773 | 8.5 | 410.9773 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.1955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 419.3645 | 0 | 83.8729 | 0.8387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 00:01 | 9 | 25 | 0 | 268 | 6408 | 55.94 | 502.5168 | 0 | 0 | 502.5168 | Heating | 443.3972 | 8.5 | 443.3972 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.6794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 452.4461 | 0 | 90.4892 | 0.9049% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 01:01 | 9 | 25 | 1 | 268 | 6409 | 55.94 | 487.715 | 0 | 0 | 487.715 | Heating | 430.3368 | 8.5 | 430.3368 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 86.0674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 439.1192 | 0 | 87.8238 | 0.8782% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 02:01 | 9 | 25 | 2 | 268 | 6410 | 55.94 | 508.3308 | 0 | 0 | 508.3308 | Heating | 448.5272 | 8.5 | 448.5272 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 89.7054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 457.6808 | 0 | 91.5362 | 0.9154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 03:01 | 9 | 25 | 3 | 268 | 6411 | 57.92 | 542.6933 | 0 | 0 | 542.6933 | Heating | 478.847 | 8.5 | 478.847 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.7694 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 488.6194 | 0 | 97.7239 | 0.9772% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 04:01 | 9 | 25 | 4 | 268 | 6412 | 55.04 | 574.1289 | 0 | 0 | 574.1289 | Heating | 506.5843 | 8.5 | 506.5843 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.3169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 516.9228 | 0 | 103.3846 | 1.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 05:01 | 9 | 25 | 5 | 268 | 6413 | 55.04 | 586.0411 | 0 | 0 | 586.0411 | Heating | 517.0951 | 8.5 | 517.0951 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 103.419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 527.6481 | 0 | 105.5296 | 1.055% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 06:01 | 9 | 25 | 6 | 268 | 6414 | 53.06 | 5786.5569 | 15.4881 | 15.4881 | 5771.0688 | Heating | 5092.1195 | 8.5 | 5092.1195 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1018.4239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5196.0403 | 0 | 1039.2081 | 10.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 07:01 | 9 | 25 | 7 | 268 | 6415 | 57.02 | 3871.7684 | 0 | 0 | 3871.7684 | Heating | 3416.2662 | 8.5 | 3416.2662 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 683.2532 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3485.9859 | 0 | 697.1972 | 6.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 08:01 | 9 | 25 | 8 | 268 | 6416 | 57.02 | 2734.1525 | 0 | 0 | 2734.1525 | Heating | 2412.4875 | 8.5 | 2412.4875 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 482.4975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2461.722 | 0 | 492.3444 | 4.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 09:01 | 9 | 25 | 9 | 268 | 6417 | 64.94 | 1468.5847 | 16.3254 | 16.3254 | 1452.2593 | Heating | 1281.4053 | 8.5 | 1281.4053 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 256.2811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1307.5564 | 0 | 261.5113 | 2.615% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 10:01 | 9 | 25 | 10 | 268 | 6418 | 68 | 529.6529 | 130.2921 | 130.2921 | 399.3608 | Heating | 352.3772 | 8.5 | 352.3772 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.4754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 359.5686 | 0 | 71.9137 | 0.7191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 11:01 | 9 | 25 | 11 | 268 | 6419 | 68 | 139.3305 | 405.7387 | 405.7387 | -266.4082 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 495.9028 | 495.9028 | 0 | 8.5 | 0 | 82.6505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 485.9848 | 97.197 | 0.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 12:01 | 9 | 25 | 12 | 268 | 6420 | 75.92 | 47.7635 | 830.5436 | 830.5436 | -782.7801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1015.1088 | 1015.1088 | 0 | 8.5 | 0 | 169.1848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 994.8067 | 198.9613 | 1.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 13:01 | 9 | 25 | 13 | 268 | 6421 | 78.98 | 12.2059 | 1709.4895 | 1709.4895 | -1697.2837 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2089.3761 | 2089.3761 | 0 | 8.5 | 0 | 348.2294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2047.5886 | 409.5177 | 4.095% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 14:01 | 9 | 25 | 14 | 268 | 6422 | 78.98 | 5.8105 | 2258.9629 | 2258.9629 | -2253.1525 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2760.9547 | 2760.9547 | 0 | 8.5 | 0 | 460.1591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2705.7356 | 541.1471 | 5.411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 15:01 | 9 | 25 | 15 | 268 | 6423 | 82.04 | 1.1371 | 2827.5203 | 2827.5203 | -2826.3833 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3455.8582 | 3455.8582 | 0 | 8.5 | 0 | 575.9764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3386.741 | 677.3482 | 6.773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 16:01 | 9 | 25 | 16 | 268 | 6424 | 82.04 | 0 | 2640.8026 | 2640.8026 | -2640.8026 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3227.6476 | 3227.6476 | 0 | 8.5 | 0 | 537.9413 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3163.0946 | 632.6189 | 6.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 17:01 | 9 | 25 | 17 | 268 | 6425 | 80.96 | 0.089966 | 1806.2207 | 1806.2207 | -1806.1307 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2207.603 | 2207.603 | 0 | 8.5 | 0 | 367.9338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2163.451 | 432.6902 | 4.327% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 18:01 | 9 | 25 | 18 | 268 | 6426 | 80.06 | 0.82484 | 391.5813 | 391.5813 | -390.7565 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 478.5994 | 478.5994 | 0 | 8.5 | 0 | 79.7666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 469.0274 | 93.8055 | 0.9381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 19:01 | 9 | 25 | 19 | 268 | 6427 | 78.08 | 4.4778 | 285.4466 | 285.4466 | -280.9688 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 348.8792 | 348.8792 | 0 | 8.5 | 0 | 58.1465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 341.9016 | 68.3803 | 0.6838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 20:01 | 9 | 25 | 20 | 268 | 6428 | 78.08 | 10.3253 | 175.1193 | 175.1193 | -164.7941 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 214.0347 | 214.0347 | 0 | 8.5 | 0 | 35.6725 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 209.7541 | 41.9508 | 0.4195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 21:01 | 9 | 25 | 21 | 268 | 6429 | 75.92 | 18.5609 | 134.0667 | 134.0667 | -115.5058 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 163.8592 | 163.8592 | 0 | 8.5 | 0 | 27.3099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 160.5821 | 32.1164 | 0.3212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 22:01 | 9 | 25 | 22 | 268 | 6430 | 75.02 | 46.7664 | 0 | 0 | 46.7664 | Heating | 41.2645 | 8.5 | 41.2645 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.2529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.1066 | 0 | 8.4213 | 0.08421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-25 23:01 | 9 | 25 | 23 | 268 | 6431 | 75.02 | 94.3319 | 0 | 0 | 94.3319 | Heating | 83.234 | 8.5 | 83.234 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.6468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 84.9327 | 0 | 16.9865 | 0.1699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 00:01 | 9 | 26 | 0 | 269 | 6432 | 73.94 | 117.5836 | 0 | 0 | 117.5836 | Heating | 103.7502 | 8.5 | 103.7502 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.75 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 105.8676 | 0 | 21.1735 | 0.2117% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 01:01 | 9 | 26 | 1 | 269 | 6433 | 73.04 | 132.1597 | 0 | 0 | 132.1597 | Heating | 116.6115 | 8.5 | 116.6115 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.3223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 118.9913 | 0 | 23.7983 | 0.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 02:01 | 9 | 26 | 2 | 269 | 6434 | 73.04 | 167.0378 | 0 | 0 | 167.0378 | Heating | 147.3863 | 8.5 | 147.3863 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.4773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 150.3942 | 0 | 30.0788 | 0.3008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 03:01 | 9 | 26 | 3 | 269 | 6435 | 71.06 | 191.5964 | 0 | 0 | 191.5964 | Heating | 169.0556 | 8.5 | 169.0556 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.8111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 172.5057 | 0 | 34.5011 | 0.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 04:01 | 9 | 26 | 4 | 269 | 6436 | 71.06 | 203.2912 | 0 | 0 | 203.2912 | Heating | 179.3746 | 8.5 | 179.3746 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.8749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 183.0353 | 0 | 36.6071 | 0.3661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 05:01 | 9 | 26 | 5 | 269 | 6437 | 71.06 | 215.5641 | 0 | 0 | 215.5641 | Heating | 190.2036 | 8.5 | 190.2036 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.0407 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 194.0853 | 0 | 38.8171 | 0.3882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 06:01 | 9 | 26 | 6 | 269 | 6438 | 69.08 | 2943.4211 | 81.1224 | 81.1224 | 2862.2988 | Heating | 2525.5577 | 8.5 | 2525.5577 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 505.1115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2577.0997 | 0 | 515.4199 | 5.154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 07:01 | 9 | 26 | 7 | 269 | 6439 | 69.98 | 2022.6358 | 0 | 0 | 2022.6358 | Heating | 1784.6787 | 8.5 | 1784.6787 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 356.9357 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1821.1007 | 0 | 364.2201 | 3.642% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 08:01 | 9 | 26 | 8 | 269 | 6440 | 69.98 | 1229.3555 | 79.6538 | 79.6538 | 1149.7017 | Heating | 1014.4427 | 8.5 | 1014.4427 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.8885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1035.1456 | 0 | 207.0291 | 2.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 09:01 | 9 | 26 | 9 | 269 | 6441 | 75.02 | 172.4469 | 325.4963 | 325.4963 | -153.0494 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 397.8289 | 397.8289 | 0 | 8.5 | 0 | 66.3048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 389.8723 | 77.9745 | 0.7797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 10:01 | 9 | 26 | 10 | 269 | 6442 | 77 | 74.9332 | 507.7751 | 507.7751 | -432.8419 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 620.614 | 620.614 | 0 | 8.5 | 0 | 103.4357 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 608.2017 | 121.6403 | 1.216% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 11:01 | 9 | 26 | 11 | 269 | 6443 | 77 | 85.8054 | 644.4638 | 644.4638 | -558.6584 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 787.678 | 787.678 | 0 | 8.5 | 0 | 131.2797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 771.9245 | 154.3849 | 1.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 12:01 | 9 | 26 | 12 | 269 | 6444 | 84.92 | 54.2786 | 944.3878 | 944.3878 | -890.1092 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1154.2518 | 1154.2518 | 0 | 8.5 | 0 | 192.3753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1131.1668 | 226.2334 | 2.262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 13:01 | 9 | 26 | 13 | 269 | 6445 | 86 | 13.2162 | 1724.5142 | 1724.5142 | -1711.298 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2107.7396 | 2107.7396 | 0 | 8.5 | 0 | 351.2899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2065.5848 | 413.117 | 4.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 14:01 | 9 | 26 | 14 | 269 | 6446 | 86 | 1.5537 | 2908.1041 | 2908.1041 | -2906.5504 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3554.3494 | 3554.3494 | 0 | 8.5 | 0 | 592.3916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3483.2624 | 696.6525 | 6.967% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 15:01 | 9 | 26 | 15 | 269 | 6447 | 86 | 2.8841 | 2184.9167 | 2184.9167 | -2182.0326 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2670.4537 | 2670.4537 | 0 | 8.5 | 0 | 445.0756 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2617.0446 | 523.4089 | 5.234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 16:01 | 9 | 26 | 16 | 269 | 6448 | 87.98 | 3.2763 | 1753.5429 | 1753.5429 | -1750.2666 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2143.2191 | 2143.2191 | 0 | 8.5 | 0 | 357.2032 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2100.3548 | 420.071 | 4.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 17:01 | 9 | 26 | 17 | 269 | 6449 | 87.98 | 1.8006 | 1217.7802 | 1217.7802 | -1215.9796 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1488.398 | 1488.398 | 0 | 8.5 | 0 | 248.0663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1458.63 | 291.726 | 2.917% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 18:01 | 9 | 26 | 18 | 269 | 6450 | 78.08 | 1.884 | 321.3785 | 321.3785 | -319.4944 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 392.7959 | 392.7959 | 0 | 8.5 | 0 | 65.466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 384.94 | 76.988 | 0.7699% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 19:01 | 9 | 26 | 19 | 269 | 6451 | 77 | 5.4682 | 283.0216 | 283.0216 | -277.5534 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 345.9153 | 345.9153 | 0 | 8.5 | 0 | 57.6526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 338.997 | 67.7994 | 0.678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 20:01 | 9 | 26 | 20 | 269 | 6452 | 77 | 14.2452 | 167.6338 | 167.6338 | -153.3886 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 204.8858 | 204.8858 | 0 | 8.5 | 0 | 34.1476 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 200.7881 | 40.1576 | 0.4016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 21:01 | 9 | 26 | 21 | 269 | 6453 | 71.96 | 47.7205 | 122.7931 | 122.7931 | -75.0726 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 150.0804 | 150.0804 | 0 | 8.5 | 0 | 25.0134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 147.0788 | 29.4158 | 0.2942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 22:01 | 9 | 26 | 22 | 269 | 6454 | 71.06 | 92.5096 | 0 | 0 | 92.5096 | Heating | 81.6261 | 8.5 | 81.6261 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.3252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.2919 | 0 | 16.6584 | 0.1666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-26 23:01 | 9 | 26 | 23 | 269 | 6455 | 71.06 | 157.2916 | 0 | 0 | 157.2916 | Heating | 138.7867 | 8.5 | 138.7867 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.7573 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 141.6191 | 0 | 28.3238 | 0.2832% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 00:01 | 9 | 27 | 0 | 270 | 6456 | 69.08 | 218.0181 | 0 | 0 | 218.0181 | Heating | 192.3689 | 8.5 | 192.3689 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.4738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 196.2948 | 0 | 39.259 | 0.3926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 01:01 | 9 | 27 | 1 | 270 | 6457 | 68 | 270.6024 | 0 | 0 | 270.6024 | Heating | 238.7669 | 8.5 | 238.7669 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.7534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 243.6396 | 0 | 48.7279 | 0.4873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 02:01 | 9 | 27 | 2 | 270 | 6458 | 68 | 368.0407 | 0 | 0 | 368.0407 | Heating | 324.7418 | 8.5 | 324.7418 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.9484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 331.3692 | 0 | 66.2738 | 0.6627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 03:01 | 9 | 27 | 3 | 270 | 6459 | 69.8 | 407.852 | 0 | 0 | 407.852 | Heating | 359.8694 | 8.5 | 359.8694 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.9739 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 367.2137 | 0 | 73.4427 | 0.7344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 04:01 | 9 | 27 | 4 | 270 | 6460 | 68 | 409.1872 | 0 | 0 | 409.1872 | Heating | 361.0475 | 8.5 | 361.0475 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.2095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 368.4158 | 0 | 73.6832 | 0.7368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 05:01 | 9 | 27 | 5 | 270 | 6461 | 68 | 425.1926 | 0 | 0 | 425.1926 | Heating | 375.1699 | 8.5 | 375.1699 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 382.8264 | 0 | 76.5653 | 0.7657% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 06:01 | 9 | 27 | 6 | 270 | 6462 | 66.92 | 4583.686 | 51.9418 | 51.9418 | 4531.7442 | Heating | 3998.5978 | 8.5 | 3998.5978 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 799.7196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4080.2019 | 0 | 816.0404 | 8.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 07:01 | 9 | 27 | 7 | 270 | 6463 | 68 | 3175.0209 | 0 | 0 | 3175.0209 | Heating | 2801.489 | 8.5 | 2801.489 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 560.2978 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2858.6622 | 0 | 571.7324 | 5.717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 08:01 | 9 | 27 | 8 | 270 | 6464 | 68 | 2182.8296 | 28.5631 | 28.5631 | 2154.2665 | Heating | 1900.8234 | 8.5 | 1900.8234 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.1647 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1939.6157 | 0 | 387.9231 | 3.879% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 09:01 | 9 | 27 | 9 | 270 | 6465 | 73.04 | 873.8935 | 294.617 | 294.617 | 579.2764 | Heating | 511.1263 | 8.5 | 511.1263 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.2253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 521.5574 | 0 | 104.3115 | 1.043% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 10:01 | 9 | 27 | 10 | 270 | 6466 | 71.06 | 97.6358 | 856.0796 | 856.0796 | -758.4438 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1046.3195 | 1046.3195 | 0 | 8.5 | 0 | 174.3866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1025.3931 | 205.0786 | 2.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 11:01 | 9 | 27 | 11 | 270 | 6467 | 71.06 | 13.172 | 1652.7474 | 1652.7474 | -1639.5754 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2020.0246 | 2020.0246 | 0 | 8.5 | 0 | 336.6708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1979.6241 | 395.9248 | 3.959% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 12:01 | 9 | 27 | 12 | 270 | 6468 | 78.08 | 1.1119 | 3941.2486 | 3941.2486 | -3940.1367 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4817.0816 | 4817.0816 | 0 | 8.5 | 0 | 802.8469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4720.74 | 944.148 | 9.441% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 13:01 | 9 | 27 | 13 | 270 | 6469 | 78.98 | 0 | 5708.6526 | 5708.6526 | -5708.6526 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6977.242 | 6977.242 | 0 | 8.5 | 0 | 1162.8737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6837.6972 | 1367.5394 | 13.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 14:01 | 9 | 27 | 14 | 270 | 6470 | 78.98 | 0 | 6795.0903 | 6795.0903 | -6795.0903 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8305.1103 | 8305.1103 | 0 | 8.5 | 0 | 1384.1851 | 30% | 1 | 55.37% | 0% | 0% | 0% | 20.9232 | 0 | 0 | 0 | 20.9232 | 0 | 8139.0081 | 1627.8016 | 16.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.1977
2007-09-27 15:01 | 9 | 27 | 15 | 270 | 6471 | 82.94 | 0 | 6989.3731 | 6989.3731 | -6989.3731 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 8542.5671 | 8542.5671 | 0 | 8.5 | 0 | 1423.7612 | 30% | 1 | 56.95% | 0% | 0% | 0% | 22.3247 | 0 | 0 | 0 | 22.3247 | 0 | 8371.7158 | 1674.3432 | 16.74% | 1 | 33.49% | 0% | 0% | 3.291 | 0 | 0 | 3.291 | 25.6157
2007-09-27 16:01 | 9 | 27 | 16 | 270 | 6472 | 82.04 | 0 | 6376.5423 | 6376.5423 | -6376.5423 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7793.5517 | 7793.5517 | 0 | 8.5 | 0 | 1298.9253 | 30% | 1 | 51.96% | 0% | 0% | 0% | 18.0769 | 0 | 0 | 0 | 18.0769 | 0 | 7637.6807 | 1527.5361 | 15.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.3515
2007-09-27 17:01 | 9 | 27 | 17 | 270 | 6473 | 82.04 | 0 | 5624.6602 | 5624.6602 | -5624.6602 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6874.5846 | 6874.5846 | 0 | 8.5 | 0 | 1145.7641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6737.0929 | 1347.4186 | 13.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 18:01 | 9 | 27 | 18 | 270 | 6474 | 75.2 | 0 | 2298.0556 | 2298.0556 | -2298.0556 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2808.7347 | 2808.7347 | 0 | 8.5 | 0 | 468.1224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2752.56 | 550.512 | 5.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 19:01 | 9 | 27 | 19 | 270 | 6475 | 71.6 | 0.82867 | 507.3571 | 507.3571 | -506.5284 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 620.1031 | 620.1031 | 0 | 8.5 | 0 | 103.3505 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 607.701 | 121.5402 | 1.215% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 20:01 | 9 | 27 | 20 | 270 | 6476 | 69.98 | 7.1736 | 321.0597 | 321.0597 | -313.8861 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 392.4063 | 392.4063 | 0 | 8.5 | 0 | 65.4011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 384.5582 | 76.9116 | 0.7691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 21:01 | 9 | 27 | 21 | 270 | 6477 | 69.08 | 20.4739 | 240.5505 | 240.5505 | -220.0767 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 294.0062 | 294.0062 | 0 | 8.5 | 0 | 49.001 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 288.1261 | 57.6252 | 0.5763% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 22:01 | 9 | 27 | 22 | 270 | 6478 | 66.92 | 39.8155 | 0 | 0 | 39.8155 | Heating | 35.1313 | 8.5 | 35.1313 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.0263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.8483 | 0 | 7.1697 | 0.0717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-27 23:01 | 9 | 27 | 23 | 270 | 6479 | 66.92 | 80.664 | 0 | 0 | 80.664 | Heating | 71.1741 | 8.5 | 71.1741 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.2348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 72.6266 | 0 | 14.5253 | 0.1453% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 00:01 | 9 | 28 | 0 | 271 | 6480 | 69.8 | 129.3721 | 0 | 0 | 129.3721 | Heating | 114.1518 | 8.5 | 114.1518 | 0 | 7.1051 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.8304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.4815 | 0 | 23.2963 | 0.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 01:01 | 9 | 28 | 1 | 271 | 6481 | 64.94 | 184.8354 | 0 | 0 | 184.8354 | Heating | 163.09 | 8.5 | 163.09 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 166.4184 | 0 | 33.2837 | 0.3328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 02:01 | 9 | 28 | 2 | 271 | 6482 | 64.94 | 231.1024 | 0 | 0 | 231.1024 | Heating | 203.9138 | 8.5 | 203.9138 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.7828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 208.0753 | 0 | 41.6151 | 0.4162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 03:01 | 9 | 28 | 3 | 271 | 6483 | 64.04 | 278.4785 | 0 | 0 | 278.4785 | Heating | 245.7163 | 8.5 | 245.7163 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.1433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 250.731 | 0 | 50.1462 | 0.5015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 04:01 | 9 | 28 | 4 | 271 | 6484 | 62.96 | 317.2035 | 0 | 0 | 317.2035 | Heating | 279.8855 | 8.5 | 279.8855 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.9771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 285.5974 | 0 | 57.1195 | 0.5712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 05:01 | 9 | 28 | 5 | 271 | 6485 | 62.96 | 356.0864 | 0 | 0 | 356.0864 | Heating | 314.1939 | 8.5 | 314.1939 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.8388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 320.606 | 0 | 64.1212 | 0.6412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 06:01 | 9 | 28 | 6 | 271 | 6486 | 62.06 | 4248.0477 | 31.4636 | 31.4636 | 4216.5841 | Heating | 3720.5154 | 8.5 | 3720.5154 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 744.1031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3796.4443 | 0 | 759.2889 | 7.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 07:01 | 9 | 28 | 7 | 271 | 6487 | 60.98 | 2711.0286 | 0 | 0 | 2711.0286 | Heating | 2392.0841 | 8.5 | 2392.0841 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 478.4168 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2440.9021 | 0 | 488.1804 | 4.882% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 08:01 | 9 | 28 | 8 | 271 | 6488 | 60.98 | 2162.6257 | 3.1645 | 3.1645 | 2159.4612 | Heating | 1905.4069 | 8.5 | 1905.4069 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 381.0814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1944.2928 | 0 | 388.8586 | 3.889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 09:01 | 9 | 28 | 9 | 271 | 6489 | 64.94 | 1311.8776 | 8.4535 | 8.4535 | 1303.4241 | Heating | 1150.0801 | 8.5 | 1150.0801 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.016 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1173.5511 | 0 | 234.7102 | 2.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 10:01 | 9 | 28 | 10 | 271 | 6490 | 66.92 | 542.8441 | 27.1054 | 27.1054 | 515.7387 | Heating | 455.0635 | 8.5 | 455.0635 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.0127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 464.3505 | 0 | 92.8701 | 0.9287% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 11:01 | 9 | 28 | 11 | 271 | 6491 | 66.92 | 76.9566 | 127.5697 | 127.5697 | -50.613 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 155.9185 | 155.9185 | 0 | 8.5 | 0 | 25.9864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 152.8001 | 30.56 | 0.3056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 12:01 | 9 | 28 | 12 | 271 | 6492 | 66.92 | 5.1388 | 748.2988 | 748.2988 | -743.16 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 914.5875 | 914.5875 | 0 | 8.5 | 0 | 152.4312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 896.2957 | 179.2591 | 1.793% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 13:01 | 9 | 28 | 13 | 271 | 6493 | 66.02 | 0 | 2715.8323 | 2715.8323 | -2715.8323 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3319.3506 | 3319.3506 | 0 | 8.5 | 0 | 553.2251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3252.9636 | 650.5927 | 6.506% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 14:01 | 9 | 28 | 14 | 271 | 6494 | 66.02 | 0 | 3353.6351 | 3353.6351 | -3353.6351 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4098.8874 | 4098.8874 | 0 | 8.5 | 0 | 683.1479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4016.9096 | 803.3819 | 8.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 15:01 | 9 | 28 | 15 | 271 | 6495 | 66.02 | 0 | 3754.4249 | 3754.4249 | -3754.4249 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4588.7415 | 4588.7415 | 0 | 8.5 | 0 | 764.7903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4496.9667 | 899.3933 | 8.994% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 16:01 | 9 | 28 | 16 | 271 | 6496 | 64.4 | 0 | 3870.1526 | 3870.1526 | -3870.1526 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4730.1866 | 4730.1866 | 0 | 8.5 | 0 | 788.3644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4635.5828 | 927.1166 | 9.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 17:01 | 9 | 28 | 17 | 271 | 6497 | 59 | 0 | 3544.0338 | 3544.0338 | -3544.0338 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4331.5969 | 4331.5969 | 0 | 8.5 | 0 | 721.9328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4244.9649 | 848.993 | 8.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 18:01 | 9 | 28 | 18 | 271 | 6498 | 57.92 | 0 | 977.8193 | 977.8193 | -977.8193 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1195.1125 | 1195.1125 | 0 | 8.5 | 0 | 199.1854 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1171.2103 | 234.2421 | 2.342% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 19:01 | 9 | 28 | 19 | 271 | 6499 | 57.02 | 0 | 19.1764 | 19.1764 | -19.1764 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 23.4379 | 23.4379 | 0 | 8.5 | 0 | 3.9063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 22.9691 | 4.5938 | 0.04594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 20:01 | 9 | 28 | 20 | 271 | 6500 | 57.02 | 1.7939 | 0.4847 | 0.4847 | 1.3092 | Heating | 1.1552 | 8.5 | 1.1552 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.23104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1.1788 | 0 | 0.23575 | 0.002358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 21:01 | 9 | 28 | 21 | 271 | 6501 | 55.94 | 191.1493 | 0 | 0 | 191.1493 | Heating | 168.6611 | 8.5 | 168.6611 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.7322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 172.1032 | 0 | 34.4206 | 0.3442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 22:01 | 9 | 28 | 22 | 271 | 6502 | 55.94 | 21.0911 | 0 | 0 | 21.0911 | Heating | 18.6098 | 8.5 | 18.6098 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.9896 | 0 | 3.7979 | 0.03798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-28 23:01 | 9 | 28 | 23 | 271 | 6503 | 55.94 | 47.697 | 0 | 0 | 47.697 | Heating | 42.0856 | 8.5 | 42.0856 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.4171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.9445 | 0 | 8.5889 | 0.08589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 00:01 | 9 | 29 | 0 | 272 | 6504 | 57.92 | 86.1495 | 0 | 0 | 86.1495 | Heating | 76.0142 | 8.5 | 76.0142 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.2028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.5656 | 0 | 15.5131 | 0.1551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 01:01 | 9 | 29 | 1 | 272 | 6505 | 57.02 | 126.0995 | 0 | 0 | 126.0995 | Heating | 111.2643 | 8.5 | 111.2643 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.2529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 113.535 | 0 | 22.707 | 0.2271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 02:01 | 9 | 29 | 2 | 272 | 6506 | 57.02 | 151.7778 | 0 | 0 | 151.7778 | Heating | 133.9216 | 8.5 | 133.9216 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.7843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 136.6547 | 0 | 27.3309 | 0.2733% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 03:01 | 9 | 29 | 3 | 272 | 6507 | 57.02 | 130.0508 | 0 | 0 | 130.0508 | Heating | 114.7507 | 8.5 | 114.7507 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.9501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 117.0925 | 0 | 23.4185 | 0.2342% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 04:01 | 9 | 29 | 4 | 272 | 6508 | 55.04 | 135.2439 | 0 | 0 | 135.2439 | Heating | 119.3328 | 8.5 | 119.3328 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.8666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 121.7682 | 0 | 24.3536 | 0.2435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 05:01 | 9 | 29 | 5 | 272 | 6509 | 55.04 | 139.8801 | 0 | 0 | 139.8801 | Heating | 123.4236 | 8.5 | 123.4236 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.6847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 125.9424 | 0 | 25.1885 | 0.2519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 06:01 | 9 | 29 | 6 | 272 | 6510 | 51.98 | 130.1218 | 0 | 0 | 130.1218 | Heating | 114.8133 | 8.5 | 114.8133 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.9627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 117.1565 | 0 | 23.4313 | 0.2343% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 07:01 | 9 | 29 | 7 | 272 | 6511 | 55.04 | 130.2951 | 0 | 0 | 130.2951 | Heating | 114.9662 | 8.5 | 114.9662 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.9932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 117.3125 | 0 | 23.4625 | 0.2346% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 08:01 | 9 | 29 | 8 | 272 | 6512 | 55.04 | 2531.103 | 0 | 0 | 2531.103 | Heating | 2233.3262 | 8.5 | 2233.3262 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 446.6652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2278.9043 | 0 | 455.7809 | 4.558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 09:01 | 9 | 29 | 9 | 272 | 6513 | 60.98 | 1584.3164 | 0 | 0 | 1584.3164 | Heating | 1397.9262 | 8.5 | 1397.9262 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.5852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1426.4553 | 0 | 285.2911 | 2.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 10:01 | 9 | 29 | 10 | 272 | 6514 | 64.04 | 843.6304 | 0 | 0 | 843.6304 | Heating | 744.3798 | 8.5 | 744.3798 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 759.5712 | 0 | 151.9142 | 1.519% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 11:01 | 9 | 29 | 11 | 272 | 6515 | 64.04 | 128.7607 | 0 | 0 | 128.7607 | Heating | 113.6123 | 8.5 | 113.6123 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.7225 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 115.931 | 0 | 23.1862 | 0.2319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 12:01 | 9 | 29 | 12 | 272 | 6516 | 68 | 0.074425 | 0 | 0 | 0.074425 | Heating | 0.065669 | 8.5 | 0.065669 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.013134 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.067009 | 0 | 0.013402 | 0.000134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 13:01 | 9 | 29 | 13 | 272 | 6517 | 69.08 | 0 | 320.4925 | 320.4925 | -320.4925 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 391.7131 | 391.7131 | 0 | 8.5 | 0 | 65.2855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 383.8789 | 76.7758 | 0.7678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 14:01 | 9 | 29 | 14 | 272 | 6518 | 69.08 | 0 | 1417.0956 | 1417.0956 | -1417.0956 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1732.0058 | 1732.0058 | 0 | 8.5 | 0 | 288.6676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1697.3657 | 339.4731 | 3.395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 15:01 | 9 | 29 | 15 | 272 | 6519 | 69.98 | 0 | 1392.9238 | 1392.9238 | -1392.9238 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1702.4624 | 1702.4624 | 0 | 8.5 | 0 | 283.7437 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1668.4131 | 333.6826 | 3.337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 16:01 | 9 | 29 | 16 | 272 | 6520 | 69.08 | 0 | 1336.7519 | 1336.7519 | -1336.7519 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1633.8079 | 1633.8079 | 0 | 8.5 | 0 | 272.3013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1601.1317 | 320.2263 | 3.202% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 17:01 | 9 | 29 | 17 | 272 | 6521 | 69.08 | 0 | 502.9262 | 502.9262 | -502.9262 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 614.6876 | 614.6876 | 0 | 8.5 | 0 | 102.4479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 602.3939 | 120.4788 | 1.205% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 18:01 | 9 | 29 | 18 | 272 | 6522 | 64.04 | 0 | 159.4029 | 159.4029 | -159.4029 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 194.8257 | 194.8257 | 0 | 8.5 | 0 | 32.471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 190.9292 | 38.1858 | 0.3819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 19:01 | 9 | 29 | 19 | 272 | 6523 | 60.08 | 0 | 25.1248 | 25.1248 | -25.1248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 30.7081 | 30.7081 | 0 | 8.5 | 0 | 5.118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 30.0939 | 6.0188 | 0.06019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 20:01 | 9 | 29 | 20 | 272 | 6524 | 60.08 | 0 | 11.5069 | 11.5069 | -11.5069 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 14.064 | 14.064 | 0 | 8.5 | 0 | 2.344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 13.7827 | 2.7565 | 0.02757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 21:01 | 9 | 29 | 21 | 272 | 6525 | 53.96 | 0.9141 | 0.88188 | 0.88188 | 0.032213 | Heating | 0.028423 | 8.5 | 0.028423 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.0056847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.029003 | 0 | 0.0058007 | 5.801e-05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 22:01 | 9 | 29 | 22 | 272 | 6526 | 51.98 | 7.0397 | 0 | 0 | 7.0397 | Heating | 6.2115 | 8.5 | 6.2115 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.2423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6.3383 | 0 | 1.2677 | 0.01268% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-29 23:01 | 9 | 29 | 23 | 272 | 6527 | 51.98 | 16.8218 | 0 | 0 | 16.8218 | Heating | 14.8428 | 8.5 | 14.8428 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.9686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 15.1457 | 0 | 3.0291 | 0.03029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 00:01 | 9 | 30 | 0 | 273 | 6528 | 48.92 | 27.1079 | 0 | 0 | 27.1079 | Heating | 23.9187 | 8.5 | 23.9187 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.7837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.4069 | 0 | 4.8814 | 0.04881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 01:01 | 9 | 30 | 1 | 273 | 6529 | 48.92 | 37.9843 | 0 | 0 | 37.9843 | Heating | 33.5156 | 8.5 | 33.5156 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.7031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.1996 | 0 | 6.8399 | 0.0684% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 02:01 | 9 | 30 | 2 | 273 | 6530 | 48.92 | 49.65 | 0 | 0 | 49.65 | Heating | 43.8088 | 8.5 | 43.8088 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.7618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.7029 | 0 | 8.9406 | 0.08941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 03:01 | 9 | 30 | 3 | 273 | 6531 | 48.02 | 58.9381 | 0 | 0 | 58.9381 | Heating | 52.0042 | 8.5 | 52.0042 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.4008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 53.0655 | 0 | 10.6131 | 0.1061% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 04:01 | 9 | 30 | 4 | 273 | 6532 | 46.94 | 66.9584 | 0 | 0 | 66.9584 | Heating | 59.0809 | 8.5 | 59.0809 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.8162 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 60.2866 | 0 | 12.0573 | 0.1206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 05:01 | 9 | 30 | 5 | 273 | 6533 | 46.94 | 62.2439 | 0 | 0 | 62.2439 | Heating | 54.9211 | 8.5 | 54.9211 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.9842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 56.0419 | 0 | 11.2084 | 0.1121% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 06:01 | 9 | 30 | 6 | 273 | 6534 | 44.96 | 1743.5412 | 88.3994 | 88.3994 | 1655.1418 | Heating | 1460.4192 | 8.5 | 1460.4192 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.0838 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1490.2237 | 0 | 298.0447 | 2.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 07:01 | 9 | 30 | 7 | 273 | 6535 | 46.94 | 1126.4116 | 16.0425 | 16.0425 | 1110.369 | Heating | 979.7374 | 8.5 | 979.7374 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.9475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 999.732 | 0 | 199.9464 | 1.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 08:01 | 9 | 30 | 8 | 273 | 6536 | 46.94 | 339.5704 | 472.1773 | 472.1773 | -132.6069 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 577.1056 | 577.1056 | 0 | 8.5 | 0 | 96.1843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 565.5635 | 113.1127 | 1.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 09:01 | 9 | 30 | 9 | 273 | 6537 | 53.96 | 7.0159 | 978.0828 | 978.0828 | -971.067 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1195.4346 | 1195.4346 | 0 | 8.5 | 0 | 199.2391 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1171.5259 | 234.3052 | 2.343% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 10:01 | 9 | 30 | 10 | 273 | 6538 | 59 | 0.16603 | 1716.048 | 1716.048 | -1715.8819 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2097.392 | 2097.392 | 0 | 8.5 | 0 | 349.5653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2055.4441 | 411.0888 | 4.111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 11:01 | 9 | 30 | 11 | 273 | 6539 | 59 | 0 | 4142.0979 | 4142.0979 | -4142.0979 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5062.5641 | 5062.5641 | 0 | 8.5 | 0 | 843.7607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4961.3129 | 992.2626 | 9.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 12:01 | 9 | 30 | 12 | 273 | 6540 | 64.94 | 0 | 5640.319 | 5640.319 | -5640.319 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 6893.7233 | 6893.7233 | 0 | 8.5 | 0 | 1148.9539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 6755.8488 | 1351.1698 | 13.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 13:01 | 9 | 30 | 13 | 273 | 6541 | 64.04 | 0 | 6498.1532 | 6498.1532 | -6498.1532 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7942.1873 | 7942.1873 | 0 | 8.5 | 0 | 1323.6979 | 30% | 1 | 52.95% | 0% | 0% | 0% | 18.8797 | 0 | 0 | 0 | 18.8797 | 0 | 7783.3435 | 1556.6687 | 15.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.1543
2007-09-30 14:01 | 9 | 30 | 14 | 273 | 6542 | 64.04 | 0 | 6404.5567 | 6404.5567 | -6404.5567 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7827.7915 | 7827.7915 | 0 | 8.5 | 0 | 1304.6319 | 30% | 1 | 52.19% | 0% | 0% | 0% | 18.2601 | 0 | 0 | 0 | 18.2601 | 0 | 7671.2356 | 1534.2471 | 15.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.5347
2007-09-30 15:01 | 9 | 30 | 15 | 273 | 6543 | 66.92 | 0 | 5853.3854 | 5853.3854 | -5853.3854 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 7154.1377 | 7154.1377 | 0 | 8.5 | 0 | 1192.3563 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 7011.055 | 1402.211 | 14.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 16:01 | 9 | 30 | 16 | 273 | 6544 | 66.92 | 0 | 4615.8115 | 4615.8115 | -4615.8115 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5641.5474 | 5641.5474 | 0 | 8.5 | 0 | 940.2579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5528.7165 | 1105.7433 | 11.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 17:01 | 9 | 30 | 17 | 273 | 6545 | 66.92 | 0.86193 | 1547.3173 | 1547.3173 | -1546.4554 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1891.1656 | 1891.1656 | 0 | 8.5 | 0 | 315.1943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1853.3423 | 370.6685 | 3.707% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 18:01 | 9 | 30 | 18 | 273 | 6546 | 60.08 | 6.0725 | 320.5762 | 320.5762 | -314.5037 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 391.8153 | 391.8153 | 0 | 8.5 | 0 | 65.3026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 383.979 | 76.7958 | 0.768% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 19:01 | 9 | 30 | 19 | 273 | 6547 | 55.4 | 11.9561 | 267.5343 | 267.5343 | -255.5782 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 326.9863 | 326.9863 | 0 | 8.5 | 0 | 54.4977 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 320.4466 | 64.0893 | 0.6409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 20:01 | 9 | 30 | 20 | 273 | 6548 | 55.76 | 25.0391 | 160.1147 | 160.1147 | -135.0756 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 195.6958 | 195.6958 | 0 | 8.5 | 0 | 32.616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 191.7819 | 38.3564 | 0.3836% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 21:01 | 9 | 30 | 21 | 273 | 6549 | 55.76 | 36.4663 | 111.5883 | 111.5883 | -75.122 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 136.3857 | 136.3857 | 0 | 8.5 | 0 | 22.731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 133.658 | 26.7316 | 0.2673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 22:01 | 9 | 30 | 22 | 273 | 6550 | 56.84 | 54.3417 | 0 | 0 | 54.3417 | Heating | 47.9485 | 8.5 | 47.9485 | 0 | 5.2321 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.5897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 48.9271 | 0 | 9.7854 | 0.09785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-09-30 23:01 | 9 | 30 | 23 | 273 | 6551 | 56.84 | 50.0727 | 0 | 0 | 50.0727 | Heating | 44.1818 | 8.5 | 44.1818 | 0 | 5.2321 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.8364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 45.0834 | 0 | 9.0167 | 0.09017% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 00:01 | 10 | 1 | 0 | 274 | 6552 | 56.48 | 41.7264 | 0 | 0 | 41.7264 | Heating | 36.8174 | 8.5 | 36.8174 | 0 | 5.19 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.3635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 37.5687 | 0 | 7.5137 | 0.07514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 01:01 | 10 | 1 | 1 | 274 | 6553 | 56.3 | 26.4253 | 0 | 0 | 26.4253 | Heating | 23.3165 | 8.5 | 23.3165 | 0 | 5.1692 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.6633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.7923 | 0 | 4.7585 | 0.04758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 02:01 | 10 | 1 | 2 | 274 | 6554 | 55.76 | 12.4973 | 0 | 0 | 12.4973 | Heating | 11.027 | 8.5 | 11.027 | 0 | 5.1073 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.2054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 11.252 | 0 | 2.2504 | 0.0225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 03:01 | 10 | 1 | 3 | 274 | 6555 | 55.04 | 3.3041 | 0 | 0 | 3.3041 | Heating | 2.9154 | 8.5 | 2.9154 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.58307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2.9748 | 0 | 0.59497 | 0.00595% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 04:01 | 10 | 1 | 4 | 274 | 6556 | 54.68 | 0 | 138.8102 | 138.8102 | -138.8102 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 169.6569 | 169.6569 | 0 | 8.5 | 0 | 28.2762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 166.2638 | 33.2528 | 0.3325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 05:01 | 10 | 1 | 5 | 274 | 6557 | 54.68 | 0 | 88.9855 | 88.9855 | -88.9855 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 108.7601 | 108.7601 | 0 | 8.5 | 0 | 18.1267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 106.5849 | 21.317 | 0.2132% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 06:01 | 10 | 1 | 6 | 274 | 6558 | 55.22 | 515.4188 | 380.8602 | 380.8602 | 134.5586 | Heating | 118.7282 | 8.5 | 118.7282 | 0 | 5.0465 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.7456 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 121.1512 | 0 | 24.2302 | 0.2423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 07:01 | 10 | 1 | 7 | 274 | 6559 | 55.04 | 302.6191 | 116.6298 | 116.6298 | 185.9893 | Heating | 164.1082 | 8.5 | 164.1082 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.8216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 167.4574 | 0 | 33.4915 | 0.3349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 08:01 | 10 | 1 | 8 | 274 | 6560 | 55.04 | 13.501 | 1397.4703 | 1397.4703 | -1383.9692 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1708.0192 | 1708.0192 | 0 | 8.5 | 0 | 284.6699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1673.8588 | 334.7718 | 3.348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 09:01 | 10 | 1 | 9 | 274 | 6561 | 57.02 | 0.92987 | 2164.6724 | 2164.6724 | -2163.7425 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2645.7107 | 2645.7107 | 0 | 8.5 | 0 | 440.9518 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2592.7965 | 518.5593 | 5.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 10:01 | 10 | 1 | 10 | 274 | 6562 | 59 | 0.13162 | 2498.8477 | 2498.8477 | -2498.7161 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3054.1472 | 3054.1472 | 0 | 8.5 | 0 | 509.0245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2993.0642 | 598.6128 | 5.986% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 11:01 | 10 | 1 | 11 | 274 | 6563 | 59 | 0 | 3233.5937 | 3233.5937 | -3233.5937 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3952.1701 | 3952.1701 | 0 | 8.5 | 0 | 658.695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3873.1267 | 774.6253 | 7.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 12:01 | 10 | 1 | 12 | 274 | 6564 | 62.96 | 0 | 3877.1947 | 3877.1947 | -3877.1947 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4738.7935 | 4738.7935 | 0 | 8.5 | 0 | 789.7989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4644.0176 | 928.8035 | 9.288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 13:01 | 10 | 1 | 13 | 274 | 6565 | 62.96 | 0 | 4380.1358 | 4380.1358 | -4380.1358 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5353.4993 | 5353.4993 | 0 | 8.5 | 0 | 892.2499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5246.4293 | 1049.2859 | 10.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 14:01 | 10 | 1 | 14 | 274 | 6566 | 62.96 | 0 | 4621.1925 | 4621.1925 | -4621.1925 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5648.1242 | 5648.1242 | 0 | 8.5 | 0 | 941.354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5535.1617 | 1107.0323 | 11.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 15:01 | 10 | 1 | 15 | 274 | 6567 | 62.96 | 0 | 4721.6738 | 4721.6738 | -4721.6738 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5770.9347 | 5770.9347 | 0 | 8.5 | 0 | 961.8224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5655.516 | 1131.1032 | 11.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 16:01 | 10 | 1 | 16 | 274 | 6568 | 62.06 | 0 | 3982.8471 | 3982.8471 | -3982.8471 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 4867.9242 | 4867.9242 | 0 | 8.5 | 0 | 811.3207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 4770.5657 | 954.1131 | 9.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 17:01 | 10 | 1 | 17 | 274 | 6569 | 62.06 | 0 | 2785.3744 | 2785.3744 | -2785.3744 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3404.3464 | 3404.3464 | 0 | 8.5 | 0 | 567.3911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3336.2595 | 667.2519 | 6.673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 18:01 | 10 | 1 | 18 | 274 | 6570 | 59 | 0 | 780.7326 | 780.7326 | -780.7326 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 954.2287 | 954.2287 | 0 | 8.5 | 0 | 159.0381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 935.1441 | 187.0288 | 1.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 19:01 | 10 | 1 | 19 | 274 | 6571 | 53.96 | 0 | 418.5733 | 418.5733 | -418.5733 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 511.5896 | 511.5896 | 0 | 8.5 | 0 | 85.2649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 501.3579 | 100.2716 | 1.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 20:01 | 10 | 1 | 20 | 274 | 6572 | 53.96 | 1.3547 | 293.2044 | 293.2044 | -291.8497 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 358.361 | 358.361 | 0 | 8.5 | 0 | 59.7268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 351.1937 | 70.2387 | 0.7024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 21:01 | 10 | 1 | 21 | 274 | 6573 | 53.06 | 3.8828 | 249.2334 | 249.2334 | -245.3506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 304.6186 | 304.6186 | 0 | 8.5 | 0 | 50.7698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 298.5263 | 59.7053 | 0.5971% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 22:01 | 10 | 1 | 22 | 274 | 6574 | 53.06 | 8.8644 | 0 | 0 | 8.8644 | Heating | 7.8215 | 8.5 | 7.8215 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.5643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.9812 | 0 | 1.5962 | 0.01596% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-01 23:01 | 10 | 1 | 23 | 274 | 6575 | 51.98 | 14.3696 | 0 | 0 | 14.3696 | Heating | 12.6791 | 8.5 | 12.6791 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2.5358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 12.9378 | 0 | 2.5876 | 0.02588% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 00:01 | 10 | 2 | 0 | 275 | 6576 | 51.08 | 22.5223 | 0 | 0 | 22.5223 | Heating | 19.8726 | 8.5 | 19.8726 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.9745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.2782 | 0 | 4.0556 | 0.04056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 01:01 | 10 | 2 | 1 | 275 | 6577 | 51.08 | 30.5155 | 0 | 0 | 30.5155 | Heating | 26.9254 | 8.5 | 26.9254 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.3851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 27.4749 | 0 | 5.495 | 0.05495% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 02:01 | 10 | 2 | 2 | 275 | 6578 | 51.08 | 35.6231 | 0 | 0 | 35.6231 | Heating | 31.4321 | 8.5 | 31.4321 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.2864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 32.0736 | 0 | 6.4147 | 0.06415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 03:01 | 10 | 2 | 3 | 275 | 6579 | 50 | 41.4249 | 0 | 0 | 41.4249 | Heating | 36.5513 | 8.5 | 36.5513 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.3103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 37.2973 | 0 | 7.4595 | 0.07459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 04:01 | 10 | 2 | 4 | 275 | 6580 | 50 | 47.3664 | 0 | 0 | 47.3664 | Heating | 41.7939 | 8.5 | 41.7939 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.3588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.6468 | 0 | 8.5294 | 0.08529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 05:01 | 10 | 2 | 5 | 275 | 6581 | 50 | 48.9183 | 0 | 0 | 48.9183 | Heating | 43.1632 | 8.5 | 43.1632 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.6326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.0441 | 0 | 8.8088 | 0.08809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 06:01 | 10 | 2 | 6 | 275 | 6582 | 50 | 1625.9579 | 152.5863 | 152.5863 | 1473.3716 | Heating | 1300.0337 | 8.5 | 1300.0337 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 260.0067 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1326.565 | 0 | 265.313 | 2.653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 07:01 | 10 | 2 | 7 | 275 | 6583 | 50 | 1240.4092 | 34.3016 | 34.3016 | 1206.1076 | Heating | 1064.2126 | 8.5 | 1064.2126 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.8425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1085.9312 | 0 | 217.1862 | 2.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 08:01 | 10 | 2 | 8 | 275 | 6584 | 50 | 811.03 | 466.2177 | 466.2177 | 344.8123 | Heating | 304.2462 | 8.5 | 304.2462 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.8492 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 310.4553 | 0 | 62.0911 | 0.6209% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 09:01 | 10 | 2 | 9 | 275 | 6585 | 53.6 | 186.4756 | 798.3525 | 798.3525 | -611.8769 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 975.7641 | 975.7641 | 0 | 8.5 | 0 | 162.6274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 956.2489 | 191.2498 | 1.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 10:01 | 10 | 2 | 10 | 275 | 6586 | 53.06 | 75.0103 | 1011.7515 | 1011.7515 | -936.7412 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1236.5851 | 1236.5851 | 0 | 8.5 | 0 | 206.0975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1211.8534 | 242.3707 | 2.424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 11:01 | 10 | 2 | 11 | 275 | 6587 | 55.04 | 58.2662 | 1065.9154 | 1065.9154 | -1007.6492 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1302.7855 | 1302.7855 | 0 | 8.5 | 0 | 217.1309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1276.7297 | 255.3459 | 2.553% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 12:01 | 10 | 2 | 12 | 275 | 6588 | 57.02 | 39.3752 | 1177.4287 | 1177.4287 | -1138.0535 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1439.0796 | 1439.0796 | 0 | 8.5 | 0 | 239.8466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1410.298 | 282.0596 | 2.821% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 13:01 | 10 | 2 | 13 | 275 | 6589 | 60.08 | 32.2517 | 1271.1356 | 1271.1356 | -1238.8839 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1553.6102 | 1553.6102 | 0 | 8.5 | 0 | 258.935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1522.538 | 304.5076 | 3.045% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 14:01 | 10 | 2 | 14 | 275 | 6590 | 60.08 | 30.6455 | 1290.6233 | 1290.6233 | -1259.9778 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1577.4284 | 1577.4284 | 0 | 8.5 | 0 | 262.9047 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1545.8799 | 309.176 | 3.092% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 15:01 | 10 | 2 | 15 | 275 | 6591 | 60.98 | 22.4753 | 1150.8956 | 1150.8956 | -1128.4203 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1406.6501 | 1406.6501 | 0 | 8.5 | 0 | 234.4417 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1378.5171 | 275.7034 | 2.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 16:01 | 10 | 2 | 16 | 275 | 6592 | 59 | 10.1315 | 1220.1026 | 1220.1026 | -1209.9711 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1491.2365 | 1491.2365 | 0 | 8.5 | 0 | 248.5394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1461.4117 | 292.2823 | 2.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 17:01 | 10 | 2 | 17 | 275 | 6593 | 59 | 4.1571 | 968.2207 | 968.2207 | -964.0636 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1183.3808 | 1183.3808 | 0 | 8.5 | 0 | 197.2301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1159.7132 | 231.9426 | 2.319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 18:01 | 10 | 2 | 18 | 275 | 6594 | 59 | 3.6416 | 326.8217 | 326.8217 | -323.1801 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 399.4488 | 399.4488 | 0 | 8.5 | 0 | 66.5748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 391.4598 | 78.292 | 0.7829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 19:01 | 10 | 2 | 19 | 275 | 6595 | 57.92 | 7.6057 | 282.9197 | 282.9197 | -275.314 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 345.7907 | 345.7907 | 0 | 8.5 | 0 | 57.6318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 338.8749 | 67.775 | 0.6777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 20:01 | 10 | 2 | 20 | 275 | 6596 | 57.92 | 11.1418 | 176.3736 | 176.3736 | -165.2317 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 215.5677 | 215.5677 | 0 | 8.5 | 0 | 35.9279 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 211.2563 | 42.2513 | 0.4225% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 21:01 | 10 | 2 | 21 | 275 | 6597 | 57.02 | 16.7438 | 134.9251 | 134.9251 | -118.1813 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 164.9085 | 164.9085 | 0 | 8.5 | 0 | 27.4847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 161.6103 | 32.3221 | 0.3232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 22:01 | 10 | 2 | 22 | 275 | 6598 | 55.94 | 57.01 | 0 | 0 | 57.01 | Heating | 50.3029 | 8.5 | 50.3029 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 10.0606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 51.3295 | 0 | 10.2659 | 0.1027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-02 23:01 | 10 | 2 | 23 | 275 | 6599 | 55.94 | 104.109 | 0 | 0 | 104.109 | Heating | 91.8609 | 8.5 | 91.8609 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.3722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 93.7356 | 0 | 18.7471 | 0.1875% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 00:01 | 10 | 3 | 0 | 276 | 6600 | 57.02 | 162.1743 | 0 | 0 | 162.1743 | Heating | 143.095 | 8.5 | 143.095 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 146.0153 | 0 | 29.2031 | 0.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 01:01 | 10 | 3 | 1 | 276 | 6601 | 57.02 | 250.6731 | 0 | 0 | 250.6731 | Heating | 221.1821 | 8.5 | 221.1821 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.2364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 225.6961 | 0 | 45.1392 | 0.4514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 02:01 | 10 | 3 | 2 | 276 | 6602 | 57.02 | 307.0317 | 0 | 0 | 307.0317 | Heating | 270.9103 | 8.5 | 270.9103 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.1821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 276.4391 | 0 | 55.2878 | 0.5529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 03:01 | 10 | 3 | 3 | 276 | 6603 | 53.96 | 360.5818 | 0 | 0 | 360.5818 | Heating | 318.1604 | 8.5 | 318.1604 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.6321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 324.6535 | 0 | 64.9307 | 0.6493% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 04:01 | 10 | 3 | 4 | 276 | 6604 | 53.96 | 418.0292 | 0 | 0 | 418.0292 | Heating | 368.8493 | 8.5 | 368.8493 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.7699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 376.3768 | 0 | 75.2754 | 0.7528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 05:01 | 10 | 3 | 5 | 276 | 6605 | 53.96 | 386.1311 | 0 | 0 | 386.1311 | Heating | 340.7039 | 8.5 | 340.7039 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.1408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 347.657 | 0 | 69.5314 | 0.6953% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 06:01 | 10 | 3 | 6 | 276 | 6606 | 53.96 | 4161.2541 | 78.8288 | 78.8288 | 4082.4253 | Heating | 3602.14 | 8.5 | 3602.14 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 720.428 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3675.653 | 0 | 735.1306 | 7.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 07:01 | 10 | 3 | 7 | 276 | 6607 | 53.6 | 2822.8197 | 0 | 0 | 2822.8197 | Heating | 2490.7233 | 8.5 | 2490.7233 | 0 | 4.8707 | 0 | 0 | 0 | 0 | 8.5 | 0 | 498.1447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2541.5544 | 0 | 508.3109 | 5.083% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 08:01 | 10 | 3 | 8 | 276 | 6608 | 53.96 | 2070.2192 | 17.0867 | 17.0867 | 2053.1324 | Heating | 1811.5874 | 8.5 | 1811.5874 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.3175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1848.5586 | 0 | 369.7117 | 3.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 09:01 | 10 | 3 | 9 | 276 | 6609 | 55.04 | 1136.6038 | 97.2335 | 97.2335 | 1039.3703 | Heating | 917.0914 | 8.5 | 917.0914 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.4183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 935.8076 | 0 | 187.1615 | 1.872% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 10:01 | 10 | 3 | 10 | 276 | 6610 | 57.92 | 718.8703 | 323.9193 | 323.9193 | 394.9509 | Heating | 348.4861 | 8.5 | 348.4861 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 69.6972 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 355.5981 | 0 | 71.1196 | 0.7112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 11:01 | 10 | 3 | 11 | 276 | 6611 | 57.92 | 312.6718 | 511.9977 | 511.9977 | -199.3259 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 625.775 | 625.775 | 0 | 8.5 | 0 | 104.2958 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 613.2595 | 122.6519 | 1.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 12:01 | 10 | 3 | 12 | 276 | 6612 | 60.98 | 158.4788 | 711.7069 | 711.7069 | -553.228 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 869.8639 | 869.8639 | 0 | 8.5 | 0 | 144.9773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 852.4667 | 170.4933 | 1.705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 13:01 | 10 | 3 | 13 | 276 | 6613 | 62.06 | 121.561 | 835.9986 | 835.9986 | -714.4376 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1021.7761 | 1021.7761 | 0 | 8.5 | 0 | 170.296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1001.3406 | 200.2681 | 2.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 14:01 | 10 | 3 | 14 | 276 | 6614 | 62.06 | 126.9298 | 870.7233 | 870.7233 | -743.7935 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1064.2173 | 1064.2173 | 0 | 8.5 | 0 | 177.3696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1042.933 | 208.5866 | 2.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 15:01 | 10 | 3 | 15 | 276 | 6615 | 62.96 | 170.2413 | 507.8523 | 507.8523 | -337.611 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 620.7084 | 620.7084 | 0 | 8.5 | 0 | 103.4514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 608.2942 | 121.6588 | 1.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 16:01 | 10 | 3 | 16 | 276 | 6616 | 62.96 | 181.6573 | 282.0698 | 282.0698 | -100.4125 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 344.7519 | 344.7519 | 0 | 8.5 | 0 | 57.4587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 337.8569 | 67.5714 | 0.6757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 17:01 | 10 | 3 | 17 | 276 | 6617 | 62.96 | 171.2441 | 209.2203 | 209.2203 | -37.9762 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 255.7138 | 255.7138 | 0 | 8.5 | 0 | 42.619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 250.5995 | 50.1199 | 0.5012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 18:01 | 10 | 3 | 18 | 276 | 6618 | 60.98 | 131.7014 | 108.6075 | 108.6075 | 23.0939 | Heating | 20.377 | 8.5 | 20.377 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.0754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 20.7928 | 0 | 4.1586 | 0.04159% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 19:01 | 10 | 3 | 19 | 276 | 6619 | 62.06 | 183.4863 | 91.5561 | 91.5561 | 91.9302 | Heating | 81.1149 | 8.5 | 81.1149 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 82.7703 | 0 | 16.5541 | 0.1655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 20:01 | 10 | 3 | 20 | 276 | 6620 | 62.06 | 286.2547 | 18.3679 | 18.3679 | 267.8868 | Heating | 236.3707 | 8.5 | 236.3707 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.2741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 241.1946 | 0 | 48.2389 | 0.4824% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 21:01 | 10 | 3 | 21 | 276 | 6621 | 60.98 | 93.2242 | 20.7581 | 20.7581 | 72.4661 | Heating | 63.9407 | 8.5 | 63.9407 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 12.7881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 65.2456 | 0 | 13.0491 | 0.1305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 22:01 | 10 | 3 | 22 | 276 | 6622 | 60.98 | 93.081 | 0 | 0 | 93.081 | Heating | 82.1303 | 8.5 | 82.1303 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.4261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.8064 | 0 | 16.7613 | 0.1676% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-03 23:01 | 10 | 3 | 23 | 276 | 6623 | 60.08 | 93.9366 | 0 | 0 | 93.9366 | Heating | 82.8852 | 8.5 | 82.8852 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 84.5768 | 0 | 16.9154 | 0.1692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 00:01 | 10 | 4 | 0 | 277 | 6624 | 60.08 | 92.0978 | 0 | 0 | 92.0978 | Heating | 81.2628 | 8.5 | 81.2628 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.2526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 82.9212 | 0 | 16.5842 | 0.1658% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 01:01 | 10 | 4 | 1 | 277 | 6625 | 59 | 89.3023 | 0 | 0 | 89.3023 | Heating | 78.7961 | 8.5 | 78.7961 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.7592 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 80.4042 | 0 | 16.0808 | 0.1608% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 02:01 | 10 | 4 | 2 | 277 | 6626 | 59 | 92.9497 | 0 | 0 | 92.9497 | Heating | 82.0145 | 8.5 | 82.0145 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.4029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.6882 | 0 | 16.7376 | 0.1674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 03:01 | 10 | 4 | 3 | 277 | 6627 | 59 | 95.3352 | 0 | 0 | 95.3352 | Heating | 84.1193 | 8.5 | 84.1193 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.8239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 85.836 | 0 | 17.1672 | 0.1717% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 04:01 | 10 | 4 | 4 | 277 | 6628 | 59 | 106.955 | 0 | 0 | 106.955 | Heating | 94.3721 | 8.5 | 94.3721 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.8744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 96.298 | 0 | 19.2596 | 0.1926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 05:01 | 10 | 4 | 5 | 277 | 6629 | 59 | 131.3607 | 0 | 0 | 131.3607 | Heating | 115.9065 | 8.5 | 115.9065 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.1813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 118.272 | 0 | 23.6544 | 0.2365% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 06:01 | 10 | 4 | 6 | 277 | 6630 | 57.2 | 1747.5849 | 86.7298 | 86.7298 | 1660.8551 | Heating | 1465.4604 | 8.5 | 1465.4604 | 0 | 5.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 293.0921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1495.3678 | 0 | 299.0736 | 2.991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 07:01 | 10 | 4 | 7 | 277 | 6631 | 59 | 1383.6733 | 0.18521 | 0.18521 | 1383.4881 | Heating | 1220.7248 | 8.5 | 1220.7248 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 244.145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1245.6375 | 0 | 249.1275 | 2.491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 08:01 | 10 | 4 | 8 | 277 | 6632 | 59 | 541.603 | 582.6238 | 582.6238 | -41.0207 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 712.0957 | 712.0957 | 0 | 8.5 | 0 | 118.6826 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 697.8538 | 139.5708 | 1.396% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 09:01 | 10 | 4 | 9 | 277 | 6633 | 62.96 | 19.3139 | 1710.5246 | 1710.5246 | -1691.2107 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2090.6412 | 2090.6412 | 0 | 8.5 | 0 | 348.4402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2048.8284 | 409.7657 | 4.098% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 10:01 | 10 | 4 | 10 | 277 | 6634 | 66.02 | 2.9964 | 2429.679 | 2429.679 | -2426.6826 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2969.6077 | 2969.6077 | 0 | 8.5 | 0 | 494.9346 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2910.2155 | 582.0431 | 5.82% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 11:01 | 10 | 4 | 11 | 277 | 6635 | 66.02 | 0.070519 | 3197.8117 | 3197.8117 | -3197.7412 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3908.4365 | 3908.4365 | 0 | 8.5 | 0 | 651.4061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3830.2678 | 766.0536 | 7.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 12:01 | 10 | 4 | 12 | 277 | 6636 | 69.98 | 0 | 4300.3767 | 4300.3767 | -4300.3767 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5256.016 | 5256.016 | 0 | 8.5 | 0 | 876.0027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5150.8957 | 1030.1791 | 10.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 13:01 | 10 | 4 | 13 | 277 | 6637 | 69.08 | 0 | 4546.9594 | 4546.9594 | -4546.9594 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5557.3948 | 5557.3948 | 0 | 8.5 | 0 | 926.2325 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5446.2469 | 1089.2494 | 10.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 14:01 | 10 | 4 | 14 | 277 | 6638 | 69.08 | 0 | 4273.8726 | 4273.8726 | -4273.8726 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 5223.6221 | 5223.6221 | 0 | 8.5 | 0 | 870.6037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 5119.1496 | 1023.8299 | 10.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 15:01 | 10 | 4 | 15 | 277 | 6639 | 71.96 | 0 | 3151.0974 | 3151.0974 | -3151.0974 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3851.3412 | 3851.3412 | 0 | 8.5 | 0 | 641.8902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3774.3144 | 754.8629 | 7.549% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 16:01 | 10 | 4 | 16 | 277 | 6640 | 71.06 | 1.9639 | 2290.3828 | 2290.3828 | -2288.4189 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2799.3568 | 2799.3568 | 0 | 8.5 | 0 | 466.5595 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2743.3696 | 548.6739 | 5.487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 17:01 | 10 | 4 | 17 | 277 | 6641 | 71.06 | 6.5638 | 941.0403 | 941.0403 | -934.4765 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1150.1604 | 1150.1604 | 0 | 8.5 | 0 | 191.6934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1127.1572 | 225.4314 | 2.254% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 18:01 | 10 | 4 | 18 | 277 | 6642 | 66.02 | 13.0644 | 310.9955 | 310.9955 | -297.9311 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 380.1057 | 380.1057 | 0 | 8.5 | 0 | 63.3509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 372.5035 | 74.5007 | 0.745% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 19:01 | 10 | 4 | 19 | 277 | 6643 | 64.04 | 27.9462 | 247.8416 | 247.8416 | -219.8954 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 302.9175 | 302.9175 | 0 | 8.5 | 0 | 50.4862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 296.8591 | 59.3718 | 0.5937% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 20:01 | 10 | 4 | 20 | 277 | 6644 | 64.04 | 87.3643 | 124.5288 | 124.5288 | -37.1645 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 152.2019 | 152.2019 | 0 | 8.5 | 0 | 25.367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 149.1579 | 29.8316 | 0.2983% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 21:01 | 10 | 4 | 21 | 277 | 6645 | 60.08 | 78.5451 | 77.7202 | 77.7202 | 0.82494 | Heating | 0.72789 | 8.5 | 0.72789 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0.14558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0.74275 | 0 | 0.14855 | 0.001485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 22:01 | 10 | 4 | 22 | 277 | 6646 | 59 | 118.8728 | 0 | 0 | 118.8728 | Heating | 104.8878 | 8.5 | 104.8878 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.9776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 107.0284 | 0 | 21.4057 | 0.2141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-04 23:01 | 10 | 4 | 23 | 277 | 6647 | 59 | 153.3956 | 0 | 0 | 153.3956 | Heating | 135.3491 | 8.5 | 135.3491 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.0698 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 138.1113 | 0 | 27.6223 | 0.2762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 00:01 | 10 | 5 | 0 | 278 | 6648 | 59 | 197.5654 | 0 | 0 | 197.5654 | Heating | 174.3224 | 8.5 | 174.3224 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.8645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 177.88 | 0 | 35.576 | 0.3558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 01:01 | 10 | 5 | 1 | 278 | 6649 | 59 | 229.0193 | 0 | 0 | 229.0193 | Heating | 202.0758 | 8.5 | 202.0758 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.4152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 206.1998 | 0 | 41.24 | 0.4124% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 02:01 | 10 | 5 | 2 | 278 | 6650 | 59 | 274.8485 | 0 | 0 | 274.8485 | Heating | 242.5134 | 8.5 | 242.5134 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.5027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 247.4626 | 0 | 49.4925 | 0.4949% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 03:01 | 10 | 5 | 3 | 278 | 6651 | 57.02 | 326.1467 | 0 | 0 | 326.1467 | Heating | 287.7765 | 8.5 | 287.7765 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.5553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 293.6494 | 0 | 58.7299 | 0.5873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 04:01 | 10 | 5 | 4 | 278 | 6652 | 57.02 | 337.1714 | 0 | 0 | 337.1714 | Heating | 297.5042 | 8.5 | 297.5042 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.5008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 303.5757 | 0 | 60.7151 | 0.6072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 05:01 | 10 | 5 | 5 | 278 | 6653 | 57.02 | 329.6804 | 0 | 0 | 329.6804 | Heating | 290.8945 | 8.5 | 290.8945 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.1789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 296.8311 | 0 | 59.3662 | 0.5937% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 06:01 | 10 | 5 | 6 | 278 | 6654 | 57.02 | 3881.9198 | 59.3226 | 59.3226 | 3822.5973 | Heating | 3372.88 | 8.5 | 3372.88 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 674.576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3441.7142 | 0 | 688.3428 | 6.883% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 07:01 | 10 | 5 | 7 | 278 | 6655 | 57.92 | 2912.833 | 0 | 0 | 2912.833 | Heating | 2570.1468 | 8.5 | 2570.1468 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 514.0294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2622.5988 | 0 | 524.5198 | 5.245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 08:01 | 10 | 5 | 8 | 278 | 6656 | 57.92 | 2420.7718 | 0 | 0 | 2420.7718 | Heating | 2135.9752 | 8.5 | 2135.9752 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.195 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2179.5665 | 0 | 435.9133 | 4.359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 09:01 | 10 | 5 | 9 | 278 | 6657 | 62.06 | 1497.9457 | 0 | 0 | 1497.9457 | Heating | 1321.7168 | 8.5 | 1321.7168 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.3434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1348.6906 | 0 | 269.7381 | 2.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 10:01 | 10 | 5 | 10 | 278 | 6658 | 62.96 | 827.0618 | 6.0154 | 6.0154 | 821.0464 | Heating | 724.4527 | 8.5 | 724.4527 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 144.8905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 739.2374 | 0 | 147.8475 | 1.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 11:01 | 10 | 5 | 11 | 278 | 6659 | 62.96 | 295.8138 | 24.3187 | 24.3187 | 271.495 | Heating | 239.5544 | 8.5 | 239.5544 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.9109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 244.4433 | 0 | 48.8887 | 0.4889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 12:01 | 10 | 5 | 12 | 278 | 6660 | 62.96 | 191.0328 | 30.2112 | 30.2112 | 160.8217 | Heating | 141.9015 | 8.5 | 141.9015 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.3803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 144.7974 | 0 | 28.9595 | 0.2896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 13:01 | 10 | 5 | 13 | 278 | 6661 | 64.4 | 200.9365 | 33.9199 | 33.9199 | 167.0166 | Heating | 147.3676 | 8.5 | 147.3676 | 0 | 6.2364 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.4735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 150.3751 | 0 | 30.075 | 0.3008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 14:01 | 10 | 5 | 14 | 278 | 6662 | 64.94 | 197.9385 | 13.5632 | 13.5632 | 184.3753 | Heating | 162.6841 | 8.5 | 162.6841 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 32.5368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 166.0042 | 0 | 33.2008 | 0.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 15:01 | 10 | 5 | 15 | 278 | 6663 | 66.92 | 188.0595 | 17.1341 | 17.1341 | 170.9253 | Heating | 150.8165 | 8.5 | 150.8165 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.1633 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 153.8943 | 0 | 30.7789 | 0.3078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 16:01 | 10 | 5 | 16 | 278 | 6664 | 66.02 | 182.7273 | 7.7712 | 7.7712 | 174.9561 | Heating | 154.373 | 8.5 | 154.373 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.8746 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 157.5235 | 0 | 31.5047 | 0.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 17:01 | 10 | 5 | 17 | 278 | 6665 | 66.02 | 177.3603 | 0 | 0 | 177.3603 | Heating | 156.4944 | 8.5 | 156.4944 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.2989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 159.6882 | 0 | 31.9376 | 0.3194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 18:01 | 10 | 5 | 18 | 278 | 6666 | 64.04 | 625.3425 | 0 | 0 | 625.3425 | Heating | 551.7728 | 8.5 | 551.7728 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.3546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 563.0335 | 0 | 112.6067 | 1.126% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 19:01 | 10 | 5 | 19 | 278 | 6667 | 62.96 | 1188.1906 | 0 | 0 | 1188.1906 | Heating | 1048.4035 | 8.5 | 1048.4035 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.6807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1069.7995 | 0 | 213.9599 | 2.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 20:01 | 10 | 5 | 20 | 278 | 6668 | 62.06 | 1777.0361 | 0 | 0 | 1777.0361 | Heating | 1567.973 | 8.5 | 1567.973 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.5946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1599.9724 | 0 | 319.9945 | 3.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 21:01 | 10 | 5 | 21 | 278 | 6669 | 59 | 2549.6984 | 0 | 0 | 2549.6984 | Heating | 2249.7339 | 8.5 | 2249.7339 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.9468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2295.6469 | 0 | 459.1294 | 4.591% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 22:01 | 10 | 5 | 22 | 278 | 6670 | 57.92 | 502.5858 | 0 | 0 | 502.5858 | Heating | 443.4581 | 8.5 | 443.4581 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.6916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 452.5082 | 0 | 90.5016 | 0.905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-05 23:01 | 10 | 5 | 23 | 278 | 6671 | 57.92 | 553.2972 | 0 | 0 | 553.2972 | Heating | 488.2034 | 8.5 | 488.2034 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 97.6407 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 498.1667 | 0 | 99.6333 | 0.9963% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 00:01 | 10 | 6 | 0 | 279 | 6672 | 53.96 | 596.3186 | 0 | 0 | 596.3186 | Heating | 526.1634 | 8.5 | 526.1634 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.2327 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 536.9015 | 0 | 107.3803 | 1.074% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 01:01 | 10 | 6 | 1 | 279 | 6673 | 52.34 | 595.1149 | 0 | 0 | 595.1149 | Heating | 525.1014 | 8.5 | 525.1014 | 0 | 4.7405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.0203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 535.8178 | 0 | 107.1636 | 1.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 02:01 | 10 | 6 | 2 | 279 | 6674 | 52.34 | 577.3181 | 0 | 0 | 577.3181 | Heating | 509.3983 | 8.5 | 509.3983 | 0 | 4.7405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.8797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 519.7942 | 0 | 103.9588 | 1.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 03:01 | 10 | 6 | 3 | 279 | 6675 | 51.08 | 562.0823 | 0 | 0 | 562.0823 | Heating | 495.955 | 8.5 | 495.955 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 506.0765 | 0 | 101.2153 | 1.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 04:01 | 10 | 6 | 4 | 279 | 6676 | 48.56 | 517.742 | 0 | 0 | 517.742 | Heating | 456.8312 | 8.5 | 456.8312 | 0 | 4.3829 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.3662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 466.1542 | 0 | 93.2308 | 0.9323% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 05:01 | 10 | 6 | 5 | 279 | 6677 | 48.02 | 495.7021 | 0 | 0 | 495.7021 | Heating | 437.3842 | 8.5 | 437.3842 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.4768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 446.3104 | 0 | 89.2621 | 0.8926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 06:01 | 10 | 6 | 6 | 279 | 6678 | 46.04 | 502.2546 | 0 | 0 | 502.2546 | Heating | 443.1658 | 8.5 | 443.1658 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.6332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 452.21 | 0 | 90.442 | 0.9044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 07:01 | 10 | 6 | 7 | 279 | 6679 | 48.02 | 493.0638 | 0 | 0 | 493.0638 | Heating | 435.0563 | 8.5 | 435.0563 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.0113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 443.935 | 0 | 88.787 | 0.8879% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 08:01 | 10 | 6 | 8 | 279 | 6680 | 48.02 | 4971.3852 | 0 | 0 | 4971.3852 | Heating | 4386.5164 | 8.5 | 4386.5164 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 877.3033 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4476.0371 | 0 | 895.2074 | 8.952% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 09:01 | 10 | 6 | 9 | 279 | 6681 | 55.04 | 3501.657 | 0 | 0 | 3501.657 | Heating | 3089.6973 | 8.5 | 3089.6973 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 617.9395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3152.7524 | 0 | 630.5505 | 6.306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 10:01 | 10 | 6 | 10 | 279 | 6682 | 60.08 | 2937.8187 | 0 | 0 | 2937.8187 | Heating | 2592.193 | 8.5 | 2592.193 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 518.4386 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2645.0949 | 0 | 529.019 | 5.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 11:01 | 10 | 6 | 11 | 279 | 6683 | 60.08 | 2422.7287 | 0 | 0 | 2422.7287 | Heating | 2137.7018 | 8.5 | 2137.7018 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.5404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2181.3283 | 0 | 436.2657 | 4.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 12:01 | 10 | 6 | 12 | 279 | 6684 | 66.92 | 1828.7433 | 0 | 0 | 1828.7433 | Heating | 1613.597 | 8.5 | 1613.597 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 322.7194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1646.5275 | 0 | 329.3055 | 3.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 13:01 | 10 | 6 | 13 | 279 | 6685 | 68 | 1763.9057 | 0 | 0 | 1763.9057 | Heating | 1556.3874 | 8.5 | 1556.3874 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.2775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1588.1504 | 0 | 317.6301 | 3.176% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 14:01 | 10 | 6 | 14 | 279 | 6686 | 68 | 1698.1648 | 0 | 0 | 1698.1648 | Heating | 1498.3807 | 8.5 | 1498.3807 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 299.6761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1528.9599 | 0 | 305.792 | 3.058% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 15:01 | 10 | 6 | 15 | 279 | 6687 | 69.98 | 1802.4728 | 0 | 0 | 1802.4728 | Heating | 1590.4172 | 8.5 | 1590.4172 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 318.0834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1622.8747 | 0 | 324.5749 | 3.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 16:01 | 10 | 6 | 16 | 279 | 6688 | 71.06 | 1952.7183 | 0 | 0 | 1952.7183 | Heating | 1722.9868 | 8.5 | 1722.9868 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.5974 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1758.1498 | 0 | 351.63 | 3.516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 17:01 | 10 | 6 | 17 | 279 | 6689 | 71.06 | 3210.0244 | 0 | 0 | 3210.0244 | Heating | 2832.3745 | 8.5 | 2832.3745 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 566.4749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2890.1781 | 0 | 578.0356 | 5.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 18:01 | 10 | 6 | 18 | 279 | 6690 | 60.98 | 3661.49 | 0 | 0 | 3661.49 | Heating | 3230.7265 | 8.5 | 3230.7265 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 646.1453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3296.6597 | 0 | 659.3319 | 6.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 19:01 | 10 | 6 | 19 | 279 | 6691 | 60.08 | 600.9418 | 0 | 0 | 600.9418 | Heating | 530.2427 | 8.5 | 530.2427 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.0485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 541.064 | 0 | 108.2128 | 1.082% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 20:01 | 10 | 6 | 20 | 279 | 6692 | 60.08 | 645.0029 | 0 | 0 | 645.0029 | Heating | 569.1202 | 8.5 | 569.1202 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 580.7349 | 0 | 116.147 | 1.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 21:01 | 10 | 6 | 21 | 279 | 6693 | 55.94 | 702.0164 | 0 | 0 | 702.0164 | Heating | 619.4263 | 8.5 | 619.4263 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.8853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 632.0676 | 0 | 126.4135 | 1.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 22:01 | 10 | 6 | 22 | 279 | 6694 | 53.06 | 767.3124 | 0 | 0 | 767.3124 | Heating | 677.0403 | 8.5 | 677.0403 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.4081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 690.8575 | 0 | 138.1715 | 1.382% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-06 23:01 | 10 | 6 | 23 | 279 | 6695 | 53.06 | 857.6235 | 0 | 0 | 857.6235 | Heating | 756.7266 | 8.5 | 756.7266 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.3453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 772.17 | 0 | 154.434 | 1.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 00:01 | 10 | 7 | 0 | 280 | 6696 | 48.92 | 997.3917 | 0 | 0 | 997.3917 | Heating | 880.0515 | 8.5 | 880.0515 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 176.0103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 898.0117 | 0 | 179.6023 | 1.796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 01:01 | 10 | 7 | 1 | 280 | 6697 | 48.92 | 1166.0205 | 0 | 0 | 1166.0205 | Heating | 1028.8416 | 8.5 | 1028.8416 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 205.7683 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1049.8384 | 0 | 209.9677 | 2.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 02:01 | 10 | 7 | 2 | 280 | 6698 | 48.92 | 1262.4944 | 0 | 0 | 1262.4944 | Heating | 1113.9656 | 8.5 | 1113.9656 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.7931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1136.6996 | 0 | 227.3399 | 2.273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 03:01 | 10 | 7 | 3 | 280 | 6699 | 46.94 | 1308.5299 | 0 | 0 | 1308.5299 | Heating | 1154.5852 | 8.5 | 1154.5852 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1178.1482 | 0 | 235.6296 | 2.356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 04:01 | 10 | 7 | 4 | 280 | 6700 | 44.96 | 1426.6871 | 0 | 0 | 1426.6871 | Heating | 1258.8415 | 8.5 | 1258.8415 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.7683 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1284.5322 | 0 | 256.9064 | 2.569% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 05:01 | 10 | 7 | 5 | 280 | 6701 | 44.96 | 1532.0789 | 0 | 0 | 1532.0789 | Heating | 1351.8343 | 8.5 | 1351.8343 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 270.3669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1379.4228 | 0 | 275.8846 | 2.759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 06:01 | 10 | 7 | 6 | 280 | 6702 | 44.06 | 10250.1297 | 0 | 0 | 10250.1297 | Heating | 9044.2321 | 8.5 | 9044.2321 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1808.8464 | 36.18% | 1 | 72.35% | 0% | 0% | 0% | 38.7173 | 0 | 0 | 0 | 38.7173 | 9228.8082 | 0 | 1845.7616 | 18.46% | 1 | 36.92% | 0% | 0% | 4.118 | 0 | 0 | 4.118 | 42.8353
2007-10-07 07:01 | 10 | 7 | 7 | 280 | 6703 | 42.98 | 7601.7665 | 0 | 0 | 7601.7665 | Heating | 6707.4411 | 8.5 | 6707.4411 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1341.4882 | 30% | 1 | 53.66% | 0% | 0% | 0% | 19.4684 | 0 | 0 | 0 | 19.4684 | 6844.3276 | 0 | 1368.8655 | 13.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.743
2007-10-07 08:01 | 10 | 7 | 8 | 280 | 6704 | 44.96 | 5693.8635 | 0 | 0 | 5693.8635 | Heating | 5023.9972 | 8.5 | 5023.9972 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1004.7994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5126.5278 | 0 | 1025.3056 | 10.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 09:01 | 10 | 7 | 9 | 280 | 6705 | 55.04 | 3705.5905 | 0 | 0 | 3705.5905 | Heating | 3269.6387 | 8.5 | 3269.6387 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 653.9277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3336.366 | 0 | 667.2732 | 6.673% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 10:01 | 10 | 7 | 10 | 280 | 6706 | 60.98 | 2445.6653 | 0 | 0 | 2445.6653 | Heating | 2157.94 | 8.5 | 2157.94 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 431.588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2201.9796 | 0 | 440.3959 | 4.404% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 11:01 | 10 | 7 | 11 | 280 | 6707 | 60.98 | 1587.9058 | 0 | 0 | 1587.9058 | Heating | 1401.0934 | 8.5 | 1401.0934 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 280.2187 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1429.6871 | 0 | 285.9374 | 2.859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 12:01 | 10 | 7 | 12 | 280 | 6708 | 68 | 1022.2513 | 3.6075 | 3.6075 | 1018.6438 | Heating | 898.8034 | 8.5 | 898.8034 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 179.7607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 917.1463 | 0 | 183.4293 | 1.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 13:01 | 10 | 7 | 13 | 280 | 6709 | 69.98 | 641.2486 | 49.5307 | 49.5307 | 591.7179 | Heating | 522.1041 | 8.5 | 522.1041 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 104.4208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 532.7593 | 0 | 106.5519 | 1.066% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 14:01 | 10 | 7 | 14 | 280 | 6710 | 69.98 | 345.7762 | 125.235 | 125.235 | 220.5411 | Heating | 194.5951 | 8.5 | 194.5951 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 198.5664 | 0 | 39.7133 | 0.3971% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 15:01 | 10 | 7 | 15 | 280 | 6711 | 73.04 | 233.9212 | 154.8159 | 154.8159 | 79.1053 | Heating | 69.7988 | 8.5 | 69.7988 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.9598 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 71.2232 | 0 | 14.2446 | 0.1424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 16:01 | 10 | 7 | 16 | 280 | 6712 | 71.96 | 187.744 | 160.5892 | 160.5892 | 27.1547 | Heating | 23.9601 | 8.5 | 23.9601 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.792 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.4491 | 0 | 4.8898 | 0.0489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 17:01 | 10 | 7 | 17 | 280 | 6713 | 71.96 | 216.4822 | 115.5818 | 115.5818 | 100.9004 | Heating | 89.0298 | 8.5 | 89.0298 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 90.8467 | 0 | 18.1693 | 0.1817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 18:01 | 10 | 7 | 18 | 280 | 6714 | 60.98 | 749.8871 | 47.8616 | 47.8616 | 702.0255 | Heating | 619.4342 | 8.5 | 619.4342 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.8868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 632.0758 | 0 | 126.4152 | 1.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 19:01 | 10 | 7 | 19 | 280 | 6715 | 55.94 | 1667.8041 | 17.1471 | 17.1471 | 1650.657 | Heating | 1456.462 | 8.5 | 1456.462 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 291.2924 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1486.1857 | 0 | 297.2371 | 2.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 20:01 | 10 | 7 | 20 | 280 | 6716 | 55.94 | 2438.3991 | 0 | 0 | 2438.3991 | Heating | 2151.5286 | 8.5 | 2151.5286 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 430.3057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2195.4373 | 0 | 439.0875 | 4.391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 21:01 | 10 | 7 | 21 | 280 | 6717 | 53.06 | 602.8612 | 0 | 0 | 602.8612 | Heating | 531.9363 | 8.5 | 531.9363 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.3873 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.7922 | 0 | 108.5584 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 22:01 | 10 | 7 | 22 | 280 | 6718 | 51.98 | 626.3946 | 0 | 0 | 626.3946 | Heating | 552.7011 | 8.5 | 552.7011 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.5402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 563.9808 | 0 | 112.7962 | 1.128% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-07 23:01 | 10 | 7 | 23 | 280 | 6719 | 51.98 | 683.1019 | 0 | 0 | 683.1019 | Heating | 602.7369 | 8.5 | 602.7369 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.5474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 615.0377 | 0 | 123.0075 | 1.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 00:01 | 10 | 8 | 0 | 281 | 6720 | 48.92 | 696.033 | 0 | 0 | 696.033 | Heating | 614.1468 | 8.5 | 614.1468 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.8294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 626.6804 | 0 | 125.3361 | 1.253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 01:01 | 10 | 8 | 1 | 281 | 6721 | 48.92 | 727.3095 | 0 | 0 | 727.3095 | Heating | 641.7436 | 8.5 | 641.7436 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.3487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 654.8405 | 0 | 130.9681 | 1.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 02:01 | 10 | 8 | 2 | 281 | 6722 | 48.02 | 736.3703 | 0 | 0 | 736.3703 | Heating | 649.7385 | 8.5 | 649.7385 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.9477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 662.9985 | 0 | 132.5997 | 1.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 03:01 | 10 | 8 | 3 | 281 | 6723 | 44.96 | 749.7648 | 0 | 0 | 749.7648 | Heating | 661.5572 | 8.5 | 661.5572 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.3114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 675.0583 | 0 | 135.0117 | 1.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 04:01 | 10 | 8 | 4 | 281 | 6724 | 46.04 | 775.5721 | 0 | 0 | 775.5721 | Heating | 684.3283 | 8.5 | 684.3283 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.8657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 698.2942 | 0 | 139.6588 | 1.397% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 05:01 | 10 | 8 | 5 | 281 | 6725 | 46.04 | 766.3436 | 0 | 0 | 766.3436 | Heating | 676.1855 | 8.5 | 676.1855 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.2371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 689.9852 | 0 | 137.997 | 1.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 06:01 | 10 | 8 | 6 | 281 | 6726 | 46.04 | 7265.6588 | 0 | 0 | 7265.6588 | Heating | 6410.8754 | 8.5 | 6410.8754 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1282.1751 | 30% | 1 | 51.29% | 0% | 0% | 0% | 17.5453 | 0 | 0 | 0 | 17.5453 | 6541.7096 | 0 | 1308.3419 | 13.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.8198
2007-10-08 07:01 | 10 | 8 | 7 | 281 | 6727 | 46.04 | 5243.1886 | 0 | 0 | 5243.1886 | Heating | 4626.3429 | 8.5 | 4626.3429 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 925.2686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4720.7581 | 0 | 944.1516 | 9.442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 08:01 | 10 | 8 | 8 | 281 | 6728 | 46.94 | 3715.5096 | 0 | 0 | 3715.5096 | Heating | 3278.3908 | 8.5 | 3278.3908 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 655.6782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3345.2968 | 0 | 669.0594 | 6.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 09:01 | 10 | 8 | 9 | 281 | 6729 | 50 | 2132.4268 | 0 | 0 | 2132.4268 | Heating | 1881.5531 | 8.5 | 1881.5531 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.3106 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1919.9521 | 0 | 383.9904 | 3.84% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 10:01 | 10 | 8 | 10 | 281 | 6730 | 60.08 | 1023.1971 | 28.8695 | 28.8695 | 994.3276 | Heating | 877.3479 | 8.5 | 877.3479 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.4696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 895.253 | 0 | 179.0506 | 1.791% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 11:01 | 10 | 8 | 11 | 281 | 6731 | 60.08 | 225.2475 | 144.7227 | 144.7227 | 80.5249 | Heating | 71.0513 | 8.5 | 71.0513 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.2103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 72.5014 | 0 | 14.5003 | 0.145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 12:01 | 10 | 8 | 12 | 281 | 6732 | 69.98 | 115.0686 | 383.8176 | 383.8176 | -268.749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 469.1104 | 469.1104 | 0 | 8.5 | 0 | 78.1851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 459.7282 | 91.9456 | 0.9195% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 13:01 | 10 | 8 | 13 | 281 | 6733 | 71.96 | 71.0519 | 608.6778 | 608.6778 | -537.6259 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 743.9396 | 743.9396 | 0 | 8.5 | 0 | 123.9899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 729.0608 | 145.8122 | 1.458% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 14:01 | 10 | 8 | 14 | 281 | 6734 | 71.96 | 24.789 | 1645.8186 | 1645.8186 | -1621.0297 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2011.5561 | 2011.5561 | 0 | 8.5 | 0 | 335.2593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1971.325 | 394.265 | 3.943% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 15:01 | 10 | 8 | 15 | 281 | 6735 | 75.02 | 4.0074 | 2443.6566 | 2443.6566 | -2439.6492 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2986.6914 | 2986.6914 | 0 | 8.5 | 0 | 497.7819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2926.9576 | 585.3915 | 5.854% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 16:01 | 10 | 8 | 16 | 281 | 6736 | 73.04 | 0.91797 | 2398.7646 | 2398.7646 | -2397.8466 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2931.8234 | 2931.8234 | 0 | 8.5 | 0 | 488.6372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2873.1869 | 574.6374 | 5.746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 17:01 | 10 | 8 | 17 | 281 | 6737 | 73.04 | 0.50964 | 1689.415 | 1689.415 | -1688.9054 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2064.8406 | 2064.8406 | 0 | 8.5 | 0 | 344.1401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2023.5438 | 404.7088 | 4.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 18:01 | 10 | 8 | 18 | 281 | 6738 | 68 | 0.55794 | 342.4087 | 342.4087 | -341.8508 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 418.4995 | 418.4995 | 0 | 8.5 | 0 | 69.7499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 410.1295 | 82.0259 | 0.8203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 19:01 | 10 | 8 | 19 | 281 | 6739 | 68 | 3.8241 | 236.4756 | 236.4756 | -232.6515 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 289.0257 | 289.0257 | 0 | 8.5 | 0 | 48.171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 283.2452 | 56.649 | 0.5665% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 20:01 | 10 | 8 | 20 | 281 | 6740 | 68 | 7.5905 | 150.4991 | 150.4991 | -142.9085 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 183.9433 | 183.9433 | 0 | 8.5 | 0 | 30.6572 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 180.2645 | 36.0529 | 0.3605% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 21:01 | 10 | 8 | 21 | 281 | 6741 | 64.94 | 11.1517 | 120.6842 | 120.6842 | -109.5325 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 147.5029 | 147.5029 | 0 | 8.5 | 0 | 24.5838 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 144.5529 | 28.9106 | 0.2891% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 22:01 | 10 | 8 | 22 | 281 | 6742 | 64.04 | 27.3722 | 0 | 0 | 27.3722 | Heating | 24.1519 | 8.5 | 24.1519 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.8304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.6448 | 0 | 4.929 | 0.04929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-08 23:01 | 10 | 8 | 23 | 281 | 6743 | 64.04 | 44.5686 | 0 | 0 | 44.5686 | Heating | 39.3252 | 8.5 | 39.3252 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 40.1278 | 0 | 8.0256 | 0.08026% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 00:01 | 10 | 9 | 0 | 282 | 6744 | 60.98 | 65.647 | 0 | 0 | 65.647 | Heating | 57.9238 | 8.5 | 57.9238 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.5848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 59.106 | 0 | 11.8212 | 0.1182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 01:01 | 10 | 9 | 1 | 282 | 6745 | 59 | 79.1758 | 0 | 0 | 79.1758 | Heating | 69.861 | 8.5 | 69.861 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.9722 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 71.2867 | 0 | 14.2573 | 0.1426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 02:01 | 10 | 9 | 2 | 282 | 6746 | 59 | 99.6104 | 0 | 0 | 99.6104 | Heating | 87.8915 | 8.5 | 87.8915 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 17.5783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 89.6852 | 0 | 17.937 | 0.1794% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 03:01 | 10 | 9 | 3 | 282 | 6747 | 55.04 | 129.1197 | 0 | 0 | 129.1197 | Heating | 113.9291 | 8.5 | 113.9291 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.7858 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.2542 | 0 | 23.2508 | 0.2325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 04:01 | 10 | 9 | 4 | 282 | 6748 | 53.96 | 155.5818 | 0 | 0 | 155.5818 | Heating | 137.2781 | 8.5 | 137.2781 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.4556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 140.0796 | 0 | 28.0159 | 0.2802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 05:01 | 10 | 9 | 5 | 282 | 6749 | 53.96 | 187.7838 | 0 | 0 | 187.7838 | Heating | 165.6916 | 8.5 | 165.6916 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.1383 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 169.0731 | 0 | 33.8146 | 0.3381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 06:01 | 10 | 9 | 6 | 282 | 6750 | 53.06 | 2786.9855 | 81.1224 | 81.1224 | 2705.8632 | Heating | 2387.5263 | 8.5 | 2387.5263 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 477.5053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2436.2513 | 0 | 487.2503 | 4.873% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 07:01 | 10 | 9 | 7 | 282 | 6751 | 53.06 | 1925.5642 | 0 | 0 | 1925.5642 | Heating | 1699.0272 | 8.5 | 1699.0272 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.8054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1733.7012 | 0 | 346.7402 | 3.467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 08:01 | 10 | 9 | 8 | 282 | 6752 | 53.06 | 1161.7387 | 100.0015 | 100.0015 | 1061.7373 | Heating | 936.827 | 8.5 | 936.827 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 187.3654 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 955.9459 | 0 | 191.1892 | 1.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 09:01 | 10 | 9 | 9 | 282 | 6753 | 57.92 | 147.3048 | 364.8575 | 364.8575 | -217.5528 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 445.937 | 445.937 | 0 | 8.5 | 0 | 74.3228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 437.0183 | 87.4037 | 0.874% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 10:01 | 10 | 9 | 10 | 282 | 6754 | 60.98 | 38.4652 | 668.2223 | 668.2223 | -629.7571 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 816.7161 | 816.7161 | 0 | 8.5 | 0 | 136.1194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 800.3818 | 160.0764 | 1.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 11:01 | 10 | 9 | 11 | 282 | 6755 | 60.98 | 19.9752 | 1042.3483 | 1042.3483 | -1022.3731 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1273.9812 | 1273.9812 | 0 | 8.5 | 0 | 212.3302 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1248.5016 | 249.7003 | 2.497% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 12:01 | 10 | 9 | 12 | 282 | 6756 | 64.94 | 62.7315 | 706.8567 | 706.8567 | -644.1252 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 863.936 | 863.936 | 0 | 8.5 | 0 | 143.9893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 846.6573 | 169.3315 | 1.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 13:01 | 10 | 9 | 13 | 282 | 6757 | 64.94 | 109.4348 | 750.6176 | 750.6176 | -641.1828 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 917.4215 | 917.4215 | 0 | 8.5 | 0 | 152.9036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 899.073 | 179.8146 | 1.798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 14:01 | 10 | 9 | 14 | 282 | 6758 | 64.94 | 192.2212 | 621.6373 | 621.6373 | -429.4161 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 759.7789 | 759.7789 | 0 | 8.5 | 0 | 126.6298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 744.5833 | 148.9167 | 1.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 15:01 | 10 | 9 | 15 | 282 | 6759 | 64.04 | 360.0785 | 252.2182 | 252.2182 | 107.8603 | Heating | 95.1708 | 8.5 | 95.1708 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.0342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 97.1131 | 0 | 19.4226 | 0.1942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 16:01 | 10 | 9 | 16 | 282 | 6760 | 64.04 | 619.6142 | 160.7631 | 160.7631 | 458.8511 | Heating | 404.8686 | 8.5 | 404.8686 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.9737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 413.1313 | 0 | 82.6263 | 0.8263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 17:01 | 10 | 9 | 17 | 282 | 6761 | 64.04 | 999.0874 | 66.2719 | 66.2719 | 932.8156 | Heating | 823.0726 | 8.5 | 823.0726 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 164.6145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 839.87 | 0 | 167.974 | 1.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 18:01 | 10 | 9 | 18 | 282 | 6762 | 64.04 | 1343.9291 | 9.1977 | 9.1977 | 1334.7314 | Heating | 1177.7042 | 8.5 | 1177.7042 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.5408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1201.739 | 0 | 240.3478 | 2.403% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 19:01 | 10 | 9 | 19 | 282 | 6763 | 62.96 | 1584.1941 | 2.9253 | 2.9253 | 1581.2687 | Heating | 1395.2371 | 8.5 | 1395.2371 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.0474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1423.7114 | 0 | 284.7423 | 2.847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 20:01 | 10 | 9 | 20 | 282 | 6764 | 62.96 | 1872.1185 | 0 | 0 | 1872.1185 | Heating | 1651.8692 | 8.5 | 1651.8692 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 330.3738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1685.5808 | 0 | 337.1162 | 3.371% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 21:01 | 10 | 9 | 21 | 282 | 6765 | 60.08 | 483.4319 | 0 | 0 | 483.4319 | Heating | 426.5575 | 8.5 | 426.5575 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.3115 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 435.2628 | 0 | 87.0526 | 0.8705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 22:01 | 10 | 9 | 22 | 282 | 6766 | 60.08 | 538.1503 | 0 | 0 | 538.1503 | Heating | 474.8385 | 8.5 | 474.8385 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 94.9677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 484.5291 | 0 | 96.9058 | 0.9691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-09 23:01 | 10 | 9 | 23 | 282 | 6767 | 60.08 | 581.8801 | 0 | 0 | 581.8801 | Heating | 513.4236 | 8.5 | 513.4236 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.6847 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 523.9017 | 0 | 104.7803 | 1.048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 00:01 | 10 | 10 | 0 | 283 | 6768 | 57.92 | 627.7485 | 0 | 0 | 627.7485 | Heating | 553.8957 | 8.5 | 553.8957 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.7791 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 565.1997 | 0 | 113.0399 | 1.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 01:01 | 10 | 10 | 1 | 283 | 6769 | 57.92 | 665.4901 | 0 | 0 | 665.4901 | Heating | 587.1972 | 8.5 | 587.1972 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 117.4394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 599.1808 | 0 | 119.8362 | 1.198% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 02:01 | 10 | 10 | 2 | 283 | 6770 | 57.92 | 709.5187 | 0 | 0 | 709.5187 | Heating | 626.0459 | 8.5 | 626.0459 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.2092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 638.8223 | 0 | 127.7645 | 1.278% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 03:01 | 10 | 10 | 3 | 283 | 6771 | 57.92 | 755.1311 | 0 | 0 | 755.1311 | Heating | 666.2921 | 8.5 | 666.2921 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.2584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 679.8899 | 0 | 135.978 | 1.36% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 04:01 | 10 | 10 | 4 | 283 | 6772 | 57.02 | 843.1058 | 0 | 0 | 843.1058 | Heating | 743.9169 | 8.5 | 743.9169 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.7834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 759.0989 | 0 | 151.8198 | 1.518% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 05:01 | 10 | 10 | 5 | 283 | 6773 | 57.02 | 924.9176 | 0 | 0 | 924.9176 | Heating | 816.1038 | 8.5 | 816.1038 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.2208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 832.759 | 0 | 166.5518 | 1.666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 06:01 | 10 | 10 | 6 | 283 | 6774 | 53.06 | 8335.2651 | 0 | 0 | 8335.2651 | Heating | 7354.6457 | 8.5 | 7354.6457 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1470.9291 | 30% | 1 | 58.84% | 0% | 0% | 0% | 24.0626 | 0 | 0 | 0 | 24.0626 | 7504.7405 | 0 | 1500.9481 | 15.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.3371
2007-10-10 07:01 | 10 | 10 | 7 | 283 | 6775 | 53.06 | 6408.0103 | 0 | 0 | 6408.0103 | Heating | 5654.1267 | 8.5 | 5654.1267 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1130.8253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5769.5171 | 0 | 1153.9034 | 11.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 08:01 | 10 | 10 | 8 | 283 | 6776 | 53.06 | 4904.2572 | 0 | 0 | 4904.2572 | Heating | 4327.2858 | 8.5 | 4327.2858 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 865.4572 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4415.5977 | 0 | 883.1195 | 8.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 09:01 | 10 | 10 | 9 | 283 | 6777 | 53.06 | 3354.1373 | 0 | 0 | 3354.1373 | Heating | 2959.5329 | 8.5 | 2959.5329 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.9066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3019.9315 | 0 | 603.9863 | 6.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 10:01 | 10 | 10 | 10 | 283 | 6778 | 53.96 | 2603.0309 | 2.6751 | 2.6751 | 2600.3558 | Heating | 2294.4316 | 8.5 | 2294.4316 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 458.8863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2341.2567 | 0 | 468.2513 | 4.683% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 11:01 | 10 | 10 | 11 | 283 | 6779 | 53.96 | 1981.8464 | 29.5986 | 29.5986 | 1952.2478 | Heating | 1722.5716 | 8.5 | 1722.5716 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.5143 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1757.7261 | 0 | 351.5452 | 3.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 12:01 | 10 | 10 | 12 | 283 | 6780 | 57.92 | 1509.2204 | 134.1828 | 134.1828 | 1375.0376 | Heating | 1213.2685 | 8.5 | 1213.2685 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.6537 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1238.029 | 0 | 247.6058 | 2.476% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 13:01 | 10 | 10 | 13 | 283 | 6781 | 59 | 1092.5808 | 283.8118 | 283.8118 | 808.7689 | Heating | 713.6197 | 8.5 | 713.6197 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 142.7239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 728.1833 | 0 | 145.6367 | 1.456% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 14:01 | 10 | 10 | 14 | 283 | 6782 | 59 | 851.2998 | 381.4576 | 381.4576 | 469.8422 | Heating | 414.5667 | 8.5 | 414.5667 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.9133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 423.0272 | 0 | 84.6054 | 0.8461% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 15:01 | 10 | 10 | 15 | 283 | 6783 | 57.92 | 718.0727 | 349.4953 | 349.4953 | 368.5774 | Heating | 325.2153 | 8.5 | 325.2153 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.0431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 331.8524 | 0 | 66.3705 | 0.6637% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 16:01 | 10 | 10 | 16 | 283 | 6784 | 57.92 | 867.5231 | 288.8483 | 288.8483 | 578.6749 | Heating | 510.5955 | 8.5 | 510.5955 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.1191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 521.0158 | 0 | 104.2032 | 1.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 17:01 | 10 | 10 | 17 | 283 | 6785 | 57.92 | 1252.0495 | 185.6152 | 185.6152 | 1066.4343 | Heating | 940.9714 | 8.5 | 940.9714 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.1943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 960.1749 | 0 | 192.035 | 1.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 18:01 | 10 | 10 | 18 | 283 | 6786 | 53.96 | 1953.3662 | 61.9272 | 61.9272 | 1891.439 | Heating | 1668.9167 | 8.5 | 1668.9167 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 333.7833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1702.9762 | 0 | 340.5952 | 3.406% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 19:01 | 10 | 10 | 19 | 283 | 6787 | 53.06 | 2817.0601 | 22.4957 | 22.4957 | 2794.5644 | Heating | 2465.7921 | 8.5 | 2465.7921 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 493.1584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2516.1144 | 0 | 503.2229 | 5.032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 20:01 | 10 | 10 | 20 | 283 | 6788 | 53.06 | 3407.9584 | 0 | 0 | 3407.9584 | Heating | 3007.0221 | 8.5 | 3007.0221 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 601.4044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3068.3899 | 0 | 613.678 | 6.137% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 21:01 | 10 | 10 | 21 | 283 | 6789 | 51.98 | 875.8852 | 0 | 0 | 875.8852 | Heating | 772.8399 | 8.5 | 772.8399 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 788.6121 | 0 | 157.7224 | 1.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 22:01 | 10 | 10 | 22 | 283 | 6790 | 50 | 900.9779 | 0 | 0 | 900.9779 | Heating | 794.9805 | 8.5 | 794.9805 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.9961 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 811.2046 | 0 | 162.2409 | 1.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-10 23:01 | 10 | 10 | 23 | 283 | 6791 | 50 | 991.4672 | 0 | 0 | 991.4672 | Heating | 874.824 | 8.5 | 874.824 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.9648 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 892.6776 | 0 | 178.5355 | 1.785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 00:01 | 10 | 11 | 0 | 284 | 6792 | 48.92 | 1111.5039 | 0 | 0 | 1111.5039 | Heating | 980.7387 | 8.5 | 980.7387 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.1477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1000.7538 | 0 | 200.1508 | 2.002% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 01:01 | 10 | 11 | 1 | 284 | 6793 | 48.92 | 1209.7317 | 0 | 0 | 1209.7317 | Heating | 1067.4104 | 8.5 | 1067.4104 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 213.4821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1089.1942 | 0 | 217.8388 | 2.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 02:01 | 10 | 11 | 2 | 284 | 6794 | 48.92 | 1352.6503 | 0 | 0 | 1352.6503 | Heating | 1193.515 | 8.5 | 1193.515 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1217.8724 | 0 | 243.5745 | 2.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 03:01 | 10 | 11 | 3 | 284 | 6795 | 46.94 | 1441.9513 | 0 | 0 | 1441.9513 | Heating | 1272.31 | 8.5 | 1272.31 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1298.2755 | 0 | 259.6551 | 2.597% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 04:01 | 10 | 11 | 4 | 284 | 6796 | 46.04 | 1527.3843 | 0 | 0 | 1527.3843 | Heating | 1347.692 | 8.5 | 1347.692 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 269.5384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1375.196 | 0 | 275.0392 | 2.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 05:01 | 10 | 11 | 5 | 284 | 6797 | 46.04 | 1605.0509 | 0 | 0 | 1605.0509 | Heating | 1416.2214 | 8.5 | 1416.2214 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 283.2443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1445.1239 | 0 | 289.0248 | 2.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 06:01 | 10 | 11 | 6 | 284 | 6798 | 42.98 | 11462.047 | 0 | 0 | 11462.047 | Heating | 10113.5709 | 8.5 | 10113.5709 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2022.7142 | 40.45% | 1 | 80.91% | 0% | 0% | 0% | 50.0646 | 0 | 0 | 0 | 50.0646 | 10319.9703 | 0 | 2063.9941 | 20.64% | 1 | 41.28% | 0% | 0% | 5.3249 | 0 | 0 | 5.3249 | 55.3895
2007-10-11 07:01 | 10 | 11 | 7 | 284 | 6799 | 42.08 | 8677.0938 | 0 | 0 | 8677.0938 | Heating | 7656.2592 | 8.5 | 7656.2592 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1531.2518 | 30.63% | 1 | 61.25% | 0% | 0% | 0% | 26.393 | 0 | 0 | 0 | 26.393 | 7812.5094 | 0 | 1562.5019 | 15.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.6675
2007-10-11 08:01 | 10 | 11 | 8 | 284 | 6800 | 42.08 | 6683.2129 | 0 | 0 | 6683.2129 | Heating | 5896.9526 | 8.5 | 5896.9526 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1179.3905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6017.2986 | 0 | 1203.4597 | 12.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 09:01 | 10 | 11 | 9 | 284 | 6801 | 48.02 | 4460.1516 | 0 | 0 | 4460.1516 | Heating | 3935.4279 | 8.5 | 3935.4279 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 787.0856 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4015.7427 | 0 | 803.1485 | 8.031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 10:01 | 10 | 11 | 10 | 284 | 6802 | 50 | 2717.9051 | 1.8974 | 1.8974 | 2716.0077 | Heating | 2396.4774 | 8.5 | 2396.4774 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 479.2955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2445.3851 | 0 | 489.077 | 4.891% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 11:01 | 10 | 11 | 11 | 284 | 6803 | 50 | 1451.5989 | 37.3512 | 37.3512 | 1414.2477 | Heating | 1247.8656 | 8.5 | 1247.8656 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.5731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1273.3322 | 0 | 254.6664 | 2.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 12:01 | 10 | 11 | 12 | 284 | 6804 | 53.96 | 733.1319 | 167.2062 | 167.2062 | 565.9256 | Heating | 499.3462 | 8.5 | 499.3462 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.8692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 509.5369 | 0 | 101.9074 | 1.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 13:01 | 10 | 11 | 13 | 284 | 6805 | 57.02 | 395.4311 | 327.6778 | 327.6778 | 67.7534 | Heating | 59.7824 | 8.5 | 59.7824 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.9565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 61.0024 | 0 | 12.2005 | 0.122% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 14:01 | 10 | 11 | 14 | 284 | 6806 | 57.02 | 269.1658 | 420.6956 | 420.6956 | -151.5298 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 514.1835 | 514.1835 | 0 | 8.5 | 0 | 85.6973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 503.8999 | 100.78 | 1.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 15:01 | 10 | 11 | 15 | 284 | 6807 | 59 | 206.3328 | 419.6042 | 419.6042 | -213.2714 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 512.8495 | 512.8495 | 0 | 8.5 | 0 | 85.4749 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 502.5926 | 100.5185 | 1.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 16:01 | 10 | 11 | 16 | 284 | 6808 | 57.02 | 166.1644 | 391.4625 | 391.4625 | -225.2982 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 478.4542 | 478.4542 | 0 | 8.5 | 0 | 79.7424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 468.8851 | 93.777 | 0.9378% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 17:01 | 10 | 11 | 17 | 284 | 6809 | 57.02 | 175.9513 | 272.4538 | 272.4538 | -96.5025 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 332.9991 | 332.9991 | 0 | 8.5 | 0 | 55.4999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 326.3391 | 65.2678 | 0.6527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 18:01 | 10 | 11 | 18 | 284 | 6810 | 50 | 525.1575 | 113.8199 | 113.8199 | 411.3376 | Heating | 362.9449 | 8.5 | 362.9449 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 72.589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 370.352 | 0 | 74.0704 | 0.7407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 19:01 | 10 | 11 | 19 | 284 | 6811 | 46.94 | 1605.3613 | 66.9801 | 66.9801 | 1538.3812 | Heating | 1357.3952 | 8.5 | 1357.3952 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 271.479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1385.0971 | 0 | 277.0194 | 2.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 20:01 | 10 | 11 | 20 | 284 | 6812 | 46.94 | 2275.7666 | 17.2514 | 17.2514 | 2258.5152 | Heating | 1992.8075 | 8.5 | 1992.8075 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 398.5615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2033.4771 | 0 | 406.6954 | 4.067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 21:01 | 10 | 11 | 21 | 284 | 6813 | 46.04 | 599.8214 | 1.257 | 1.257 | 598.5645 | Heating | 528.1451 | 8.5 | 528.1451 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.629 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 538.9236 | 0 | 107.7847 | 1.078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 22:01 | 10 | 11 | 22 | 284 | 6814 | 42.98 | 690.139 | 0 | 0 | 690.139 | Heating | 608.9462 | 8.5 | 608.9462 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.7892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 621.3737 | 0 | 124.2747 | 1.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-11 23:01 | 10 | 11 | 23 | 284 | 6815 | 42.98 | 768.494 | 0 | 0 | 768.494 | Heating | 678.0829 | 8.5 | 678.0829 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.6166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 691.9213 | 0 | 138.3843 | 1.384% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 00:01 | 10 | 12 | 0 | 285 | 6816 | 41 | 841.2305 | 0 | 0 | 841.2305 | Heating | 742.2622 | 8.5 | 742.2622 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.4524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 757.4105 | 0 | 151.4821 | 1.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 01:01 | 10 | 12 | 1 | 285 | 6817 | 39.02 | 903.7818 | 0 | 0 | 903.7818 | Heating | 797.4546 | 8.5 | 797.4546 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 159.4909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 813.7291 | 0 | 162.7458 | 1.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 02:01 | 10 | 12 | 2 | 285 | 6818 | 39.02 | 963.3505 | 0 | 0 | 963.3505 | Heating | 850.0151 | 8.5 | 850.0151 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 867.3624 | 0 | 173.4725 | 1.735% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 03:01 | 10 | 12 | 3 | 285 | 6819 | 35.96 | 1013.7873 | 0 | 0 | 1013.7873 | Heating | 894.5182 | 8.5 | 894.5182 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 178.9036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 912.7736 | 0 | 182.5547 | 1.826% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 04:01 | 10 | 12 | 4 | 285 | 6820 | 33.98 | 1035.1161 | 0 | 0 | 1035.1161 | Heating | 913.3378 | 8.5 | 913.3378 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.6676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 931.9773 | 0 | 186.3955 | 1.864% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 05:01 | 10 | 12 | 5 | 285 | 6821 | 33.98 | 1029.9242 | 0 | 0 | 1029.9242 | Heating | 908.7567 | 8.5 | 908.7567 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 181.7513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 927.3027 | 0 | 185.4605 | 1.855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 06:01 | 10 | 12 | 6 | 285 | 6822 | 35.6 | 8361.0796 | 0 | 0 | 8361.0796 | Heating | 7377.4232 | 8.5 | 7377.4232 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1475.4846 | 30% | 1 | 59.02% | 0% | 0% | 0% | 24.2343 | 0 | 0 | 0 | 24.2343 | 7527.9828 | 0 | 1505.5966 | 15.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.5089
2007-10-12 07:01 | 10 | 12 | 7 | 285 | 6823 | 35.96 | 6281.0638 | 0 | 0 | 6281.0638 | Heating | 5542.1151 | 8.5 | 5542.1151 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1108.423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5655.2195 | 0 | 1131.0439 | 11.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 08:01 | 10 | 12 | 8 | 285 | 6824 | 35.96 | 5025.8576 | 0 | 0 | 5025.8576 | Heating | 4434.5802 | 8.5 | 4434.5802 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 886.916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4525.0819 | 0 | 905.0164 | 9.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 09:01 | 10 | 12 | 9 | 285 | 6825 | 46.94 | 3322.253 | 0 | 0 | 3322.253 | Heating | 2931.3997 | 8.5 | 2931.3997 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 586.2799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2991.2242 | 0 | 598.2448 | 5.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 10:01 | 10 | 12 | 10 | 285 | 6826 | 51.08 | 1762.3942 | 0 | 0 | 1762.3942 | Heating | 1555.0537 | 8.5 | 1555.0537 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.0107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1586.7895 | 0 | 317.3579 | 3.174% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 11:01 | 10 | 12 | 11 | 285 | 6827 | 51.08 | 774.4719 | 8.4733 | 8.4733 | 765.9987 | Heating | 675.8812 | 8.5 | 675.8812 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.1762 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 689.6747 | 0 | 137.9349 | 1.379% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 12:01 | 10 | 12 | 12 | 285 | 6828 | 57.92 | 304.1361 | 43.7204 | 43.7204 | 260.4157 | Heating | 229.7786 | 8.5 | 229.7786 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.9557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 234.4679 | 0 | 46.8936 | 0.4689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 13:01 | 10 | 12 | 13 | 285 | 6829 | 60.98 | 199.0183 | 94.5406 | 94.5406 | 104.4777 | Heating | 92.1862 | 8.5 | 92.1862 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.4372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 94.0676 | 0 | 18.8135 | 0.1881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 14:01 | 10 | 12 | 14 | 285 | 6830 | 60.98 | 143.22 | 90.2804 | 90.2804 | 52.9396 | Heating | 46.7114 | 8.5 | 46.7114 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.3423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.6647 | 0 | 9.5329 | 0.09533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 15:01 | 10 | 12 | 15 | 285 | 6831 | 64.04 | 104.8503 | 81.4532 | 81.4532 | 23.3971 | Heating | 20.6445 | 8.5 | 20.6445 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.1289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 21.0658 | 0 | 4.2132 | 0.04213% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 16:01 | 10 | 12 | 16 | 285 | 6832 | 64.94 | 92.7228 | 66.4123 | 66.4123 | 26.3106 | Heating | 23.2152 | 8.5 | 23.2152 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.643 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 23.689 | 0 | 4.7378 | 0.04738% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 17:01 | 10 | 12 | 17 | 285 | 6833 | 64.94 | 94.4733 | 40.8812 | 40.8812 | 53.5921 | Heating | 47.2871 | 8.5 | 47.2871 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.4574 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 48.2522 | 0 | 9.6504 | 0.0965% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 18:01 | 10 | 12 | 18 | 285 | 6834 | 53.96 | 121.0378 | 0 | 0 | 121.0378 | Heating | 106.7981 | 8.5 | 106.7981 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.3596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 108.9777 | 0 | 21.7955 | 0.218% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 19:01 | 10 | 12 | 19 | 285 | 6835 | 51.98 | 387.9399 | 0 | 0 | 387.9399 | Heating | 342.2999 | 8.5 | 342.2999 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 68.46 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 349.2857 | 0 | 69.8571 | 0.6986% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 20:01 | 10 | 12 | 20 | 285 | 6836 | 51.98 | 701.4391 | 0 | 0 | 701.4391 | Heating | 618.9169 | 8.5 | 618.9169 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.7834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 631.5478 | 0 | 126.3096 | 1.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 21:01 | 10 | 12 | 21 | 285 | 6837 | 48.92 | 1148.0007 | 0 | 0 | 1148.0007 | Heating | 1012.9418 | 8.5 | 1012.9418 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.5884 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1033.6141 | 0 | 206.7228 | 2.067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 22:01 | 10 | 12 | 22 | 285 | 6838 | 50 | 210.8034 | 0 | 0 | 210.8034 | Heating | 186.003 | 8.5 | 186.003 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 37.2006 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 189.799 | 0 | 37.9598 | 0.3796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-12 23:01 | 10 | 12 | 23 | 285 | 6839 | 50 | 254.5457 | 0 | 0 | 254.5457 | Heating | 224.5992 | 8.5 | 224.5992 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.9198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 229.1828 | 0 | 45.8366 | 0.4584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 00:01 | 10 | 13 | 0 | 286 | 6840 | 51.98 | 303.175 | 0 | 0 | 303.175 | Heating | 267.5074 | 8.5 | 267.5074 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.5015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 272.9667 | 0 | 54.5933 | 0.5459% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 01:01 | 10 | 13 | 1 | 286 | 6841 | 49.46 | 328.4356 | 0 | 0 | 328.4356 | Heating | 289.7961 | 8.5 | 289.7961 | 0 | 4.4637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.9592 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 295.7103 | 0 | 59.1421 | 0.5914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 02:01 | 10 | 13 | 2 | 286 | 6842 | 49.46 | 329.7938 | 0 | 0 | 329.7938 | Heating | 290.9945 | 8.5 | 290.9945 | 0 | 4.4637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.1989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 296.9332 | 0 | 59.3866 | 0.5939% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 03:01 | 10 | 13 | 3 | 286 | 6843 | 48.92 | 330.4839 | 0 | 0 | 330.4839 | Heating | 291.6035 | 8.5 | 291.6035 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 58.3207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 297.5546 | 0 | 59.5109 | 0.5951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 04:01 | 10 | 13 | 4 | 286 | 6844 | 50 | 344.6614 | 0 | 0 | 344.6614 | Heating | 304.113 | 8.5 | 304.113 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 60.8226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 310.3194 | 0 | 62.0639 | 0.6206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 05:01 | 10 | 13 | 5 | 286 | 6845 | 50 | 321.9633 | 0 | 0 | 321.9633 | Heating | 284.0853 | 8.5 | 284.0853 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 56.8171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 289.8829 | 0 | 57.9766 | 0.5798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 06:01 | 10 | 13 | 6 | 286 | 6846 | 48.92 | 292.5723 | 0 | 0 | 292.5723 | Heating | 258.152 | 8.5 | 258.152 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.6304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 263.4204 | 0 | 52.6841 | 0.5268% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 07:01 | 10 | 13 | 7 | 286 | 6847 | 48.92 | 287.2659 | 0 | 0 | 287.2659 | Heating | 253.4699 | 8.5 | 253.4699 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.694 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 258.6428 | 0 | 51.7286 | 0.5173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 08:01 | 10 | 13 | 8 | 286 | 6848 | 48.92 | 3179.6105 | 0 | 0 | 3179.6105 | Heating | 2805.5387 | 8.5 | 2805.5387 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 561.1077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2862.7946 | 0 | 572.5589 | 5.726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 09:01 | 10 | 13 | 9 | 286 | 6849 | 55.04 | 1989.8116 | 0 | 0 | 1989.8116 | Heating | 1755.7161 | 8.5 | 1755.7161 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 351.1432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1791.547 | 0 | 358.3094 | 3.583% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 10:01 | 10 | 13 | 10 | 286 | 6850 | 57.92 | 1245.4924 | 0 | 0 | 1245.4924 | Heating | 1098.9638 | 8.5 | 1098.9638 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.7928 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1121.3917 | 0 | 224.2783 | 2.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 11:01 | 10 | 13 | 11 | 286 | 6851 | 57.92 | 996.1095 | 0 | 0 | 996.1095 | Heating | 878.9202 | 8.5 | 878.9202 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 896.8573 | 0 | 179.3715 | 1.794% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 12:01 | 10 | 13 | 12 | 286 | 6852 | 64.04 | 602.8827 | 0 | 0 | 602.8827 | Heating | 531.9553 | 8.5 | 531.9553 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.3911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.8115 | 0 | 108.5623 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 13:01 | 10 | 13 | 13 | 286 | 6853 | 64.94 | 442.4903 | 0 | 0 | 442.4903 | Heating | 390.4326 | 8.5 | 390.4326 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.0865 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 398.4006 | 0 | 79.6801 | 0.7968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 14:01 | 10 | 13 | 14 | 286 | 6854 | 64.94 | 275.285 | 0 | 0 | 275.285 | Heating | 242.8985 | 8.5 | 242.8985 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.5797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 247.8557 | 0 | 49.5711 | 0.4957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 15:01 | 10 | 13 | 15 | 286 | 6855 | 66.92 | 131.7714 | 0 | 0 | 131.7714 | Heating | 116.2689 | 8.5 | 116.2689 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 23.2538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 118.6417 | 0 | 23.7283 | 0.2373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 16:01 | 10 | 13 | 16 | 286 | 6856 | 66.02 | 93.8476 | 0 | 0 | 93.8476 | Heating | 82.8067 | 8.5 | 82.8067 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.5613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 84.4967 | 0 | 16.8993 | 0.169% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 17:01 | 10 | 13 | 17 | 286 | 6857 | 66.02 | 450.8841 | 0 | 0 | 450.8841 | Heating | 397.8389 | 8.5 | 397.8389 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 79.5678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 405.9581 | 0 | 81.1916 | 0.8119% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 18:01 | 10 | 13 | 18 | 286 | 6858 | 60.98 | 717.0656 | 0 | 0 | 717.0656 | Heating | 632.7049 | 8.5 | 632.7049 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 645.6173 | 0 | 129.1235 | 1.291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 19:01 | 10 | 13 | 19 | 286 | 6859 | 60.08 | 46.7948 | 0 | 0 | 46.7948 | Heating | 41.2895 | 8.5 | 41.2895 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.2579 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.1321 | 0 | 8.4264 | 0.08426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 20:01 | 10 | 13 | 20 | 286 | 6860 | 60.08 | 48.4608 | 0 | 0 | 48.4608 | Heating | 42.7595 | 8.5 | 42.7595 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.5519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.6322 | 0 | 8.7264 | 0.08726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 21:01 | 10 | 13 | 21 | 286 | 6861 | 57.02 | 49.7452 | 0 | 0 | 49.7452 | Heating | 43.8928 | 8.5 | 43.8928 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.7786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 44.7886 | 0 | 8.9577 | 0.08958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 22:01 | 10 | 13 | 22 | 286 | 6862 | 55.94 | 64.8238 | 0 | 0 | 64.8238 | Heating | 57.1975 | 8.5 | 57.1975 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 11.4395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 58.3648 | 0 | 11.673 | 0.1167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-13 23:01 | 10 | 13 | 23 | 286 | 6863 | 55.94 | 84.018 | 0 | 0 | 84.018 | Heating | 74.1335 | 8.5 | 74.1335 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.8267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 75.6464 | 0 | 15.1293 | 0.1513% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 00:01 | 10 | 14 | 0 | 287 | 6864 | 53.96 | 103.7622 | 0 | 0 | 103.7622 | Heating | 91.5549 | 8.5 | 91.5549 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.311 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 93.4234 | 0 | 18.6847 | 0.1868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 01:01 | 10 | 14 | 1 | 287 | 6865 | 53.06 | 112.6843 | 0 | 0 | 112.6843 | Heating | 99.4273 | 8.5 | 99.4273 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.8855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 101.4564 | 0 | 20.2913 | 0.2029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 02:01 | 10 | 14 | 2 | 287 | 6866 | 53.06 | 118.484 | 0 | 0 | 118.484 | Heating | 104.5447 | 8.5 | 104.5447 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.9089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 106.6783 | 0 | 21.3357 | 0.2134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 03:01 | 10 | 14 | 3 | 287 | 6867 | 53.06 | 123.0119 | 0 | 0 | 123.0119 | Heating | 108.5399 | 8.5 | 108.5399 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 110.755 | 0 | 22.151 | 0.2215% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 04:01 | 10 | 14 | 4 | 287 | 6868 | 53.06 | 123.3982 | 0 | 0 | 123.3982 | Heating | 108.8807 | 8.5 | 108.8807 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 21.7761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 111.1028 | 0 | 22.2206 | 0.2222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 05:01 | 10 | 14 | 5 | 287 | 6869 | 53.06 | 115.3443 | 0 | 0 | 115.3443 | Heating | 101.7744 | 8.5 | 101.7744 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.3549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 103.8514 | 0 | 20.7703 | 0.2077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 06:01 | 10 | 14 | 6 | 287 | 6870 | 53.96 | 1810.0701 | 88.2426 | 88.2426 | 1721.8275 | Heating | 1519.2595 | 8.5 | 1519.2595 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 303.8519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1550.2648 | 0 | 310.053 | 3.101% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 07:01 | 10 | 14 | 7 | 287 | 6871 | 55.4 | 1345.2195 | 0 | 0 | 1345.2195 | Heating | 1186.9584 | 8.5 | 1186.9584 | 0 | 5.0667 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.3917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1211.182 | 0 | 242.2364 | 2.422% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 08:01 | 10 | 14 | 8 | 287 | 6872 | 55.04 | 803.1581 | 0 | 0 | 803.1581 | Heating | 708.6689 | 8.5 | 708.6689 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.7338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 723.1315 | 0 | 144.6263 | 1.446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 09:01 | 10 | 14 | 9 | 287 | 6873 | 59 | 153.9359 | 17.0273 | 17.0273 | 136.9086 | Heating | 120.8017 | 8.5 | 120.8017 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 24.1603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 123.2671 | 0 | 24.6534 | 0.2465% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 10:01 | 10 | 14 | 10 | 287 | 6874 | 62.06 | 105.8577 | 74.2888 | 74.2888 | 31.5689 | Heating | 27.8549 | 8.5 | 27.8549 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 5.571 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 28.4234 | 0 | 5.6847 | 0.05685% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 11:01 | 10 | 14 | 11 | 287 | 6875 | 62.06 | 69.7409 | 196.0912 | 196.0912 | -126.3503 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 239.6671 | 239.6671 | 0 | 8.5 | 0 | 39.9445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 234.8737 | 46.9747 | 0.4697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 12:01 | 10 | 14 | 12 | 287 | 6876 | 62.06 | 38.9118 | 223.4936 | 223.4936 | -184.5818 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 273.1588 | 273.1588 | 0 | 8.5 | 0 | 45.5265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 267.6956 | 53.5391 | 0.5354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 13:01 | 10 | 14 | 13 | 287 | 6877 | 59 | 19.7167 | 415.8299 | 415.8299 | -396.1132 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 508.2366 | 508.2366 | 0 | 8.5 | 0 | 84.7061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 498.0718 | 99.6144 | 0.9961% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 14:01 | 10 | 14 | 14 | 287 | 6878 | 59 | 4.2327 | 1771.7593 | 1771.7593 | -1767.5267 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2165.4836 | 2165.4836 | 0 | 8.5 | 0 | 360.9139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2122.174 | 424.4348 | 4.244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 15:01 | 10 | 14 | 15 | 287 | 6879 | 57.92 | 5.3579 | 1773.4218 | 1773.4218 | -1768.0639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2167.5155 | 2167.5155 | 0 | 8.5 | 0 | 361.2526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2124.1652 | 424.833 | 4.248% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 16:01 | 10 | 14 | 16 | 287 | 6880 | 57.2 | 6.1564 | 1433.2489 | 1433.2489 | -1427.0925 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1751.7486 | 1751.7486 | 0 | 8.5 | 0 | 291.9581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1716.7137 | 343.3427 | 3.433% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 17:01 | 10 | 14 | 17 | 287 | 6881 | 57.02 | 2.2657 | 1045.7504 | 1045.7504 | -1043.4846 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1278.1393 | 1278.1393 | 0 | 8.5 | 0 | 213.0232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1252.5766 | 250.5153 | 2.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 18:01 | 10 | 14 | 18 | 287 | 6882 | 55.04 | 2.9466 | 182.8747 | 182.8747 | -179.928 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 223.5135 | 223.5135 | 0 | 8.5 | 0 | 37.2522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 219.0432 | 43.8086 | 0.4381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 19:01 | 10 | 14 | 19 | 287 | 6883 | 53.06 | 19.5767 | 118.1649 | 118.1649 | -98.5882 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 144.4238 | 144.4238 | 0 | 8.5 | 0 | 24.0706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 141.5353 | 28.3071 | 0.2831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 20:01 | 10 | 14 | 20 | 287 | 6884 | 53.06 | 67.6426 | 15.4852 | 15.4852 | 52.1574 | Heating | 46.0212 | 8.5 | 46.0212 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.2042 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 46.9604 | 0 | 9.3921 | 0.09392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 21:01 | 10 | 14 | 21 | 287 | 6885 | 50 | 88.0236 | 1.9829 | 1.9829 | 86.0408 | Heating | 75.9183 | 8.5 | 75.9183 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.1837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.4677 | 0 | 15.4935 | 0.1549% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 22:01 | 10 | 14 | 22 | 287 | 6886 | 48.92 | 148.5434 | 0 | 0 | 148.5434 | Heating | 131.0677 | 8.5 | 131.0677 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.2135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 133.7426 | 0 | 26.7485 | 0.2675% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-14 23:01 | 10 | 14 | 23 | 287 | 6887 | 48.92 | 226.483 | 0 | 0 | 226.483 | Heating | 199.838 | 8.5 | 199.838 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.9676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 203.9163 | 0 | 40.7833 | 0.4078% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 00:01 | 10 | 15 | 0 | 288 | 6888 | 46.04 | 307.4104 | 0 | 0 | 307.4104 | Heating | 271.2445 | 8.5 | 271.2445 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.2489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 276.7801 | 0 | 55.356 | 0.5536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 01:01 | 10 | 15 | 1 | 288 | 6889 | 44.06 | 366.9929 | 0 | 0 | 366.9929 | Heating | 323.8173 | 8.5 | 323.8173 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.7635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 330.4258 | 0 | 66.0852 | 0.6609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 02:01 | 10 | 15 | 2 | 288 | 6890 | 44.06 | 425.9403 | 0 | 0 | 425.9403 | Heating | 375.8297 | 8.5 | 375.8297 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.1659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 383.4997 | 0 | 76.6999 | 0.767% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 03:01 | 10 | 15 | 3 | 288 | 6891 | 39.02 | 515.7743 | 0 | 0 | 515.7743 | Heating | 455.095 | 8.5 | 455.095 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 464.3827 | 0 | 92.8765 | 0.9288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 04:01 | 10 | 15 | 4 | 288 | 6892 | 39.02 | 597.9663 | 0 | 0 | 597.9663 | Heating | 527.6173 | 8.5 | 527.6173 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.5235 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 538.385 | 0 | 107.677 | 1.077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 05:01 | 10 | 15 | 5 | 288 | 6893 | 39.02 | 635.0044 | 0 | 0 | 635.0044 | Heating | 560.298 | 8.5 | 560.298 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.0596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 571.7327 | 0 | 114.3465 | 1.143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 06:01 | 10 | 15 | 6 | 288 | 6894 | 37.94 | 6244.8968 | 0 | 0 | 6244.8968 | Heating | 5510.2031 | 8.5 | 5510.2031 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1102.0406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5622.6562 | 0 | 1124.5312 | 11.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 07:01 | 10 | 15 | 7 | 288 | 6895 | 39.02 | 4251.64 | 0 | 0 | 4251.64 | Heating | 3751.4471 | 8.5 | 3751.4471 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.2894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3828.0072 | 0 | 765.6014 | 7.656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 08:01 | 10 | 15 | 8 | 288 | 6896 | 39.02 | 2981.1981 | 0 | 0 | 2981.1981 | Heating | 2630.4689 | 8.5 | 2630.4689 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 526.0938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2684.152 | 0 | 536.8304 | 5.368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 09:01 | 10 | 15 | 9 | 288 | 6897 | 46.94 | 1809.4272 | 1.8379 | 1.8379 | 1807.5893 | Heating | 1594.9317 | 8.5 | 1594.9317 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 318.9863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1627.4813 | 0 | 325.4963 | 3.255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 10:01 | 10 | 15 | 10 | 288 | 6898 | 48.92 | 1200.5705 | 25.8025 | 25.8025 | 1174.768 | Heating | 1036.56 | 8.5 | 1036.56 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1057.7143 | 0 | 211.5429 | 2.115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 11:01 | 10 | 15 | 11 | 288 | 6899 | 48.92 | 744.3166 | 82.0987 | 82.0987 | 662.2179 | Heating | 584.3099 | 8.5 | 584.3099 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 596.2346 | 0 | 119.2469 | 1.192% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 12:01 | 10 | 15 | 12 | 288 | 6900 | 51.98 | 434.768 | 164.8439 | 164.8439 | 269.9241 | Heating | 238.1683 | 8.5 | 238.1683 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.6337 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 243.0289 | 0 | 48.6058 | 0.4861% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 13:01 | 10 | 15 | 13 | 288 | 6901 | 55.04 | 317.9212 | 264.9058 | 264.9058 | 53.0154 | Heating | 46.7783 | 8.5 | 46.7783 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 9.3557 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 47.7329 | 0 | 9.5466 | 0.09547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 14:01 | 10 | 15 | 14 | 288 | 6902 | 55.04 | 363.4932 | 253.4892 | 253.4892 | 110.004 | Heating | 97.0624 | 8.5 | 97.0624 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.4125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 99.0432 | 0 | 19.8086 | 0.1981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 15:01 | 10 | 15 | 15 | 288 | 6903 | 55.94 | 321.8382 | 216.3756 | 216.3756 | 105.4626 | Heating | 93.0552 | 8.5 | 93.0552 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 18.611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 94.9543 | 0 | 18.9909 | 0.1899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 16:01 | 10 | 15 | 16 | 288 | 6904 | 55.04 | 303.4012 | 177.3928 | 177.3928 | 126.0084 | Heating | 111.1839 | 8.5 | 111.1839 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.2368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 113.4529 | 0 | 22.6906 | 0.2269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 17:01 | 10 | 15 | 17 | 288 | 6905 | 55.04 | 380.5921 | 112.7169 | 112.7169 | 267.8752 | Heating | 236.3605 | 8.5 | 236.3605 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.2721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 241.1841 | 0 | 48.2368 | 0.4824% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 18:01 | 10 | 15 | 18 | 288 | 6906 | 46.94 | 811.5658 | 34.2377 | 34.2377 | 777.3281 | Heating | 685.8777 | 8.5 | 685.8777 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.1755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 699.8752 | 0 | 139.975 | 1.4% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 19:01 | 10 | 15 | 19 | 288 | 6907 | 42.08 | 1345.4636 | 19.6899 | 19.6899 | 1325.7737 | Heating | 1169.8003 | 8.5 | 1169.8003 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.9601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1193.6738 | 0 | 238.7348 | 2.387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 20:01 | 10 | 15 | 20 | 288 | 6908 | 42.08 | 2113.4618 | 0.022598 | 0.022598 | 2113.4392 | Heating | 1864.7993 | 8.5 | 1864.7993 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.9599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1902.8565 | 0 | 380.5713 | 3.806% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 21:01 | 10 | 15 | 21 | 288 | 6909 | 39.92 | 565.31 | 0 | 0 | 565.31 | Heating | 498.803 | 8.5 | 498.803 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.7606 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 508.9826 | 0 | 101.7965 | 1.018% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 22:01 | 10 | 15 | 22 | 288 | 6910 | 35.06 | 634.2989 | 0 | 0 | 634.2989 | Heating | 559.6755 | 8.5 | 559.6755 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.9351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 571.0974 | 0 | 114.2195 | 1.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-15 23:01 | 10 | 15 | 23 | 288 | 6911 | 35.06 | 737.8329 | 0 | 0 | 737.8329 | Heating | 651.029 | 8.5 | 651.029 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.2058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 664.3154 | 0 | 132.8631 | 1.329% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 00:01 | 10 | 16 | 0 | 289 | 6912 | 33.98 | 824.6215 | 0 | 0 | 824.6215 | Heating | 727.6072 | 8.5 | 727.6072 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.5214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 742.4563 | 0 | 148.4913 | 1.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 01:01 | 10 | 16 | 1 | 289 | 6913 | 35.06 | 862.9948 | 0 | 0 | 862.9948 | Heating | 761.466 | 8.5 | 761.466 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.2932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 777.0061 | 0 | 155.4012 | 1.554% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 02:01 | 10 | 16 | 2 | 289 | 6914 | 35.06 | 895.1233 | 0 | 0 | 895.1233 | Heating | 789.8147 | 8.5 | 789.8147 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.9629 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 805.9334 | 0 | 161.1867 | 1.612% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 03:01 | 10 | 16 | 3 | 289 | 6915 | 33.08 | 914.7754 | 0 | 0 | 914.7754 | Heating | 807.1548 | 8.5 | 807.1548 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 161.431 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 823.6273 | 0 | 164.7255 | 1.647% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 04:01 | 10 | 16 | 4 | 289 | 6916 | 30.92 | 876.1792 | 0 | 0 | 876.1792 | Heating | 773.0993 | 8.5 | 773.0993 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.6199 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 788.8768 | 0 | 157.7754 | 1.578% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 05:01 | 10 | 16 | 5 | 289 | 6917 | 30.92 | 836.6672 | 0 | 0 | 836.6672 | Heating | 738.2358 | 8.5 | 738.2358 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 147.6472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 753.3018 | 0 | 150.6604 | 1.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 06:01 | 10 | 16 | 6 | 289 | 6918 | 30.02 | 7572.5214 | 0 | 0 | 7572.5214 | Heating | 6681.6365 | 8.5 | 6681.6365 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1336.3273 | 30% | 1 | 53.45% | 0% | 0% | 0% | 19.2966 | 0 | 0 | 0 | 19.2966 | 6817.9964 | 0 | 1363.5993 | 13.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.5711
2007-10-16 07:01 | 10 | 16 | 7 | 289 | 6919 | 30.02 | 5450.1219 | 0 | 0 | 5450.1219 | Heating | 4808.9311 | 8.5 | 4808.9311 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 961.7862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4907.0725 | 0 | 981.4145 | 9.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 08:01 | 10 | 16 | 8 | 289 | 6920 | 32 | 4223.0019 | 0 | 0 | 4223.0019 | Heating | 3726.1782 | 8.5 | 3726.1782 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.2356 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3802.2226 | 0 | 760.4445 | 7.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 09:01 | 10 | 16 | 9 | 289 | 6921 | 42.98 | 3004.9648 | 0 | 0 | 3004.9648 | Heating | 2651.4395 | 8.5 | 2651.4395 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 530.2879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2705.5506 | 0 | 541.1101 | 5.411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 10:01 | 10 | 16 | 10 | 289 | 6922 | 48.92 | 2184.3662 | 0 | 0 | 2184.3662 | Heating | 1927.3819 | 8.5 | 1927.3819 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.4764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1966.7162 | 0 | 393.3432 | 3.933% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 11:01 | 10 | 16 | 11 | 289 | 6923 | 48.92 | 1531.9217 | 0.87933 | 0.87933 | 1531.0423 | Heating | 1350.9197 | 8.5 | 1350.9197 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 270.1839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1378.4895 | 0 | 275.6979 | 2.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 12:01 | 10 | 16 | 12 | 289 | 6924 | 57.02 | 1284.4636 | 1.7059 | 1.7059 | 1282.7578 | Heating | 1131.8451 | 8.5 | 1131.8451 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 226.369 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1154.944 | 0 | 230.9888 | 2.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 13:01 | 10 | 16 | 13 | 289 | 6925 | 60.08 | 1077.6548 | 12.3767 | 12.3767 | 1065.2781 | Heating | 939.9512 | 8.5 | 939.9512 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 187.9902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 959.1339 | 0 | 191.8268 | 1.918% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 14:01 | 10 | 16 | 14 | 289 | 6926 | 60.08 | 917.5237 | 32.0958 | 32.0958 | 885.4279 | Heating | 781.2599 | 8.5 | 781.2599 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 797.204 | 0 | 159.4408 | 1.594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 15:01 | 10 | 16 | 15 | 289 | 6927 | 62.96 | 779.4674 | 38.9586 | 38.9586 | 740.5088 | Heating | 653.3901 | 8.5 | 653.3901 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 666.7246 | 0 | 133.3449 | 1.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 16:01 | 10 | 16 | 16 | 289 | 6928 | 62.96 | 765.4178 | 63.4352 | 63.4352 | 701.9826 | Heating | 619.3964 | 8.5 | 619.3964 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.8793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 632.0372 | 0 | 126.4074 | 1.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 17:01 | 10 | 16 | 17 | 289 | 6929 | 62.96 | 865.8958 | 20.502 | 20.502 | 845.3939 | Heating | 745.9358 | 8.5 | 745.9358 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.1872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 761.1589 | 0 | 152.2318 | 1.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 18:01 | 10 | 16 | 18 | 289 | 6930 | 57.92 | 1228.4985 | 0 | 0 | 1228.4985 | Heating | 1083.9693 | 8.5 | 1083.9693 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 216.7939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1106.0911 | 0 | 221.2182 | 2.212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 19:01 | 10 | 16 | 19 | 289 | 6931 | 57.02 | 1582.0797 | 0 | 0 | 1582.0797 | Heating | 1395.9527 | 8.5 | 1395.9527 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.1905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1424.4415 | 0 | 284.8883 | 2.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 20:01 | 10 | 16 | 20 | 289 | 6932 | 57.02 | 1863.473 | 0 | 0 | 1863.473 | Heating | 1644.2409 | 8.5 | 1644.2409 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.8482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1677.7968 | 0 | 335.5594 | 3.356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 21:01 | 10 | 16 | 21 | 289 | 6933 | 53.96 | 493.8404 | 0 | 0 | 493.8404 | Heating | 435.7416 | 8.5 | 435.7416 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.1483 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 444.6342 | 0 | 88.9268 | 0.8893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 22:01 | 10 | 16 | 22 | 289 | 6934 | 53.06 | 590.3081 | 0 | 0 | 590.3081 | Heating | 520.8601 | 8.5 | 520.8601 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 104.172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 531.4899 | 0 | 106.298 | 1.063% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-16 23:01 | 10 | 16 | 23 | 289 | 6935 | 53.06 | 703.0044 | 0 | 0 | 703.0044 | Heating | 620.298 | 8.5 | 620.298 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.0596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 632.9571 | 0 | 126.5914 | 1.266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 00:01 | 10 | 17 | 0 | 290 | 6936 | 51.08 | 775.6257 | 0 | 0 | 775.6257 | Heating | 684.3756 | 8.5 | 684.3756 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.8751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 698.3425 | 0 | 139.6685 | 1.397% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 01:01 | 10 | 17 | 1 | 290 | 6937 | 51.08 | 765.7676 | 0 | 0 | 765.7676 | Heating | 675.6773 | 8.5 | 675.6773 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.1355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 689.4666 | 0 | 137.8933 | 1.379% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 02:01 | 10 | 17 | 2 | 290 | 6938 | 51.08 | 757.3076 | 0 | 0 | 757.3076 | Heating | 668.2126 | 8.5 | 668.2126 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.6425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 681.8496 | 0 | 136.3699 | 1.364% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 03:01 | 10 | 17 | 3 | 290 | 6939 | 48.02 | 768.8216 | 0 | 0 | 768.8216 | Heating | 678.372 | 8.5 | 678.372 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.6744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 692.2163 | 0 | 138.4433 | 1.384% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 04:01 | 10 | 17 | 4 | 290 | 6940 | 46.94 | 759.5785 | 0 | 0 | 759.5785 | Heating | 670.2163 | 8.5 | 670.2163 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 134.0433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 683.8942 | 0 | 136.7788 | 1.368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 05:01 | 10 | 17 | 5 | 290 | 6941 | 46.94 | 747.1304 | 0 | 0 | 747.1304 | Heating | 659.2327 | 8.5 | 659.2327 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.8465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 672.6864 | 0 | 134.5373 | 1.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 06:01 | 10 | 17 | 6 | 290 | 6942 | 50 | 6976.0606 | 0 | 0 | 6976.0606 | Heating | 6155.3476 | 8.5 | 6155.3476 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1231.0695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6280.9669 | 0 | 1256.1934 | 12.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 07:01 | 10 | 17 | 7 | 290 | 6943 | 50 | 4989.4597 | 0 | 0 | 4989.4597 | Heating | 4402.4645 | 8.5 | 4402.4645 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 880.4929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4492.3107 | 0 | 898.4621 | 8.985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 08:01 | 10 | 17 | 8 | 290 | 6944 | 50 | 3804.5323 | 0 | 0 | 3804.5323 | Heating | 3356.9403 | 8.5 | 3356.9403 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 671.3881 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3425.4493 | 0 | 685.0899 | 6.851% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 09:01 | 10 | 17 | 9 | 290 | 6945 | 53.06 | 2640.4199 | 0 | 0 | 2640.4199 | Heating | 2329.7822 | 8.5 | 2329.7822 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 465.9564 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2377.3288 | 0 | 475.4658 | 4.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 10:01 | 10 | 17 | 10 | 290 | 6946 | 57.02 | 1907.6501 | 0 | 0 | 1907.6501 | Heating | 1683.2207 | 8.5 | 1683.2207 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.6441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1717.5722 | 0 | 343.5144 | 3.435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 11:01 | 10 | 17 | 11 | 290 | 6947 | 57.02 | 1112.2193 | 1.3312 | 1.3312 | 1110.8881 | Heating | 980.1954 | 8.5 | 980.1954 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.0391 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1000.1994 | 0 | 200.0399 | 2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 12:01 | 10 | 17 | 12 | 290 | 6948 | 59 | 686.5211 | 12.4113 | 12.4113 | 674.1097 | Heating | 594.8027 | 8.5 | 594.8027 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.9605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 606.9415 | 0 | 121.3883 | 1.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 13:01 | 10 | 17 | 13 | 290 | 6949 | 62.06 | 433.0859 | 38.3288 | 38.3288 | 394.7571 | Heating | 348.3151 | 8.5 | 348.3151 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 69.663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 355.4235 | 0 | 71.0847 | 0.7108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 14:01 | 10 | 17 | 14 | 290 | 6950 | 62.06 | 329.0727 | 61.2243 | 61.2243 | 267.8483 | Heating | 236.3368 | 8.5 | 236.3368 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.2674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 241.16 | 0 | 48.232 | 0.4823% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 15:01 | 10 | 17 | 15 | 290 | 6951 | 66.92 | 312.2998 | 86.2584 | 86.2584 | 226.0413 | Heating | 199.4482 | 8.5 | 199.4482 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.8896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 203.5186 | 0 | 40.7037 | 0.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 16:01 | 10 | 17 | 16 | 290 | 6952 | 66.92 | 345.1592 | 97.2574 | 97.2574 | 247.9018 | Heating | 218.7369 | 8.5 | 218.7369 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.7474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 223.2009 | 0 | 44.6402 | 0.4464% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 17:01 | 10 | 17 | 17 | 290 | 6953 | 66.92 | 635.3484 | 31.3487 | 31.3487 | 603.9996 | Heating | 532.9408 | 8.5 | 532.9408 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.5882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 543.8172 | 0 | 108.7634 | 1.088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 18:01 | 10 | 17 | 18 | 290 | 6954 | 66.92 | 1097.3996 | 0.093915 | 0.093915 | 1097.3057 | Heating | 968.2109 | 8.5 | 968.2109 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 193.6422 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 987.9703 | 0 | 197.5941 | 1.976% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 19:01 | 10 | 17 | 19 | 290 | 6955 | 66.02 | 1373.8567 | 0 | 0 | 1373.8567 | Heating | 1212.2265 | 8.5 | 1212.2265 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.4453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1236.9658 | 0 | 247.3932 | 2.474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 20:01 | 10 | 17 | 20 | 290 | 6956 | 66.02 | 1608.3261 | 0 | 0 | 1608.3261 | Heating | 1419.1113 | 8.5 | 1419.1113 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 283.8223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1448.0727 | 0 | 289.6145 | 2.896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 21:01 | 10 | 17 | 21 | 290 | 6957 | 64.94 | 433.7415 | 0 | 0 | 433.7415 | Heating | 382.7131 | 8.5 | 382.7131 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.5426 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 390.5235 | 0 | 78.1047 | 0.781% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 22:01 | 10 | 17 | 22 | 290 | 6958 | 62.96 | 475.8101 | 0 | 0 | 475.8101 | Heating | 419.8325 | 8.5 | 419.8325 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.9665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 428.4005 | 0 | 85.6801 | 0.8568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-17 23:01 | 10 | 17 | 23 | 290 | 6959 | 62.96 | 521.3212 | 0 | 0 | 521.3212 | Heating | 459.9893 | 8.5 | 459.9893 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.9979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 469.3769 | 0 | 93.8754 | 0.9388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 00:01 | 10 | 18 | 0 | 291 | 6960 | 62.06 | 574.3412 | 0 | 0 | 574.3412 | Heating | 506.7717 | 8.5 | 506.7717 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.3543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 517.1139 | 0 | 103.4228 | 1.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 01:01 | 10 | 18 | 1 | 291 | 6961 | 62.06 | 656.9022 | 0 | 0 | 656.9022 | Heating | 579.6196 | 8.5 | 579.6196 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.9239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 591.4486 | 0 | 118.2897 | 1.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 02:01 | 10 | 18 | 2 | 291 | 6962 | 62.06 | 743.1838 | 0 | 0 | 743.1838 | Heating | 655.7504 | 8.5 | 655.7504 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.1501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 669.133 | 0 | 133.8266 | 1.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 03:01 | 10 | 18 | 3 | 291 | 6963 | 60.98 | 818.6122 | 0 | 0 | 818.6122 | Heating | 722.3049 | 8.5 | 722.3049 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 144.461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 737.0458 | 0 | 147.4092 | 1.474% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 04:01 | 10 | 18 | 4 | 291 | 6964 | 60.98 | 868.2401 | 0 | 0 | 868.2401 | Heating | 766.0942 | 8.5 | 766.0942 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 153.2188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 781.7288 | 0 | 156.3458 | 1.563% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 05:01 | 10 | 18 | 5 | 291 | 6965 | 60.98 | 892.1645 | 0 | 0 | 892.1645 | Heating | 787.2039 | 8.5 | 787.2039 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.4408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 803.2693 | 0 | 160.6539 | 1.607% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 06:01 | 10 | 18 | 6 | 291 | 6966 | 60.98 | 8074.3054 | 0 | 0 | 8074.3054 | Heating | 7124.3871 | 8.5 | 7124.3871 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1424.8774 | 30% | 1 | 57% | 0% | 0% | 0% | 22.365 | 0 | 0 | 0 | 22.365 | 7269.7828 | 0 | 1453.9566 | 14.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.6396
2007-10-18 07:01 | 10 | 18 | 7 | 291 | 6967 | 60.98 | 5782.7444 | 0 | 0 | 5782.7444 | Heating | 5102.4215 | 8.5 | 5102.4215 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1020.4843 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5206.5526 | 0 | 1041.3105 | 10.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 08:01 | 10 | 18 | 8 | 291 | 6968 | 60.98 | 4161.7829 | 0 | 0 | 4161.7829 | Heating | 3672.1614 | 8.5 | 3672.1614 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 734.4323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3747.1034 | 0 | 749.4207 | 7.494% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 09:01 | 10 | 18 | 9 | 291 | 6969 | 64.04 | 2656.7854 | 0 | 0 | 2656.7854 | Heating | 2344.2224 | 8.5 | 2344.2224 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 468.8445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2392.0636 | 0 | 478.4127 | 4.784% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 10:01 | 10 | 18 | 10 | 291 | 6970 | 66.02 | 1925.5395 | 4.0724 | 4.0724 | 1921.4671 | Heating | 1695.4122 | 8.5 | 1695.4122 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.0824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1730.0124 | 0 | 346.0025 | 3.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 11:01 | 10 | 18 | 11 | 291 | 6971 | 66.02 | 1352.8989 | 39.2133 | 39.2133 | 1313.6856 | Heating | 1159.1344 | 8.5 | 1159.1344 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.8269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1182.7902 | 0 | 236.558 | 2.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 12:01 | 10 | 18 | 12 | 291 | 6972 | 66.92 | 836.8509 | 189.0299 | 189.0299 | 647.821 | Heating | 571.6068 | 8.5 | 571.6068 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.3214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 583.2722 | 0 | 116.6544 | 1.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 13:01 | 10 | 18 | 13 | 291 | 6973 | 69.08 | 448.2867 | 362.6261 | 362.6261 | 85.6605 | Heating | 75.5828 | 8.5 | 75.5828 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 15.1166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 77.1253 | 0 | 15.4251 | 0.1543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 14:01 | 10 | 18 | 14 | 291 | 6974 | 69.08 | 283.8872 | 453.6346 | 453.6346 | -169.7474 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 554.4423 | 554.4423 | 0 | 8.5 | 0 | 92.407 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 543.3534 | 108.6707 | 1.087% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 15:01 | 10 | 18 | 15 | 291 | 6975 | 69.08 | 214.8729 | 460.1582 | 460.1582 | -245.2853 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 562.4156 | 562.4156 | 0 | 8.5 | 0 | 93.7359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 551.1673 | 110.2335 | 1.102% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 16:01 | 10 | 18 | 16 | 291 | 6976 | 66.92 | 235.4049 | 380.8754 | 380.8754 | -145.4705 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 465.5144 | 465.5144 | 0 | 8.5 | 0 | 77.5857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 456.2041 | 91.2408 | 0.9124% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 17:01 | 10 | 18 | 17 | 291 | 6977 | 66.92 | 543.8686 | 231.6088 | 231.6088 | 312.2599 | Heating | 275.5234 | 8.5 | 275.5234 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.1047 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 281.1463 | 0 | 56.2293 | 0.5623% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 18:01 | 10 | 18 | 18 | 291 | 6978 | 64.94 | 1306.5354 | 95.1312 | 95.1312 | 1211.4042 | Heating | 1068.8861 | 8.5 | 1068.8861 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 213.7772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1090.7001 | 0 | 218.14 | 2.181% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 19:01 | 10 | 18 | 19 | 291 | 6979 | 62.96 | 2143.6706 | 52.2878 | 52.2878 | 2091.3828 | Heating | 1845.3378 | 8.5 | 1845.3378 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.0676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1882.9978 | 0 | 376.5996 | 3.766% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 20:01 | 10 | 18 | 20 | 291 | 6980 | 62.96 | 2772.1454 | 6.9991 | 6.9991 | 2765.1463 | Heating | 2439.8349 | 8.5 | 2439.8349 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 487.967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2489.6275 | 0 | 497.9255 | 4.979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 21:01 | 10 | 18 | 21 | 291 | 6981 | 60.98 | 681.1622 | 0 | 0 | 681.1622 | Heating | 601.0254 | 8.5 | 601.0254 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.2051 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 613.2913 | 0 | 122.6583 | 1.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 22:01 | 10 | 18 | 22 | 291 | 6982 | 60.98 | 741.0623 | 0 | 0 | 741.0623 | Heating | 653.8785 | 8.5 | 653.8785 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.7757 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 667.2229 | 0 | 133.4446 | 1.334% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-18 23:01 | 10 | 18 | 23 | 291 | 6983 | 60.98 | 802.7521 | 0 | 0 | 802.7521 | Heating | 708.3107 | 8.5 | 708.3107 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.6621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 722.766 | 0 | 144.5532 | 1.446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 00:01 | 10 | 19 | 0 | 292 | 6984 | 62.6 | 873.0839 | 0 | 0 | 873.0839 | Heating | 770.3681 | 8.5 | 770.3681 | 0 | 5.9758 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.0736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 786.0899 | 0 | 157.218 | 1.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 01:01 | 10 | 19 | 1 | 292 | 6985 | 60.08 | 950.2782 | 0 | 0 | 950.2782 | Heating | 838.4808 | 8.5 | 838.4808 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 167.6962 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 855.5926 | 0 | 171.1185 | 1.711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 02:01 | 10 | 19 | 2 | 292 | 6986 | 60.08 | 1048.1323 | 0 | 0 | 1048.1323 | Heating | 924.8226 | 8.5 | 924.8226 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.9645 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 943.6966 | 0 | 188.7393 | 1.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 03:01 | 10 | 19 | 3 | 292 | 6987 | 57.2 | 1157.1877 | 0 | 0 | 1157.1877 | Heating | 1021.048 | 8.5 | 1021.048 | 0 | 5.2747 | 0 | 0 | 0 | 0 | 8.5 | 0 | 204.2096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1041.8857 | 0 | 208.3771 | 2.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 04:01 | 10 | 19 | 4 | 292 | 6988 | 57.92 | 1243.1781 | 0 | 0 | 1243.1781 | Heating | 1096.9218 | 8.5 | 1096.9218 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.3844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1119.308 | 0 | 223.8616 | 2.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 05:01 | 10 | 19 | 5 | 292 | 6989 | 59 | 1329.6213 | 0 | 0 | 1329.6213 | Heating | 1173.1953 | 8.5 | 1173.1953 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 234.6391 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1197.138 | 0 | 239.4276 | 2.394% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 06:01 | 10 | 19 | 6 | 292 | 6990 | 62.96 | 9892.9017 | 0 | 0 | 9892.9017 | Heating | 8729.0309 | 8.5 | 8729.0309 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1745.8062 | 34.92% | 1 | 69.83% | 0% | 0% | 0% | 35.6839 | 0 | 0 | 0 | 35.6839 | 8907.1744 | 0 | 1781.4349 | 17.81% | 1 | 35.63% | 0% | 0% | 3.7954 | 0 | 0 | 3.7954 | 39.4792
2007-10-19 07:01 | 10 | 19 | 7 | 292 | 6991 | 62.96 | 7541.0555 | 0 | 0 | 7541.0555 | Heating | 6653.8725 | 8.5 | 6653.8725 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1330.7745 | 30% | 1 | 53.23% | 0% | 0% | 0% | 19.1127 | 0 | 0 | 0 | 19.1127 | 6789.6658 | 0 | 1357.9332 | 13.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.3872
2007-10-19 08:01 | 10 | 19 | 8 | 292 | 6992 | 62.96 | 6127.7356 | 0 | 0 | 6127.7356 | Heating | 5406.8256 | 8.5 | 5406.8256 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1081.3651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5517.1689 | 0 | 1103.4338 | 11.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 09:01 | 10 | 19 | 9 | 292 | 6993 | 68 | 4126.4472 | 0 | 0 | 4126.4472 | Heating | 3640.9828 | 8.5 | 3640.9828 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 728.1966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3715.2886 | 0 | 743.0577 | 7.431% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 10:01 | 10 | 19 | 10 | 292 | 6994 | 71.06 | 2410.2406 | 1.1006 | 1.1006 | 2409.14 | Heating | 2125.7118 | 8.5 | 2125.7118 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 425.1424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2169.0936 | 0 | 433.8187 | 4.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 11:01 | 10 | 19 | 11 | 292 | 6995 | 71.06 | 1192.5139 | 33.1061 | 33.1061 | 1159.4078 | Heating | 1023.0069 | 8.5 | 1023.0069 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 204.6014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1043.8846 | 0 | 208.7769 | 2.088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 12:01 | 10 | 19 | 12 | 292 | 6996 | 80.06 | 379.8692 | 90.8953 | 90.8953 | 288.9739 | Heating | 254.977 | 8.5 | 254.977 | 0 | 9.1467 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.9954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 260.1806 | 0 | 52.0361 | 0.5204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 13:01 | 10 | 19 | 13 | 292 | 6997 | 82.94 | 184.0959 | 145.0843 | 145.0843 | 39.0115 | Heating | 34.422 | 8.5 | 34.422 | 0 | 9.8202 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.8844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 35.1244 | 0 | 7.0249 | 0.07025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 14:01 | 10 | 19 | 14 | 292 | 6998 | 82.94 | 136.7507 | 156.8745 | 156.8745 | -20.1239 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 191.7356 | 191.7356 | 0 | 8.5 | 0 | 31.9559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 187.9008 | 37.5802 | 0.3758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 15:01 | 10 | 19 | 15 | 292 | 6999 | 84.02 | 101.4983 | 161.2877 | 161.2877 | -59.7894 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 197.1294 | 197.1294 | 0 | 8.5 | 0 | 32.8549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 193.1868 | 38.6374 | 0.3864% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 16:01 | 10 | 19 | 16 | 292 | 7000 | 82.94 | 81.4859 | 150.513 | 150.513 | -69.0271 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 183.9603 | 183.9603 | 0 | 8.5 | 0 | 30.6601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 180.2811 | 36.0562 | 0.3606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 17:01 | 10 | 19 | 17 | 292 | 7001 | 82.94 | 85.8791 | 104.8637 | 104.8637 | -18.9846 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 128.1668 | 128.1668 | 0 | 8.5 | 0 | 21.3611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 125.6034 | 25.1207 | 0.2512% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 18:01 | 10 | 19 | 18 | 292 | 7002 | 78.98 | 154.4104 | 0 | 0 | 154.4104 | Heating | 136.2445 | 8.5 | 136.2445 | 0 | 8.9059 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.2489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 139.025 | 0 | 27.805 | 0.278% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 19:01 | 10 | 19 | 19 | 292 | 7003 | 77 | 746.2729 | 0 | 0 | 746.2729 | Heating | 658.4761 | 8.5 | 658.4761 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.6952 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 671.9143 | 0 | 134.3829 | 1.344% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 20:01 | 10 | 19 | 20 | 292 | 7004 | 77 | 1185.9631 | 0 | 0 | 1185.9631 | Heating | 1046.4381 | 8.5 | 1046.4381 | 0 | 8.4809 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.2876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1067.7939 | 0 | 213.5588 | 2.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 21:01 | 10 | 19 | 21 | 292 | 7005 | 75.02 | 1683.2404 | 0 | 0 | 1683.2404 | Heating | 1485.2122 | 8.5 | 1485.2122 | 0 | 8.0764 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.0424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1515.5226 | 0 | 303.1045 | 3.031% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 22:01 | 10 | 19 | 22 | 292 | 7006 | 73.94 | 370.9219 | 0 | 0 | 370.9219 | Heating | 327.284 | 8.5 | 327.284 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.4568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 333.9633 | 0 | 66.7927 | 0.6679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-19 23:01 | 10 | 19 | 23 | 292 | 7007 | 73.94 | 473.7564 | 0 | 0 | 473.7564 | Heating | 418.0204 | 8.5 | 418.0204 | 0 | 7.8643 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.6041 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 426.5514 | 0 | 85.3103 | 0.8531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 00:01 | 10 | 20 | 0 | 293 | 7008 | 73.04 | 544.8246 | 0 | 0 | 544.8246 | Heating | 480.7276 | 8.5 | 480.7276 | 0 | 7.6921 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.1455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 490.5383 | 0 | 98.1077 | 0.9811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 01:01 | 10 | 20 | 1 | 293 | 7009 | 69.08 | 656.7077 | 0 | 0 | 656.7077 | Heating | 579.448 | 8.5 | 579.448 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.8896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 591.2735 | 0 | 118.2547 | 1.183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 02:01 | 10 | 20 | 2 | 293 | 7010 | 69.08 | 701.3934 | 0 | 0 | 701.3934 | Heating | 618.8765 | 8.5 | 618.8765 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.7753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 631.5066 | 0 | 126.3013 | 1.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 03:01 | 10 | 20 | 3 | 293 | 7011 | 68 | 832.8888 | 0 | 0 | 832.8888 | Heating | 734.9019 | 8.5 | 734.9019 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 146.9804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 749.8999 | 0 | 149.98 | 1.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 04:01 | 10 | 20 | 4 | 293 | 7012 | 68 | 972.3274 | 0 | 0 | 972.3274 | Heating | 857.9359 | 8.5 | 857.9359 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.5872 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 875.4448 | 0 | 175.089 | 1.751% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 05:01 | 10 | 20 | 5 | 293 | 7013 | 68 | 1020.9702 | 0 | 0 | 1020.9702 | Heating | 900.8561 | 8.5 | 900.8561 | 0 | 6.8007 | 0 | 0 | 0 | 0 | 8.5 | 0 | 180.1712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 919.2409 | 0 | 183.8482 | 1.838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 06:01 | 10 | 20 | 6 | 293 | 7014 | 66.92 | 1093.3685 | 0 | 0 | 1093.3685 | Heating | 964.7369 | 8.5 | 964.7369 | 0 | 6.6252 | 0 | 0 | 0 | 0 | 8.5 | 0 | 192.9474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 984.4254 | 0 | 196.8851 | 1.969% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 07:01 | 10 | 20 | 7 | 293 | 7015 | 64.94 | 1136.2948 | 0 | 0 | 1136.2948 | Heating | 1002.6131 | 8.5 | 1002.6131 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 200.5226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1023.0745 | 0 | 204.6149 | 2.046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 08:01 | 10 | 20 | 8 | 293 | 7016 | 64.94 | 7603.9479 | 0 | 0 | 7603.9479 | Heating | 6709.3658 | 8.5 | 6709.3658 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1341.8732 | 30% | 1 | 53.67% | 0% | 0% | 0% | 19.4813 | 0 | 0 | 0 | 19.4813 | 6846.2916 | 0 | 1369.2583 | 13.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.7558
2007-10-20 09:01 | 10 | 20 | 9 | 293 | 7017 | 66.02 | 4412.9843 | 0 | 0 | 4412.9843 | Heating | 3893.8097 | 8.5 | 3893.8097 | 0 | 6.4831 | 0 | 0 | 0 | 0 | 8.5 | 0 | 778.7619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3973.2752 | 0 | 794.655 | 7.947% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 10:01 | 10 | 20 | 10 | 293 | 7018 | 69.08 | 2645.8145 | 0 | 0 | 2645.8145 | Heating | 2334.5422 | 8.5 | 2334.5422 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 466.9084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2382.186 | 0 | 476.4372 | 4.764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 11:01 | 10 | 20 | 11 | 293 | 7019 | 69.08 | 1572.4176 | 0 | 0 | 1572.4176 | Heating | 1387.4273 | 8.5 | 1387.4273 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 277.4855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1415.7421 | 0 | 283.1484 | 2.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 12:01 | 10 | 20 | 12 | 293 | 7020 | 69.98 | 486.5674 | 0 | 0 | 486.5674 | Heating | 429.3242 | 8.5 | 429.3242 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.8648 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 438.0859 | 0 | 87.6172 | 0.8762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 13:01 | 10 | 20 | 13 | 293 | 7021 | 71.96 | 110.7237 | 0 | 0 | 110.7237 | Heating | 97.6974 | 8.5 | 97.6974 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.5395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 99.6912 | 0 | 19.9382 | 0.1994% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 14:01 | 10 | 20 | 14 | 293 | 7022 | 71.96 | 75.8696 | 0 | 0 | 75.8696 | Heating | 66.9438 | 8.5 | 66.9438 | 0 | 7.4907 | 0 | 0 | 0 | 0 | 8.5 | 0 | 13.3888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 68.31 | 0 | 13.662 | 0.1366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 15:01 | 10 | 20 | 15 | 293 | 7023 | 71.06 | 48.6011 | 0 | 0 | 48.6011 | Heating | 42.8833 | 8.5 | 42.8833 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.5767 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 43.7585 | 0 | 8.7517 | 0.08752% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 16:01 | 10 | 20 | 16 | 293 | 7024 | 69.98 | 43.2239 | 0 | 0 | 43.2239 | Heating | 38.1388 | 8.5 | 38.1388 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 7.6278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 38.9171 | 0 | 7.7834 | 0.07783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 17:01 | 10 | 20 | 17 | 293 | 7025 | 69.98 | 587.658 | 0 | 0 | 587.658 | Heating | 518.5217 | 8.5 | 518.5217 | 0 | 7.1363 | 0 | 0 | 0 | 0 | 8.5 | 0 | 103.7043 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 529.1038 | 0 | 105.8208 | 1.058% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 18:01 | 10 | 20 | 18 | 293 | 7026 | 62.06 | 1474.4327 | 0 | 0 | 1474.4327 | Heating | 1300.97 | 8.5 | 1300.97 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 260.194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1327.5204 | 0 | 265.5041 | 2.655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 19:01 | 10 | 20 | 19 | 293 | 7027 | 60.08 | 166.4957 | 0 | 0 | 166.4957 | Heating | 146.908 | 8.5 | 146.908 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.3816 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 149.9061 | 0 | 29.9812 | 0.2998% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 20:01 | 10 | 20 | 20 | 293 | 7028 | 60.08 | 236.6622 | 0 | 0 | 236.6622 | Heating | 208.8196 | 8.5 | 208.8196 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.7639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 213.0812 | 0 | 42.6162 | 0.4262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 21:01 | 10 | 20 | 21 | 293 | 7029 | 57.92 | 299.5753 | 0 | 0 | 299.5753 | Heating | 264.3312 | 8.5 | 264.3312 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.8662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 269.7257 | 0 | 53.9451 | 0.5395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 22:01 | 10 | 20 | 22 | 293 | 7030 | 55.04 | 392.0183 | 0 | 0 | 392.0183 | Heating | 345.8985 | 8.5 | 345.8985 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 69.1797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 352.9576 | 0 | 70.5915 | 0.7059% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-20 23:01 | 10 | 20 | 23 | 293 | 7031 | 55.04 | 500.9308 | 0 | 0 | 500.9308 | Heating | 441.9977 | 8.5 | 441.9977 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 88.3995 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 451.0181 | 0 | 90.2036 | 0.902% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 00:01 | 10 | 21 | 0 | 294 | 7032 | 51.08 | 630.9573 | 0 | 0 | 630.9573 | Heating | 556.7271 | 8.5 | 556.7271 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.3454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 568.0888 | 0 | 113.6178 | 1.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 01:01 | 10 | 21 | 1 | 294 | 7033 | 50 | 678.0648 | 0 | 0 | 678.0648 | Heating | 598.2925 | 8.5 | 598.2925 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.6585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 610.5025 | 0 | 122.1005 | 1.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 02:01 | 10 | 21 | 2 | 294 | 7034 | 50 | 713.9466 | 0 | 0 | 713.9466 | Heating | 629.9529 | 8.5 | 629.9529 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.9906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 642.8091 | 0 | 128.5618 | 1.286% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 03:01 | 10 | 21 | 3 | 294 | 7035 | 48.02 | 743.636 | 0 | 0 | 743.636 | Heating | 656.1494 | 8.5 | 656.1494 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.2299 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 669.5402 | 0 | 133.908 | 1.339% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 04:01 | 10 | 21 | 4 | 294 | 7036 | 46.94 | 799.6838 | 0 | 0 | 799.6838 | Heating | 705.6033 | 8.5 | 705.6033 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.1207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 720.0034 | 0 | 144.0007 | 1.44% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 05:01 | 10 | 21 | 5 | 294 | 7037 | 46.94 | 887.5326 | 0 | 0 | 887.5326 | Heating | 783.117 | 8.5 | 783.117 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.6234 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 799.099 | 0 | 159.8198 | 1.598% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 06:01 | 10 | 21 | 6 | 294 | 7038 | 44.6 | 8359.7069 | 0 | 0 | 8359.7069 | Heating | 7376.212 | 8.5 | 7376.212 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1475.2424 | 30% | 1 | 59.01% | 0% | 0% | 0% | 24.2252 | 0 | 0 | 0 | 24.2252 | 7526.747 | 0 | 1505.3494 | 15.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.4997
2007-10-21 07:01 | 10 | 21 | 7 | 294 | 7039 | 46.04 | 5927.2956 | 0 | 0 | 5927.2956 | Heating | 5229.9667 | 8.5 | 5229.9667 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1045.9933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5336.7007 | 0 | 1067.3401 | 10.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 08:01 | 10 | 21 | 8 | 294 | 7040 | 48.92 | 4205.0033 | 0 | 0 | 4205.0033 | Heating | 3710.297 | 8.5 | 3710.297 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 742.0594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3786.0174 | 0 | 757.2035 | 7.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 09:01 | 10 | 21 | 9 | 294 | 7041 | 51.98 | 2556.3688 | 0 | 0 | 2556.3688 | Heating | 2255.6195 | 8.5 | 2255.6195 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 451.1239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2301.6526 | 0 | 460.3305 | 4.603% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 10:01 | 10 | 21 | 10 | 294 | 7042 | 53.96 | 1651.6279 | 0.069464 | 0.069464 | 1651.5585 | Heating | 1457.2575 | 8.5 | 1457.2575 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 291.4515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1486.9974 | 0 | 297.3995 | 2.974% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 11:01 | 10 | 21 | 11 | 294 | 7043 | 53.96 | 686.7543 | 13.1208 | 13.1208 | 673.6335 | Heating | 594.3825 | 8.5 | 594.3825 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.8765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 606.5127 | 0 | 121.3025 | 1.213% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 12:01 | 10 | 21 | 12 | 294 | 7044 | 53.96 | 204.2957 | 44.4466 | 44.4466 | 159.8491 | Heating | 141.0433 | 8.5 | 141.0433 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.2087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 143.9217 | 0 | 28.7843 | 0.2878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 13:01 | 10 | 21 | 13 | 294 | 7045 | 51.8 | 103.7752 | 105.8317 | 105.8317 | -2.0565 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 129.3499 | 129.3499 | 0 | 8.5 | 0 | 21.5583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 126.7629 | 25.3526 | 0.2535% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 14:01 | 10 | 21 | 14 | 294 | 7046 | 53.06 | 84.0138 | 147.7916 | 147.7916 | -63.7778 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 180.6342 | 180.6342 | 0 | 8.5 | 0 | 30.1057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 177.0215 | 35.4043 | 0.354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 15:01 | 10 | 21 | 15 | 294 | 7047 | 53.96 | 95.5345 | 153.8487 | 153.8487 | -58.3141 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 188.0373 | 188.0373 | 0 | 8.5 | 0 | 31.3395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 184.2765 | 36.8553 | 0.3686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 16:01 | 10 | 21 | 16 | 294 | 7048 | 53.96 | 95.0207 | 168.1811 | 168.1811 | -73.1604 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 205.5547 | 205.5547 | 0 | 8.5 | 0 | 34.2591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 201.4436 | 40.2887 | 0.4029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 17:01 | 10 | 21 | 17 | 294 | 7049 | 53.96 | 90.1144 | 112.3345 | 112.3345 | -22.2201 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 137.2977 | 137.2977 | 0 | 8.5 | 0 | 22.883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 134.5518 | 26.9104 | 0.2691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 18:01 | 10 | 21 | 18 | 294 | 7050 | 53.96 | 94.7929 | 47.1043 | 47.1043 | 47.6886 | Heating | 42.0782 | 8.5 | 42.0782 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.4156 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 42.9369 | 0 | 8.5874 | 0.08587% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 19:01 | 10 | 21 | 19 | 294 | 7051 | 53.96 | 147.9308 | 36.8969 | 36.8969 | 111.0339 | Heating | 97.9711 | 8.5 | 97.9711 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 19.5942 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 99.9705 | 0 | 19.9941 | 0.1999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 20:01 | 10 | 21 | 20 | 294 | 7052 | 53.96 | 360.8847 | 8.8214 | 8.8214 | 352.0633 | Heating | 310.6441 | 8.5 | 310.6441 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.1288 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 316.9837 | 0 | 63.3967 | 0.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 21:01 | 10 | 21 | 21 | 294 | 7053 | 55.94 | 169.3602 | 1.382 | 1.382 | 167.9782 | Heating | 148.2161 | 8.5 | 148.2161 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.6432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 151.2409 | 0 | 30.2482 | 0.3025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 22:01 | 10 | 21 | 22 | 294 | 7054 | 55.94 | 223.9115 | 0 | 0 | 223.9115 | Heating | 197.5689 | 8.5 | 197.5689 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 39.5138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 201.601 | 0 | 40.3202 | 0.4032% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-21 23:01 | 10 | 21 | 23 | 294 | 7055 | 55.94 | 297.3108 | 0 | 0 | 297.3108 | Heating | 262.3331 | 8.5 | 262.3331 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.4666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 267.6868 | 0 | 53.5374 | 0.5354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 00:01 | 10 | 22 | 0 | 295 | 7056 | 60.08 | 372.5396 | 0 | 0 | 372.5396 | Heating | 328.7114 | 8.5 | 328.7114 | 0 | 5.6339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.7423 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 335.4198 | 0 | 67.084 | 0.6708% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 01:01 | 10 | 22 | 1 | 295 | 7057 | 60.98 | 461.9282 | 0 | 0 | 461.9282 | Heating | 407.5837 | 8.5 | 407.5837 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.5167 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 415.9018 | 0 | 83.1804 | 0.8318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 02:01 | 10 | 22 | 2 | 295 | 7058 | 60.98 | 519.8533 | 0 | 0 | 519.8533 | Heating | 458.6941 | 8.5 | 458.6941 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.7388 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 468.0552 | 0 | 93.611 | 0.9361% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 03:01 | 10 | 22 | 3 | 295 | 7059 | 60.98 | 596.3689 | 0 | 0 | 596.3689 | Heating | 526.2079 | 8.5 | 526.2079 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.2416 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 536.9468 | 0 | 107.3894 | 1.074% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 04:01 | 10 | 22 | 4 | 295 | 7060 | 62.96 | 653.8036 | 0 | 0 | 653.8036 | Heating | 576.8855 | 8.5 | 576.8855 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.3771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 588.6587 | 0 | 117.7317 | 1.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 05:01 | 10 | 22 | 5 | 295 | 7061 | 62.96 | 679.7016 | 0 | 0 | 679.7016 | Heating | 599.7367 | 8.5 | 599.7367 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.9473 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 611.9762 | 0 | 122.3952 | 1.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 06:01 | 10 | 22 | 6 | 295 | 7062 | 64.94 | 6584.2037 | 0 | 0 | 6584.2037 | Heating | 5809.5915 | 8.5 | 5809.5915 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1161.9183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5928.1546 | 0 | 1185.6309 | 11.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 07:01 | 10 | 22 | 7 | 295 | 7063 | 64.94 | 4436.5191 | 0 | 0 | 4436.5191 | Heating | 3914.5757 | 8.5 | 3914.5757 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 782.9151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3994.465 | 0 | 798.893 | 7.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 08:01 | 10 | 22 | 8 | 295 | 7064 | 64.94 | 2928.955 | 0 | 0 | 2928.955 | Heating | 2584.3721 | 8.5 | 2584.3721 | 0 | 6.3174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 516.8744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2637.1144 | 0 | 527.4229 | 5.274% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 09:01 | 10 | 22 | 9 | 295 | 7065 | 69.08 | 1579.3057 | 21.7573 | 21.7573 | 1557.5485 | Heating | 1374.3075 | 8.5 | 1374.3075 | 0 | 6.9815 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.8615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1402.3546 | 0 | 280.4709 | 2.805% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 10:01 | 10 | 22 | 10 | 295 | 7066 | 71.06 | 680.5372 | 120.7982 | 120.7982 | 559.739 | Heating | 493.8873 | 8.5 | 493.8873 | 0 | 7.3273 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.7775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 503.9667 | 0 | 100.7933 | 1.008% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 11:01 | 10 | 22 | 11 | 295 | 7067 | 71.06 | 151.288 | 400.4935 | 400.4935 | -249.2055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 489.4921 | 489.4921 | 0 | 8.5 | 0 | 81.582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 479.7022 | 95.9404 | 0.9594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 12:01 | 10 | 22 | 12 | 295 | 7068 | 69.08 | 72.1971 | 635.2196 | 635.2196 | -563.0225 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 776.3795 | 776.3795 | 0 | 8.5 | 0 | 129.3966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 760.8519 | 152.1704 | 1.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 13:01 | 10 | 22 | 13 | 295 | 7069 | 66.92 | 36.6501 | 1323.2126 | 1323.2126 | -1286.5624 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1617.2598 | 1617.2598 | 0 | 8.5 | 0 | 269.5433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1584.9146 | 316.9829 | 3.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 14:01 | 10 | 22 | 14 | 295 | 7070 | 69.08 | 10.8896 | 2270.4544 | 2270.4544 | -2259.5648 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2774.9999 | 2774.9999 | 0 | 8.5 | 0 | 462.5 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2719.4999 | 543.9 | 5.439% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 15:01 | 10 | 22 | 15 | 295 | 7071 | 68 | 2.3682 | 2843.0697 | 2843.0697 | -2840.7015 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3474.863 | 3474.863 | 0 | 8.5 | 0 | 579.1438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3405.3657 | 681.0731 | 6.811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 16:01 | 10 | 22 | 16 | 295 | 7072 | 66.2 | 0.25621 | 2651.9026 | 2651.9026 | -2651.6463 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 3241.2142 | 3241.2142 | 0 | 8.5 | 0 | 540.2024 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 3176.39 | 635.278 | 6.353% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 17:01 | 10 | 22 | 17 | 295 | 7073 | 66.92 | 3.1693 | 1427.6198 | 1427.6198 | -1424.4506 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1744.8687 | 1744.8687 | 0 | 8.5 | 0 | 290.8114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1709.9713 | 341.9943 | 3.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 18:01 | 10 | 22 | 18 | 295 | 7074 | 64.04 | 46.3819 | 268.8458 | 268.8458 | -222.4639 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 328.5893 | 328.5893 | 0 | 8.5 | 0 | 54.7649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 322.0175 | 64.4035 | 0.644% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 19:01 | 10 | 22 | 19 | 295 | 7075 | 62.6 | 184.2742 | 186.3014 | 186.3014 | -2.0271 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 227.7017 | 227.7017 | 0 | 8.5 | 0 | 37.9503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 223.1476 | 44.6295 | 0.4463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 20:01 | 10 | 22 | 20 | 295 | 7076 | 62.06 | 760.7602 | 91.4786 | 91.4786 | 669.2816 | Heating | 590.5426 | 8.5 | 590.5426 | 0 | 5.9003 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.1085 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 602.5944 | 0 | 120.5189 | 1.205% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 21:01 | 10 | 22 | 21 | 295 | 7077 | 55.04 | 241.2713 | 51.3789 | 51.3789 | 189.8925 | Heating | 167.5522 | 8.5 | 167.5522 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 33.5104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 170.9716 | 0 | 34.1943 | 0.3419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 22:01 | 10 | 22 | 22 | 295 | 7078 | 53.06 | 296.9412 | 0 | 0 | 296.9412 | Heating | 262.007 | 8.5 | 262.007 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.4014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 267.354 | 0 | 53.4708 | 0.5347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-22 23:01 | 10 | 22 | 23 | 295 | 7079 | 51.98 | 296.7281 | 0 | 0 | 296.7281 | Heating | 261.8189 | 8.5 | 261.8189 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.3638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 267.1622 | 0 | 53.4324 | 0.5343% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 00:01 | 10 | 23 | 0 | 296 | 7080 | 51.08 | 273.9043 | 0 | 0 | 273.9043 | Heating | 241.6803 | 8.5 | 241.6803 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 48.3361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 246.6125 | 0 | 49.3225 | 0.4932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 01:01 | 10 | 23 | 1 | 296 | 7081 | 50 | 265.7045 | 0 | 0 | 265.7045 | Heating | 234.4451 | 8.5 | 234.4451 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 46.889 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 239.2297 | 0 | 47.8459 | 0.4785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 02:01 | 10 | 23 | 2 | 296 | 7082 | 50 | 277.8875 | 0 | 0 | 277.8875 | Heating | 245.1949 | 8.5 | 245.1949 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 49.039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 250.1988 | 0 | 50.0398 | 0.5004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 03:01 | 10 | 23 | 3 | 296 | 7083 | 50 | 290.2465 | 0 | 0 | 290.2465 | Heating | 256.0998 | 8.5 | 256.0998 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 51.22 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 261.3263 | 0 | 52.2653 | 0.5227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 04:01 | 10 | 23 | 4 | 296 | 7084 | 48.92 | 297.9329 | 0 | 0 | 297.9329 | Heating | 262.882 | 8.5 | 262.882 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.5764 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 268.2469 | 0 | 53.6494 | 0.5365% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 05:01 | 10 | 23 | 5 | 296 | 7085 | 48.02 | 307.4674 | 0 | 0 | 307.4674 | Heating | 271.2947 | 8.5 | 271.2947 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.2589 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 276.8314 | 0 | 55.3663 | 0.5537% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 06:01 | 10 | 23 | 6 | 296 | 7086 | 46.04 | 3582.4886 | 76.8101 | 76.8101 | 3505.6784 | Heating | 3093.2457 | 8.5 | 3093.2457 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 618.6491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3156.3731 | 0 | 631.2746 | 6.313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 07:01 | 10 | 23 | 7 | 296 | 7087 | 44.96 | 2391.501 | 0 | 0 | 2391.501 | Heating | 2110.148 | 8.5 | 2110.148 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 422.0296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2153.2122 | 0 | 430.6424 | 4.306% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 08:01 | 10 | 23 | 8 | 296 | 7088 | 44.96 | 1722.0986 | 18.5087 | 18.5087 | 1703.5898 | Heating | 1503.1675 | 8.5 | 1503.1675 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.6335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1533.8444 | 0 | 306.7689 | 3.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 09:01 | 10 | 23 | 9 | 296 | 7089 | 44.06 | 752.4026 | 106.912 | 106.912 | 645.4906 | Heating | 569.5505 | 8.5 | 569.5505 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.9101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 581.174 | 0 | 116.2348 | 1.162% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 10:01 | 10 | 23 | 10 | 296 | 7090 | 44.06 | 159.096 | 393.3452 | 393.3452 | -234.2492 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 480.7552 | 480.7552 | 0 | 8.5 | 0 | 80.1259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 471.1401 | 94.228 | 0.9423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 11:01 | 10 | 23 | 11 | 296 | 7091 | 44.06 | 37.3265 | 769.9045 | 769.9045 | -732.578 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 940.9944 | 940.9944 | 0 | 8.5 | 0 | 156.8324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 922.1745 | 184.4349 | 1.844% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 12:01 | 10 | 23 | 12 | 296 | 7092 | 41 | 6.4746 | 1449.1495 | 1449.1495 | -1442.6749 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1771.1828 | 1771.1828 | 0 | 8.5 | 0 | 295.1971 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1735.7591 | 347.1518 | 3.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 13:01 | 10 | 23 | 13 | 296 | 7093 | 39.92 | 0.93034 | 2422.1469 | 2422.1469 | -2421.2165 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2960.4017 | 2960.4017 | 0 | 8.5 | 0 | 493.4003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2901.1937 | 580.2387 | 5.802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 14:01 | 10 | 23 | 14 | 296 | 7094 | 39.92 | 14.378 | 1703.7211 | 1703.7211 | -1689.3431 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2082.3258 | 2082.3258 | 0 | 8.5 | 0 | 347.0543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2040.6793 | 408.1359 | 4.081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 15:01 | 10 | 23 | 15 | 296 | 7095 | 39.92 | 78.4868 | 548.9267 | 548.9267 | -470.44 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 670.9105 | 670.9105 | 0 | 8.5 | 0 | 111.8184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 657.4922 | 131.4984 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 16:01 | 10 | 23 | 16 | 296 | 7096 | 41 | 78.5878 | 487.3952 | 487.3952 | -408.8075 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 595.7053 | 595.7053 | 0 | 8.5 | 0 | 99.2842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 583.7912 | 116.7582 | 1.168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 17:01 | 10 | 23 | 17 | 296 | 7097 | 41 | 72.7937 | 339.3623 | 339.3623 | -266.5686 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 414.7762 | 414.7762 | 0 | 8.5 | 0 | 69.1294 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 406.4806 | 81.2961 | 0.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 18:01 | 10 | 23 | 18 | 296 | 7098 | 42.08 | 79.0486 | 156.3771 | 156.3771 | -77.3285 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 191.1276 | 191.1276 | 0 | 8.5 | 0 | 31.8546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 187.305 | 37.461 | 0.3746% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 19:01 | 10 | 23 | 19 | 296 | 7099 | 42.08 | 136.0162 | 115.8365 | 115.8365 | 20.1797 | Heating | 17.8056 | 8.5 | 17.8056 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 3.5611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 18.169 | 0 | 3.6338 | 0.03634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 20:01 | 10 | 23 | 20 | 296 | 7100 | 42.08 | 354.1094 | 37.2999 | 37.2999 | 316.8095 | Heating | 279.5378 | 8.5 | 279.5378 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 55.9076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 285.2426 | 0 | 57.0485 | 0.5705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 21:01 | 10 | 23 | 21 | 296 | 7101 | 42.98 | 180.6112 | 15.7626 | 15.7626 | 164.8486 | Heating | 145.4546 | 8.5 | 145.4546 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.0909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 148.4231 | 0 | 29.6846 | 0.2968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 22:01 | 10 | 23 | 22 | 296 | 7102 | 42.98 | 269.6192 | 0 | 0 | 269.6192 | Heating | 237.8993 | 8.5 | 237.8993 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 47.5799 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 242.7544 | 0 | 48.5509 | 0.4855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-23 23:01 | 10 | 23 | 23 | 296 | 7103 | 44.06 | 351.6823 | 0 | 0 | 351.6823 | Heating | 310.3079 | 8.5 | 310.3079 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 62.0616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 316.6407 | 0 | 63.3281 | 0.6333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 00:01 | 10 | 24 | 0 | 297 | 7104 | 44.6 | 420.9402 | 0 | 0 | 420.9402 | Heating | 371.4179 | 8.5 | 371.4179 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.2836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 378.9978 | 0 | 75.7996 | 0.758% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 01:01 | 10 | 24 | 1 | 297 | 7105 | 44.6 | 492.6705 | 0 | 0 | 492.6705 | Heating | 434.7092 | 8.5 | 434.7092 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 86.9418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 443.5809 | 0 | 88.7162 | 0.8872% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 02:01 | 10 | 24 | 2 | 297 | 7106 | 44.06 | 557.4797 | 0 | 0 | 557.4797 | Heating | 491.8938 | 8.5 | 491.8938 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.3788 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 501.9325 | 0 | 100.3865 | 1.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 03:01 | 10 | 24 | 3 | 297 | 7107 | 42.98 | 597.4966 | 0 | 0 | 597.4966 | Heating | 527.2029 | 8.5 | 527.2029 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.4406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 537.9622 | 0 | 107.5924 | 1.076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 04:01 | 10 | 24 | 4 | 297 | 7108 | 42.08 | 629.956 | 0 | 0 | 629.956 | Heating | 555.8436 | 8.5 | 555.8436 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.1687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 567.1873 | 0 | 113.4375 | 1.134% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 05:01 | 10 | 24 | 5 | 297 | 7109 | 42.08 | 686.8037 | 0 | 0 | 686.8037 | Heating | 606.0033 | 8.5 | 606.0033 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.2007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 618.3707 | 0 | 123.6741 | 1.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 06:01 | 10 | 24 | 6 | 297 | 7110 | 42.98 | 6991.7124 | 0 | 0 | 6991.7124 | Heating | 6169.158 | 8.5 | 6169.158 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1233.8316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6295.0592 | 0 | 1259.0118 | 12.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 07:01 | 10 | 24 | 7 | 297 | 7111 | 44.06 | 5139.358 | 0 | 0 | 5139.358 | Heating | 4534.7277 | 8.5 | 4534.7277 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 906.9455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4627.2731 | 0 | 925.4546 | 9.255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 08:01 | 10 | 24 | 8 | 297 | 7112 | 44.06 | 3629.3868 | 0 | 0 | 3629.3868 | Heating | 3202.4001 | 8.5 | 3202.4001 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 640.48 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3267.7552 | 0 | 653.551 | 6.536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 09:01 | 10 | 24 | 9 | 297 | 7113 | 48.02 | 2173.3335 | 22.1888 | 22.1888 | 2151.1447 | Heating | 1898.0689 | 8.5 | 1898.0689 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.6138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1936.805 | 0 | 387.361 | 3.874% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 10:01 | 10 | 24 | 10 | 297 | 7114 | 51.08 | 1438.6333 | 106.6347 | 106.6347 | 1331.9986 | Heating | 1175.2929 | 8.5 | 1175.2929 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.0586 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1199.2784 | 0 | 239.8557 | 2.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 11:01 | 10 | 24 | 11 | 297 | 7115 | 51.08 | 908.6784 | 164.1596 | 164.1596 | 744.5188 | Heating | 656.9283 | 8.5 | 656.9283 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.3857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 670.335 | 0 | 134.067 | 1.341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 12:01 | 10 | 24 | 12 | 297 | 7116 | 53.96 | 518.5623 | 349.8725 | 349.8725 | 168.6898 | Heating | 148.844 | 8.5 | 148.844 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.7688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 151.8816 | 0 | 30.3763 | 0.3038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 13:01 | 10 | 24 | 13 | 297 | 7117 | 55.04 | 255.7384 | 518.8769 | 518.8769 | -263.1385 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 634.1829 | 634.1829 | 0 | 8.5 | 0 | 105.6972 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 621.4993 | 124.2999 | 1.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 14:01 | 10 | 24 | 14 | 297 | 7118 | 55.04 | 157.5945 | 703.9693 | 703.9693 | -546.3748 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 860.4069 | 860.4069 | 0 | 8.5 | 0 | 143.4011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 843.1987 | 168.6397 | 1.686% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 15:01 | 10 | 24 | 15 | 297 | 7119 | 55.94 | 122.8975 | 694.5894 | 694.5894 | -571.6919 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 848.9426 | 848.9426 | 0 | 8.5 | 0 | 141.4904 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 831.9638 | 166.3928 | 1.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 16:01 | 10 | 24 | 16 | 297 | 7120 | 53.96 | 117.5437 | 591.3933 | 591.3933 | -473.8496 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 722.814 | 722.814 | 0 | 8.5 | 0 | 120.469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 708.3578 | 141.6716 | 1.417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 17:01 | 10 | 24 | 17 | 297 | 7121 | 53.96 | 188.4092 | 370.0799 | 370.0799 | -181.6707 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 452.3199 | 452.3199 | 0 | 8.5 | 0 | 75.3867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 443.2735 | 88.6547 | 0.8865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 18:01 | 10 | 24 | 18 | 297 | 7122 | 51.98 | 805.3183 | 114.0922 | 114.0922 | 691.2261 | Heating | 609.9054 | 8.5 | 609.9054 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.9811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 622.3525 | 0 | 124.4705 | 1.245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 19:01 | 10 | 24 | 19 | 297 | 7123 | 51.08 | 1543.6167 | 62.4108 | 62.4108 | 1481.2058 | Heating | 1306.9463 | 8.5 | 1306.9463 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.3893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1333.6187 | 0 | 266.7237 | 2.667% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 20:01 | 10 | 24 | 20 | 297 | 7124 | 51.08 | 2208.4242 | 8.965 | 8.965 | 2199.4592 | Heating | 1940.6993 | 8.5 | 1940.6993 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 388.1399 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1980.3054 | 0 | 396.0611 | 3.961% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 21:01 | 10 | 24 | 21 | 297 | 7125 | 48.02 | 576.3677 | 0 | 0 | 576.3677 | Heating | 508.5598 | 8.5 | 508.5598 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 101.712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 518.9385 | 0 | 103.7877 | 1.038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 22:01 | 10 | 24 | 22 | 297 | 7126 | 46.94 | 649.3966 | 0 | 0 | 649.3966 | Heating | 572.997 | 8.5 | 572.997 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.5994 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 584.6908 | 0 | 116.9382 | 1.169% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-24 23:01 | 10 | 24 | 23 | 297 | 7127 | 46.94 | 730.4442 | 0 | 0 | 730.4442 | Heating | 644.5096 | 8.5 | 644.5096 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.9019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 657.6629 | 0 | 131.5326 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 00:01 | 10 | 25 | 0 | 298 | 7128 | 48.92 | 826.687 | 0 | 0 | 826.687 | Heating | 729.4297 | 8.5 | 729.4297 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.8859 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 744.316 | 0 | 148.8632 | 1.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 01:01 | 10 | 25 | 1 | 298 | 7129 | 48.92 | 863.2846 | 0 | 0 | 863.2846 | Heating | 761.7217 | 8.5 | 761.7217 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.3443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 777.2671 | 0 | 155.4534 | 1.555% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 02:01 | 10 | 25 | 2 | 298 | 7130 | 48.92 | 924.9899 | 0 | 0 | 924.9899 | Heating | 816.1676 | 8.5 | 816.1676 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.2335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 832.8241 | 0 | 166.5648 | 1.666% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 03:01 | 10 | 25 | 3 | 298 | 7131 | 48.02 | 1032.4932 | 0 | 0 | 1032.4932 | Heating | 911.0234 | 8.5 | 911.0234 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.2047 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 929.6158 | 0 | 185.9232 | 1.859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 04:01 | 10 | 25 | 4 | 298 | 7132 | 46.94 | 1157.7847 | 0 | 0 | 1157.7847 | Heating | 1021.5748 | 8.5 | 1021.5748 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 204.315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1042.4232 | 0 | 208.4846 | 2.085% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 05:01 | 10 | 25 | 5 | 298 | 7133 | 46.94 | 1244.2331 | 0 | 0 | 1244.2331 | Heating | 1097.8528 | 8.5 | 1097.8528 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.5706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1120.2579 | 0 | 224.0516 | 2.241% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 06:01 | 10 | 25 | 6 | 298 | 7134 | 44.06 | 10003.3765 | 0 | 0 | 10003.3765 | Heating | 8826.5086 | 8.5 | 8826.5086 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1765.3017 | 35.31% | 1 | 70.61% | 0% | 0% | 0% | 36.607 | 0 | 0 | 0 | 36.607 | 9006.6415 | 0 | 1801.3283 | 18.01% | 1 | 36.03% | 0% | 0% | 3.8935 | 0 | 0 | 3.8935 | 40.5006
2007-10-25 07:01 | 10 | 25 | 7 | 298 | 7135 | 44.06 | 7813.6665 | 0 | 0 | 7813.6665 | Heating | 6894.4116 | 8.5 | 6894.4116 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1378.8823 | 30% | 1 | 55.16% | 0% | 0% | 0% | 20.7393 | 0 | 0 | 0 | 20.7393 | 7035.1139 | 0 | 1407.0228 | 14.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.0138
2007-10-25 08:01 | 10 | 25 | 8 | 298 | 7136 | 44.06 | 6140.3049 | 0 | 0 | 6140.3049 | Heating | 5417.9161 | 8.5 | 5417.9161 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1083.5832 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5528.4858 | 0 | 1105.6972 | 11.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 09:01 | 10 | 25 | 9 | 298 | 7137 | 50 | 4101.3213 | 0 | 0 | 4101.3213 | Heating | 3618.8129 | 8.5 | 3618.8129 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 723.7626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3692.6663 | 0 | 738.5333 | 7.385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 10:01 | 10 | 25 | 10 | 298 | 7138 | 50 | 2707.5306 | 7.7498 | 7.7498 | 2699.7808 | Heating | 2382.1595 | 8.5 | 2382.1595 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.4319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2430.775 | 0 | 486.155 | 4.862% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 11:01 | 10 | 25 | 11 | 298 | 7139 | 50 | 1623.1201 | 81.251 | 81.251 | 1541.8691 | Heating | 1360.4727 | 8.5 | 1360.4727 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.0945 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1388.2375 | 0 | 277.6475 | 2.776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 12:01 | 10 | 25 | 12 | 298 | 7140 | 50 | 1070.3805 | 246.4427 | 246.4427 | 823.9378 | Heating | 727.004 | 8.5 | 727.004 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.4008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 741.8408 | 0 | 148.3682 | 1.484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 13:01 | 10 | 25 | 13 | 298 | 7141 | 50 | 619.8895 | 376.9948 | 376.9948 | 242.8947 | Heating | 214.3188 | 8.5 | 214.3188 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 42.8638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 218.6927 | 0 | 43.7385 | 0.4374% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 14:01 | 10 | 25 | 14 | 298 | 7142 | 50 | 301.0395 | 438.7251 | 438.7251 | -137.6856 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 536.2196 | 536.2196 | 0 | 8.5 | 0 | 89.3699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 525.4952 | 105.099 | 1.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 15:01 | 10 | 25 | 15 | 298 | 7143 | 48.92 | 268.9492 | 308.7435 | 308.7435 | -39.7943 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 377.3531 | 377.3531 | 0 | 8.5 | 0 | 62.8922 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 369.8061 | 73.9612 | 0.7396% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 16:01 | 10 | 25 | 16 | 298 | 7144 | 48.92 | 380.2561 | 213.8733 | 213.8733 | 166.3828 | Heating | 146.8083 | 8.5 | 146.8083 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 29.3617 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 149.8044 | 0 | 29.9609 | 0.2996% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 17:01 | 10 | 25 | 17 | 298 | 7145 | 48.92 | 707.5189 | 104.2161 | 104.2161 | 603.3028 | Heating | 532.326 | 8.5 | 532.326 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.4652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 543.1898 | 0 | 108.638 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 18:01 | 10 | 25 | 18 | 298 | 7146 | 44.96 | 1100.0113 | 51.7794 | 51.7794 | 1048.2319 | Heating | 924.9105 | 8.5 | 924.9105 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.9821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 943.7862 | 0 | 188.7572 | 1.888% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 19:01 | 10 | 25 | 19 | 298 | 7147 | 46.04 | 1427.0682 | 35.8279 | 35.8279 | 1391.2403 | Heating | 1227.565 | 8.5 | 1227.565 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1252.6173 | 0 | 250.5235 | 2.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 20:01 | 10 | 25 | 20 | 298 | 7148 | 46.04 | 1745.9105 | 7.1673 | 7.1673 | 1738.7433 | Heating | 1534.1852 | 8.5 | 1534.1852 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 306.837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1565.4951 | 0 | 313.099 | 3.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 21:01 | 10 | 25 | 21 | 298 | 7149 | 44.06 | 480.943 | 0.3029 | 0.3029 | 480.6401 | Heating | 424.0942 | 8.5 | 424.0942 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 84.8188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 432.7492 | 0 | 86.5498 | 0.8655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 22:01 | 10 | 25 | 22 | 298 | 7150 | 44.06 | 568.7074 | 0 | 0 | 568.7074 | Heating | 501.8007 | 8.5 | 501.8007 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.3601 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 512.0415 | 0 | 102.4083 | 1.024% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-25 23:01 | 10 | 25 | 23 | 298 | 7151 | 44.06 | 606.9293 | 0 | 0 | 606.9293 | Heating | 535.5259 | 8.5 | 535.5259 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.1052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 546.455 | 0 | 109.291 | 1.093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 00:01 | 10 | 26 | 0 | 299 | 7152 | 44.96 | 649.4709 | 0 | 0 | 649.4709 | Heating | 573.0626 | 8.5 | 573.0626 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.6125 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 584.7577 | 0 | 116.9515 | 1.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 01:01 | 10 | 26 | 1 | 299 | 7153 | 42.98 | 683.5383 | 0 | 0 | 683.5383 | Heating | 603.122 | 8.5 | 603.122 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.6244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 615.4306 | 0 | 123.0861 | 1.231% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 02:01 | 10 | 26 | 2 | 299 | 7154 | 42.98 | 703.2658 | 0 | 0 | 703.2658 | Heating | 620.5287 | 8.5 | 620.5287 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.1057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 633.1925 | 0 | 126.6385 | 1.266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 03:01 | 10 | 26 | 3 | 299 | 7155 | 37.94 | 719.5988 | 0 | 0 | 719.5988 | Heating | 634.9402 | 8.5 | 634.9402 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.988 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 647.8981 | 0 | 129.5796 | 1.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 04:01 | 10 | 26 | 4 | 299 | 7156 | 39.92 | 731.1084 | 0 | 0 | 731.1084 | Heating | 645.0956 | 8.5 | 645.0956 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.0191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 658.2608 | 0 | 131.6522 | 1.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 05:01 | 10 | 26 | 5 | 299 | 7157 | 39.92 | 717.4258 | 0 | 0 | 717.4258 | Heating | 633.0228 | 8.5 | 633.0228 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.6046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 645.9416 | 0 | 129.1883 | 1.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 06:01 | 10 | 26 | 6 | 299 | 7158 | 37.94 | 6496.4659 | 0 | 0 | 6496.4659 | Heating | 5732.1758 | 8.5 | 5732.1758 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1146.4352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5849.159 | 0 | 1169.8318 | 11.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 07:01 | 10 | 26 | 7 | 299 | 7159 | 35.96 | 4689.8292 | 0 | 0 | 4689.8292 | Heating | 4138.0846 | 8.5 | 4138.0846 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 827.6169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4222.5353 | 0 | 844.5071 | 8.445% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 08:01 | 10 | 26 | 8 | 299 | 7160 | 35.96 | 3972.6727 | 0 | 0 | 3972.6727 | Heating | 3505.2994 | 8.5 | 3505.2994 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 701.0599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3576.8362 | 0 | 715.3672 | 7.154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 09:01 | 10 | 26 | 9 | 299 | 7161 | 42.98 | 3097.6232 | 0 | 0 | 3097.6232 | Heating | 2733.197 | 8.5 | 2733.197 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 546.6394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2788.9765 | 0 | 557.7953 | 5.578% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 10:01 | 10 | 26 | 10 | 299 | 7162 | 44.06 | 2430.2698 | 0 | 0 | 2430.2698 | Heating | 2144.3557 | 8.5 | 2144.3557 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 428.8711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2188.1181 | 0 | 437.6236 | 4.376% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 11:01 | 10 | 26 | 11 | 299 | 7163 | 44.06 | 1931.5144 | 0 | 0 | 1931.5144 | Heating | 1704.2774 | 8.5 | 1704.2774 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.8555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1739.0586 | 0 | 347.8117 | 3.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 12:01 | 10 | 26 | 12 | 299 | 7164 | 46.04 | 1635.3618 | 0 | 0 | 1635.3618 | Heating | 1442.9663 | 8.5 | 1442.9663 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 288.5933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1472.4146 | 0 | 294.4829 | 2.945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 13:01 | 10 | 26 | 13 | 299 | 7165 | 44.06 | 1406.8978 | 0 | 0 | 1406.8978 | Heating | 1241.3804 | 8.5 | 1241.3804 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.2761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1266.7147 | 0 | 253.3429 | 2.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 14:01 | 10 | 26 | 14 | 299 | 7166 | 44.06 | 1302.3722 | 0 | 0 | 1302.3722 | Heating | 1149.1519 | 8.5 | 1149.1519 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.8304 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1172.604 | 0 | 234.5208 | 2.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 15:01 | 10 | 26 | 15 | 299 | 7167 | 44.06 | 1237.7484 | 0 | 0 | 1237.7484 | Heating | 1092.1309 | 8.5 | 1092.1309 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.4262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1114.4193 | 0 | 222.8839 | 2.229% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 16:01 | 10 | 26 | 16 | 299 | 7168 | 44.06 | 1253.894 | 0 | 0 | 1253.894 | Heating | 1106.3771 | 8.5 | 1106.3771 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.2754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1128.9562 | 0 | 225.7912 | 2.258% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 17:01 | 10 | 26 | 17 | 299 | 7169 | 44.06 | 1376.587 | 0 | 0 | 1376.587 | Heating | 1214.6356 | 8.5 | 1214.6356 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.9271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1239.4241 | 0 | 247.8848 | 2.479% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 18:01 | 10 | 26 | 18 | 299 | 7170 | 42.08 | 1812.4252 | 0 | 0 | 1812.4252 | Heating | 1599.1987 | 8.5 | 1599.1987 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 319.8397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1631.8354 | 0 | 326.3671 | 3.264% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 19:01 | 10 | 26 | 19 | 299 | 7171 | 42.08 | 2013.6029 | 0 | 0 | 2013.6029 | Heating | 1776.7084 | 8.5 | 1776.7084 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 355.3417 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1812.9678 | 0 | 362.5936 | 3.626% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 20:01 | 10 | 26 | 20 | 299 | 7172 | 42.08 | 2178.4596 | 0 | 0 | 2178.4596 | Heating | 1922.1702 | 8.5 | 1922.1702 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.434 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1961.3982 | 0 | 392.2796 | 3.923% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 21:01 | 10 | 26 | 21 | 299 | 7173 | 39.02 | 2546.1047 | 0 | 0 | 2546.1047 | Heating | 2246.5629 | 8.5 | 2246.5629 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.3126 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2292.4112 | 0 | 458.4822 | 4.585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 22:01 | 10 | 26 | 22 | 299 | 7174 | 35.96 | 513.2371 | 0 | 0 | 513.2371 | Heating | 452.8563 | 8.5 | 452.8563 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 90.5713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 462.0983 | 0 | 92.4197 | 0.9242% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-26 23:01 | 10 | 26 | 23 | 299 | 7175 | 35.96 | 541.4775 | 0 | 0 | 541.4775 | Heating | 477.7743 | 8.5 | 477.7743 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.5549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 487.5248 | 0 | 97.505 | 0.975% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 00:01 | 10 | 27 | 0 | 300 | 7176 | 37.04 | 567.3702 | 0 | 0 | 567.3702 | Heating | 500.6208 | 8.5 | 500.6208 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 100.1242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 510.8376 | 0 | 102.1675 | 1.022% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 01:01 | 10 | 27 | 1 | 300 | 7177 | 39.02 | 581.0759 | 0 | 0 | 581.0759 | Heating | 512.7141 | 8.5 | 512.7141 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 102.5428 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 523.1776 | 0 | 104.6355 | 1.046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 02:01 | 10 | 27 | 2 | 300 | 7178 | 39.02 | 602.8373 | 0 | 0 | 602.8373 | Heating | 531.9153 | 8.5 | 531.9153 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.3831 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.7707 | 0 | 108.5541 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 03:01 | 10 | 27 | 3 | 300 | 7179 | 39.02 | 607.9864 | 0 | 0 | 607.9864 | Heating | 536.4586 | 8.5 | 536.4586 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.2917 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 547.4067 | 0 | 109.4813 | 1.095% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 04:01 | 10 | 27 | 4 | 300 | 7180 | 39.02 | 602.9011 | 0 | 0 | 602.9011 | Heating | 531.9715 | 8.5 | 531.9715 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.3943 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 542.8281 | 0 | 108.5656 | 1.086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 05:01 | 10 | 27 | 5 | 300 | 7181 | 39.02 | 606.1612 | 0 | 0 | 606.1612 | Heating | 534.8482 | 8.5 | 534.8482 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 106.9696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 545.7634 | 0 | 109.1527 | 1.092% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 06:01 | 10 | 27 | 6 | 300 | 7182 | 37.94 | 600.3748 | 0 | 0 | 600.3748 | Heating | 529.7425 | 8.5 | 529.7425 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.9485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 540.5536 | 0 | 108.1107 | 1.081% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 07:01 | 10 | 27 | 7 | 300 | 7183 | 33.98 | 597.8989 | 0 | 0 | 597.8989 | Heating | 527.5579 | 8.5 | 527.5579 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 105.5116 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 538.3244 | 0 | 107.6649 | 1.077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 08:01 | 10 | 27 | 8 | 300 | 7184 | 33.98 | 5437.5823 | 0 | 0 | 5437.5823 | Heating | 4797.8668 | 8.5 | 4797.8668 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 959.5734 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4895.7824 | 0 | 979.1565 | 9.792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 09:01 | 10 | 27 | 9 | 300 | 7185 | 41 | 3877.8858 | 0 | 0 | 3877.8858 | Heating | 3421.664 | 8.5 | 3421.664 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 684.3328 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3491.4938 | 0 | 698.2988 | 6.983% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 10:01 | 10 | 27 | 10 | 300 | 7186 | 42.08 | 3049.9025 | 0 | 0 | 3049.9025 | Heating | 2691.0904 | 8.5 | 2691.0904 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 538.2181 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2746.0106 | 0 | 549.2021 | 5.492% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 11:01 | 10 | 27 | 11 | 300 | 7187 | 42.08 | 2539.5644 | 0 | 0 | 2539.5644 | Heating | 2240.7922 | 8.5 | 2240.7922 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 448.1584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2286.5226 | 0 | 457.3045 | 4.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 12:01 | 10 | 27 | 12 | 300 | 7188 | 42.98 | 1890.8618 | 0 | 0 | 1890.8618 | Heating | 1668.4075 | 8.5 | 1668.4075 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 333.6815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1702.4566 | 0 | 340.4913 | 3.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 13:01 | 10 | 27 | 13 | 300 | 7189 | 44.06 | 1561.575 | 0 | 0 | 1561.575 | Heating | 1377.8603 | 8.5 | 1377.8603 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 275.5721 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1405.9799 | 0 | 281.196 | 2.812% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 14:01 | 10 | 27 | 14 | 300 | 7190 | 44.06 | 1414.8767 | 0 | 0 | 1414.8767 | Heating | 1248.4206 | 8.5 | 1248.4206 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.6841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1273.8986 | 0 | 254.7797 | 2.548% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 15:01 | 10 | 27 | 15 | 300 | 7191 | 42.98 | 1351.8216 | 0 | 0 | 1351.8216 | Heating | 1192.7838 | 8.5 | 1192.7838 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.5568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1217.1263 | 0 | 243.4253 | 2.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 16:01 | 10 | 27 | 16 | 300 | 7192 | 42.08 | 1304.1275 | 0 | 0 | 1304.1275 | Heating | 1150.7008 | 8.5 | 1150.7008 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.1402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1174.1845 | 0 | 234.8369 | 2.348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 17:01 | 10 | 27 | 17 | 300 | 7193 | 42.08 | 2090.5263 | 0 | 0 | 2090.5263 | Heating | 1844.582 | 8.5 | 1844.582 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.9164 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1882.2265 | 0 | 376.4453 | 3.764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 18:01 | 10 | 27 | 18 | 300 | 7194 | 35.96 | 2366.5061 | 0 | 0 | 2366.5061 | Heating | 2088.0937 | 8.5 | 2088.0937 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 417.6187 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2130.7078 | 0 | 426.1416 | 4.261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 19:01 | 10 | 27 | 19 | 300 | 7195 | 35.96 | 338.3604 | 0 | 0 | 338.3604 | Heating | 298.5533 | 8.5 | 298.5533 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.7107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 304.6462 | 0 | 60.9292 | 0.6093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 20:01 | 10 | 27 | 20 | 300 | 7196 | 35.96 | 358.1824 | 0 | 0 | 358.1824 | Heating | 316.0433 | 8.5 | 316.0433 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 63.2087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 322.4932 | 0 | 64.4986 | 0.645% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 21:01 | 10 | 27 | 21 | 300 | 7197 | 33.98 | 372.8797 | 0 | 0 | 372.8797 | Heating | 329.0115 | 8.5 | 329.0115 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.8023 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 335.726 | 0 | 67.1452 | 0.6715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 22:01 | 10 | 27 | 22 | 300 | 7198 | 33.08 | 401.9675 | 0 | 0 | 401.9675 | Heating | 354.6772 | 8.5 | 354.6772 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.9354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 361.9155 | 0 | 72.3831 | 0.7238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-27 23:01 | 10 | 27 | 23 | 300 | 7199 | 33.08 | 416.9335 | 0 | 0 | 416.9335 | Heating | 367.8825 | 8.5 | 367.8825 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.5765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 375.3903 | 0 | 75.0781 | 0.7508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 00:01 | 10 | 28 | 0 | 301 | 7200 | 33.08 | 445.7937 | 0 | 0 | 445.7937 | Heating | 393.3474 | 8.5 | 393.3474 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.6695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 401.3749 | 0 | 80.275 | 0.8027% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 01:01 | 10 | 28 | 1 | 301 | 7201 | 32 | 469.0908 | 0 | 0 | 469.0908 | Heating | 413.9037 | 8.5 | 413.9037 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.7807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 422.3507 | 0 | 84.4701 | 0.8447% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 02:01 | 10 | 28 | 2 | 301 | 7202 | 32 | 465.6541 | 0 | 0 | 465.6541 | Heating | 410.8712 | 8.5 | 410.8712 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 82.1742 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 419.2564 | 0 | 83.8513 | 0.8385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 03:01 | 10 | 28 | 3 | 301 | 7203 | 32 | 462.5019 | 0 | 0 | 462.5019 | Heating | 408.0899 | 8.5 | 408.0899 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 416.4182 | 0 | 83.2836 | 0.8328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 04:01 | 10 | 28 | 4 | 301 | 7204 | 30.92 | 463.1469 | 0 | 0 | 463.1469 | Heating | 408.659 | 8.5 | 408.659 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.7318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 416.999 | 0 | 83.3998 | 0.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 05:01 | 10 | 28 | 5 | 301 | 7205 | 30.92 | 454.2387 | 0 | 0 | 454.2387 | Heating | 400.7989 | 8.5 | 400.7989 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.1598 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 408.9785 | 0 | 81.7957 | 0.818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 06:01 | 10 | 28 | 6 | 301 | 7206 | 32 | 4872.9491 | 24.2853 | 24.2853 | 4848.6638 | Heating | 4278.2328 | 8.5 | 4278.2328 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 855.6466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4365.5437 | 0 | 873.1087 | 8.731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 07:01 | 10 | 28 | 7 | 301 | 7207 | 32 | 3695.7626 | 0 | 0 | 3695.7626 | Heating | 3260.967 | 8.5 | 3260.967 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 652.1934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3327.5173 | 0 | 665.5035 | 6.655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 08:01 | 10 | 28 | 8 | 301 | 7208 | 32 | 2507.2538 | 0 | 0 | 2507.2538 | Heating | 2212.2828 | 8.5 | 2212.2828 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 442.4566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2257.4314 | 0 | 451.4863 | 4.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 09:01 | 10 | 28 | 9 | 301 | 7209 | 35.06 | 1203.0033 | 0 | 0 | 1203.0033 | Heating | 1061.4735 | 8.5 | 1061.4735 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.2947 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1083.1362 | 0 | 216.6272 | 2.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 10:01 | 10 | 28 | 10 | 301 | 7210 | 35.06 | 642.3061 | 0 | 0 | 642.3061 | Heating | 566.7407 | 8.5 | 566.7407 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.3481 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 578.3068 | 0 | 115.6614 | 1.157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 11:01 | 10 | 28 | 11 | 301 | 7211 | 35.06 | 392.15 | 0 | 0 | 392.15 | Heating | 346.0147 | 8.5 | 346.0147 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 69.2029 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 353.0762 | 0 | 70.6152 | 0.7062% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 12:01 | 10 | 28 | 12 | 301 | 7212 | 33.08 | 284.217 | 0 | 0 | 284.217 | Heating | 250.7797 | 8.5 | 250.7797 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.1559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 255.8977 | 0 | 51.1795 | 0.5118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 13:01 | 10 | 28 | 13 | 301 | 7213 | 33.08 | 229.5611 | 0.76865 | 0.76865 | 228.7924 | Heating | 201.8757 | 8.5 | 201.8757 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.3751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 205.9956 | 0 | 41.1991 | 0.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 14:01 | 10 | 28 | 14 | 301 | 7214 | 33.08 | 226.7745 | 6.36 | 6.36 | 220.4145 | Heating | 194.4834 | 8.5 | 194.4834 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.8967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 198.4524 | 0 | 39.6905 | 0.3969% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 15:01 | 10 | 28 | 15 | 301 | 7215 | 33.08 | 231.719 | 22.6264 | 22.6264 | 209.0927 | Heating | 184.4935 | 8.5 | 184.4935 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.8987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 188.2587 | 0 | 37.6517 | 0.3765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 16:01 | 10 | 28 | 16 | 301 | 7216 | 33.08 | 216.1134 | 57.6606 | 57.6606 | 158.4528 | Heating | 139.8113 | 8.5 | 139.8113 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.9623 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 142.6646 | 0 | 28.5329 | 0.2853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 17:01 | 10 | 28 | 17 | 301 | 7217 | 32 | 252.1957 | 11.2464 | 11.2464 | 240.9493 | Heating | 212.6024 | 8.5 | 212.6024 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 42.5205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 216.9412 | 0 | 43.3882 | 0.4339% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 18:01 | 10 | 28 | 18 | 301 | 7218 | 33.08 | 461.5095 | 0 | 0 | 461.5095 | Heating | 407.2143 | 8.5 | 407.2143 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.4429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 415.5248 | 0 | 83.105 | 0.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 19:01 | 10 | 28 | 19 | 301 | 7219 | 33.98 | 770.4167 | 0 | 0 | 770.4167 | Heating | 679.7794 | 8.5 | 679.7794 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.9559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 693.6525 | 0 | 138.7305 | 1.387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 20:01 | 10 | 28 | 20 | 301 | 7220 | 33.98 | 1099.2394 | 0 | 0 | 1099.2394 | Heating | 969.9171 | 8.5 | 969.9171 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 193.9834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 989.7113 | 0 | 197.9423 | 1.979% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 21:01 | 10 | 28 | 21 | 301 | 7221 | 33.08 | 317.6938 | 0 | 0 | 317.6938 | Heating | 280.3181 | 8.5 | 280.3181 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 56.0636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 286.0389 | 0 | 57.2078 | 0.5721% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 22:01 | 10 | 28 | 22 | 301 | 7222 | 33.08 | 492.474 | 0 | 0 | 492.474 | Heating | 434.5359 | 8.5 | 434.5359 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 86.9072 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 443.404 | 0 | 88.6808 | 0.8868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-28 23:01 | 10 | 28 | 23 | 301 | 7223 | 33.08 | 610.1176 | 0 | 0 | 610.1176 | Heating | 538.3391 | 8.5 | 538.3391 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.6678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 549.3256 | 0 | 109.8651 | 1.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 00:01 | 10 | 29 | 0 | 302 | 7224 | 33.8 | 700.5533 | 0 | 0 | 700.5533 | Heating | 618.1352 | 8.5 | 618.1352 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.627 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 630.7502 | 0 | 126.15 | 1.262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 01:01 | 10 | 29 | 1 | 302 | 7225 | 33.98 | 758.4674 | 0 | 0 | 758.4674 | Heating | 669.2359 | 8.5 | 669.2359 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 133.8472 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 682.8938 | 0 | 136.5788 | 1.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 02:01 | 10 | 29 | 2 | 302 | 7226 | 33.98 | 760.1151 | 0 | 0 | 760.1151 | Heating | 670.6898 | 8.5 | 670.6898 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 134.138 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 684.3774 | 0 | 136.8755 | 1.369% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 03:01 | 10 | 29 | 3 | 302 | 7227 | 33.98 | 771.9774 | 0 | 0 | 771.9774 | Heating | 681.1565 | 8.5 | 681.1565 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.2313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 695.0577 | 0 | 139.0115 | 1.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 04:01 | 10 | 29 | 4 | 302 | 7228 | 35.06 | 780.3071 | 0 | 0 | 780.3071 | Heating | 688.5063 | 8.5 | 688.5063 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.7013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 702.5574 | 0 | 140.5115 | 1.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 05:01 | 10 | 29 | 5 | 302 | 7229 | 35.06 | 766.9643 | 0 | 0 | 766.9643 | Heating | 676.7332 | 8.5 | 676.7332 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.3466 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 690.5441 | 0 | 138.1088 | 1.381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 06:01 | 10 | 29 | 6 | 302 | 7230 | 35.06 | 6916.2815 | 0 | 0 | 6916.2815 | Heating | 6102.6013 | 8.5 | 6102.6013 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1220.5203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6227.1442 | 0 | 1245.4288 | 12.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 07:01 | 10 | 29 | 7 | 302 | 7231 | 37.94 | 5317.1409 | 0 | 0 | 5317.1409 | Heating | 4691.5949 | 8.5 | 4691.5949 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 938.319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4787.3418 | 0 | 957.4684 | 9.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 08:01 | 10 | 29 | 8 | 302 | 7232 | 37.94 | 3923.9066 | 0 | 0 | 3923.9066 | Heating | 3462.2705 | 8.5 | 3462.2705 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 692.4541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3532.9291 | 0 | 706.5858 | 7.066% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 09:01 | 10 | 29 | 9 | 302 | 7233 | 39.02 | 2515.3177 | 0 | 0 | 2515.3177 | Heating | 2219.398 | 8.5 | 2219.398 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 443.8796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2264.6918 | 0 | 452.9384 | 4.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 10:01 | 10 | 29 | 10 | 302 | 7234 | 41 | 1575.3076 | 4.831 | 4.831 | 1570.4766 | Heating | 1385.7147 | 8.5 | 1385.7147 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 277.1429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1413.9946 | 0 | 282.7989 | 2.828% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 11:01 | 10 | 29 | 11 | 302 | 7235 | 41 | 612.5699 | 70.0869 | 70.0869 | 542.4829 | Heating | 478.6614 | 8.5 | 478.6614 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.7323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 488.43 | 0 | 97.686 | 0.9769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 12:01 | 10 | 29 | 12 | 302 | 7236 | 42.08 | 196.6145 | 198.0193 | 198.0193 | -1.4048 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 242.0236 | 242.0236 | 0 | 8.5 | 0 | 40.3373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 237.1831 | 47.4366 | 0.4744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 13:01 | 10 | 29 | 13 | 302 | 7237 | 44.06 | 99.3421 | 466.3534 | 466.3534 | -367.0114 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 569.9875 | 569.9875 | 0 | 8.5 | 0 | 94.9979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 558.5878 | 111.7176 | 1.117% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 14:01 | 10 | 29 | 14 | 302 | 7238 | 44.96 | 41.3326 | 1318.0258 | 1318.0258 | -1276.6932 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1610.9204 | 1610.9204 | 0 | 8.5 | 0 | 268.4867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1578.702 | 315.7404 | 3.157% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 15:01 | 10 | 29 | 15 | 302 | 7239 | 46.04 | 12.1495 | 2039.7816 | 2039.7816 | -2027.6321 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2493.0664 | 2493.0664 | 0 | 8.5 | 0 | 415.5111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2443.2051 | 488.641 | 4.886% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 16:01 | 10 | 29 | 16 | 302 | 7240 | 44.96 | 4.428 | 2053.3588 | 2053.3588 | -2048.9308 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 2509.6608 | 2509.6608 | 0 | 8.5 | 0 | 418.2768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 2459.4676 | 491.8935 | 4.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 17:01 | 10 | 29 | 17 | 302 | 7241 | 44.96 | 3.9773 | 1167.043 | 1167.043 | -1163.0657 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 1426.3859 | 1426.3859 | 0 | 8.5 | 0 | 237.731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 1397.8582 | 279.5716 | 2.796% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 18:01 | 10 | 29 | 18 | 302 | 7242 | 42.08 | 10.0941 | 272.8512 | 272.8512 | -262.7571 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 333.4848 | 333.4848 | 0 | 8.5 | 0 | 55.5808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 326.8151 | 65.363 | 0.6536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 19:01 | 10 | 29 | 19 | 302 | 7243 | 42.08 | 35.6791 | 154.1209 | 154.1209 | -118.4418 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 188.37 | 188.37 | 0 | 8.5 | 0 | 31.395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 184.6026 | 36.9205 | 0.3692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 20:01 | 10 | 29 | 20 | 302 | 7244 | 42.08 | 104.9912 | 78.0989 | 78.0989 | 26.8922 | Heating | 23.7284 | 8.5 | 23.7284 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 4.7457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 24.2127 | 0 | 4.8425 | 0.04843% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 21:01 | 10 | 29 | 21 | 302 | 7245 | 41 | 92.5263 | 57.6546 | 57.6546 | 34.8717 | Heating | 30.7692 | 8.5 | 30.7692 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.1538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 31.3971 | 0 | 6.2794 | 0.06279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 22:01 | 10 | 29 | 22 | 302 | 7246 | 39.92 | 91.9428 | 0 | 0 | 91.9428 | Heating | 81.126 | 8.5 | 81.126 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.2252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 82.7816 | 0 | 16.5563 | 0.1656% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-29 23:01 | 10 | 29 | 23 | 302 | 7247 | 39.92 | 81.2114 | 0 | 0 | 81.2114 | Heating | 71.6571 | 8.5 | 71.6571 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 14.3314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 73.1195 | 0 | 14.6239 | 0.1462% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 00:01 | 10 | 30 | 0 | 303 | 7248 | 39.02 | 93.2771 | 0 | 0 | 93.2771 | Heating | 82.3033 | 8.5 | 82.3033 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 16.4607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 83.983 | 0 | 16.7966 | 0.168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 01:01 | 10 | 30 | 1 | 303 | 7249 | 39.02 | 129.1499 | 0 | 0 | 129.1499 | Heating | 113.9558 | 8.5 | 113.9558 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 22.7912 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 116.2814 | 0 | 23.2563 | 0.2326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 02:01 | 10 | 30 | 2 | 303 | 7250 | 39.02 | 154.4534 | 0 | 0 | 154.4534 | Heating | 136.2824 | 8.5 | 136.2824 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.2565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 139.0637 | 0 | 27.8127 | 0.2781% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 03:01 | 10 | 30 | 3 | 303 | 7251 | 37.94 | 176.7848 | 0 | 0 | 176.7848 | Heating | 155.9866 | 8.5 | 155.9866 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 31.1973 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 159.17 | 0 | 31.834 | 0.3183% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 04:01 | 10 | 30 | 4 | 303 | 7252 | 37.04 | 207.0636 | 0 | 0 | 207.0636 | Heating | 182.7032 | 8.5 | 182.7032 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 36.5406 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 186.4318 | 0 | 37.2864 | 0.3729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 05:01 | 10 | 30 | 5 | 303 | 7253 | 37.04 | 243.8825 | 0 | 0 | 243.8825 | Heating | 215.1904 | 8.5 | 215.1904 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.0381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 219.5821 | 0 | 43.9164 | 0.4392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 06:01 | 10 | 30 | 6 | 303 | 7254 | 37.04 | 3179.7063 | 59.4651 | 59.4651 | 3120.2412 | Heating | 2753.154 | 8.5 | 2753.154 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.6308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2809.3408 | 0 | 561.8682 | 5.619% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 07:01 | 10 | 30 | 7 | 303 | 7255 | 37.94 | 2332.9071 | 0 | 0 | 2332.9071 | Heating | 2058.4475 | 8.5 | 2058.4475 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.6895 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2100.4566 | 0 | 420.0913 | 4.201% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 08:01 | 10 | 30 | 8 | 303 | 7256 | 37.94 | 1877.792 | 8.1768 | 8.1768 | 1869.6152 | Heating | 1649.6605 | 8.5 | 1649.6605 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.9321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1683.327 | 0 | 336.6654 | 3.367% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 09:01 | 10 | 30 | 9 | 303 | 7257 | 39.02 | 1236.2844 | 34.473 | 34.473 | 1201.8114 | Heating | 1060.4219 | 8.5 | 1060.4219 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.0844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1082.0631 | 0 | 216.4126 | 2.164% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 10:01 | 10 | 30 | 10 | 303 | 7258 | 39.92 | 959.0967 | 84.5807 | 84.5807 | 874.516 | Heating | 771.6317 | 8.5 | 771.6317 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.3263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 787.3793 | 0 | 157.4759 | 1.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 11:01 | 10 | 30 | 11 | 303 | 7259 | 39.92 | 640.222 | 202.554 | 202.554 | 437.668 | Heating | 386.1776 | 8.5 | 386.1776 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.2355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 394.0588 | 0 | 78.8118 | 0.7881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 12:01 | 10 | 30 | 12 | 303 | 7260 | 46.04 | 431.2294 | 282.5474 | 282.5474 | 148.682 | Heating | 131.19 | 8.5 | 131.19 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 26.238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 133.8674 | 0 | 26.7735 | 0.2677% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 13:01 | 10 | 30 | 13 | 303 | 7261 | 48.02 | 306.8562 | 434.853 | 434.853 | -127.9968 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 531.487 | 531.487 | 0 | 8.5 | 0 | 88.5812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 520.8572 | 104.1714 | 1.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 14:01 | 10 | 30 | 14 | 303 | 7262 | 48.02 | 302.896 | 513.4714 | 513.4714 | -210.5754 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 627.5762 | 627.5762 | 0 | 8.5 | 0 | 104.596 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 615.0247 | 123.0049 | 1.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 15:01 | 10 | 30 | 15 | 303 | 7263 | 51.98 | 348.8872 | 458.7151 | 458.7151 | -109.8279 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 560.6518 | 560.6518 | 0 | 8.5 | 0 | 93.442 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 549.4388 | 109.8878 | 1.099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 16:01 | 10 | 30 | 16 | 303 | 7264 | 53.06 | 562.1829 | 325.6491 | 325.6491 | 236.5338 | Heating | 208.7063 | 8.5 | 208.7063 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.7413 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 212.9656 | 0 | 42.5931 | 0.4259% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 17:01 | 10 | 30 | 17 | 303 | 7265 | 53.06 | 1000.7524 | 143.0946 | 143.0946 | 857.6578 | Heating | 756.7569 | 8.5 | 756.7569 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.3514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 772.2009 | 0 | 154.4402 | 1.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 18:01 | 10 | 30 | 18 | 303 | 7266 | 46.94 | 1619.5545 | 51.1763 | 51.1763 | 1568.3782 | Heating | 1383.8631 | 8.5 | 1383.8631 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 276.7726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1412.1052 | 0 | 282.421 | 2.824% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 19:01 | 10 | 30 | 19 | 303 | 7267 | 46.04 | 2238.6637 | 23.0809 | 23.0809 | 2215.5828 | Heating | 1954.926 | 8.5 | 1954.926 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.9852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1994.8224 | 0 | 398.9645 | 3.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 20:01 | 10 | 30 | 20 | 303 | 7268 | 46.04 | 2889.4872 | 0 | 0 | 2889.4872 | Heating | 2549.5475 | 8.5 | 2549.5475 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 509.9095 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2601.5791 | 0 | 520.3158 | 5.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 21:01 | 10 | 30 | 21 | 303 | 7269 | 42.98 | 692.7485 | 0 | 0 | 692.7485 | Heating | 611.2487 | 8.5 | 611.2487 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.2497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 623.7232 | 0 | 124.7446 | 1.247% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 22:01 | 10 | 30 | 22 | 303 | 7270 | 41 | 788.2375 | 0 | 0 | 788.2375 | Heating | 695.5037 | 8.5 | 695.5037 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.1007 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 709.6977 | 0 | 141.9395 | 1.419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-30 23:01 | 10 | 30 | 23 | 303 | 7271 | 41 | 880.3861 | 0 | 0 | 880.3861 | Heating | 776.8113 | 8.5 | 776.8113 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.3623 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 792.6646 | 0 | 158.5329 | 1.585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 00:01 | 10 | 31 | 0 | 304 | 7272 | 46.04 | 975.9348 | 0 | 0 | 975.9348 | Heating | 861.1189 | 8.5 | 861.1189 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.2238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 878.6928 | 0 | 175.7386 | 1.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 01:01 | 10 | 31 | 1 | 304 | 7273 | 55.04 | 1078.3619 | 0 | 0 | 1078.3619 | Heating | 951.4958 | 8.5 | 951.4958 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.2992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 970.914 | 0 | 194.1828 | 1.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 02:01 | 10 | 31 | 2 | 304 | 7274 | 55.04 | 1153.072 | 0 | 0 | 1153.072 | Heating | 1017.4165 | 8.5 | 1017.4165 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 203.4833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1038.1801 | 0 | 207.636 | 2.076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 03:01 | 10 | 31 | 3 | 304 | 7275 | 59 | 1324.9289 | 0 | 0 | 1324.9289 | Heating | 1169.0549 | 8.5 | 1169.0549 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1192.9132 | 0 | 238.5826 | 2.386% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 04:01 | 10 | 31 | 4 | 304 | 7276 | 53.96 | 1412.8309 | 0 | 0 | 1412.8309 | Heating | 1246.6155 | 8.5 | 1246.6155 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.3231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1272.0566 | 0 | 254.4113 | 2.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 05:01 | 10 | 31 | 5 | 304 | 7277 | 53.96 | 1565.0885 | 0 | 0 | 1565.0885 | Heating | 1380.9604 | 8.5 | 1380.9604 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 276.1921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1409.1433 | 0 | 281.8287 | 2.818% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 06:01 | 10 | 31 | 6 | 304 | 7278 | 53.96 | 1569.9025 | 0 | 0 | 1569.9025 | Heating | 1385.2081 | 8.5 | 1385.2081 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 277.0416 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1413.4776 | 0 | 282.6955 | 2.827% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 07:01 | 10 | 31 | 7 | 304 | 7279 | 53.96 | 11204.1342 | 0 | 0 | 11204.1342 | Heating | 9886.0008 | 8.5 | 9886.0008 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1977.2002 | 39.54% | 1 | 79.09% | 0% | 0% | 0% | 47.5114 | 0 | 0 | 0 | 47.5114 | 10087.7559 | 0 | 2017.5512 | 20.18% | 1 | 40.35% | 0% | 0% | 5.0533 | 0 | 0 | 5.0533 | 52.5647
2007-10-31 08:01 | 10 | 31 | 8 | 304 | 7280 | 53.96 | 8142.6432 | 0 | 0 | 8142.6432 | Heating | 7184.6852 | 8.5 | 7184.6852 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1436.937 | 30% | 1 | 57.48% | 0% | 0% | 0% | 22.8028 | 0 | 0 | 0 | 22.8028 | 7331.3114 | 0 | 1466.2623 | 14.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.0773
2007-10-31 09:01 | 10 | 31 | 9 | 304 | 7281 | 57.92 | 5886.4663 | 0 | 0 | 5886.4663 | Heating | 5193.9409 | 8.5 | 5193.9409 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1038.7882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5299.9397 | 0 | 1059.9879 | 10.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 10:01 | 10 | 31 | 10 | 304 | 7282 | 57.02 | 4096.8299 | 1.061 | 1.061 | 4095.7689 | Heating | 3613.9137 | 8.5 | 3613.9137 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 722.7827 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3687.6671 | 0 | 737.5334 | 7.375% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 11:01 | 10 | 31 | 11 | 304 | 7283 | 57.02 | 2769.3866 | 41.5723 | 41.5723 | 2727.8143 | Heating | 2406.8949 | 8.5 | 2406.8949 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 481.379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2456.0153 | 0 | 491.2031 | 4.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 12:01 | 10 | 31 | 12 | 304 | 7284 | 57.92 | 1915.2366 | 160.0013 | 160.0013 | 1755.2353 | Heating | 1548.7371 | 8.5 | 1548.7371 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 309.7474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1580.3439 | 0 | 316.0688 | 3.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 13:01 | 10 | 31 | 13 | 304 | 7285 | 57.92 | 1554.9356 | 284.6504 | 284.6504 | 1270.2852 | Heating | 1120.8399 | 8.5 | 1120.8399 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.168 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1143.7142 | 0 | 228.7428 | 2.287% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 14:01 | 10 | 31 | 14 | 304 | 7286 | 57.92 | 1135.6756 | 383.6172 | 383.6172 | 752.0584 | Heating | 663.581 | 8.5 | 663.581 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.7162 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 677.1234 | 0 | 135.4247 | 1.354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 15:01 | 10 | 31 | 15 | 304 | 7287 | 53.96 | 880.2867 | 409.0172 | 409.0172 | 471.2695 | Heating | 415.826 | 8.5 | 415.826 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 83.1652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 424.3123 | 0 | 84.8625 | 0.8486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 16:01 | 10 | 31 | 16 | 304 | 7288 | 51.98 | 770.8473 | 343.9463 | 343.9463 | 426.901 | Heating | 376.6773 | 8.5 | 376.6773 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 75.3355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 384.3646 | 0 | 76.8729 | 0.7687% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 17:01 | 10 | 31 | 17 | 304 | 7289 | 51.98 | 1246.1479 | 185.4527 | 185.4527 | 1060.6952 | Heating | 935.9075 | 8.5 | 935.9075 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 187.1815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 955.0077 | 0 | 191.0015 | 1.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 18:01 | 10 | 31 | 18 | 304 | 7290 | 51.08 | 1811.4192 | 87.4672 | 87.4672 | 1723.952 | Heating | 1521.1341 | 8.5 | 1521.1341 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 304.2268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1552.1777 | 0 | 310.4355 | 3.104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 19:01 | 10 | 31 | 19 | 304 | 7291 | 44.96 | 2102.1313 | 41.1707 | 41.1707 | 2060.9606 | Heating | 1818.4946 | 8.5 | 1818.4946 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.6989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1855.6068 | 0 | 371.1214 | 3.711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 20:01 | 10 | 31 | 20 | 304 | 7292 | 44.06 | 2408.2245 | 20.1376 | 20.1376 | 2388.0869 | Heating | 2107.1355 | 8.5 | 2107.1355 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.4271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2150.1383 | 0 | 430.0277 | 4.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 21:01 | 10 | 31 | 21 | 304 | 7293 | 43.16 | 2588.577 | 0 | 0 | 2588.577 | Heating | 2284.0385 | 8.5 | 2284.0385 | 0 | 3.9517 | 0 | 0 | 0 | 0 | 8.5 | 0 | 456.8077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2330.6515 | 0 | 466.1303 | 4.661% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 22:01 | 10 | 31 | 22 | 304 | 7294 | 42.98 | 635.7804 | 0 | 0 | 635.7804 | Heating | 560.9827 | 8.5 | 560.9827 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 112.1965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 572.4313 | 0 | 114.4863 | 1.145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-10-31 23:01 | 10 | 31 | 23 | 304 | 7295 | 42.8 | 613.3283 | 0 | 0 | 613.3283 | Heating | 541.172 | 8.5 | 541.172 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.2344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 552.2164 | 0 | 110.4433 | 1.104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 00:01 | 11 | 1 | 0 | 305 | 7296 | 41.9 | 628.8738 | 0 | 0 | 628.8738 | Heating | 554.8886 | 8.5 | 554.8886 | 0 | 3.8636 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.9777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 566.2129 | 0 | 113.2426 | 1.132% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 01:01 | 11 | 1 | 1 | 305 | 7297 | 41 | 633.722 | 0 | 0 | 633.722 | Heating | 559.1665 | 8.5 | 559.1665 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.8333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 570.5781 | 0 | 114.1156 | 1.141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 02:01 | 11 | 1 | 2 | 305 | 7298 | 39.92 | 627.0649 | 0 | 0 | 627.0649 | Heating | 553.2925 | 8.5 | 553.2925 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.6585 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 564.5842 | 0 | 112.9168 | 1.129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 03:01 | 11 | 1 | 3 | 305 | 7299 | 38.48 | 620.7897 | 0 | 0 | 620.7897 | Heating | 547.7556 | 8.5 | 547.7556 | 0 | 3.6462 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.5511 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 558.9343 | 0 | 111.7869 | 1.118% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 04:01 | 11 | 1 | 4 | 305 | 7300 | 37.4 | 612.9325 | 0 | 0 | 612.9325 | Heating | 540.8228 | 8.5 | 540.8228 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.1646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 551.86 | 0 | 110.372 | 1.104% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 05:01 | 11 | 1 | 5 | 305 | 7301 | 36.68 | 608.1528 | 0 | 0 | 608.1528 | Heating | 536.6054 | 8.5 | 536.6054 | 0 | 3.5439 | 0 | 0 | 0 | 0 | 8.5 | 0 | 107.3211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 547.5566 | 0 | 109.5113 | 1.095% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 06:01 | 11 | 1 | 6 | 305 | 7302 | 37.76 | 613.9449 | 0 | 0 | 613.9449 | Heating | 541.7161 | 8.5 | 541.7161 | 0 | 3.6043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.3432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 552.7716 | 0 | 110.5543 | 1.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 07:01 | 11 | 1 | 7 | 305 | 7303 | 35.96 | 6273.5277 | 18.97 | 18.97 | 6254.5576 | Heating | 5518.7273 | 8.5 | 5518.7273 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1103.7455 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5631.3544 | 0 | 1126.2709 | 11.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 08:01 | 11 | 1 | 8 | 305 | 7304 | 35.96 | 4427.2131 | 0 | 0 | 4427.2131 | Heating | 3906.3645 | 8.5 | 3906.3645 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 781.2729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3986.0862 | 0 | 797.2172 | 7.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 09:01 | 11 | 1 | 9 | 305 | 7305 | 42.98 | 3217.7634 | 0.15816 | 0.15816 | 3217.6052 | Heating | 2839.0634 | 8.5 | 2839.0634 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 567.8127 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2897.0035 | 0 | 579.4007 | 5.794% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 10:01 | 11 | 1 | 10 | 305 | 7306 | 46.04 | 2157.774 | 10.7405 | 10.7405 | 2147.0335 | Heating | 1894.4413 | 8.5 | 1894.4413 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.8883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1933.1034 | 0 | 386.6207 | 3.866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 11:01 | 11 | 1 | 11 | 305 | 7307 | 46.04 | 1569.7498 | 57.2501 | 57.2501 | 1512.4997 | Heating | 1334.5586 | 8.5 | 1334.5586 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.9117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1361.7944 | 0 | 272.3589 | 2.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 12:01 | 11 | 1 | 12 | 305 | 7308 | 46.04 | 1086.4936 | 125.9839 | 125.9839 | 960.5097 | Heating | 847.5085 | 8.5 | 847.5085 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.5017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 864.8046 | 0 | 172.9609 | 1.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 13:01 | 11 | 1 | 13 | 305 | 7309 | 48.02 | 877.402 | 194.6384 | 194.6384 | 682.7636 | Heating | 602.4384 | 8.5 | 602.4384 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.4877 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 614.7331 | 0 | 122.9466 | 1.229% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 14:01 | 11 | 1 | 14 | 305 | 7310 | 48.02 | 666.8572 | 268.4293 | 268.4293 | 398.4279 | Heating | 351.554 | 8.5 | 351.554 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 70.3108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 358.7286 | 0 | 71.7457 | 0.7175% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 15:01 | 11 | 1 | 15 | 305 | 7311 | 48.02 | 618.8315 | 294.8206 | 294.8206 | 324.0109 | Heating | 285.892 | 8.5 | 285.892 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 57.1784 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 291.7265 | 0 | 58.3453 | 0.5835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 16:01 | 11 | 1 | 16 | 305 | 7312 | 46.04 | 668.9272 | 226.4893 | 226.4893 | 442.4378 | Heating | 390.3863 | 8.5 | 390.3863 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.0773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 398.3534 | 0 | 79.6707 | 0.7967% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 17:01 | 11 | 1 | 17 | 305 | 7313 | 46.04 | 994.5278 | 120.5875 | 120.5875 | 873.9403 | Heating | 771.1238 | 8.5 | 771.1238 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.2248 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 786.861 | 0 | 157.3722 | 1.574% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 18:01 | 11 | 1 | 18 | 305 | 7314 | 39.92 | 1416.8023 | 66.8327 | 66.8327 | 1349.9697 | Heating | 1191.1497 | 8.5 | 1191.1497 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.2299 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1215.4589 | 0 | 243.0918 | 2.431% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 19:01 | 11 | 1 | 19 | 305 | 7315 | 37.04 | 1708.4803 | 39.702 | 39.702 | 1668.7783 | Heating | 1472.4515 | 8.5 | 1472.4515 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 294.4903 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1502.5015 | 0 | 300.5003 | 3.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 20:01 | 11 | 1 | 20 | 305 | 7316 | 37.04 | 1973.9518 | 24.7361 | 24.7361 | 1949.2158 | Heating | 1719.8963 | 8.5 | 1719.8963 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.9793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1754.9962 | 0 | 350.9992 | 3.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 21:01 | 11 | 1 | 21 | 305 | 7317 | 35.06 | 2196.4894 | 0.34842 | 0.34842 | 2196.141 | Heating | 1937.7715 | 8.5 | 1937.7715 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.5543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1977.3178 | 0 | 395.4636 | 3.955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 22:01 | 11 | 1 | 22 | 305 | 7318 | 35.06 | 559.2747 | 0 | 0 | 559.2747 | Heating | 493.4777 | 8.5 | 493.4777 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.6955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 503.5487 | 0 | 100.7097 | 1.007% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-01 23:01 | 11 | 1 | 23 | 305 | 7319 | 35.06 | 615.5984 | 0 | 0 | 615.5984 | Heating | 543.175 | 8.5 | 543.175 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 554.2602 | 0 | 110.852 | 1.109% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 00:01 | 11 | 2 | 0 | 306 | 7320 | 30.92 | 705.4178 | 0 | 0 | 705.4178 | Heating | 622.4274 | 8.5 | 622.4274 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.4855 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 635.13 | 0 | 127.026 | 1.27% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 01:01 | 11 | 2 | 1 | 306 | 7321 | 28.94 | 804.4478 | 0 | 0 | 804.4478 | Heating | 709.8069 | 8.5 | 709.8069 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 141.9614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 724.2927 | 0 | 144.8585 | 1.449% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 02:01 | 11 | 2 | 2 | 306 | 7322 | 28.94 | 888.536 | 0 | 0 | 888.536 | Heating | 784.0023 | 8.5 | 784.0023 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.8005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 800.0024 | 0 | 160.0005 | 1.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 03:01 | 11 | 2 | 3 | 306 | 7323 | 28.04 | 924.7684 | 0 | 0 | 924.7684 | Heating | 815.9722 | 8.5 | 815.9722 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 163.1944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 832.6246 | 0 | 166.5249 | 1.665% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 04:01 | 11 | 2 | 4 | 306 | 7324 | 26.06 | 931.5982 | 0 | 0 | 931.5982 | Heating | 821.9984 | 8.5 | 821.9984 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 164.3997 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 838.7739 | 0 | 167.7548 | 1.678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 05:01 | 11 | 2 | 5 | 306 | 7325 | 26.96 | 910.7561 | 0 | 0 | 910.7561 | Heating | 803.6083 | 8.5 | 803.6083 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.7217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 820.0085 | 0 | 164.0017 | 1.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 06:01 | 11 | 2 | 6 | 306 | 7326 | 26.6 | 883.1461 | 0 | 0 | 883.1461 | Heating | 779.2466 | 8.5 | 779.2466 | 0 | 3.104 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.8493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 795.1495 | 0 | 159.0299 | 1.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 07:01 | 11 | 2 | 7 | 306 | 7327 | 26.06 | 7583.9485 | 0 | 0 | 7583.9485 | Heating | 6691.7193 | 8.5 | 6691.7193 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1338.3439 | 30% | 1 | 53.53% | 0% | 0% | 0% | 19.3636 | 0 | 0 | 0 | 19.3636 | 6828.285 | 0 | 1365.657 | 13.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.6382
2007-11-02 08:01 | 11 | 2 | 8 | 306 | 7328 | 26.06 | 5359.2826 | 0 | 0 | 5359.2826 | Heating | 4728.7788 | 8.5 | 4728.7788 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 945.7558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4825.2845 | 0 | 965.0569 | 9.651% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 09:01 | 11 | 2 | 9 | 306 | 7329 | 35.96 | 4428.6082 | 0 | 0 | 4428.6082 | Heating | 3907.5955 | 8.5 | 3907.5955 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 781.5191 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3987.3424 | 0 | 797.4685 | 7.975% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 10:01 | 11 | 2 | 10 | 306 | 7330 | 41 | 3481.5564 | 0 | 0 | 3481.5564 | Heating | 3071.9615 | 8.5 | 3071.9615 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 614.3923 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3134.6546 | 0 | 626.9309 | 6.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 11:01 | 11 | 2 | 11 | 306 | 7331 | 41 | 2541.6732 | 0 | 0 | 2541.6732 | Heating | 2242.6528 | 8.5 | 2242.6528 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 448.5306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2288.4212 | 0 | 457.6842 | 4.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 12:01 | 11 | 2 | 12 | 306 | 7332 | 48.92 | 1897.234 | 0 | 0 | 1897.234 | Heating | 1674.03 | 8.5 | 1674.03 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 334.806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1708.1939 | 0 | 341.6388 | 3.416% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 13:01 | 11 | 2 | 13 | 306 | 7333 | 51.08 | 1645.005 | 0 | 0 | 1645.005 | Heating | 1451.475 | 8.5 | 1451.475 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1481.097 | 0 | 296.2194 | 2.962% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 14:01 | 11 | 2 | 14 | 306 | 7334 | 51.08 | 1376.7425 | 0 | 0 | 1376.7425 | Heating | 1214.7728 | 8.5 | 1214.7728 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.9546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1239.5641 | 0 | 247.9128 | 2.479% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 15:01 | 11 | 2 | 15 | 306 | 7335 | 55.04 | 1011.8885 | 0 | 0 | 1011.8885 | Heating | 892.8428 | 8.5 | 892.8428 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 178.5686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 911.064 | 0 | 182.2128 | 1.822% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 16:01 | 11 | 2 | 16 | 306 | 7336 | 55.04 | 730.2786 | 0 | 0 | 730.2786 | Heating | 644.3635 | 8.5 | 644.3635 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.8727 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 657.5138 | 0 | 131.5028 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 17:01 | 11 | 2 | 17 | 306 | 7337 | 55.04 | 625.5443 | 0 | 0 | 625.5443 | Heating | 551.9508 | 8.5 | 551.9508 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.3902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 563.2151 | 0 | 112.643 | 1.126% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 18:01 | 11 | 2 | 18 | 306 | 7338 | 53.06 | 677.8662 | 0 | 0 | 677.8662 | Heating | 598.1172 | 8.5 | 598.1172 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 119.6234 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 610.3237 | 0 | 122.0647 | 1.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 19:01 | 11 | 2 | 19 | 306 | 7339 | 53.06 | 1119.1596 | 0 | 0 | 1119.1596 | Heating | 987.4938 | 8.5 | 987.4938 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 197.4988 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1007.6467 | 0 | 201.5293 | 2.015% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 20:01 | 11 | 2 | 20 | 306 | 7340 | 53.06 | 1407.8078 | 0 | 0 | 1407.8078 | Heating | 1242.1834 | 8.5 | 1242.1834 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.4367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1267.5341 | 0 | 253.5068 | 2.535% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 21:01 | 11 | 2 | 21 | 306 | 7341 | 53.06 | 1512.54 | 0 | 0 | 1512.54 | Heating | 1334.5941 | 8.5 | 1334.5941 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.9188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1361.8308 | 0 | 272.3662 | 2.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 22:01 | 11 | 2 | 22 | 306 | 7342 | 51.98 | 1792.6786 | 0 | 0 | 1792.6786 | Heating | 1581.7752 | 8.5 | 1581.7752 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 316.355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1614.0563 | 0 | 322.8113 | 3.228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-02 23:01 | 11 | 2 | 23 | 306 | 7343 | 51.98 | 373.6125 | 0 | 0 | 373.6125 | Heating | 329.6581 | 8.5 | 329.6581 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 65.9316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 336.3858 | 0 | 67.2772 | 0.6728% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 00:01 | 11 | 3 | 0 | 307 | 7344 | 53.06 | 416.2677 | 0 | 0 | 416.2677 | Heating | 367.2951 | 8.5 | 367.2951 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 73.459 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 374.7909 | 0 | 74.9582 | 0.7496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 01:01 | 11 | 3 | 1 | 307 | 7345 | 53.6 | 461.5264 | 0 | 0 | 461.5264 | Heating | 407.2291 | 8.5 | 407.2291 | 0 | 4.8707 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.4458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 415.5399 | 0 | 83.108 | 0.8311% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 02:01 | 11 | 3 | 2 | 307 | 7346 | 53.06 | 462.3395 | 0 | 0 | 462.3395 | Heating | 407.9466 | 8.5 | 407.9466 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 81.5893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 416.272 | 0 | 83.2544 | 0.8325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 03:01 | 11 | 3 | 3 | 307 | 7347 | 51.08 | 495.8897 | 0 | 0 | 495.8897 | Heating | 437.5497 | 8.5 | 437.5497 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.5099 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 446.4793 | 0 | 89.2959 | 0.893% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 04:01 | 11 | 3 | 4 | 307 | 7348 | 50 | 557.8803 | 0 | 0 | 557.8803 | Heating | 492.2474 | 8.5 | 492.2474 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 98.4495 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 502.2932 | 0 | 100.4586 | 1.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 05:01 | 11 | 3 | 5 | 307 | 7349 | 50 | 614.1402 | 0 | 0 | 614.1402 | Heating | 541.8884 | 8.5 | 541.8884 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.3777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 552.9474 | 0 | 110.5895 | 1.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 06:01 | 11 | 3 | 6 | 307 | 7350 | 50 | 666.1421 | 0 | 0 | 666.1421 | Heating | 587.7725 | 8.5 | 587.7725 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 117.5545 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 599.7678 | 0 | 119.9536 | 1.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 07:01 | 11 | 3 | 7 | 307 | 7351 | 50 | 734.3505 | 0 | 0 | 734.3505 | Heating | 647.9563 | 8.5 | 647.9563 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.5913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 661.1799 | 0 | 132.236 | 1.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 08:01 | 11 | 3 | 8 | 307 | 7352 | 50 | 750.0805 | 0 | 0 | 750.0805 | Heating | 661.8358 | 8.5 | 661.8358 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.3672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 675.3426 | 0 | 135.0685 | 1.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 09:01 | 11 | 3 | 9 | 307 | 7353 | 53.96 | 5952.7991 | 0 | 0 | 5952.7991 | Heating | 5252.4698 | 8.5 | 5252.4698 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1050.494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5359.6631 | 0 | 1071.9326 | 10.72% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 10:01 | 11 | 3 | 10 | 307 | 7354 | 55.94 | 4039.2475 | 0 | 0 | 4039.2475 | Heating | 3564.0419 | 8.5 | 3564.0419 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 712.8084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3636.7774 | 0 | 727.3555 | 7.274% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 11:01 | 11 | 3 | 11 | 307 | 7355 | 55.94 | 2979.934 | 0 | 0 | 2979.934 | Heating | 2629.3536 | 8.5 | 2629.3536 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 525.8707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2683.0138 | 0 | 536.6028 | 5.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 12:01 | 11 | 3 | 12 | 307 | 7356 | 57.02 | 2404.5356 | 0 | 0 | 2404.5356 | Heating | 2121.6491 | 8.5 | 2121.6491 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.3298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2164.9481 | 0 | 432.9896 | 4.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 13:01 | 11 | 3 | 13 | 307 | 7357 | 60.98 | 1757.5065 | 0 | 0 | 1757.5065 | Heating | 1550.741 | 8.5 | 1550.741 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 310.1482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1582.3888 | 0 | 316.4778 | 3.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 14:01 | 11 | 3 | 14 | 307 | 7358 | 60.98 | 1553.3579 | 0 | 0 | 1553.3579 | Heating | 1370.6099 | 8.5 | 1370.6099 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 274.122 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1398.5815 | 0 | 279.7163 | 2.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 15:01 | 11 | 3 | 15 | 307 | 7359 | 62.96 | 1642.1542 | 0 | 0 | 1642.1542 | Heating | 1448.9596 | 8.5 | 1448.9596 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 289.7919 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1478.5302 | 0 | 295.706 | 2.957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 16:01 | 11 | 3 | 16 | 307 | 7360 | 62.96 | 1804.3344 | 0 | 0 | 1804.3344 | Heating | 1592.0597 | 8.5 | 1592.0597 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 318.4119 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1624.5507 | 0 | 324.9101 | 3.249% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 17:01 | 11 | 3 | 17 | 307 | 7361 | 62.96 | 2200.1002 | 0 | 0 | 2200.1002 | Heating | 1941.2649 | 8.5 | 1941.2649 | 0 | 6.0268 | 0 | 0 | 0 | 0 | 8.5 | 0 | 388.253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1980.8825 | 0 | 396.1765 | 3.962% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 18:01 | 11 | 3 | 18 | 307 | 7362 | 59 | 3690.8657 | 0 | 0 | 3690.8657 | Heating | 3256.6462 | 8.5 | 3256.6462 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 651.3292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3323.1083 | 0 | 664.6217 | 6.646% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 19:01 | 11 | 3 | 19 | 307 | 7363 | 57.02 | 4338.5413 | 0 | 0 | 4338.5413 | Heating | 3828.1247 | 8.5 | 3828.1247 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 765.6249 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3906.2496 | 0 | 781.2499 | 7.812% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 20:01 | 11 | 3 | 20 | 307 | 7364 | 57.02 | 842.3468 | 0 | 0 | 842.3468 | Heating | 743.2471 | 8.5 | 743.2471 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.6494 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 758.4154 | 0 | 151.6831 | 1.517% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 21:01 | 11 | 3 | 21 | 307 | 7365 | 55.04 | 894.4101 | 0 | 0 | 894.4101 | Heating | 789.1854 | 8.5 | 789.1854 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.8371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 805.2912 | 0 | 161.0582 | 1.611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 22:01 | 11 | 3 | 22 | 307 | 7366 | 55.94 | 982.1802 | 0 | 0 | 982.1802 | Heating | 866.6296 | 8.5 | 866.6296 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 173.3259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 884.3159 | 0 | 176.8632 | 1.769% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-03 23:01 | 11 | 3 | 23 | 307 | 7367 | 55.94 | 1084.6502 | 0 | 0 | 1084.6502 | Heating | 957.0443 | 8.5 | 957.0443 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.4089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 976.5758 | 0 | 195.3152 | 1.953% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 00:01 | 11 | 4 | 0 | 308 | 7368 | 55.94 | 1288.0641 | 0 | 0 | 1288.0641 | Heating | 1136.5271 | 8.5 | 1136.5271 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 227.3054 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1159.7216 | 0 | 231.9443 | 2.319% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 01:01 | 11 | 4 | 1 | 308 | 7369 | 55.04 | 1462.2122 | 0 | 0 | 1462.2122 | Heating | 1290.1872 | 8.5 | 1290.1872 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 258.0374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1316.5176 | 0 | 263.3035 | 2.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 02:01 | 11 | 4 | 2 | 308 | 7370 | 55.04 | 1566.3382 | 0 | 0 | 1566.3382 | Heating | 1382.0631 | 8.5 | 1382.0631 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 276.4126 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1410.2685 | 0 | 282.0537 | 2.821% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 03:01 | 11 | 4 | 3 | 308 | 7371 | 53.06 | 1638.8576 | 0 | 0 | 1638.8576 | Heating | 1446.0508 | 8.5 | 1446.0508 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 289.2102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1475.562 | 0 | 295.1124 | 2.951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 04:01 | 11 | 4 | 4 | 308 | 7372 | 51.98 | 1655.8985 | 0 | 0 | 1655.8985 | Heating | 1461.0869 | 8.5 | 1461.0869 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.2174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1490.905 | 0 | 298.181 | 2.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 05:01 | 11 | 4 | 5 | 308 | 7373 | 53.06 | 1807.8451 | 0 | 0 | 1807.8451 | Heating | 1595.1575 | 8.5 | 1595.1575 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 319.0315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1627.7117 | 0 | 325.5423 | 3.255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 06:01 | 11 | 4 | 6 | 308 | 7374 | 51.98 | 1840.7535 | 0 | 0 | 1840.7535 | Heating | 1624.1943 | 8.5 | 1624.1943 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.8389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1657.3411 | 0 | 331.4682 | 3.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 07:01 | 11 | 4 | 7 | 308 | 7375 | 51.98 | 11545.5822 | 0 | 0 | 11545.5822 | Heating | 10187.2784 | 8.5 | 10187.2784 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2037.4557 | 40.75% | 1 | 81.5% | 0% | 0% | 0% | 50.9077 | 0 | 0 | 0 | 50.9077 | 10395.182 | 0 | 2079.0364 | 20.79% | 1 | 41.58% | 0% | 0% | 5.4146 | 0 | 0 | 5.4146 | 56.3223
2007-11-04 08:01 | 11 | 4 | 8 | 308 | 7376 | 51.98 | 8558.6675 | 0 | 0 | 8558.6675 | Heating | 7551.7654 | 8.5 | 7551.7654 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1510.3531 | 30.21% | 1 | 60.41% | 0% | 0% | 0% | 25.5718 | 0 | 0 | 0 | 25.5718 | 7705.8831 | 0 | 1541.1766 | 15.41% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.8464
2007-11-04 09:01 | 11 | 4 | 9 | 308 | 7377 | 53.06 | 6531.6385 | 0 | 0 | 6531.6385 | Heating | 5763.2105 | 8.5 | 5763.2105 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1152.6421 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5880.827 | 0 | 1176.1654 | 11.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 10:01 | 11 | 4 | 10 | 308 | 7378 | 53.06 | 4914.4185 | 0 | 0 | 4914.4185 | Heating | 4336.2516 | 8.5 | 4336.2516 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 867.2503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4424.7465 | 0 | 884.9493 | 8.849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 11:01 | 11 | 4 | 11 | 308 | 7379 | 53.06 | 3853.309 | 0 | 0 | 3853.309 | Heating | 3399.9785 | 8.5 | 3399.9785 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 679.9957 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3469.3658 | 0 | 693.8732 | 6.939% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 12:01 | 11 | 4 | 12 | 308 | 7380 | 53.06 | 3128.3103 | 0 | 0 | 3128.3103 | Heating | 2760.2738 | 8.5 | 2760.2738 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 552.0548 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2816.6059 | 0 | 563.3212 | 5.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 13:01 | 11 | 4 | 13 | 308 | 7381 | 55.04 | 2818.2947 | 0 | 0 | 2818.2947 | Heating | 2486.7306 | 8.5 | 2486.7306 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 497.3461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2537.4802 | 0 | 507.496 | 5.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 14:01 | 11 | 4 | 14 | 308 | 7382 | 55.04 | 2603.24 | 0 | 0 | 2603.24 | Heating | 2296.9765 | 8.5 | 2296.9765 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 459.3953 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2343.8536 | 0 | 468.7707 | 4.688% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 15:01 | 11 | 4 | 15 | 308 | 7383 | 57.02 | 2594.4707 | 0 | 0 | 2594.4707 | Heating | 2289.2388 | 8.5 | 2289.2388 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 457.8478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2335.958 | 0 | 467.1916 | 4.672% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 16:01 | 11 | 4 | 16 | 308 | 7384 | 57.92 | 2834.7373 | 0 | 0 | 2834.7373 | Heating | 2501.2388 | 8.5 | 2501.2388 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 500.2478 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2552.2845 | 0 | 510.4569 | 5.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 17:01 | 11 | 4 | 17 | 308 | 7385 | 57.92 | 3014.5456 | 0 | 0 | 3014.5456 | Heating | 2659.8932 | 8.5 | 2659.8932 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 531.9786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2714.1767 | 0 | 542.8353 | 5.428% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 18:01 | 11 | 4 | 18 | 308 | 7386 | 55.04 | 3092.221 | 0 | 0 | 3092.221 | Heating | 2728.4303 | 8.5 | 2728.4303 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 545.6861 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2784.1126 | 0 | 556.8225 | 5.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 19:01 | 11 | 4 | 19 | 308 | 7387 | 53.06 | 3128.2796 | 0 | 0 | 3128.2796 | Heating | 2760.2467 | 8.5 | 2760.2467 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 552.0493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2816.5783 | 0 | 563.3157 | 5.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 20:01 | 11 | 4 | 20 | 308 | 7388 | 53.6 | 3100.0186 | 0 | 0 | 3100.0186 | Heating | 2735.3105 | 8.5 | 2735.3105 | 0 | 4.8707 | 0 | 0 | 0 | 0 | 8.5 | 0 | 547.0621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2791.1332 | 0 | 558.2266 | 5.582% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 21:01 | 11 | 4 | 21 | 308 | 7389 | 53.06 | 3109.1134 | 0 | 0 | 3109.1134 | Heating | 2743.3354 | 8.5 | 2743.3354 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 548.6671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2799.3218 | 0 | 559.8644 | 5.599% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 22:01 | 11 | 4 | 22 | 308 | 7390 | 53.06 | 865.6478 | 0 | 0 | 865.6478 | Heating | 763.8069 | 8.5 | 763.8069 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.7614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 779.3947 | 0 | 155.8789 | 1.559% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-04 23:01 | 11 | 4 | 23 | 308 | 7391 | 53.06 | 712.2605 | 0 | 0 | 712.2605 | Heating | 628.4651 | 8.5 | 628.4651 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 641.2909 | 0 | 128.2582 | 1.283% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 00:01 | 11 | 5 | 0 | 309 | 7392 | 51.98 | 709.7752 | 0 | 0 | 709.7752 | Heating | 626.2723 | 8.5 | 626.2723 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.2545 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 639.0533 | 0 | 127.8107 | 1.278% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 01:01 | 11 | 5 | 1 | 309 | 7393 | 50 | 718.3018 | 0 | 0 | 718.3018 | Heating | 633.7957 | 8.5 | 633.7957 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.7591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 646.7303 | 0 | 129.3461 | 1.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 02:01 | 11 | 5 | 2 | 309 | 7394 | 50 | 723.0084 | 0 | 0 | 723.0084 | Heating | 637.9486 | 8.5 | 637.9486 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.5897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 650.968 | 0 | 130.1936 | 1.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 03:01 | 11 | 5 | 3 | 309 | 7395 | 50 | 700.5833 | 0 | 0 | 700.5833 | Heating | 618.1617 | 8.5 | 618.1617 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.6323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 630.7773 | 0 | 126.1555 | 1.262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 04:01 | 11 | 5 | 4 | 309 | 7396 | 48.92 | 687.3826 | 0 | 0 | 687.3826 | Heating | 606.5141 | 8.5 | 606.5141 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.3028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 618.8919 | 0 | 123.7784 | 1.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 05:01 | 11 | 5 | 5 | 309 | 7397 | 48.92 | 714.2358 | 0 | 0 | 714.2358 | Heating | 630.2081 | 8.5 | 630.2081 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 126.0416 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 643.0695 | 0 | 128.6139 | 1.286% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 06:01 | 11 | 5 | 6 | 309 | 7398 | 48.02 | 771.8419 | 0 | 0 | 771.8419 | Heating | 681.0369 | 8.5 | 681.0369 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.2074 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 694.9356 | 0 | 138.9871 | 1.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 07:01 | 11 | 5 | 7 | 309 | 7399 | 48.02 | 7356.4203 | 0 | 0 | 7356.4203 | Heating | 6490.9591 | 8.5 | 6490.9591 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1298.1918 | 30% | 1 | 51.93% | 0% | 0% | 0% | 18.0535 | 0 | 0 | 0 | 18.0535 | 6623.4276 | 0 | 1324.6855 | 13.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.328
2007-11-05 08:01 | 11 | 5 | 8 | 309 | 7400 | 48.02 | 5630.8325 | 0 | 0 | 5630.8325 | Heating | 4968.3816 | 8.5 | 4968.3816 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 993.6763 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5069.7772 | 0 | 1013.9554 | 10.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 09:01 | 11 | 5 | 9 | 309 | 7401 | 50 | 4562.694 | 0 | 0 | 4562.694 | Heating | 4025.9065 | 8.5 | 4025.9065 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 805.1813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4108.0679 | 0 | 821.6136 | 8.216% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 10:01 | 11 | 5 | 10 | 309 | 7402 | 50 | 3254.0546 | 0 | 0 | 3254.0546 | Heating | 2871.2247 | 8.5 | 2871.2247 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 574.2449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2929.8211 | 0 | 585.9642 | 5.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 11:01 | 11 | 5 | 11 | 309 | 7403 | 50 | 2736.7982 | 0 | 0 | 2736.7982 | Heating | 2414.822 | 8.5 | 2414.822 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 482.9644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2464.104 | 0 | 492.8208 | 4.928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 12:01 | 11 | 5 | 12 | 309 | 7404 | 51.08 | 2362.6162 | 0 | 0 | 2362.6162 | Heating | 2084.6614 | 8.5 | 2084.6614 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 416.9323 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2127.2055 | 0 | 425.4411 | 4.254% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 13:01 | 11 | 5 | 13 | 309 | 7405 | 51.98 | 2151.9878 | 0 | 0 | 2151.9878 | Heating | 1898.8128 | 8.5 | 1898.8128 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.7626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1937.5641 | 0 | 387.5128 | 3.875% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 14:01 | 11 | 5 | 14 | 309 | 7406 | 51.98 | 2029.7362 | 1.4223 | 1.4223 | 2028.3139 | Heating | 1789.6887 | 8.5 | 1789.6887 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 357.9377 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1826.213 | 0 | 365.2426 | 3.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 15:01 | 11 | 5 | 15 | 309 | 7407 | 51.98 | 2134.8508 | 4.935 | 4.935 | 2129.9158 | Heating | 1879.3375 | 8.5 | 1879.3375 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 375.8675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1917.6913 | 0 | 383.5383 | 3.835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 16:01 | 11 | 5 | 16 | 309 | 7408 | 50 | 2119.805 | 4.4327 | 4.4327 | 2115.3724 | Heating | 1866.505 | 8.5 | 1866.505 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1904.597 | 0 | 380.9194 | 3.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 17:01 | 11 | 5 | 17 | 309 | 7409 | 50 | 2275.3579 | 0.15365 | 0.15365 | 2275.2043 | Heating | 2007.5332 | 8.5 | 2007.5332 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 401.5066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2048.5032 | 0 | 409.7006 | 4.097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 18:01 | 11 | 5 | 18 | 309 | 7410 | 44.96 | 2523.843 | 0 | 0 | 2523.843 | Heating | 2226.9203 | 8.5 | 2226.9203 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.3841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2272.3676 | 0 | 454.4735 | 4.545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 19:01 | 11 | 5 | 19 | 309 | 7411 | 44.06 | 2673.404 | 0 | 0 | 2673.404 | Heating | 2358.8859 | 8.5 | 2358.8859 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.7772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2407.0264 | 0 | 481.4053 | 4.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 20:01 | 11 | 5 | 20 | 309 | 7412 | 44.06 | 2834.7138 | 0 | 0 | 2834.7138 | Heating | 2501.2181 | 8.5 | 2501.2181 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 500.2436 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2552.2633 | 0 | 510.4527 | 5.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 21:01 | 11 | 5 | 21 | 309 | 7413 | 41 | 2932.6323 | 0 | 0 | 2932.6323 | Heating | 2587.6167 | 8.5 | 2587.6167 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.5233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2640.4252 | 0 | 528.085 | 5.281% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 22:01 | 11 | 5 | 22 | 309 | 7414 | 37.94 | 797.9863 | 0 | 0 | 797.9863 | Heating | 704.1056 | 8.5 | 704.1056 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 140.8211 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 718.4751 | 0 | 143.695 | 1.437% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-05 23:01 | 11 | 5 | 23 | 309 | 7415 | 37.94 | 728.4973 | 0 | 0 | 728.4973 | Heating | 642.7917 | 8.5 | 642.7917 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.5583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 655.9099 | 0 | 131.182 | 1.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 00:01 | 11 | 6 | 0 | 310 | 7416 | 32 | 748.3174 | 0 | 0 | 748.3174 | Heating | 660.2801 | 8.5 | 660.2801 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 673.7552 | 0 | 134.751 | 1.348% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 01:01 | 11 | 6 | 1 | 310 | 7417 | 33.08 | 788.1127 | 0 | 0 | 788.1127 | Heating | 695.3936 | 8.5 | 695.3936 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.0787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 709.5853 | 0 | 141.9171 | 1.419% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 02:01 | 11 | 6 | 2 | 310 | 7418 | 33.08 | 899.7473 | 0 | 0 | 899.7473 | Heating | 793.8947 | 8.5 | 793.8947 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 158.7789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 810.0966 | 0 | 162.0193 | 1.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 03:01 | 11 | 6 | 3 | 310 | 7419 | 35.06 | 959.129 | 0 | 0 | 959.129 | Heating | 846.2903 | 8.5 | 846.2903 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.2581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 863.5615 | 0 | 172.7123 | 1.727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 04:01 | 11 | 6 | 4 | 310 | 7420 | 37.04 | 956.064 | 0 | 0 | 956.064 | Heating | 843.5859 | 8.5 | 843.5859 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.7172 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 860.8019 | 0 | 172.1604 | 1.722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 05:01 | 11 | 6 | 5 | 310 | 7421 | 35.06 | 1013.5331 | 0 | 0 | 1013.5331 | Heating | 894.2939 | 8.5 | 894.2939 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 178.8588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 912.5448 | 0 | 182.509 | 1.825% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 06:01 | 11 | 6 | 6 | 310 | 7422 | 39.2 | 1053.9157 | 0 | 0 | 1053.9157 | Heating | 929.9256 | 8.5 | 929.9256 | 0 | 3.6894 | 0 | 0 | 0 | 0 | 8.5 | 0 | 185.9851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 948.9037 | 0 | 189.7807 | 1.898% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 07:01 | 11 | 6 | 7 | 310 | 7423 | 41 | 8332.1062 | 0 | 0 | 8332.1062 | Heating | 7351.8584 | 8.5 | 7351.8584 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1470.3717 | 30% | 1 | 58.81% | 0% | 0% | 0% | 24.0416 | 0 | 0 | 0 | 24.0416 | 7501.8964 | 0 | 1500.3793 | 15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.3161
2007-11-06 08:01 | 11 | 6 | 8 | 310 | 7424 | 41 | 6036.2566 | 0 | 0 | 6036.2566 | Heating | 5326.1087 | 8.5 | 5326.1087 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1065.2217 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5434.8048 | 0 | 1086.961 | 10.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 09:01 | 11 | 6 | 9 | 310 | 7425 | 42.98 | 4535.5573 | 0 | 0 | 4535.5573 | Heating | 4001.9623 | 8.5 | 4001.9623 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 800.3925 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4083.635 | 0 | 816.727 | 8.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 10:01 | 11 | 6 | 10 | 310 | 7426 | 46.04 | 2957.3235 | 0 | 0 | 2957.3235 | Heating | 2609.4031 | 8.5 | 2609.4031 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 521.8806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2662.6562 | 0 | 532.5312 | 5.325% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 11:01 | 11 | 6 | 11 | 310 | 7427 | 46.04 | 1874.7499 | 0.33651 | 0.33651 | 1874.4134 | Heating | 1653.8942 | 8.5 | 1653.8942 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 330.7788 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1687.6471 | 0 | 337.5294 | 3.375% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 12:01 | 11 | 6 | 12 | 310 | 7428 | 51.08 | 964.4547 | 43.2418 | 43.2418 | 921.2129 | Heating | 812.8349 | 8.5 | 812.8349 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.567 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 829.4234 | 0 | 165.8847 | 1.659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 13:01 | 11 | 6 | 13 | 310 | 7429 | 55.94 | 534.3721 | 109.5112 | 109.5112 | 424.8609 | Heating | 374.8773 | 8.5 | 374.8773 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 74.9755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 382.5278 | 0 | 76.5056 | 0.7651% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 14:01 | 11 | 6 | 14 | 310 | 7430 | 55.94 | 268.5804 | 229.7098 | 229.7098 | 38.8706 | Heating | 34.2976 | 8.5 | 34.2976 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 6.8595 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 34.9975 | 0 | 6.9995 | 0.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 15:01 | 11 | 6 | 15 | 310 | 7431 | 55.94 | 219.4808 | 301.4863 | 301.4863 | -82.0055 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 368.4833 | 368.4833 | 0 | 8.5 | 0 | 61.4139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 361.1136 | 72.2227 | 0.7222% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 16:01 | 11 | 6 | 16 | 310 | 7432 | 57.02 | 228.9366 | 238.7662 | 238.7662 | -9.8296 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 291.8254 | 291.8254 | 0 | 8.5 | 0 | 48.6376 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 285.9889 | 57.1978 | 0.572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 17:01 | 11 | 6 | 17 | 310 | 7433 | 57.02 | 303.1233 | 131.0516 | 131.0516 | 172.0717 | Heating | 151.8279 | 8.5 | 151.8279 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 30.3656 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 154.9265 | 0 | 30.9853 | 0.3099% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 18:01 | 11 | 6 | 18 | 310 | 7434 | 51.98 | 572.6941 | 75.508 | 75.508 | 497.1861 | Heating | 438.6936 | 8.5 | 438.6936 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 87.7387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 447.6466 | 0 | 89.5293 | 0.8953% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 19:01 | 11 | 6 | 19 | 310 | 7435 | 48.02 | 971.8962 | 36.1668 | 36.1668 | 935.7293 | Heating | 825.6435 | 8.5 | 825.6435 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.1287 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 842.4934 | 0 | 168.4987 | 1.685% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 20:01 | 11 | 6 | 20 | 310 | 7436 | 48.02 | 1241.5954 | 23.5277 | 23.5277 | 1218.0677 | Heating | 1074.7656 | 8.5 | 1074.7656 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 214.9531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1096.6996 | 0 | 219.3399 | 2.193% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 21:01 | 11 | 6 | 21 | 310 | 7437 | 44.06 | 1561.5432 | 1.9545 | 1.9545 | 1559.5887 | Heating | 1376.1077 | 8.5 | 1376.1077 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 275.2215 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1404.1915 | 0 | 280.8383 | 2.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 22:01 | 11 | 6 | 22 | 310 | 7438 | 44.06 | 508.3579 | 0 | 0 | 508.3579 | Heating | 448.551 | 8.5 | 448.551 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 89.7102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 457.7051 | 0 | 91.541 | 0.9154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-06 23:01 | 11 | 6 | 23 | 310 | 7439 | 44.06 | 627.9421 | 0 | 0 | 627.9421 | Heating | 554.0666 | 8.5 | 554.0666 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.8133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 565.3741 | 0 | 113.0748 | 1.131% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 00:01 | 11 | 7 | 0 | 311 | 7440 | 46.94 | 698.9563 | 0 | 0 | 698.9563 | Heating | 616.7261 | 8.5 | 616.7261 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.3452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 629.3124 | 0 | 125.8625 | 1.259% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 01:01 | 11 | 7 | 1 | 311 | 7441 | 46.04 | 708.1864 | 0 | 0 | 708.1864 | Heating | 624.8703 | 8.5 | 624.8703 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.9741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 637.6228 | 0 | 127.5246 | 1.275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 02:01 | 11 | 7 | 2 | 311 | 7442 | 42.98 | 783.5986 | 0 | 0 | 783.5986 | Heating | 691.4105 | 8.5 | 691.4105 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.2821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 705.5209 | 0 | 141.1042 | 1.411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 03:01 | 11 | 7 | 3 | 311 | 7443 | 48.92 | 836.9961 | 0 | 0 | 836.9961 | Heating | 738.526 | 8.5 | 738.526 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 147.7052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 753.5979 | 0 | 150.7196 | 1.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 04:01 | 11 | 7 | 4 | 311 | 7444 | 48.02 | 761.7353 | 0 | 0 | 761.7353 | Heating | 672.1194 | 8.5 | 672.1194 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 134.4239 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 685.8361 | 0 | 137.1672 | 1.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 05:01 | 11 | 7 | 5 | 311 | 7445 | 46.94 | 708.8639 | 0 | 0 | 708.8639 | Heating | 625.4681 | 8.5 | 625.4681 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.0936 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 638.2328 | 0 | 127.6466 | 1.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 06:01 | 11 | 7 | 6 | 311 | 7446 | 44.06 | 697.0925 | 0 | 0 | 697.0925 | Heating | 615.0817 | 8.5 | 615.0817 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.0163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 627.6343 | 0 | 125.5269 | 1.255% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 07:01 | 11 | 7 | 7 | 311 | 7447 | 44.96 | 6676.6849 | 0 | 0 | 6676.6849 | Heating | 5891.1925 | 8.5 | 5891.1925 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1178.2385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6011.421 | 0 | 1202.2842 | 12.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 08:01 | 11 | 7 | 8 | 311 | 7448 | 44.96 | 4637.1036 | 0 | 0 | 4637.1036 | Heating | 4091.562 | 8.5 | 4091.562 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 818.3124 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4175.0633 | 0 | 835.0127 | 8.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 09:01 | 11 | 7 | 9 | 311 | 7449 | 44.96 | 3312.8948 | 0 | 0 | 3312.8948 | Heating | 2923.1425 | 8.5 | 2923.1425 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 584.6285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2982.7985 | 0 | 596.5597 | 5.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 10:01 | 11 | 7 | 10 | 311 | 7450 | 44.96 | 2062.5771 | 0 | 0 | 2062.5771 | Heating | 1819.921 | 8.5 | 1819.921 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.9842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1857.0622 | 0 | 371.4124 | 3.714% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 11:01 | 11 | 7 | 11 | 311 | 7451 | 44.96 | 992.7268 | 20.4908 | 20.4908 | 972.236 | Heating | 857.8553 | 8.5 | 857.8553 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.5711 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 875.3626 | 0 | 175.0725 | 1.751% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 12:01 | 11 | 7 | 12 | 311 | 7452 | 46.04 | 231.0792 | 68.4158 | 68.4158 | 162.6634 | Heating | 143.5265 | 8.5 | 143.5265 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 28.7053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 146.4557 | 0 | 29.2911 | 0.2929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 13:01 | 11 | 7 | 13 | 311 | 7453 | 48.02 | 146.6525 | 172.8223 | 172.8223 | -26.1698 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 211.2273 | 211.2273 | 0 | 8.5 | 0 | 35.2045 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 207.0027 | 41.4005 | 0.414% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 14:01 | 11 | 7 | 14 | 311 | 7454 | 48.02 | 81.8362 | 421.8246 | 421.8246 | -339.9884 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 515.5634 | 515.5634 | 0 | 8.5 | 0 | 85.9272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 505.2521 | 101.0504 | 1.011% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 15:01 | 11 | 7 | 15 | 311 | 7455 | 50 | 62.3334 | 389.5869 | 389.5869 | -327.2536 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 476.1618 | 476.1618 | 0 | 8.5 | 0 | 79.3603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 466.6386 | 93.3277 | 0.9333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 16:01 | 11 | 7 | 16 | 311 | 7456 | 48.02 | 71.4373 | 337.0956 | 337.0956 | -265.6583 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 412.0057 | 412.0057 | 0 | 8.5 | 0 | 68.6676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 403.7656 | 80.7531 | 0.8075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 17:01 | 11 | 7 | 17 | 311 | 7457 | 48.02 | 94.8982 | 250.623 | 250.623 | -155.7248 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 306.317 | 306.317 | 0 | 8.5 | 0 | 51.0528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 300.1907 | 60.0381 | 0.6004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 18:01 | 11 | 7 | 18 | 311 | 7458 | 44.96 | 58.8608 | 191.3603 | 191.3603 | -132.4995 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 233.8848 | 233.8848 | 0 | 8.5 | 0 | 38.9808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 229.2071 | 45.8414 | 0.4584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 19:01 | 11 | 7 | 19 | 311 | 7459 | 44.06 | 26.2552 | 114.4 | 114.4 | -88.1448 | Cooling | 0 | 8.5 | 0 | 0 | 0 | 0 | 139.8222 | 139.8222 | 0 | 8.5 | 0 | 23.3037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 0 | 137.0258 | 27.4052 | 0.2741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 20:01 | 11 | 7 | 20 | 311 | 7460 | 44.06 | 74.6372 | 66.3965 | 66.3965 | 8.2407 | Heating | 7.2712 | 8.5 | 7.2712 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1.4542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 7.4196 | 0 | 1.4839 | 0.01484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 21:01 | 11 | 7 | 21 | 311 | 7461 | 39.92 | 264.4227 | 18.7432 | 18.7432 | 245.6795 | Heating | 216.776 | 8.5 | 216.776 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 43.3552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 221.2 | 0 | 44.24 | 0.4424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 22:01 | 11 | 7 | 22 | 311 | 7462 | 37.94 | 197.3095 | 2.6422 | 2.6422 | 194.6673 | Heating | 171.7652 | 8.5 | 171.7652 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 34.353 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 175.2706 | 0 | 35.0541 | 0.3505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-07 23:01 | 11 | 7 | 23 | 311 | 7463 | 37.94 | 297.6476 | 0 | 0 | 297.6476 | Heating | 262.6302 | 8.5 | 262.6302 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 52.526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 267.99 | 0 | 53.598 | 0.536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 00:01 | 11 | 8 | 0 | 312 | 7464 | 35.96 | 375.8744 | 0 | 0 | 375.8744 | Heating | 331.6539 | 8.5 | 331.6539 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 66.3308 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 338.4223 | 0 | 67.6845 | 0.6768% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 01:01 | 11 | 8 | 1 | 312 | 7465 | 37.04 | 445.8737 | 0 | 0 | 445.8737 | Heating | 393.418 | 8.5 | 393.418 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.6836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 401.4469 | 0 | 80.2894 | 0.8029% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 02:01 | 11 | 8 | 2 | 312 | 7466 | 37.04 | 526.0067 | 0 | 0 | 526.0067 | Heating | 464.1236 | 8.5 | 464.1236 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.8247 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 473.5955 | 0 | 94.7191 | 0.9472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 03:01 | 11 | 8 | 3 | 312 | 7467 | 30.02 | 634.4661 | 0 | 0 | 634.4661 | Heating | 559.8231 | 8.5 | 559.8231 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 111.9646 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 571.248 | 0 | 114.2496 | 1.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 04:01 | 11 | 8 | 4 | 312 | 7468 | 30.92 | 742.9958 | 0 | 0 | 742.9958 | Heating | 655.5845 | 8.5 | 655.5845 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.1169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 668.9638 | 0 | 133.7928 | 1.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 05:01 | 11 | 8 | 5 | 312 | 7469 | 30.92 | 842.1059 | 0 | 0 | 842.1059 | Heating | 743.0346 | 8.5 | 743.0346 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.6069 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 758.1986 | 0 | 151.6397 | 1.516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 06:01 | 11 | 8 | 6 | 312 | 7470 | 30.02 | 901.0094 | 0 | 0 | 901.0094 | Heating | 795.0083 | 8.5 | 795.0083 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 159.0017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 811.2329 | 0 | 162.2466 | 1.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 07:01 | 11 | 8 | 7 | 312 | 7471 | 28.94 | 8271.8111 | 0 | 0 | 8271.8111 | Heating | 7298.6568 | 8.5 | 7298.6568 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1459.7314 | 30% | 1 | 58.39% | 0% | 0% | 0% | 23.6433 | 0 | 0 | 0 | 23.6433 | 7447.609 | 0 | 1489.5218 | 14.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.9179
2007-11-08 08:01 | 11 | 8 | 8 | 312 | 7472 | 28.94 | 5962.6366 | 0 | 0 | 5962.6366 | Heating | 5261.15 | 8.5 | 5261.15 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1052.23 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5368.5204 | 0 | 1073.7041 | 10.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 09:01 | 11 | 8 | 9 | 312 | 7473 | 37.94 | 4295.3451 | 0 | 0 | 4295.3451 | Heating | 3790.0103 | 8.5 | 3790.0103 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 758.0021 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3867.3575 | 0 | 773.4715 | 7.735% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 10:01 | 11 | 8 | 10 | 312 | 7474 | 42.98 | 2970.374 | 3.397 | 3.397 | 2966.9771 | Heating | 2617.9209 | 8.5 | 2617.9209 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.5842 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2671.3479 | 0 | 534.2696 | 5.343% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 11:01 | 11 | 8 | 11 | 312 | 7475 | 42.98 | 2350.4112 | 29.7046 | 29.7046 | 2320.7066 | Heating | 2047.6823 | 8.5 | 2047.6823 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.5365 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2089.4718 | 0 | 417.8944 | 4.179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 12:01 | 11 | 8 | 12 | 312 | 7476 | 48.02 | 1820.3641 | 113.8556 | 113.8556 | 1706.5085 | Heating | 1505.7428 | 8.5 | 1505.7428 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.1486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1536.4722 | 0 | 307.2944 | 3.073% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 13:01 | 11 | 8 | 13 | 312 | 7477 | 50 | 1479.4507 | 205.7933 | 205.7933 | 1273.6574 | Heating | 1123.8153 | 8.5 | 1123.8153 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.7631 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1146.7504 | 0 | 229.3501 | 2.294% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 14:01 | 11 | 8 | 14 | 312 | 7478 | 50 | 2019.1698 | 89.0669 | 89.0669 | 1930.1029 | Heating | 1703.0319 | 8.5 | 1703.0319 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.6064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1737.7877 | 0 | 347.5575 | 3.476% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 15:01 | 11 | 8 | 15 | 312 | 7479 | 53.06 | 2199.3883 | 42.9314 | 42.9314 | 2156.4568 | Heating | 1902.756 | 8.5 | 1902.756 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.5512 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1941.5878 | 0 | 388.3176 | 3.883% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 16:01 | 11 | 8 | 16 | 312 | 7480 | 51.98 | 2163.2476 | 43.4254 | 43.4254 | 2119.8222 | Heating | 1870.4314 | 8.5 | 1870.4314 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.0863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1908.6034 | 0 | 381.7207 | 3.817% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 17:01 | 11 | 8 | 17 | 312 | 7481 | 51.98 | 2590.5836 | 18.9653 | 18.9653 | 2571.6183 | Heating | 2269.075 | 8.5 | 2269.075 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 453.815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2315.3826 | 0 | 463.0765 | 4.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 18:01 | 11 | 8 | 18 | 312 | 7482 | 42.08 | 3117.8516 | 0 | 0 | 3117.8516 | Heating | 2751.0456 | 8.5 | 2751.0456 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.2091 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2807.1894 | 0 | 561.4379 | 5.614% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 19:01 | 11 | 8 | 19 | 312 | 7483 | 39.02 | 3468.4036 | 0 | 0 | 3468.4036 | Heating | 3060.3561 | 8.5 | 3060.3561 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 612.0712 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3122.8124 | 0 | 624.5625 | 6.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 20:01 | 11 | 8 | 20 | 312 | 7484 | 39.02 | 3976.4593 | 0 | 0 | 3976.4593 | Heating | 3508.6406 | 8.5 | 3508.6406 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 701.7281 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3580.2455 | 0 | 716.0491 | 7.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 21:01 | 11 | 8 | 21 | 312 | 7485 | 35.96 | 4344.2486 | 0 | 0 | 4344.2486 | Heating | 3833.1606 | 8.5 | 3833.1606 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 766.6321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3911.3883 | 0 | 782.2777 | 7.823% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 22:01 | 11 | 8 | 22 | 312 | 7486 | 35.06 | 1150.0535 | 0 | 0 | 1150.0535 | Heating | 1014.7531 | 8.5 | 1014.7531 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.9506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1035.4624 | 0 | 207.0925 | 2.071% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-08 23:01 | 11 | 8 | 23 | 312 | 7487 | 35.06 | 1098.2669 | 0 | 0 | 1098.2669 | Heating | 969.059 | 8.5 | 969.059 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 193.8118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 988.8357 | 0 | 197.7671 | 1.978% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 00:01 | 11 | 9 | 0 | 313 | 7488 | 33.08 | 1250.5121 | 0 | 0 | 1250.5121 | Heating | 1103.393 | 8.5 | 1103.393 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 220.6786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1125.9113 | 0 | 225.1823 | 2.252% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 01:01 | 11 | 9 | 1 | 313 | 7489 | 32 | 1324.7874 | 0 | 0 | 1324.7874 | Heating | 1168.9301 | 8.5 | 1168.9301 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1192.7858 | 0 | 238.5572 | 2.386% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 02:01 | 11 | 9 | 2 | 313 | 7490 | 32 | 1462.6945 | 0 | 0 | 1462.6945 | Heating | 1290.6128 | 8.5 | 1290.6128 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 258.1226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1316.9518 | 0 | 263.3904 | 2.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 03:01 | 11 | 9 | 3 | 313 | 7491 | 30.02 | 1621.1728 | 0 | 0 | 1621.1728 | Heating | 1430.4466 | 8.5 | 1430.4466 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.0893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1459.6394 | 0 | 291.9279 | 2.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 04:01 | 11 | 9 | 4 | 313 | 7492 | 26.96 | 1676.4252 | 0 | 0 | 1676.4252 | Heating | 1479.1987 | 8.5 | 1479.1987 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.8397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1509.3864 | 0 | 301.8773 | 3.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 05:01 | 11 | 9 | 5 | 313 | 7493 | 26.96 | 1764.4632 | 0 | 0 | 1764.4632 | Heating | 1556.8793 | 8.5 | 1556.8793 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.3759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1588.6523 | 0 | 317.7305 | 3.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 06:01 | 11 | 9 | 6 | 313 | 7494 | 28.04 | 1872.5412 | 0 | 0 | 1872.5412 | Heating | 1652.2422 | 8.5 | 1652.2422 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 330.4484 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1685.9615 | 0 | 337.1923 | 3.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 07:01 | 11 | 9 | 7 | 313 | 7495 | 28.04 | 11261.2291 | 0 | 0 | 11261.2291 | Heating | 9936.3786 | 8.5 | 9936.3786 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1987.2757 | 39.75% | 1 | 79.49% | 0% | 0% | 0% | 48.0701 | 0 | 0 | 0 | 48.0701 | 10139.1618 | 0 | 2027.8324 | 20.28% | 1 | 40.56% | 0% | 0% | 5.1128 | 0 | 0 | 5.1128 | 53.1828
2007-11-09 08:01 | 11 | 9 | 8 | 313 | 7496 | 28.04 | 8281.3946 | 0 | 0 | 8281.3946 | Heating | 7307.1129 | 8.5 | 7307.1129 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1461.4226 | 30% | 1 | 58.46% | 0% | 0% | 0% | 23.7064 | 0 | 0 | 0 | 23.7064 | 7456.2376 | 0 | 1491.2475 | 14.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.9809
2007-11-09 09:01 | 11 | 9 | 9 | 313 | 7497 | 37.94 | 6779.8888 | 0 | 0 | 6779.8888 | Heating | 5982.2548 | 8.5 | 5982.2548 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1196.451 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6104.3417 | 0 | 1220.8683 | 12.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 10:01 | 11 | 9 | 10 | 313 | 7498 | 42.98 | 5348.1003 | 0 | 0 | 5348.1003 | Heating | 4718.912 | 8.5 | 4718.912 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 943.7824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4815.2163 | 0 | 963.0433 | 9.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 11:01 | 11 | 9 | 11 | 313 | 7499 | 42.98 | 4383.96 | 0 | 0 | 4383.96 | Heating | 3868.2 | 8.5 | 3868.2 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 773.64 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3947.1429 | 0 | 789.4286 | 7.894% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 12:01 | 11 | 9 | 12 | 313 | 7500 | 51.98 | 3708.963 | 0 | 0 | 3708.963 | Heating | 3272.6145 | 8.5 | 3272.6145 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 654.5229 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3339.4025 | 0 | 667.8805 | 6.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 13:01 | 11 | 9 | 13 | 313 | 7501 | 55.94 | 3275.2816 | 0 | 0 | 3275.2816 | Heating | 2889.9543 | 8.5 | 2889.9543 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 577.9909 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2948.933 | 0 | 589.7866 | 5.898% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 14:01 | 11 | 9 | 14 | 313 | 7502 | 55.94 | 3225.4858 | 0 | 0 | 3225.4858 | Heating | 2846.0168 | 8.5 | 2846.0168 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 569.2034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2904.0988 | 0 | 580.8198 | 5.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 15:01 | 11 | 9 | 15 | 313 | 7503 | 59 | 3370.9128 | 0 | 0 | 3370.9128 | Heating | 2974.3348 | 8.5 | 2974.3348 | 0 | 5.4953 | 0 | 0 | 0 | 0 | 8.5 | 0 | 594.867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3035.0355 | 0 | 607.0071 | 6.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 16:01 | 11 | 9 | 16 | 313 | 7504 | 57.92 | 3488.1468 | 0 | 0 | 3488.1468 | Heating | 3077.7766 | 8.5 | 3077.7766 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 615.5553 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3140.5884 | 0 | 628.1177 | 6.281% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 17:01 | 11 | 9 | 17 | 313 | 7505 | 57.92 | 3855.2153 | 0 | 0 | 3855.2153 | Heating | 3401.6605 | 8.5 | 3401.6605 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 680.3321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3471.0822 | 0 | 694.2164 | 6.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 18:01 | 11 | 9 | 18 | 313 | 7506 | 46.94 | 4273.3857 | 0 | 0 | 4273.3857 | Heating | 3770.6344 | 8.5 | 3770.6344 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 754.1269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3847.5862 | 0 | 769.5172 | 7.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 19:01 | 11 | 9 | 19 | 313 | 7507 | 44.96 | 4660.3892 | 0 | 0 | 4660.3892 | Heating | 4112.1081 | 8.5 | 4112.1081 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 822.4216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4196.0287 | 0 | 839.2057 | 8.392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 20:01 | 11 | 9 | 20 | 313 | 7508 | 44.96 | 5355.1775 | 0 | 0 | 5355.1775 | Heating | 4725.1566 | 8.5 | 4725.1566 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 945.0313 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4821.5884 | 0 | 964.3177 | 9.643% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 21:01 | 11 | 9 | 21 | 313 | 7509 | 41 | 5614.225 | 0 | 0 | 5614.225 | Heating | 4953.7279 | 8.5 | 4953.7279 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 990.7456 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5054.8244 | 0 | 1010.9649 | 10.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 22:01 | 11 | 9 | 22 | 313 | 7510 | 41 | 6290.9768 | 0 | 0 | 6290.9768 | Heating | 5550.8619 | 8.5 | 5550.8619 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1110.1724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5664.1448 | 0 | 1132.829 | 11.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-09 23:01 | 11 | 9 | 23 | 313 | 7511 | 41 | 1933.4267 | 0 | 0 | 1933.4267 | Heating | 1705.9648 | 8.5 | 1705.9648 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 341.193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1740.7804 | 0 | 348.1561 | 3.482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 00:01 | 11 | 10 | 0 | 314 | 7512 | 39.92 | 2050.3988 | 0 | 0 | 2050.3988 | Heating | 1809.1754 | 8.5 | 1809.1754 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.8351 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1846.0974 | 0 | 369.2195 | 3.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 01:01 | 11 | 10 | 1 | 314 | 7513 | 39.92 | 2121.0443 | 0 | 0 | 2121.0443 | Heating | 1871.5097 | 8.5 | 1871.5097 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.3019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1909.7038 | 0 | 381.9408 | 3.819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 02:01 | 11 | 10 | 2 | 314 | 7514 | 39.92 | 2280.7672 | 0 | 0 | 2280.7672 | Heating | 2012.4417 | 8.5 | 2012.4417 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.4883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2053.5119 | 0 | 410.7024 | 4.107% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 03:01 | 11 | 10 | 3 | 314 | 7515 | 42.98 | 2427.0397 | 0 | 0 | 2427.0397 | Heating | 2141.5056 | 8.5 | 2141.5056 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 428.3011 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2185.2098 | 0 | 437.042 | 4.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 04:01 | 11 | 10 | 4 | 314 | 7516 | 44.06 | 2424.6183 | 0 | 0 | 2424.6183 | Heating | 2139.3691 | 8.5 | 2139.3691 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.8738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2183.0297 | 0 | 436.6059 | 4.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 05:01 | 11 | 10 | 5 | 314 | 7517 | 44.06 | 2444.41 | 0 | 0 | 2444.41 | Heating | 2156.8324 | 8.5 | 2156.8324 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 431.3665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2200.8493 | 0 | 440.1699 | 4.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 06:01 | 11 | 10 | 6 | 314 | 7518 | 42.98 | 2368.4811 | 0 | 0 | 2368.4811 | Heating | 2089.8363 | 8.5 | 2089.8363 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 417.9673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2132.486 | 0 | 426.4972 | 4.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 07:01 | 11 | 10 | 7 | 314 | 7519 | 42.98 | 2248.9151 | 0 | 0 | 2248.9151 | Heating | 1984.3369 | 8.5 | 1984.3369 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 396.8674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2024.8335 | 0 | 404.9667 | 4.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 08:01 | 11 | 10 | 8 | 314 | 7520 | 42.98 | 2158.4481 | 0 | 0 | 2158.4481 | Heating | 1904.5131 | 8.5 | 1904.5131 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.9026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1943.3807 | 0 | 388.6761 | 3.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 09:01 | 11 | 10 | 9 | 314 | 7521 | 46.04 | 11556.5563 | 0 | 0 | 11556.5563 | Heating | 10196.9614 | 8.5 | 10196.9614 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2039.3923 | 40.79% | 1 | 81.58% | 0% | 0% | 0% | 51.0191 | 0 | 0 | 0 | 51.0191 | 10405.0627 | 0 | 2081.0125 | 20.81% | 1 | 41.62% | 0% | 0% | 5.4264 | 0 | 0 | 5.4264 | 56.4455
2007-11-10 10:01 | 11 | 10 | 10 | 314 | 7522 | 48.02 | 8687.1776 | 0 | 0 | 8687.1776 | Heating | 7665.1567 | 8.5 | 7665.1567 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1533.0313 | 30.66% | 1 | 61.32% | 0% | 0% | 0% | 26.4636 | 0 | 0 | 0 | 26.4636 | 7821.5885 | 0 | 1564.3177 | 15.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.7381
2007-11-10 11:01 | 11 | 10 | 11 | 314 | 7523 | 48.02 | 7390.3228 | 0 | 0 | 7390.3228 | Heating | 6520.873 | 8.5 | 6520.873 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1304.1746 | 30% | 1 | 52.17% | 0% | 0% | 0% | 18.2454 | 0 | 0 | 0 | 18.2454 | 6653.9521 | 0 | 1330.7904 | 13.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.5199
2007-11-10 12:01 | 11 | 10 | 12 | 314 | 7524 | 50 | 6679.5404 | 0 | 0 | 6679.5404 | Heating | 5893.7121 | 8.5 | 5893.7121 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1178.7424 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6013.9919 | 0 | 1202.7984 | 12.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 13:01 | 11 | 10 | 13 | 314 | 7525 | 50 | 5694.0728 | 0 | 0 | 5694.0728 | Heating | 5024.1819 | 8.5 | 5024.1819 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1004.8364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5126.7162 | 0 | 1025.3432 | 10.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 14:01 | 11 | 10 | 14 | 314 | 7526 | 50 | 4974.5429 | 0 | 0 | 4974.5429 | Heating | 4389.3026 | 8.5 | 4389.3026 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 877.8605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4478.8802 | 0 | 895.776 | 8.958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 15:01 | 11 | 10 | 15 | 314 | 7527 | 48.02 | 4415.6549 | 0 | 0 | 4415.6549 | Heating | 3896.1661 | 8.5 | 3896.1661 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 779.2332 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3975.6797 | 0 | 795.1359 | 7.951% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 16:01 | 11 | 10 | 16 | 314 | 7528 | 46.94 | 4205.5427 | 0 | 0 | 4205.5427 | Heating | 3710.773 | 8.5 | 3710.773 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 742.1546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3786.503 | 0 | 757.3006 | 7.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 17:01 | 11 | 10 | 17 | 314 | 7529 | 44.96 | 4190.24 | 0 | 0 | 4190.24 | Heating | 3697.2706 | 8.5 | 3697.2706 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 739.4541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3772.7251 | 0 | 754.545 | 7.545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 18:01 | 11 | 10 | 18 | 314 | 7530 | 44.06 | 5689.4149 | 0 | 0 | 5689.4149 | Heating | 5020.0719 | 8.5 | 5020.0719 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1004.0144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5122.5224 | 0 | 1024.5045 | 10.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 19:01 | 11 | 10 | 19 | 314 | 7531 | 44.06 | 5811.7445 | 0 | 0 | 5811.7445 | Heating | 5128.0098 | 8.5 | 5128.0098 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1025.602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5232.6631 | 0 | 1046.5326 | 10.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 20:01 | 11 | 10 | 20 | 314 | 7532 | 44.06 | 1253.5096 | 0 | 0 | 1253.5096 | Heating | 1106.0379 | 8.5 | 1106.0379 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.2076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1128.6101 | 0 | 225.722 | 2.257% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 21:01 | 11 | 10 | 21 | 314 | 7533 | 42.98 | 1227.1627 | 0 | 0 | 1227.1627 | Heating | 1082.7906 | 8.5 | 1082.7906 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 216.5581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1104.8884 | 0 | 220.9777 | 2.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 22:01 | 11 | 10 | 22 | 314 | 7534 | 42.08 | 1223.7035 | 0 | 0 | 1223.7035 | Heating | 1079.7383 | 8.5 | 1079.7383 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.9477 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1101.7738 | 0 | 220.3548 | 2.204% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-10 23:01 | 11 | 10 | 23 | 314 | 7535 | 42.08 | 1253.9037 | 0 | 0 | 1253.9037 | Heating | 1106.3856 | 8.5 | 1106.3856 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.2771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1128.9649 | 0 | 225.793 | 2.258% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 00:01 | 11 | 11 | 0 | 315 | 7536 | 39.92 | 1275.2519 | 0 | 0 | 1275.2519 | Heating | 1125.2223 | 8.5 | 1125.2223 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.0445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1148.186 | 0 | 229.6372 | 2.296% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 01:01 | 11 | 11 | 1 | 315 | 7537 | 39.02 | 1309.4101 | 0 | 0 | 1309.4101 | Heating | 1155.3619 | 8.5 | 1155.3619 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.0724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1178.9407 | 0 | 235.7881 | 2.358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 02:01 | 11 | 11 | 2 | 315 | 7538 | 39.02 | 1325.518 | 0 | 0 | 1325.518 | Heating | 1169.5747 | 8.5 | 1169.5747 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.9149 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1193.4436 | 0 | 238.6887 | 2.387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 03:01 | 11 | 11 | 3 | 315 | 7539 | 33.98 | 1371.1745 | 0 | 0 | 1371.1745 | Heating | 1209.8598 | 8.5 | 1209.8598 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 241.972 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1234.5508 | 0 | 246.9102 | 2.469% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 04:01 | 11 | 11 | 4 | 315 | 7540 | 33.08 | 1392.9838 | 0 | 0 | 1392.9838 | Heating | 1229.1034 | 8.5 | 1229.1034 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.8207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1254.1871 | 0 | 250.8374 | 2.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 05:01 | 11 | 11 | 5 | 315 | 7541 | 33.08 | 1345.8861 | 0 | 0 | 1345.8861 | Heating | 1187.5466 | 8.5 | 1187.5466 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.5093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1211.7822 | 0 | 242.3564 | 2.424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 06:01 | 11 | 11 | 6 | 315 | 7542 | 30.92 | 1335.0761 | 0 | 0 | 1335.0761 | Heating | 1178.0084 | 8.5 | 1178.0084 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.6017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1202.0493 | 0 | 240.4099 | 2.404% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 07:01 | 11 | 11 | 7 | 315 | 7543 | 30.92 | 8964.4798 | 0 | 0 | 8964.4798 | Heating | 7909.8351 | 8.5 | 7909.8351 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1581.967 | 31.64% | 1 | 63.28% | 0% | 0% | 0% | 28.4469 | 0 | 0 | 0 | 28.4469 | 8071.2603 | 0 | 1614.2521 | 16.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.7215
2007-11-11 08:01 | 11 | 11 | 8 | 315 | 7544 | 30.92 | 6450.7585 | 0 | 0 | 6450.7585 | Heating | 5691.8457 | 8.5 | 5691.8457 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1138.3691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5808.0058 | 0 | 1161.6012 | 11.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 09:01 | 11 | 11 | 9 | 315 | 7545 | 39.02 | 4959.9743 | 0 | 0 | 4959.9743 | Heating | 4376.4479 | 8.5 | 4376.4479 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 875.2896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4465.7632 | 0 | 893.1526 | 8.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 10:01 | 11 | 11 | 10 | 315 | 7546 | 42.08 | 3634.3699 | 0 | 0 | 3634.3699 | Heating | 3206.7969 | 8.5 | 3206.7969 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 641.3594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3272.2418 | 0 | 654.4484 | 6.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 11:01 | 11 | 11 | 11 | 315 | 7547 | 42.08 | 2819.2778 | 0 | 0 | 2819.2778 | Heating | 2487.598 | 8.5 | 2487.598 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 497.5196 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2538.3653 | 0 | 507.6731 | 5.077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 12:01 | 11 | 11 | 12 | 315 | 7548 | 44.96 | 1860.6533 | 0 | 0 | 1860.6533 | Heating | 1641.753 | 8.5 | 1641.753 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.3506 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1675.2581 | 0 | 335.0516 | 3.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 13:01 | 11 | 11 | 13 | 315 | 7549 | 48.92 | 1437.0286 | 0 | 0 | 1437.0286 | Heating | 1267.9664 | 8.5 | 1267.9664 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.5933 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1293.8433 | 0 | 258.7687 | 2.588% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 14:01 | 11 | 11 | 14 | 315 | 7550 | 48.92 | 1056.8101 | 0 | 0 | 1056.8101 | Heating | 932.4795 | 8.5 | 932.4795 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 186.4959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 951.5097 | 0 | 190.3019 | 1.903% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 15:01 | 11 | 11 | 15 | 315 | 7551 | 48.02 | 910.3719 | 0 | 0 | 910.3719 | Heating | 803.2693 | 8.5 | 803.2693 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.6539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 819.6625 | 0 | 163.9325 | 1.639% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 16:01 | 11 | 11 | 16 | 315 | 7552 | 48.02 | 889.5937 | 0 | 0 | 889.5937 | Heating | 784.9356 | 8.5 | 784.9356 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.9871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 800.9547 | 0 | 160.1909 | 1.602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 17:01 | 11 | 11 | 17 | 315 | 7553 | 48.02 | 1176.8139 | 0 | 0 | 1176.8139 | Heating | 1038.3652 | 8.5 | 1038.3652 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1059.5564 | 0 | 211.9113 | 2.119% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 18:01 | 11 | 11 | 18 | 315 | 7554 | 44.96 | 1599.8074 | 0 | 0 | 1599.8074 | Heating | 1411.5948 | 8.5 | 1411.5948 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 282.319 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1440.4028 | 0 | 288.0806 | 2.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 19:01 | 11 | 11 | 19 | 315 | 7555 | 44.06 | 2089.1311 | 0 | 0 | 2089.1311 | Heating | 1843.351 | 8.5 | 1843.351 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.6702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1880.9704 | 0 | 376.1941 | 3.762% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 20:01 | 11 | 11 | 20 | 315 | 7556 | 44.06 | 2708.5251 | 0 | 0 | 2708.5251 | Heating | 2389.8751 | 8.5 | 2389.8751 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 477.975 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2438.6481 | 0 | 487.7296 | 4.877% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 21:01 | 11 | 11 | 21 | 315 | 7557 | 42.08 | 3180.284 | 0 | 0 | 3180.284 | Heating | 2806.1329 | 8.5 | 2806.1329 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 561.2266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2863.4009 | 0 | 572.6802 | 5.727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 22:01 | 11 | 11 | 22 | 315 | 7558 | 42.08 | 956.1117 | 0 | 0 | 956.1117 | Heating | 843.628 | 8.5 | 843.628 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 168.7256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 860.8449 | 0 | 172.169 | 1.722% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-11 23:01 | 11 | 11 | 23 | 315 | 7559 | 42.08 | 876.6589 | 0 | 0 | 876.6589 | Heating | 773.5226 | 8.5 | 773.5226 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.7045 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 789.3088 | 0 | 157.8618 | 1.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 00:01 | 11 | 12 | 0 | 316 | 7560 | 44.96 | 1034.3582 | 0 | 0 | 1034.3582 | Heating | 912.669 | 8.5 | 912.669 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.5338 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 931.2949 | 0 | 186.259 | 1.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 01:01 | 11 | 12 | 1 | 316 | 7561 | 44.96 | 1166.3932 | 0 | 0 | 1166.3932 | Heating | 1029.1705 | 8.5 | 1029.1705 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 205.8341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1050.174 | 0 | 210.0348 | 2.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 02:01 | 11 | 12 | 2 | 316 | 7562 | 44.96 | 1262.3049 | 0 | 0 | 1262.3049 | Heating | 1113.7984 | 8.5 | 1113.7984 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.7597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1136.529 | 0 | 227.3058 | 2.273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 03:01 | 11 | 12 | 3 | 316 | 7563 | 39.92 | 1345.689 | 0 | 0 | 1345.689 | Heating | 1187.3726 | 8.5 | 1187.3726 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 237.4745 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1211.6047 | 0 | 242.3209 | 2.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 04:01 | 11 | 12 | 4 | 316 | 7564 | 46.04 | 1457.8824 | 0 | 0 | 1457.8824 | Heating | 1286.3668 | 8.5 | 1286.3668 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 257.2734 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1312.6192 | 0 | 262.5238 | 2.625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 05:01 | 11 | 12 | 5 | 316 | 7565 | 46.04 | 1523.7074 | 0 | 0 | 1523.7074 | Heating | 1344.4477 | 8.5 | 1344.4477 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.8895 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1371.8854 | 0 | 274.3771 | 2.744% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 06:01 | 11 | 12 | 6 | 316 | 7566 | 53.96 | 1530.1977 | 0 | 0 | 1530.1977 | Heating | 1350.1744 | 8.5 | 1350.1744 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 270.0349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1377.729 | 0 | 275.5458 | 2.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 07:01 | 11 | 12 | 7 | 316 | 7567 | 51.98 | 10003.1403 | 0 | 0 | 10003.1403 | Heating | 8826.3002 | 8.5 | 8826.3002 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1765.26 | 35.31% | 1 | 70.61% | 0% | 0% | 0% | 36.6051 | 0 | 0 | 0 | 36.6051 | 9006.4288 | 0 | 1801.2858 | 18.01% | 1 | 36.03% | 0% | 0% | 3.8933 | 0 | 0 | 3.8933 | 40.4984
2007-11-12 08:01 | 11 | 12 | 8 | 316 | 7568 | 51.98 | 7596.4662 | 0 | 0 | 7596.4662 | Heating | 6702.7643 | 8.5 | 6702.7643 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1340.5529 | 30% | 1 | 53.62% | 0% | 0% | 0% | 19.4372 | 0 | 0 | 0 | 19.4372 | 6839.5554 | 0 | 1367.9111 | 13.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.7118
2007-11-12 09:01 | 11 | 12 | 9 | 316 | 7569 | 51.98 | 6493.8705 | 0 | 0 | 6493.8705 | Heating | 5729.8857 | 8.5 | 5729.8857 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1145.9771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5846.8222 | 0 | 1169.3644 | 11.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 10:01 | 11 | 12 | 10 | 316 | 7570 | 51.08 | 5629.5003 | 0 | 0 | 5629.5003 | Heating | 4967.2061 | 8.5 | 4967.2061 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 993.4412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5068.5777 | 0 | 1013.7155 | 10.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 11:01 | 11 | 12 | 11 | 316 | 7571 | 51.08 | 5306.7932 | 0 | 0 | 5306.7932 | Heating | 4682.4646 | 8.5 | 4682.4646 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 936.4929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4778.0251 | 0 | 955.605 | 9.556% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 12:01 | 11 | 12 | 12 | 316 | 7572 | 48.92 | 4952.7759 | 0 | 0 | 4952.7759 | Heating | 4370.0964 | 8.5 | 4370.0964 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 874.0193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4459.282 | 0 | 891.8564 | 8.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 13:01 | 11 | 12 | 13 | 316 | 7573 | 44.96 | 4646.9674 | 0 | 0 | 4646.9674 | Heating | 4100.2653 | 8.5 | 4100.2653 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 820.0531 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4183.9442 | 0 | 836.7888 | 8.368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 14:01 | 11 | 12 | 14 | 316 | 7574 | 44.96 | 4370.2541 | 0 | 0 | 4370.2541 | Heating | 3856.1066 | 8.5 | 3856.1066 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 771.2213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3934.8026 | 0 | 786.9605 | 7.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 15:01 | 11 | 12 | 15 | 316 | 7575 | 44.96 | 4271.611 | 0 | 0 | 4271.611 | Heating | 3769.0685 | 8.5 | 3769.0685 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 753.8137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3845.9883 | 0 | 769.1977 | 7.692% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 16:01 | 11 | 12 | 16 | 316 | 7576 | 42.98 | 4121.3471 | 0 | 0 | 4121.3471 | Heating | 3636.4828 | 8.5 | 3636.4828 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.2966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3710.6967 | 0 | 742.1393 | 7.421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 17:01 | 11 | 12 | 17 | 316 | 7577 | 42.98 | 4106.2032 | 0 | 0 | 4106.2032 | Heating | 3623.1205 | 8.5 | 3623.1205 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 724.6241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3697.0617 | 0 | 739.4123 | 7.394% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 18:01 | 11 | 12 | 18 | 316 | 7578 | 41 | 4226.0247 | 0 | 0 | 4226.0247 | Heating | 3728.8453 | 8.5 | 3728.8453 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.7691 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3804.9442 | 0 | 760.9888 | 7.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 19:01 | 11 | 12 | 19 | 316 | 7579 | 39.02 | 4306.1207 | 0 | 0 | 4306.1207 | Heating | 3799.5183 | 8.5 | 3799.5183 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 759.9037 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3877.0595 | 0 | 775.4119 | 7.754% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 20:01 | 11 | 12 | 20 | 316 | 7580 | 39.02 | 4538.6182 | 0 | 0 | 4538.6182 | Heating | 4004.6631 | 8.5 | 4004.6631 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 800.9326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4086.3909 | 0 | 817.2782 | 8.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 21:01 | 11 | 12 | 21 | 316 | 7581 | 37.04 | 4694.4858 | 0 | 0 | 4694.4858 | Heating | 4142.1934 | 8.5 | 4142.1934 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 828.4387 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4226.7279 | 0 | 845.3456 | 8.453% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 22:01 | 11 | 12 | 22 | 316 | 7582 | 37.04 | 1324.6344 | 0 | 0 | 1324.6344 | Heating | 1168.795 | 8.5 | 1168.795 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1192.648 | 0 | 238.5296 | 2.385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-12 23:01 | 11 | 12 | 23 | 316 | 7583 | 37.04 | 1131.8003 | 0 | 0 | 1131.8003 | Heating | 998.6473 | 8.5 | 998.6473 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.7295 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1019.0279 | 0 | 203.8056 | 2.038% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 00:01 | 11 | 13 | 0 | 317 | 7584 | 35.06 | 1327.9546 | 0 | 0 | 1327.9546 | Heating | 1171.7246 | 8.5 | 1171.7246 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 234.3449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1195.6374 | 0 | 239.1275 | 2.391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 01:01 | 11 | 13 | 1 | 317 | 7585 | 33.98 | 1459.878 | 0 | 0 | 1459.878 | Heating | 1288.1277 | 8.5 | 1288.1277 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 257.6255 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1314.416 | 0 | 262.8832 | 2.629% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 02:01 | 11 | 13 | 2 | 317 | 7586 | 33.98 | 1584.1871 | 0 | 0 | 1584.1871 | Heating | 1397.8122 | 8.5 | 1397.8122 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.5624 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1426.339 | 0 | 285.2678 | 2.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 03:01 | 11 | 13 | 3 | 317 | 7587 | 30.92 | 1715.0243 | 0 | 0 | 1715.0243 | Heating | 1513.2568 | 8.5 | 1513.2568 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 302.6514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1544.1395 | 0 | 308.8279 | 3.088% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 04:01 | 11 | 13 | 4 | 317 | 7588 | 28.94 | 1798.9025 | 0 | 0 | 1798.9025 | Heating | 1587.2669 | 8.5 | 1587.2669 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.4534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1619.6601 | 0 | 323.932 | 3.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 05:01 | 11 | 13 | 5 | 317 | 7589 | 28.94 | 1879.8835 | 0 | 0 | 1879.8835 | Heating | 1658.7207 | 8.5 | 1658.7207 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 331.7441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1692.5722 | 0 | 338.5144 | 3.385% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 06:01 | 11 | 13 | 6 | 317 | 7590 | 26.96 | 2001.6644 | 0 | 0 | 2001.6644 | Heating | 1766.1745 | 8.5 | 1766.1745 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 353.2349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1802.2189 | 0 | 360.4438 | 3.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 07:01 | 11 | 13 | 7 | 317 | 7591 | 28.94 | 11874.4625 | 0 | 0 | 11874.4625 | Heating | 10477.4669 | 8.5 | 10477.4669 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2095.4934 | 41.91% | 1 | 83.82% | 0% | 0% | 0% | 54.305 | 0 | 0 | 0 | 54.305 | 10691.2928 | 0 | 2138.2586 | 21.38% | 1 | 42.77% | 0% | 0% | 5.7759 | 0 | 0 | 5.7759 | 60.0809
2007-11-13 08:01 | 11 | 13 | 8 | 317 | 7592 | 28.94 | 8931.2054 | 0 | 0 | 8931.2054 | Heating | 7880.4753 | 8.5 | 7880.4753 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1576.0951 | 31.52% | 1 | 63.04% | 0% | 0% | 0% | 28.2046 | 0 | 0 | 0 | 28.2046 | 8041.3014 | 0 | 1608.2603 | 16.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.4792
2007-11-13 09:01 | 11 | 13 | 9 | 317 | 7593 | 35.96 | 7033.1278 | 0 | 0 | 7033.1278 | Heating | 6205.701 | 8.5 | 6205.701 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1241.1402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6332.348 | 0 | 1266.4696 | 12.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 10:01 | 11 | 13 | 10 | 317 | 7594 | 37.94 | 5340.2998 | 0 | 0 | 5340.2998 | Heating | 4712.0292 | 8.5 | 4712.0292 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 942.4058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4808.1931 | 0 | 961.6386 | 9.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 11:01 | 11 | 13 | 11 | 317 | 7595 | 37.94 | 4251.1921 | 0 | 0 | 4251.1921 | Heating | 3751.0519 | 8.5 | 3751.0519 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.2104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3827.604 | 0 | 765.5208 | 7.655% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 12:01 | 11 | 13 | 12 | 317 | 7596 | 41 | 3412.2592 | 0 | 0 | 3412.2592 | Heating | 3010.8169 | 8.5 | 3010.8169 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 602.1634 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3072.2621 | 0 | 614.4524 | 6.145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 13:01 | 11 | 13 | 13 | 317 | 7597 | 42.98 | 2998.4458 | 1.5059 | 1.5059 | 2996.9399 | Heating | 2644.3588 | 8.5 | 2644.3588 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 528.8718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2698.3253 | 0 | 539.6651 | 5.397% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 14:01 | 11 | 13 | 14 | 317 | 7598 | 42.98 | 2763.8199 | 30.247 | 30.247 | 2733.5729 | Heating | 2411.9761 | 8.5 | 2411.9761 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 482.3952 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2461.2001 | 0 | 492.24 | 4.922% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 15:01 | 11 | 13 | 15 | 317 | 7599 | 44.06 | 2737.7188 | 42.9782 | 42.9782 | 2694.7407 | Heating | 2377.7123 | 8.5 | 2377.7123 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 475.5425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2426.2371 | 0 | 485.2474 | 4.852% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 16:01 | 11 | 13 | 16 | 317 | 7600 | 44.06 | 2853.5455 | 26.0451 | 26.0451 | 2827.5003 | Heating | 2494.8532 | 8.5 | 2494.8532 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 498.9706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2545.7686 | 0 | 509.1537 | 5.092% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 17:01 | 11 | 13 | 17 | 317 | 7601 | 44.06 | 3292.2749 | 3.9814 | 3.9814 | 3288.2934 | Heating | 2901.4354 | 8.5 | 2901.4354 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 580.2871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2960.6483 | 0 | 592.1297 | 5.921% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 18:01 | 11 | 13 | 18 | 317 | 7602 | 37.94 | 3829.2429 | 0 | 0 | 3829.2429 | Heating | 3378.7437 | 8.5 | 3378.7437 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 675.7487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3447.6977 | 0 | 689.5395 | 6.895% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 19:01 | 11 | 13 | 19 | 317 | 7603 | 33.08 | 4355.9465 | 0 | 0 | 4355.9465 | Heating | 3843.4822 | 8.5 | 3843.4822 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 768.6964 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3921.9206 | 0 | 784.3841 | 7.844% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 20:01 | 11 | 13 | 20 | 317 | 7604 | 33.08 | 4776.1436 | 0 | 0 | 4776.1436 | Heating | 4214.2444 | 8.5 | 4214.2444 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 842.8489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4300.2494 | 0 | 860.0499 | 8.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 21:01 | 11 | 13 | 21 | 317 | 7605 | 28.94 | 5164.2114 | 0 | 0 | 5164.2114 | Heating | 4556.6571 | 8.5 | 4556.6571 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 911.3314 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4649.6501 | 0 | 929.93 | 9.299% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 22:01 | 11 | 13 | 22 | 317 | 7606 | 30.02 | 1546.7448 | 0 | 0 | 1546.7448 | Heating | 1364.7749 | 8.5 | 1364.7749 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1392.6274 | 0 | 278.5255 | 2.785% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-13 23:01 | 11 | 13 | 23 | 317 | 7607 | 30.02 | 1444.256 | 0 | 0 | 1444.256 | Heating | 1274.3436 | 8.5 | 1274.3436 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.8687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1300.3506 | 0 | 260.0701 | 2.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 00:01 | 11 | 14 | 0 | 318 | 7608 | 30.92 | 1667.4513 | 0 | 0 | 1667.4513 | Heating | 1471.2805 | 8.5 | 1471.2805 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 294.2561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1501.3067 | 0 | 300.2613 | 3.003% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 01:01 | 11 | 14 | 1 | 318 | 7609 | 33.08 | 1821.2121 | 0 | 0 | 1821.2121 | Heating | 1606.9518 | 8.5 | 1606.9518 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.3904 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1639.7467 | 0 | 327.9493 | 3.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 02:01 | 11 | 14 | 2 | 318 | 7610 | 33.08 | 2062.0007 | 0 | 0 | 2062.0007 | Heating | 1819.4123 | 8.5 | 1819.4123 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.8825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1856.5432 | 0 | 371.3086 | 3.713% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 03:01 | 11 | 14 | 3 | 318 | 7611 | 35.96 | 2093.4749 | 0 | 0 | 2093.4749 | Heating | 1847.1837 | 8.5 | 1847.1837 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.4367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1884.8813 | 0 | 376.9763 | 3.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 04:01 | 11 | 14 | 4 | 318 | 7612 | 35.06 | 2154.9456 | 0 | 0 | 2154.9456 | Heating | 1901.4226 | 8.5 | 1901.4226 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.2845 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1940.2271 | 0 | 388.0454 | 3.88% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 05:01 | 11 | 14 | 5 | 318 | 7613 | 35.06 | 2299.6716 | 0 | 0 | 2299.6716 | Heating | 2029.122 | 8.5 | 2029.122 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 405.8244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2070.5326 | 0 | 414.1065 | 4.141% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 06:01 | 11 | 14 | 6 | 318 | 7614 | 35.06 | 2407.8462 | 0 | 0 | 2407.8462 | Heating | 2124.5702 | 8.5 | 2124.5702 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.914 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2167.9287 | 0 | 433.5857 | 4.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 07:01 | 11 | 14 | 7 | 318 | 7615 | 35.96 | 12970.6837 | 0 | 0 | 12970.6837 | Heating | 11444.7209 | 8.5 | 11444.7209 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2288.9442 | 45.78% | 1 | 91.56% | 0% | 0% | 0% | 66.5337 | 0 | 0 | 0 | 66.5337 | 11678.2867 | 0 | 2335.6573 | 23.36% | 1 | 46.71% | 0% | 0% | 7.0766 | 0 | 0 | 7.0766 | 73.6103
2007-11-14 08:01 | 11 | 14 | 8 | 318 | 7616 | 35.96 | 9955.7697 | 0 | 0 | 9955.7697 | Heating | 8784.5027 | 8.5 | 8784.5027 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1756.9005 | 35.14% | 1 | 70.28% | 0% | 0% | 0% | 36.2076 | 0 | 0 | 0 | 36.2076 | 8963.7783 | 0 | 1792.7557 | 17.93% | 1 | 35.86% | 0% | 0% | 3.8511 | 0 | 0 | 3.8511 | 40.0586
2007-11-14 09:01 | 11 | 14 | 9 | 318 | 7617 | 39.92 | 7721.0758 | 0 | 0 | 7721.0758 | Heating | 6812.7139 | 8.5 | 6812.7139 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1362.5428 | 30% | 1 | 54.5% | 0% | 0% | 0% | 20.1784 | 0 | 0 | 0 | 20.1784 | 6951.7489 | 0 | 1390.3498 | 13.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.4529
2007-11-14 10:01 | 11 | 14 | 10 | 318 | 7618 | 46.94 | 5576.6213 | 0 | 0 | 5576.6213 | Heating | 4920.5482 | 8.5 | 4920.5482 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 984.1096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5020.9675 | 0 | 1004.1935 | 10.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 11:01 | 11 | 14 | 11 | 318 | 7619 | 46.94 | 3892.9534 | 0 | 0 | 3892.9534 | Heating | 3434.9589 | 8.5 | 3434.9589 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 686.9918 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3505.0601 | 0 | 701.012 | 7.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 12:01 | 11 | 14 | 12 | 318 | 7620 | 53.96 | 2684.5407 | 20.6534 | 20.6534 | 2663.8872 | Heating | 2350.4887 | 8.5 | 2350.4887 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 470.0977 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2398.4579 | 0 | 479.6916 | 4.797% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 13:01 | 11 | 14 | 13 | 318 | 7621 | 55.94 | 2040.1667 | 55.8393 | 55.8393 | 1984.3274 | Heating | 1750.8771 | 8.5 | 1750.8771 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 350.1754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1786.6093 | 0 | 357.3219 | 3.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 14:01 | 11 | 14 | 14 | 318 | 7622 | 55.94 | 1613.9021 | 115.8655 | 115.8655 | 1498.0365 | Heating | 1321.797 | 8.5 | 1321.797 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.3594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1348.7724 | 0 | 269.7545 | 2.698% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 15:01 | 11 | 14 | 15 | 318 | 7623 | 57.92 | 1474.3477 | 147.8494 | 147.8494 | 1326.4983 | Heating | 1170.4396 | 8.5 | 1170.4396 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 234.0879 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1194.3262 | 0 | 238.8652 | 2.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 16:01 | 11 | 14 | 16 | 318 | 7624 | 55.04 | 1595.6425 | 81.9326 | 81.9326 | 1513.7099 | Heating | 1335.6264 | 8.5 | 1335.6264 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.1253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1362.884 | 0 | 272.5768 | 2.726% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 17:01 | 11 | 14 | 17 | 318 | 7625 | 55.04 | 1955.4623 | 52.8366 | 52.8366 | 1902.6256 | Heating | 1678.7873 | 8.5 | 1678.7873 | 0 | 5.0265 | 0 | 0 | 0 | 0 | 8.5 | 0 | 335.7575 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1713.0483 | 0 | 342.6097 | 3.426% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 18:01 | 11 | 14 | 18 | 318 | 7626 | 42.98 | 2225.8558 | 19.9588 | 19.9588 | 2205.897 | Heating | 1946.3797 | 8.5 | 1946.3797 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 389.2759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1986.1017 | 0 | 397.2203 | 3.972% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 19:01 | 11 | 14 | 19 | 318 | 7627 | 39.92 | 2561.9908 | 0.13595 | 0.13595 | 2561.8549 | Heating | 2260.4602 | 8.5 | 2260.4602 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 452.092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2306.592 | 0 | 461.3184 | 4.613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 20:01 | 11 | 14 | 20 | 318 | 7628 | 39.92 | 2907.8969 | 0 | 0 | 2907.8969 | Heating | 2565.7914 | 8.5 | 2565.7914 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 513.1583 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2618.1545 | 0 | 523.6309 | 5.236% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 21:01 | 11 | 14 | 21 | 318 | 7629 | 35.96 | 3154.7513 | 0 | 0 | 3154.7513 | Heating | 2783.6041 | 8.5 | 2783.6041 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 556.7208 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2840.4123 | 0 | 568.0825 | 5.681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 22:01 | 11 | 14 | 22 | 318 | 7630 | 33.08 | 850.2636 | 0 | 0 | 850.2636 | Heating | 750.2326 | 8.5 | 750.2326 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.0465 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 765.5435 | 0 | 153.1087 | 1.531% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-14 23:01 | 11 | 14 | 23 | 318 | 7631 | 33.08 | 777.7622 | 0 | 0 | 777.7622 | Heating | 686.2608 | 8.5 | 686.2608 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.2522 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 700.2661 | 0 | 140.0532 | 1.401% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 00:01 | 11 | 15 | 0 | 319 | 7632 | 33.98 | 854.2291 | 0 | 0 | 854.2291 | Heating | 753.7315 | 8.5 | 753.7315 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.7463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 769.1138 | 0 | 153.8228 | 1.538% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 01:01 | 11 | 15 | 1 | 319 | 7633 | 32 | 1031.2458 | 0 | 0 | 1031.2458 | Heating | 909.9227 | 8.5 | 909.9227 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 181.9845 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 928.4926 | 0 | 185.6985 | 1.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 02:01 | 11 | 15 | 2 | 319 | 7634 | 32 | 1110.8787 | 0 | 0 | 1110.8787 | Heating | 980.1871 | 8.5 | 980.1871 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.0374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1000.1909 | 0 | 200.0382 | 2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 03:01 | 11 | 15 | 3 | 319 | 7635 | 32 | 1152.6029 | 0 | 0 | 1152.6029 | Heating | 1017.0026 | 8.5 | 1017.0026 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 203.4005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1037.7577 | 0 | 207.5515 | 2.076% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 04:01 | 11 | 15 | 4 | 319 | 7636 | 30.02 | 1237.9179 | 0 | 0 | 1237.9179 | Heating | 1092.2805 | 8.5 | 1092.2805 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.4561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1114.5719 | 0 | 222.9144 | 2.229% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 05:01 | 11 | 15 | 5 | 319 | 7637 | 30.02 | 1223.1827 | 0 | 0 | 1223.1827 | Heating | 1079.2789 | 8.5 | 1079.2789 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 215.8558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1101.305 | 0 | 220.261 | 2.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 06:01 | 11 | 15 | 6 | 319 | 7638 | 26.06 | 1235.2405 | 0 | 0 | 1235.2405 | Heating | 1089.9181 | 8.5 | 1089.9181 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 217.9836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1112.1613 | 0 | 222.4323 | 2.224% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 07:01 | 11 | 15 | 7 | 319 | 7639 | 26.06 | 9328.9789 | 0 | 0 | 9328.9789 | Heating | 8231.452 | 8.5 | 8231.452 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1646.2904 | 32.93% | 1 | 65.85% | 0% | 0% | 0% | 31.1778 | 0 | 0 | 0 | 31.1778 | 8399.4408 | 0 | 1679.8882 | 16.8% | 1 | 33.6% | 0% | 0% | 3.3161 | 0 | 0 | 3.3161 | 34.4939
2007-11-15 08:01 | 11 | 15 | 8 | 319 | 7640 | 26.06 | 6756.2535 | 0 | 0 | 6756.2535 | Heating | 5961.4002 | 8.5 | 5961.4002 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1192.28 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6083.0614 | 0 | 1216.6123 | 12.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 09:01 | 11 | 15 | 9 | 319 | 7641 | 42.98 | 4866.5107 | 0 | 0 | 4866.5107 | Heating | 4293.98 | 8.5 | 4293.98 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 858.796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4381.6123 | 0 | 876.3225 | 8.763% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 10:01 | 11 | 15 | 10 | 319 | 7642 | 46.94 | 3215.2316 | 0 | 0 | 3215.2316 | Heating | 2836.969 | 8.5 | 2836.969 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 567.3938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2894.8664 | 0 | 578.9733 | 5.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 11:01 | 11 | 15 | 11 | 319 | 7643 | 46.94 | 2229.102 | 15.1922 | 15.1922 | 2213.9098 | Heating | 1953.4498 | 8.5 | 1953.4498 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.69 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1993.3161 | 0 | 398.6632 | 3.987% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 12:01 | 11 | 15 | 12 | 319 | 7644 | 53.96 | 1443.8015 | 71.0831 | 71.0831 | 1372.7185 | Heating | 1211.2222 | 8.5 | 1211.2222 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.2444 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1235.941 | 0 | 247.1882 | 2.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 13:01 | 11 | 15 | 13 | 319 | 7645 | 57.02 | 959.9696 | 209.0156 | 209.0156 | 750.954 | Heating | 662.6065 | 8.5 | 662.6065 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.5213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 676.1291 | 0 | 135.2258 | 1.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 14:01 | 11 | 15 | 14 | 319 | 7646 | 57.02 | 617.9173 | 313.2931 | 313.2931 | 304.6242 | Heating | 268.786 | 8.5 | 268.786 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 53.7572 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 274.2715 | 0 | 54.8543 | 0.5485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 15:01 | 11 | 15 | 15 | 319 | 7647 | 57.02 | 547.2415 | 328.3429 | 328.3429 | 218.8985 | Heating | 193.1458 | 8.5 | 193.1458 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 38.6292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 197.0875 | 0 | 39.4175 | 0.3942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 16:01 | 11 | 15 | 16 | 319 | 7648 | 57.02 | 591.3562 | 240.6535 | 240.6535 | 350.7027 | Heating | 309.4435 | 8.5 | 309.4435 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 61.8887 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 315.7587 | 0 | 63.1517 | 0.6315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 17:01 | 11 | 15 | 17 | 319 | 7649 | 53.06 | 1081.1802 | 111.1103 | 111.1103 | 970.0699 | Heating | 855.944 | 8.5 | 855.944 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.1888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 873.4123 | 0 | 174.6825 | 1.747% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 18:01 | 11 | 15 | 18 | 319 | 7650 | 46.04 | 1466.3151 | 65.7837 | 65.7837 | 1400.5314 | Heating | 1235.763 | 8.5 | 1235.763 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.1526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1260.9827 | 0 | 252.1965 | 2.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 19:01 | 11 | 15 | 19 | 319 | 7651 | 39.92 | 1729.2548 | 25.8099 | 25.8099 | 1703.445 | Heating | 1503.0397 | 8.5 | 1503.0397 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.6079 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1533.7139 | 0 | 306.7428 | 3.067% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 20:01 | 11 | 15 | 20 | 319 | 7652 | 39.92 | 2052.591 | 8.5467 | 8.5467 | 2044.0443 | Heating | 1803.5685 | 8.5 | 1803.5685 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 360.7137 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1840.376 | 0 | 368.0752 | 3.681% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 21:01 | 11 | 15 | 21 | 319 | 7653 | 41 | 2216.1611 | 0 | 0 | 2216.1611 | Heating | 1955.4363 | 8.5 | 1955.4363 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 391.0873 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1995.3431 | 0 | 399.0686 | 3.991% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 22:01 | 11 | 15 | 22 | 319 | 7654 | 39.92 | 619.1626 | 0 | 0 | 619.1626 | Heating | 546.3199 | 8.5 | 546.3199 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 557.4693 | 0 | 111.4939 | 1.115% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-15 23:01 | 11 | 15 | 23 | 319 | 7655 | 39.92 | 731.697 | 0 | 0 | 731.697 | Heating | 645.615 | 8.5 | 645.615 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 658.7908 | 0 | 131.7582 | 1.318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 00:01 | 11 | 16 | 0 | 320 | 7656 | 39.92 | 894.6743 | 0 | 0 | 894.6743 | Heating | 789.4185 | 8.5 | 789.4185 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.8837 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 805.5291 | 0 | 161.1058 | 1.611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 01:01 | 11 | 16 | 1 | 320 | 7657 | 35.06 | 1001.2801 | 0 | 0 | 1001.2801 | Heating | 883.4824 | 8.5 | 883.4824 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 176.6965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 901.5127 | 0 | 180.3025 | 1.803% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 02:01 | 11 | 16 | 2 | 320 | 7658 | 35.06 | 1118.64 | 0 | 0 | 1118.64 | Heating | 987.0353 | 8.5 | 987.0353 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 197.4071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1007.1788 | 0 | 201.4358 | 2.014% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 03:01 | 11 | 16 | 3 | 320 | 7659 | 37.04 | 1195.3971 | 0 | 0 | 1195.3971 | Heating | 1054.7622 | 8.5 | 1054.7622 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 210.9524 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1076.2879 | 0 | 215.2576 | 2.153% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 04:01 | 11 | 16 | 4 | 320 | 7660 | 37.94 | 1046.0083 | 0 | 0 | 1046.0083 | Heating | 922.9485 | 8.5 | 922.9485 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.5897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 941.7842 | 0 | 188.3568 | 1.884% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 05:01 | 11 | 16 | 5 | 320 | 7661 | 37.94 | 979.7065 | 0 | 0 | 979.7065 | Heating | 864.4469 | 8.5 | 864.4469 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.8894 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 882.0886 | 0 | 176.4177 | 1.764% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 06:01 | 11 | 16 | 6 | 320 | 7662 | 37.94 | 1078.2623 | 0 | 0 | 1078.2623 | Heating | 951.4079 | 8.5 | 951.4079 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.2816 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 970.8244 | 0 | 194.1649 | 1.942% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 07:01 | 11 | 16 | 7 | 320 | 7663 | 35.96 | 8860.1685 | 0 | 0 | 8860.1685 | Heating | 7817.7958 | 8.5 | 7817.7958 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1563.5592 | 31.27% | 1 | 62.54% | 0% | 0% | 0% | 27.6913 | 0 | 0 | 0 | 27.6913 | 7977.3426 | 0 | 1595.4685 | 15.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.9659
2007-11-16 08:01 | 11 | 16 | 8 | 320 | 7664 | 35.96 | 6229.4246 | 0 | 0 | 6229.4246 | Heating | 5496.5511 | 8.5 | 5496.5511 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1099.3102 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5608.7257 | 0 | 1121.7451 | 11.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 09:01 | 11 | 16 | 9 | 320 | 7665 | 39.02 | 4899.6062 | 0 | 0 | 4899.6062 | Heating | 4323.182 | 8.5 | 4323.182 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 864.6364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4411.4102 | 0 | 882.282 | 8.823% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 10:01 | 11 | 16 | 10 | 320 | 7666 | 42.08 | 3829.4729 | 0 | 0 | 3829.4729 | Heating | 3378.9467 | 8.5 | 3378.9467 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 675.7893 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3447.9048 | 0 | 689.581 | 6.896% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 11:01 | 11 | 16 | 11 | 320 | 7667 | 42.08 | 2911.0456 | 0 | 0 | 2911.0456 | Heating | 2568.5696 | 8.5 | 2568.5696 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 513.7139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2620.9894 | 0 | 524.1979 | 5.242% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 12:01 | 11 | 16 | 12 | 320 | 7668 | 42.08 | 2147.7811 | 0 | 0 | 2147.7811 | Heating | 1895.101 | 8.5 | 1895.101 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.0202 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1933.7765 | 0 | 386.7553 | 3.868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 13:01 | 11 | 16 | 13 | 320 | 7669 | 42.98 | 1514.5165 | 0 | 0 | 1514.5165 | Heating | 1336.3381 | 8.5 | 1336.3381 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.2676 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1363.6103 | 0 | 272.7221 | 2.727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 14:01 | 11 | 16 | 14 | 320 | 7670 | 42.98 | 1081.4065 | 1.2028 | 1.2028 | 1080.2037 | Heating | 953.1209 | 8.5 | 953.1209 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 190.6242 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 972.5724 | 0 | 194.5145 | 1.945% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 15:01 | 11 | 16 | 15 | 320 | 7671 | 41 | 827.0003 | 0 | 0 | 827.0003 | Heating | 729.7061 | 8.5 | 729.7061 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.9412 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 744.5981 | 0 | 148.9196 | 1.489% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 16:01 | 11 | 16 | 16 | 320 | 7672 | 42.08 | 875.7852 | 0 | 0 | 875.7852 | Heating | 772.7516 | 8.5 | 772.7516 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.5503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 788.522 | 0 | 157.7044 | 1.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 17:01 | 11 | 16 | 17 | 320 | 7673 | 42.08 | 1273.3964 | 0 | 0 | 1273.3964 | Heating | 1123.5851 | 8.5 | 1123.5851 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1146.5154 | 0 | 229.3031 | 2.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 18:01 | 11 | 16 | 18 | 320 | 7674 | 44.06 | 2124.5087 | 0 | 0 | 2124.5087 | Heating | 1874.5665 | 8.5 | 1874.5665 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.9133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1912.8229 | 0 | 382.5646 | 3.826% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 19:01 | 11 | 16 | 19 | 320 | 7675 | 44.96 | 2905.9827 | 0 | 0 | 2905.9827 | Heating | 2564.1024 | 8.5 | 2564.1024 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 512.8205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2616.431 | 0 | 523.2862 | 5.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 20:01 | 11 | 16 | 20 | 320 | 7676 | 46.04 | 3481.1156 | 0 | 0 | 3481.1156 | Heating | 3071.5726 | 8.5 | 3071.5726 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 614.3145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3134.2578 | 0 | 626.8516 | 6.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 21:01 | 11 | 16 | 21 | 320 | 7677 | 46.04 | 3996.107 | 0 | 0 | 3996.107 | Heating | 3525.9768 | 8.5 | 3525.9768 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 705.1954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3597.9355 | 0 | 719.5871 | 7.196% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 22:01 | 11 | 16 | 22 | 320 | 7678 | 46.04 | 4635.5857 | 0 | 0 | 4635.5857 | Heating | 4090.2227 | 8.5 | 4090.2227 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 818.0445 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4173.6966 | 0 | 834.7393 | 8.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-16 23:01 | 11 | 16 | 23 | 320 | 7679 | 46.04 | 1084.6872 | 0 | 0 | 1084.6872 | Heating | 957.0769 | 8.5 | 957.0769 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 191.4154 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 976.6091 | 0 | 195.3218 | 1.953% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 00:01 | 11 | 17 | 0 | 321 | 7680 | 46.04 | 1169.0999 | 0 | 0 | 1169.0999 | Heating | 1031.5588 | 8.5 | 1031.5588 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.3118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1052.611 | 0 | 210.5222 | 2.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 01:01 | 11 | 17 | 1 | 321 | 7681 | 46.04 | 1307.5265 | 0 | 0 | 1307.5265 | Heating | 1153.6999 | 8.5 | 1153.6999 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 230.74 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1177.2448 | 0 | 235.449 | 2.354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 02:01 | 11 | 17 | 2 | 321 | 7682 | 46.04 | 1380.7639 | 0 | 0 | 1380.7639 | Heating | 1218.3211 | 8.5 | 1218.3211 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 243.6642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1243.1848 | 0 | 248.637 | 2.486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 03:01 | 11 | 17 | 3 | 321 | 7683 | 46.4 | 1440.3292 | 0 | 0 | 1440.3292 | Heating | 1270.8787 | 8.5 | 1270.8787 | 0 | 4.1996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.1757 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1296.815 | 0 | 259.363 | 2.594% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 04:01 | 11 | 17 | 4 | 321 | 7684 | 46.4 | 1506.0724 | 0 | 0 | 1506.0724 | Heating | 1328.8874 | 8.5 | 1328.8874 | 0 | 4.1996 | 0 | 0 | 0 | 0 | 8.5 | 0 | 265.7775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1356.0076 | 0 | 271.2015 | 2.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 05:01 | 11 | 17 | 5 | 321 | 7685 | 46.04 | 1475.5141 | 0 | 0 | 1475.5141 | Heating | 1301.9242 | 8.5 | 1301.9242 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 260.3848 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1328.4941 | 0 | 265.6988 | 2.657% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 06:01 | 11 | 17 | 6 | 321 | 7686 | 46.04 | 1449.2809 | 0 | 0 | 1449.2809 | Heating | 1278.7773 | 8.5 | 1278.7773 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 255.7555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1304.8748 | 0 | 260.975 | 2.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 07:01 | 11 | 17 | 7 | 321 | 7687 | 46.04 | 1417.6719 | 0 | 0 | 1417.6719 | Heating | 1250.887 | 8.5 | 1250.887 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 250.1774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1276.4153 | 0 | 255.2831 | 2.553% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 08:01 | 11 | 17 | 8 | 321 | 7688 | 46.04 | 1339.4766 | 0 | 0 | 1339.4766 | Heating | 1181.8911 | 8.5 | 1181.8911 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 236.3782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1206.0113 | 0 | 241.2023 | 2.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 09:01 | 11 | 17 | 9 | 321 | 7689 | 48.02 | 8364.3197 | 0 | 0 | 8364.3197 | Heating | 7380.2821 | 8.5 | 7380.2821 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1476.0564 | 30% | 1 | 59.04% | 0% | 0% | 0% | 24.2559 | 0 | 0 | 0 | 24.2559 | 7530.9001 | 0 | 1506.18 | 15.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.5305
2007-11-17 10:01 | 11 | 17 | 10 | 321 | 7690 | 48.92 | 5947.2055 | 0 | 0 | 5947.2055 | Heating | 5247.5343 | 8.5 | 5247.5343 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1049.5069 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5354.6268 | 0 | 1070.9254 | 10.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 11:01 | 11 | 17 | 11 | 321 | 7691 | 48.92 | 4595.6299 | 0 | 0 | 4595.6299 | Heating | 4054.9676 | 8.5 | 4054.9676 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 810.9935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4137.722 | 0 | 827.5444 | 8.275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 12:01 | 11 | 17 | 12 | 321 | 7692 | 51.98 | 3660.981 | 0 | 0 | 3660.981 | Heating | 3230.2773 | 8.5 | 3230.2773 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 646.0555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3296.2014 | 0 | 659.2403 | 6.592% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 13:01 | 11 | 17 | 13 | 321 | 7693 | 51.98 | 2806.3103 | 0 | 0 | 2806.3103 | Heating | 2476.1561 | 8.5 | 2476.1561 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 495.2312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2526.6899 | 0 | 505.338 | 5.053% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 14:01 | 11 | 17 | 14 | 321 | 7694 | 51.98 | 2382.7001 | 0 | 0 | 2382.7001 | Heating | 2102.3824 | 8.5 | 2102.3824 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 420.4765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2145.2882 | 0 | 429.0576 | 4.291% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 15:01 | 11 | 17 | 15 | 321 | 7695 | 53.96 | 2174.2779 | 0 | 0 | 2174.2779 | Heating | 1918.4805 | 8.5 | 1918.4805 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 383.6961 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1957.6332 | 0 | 391.5266 | 3.915% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 16:01 | 11 | 17 | 16 | 321 | 7696 | 53.06 | 2097.7742 | 0 | 0 | 2097.7742 | Heating | 1850.9772 | 8.5 | 1850.9772 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 370.1954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1888.7523 | 0 | 377.7505 | 3.778% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 17:01 | 11 | 17 | 17 | 321 | 7697 | 53.06 | 2133.6363 | 0 | 0 | 2133.6363 | Heating | 1882.6203 | 8.5 | 1882.6203 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.5241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1921.0411 | 0 | 384.2082 | 3.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 18:01 | 11 | 17 | 18 | 321 | 7698 | 48.02 | 3334.2761 | 0 | 0 | 3334.2761 | Heating | 2942.0084 | 8.5 | 2942.0084 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 588.4017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3002.0493 | 0 | 600.4099 | 6.004% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 19:01 | 11 | 17 | 19 | 321 | 7699 | 46.94 | 3753.4025 | 0 | 0 | 3753.4025 | Heating | 3311.8258 | 8.5 | 3311.8258 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 662.3652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3379.414 | 0 | 675.8828 | 6.759% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 20:01 | 11 | 17 | 20 | 321 | 7700 | 46.94 | 650.0102 | 0 | 0 | 650.0102 | Heating | 573.5384 | 8.5 | 573.5384 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 114.7077 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 585.2432 | 0 | 117.0486 | 1.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 21:01 | 11 | 17 | 21 | 321 | 7701 | 39.92 | 657.4579 | 0 | 0 | 657.4579 | Heating | 580.1099 | 8.5 | 580.1099 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 591.9489 | 0 | 118.3898 | 1.184% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 22:01 | 11 | 17 | 22 | 321 | 7702 | 42.98 | 687.6193 | 0 | 0 | 687.6193 | Heating | 606.7229 | 8.5 | 606.7229 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.3446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 619.105 | 0 | 123.821 | 1.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-17 23:01 | 11 | 17 | 23 | 321 | 7703 | 42.98 | 733.3068 | 0 | 0 | 733.3068 | Heating | 647.0355 | 8.5 | 647.0355 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.4071 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 660.2403 | 0 | 132.0481 | 1.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 00:01 | 11 | 18 | 0 | 322 | 7704 | 41 | 783.5093 | 0 | 0 | 783.5093 | Heating | 691.3317 | 8.5 | 691.3317 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.2663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 705.4405 | 0 | 141.0881 | 1.411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 01:01 | 11 | 18 | 1 | 322 | 7705 | 41 | 845.9624 | 0 | 0 | 845.9624 | Heating | 746.4374 | 8.5 | 746.4374 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.2875 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 761.6708 | 0 | 152.3342 | 1.523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 02:01 | 11 | 18 | 2 | 322 | 7706 | 41 | 855.64 | 0 | 0 | 855.64 | Heating | 754.9764 | 8.5 | 754.9764 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.9953 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 770.3841 | 0 | 154.0768 | 1.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 03:01 | 11 | 18 | 3 | 322 | 7707 | 37.04 | 893.74 | 0 | 0 | 893.74 | Heating | 788.5941 | 8.5 | 788.5941 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.7188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 804.6878 | 0 | 160.9376 | 1.609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 04:01 | 11 | 18 | 4 | 322 | 7708 | 39.02 | 932.3988 | 0 | 0 | 932.3988 | Heating | 822.7049 | 8.5 | 822.7049 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 164.541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 839.4948 | 0 | 167.899 | 1.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 05:01 | 11 | 18 | 5 | 322 | 7709 | 39.02 | 1053.5842 | 0 | 0 | 1053.5842 | Heating | 929.6331 | 8.5 | 929.6331 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 185.9266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 948.6052 | 0 | 189.721 | 1.897% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 06:01 | 11 | 18 | 6 | 322 | 7710 | 44.96 | 1205.6064 | 0 | 0 | 1205.6064 | Heating | 1063.7703 | 8.5 | 1063.7703 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.7541 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1085.4799 | 0 | 217.096 | 2.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 07:01 | 11 | 18 | 7 | 322 | 7711 | 39.02 | 8628.2731 | 0 | 0 | 8628.2731 | Heating | 7613.1822 | 8.5 | 7613.1822 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1522.6364 | 30.45% | 1 | 60.91% | 0% | 0% | 0% | 26.0527 | 0 | 0 | 0 | 26.0527 | 7768.5532 | 0 | 1553.7106 | 15.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.3272
2007-11-18 08:01 | 11 | 18 | 8 | 322 | 7712 | 39.02 | 5958.6679 | 0 | 0 | 5958.6679 | Heating | 5257.6481 | 8.5 | 5257.6481 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1051.5296 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5364.9471 | 0 | 1072.9894 | 10.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 09:01 | 11 | 18 | 9 | 322 | 7713 | 50 | 4456.7364 | 0 | 0 | 4456.7364 | Heating | 3932.4145 | 8.5 | 3932.4145 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 786.4829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4012.6679 | 0 | 802.5336 | 8.025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 10:01 | 11 | 18 | 10 | 322 | 7714 | 53.06 | 3067.2919 | 0 | 0 | 3067.2919 | Heating | 2706.4341 | 8.5 | 2706.4341 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 541.2868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2761.6674 | 0 | 552.3335 | 5.523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 11:01 | 11 | 18 | 11 | 322 | 7715 | 53.06 | 2133.1443 | 0 | 0 | 2133.1443 | Heating | 1882.1861 | 8.5 | 1882.1861 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.4372 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1920.5981 | 0 | 384.1196 | 3.841% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 12:01 | 11 | 18 | 12 | 322 | 7716 | 51.08 | 1374.309 | 0 | 0 | 1374.309 | Heating | 1212.6256 | 8.5 | 1212.6256 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 242.5251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1237.373 | 0 | 247.4746 | 2.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 13:01 | 11 | 18 | 13 | 322 | 7717 | 51.98 | 1065.5689 | 0 | 0 | 1065.5689 | Heating | 940.2079 | 8.5 | 940.2079 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.0416 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 959.3958 | 0 | 191.8792 | 1.919% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 14:01 | 11 | 18 | 14 | 322 | 7718 | 51.98 | 975.4233 | 0 | 0 | 975.4233 | Heating | 860.6676 | 8.5 | 860.6676 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.1335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 878.2322 | 0 | 175.6464 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 15:01 | 11 | 18 | 15 | 322 | 7719 | 55.94 | 960.3932 | 0 | 0 | 960.3932 | Heating | 847.4057 | 8.5 | 847.4057 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.4811 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 864.6997 | 0 | 172.9399 | 1.729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 16:01 | 11 | 18 | 16 | 322 | 7720 | 53.96 | 869.8784 | 0 | 0 | 869.8784 | Heating | 767.5398 | 8.5 | 767.5398 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 153.508 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 783.2038 | 0 | 156.6408 | 1.566% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 17:01 | 11 | 18 | 17 | 322 | 7721 | 53.96 | 984.4474 | 0 | 0 | 984.4474 | Heating | 868.63 | 8.5 | 868.63 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 173.726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 886.3572 | 0 | 177.2714 | 1.773% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 18:01 | 11 | 18 | 18 | 322 | 7722 | 46.94 | 1213.2663 | 0 | 0 | 1213.2663 | Heating | 1070.5291 | 8.5 | 1070.5291 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 214.1058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1092.3766 | 0 | 218.4753 | 2.185% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 19:01 | 11 | 18 | 19 | 322 | 7723 | 44.06 | 1397.2229 | 0 | 0 | 1397.2229 | Heating | 1232.8437 | 8.5 | 1232.8437 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 246.5687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1258.0038 | 0 | 251.6008 | 2.516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 20:01 | 11 | 18 | 20 | 322 | 7724 | 44.06 | 1622.1791 | 0 | 0 | 1622.1791 | Heating | 1431.3345 | 8.5 | 1431.3345 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 286.2669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1460.5454 | 0 | 292.1091 | 2.921% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 21:01 | 11 | 18 | 21 | 322 | 7725 | 42.08 | 1835.3393 | 0 | 0 | 1835.3393 | Heating | 1619.4171 | 8.5 | 1619.4171 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.8834 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1652.4664 | 0 | 330.4933 | 3.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 22:01 | 11 | 18 | 22 | 322 | 7726 | 41 | 524.5764 | 0 | 0 | 524.5764 | Heating | 462.8615 | 8.5 | 462.8615 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 92.5723 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 472.3077 | 0 | 94.4615 | 0.9446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-18 23:01 | 11 | 18 | 23 | 322 | 7727 | 41 | 516.8489 | 0 | 0 | 516.8489 | Heating | 456.0431 | 8.5 | 456.0431 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.2086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 465.3501 | 0 | 93.07 | 0.9307% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 00:01 | 11 | 19 | 0 | 323 | 7728 | 37.94 | 543.2681 | 0 | 0 | 543.2681 | Heating | 479.3542 | 8.5 | 479.3542 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 95.8708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 489.137 | 0 | 97.8274 | 0.9783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 01:01 | 11 | 19 | 1 | 323 | 7729 | 35.96 | 553.6714 | 0 | 0 | 553.6714 | Heating | 488.5336 | 8.5 | 488.5336 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 97.7067 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 498.5037 | 0 | 99.7007 | 0.997% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 02:01 | 11 | 19 | 2 | 323 | 7730 | 35.96 | 546.9237 | 0 | 0 | 546.9237 | Heating | 482.5798 | 8.5 | 482.5798 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.516 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 492.4283 | 0 | 98.4857 | 0.9849% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 03:01 | 11 | 19 | 3 | 323 | 7731 | 33.98 | 545.4578 | 0 | 0 | 545.4578 | Heating | 481.2863 | 8.5 | 481.2863 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 96.2573 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 491.1085 | 0 | 98.2217 | 0.9822% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 04:01 | 11 | 19 | 4 | 323 | 7732 | 33.08 | 562.3235 | 0 | 0 | 562.3235 | Heating | 496.1678 | 8.5 | 496.1678 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 99.2336 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 506.2936 | 0 | 101.2587 | 1.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 05:01 | 11 | 19 | 5 | 323 | 7733 | 33.08 | 520.9827 | 0 | 0 | 520.9827 | Heating | 459.6906 | 8.5 | 459.6906 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 91.9381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 469.072 | 0 | 93.8144 | 0.9381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 06:01 | 11 | 19 | 6 | 323 | 7734 | 32 | 484.2693 | 0 | 0 | 484.2693 | Heating | 427.2965 | 8.5 | 427.2965 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 85.4593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 436.0168 | 0 | 87.2034 | 0.872% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 07:01 | 11 | 19 | 7 | 323 | 7735 | 30.92 | 5102.602 | 23.8211 | 23.8211 | 5078.7809 | Heating | 4481.2773 | 8.5 | 4481.2773 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 896.2555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4572.7319 | 0 | 914.5464 | 9.145% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 08:01 | 11 | 19 | 8 | 323 | 7736 | 30.92 | 3350.6051 | 0 | 0 | 3350.6051 | Heating | 2956.4163 | 8.5 | 2956.4163 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.2833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3016.7513 | 0 | 603.3503 | 6.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 09:01 | 11 | 19 | 9 | 323 | 7737 | 39.02 | 2291.6946 | 0 | 0 | 2291.6946 | Heating | 2022.0834 | 8.5 | 2022.0834 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.4167 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2063.3504 | 0 | 412.6701 | 4.127% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 10:01 | 11 | 19 | 10 | 323 | 7738 | 44.06 | 1262.4123 | 0 | 0 | 1262.4123 | Heating | 1113.8932 | 8.5 | 1113.8932 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.7786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1136.6258 | 0 | 227.3252 | 2.273% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 11:01 | 11 | 19 | 11 | 323 | 7739 | 44.06 | 823.2921 | 0 | 0 | 823.2921 | Heating | 726.4342 | 8.5 | 726.4342 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.2868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 741.2594 | 0 | 148.2519 | 1.483% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 12:01 | 11 | 19 | 12 | 323 | 7740 | 51.08 | 358.0426 | 20.0912 | 20.0912 | 337.9514 | Heating | 298.1924 | 8.5 | 298.1924 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.6385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 304.278 | 0 | 60.8556 | 0.6086% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 13:01 | 11 | 19 | 13 | 323 | 7741 | 53.06 | 282.7714 | 32.3453 | 32.3453 | 250.4262 | Heating | 220.9643 | 8.5 | 220.9643 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 44.1929 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 225.4737 | 0 | 45.0947 | 0.4509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 14:01 | 11 | 19 | 14 | 323 | 7742 | 53.06 | 245.5474 | 98.403 | 98.403 | 147.1443 | Heating | 129.8332 | 8.5 | 129.8332 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 25.9666 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 132.4829 | 0 | 26.4966 | 0.265% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 15:01 | 11 | 19 | 15 | 323 | 7743 | 55.94 | 259.3707 | 102.6823 | 102.6823 | 156.6884 | Heating | 138.2545 | 8.5 | 138.2545 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 27.6509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 141.076 | 0 | 28.2152 | 0.2822% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 16:01 | 11 | 19 | 16 | 323 | 7744 | 53.96 | 324.7675 | 92.2179 | 92.2179 | 232.5496 | Heating | 205.1908 | 8.5 | 205.1908 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 41.0382 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 209.3784 | 0 | 41.8757 | 0.4188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 17:01 | 11 | 19 | 17 | 323 | 7745 | 53.96 | 512.02 | 73.0408 | 73.0408 | 438.9792 | Heating | 387.3346 | 8.5 | 387.3346 | 0 | 4.9089 | 0 | 0 | 0 | 0 | 8.5 | 0 | 77.4669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 395.2394 | 0 | 79.0479 | 0.7905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 18:01 | 11 | 19 | 18 | 323 | 7746 | 41 | 1347.4629 | 17.3571 | 17.3571 | 1330.1058 | Heating | 1173.6227 | 8.5 | 1173.6227 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 234.7245 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1197.5742 | 0 | 239.5148 | 2.395% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 19:01 | 11 | 19 | 19 | 323 | 7747 | 42.08 | 1802.5294 | 0 | 0 | 1802.5294 | Heating | 1590.4671 | 8.5 | 1590.4671 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 318.0934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1622.9256 | 0 | 324.5851 | 3.246% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 20:01 | 11 | 19 | 20 | 323 | 7748 | 42.08 | 2113.4799 | 0 | 0 | 2113.4799 | Heating | 1864.8352 | 8.5 | 1864.8352 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1902.8931 | 0 | 380.5786 | 3.806% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 21:01 | 11 | 19 | 21 | 323 | 7749 | 37.04 | 2478.4945 | 0 | 0 | 2478.4945 | Heating | 2186.9069 | 8.5 | 2186.9069 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 437.3814 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2231.5377 | 0 | 446.3075 | 4.463% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 22:01 | 11 | 19 | 22 | 323 | 7750 | 35.96 | 615.4792 | 0 | 0 | 615.4792 | Heating | 543.0699 | 8.5 | 543.0699 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 108.614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 554.153 | 0 | 110.8306 | 1.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-19 23:01 | 11 | 19 | 23 | 323 | 7751 | 35.96 | 641.3458 | 0 | 0 | 641.3458 | Heating | 565.8933 | 8.5 | 565.8933 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.1787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 577.4422 | 0 | 115.4884 | 1.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 00:01 | 11 | 20 | 0 | 324 | 7752 | 35.06 | 681.2698 | 0 | 0 | 681.2698 | Heating | 601.1204 | 8.5 | 601.1204 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.2241 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 613.3882 | 0 | 122.6776 | 1.227% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 01:01 | 11 | 20 | 1 | 324 | 7753 | 33.98 | 730.0919 | 0 | 0 | 730.0919 | Heating | 644.1987 | 8.5 | 644.1987 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.8397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 657.3456 | 0 | 131.4691 | 1.315% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 02:01 | 11 | 20 | 2 | 324 | 7754 | 33.98 | 788.9685 | 0 | 0 | 788.9685 | Heating | 696.1487 | 8.5 | 696.1487 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.2297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 710.3558 | 0 | 142.0712 | 1.421% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 03:01 | 11 | 20 | 3 | 324 | 7755 | 33.08 | 845.6219 | 0 | 0 | 845.6219 | Heating | 746.137 | 8.5 | 746.137 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 149.2274 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 761.3643 | 0 | 152.2729 | 1.523% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 04:01 | 11 | 20 | 4 | 324 | 7756 | 30.92 | 852.9717 | 0 | 0 | 852.9717 | Heating | 752.6221 | 8.5 | 752.6221 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 150.5244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 767.9818 | 0 | 153.5964 | 1.536% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 05:01 | 11 | 20 | 5 | 324 | 7757 | 30.92 | 871.0312 | 0 | 0 | 871.0312 | Heating | 768.5569 | 8.5 | 768.5569 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 153.7114 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 784.2417 | 0 | 156.8483 | 1.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 06:01 | 11 | 20 | 6 | 324 | 7758 | 30.92 | 906.9278 | 0 | 0 | 906.9278 | Heating | 800.2304 | 8.5 | 800.2304 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 160.0461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 816.5616 | 0 | 163.3123 | 1.633% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 07:01 | 11 | 20 | 7 | 324 | 7759 | 30.02 | 8143.1372 | 0 | 0 | 8143.1372 | Heating | 7185.1211 | 8.5 | 7185.1211 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1437.0242 | 30% | 1 | 57.48% | 0% | 0% | 0% | 22.806 | 0 | 0 | 0 | 22.806 | 7331.7562 | 0 | 1466.3512 | 14.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.0805
2007-11-20 08:01 | 11 | 20 | 8 | 324 | 7760 | 30.02 | 6100.1726 | 0 | 0 | 6100.1726 | Heating | 5382.5052 | 8.5 | 5382.5052 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1076.501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5492.3523 | 0 | 1098.4705 | 10.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 09:01 | 11 | 20 | 9 | 324 | 7761 | 32 | 4870.0487 | 0 | 0 | 4870.0487 | Heating | 4297.1018 | 8.5 | 4297.1018 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 859.4204 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4384.7977 | 0 | 876.9595 | 8.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 10:01 | 11 | 20 | 10 | 324 | 7762 | 37.04 | 3653.5851 | 0 | 0 | 3653.5851 | Heating | 3223.7515 | 8.5 | 3223.7515 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 644.7503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3289.5424 | 0 | 657.9085 | 6.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 11:01 | 11 | 20 | 11 | 324 | 7763 | 44.06 | 2978.1545 | 0 | 0 | 2978.1545 | Heating | 2627.7834 | 8.5 | 2627.7834 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 525.5567 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2681.4116 | 0 | 536.2823 | 5.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 12:01 | 11 | 20 | 12 | 324 | 7764 | 55.94 | 2422.7415 | 0 | 0 | 2422.7415 | Heating | 2137.7131 | 8.5 | 2137.7131 | 0 | 5.1278 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.5426 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2181.3398 | 0 | 436.268 | 4.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 13:01 | 11 | 20 | 13 | 324 | 7765 | 60.98 | 2146.098 | 0 | 0 | 2146.098 | Heating | 1893.6159 | 8.5 | 1893.6159 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.7232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1932.2611 | 0 | 386.4522 | 3.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 14:01 | 11 | 20 | 14 | 324 | 7766 | 60.98 | 1976.0647 | 0 | 0 | 1976.0647 | Heating | 1743.5865 | 8.5 | 1743.5865 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 348.7173 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1779.1699 | 0 | 355.834 | 3.558% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 15:01 | 11 | 20 | 15 | 324 | 7767 | 64.04 | 1965.1039 | 0 | 0 | 1965.1039 | Heating | 1733.9152 | 8.5 | 1733.9152 | 0 | 6.1832 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.783 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1769.3012 | 0 | 353.8602 | 3.539% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 16:01 | 11 | 20 | 16 | 324 | 7768 | 60.98 | 2117.2912 | 0 | 0 | 2117.2912 | Heating | 1868.1981 | 8.5 | 1868.1981 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.6396 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1906.3246 | 0 | 381.2649 | 3.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 17:01 | 11 | 20 | 17 | 324 | 7769 | 60.98 | 2300.3975 | 0 | 0 | 2300.3975 | Heating | 2029.7625 | 8.5 | 2029.7625 | 0 | 5.753 | 0 | 0 | 0 | 0 | 8.5 | 0 | 405.9525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2071.1862 | 0 | 414.2372 | 4.142% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 18:01 | 11 | 20 | 18 | 324 | 7770 | 57.92 | 2425.4507 | 0 | 0 | 2425.4507 | Heating | 2140.1035 | 8.5 | 2140.1035 | 0 | 5.3615 | 0 | 0 | 0 | 0 | 8.5 | 0 | 428.0207 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2183.7791 | 0 | 436.7558 | 4.368% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 19:01 | 11 | 20 | 19 | 324 | 7771 | 57.02 | 2566.587 | 0 | 0 | 2566.587 | Heating | 2264.6356 | 8.5 | 2264.6356 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 452.9271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2310.8527 | 0 | 462.1705 | 4.622% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 20:01 | 11 | 20 | 20 | 324 | 7772 | 57.02 | 2623.8877 | 0 | 0 | 2623.8877 | Heating | 2315.195 | 8.5 | 2315.195 | 0 | 5.2534 | 0 | 0 | 0 | 0 | 8.5 | 0 | 463.039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2362.4439 | 0 | 472.4888 | 4.725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 21:01 | 11 | 20 | 21 | 324 | 7773 | 48.92 | 2760.7509 | 0 | 0 | 2760.7509 | Heating | 2435.9567 | 8.5 | 2435.9567 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 487.1913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2485.6701 | 0 | 497.134 | 4.971% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 22:01 | 11 | 20 | 22 | 324 | 7774 | 46.94 | 751.5313 | 0 | 0 | 751.5313 | Heating | 663.1158 | 8.5 | 663.1158 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.6232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 676.6488 | 0 | 135.3298 | 1.353% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-20 23:01 | 11 | 20 | 23 | 324 | 7775 | 46.94 | 694.643 | 0 | 0 | 694.643 | Heating | 612.9203 | 8.5 | 612.9203 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 122.5841 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 625.4289 | 0 | 125.0858 | 1.251% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 00:01 | 11 | 21 | 0 | 325 | 7776 | 42.08 | 724.8892 | 0 | 0 | 724.8892 | Heating | 639.6081 | 8.5 | 639.6081 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.9216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 652.6613 | 0 | 130.5323 | 1.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 01:01 | 11 | 21 | 1 | 325 | 7777 | 41 | 739.4831 | 0 | 0 | 739.4831 | Heating | 652.4851 | 8.5 | 652.4851 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 665.8011 | 0 | 133.1602 | 1.332% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 02:01 | 11 | 21 | 2 | 325 | 7778 | 41 | 743.9344 | 0 | 0 | 743.9344 | Heating | 656.4127 | 8.5 | 656.4127 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.2825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 669.8088 | 0 | 133.9618 | 1.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 03:01 | 11 | 21 | 3 | 325 | 7779 | 35.96 | 751.9405 | 0 | 0 | 751.9405 | Heating | 663.4769 | 8.5 | 663.4769 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.6954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 677.0173 | 0 | 135.4035 | 1.354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 04:01 | 11 | 21 | 4 | 325 | 7780 | 33.98 | 744.1613 | 0 | 0 | 744.1613 | Heating | 656.6129 | 8.5 | 656.6129 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 131.3226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 670.0132 | 0 | 134.0026 | 1.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 05:01 | 11 | 21 | 5 | 325 | 7781 | 33.98 | 736.5731 | 0 | 0 | 736.5731 | Heating | 649.9174 | 8.5 | 649.9174 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.9835 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 663.181 | 0 | 132.6362 | 1.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 06:01 | 11 | 21 | 6 | 325 | 7782 | 33.08 | 726.3998 | 0 | 0 | 726.3998 | Heating | 640.941 | 8.5 | 640.941 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 128.1882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 654.0214 | 0 | 130.8043 | 1.308% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 07:01 | 11 | 21 | 7 | 325 | 7783 | 33.98 | 6794.0744 | 0 | 0 | 6794.0744 | Heating | 5994.7715 | 8.5 | 5994.7715 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1198.9543 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6117.1138 | 0 | 1223.4228 | 12.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 08:01 | 11 | 21 | 8 | 325 | 7784 | 33.98 | 4801.7292 | 0 | 0 | 4801.7292 | Heating | 4236.8199 | 8.5 | 4236.8199 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 847.364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4323.2856 | 0 | 864.6571 | 8.647% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 09:01 | 11 | 21 | 9 | 325 | 7785 | 33.98 | 3759.9913 | 0 | 0 | 3759.9913 | Heating | 3317.6394 | 8.5 | 3317.6394 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 663.5279 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3385.3463 | 0 | 677.0693 | 6.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 10:01 | 11 | 21 | 10 | 325 | 7786 | 33.98 | 2757.6476 | 0 | 0 | 2757.6476 | Heating | 2433.2185 | 8.5 | 2433.2185 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 486.6437 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2482.876 | 0 | 496.5752 | 4.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 11:01 | 11 | 21 | 11 | 325 | 7787 | 33.98 | 2334.1146 | 0 | 0 | 2334.1146 | Heating | 2059.5129 | 8.5 | 2059.5129 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 411.9026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2101.5437 | 0 | 420.3087 | 4.203% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 12:01 | 11 | 21 | 12 | 325 | 7788 | 33.98 | 1951.3431 | 0 | 0 | 1951.3431 | Heating | 1721.7733 | 8.5 | 1721.7733 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.3547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1756.9115 | 0 | 351.3823 | 3.514% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 13:01 | 11 | 21 | 13 | 325 | 7789 | 35.96 | 1687.7088 | 0 | 0 | 1687.7088 | Heating | 1489.1548 | 8.5 | 1489.1548 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.831 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1519.5457 | 0 | 303.9091 | 3.039% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 14:01 | 11 | 21 | 14 | 325 | 7790 | 37.04 | 1526.1392 | 0 | 0 | 1526.1392 | Heating | 1346.5934 | 8.5 | 1346.5934 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 269.3187 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1374.0749 | 0 | 274.815 | 2.748% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 15:01 | 11 | 21 | 15 | 325 | 7791 | 35.96 | 1437.7371 | 0 | 0 | 1437.7371 | Heating | 1268.5916 | 8.5 | 1268.5916 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.7183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1294.4812 | 0 | 258.8962 | 2.589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 16:01 | 11 | 21 | 16 | 325 | 7792 | 35.06 | 1385.9265 | 0 | 0 | 1385.9265 | Heating | 1222.8763 | 8.5 | 1222.8763 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 244.5753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1247.833 | 0 | 249.5666 | 2.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 17:01 | 11 | 21 | 17 | 325 | 7793 | 35.06 | 1406.0283 | 0 | 0 | 1406.0283 | Heating | 1240.6132 | 8.5 | 1240.6132 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.1226 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1265.9319 | 0 | 253.1864 | 2.532% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 18:01 | 11 | 21 | 18 | 325 | 7794 | 33.08 | 1587.6093 | 0 | 0 | 1587.6093 | Heating | 1400.8317 | 8.5 | 1400.8317 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 280.1663 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1429.4201 | 0 | 285.884 | 2.859% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 19:01 | 11 | 21 | 19 | 325 | 7795 | 32 | 1821.2561 | 0 | 0 | 1821.2561 | Heating | 1606.9907 | 8.5 | 1606.9907 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 321.3981 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1639.7864 | 0 | 327.9573 | 3.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 20:01 | 11 | 21 | 20 | 325 | 7796 | 32 | 2010.5246 | 0 | 0 | 2010.5246 | Heating | 1773.9923 | 8.5 | 1773.9923 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 354.7985 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1810.1962 | 0 | 362.0392 | 3.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 21:01 | 11 | 21 | 21 | 325 | 7797 | 30.02 | 2274.7893 | 0 | 0 | 2274.7893 | Heating | 2007.1671 | 8.5 | 2007.1671 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 401.4334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2048.1297 | 0 | 409.6259 | 4.096% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 22:01 | 11 | 21 | 22 | 325 | 7798 | 30.02 | 657.268 | 0 | 0 | 657.268 | Heating | 579.9424 | 8.5 | 579.9424 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.9885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 591.7779 | 0 | 118.3556 | 1.184% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-21 23:01 | 11 | 21 | 23 | 325 | 7799 | 30.02 | 684.964 | 0 | 0 | 684.964 | Heating | 604.38 | 8.5 | 604.38 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 616.7142 | 0 | 123.3428 | 1.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 00:01 | 11 | 22 | 0 | 326 | 7800 | 30.92 | 784.3593 | 0 | 0 | 784.3593 | Heating | 692.0817 | 8.5 | 692.0817 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.4163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 706.2059 | 0 | 141.2412 | 1.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 01:01 | 11 | 22 | 1 | 326 | 7801 | 30.92 | 884.5812 | 0 | 0 | 884.5812 | Heating | 780.5128 | 8.5 | 780.5128 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.1026 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 796.4416 | 0 | 159.2883 | 1.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 02:01 | 11 | 22 | 2 | 326 | 7802 | 30.92 | 960.1267 | 0 | 0 | 960.1267 | Heating | 847.1707 | 8.5 | 847.1707 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 169.4341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 864.4599 | 0 | 172.892 | 1.729% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 03:01 | 11 | 22 | 3 | 326 | 7803 | 30.02 | 1038.764 | 0 | 0 | 1038.764 | Heating | 916.5565 | 8.5 | 916.5565 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.3113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 935.2617 | 0 | 187.0523 | 1.871% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 04:01 | 11 | 22 | 4 | 326 | 7804 | 30.02 | 1109.3858 | 0 | 0 | 1109.3858 | Heating | 978.8698 | 8.5 | 978.8698 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 998.8467 | 0 | 199.7693 | 1.998% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 05:01 | 11 | 22 | 5 | 326 | 7805 | 30.02 | 1162.0868 | 0 | 0 | 1162.0868 | Heating | 1025.3707 | 8.5 | 1025.3707 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 205.0741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1046.2967 | 0 | 209.2593 | 2.093% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 06:01 | 11 | 22 | 6 | 326 | 7806 | 30.02 | 1196.8424 | 0 | 0 | 1196.8424 | Heating | 1056.0374 | 8.5 | 1056.0374 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.2075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1077.5892 | 0 | 215.5178 | 2.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 07:01 | 11 | 22 | 7 | 326 | 7807 | 28.94 | 9245.0616 | 0 | 0 | 9245.0616 | Heating | 8157.4073 | 8.5 | 8157.4073 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1631.4815 | 32.63% | 1 | 65.26% | 0% | 0% | 0% | 30.5365 | 0 | 0 | 0 | 30.5365 | 8323.885 | 0 | 1664.777 | 16.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.8111
2007-11-22 08:01 | 11 | 22 | 8 | 326 | 7808 | 28.94 | 6632.4538 | 0 | 0 | 6632.4538 | Heating | 5852.1651 | 8.5 | 5852.1651 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1170.433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5971.5971 | 0 | 1194.3194 | 11.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 09:01 | 11 | 22 | 9 | 326 | 7809 | 30.92 | 4998.5491 | 0 | 0 | 4998.5491 | Heating | 4410.4845 | 8.5 | 4410.4845 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 882.0969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4500.4944 | 0 | 900.0989 | 9.001% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 10:01 | 11 | 22 | 10 | 326 | 7810 | 30.92 | 3279.2255 | 0 | 0 | 3279.2255 | Heating | 2893.4343 | 8.5 | 2893.4343 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 578.6869 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2952.484 | 0 | 590.4968 | 5.905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 11:01 | 11 | 22 | 11 | 326 | 7811 | 30.92 | 2415.8295 | 0 | 0 | 2415.8295 | Heating | 2131.6143 | 8.5 | 2131.6143 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.3229 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2175.1166 | 0 | 435.0233 | 4.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 12:01 | 11 | 22 | 12 | 326 | 7812 | 33.08 | 1860.5489 | 0 | 0 | 1860.5489 | Heating | 1641.6608 | 8.5 | 1641.6608 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.3322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1675.1641 | 0 | 335.0328 | 3.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 13:01 | 11 | 22 | 13 | 326 | 7813 | 33.08 | 1642.1213 | 0 | 0 | 1642.1213 | Heating | 1448.9306 | 8.5 | 1448.9306 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 289.7861 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1478.5006 | 0 | 295.7001 | 2.957% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 14:01 | 11 | 22 | 14 | 326 | 7814 | 33.08 | 1304.2726 | 8.6357 | 8.6357 | 1295.6369 | Heating | 1143.209 | 8.5 | 1143.209 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 228.6418 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1166.5398 | 0 | 233.308 | 2.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 15:01 | 11 | 22 | 15 | 326 | 7815 | 33.08 | 1142.9575 | 31.2114 | 31.2114 | 1111.746 | Heating | 980.9524 | 8.5 | 980.9524 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 196.1905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1000.9718 | 0 | 200.1944 | 2.002% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 16:01 | 11 | 22 | 16 | 326 | 7816 | 30.92 | 1356.7608 | 20.1682 | 20.1682 | 1336.5925 | Heating | 1179.3463 | 8.5 | 1179.3463 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.8693 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1203.4146 | 0 | 240.6829 | 2.407% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 17:01 | 11 | 22 | 17 | 326 | 7817 | 30.92 | 1590.8713 | 14.5568 | 14.5568 | 1576.3145 | Heating | 1390.8657 | 8.5 | 1390.8657 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 278.1731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1419.2507 | 0 | 283.8501 | 2.839% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 18:01 | 11 | 22 | 18 | 326 | 7818 | 30.92 | 2208.2687 | 0.36542 | 0.36542 | 2207.9032 | Heating | 1948.1499 | 8.5 | 1948.1499 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 389.63 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1987.9081 | 0 | 397.5816 | 3.976% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 19:01 | 11 | 22 | 19 | 326 | 7819 | 30.92 | 2804.395 | 0 | 0 | 2804.395 | Heating | 2474.4662 | 8.5 | 2474.4662 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.8932 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2524.9655 | 0 | 504.9931 | 5.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 20:01 | 11 | 22 | 20 | 326 | 7820 | 30.92 | 3238.3297 | 0 | 0 | 3238.3297 | Heating | 2857.3497 | 8.5 | 2857.3497 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 571.4699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2915.663 | 0 | 583.1326 | 5.831% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 21:01 | 11 | 22 | 21 | 326 | 7821 | 30.92 | 3725.8706 | 0 | 0 | 3725.8706 | Heating | 3287.5329 | 8.5 | 3287.5329 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 657.5066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3354.6254 | 0 | 670.9251 | 6.709% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 22:01 | 11 | 22 | 22 | 326 | 7822 | 30.02 | 1034.3374 | 0 | 0 | 1034.3374 | Heating | 912.6507 | 8.5 | 912.6507 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.5301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 931.2762 | 0 | 186.2552 | 1.863% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-22 23:01 | 11 | 22 | 23 | 326 | 7823 | 30.02 | 993.3926 | 0 | 0 | 993.3926 | Heating | 876.5229 | 8.5 | 876.5229 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.3046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 894.4111 | 0 | 178.8822 | 1.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 00:01 | 11 | 23 | 0 | 327 | 7824 | 30.92 | 1068.8501 | 0 | 0 | 1068.8501 | Heating | 943.1031 | 8.5 | 943.1031 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 188.6206 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 962.3501 | 0 | 192.47 | 1.925% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 01:01 | 11 | 23 | 1 | 327 | 7825 | 30.02 | 1208.7741 | 0 | 0 | 1208.7741 | Heating | 1066.5654 | 8.5 | 1066.5654 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 213.3131 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1088.332 | 0 | 217.6664 | 2.177% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 02:01 | 11 | 23 | 2 | 327 | 7826 | 30.02 | 1337.3125 | 0 | 0 | 1337.3125 | Heating | 1179.9816 | 8.5 | 1179.9816 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.9963 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1204.0629 | 0 | 240.8126 | 2.408% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 03:01 | 11 | 23 | 3 | 327 | 7827 | 30.02 | 1472.8185 | 0 | 0 | 1472.8185 | Heating | 1299.5458 | 8.5 | 1299.5458 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 259.9092 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1326.0671 | 0 | 265.2134 | 2.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 04:01 | 11 | 23 | 4 | 327 | 7828 | 30.02 | 1565.4952 | 0 | 0 | 1565.4952 | Heating | 1381.3193 | 8.5 | 1381.3193 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 276.2639 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1409.5095 | 0 | 281.9019 | 2.819% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 05:01 | 11 | 23 | 5 | 327 | 7829 | 30.02 | 1626.8375 | 0 | 0 | 1626.8375 | Heating | 1435.4449 | 8.5 | 1435.4449 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 287.089 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1464.7396 | 0 | 292.9479 | 2.929% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 06:01 | 11 | 23 | 6 | 327 | 7830 | 30.02 | 1725.7292 | 0 | 0 | 1725.7292 | Heating | 1522.7022 | 8.5 | 1522.7022 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 304.5404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1553.7778 | 0 | 310.7556 | 3.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 07:01 | 11 | 23 | 7 | 327 | 7831 | 30.02 | 10945.9805 | 0 | 0 | 10945.9805 | Heating | 9658.218 | 8.5 | 9658.218 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1931.6436 | 38.63% | 1 | 77.27% | 0% | 0% | 0% | 45.0312 | 0 | 0 | 0 | 45.0312 | 9855.3245 | 0 | 1971.0649 | 19.71% | 1 | 39.42% | 0% | 0% | 4.7895 | 0 | 0 | 4.7895 | 49.8207
2007-11-23 08:01 | 11 | 23 | 8 | 327 | 7832 | 30.02 | 8340.6568 | 0 | 0 | 8340.6568 | Heating | 7359.403 | 8.5 | 7359.403 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1471.8806 | 30% | 1 | 58.88% | 0% | 0% | 0% | 24.0984 | 0 | 0 | 0 | 24.0984 | 7509.5949 | 0 | 1501.919 | 15.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.3729
2007-11-23 09:01 | 11 | 23 | 9 | 327 | 7833 | 32 | 6846.338 | 0 | 0 | 6846.338 | Heating | 6040.8865 | 8.5 | 6040.8865 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1208.1773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6164.1699 | 0 | 1232.834 | 12.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 10:01 | 11 | 23 | 10 | 327 | 7834 | 32 | 5057.9409 | 0 | 0 | 5057.9409 | Heating | 4462.889 | 8.5 | 4462.889 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 892.5778 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4553.9684 | 0 | 910.7937 | 9.108% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 11:01 | 11 | 23 | 11 | 327 | 7835 | 32 | 3418.0681 | 0 | 0 | 3418.0681 | Heating | 3015.9425 | 8.5 | 3015.9425 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 603.1885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3077.4923 | 0 | 615.4985 | 6.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 12:01 | 11 | 23 | 12 | 327 | 7836 | 37.04 | 2159.7833 | 2.1094 | 2.1094 | 2157.6739 | Heating | 1903.8299 | 8.5 | 1903.8299 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1942.6836 | 0 | 388.5367 | 3.885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 13:01 | 11 | 23 | 13 | 327 | 7837 | 35.96 | 1453.5315 | 35.6995 | 35.6995 | 1417.832 | Heating | 1251.0282 | 8.5 | 1251.0282 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 250.2056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1276.5594 | 0 | 255.3119 | 2.553% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 14:01 | 11 | 23 | 14 | 327 | 7838 | 35.96 | 979.3213 | 63.1698 | 63.1698 | 916.1515 | Heating | 808.369 | 8.5 | 808.369 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 161.6738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 824.8663 | 0 | 164.9733 | 1.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 15:01 | 11 | 23 | 15 | 327 | 7839 | 33.98 | 734.0972 | 47.8583 | 47.8583 | 686.2389 | Heating | 605.5049 | 8.5 | 605.5049 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 617.8622 | 0 | 123.5724 | 1.236% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 16:01 | 11 | 23 | 16 | 327 | 7840 | 33.98 | 734.6618 | 34.8657 | 34.8657 | 699.7961 | Heating | 617.4671 | 8.5 | 617.4671 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 123.4934 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 630.0685 | 0 | 126.0137 | 1.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 17:01 | 11 | 23 | 17 | 327 | 7841 | 33.98 | 972.7418 | 6.6968 | 6.6968 | 966.045 | Heating | 852.3926 | 8.5 | 852.3926 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.4785 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 869.7884 | 0 | 173.9577 | 1.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 18:01 | 11 | 23 | 18 | 327 | 7842 | 33.08 | 1284.0414 | 0 | 0 | 1284.0414 | Heating | 1132.9777 | 8.5 | 1132.9777 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 226.5955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1156.0997 | 0 | 231.2199 | 2.312% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 19:01 | 11 | 23 | 19 | 327 | 7843 | 32 | 1924.5456 | 0 | 0 | 1924.5456 | Heating | 1698.1285 | 8.5 | 1698.1285 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 339.6257 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1732.7842 | 0 | 346.5568 | 3.466% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 20:01 | 11 | 23 | 20 | 327 | 7844 | 32 | 2336.1427 | 0 | 0 | 2336.1427 | Heating | 2061.3023 | 8.5 | 2061.3023 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.2605 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2103.3697 | 0 | 420.6739 | 4.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 21:01 | 11 | 23 | 21 | 327 | 7845 | 32 | 2787.381 | 0 | 0 | 2787.381 | Heating | 2459.4538 | 8.5 | 2459.4538 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 491.8908 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2509.6468 | 0 | 501.9294 | 5.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 22:01 | 11 | 23 | 22 | 327 | 7846 | 32 | 3408.8843 | 0 | 0 | 3408.8843 | Heating | 3007.8391 | 8.5 | 3007.8391 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 601.5678 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3069.2235 | 0 | 613.8447 | 6.138% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-23 23:01 | 11 | 23 | 23 | 327 | 7847 | 32 | 686.3708 | 0 | 0 | 686.3708 | Heating | 605.6213 | 8.5 | 605.6213 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.1243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 617.9809 | 0 | 123.5962 | 1.236% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 00:01 | 11 | 24 | 0 | 328 | 7848 | 32 | 772.3332 | 0 | 0 | 772.3332 | Heating | 681.4705 | 8.5 | 681.4705 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 136.2941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 695.3781 | 0 | 139.0756 | 1.391% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 01:01 | 11 | 24 | 1 | 328 | 7849 | 30.92 | 819.1824 | 0 | 0 | 819.1824 | Heating | 722.808 | 8.5 | 722.808 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 144.5616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 737.5592 | 0 | 147.5118 | 1.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 02:01 | 11 | 24 | 2 | 328 | 7850 | 30.92 | 824.0818 | 0 | 0 | 824.0818 | Heating | 727.131 | 8.5 | 727.131 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.4262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 741.9704 | 0 | 148.3941 | 1.484% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 03:01 | 11 | 24 | 3 | 328 | 7851 | 30.02 | 825.0386 | 0 | 0 | 825.0386 | Heating | 727.9752 | 8.5 | 727.9752 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 145.595 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 742.8319 | 0 | 148.5664 | 1.486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 04:01 | 11 | 24 | 4 | 328 | 7852 | 28.94 | 806.4979 | 0 | 0 | 806.4979 | Heating | 711.6158 | 8.5 | 711.6158 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 142.3232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 726.1386 | 0 | 145.2277 | 1.452% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 05:01 | 11 | 24 | 5 | 328 | 7853 | 28.94 | 739.1744 | 0 | 0 | 739.1744 | Heating | 652.2127 | 8.5 | 652.2127 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 130.4425 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 665.5231 | 0 | 133.1046 | 1.331% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 06:01 | 11 | 24 | 6 | 328 | 7854 | 28.04 | 680.6118 | 0 | 0 | 680.6118 | Heating | 600.5399 | 8.5 | 600.5399 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.108 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 612.7958 | 0 | 122.5592 | 1.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 07:01 | 11 | 24 | 7 | 328 | 7855 | 28.4 | 659.2396 | 0 | 0 | 659.2396 | Heating | 581.682 | 8.5 | 581.682 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.3364 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 593.553 | 0 | 118.7106 | 1.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 08:01 | 11 | 24 | 8 | 328 | 7856 | 28.04 | 626.6964 | 0 | 0 | 626.6964 | Heating | 552.9674 | 8.5 | 552.9674 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 110.5935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 564.2524 | 0 | 112.8505 | 1.129% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 09:01 | 11 | 24 | 9 | 328 | 7857 | 28.94 | 5388.649 | 0 | 0 | 5388.649 | Heating | 4754.6903 | 8.5 | 4754.6903 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 950.9381 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4851.7248 | 0 | 970.345 | 9.703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 10:01 | 11 | 24 | 10 | 328 | 7858 | 32 | 3846.2324 | 0 | 0 | 3846.2324 | Heating | 3393.7344 | 8.5 | 3393.7344 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 678.7469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3462.9943 | 0 | 692.5989 | 6.926% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 11:01 | 11 | 24 | 11 | 328 | 7859 | 32 | 3195.8806 | 0 | 0 | 3195.8806 | Heating | 2819.8946 | 8.5 | 2819.8946 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 563.9789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2877.4435 | 0 | 575.4887 | 5.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 12:01 | 11 | 24 | 12 | 328 | 7860 | 35.06 | 2820.7233 | 0 | 0 | 2820.7233 | Heating | 2488.8735 | 8.5 | 2488.8735 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 497.7747 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2539.6669 | 0 | 507.9334 | 5.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 13:01 | 11 | 24 | 13 | 328 | 7861 | 35.96 | 2186.06 | 0 | 0 | 2186.06 | Heating | 1928.8765 | 8.5 | 1928.8765 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.7753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1968.2413 | 0 | 393.6483 | 3.936% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 14:01 | 11 | 24 | 14 | 328 | 7862 | 35.96 | 1833.1189 | 0 | 0 | 1833.1189 | Heating | 1617.4578 | 8.5 | 1617.4578 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.4916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1650.4672 | 0 | 330.0934 | 3.301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 15:01 | 11 | 24 | 15 | 328 | 7863 | 37.04 | 1655.437 | 0 | 0 | 1655.437 | Heating | 1460.6797 | 8.5 | 1460.6797 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.1359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1490.4895 | 0 | 298.0979 | 2.981% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 16:01 | 11 | 24 | 16 | 328 | 7864 | 35.06 | 1654.9519 | 0 | 0 | 1654.9519 | Heating | 1460.2516 | 8.5 | 1460.2516 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.0503 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1490.0527 | 0 | 298.0105 | 2.98% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 17:01 | 11 | 24 | 17 | 328 | 7865 | 35.06 | 1729.4478 | 0 | 0 | 1729.4478 | Heating | 1525.9834 | 8.5 | 1525.9834 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 305.1967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1557.1259 | 0 | 311.4252 | 3.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 18:01 | 11 | 24 | 18 | 328 | 7866 | 30.02 | 2728.7312 | 0 | 0 | 2728.7312 | Heating | 2407.704 | 8.5 | 2407.704 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 481.5408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2456.8408 | 0 | 491.3682 | 4.914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 19:01 | 11 | 24 | 19 | 328 | 7867 | 30.02 | 2968.4922 | 0 | 0 | 2968.4922 | Heating | 2619.2578 | 8.5 | 2619.2578 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.8516 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2672.712 | 0 | 534.5424 | 5.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 20:01 | 11 | 24 | 20 | 328 | 7868 | 30.02 | 436.3177 | 0 | 0 | 436.3177 | Heating | 384.9862 | 8.5 | 384.9862 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.9972 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 392.8431 | 0 | 78.5686 | 0.7857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 21:01 | 11 | 24 | 21 | 328 | 7869 | 28.04 | 436.2774 | 0 | 0 | 436.2774 | Heating | 384.9506 | 8.5 | 384.9506 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 76.9901 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 392.8068 | 0 | 78.5614 | 0.7856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 22:01 | 11 | 24 | 22 | 328 | 7870 | 28.04 | 406.3668 | 0 | 0 | 406.3668 | Heating | 358.559 | 8.5 | 358.559 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 71.7118 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 365.8765 | 0 | 73.1753 | 0.7318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-24 23:01 | 11 | 24 | 23 | 328 | 7871 | 28.04 | 385.3147 | 0 | 0 | 385.3147 | Heating | 339.9836 | 8.5 | 339.9836 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 67.9967 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 346.922 | 0 | 69.3844 | 0.6938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 00:01 | 11 | 25 | 0 | 329 | 7872 | 30.92 | 365.6043 | 0 | 0 | 365.6043 | Heating | 322.5921 | 8.5 | 322.5921 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 64.5184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 329.1756 | 0 | 65.8351 | 0.6584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 01:01 | 11 | 25 | 1 | 329 | 7873 | 30.02 | 338.2653 | 0 | 0 | 338.2653 | Heating | 298.4694 | 8.5 | 298.4694 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 59.6939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 304.5606 | 0 | 60.9121 | 0.6091% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 02:01 | 11 | 25 | 2 | 329 | 7874 | 30.02 | 310.5861 | 0 | 0 | 310.5861 | Heating | 274.0466 | 8.5 | 274.0466 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 54.8093 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 279.6394 | 0 | 55.9279 | 0.5593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 03:01 | 11 | 25 | 3 | 329 | 7875 | 30.92 | 285.7481 | 0 | 0 | 285.7481 | Heating | 252.1307 | 8.5 | 252.1307 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 50.4261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 257.2762 | 0 | 51.4552 | 0.5146% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 04:01 | 11 | 25 | 4 | 329 | 7876 | 30.92 | 258.1538 | 0 | 0 | 258.1538 | Heating | 227.7827 | 8.5 | 227.7827 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 45.5565 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 232.4314 | 0 | 46.4863 | 0.4649% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 05:01 | 11 | 25 | 5 | 329 | 7877 | 30.92 | 227.9798 | 0 | 0 | 227.9798 | Heating | 201.1587 | 8.5 | 201.1587 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 40.2317 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 205.2639 | 0 | 41.0528 | 0.4105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 06:01 | 11 | 25 | 6 | 329 | 7878 | 32 | 201.4649 | 0 | 0 | 201.4649 | Heating | 177.7632 | 8.5 | 177.7632 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 35.5526 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 181.391 | 0 | 36.2782 | 0.3628% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 07:01 | 11 | 25 | 7 | 329 | 7879 | 32 | 2616.8824 | 0 | 0 | 2616.8824 | Heating | 2309.0139 | 8.5 | 2309.0139 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 461.8028 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2356.1366 | 0 | 471.2273 | 4.712% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 08:01 | 11 | 25 | 8 | 329 | 7880 | 32 | 1798.5927 | 0 | 0 | 1798.5927 | Heating | 1586.9936 | 8.5 | 1586.9936 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.3987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1619.3812 | 0 | 323.8762 | 3.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 09:01 | 11 | 25 | 9 | 329 | 7881 | 33.98 | 785.6495 | 0 | 0 | 785.6495 | Heating | 693.2202 | 8.5 | 693.2202 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 707.3675 | 0 | 141.4735 | 1.415% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 10:01 | 11 | 25 | 10 | 329 | 7882 | 35.06 | 118.0073 | 0 | 0 | 118.0073 | Heating | 104.1241 | 8.5 | 104.1241 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 20.8248 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 106.2491 | 0 | 21.2498 | 0.2125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 11:01 | 11 | 25 | 11 | 329 | 7883 | 35.06 | 447.1423 | 0 | 0 | 447.1423 | Heating | 394.5373 | 8.5 | 394.5373 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 78.9075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 402.5891 | 0 | 80.5178 | 0.8052% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 12:01 | 11 | 25 | 12 | 329 | 7884 | 39.02 | 531.558 | 0 | 0 | 531.558 | Heating | 469.0218 | 8.5 | 469.0218 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 93.8044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 478.5937 | 0 | 95.7187 | 0.9572% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 13:01 | 11 | 25 | 13 | 329 | 7885 | 37.94 | 787.0049 | 0 | 0 | 787.0049 | Heating | 694.4161 | 8.5 | 694.4161 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 138.8832 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 708.5878 | 0 | 141.7176 | 1.417% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 14:01 | 11 | 25 | 14 | 329 | 7886 | 35.96 | 1425.9835 | 0 | 0 | 1425.9835 | Heating | 1258.2207 | 8.5 | 1258.2207 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 251.6441 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1283.8987 | 0 | 256.7797 | 2.568% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 15:01 | 11 | 25 | 15 | 329 | 7887 | 35.06 | 1757.0915 | 0 | 0 | 1757.0915 | Heating | 1550.3748 | 8.5 | 1550.3748 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 310.075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1582.0151 | 0 | 316.403 | 3.164% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 16:01 | 11 | 25 | 16 | 329 | 7888 | 35.06 | 2000.5087 | 0 | 0 | 2000.5087 | Heating | 1765.1548 | 8.5 | 1765.1548 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 353.031 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1801.1783 | 0 | 360.2357 | 3.602% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 17:01 | 11 | 25 | 17 | 329 | 7889 | 35.06 | 2490.8118 | 0 | 0 | 2490.8118 | Heating | 2197.7751 | 8.5 | 2197.7751 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 439.555 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2242.6277 | 0 | 448.5255 | 4.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 18:01 | 11 | 25 | 18 | 329 | 7890 | 33.98 | 2948.9939 | 0 | 0 | 2948.9939 | Heating | 2602.0535 | 8.5 | 2602.0535 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 520.4107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2655.1566 | 0 | 531.0313 | 5.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 19:01 | 11 | 25 | 19 | 329 | 7891 | 33.98 | 3220.0782 | 0 | 0 | 3220.0782 | Heating | 2841.2455 | 8.5 | 2841.2455 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 568.2491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2899.2301 | 0 | 579.846 | 5.798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 20:01 | 11 | 25 | 20 | 329 | 7892 | 33.98 | 3535.3363 | 0 | 0 | 3535.3363 | Heating | 3119.4144 | 8.5 | 3119.4144 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 623.8829 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3183.0759 | 0 | 636.6152 | 6.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 21:01 | 11 | 25 | 21 | 329 | 7893 | 33.98 | 3827.1403 | 0 | 0 | 3827.1403 | Heating | 3376.8885 | 8.5 | 3376.8885 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 675.3777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3445.8046 | 0 | 689.1609 | 6.892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 22:01 | 11 | 25 | 22 | 329 | 7894 | 35.06 | 1130.9333 | 0 | 0 | 1130.9333 | Heating | 997.8824 | 8.5 | 997.8824 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 199.5765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1018.2473 | 0 | 203.6495 | 2.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-25 23:01 | 11 | 25 | 23 | 329 | 7895 | 35.06 | 1042.9284 | 0 | 0 | 1042.9284 | Heating | 920.231 | 8.5 | 920.231 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.0462 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 939.0112 | 0 | 187.8022 | 1.878% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 00:01 | 11 | 26 | 0 | 330 | 7896 | 35.06 | 1325.4197 | 0 | 0 | 1325.4197 | Heating | 1169.488 | 8.5 | 1169.488 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.8976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1193.3551 | 0 | 238.671 | 2.387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 01:01 | 11 | 26 | 1 | 330 | 7897 | 35.06 | 1470.5794 | 0 | 0 | 1470.5794 | Heating | 1297.5701 | 8.5 | 1297.5701 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 259.514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1324.0511 | 0 | 264.8102 | 2.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 02:01 | 11 | 26 | 2 | 330 | 7898 | 35.06 | 1583.2123 | 0 | 0 | 1583.2123 | Heating | 1396.952 | 8.5 | 1396.952 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.3904 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1425.4612 | 0 | 285.0922 | 2.851% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 03:01 | 11 | 26 | 3 | 330 | 7899 | 35.96 | 1709.6442 | 0 | 0 | 1709.6442 | Heating | 1508.5096 | 8.5 | 1508.5096 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.7019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1539.2955 | 0 | 307.8591 | 3.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 04:01 | 11 | 26 | 4 | 330 | 7900 | 37.04 | 1783.9297 | 0 | 0 | 1783.9297 | Heating | 1574.0557 | 8.5 | 1574.0557 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 314.8111 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1606.1792 | 0 | 321.2358 | 3.212% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 05:01 | 11 | 26 | 5 | 330 | 7901 | 37.04 | 1839.7294 | 0 | 0 | 1839.7294 | Heating | 1623.2906 | 8.5 | 1623.2906 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.6581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1656.419 | 0 | 331.2838 | 3.313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 06:01 | 11 | 26 | 6 | 330 | 7902 | 37.04 | 1929.6979 | 0 | 0 | 1929.6979 | Heating | 1702.6746 | 8.5 | 1702.6746 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.5349 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1737.4231 | 0 | 347.4846 | 3.475% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 07:01 | 11 | 26 | 7 | 330 | 7903 | 37.04 | 11556.054 | 0 | 0 | 11556.054 | Heating | 10196.5183 | 8.5 | 10196.5183 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2039.3037 | 40.79% | 1 | 81.57% | 0% | 0% | 0% | 51.014 | 0 | 0 | 0 | 51.014 | 10404.6105 | 0 | 2080.9221 | 20.81% | 1 | 41.62% | 0% | 0% | 5.4259 | 0 | 0 | 5.4259 | 56.4399
2007-11-26 08:01 | 11 | 26 | 8 | 330 | 7904 | 37.04 | 8823.4793 | 0 | 0 | 8823.4793 | Heating | 7785.4229 | 8.5 | 7785.4229 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1557.0846 | 31.14% | 1 | 62.28% | 0% | 0% | 0% | 27.4283 | 0 | 0 | 0 | 27.4283 | 7944.3091 | 0 | 1588.8618 | 15.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.7029
2007-11-26 09:01 | 11 | 26 | 9 | 330 | 7905 | 39.02 | 7025.9707 | 0 | 0 | 7025.9707 | Heating | 6199.3859 | 8.5 | 6199.3859 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1239.8772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6325.904 | 0 | 1265.1808 | 12.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 10:01 | 11 | 26 | 10 | 330 | 7906 | 39.02 | 5382.8651 | 0 | 0 | 5382.8651 | Heating | 4749.5868 | 8.5 | 4749.5868 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 949.9174 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4846.5172 | 0 | 969.3034 | 9.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 11:01 | 11 | 26 | 11 | 330 | 7907 | 39.92 | 4480.481 | 0 | 0 | 4480.481 | Heating | 3953.3656 | 8.5 | 3953.3656 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 790.6731 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4034.0465 | 0 | 806.8093 | 8.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 12:01 | 11 | 26 | 12 | 330 | 7908 | 42.08 | 3861.6578 | 0 | 0 | 3861.6578 | Heating | 3407.3452 | 8.5 | 3407.3452 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 681.469 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3476.8828 | 0 | 695.3766 | 6.954% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 13:01 | 11 | 26 | 13 | 330 | 7909 | 42.08 | 3195.9886 | 0 | 0 | 3195.9886 | Heating | 2819.99 | 8.5 | 2819.99 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 563.998 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2877.5408 | 0 | 575.5082 | 5.755% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 14:01 | 11 | 26 | 14 | 330 | 7910 | 42.98 | 2816.2407 | 13.7649 | 13.7649 | 2802.4758 | Heating | 2472.7728 | 8.5 | 2472.7728 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 494.5546 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2523.2376 | 0 | 504.6475 | 5.046% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 15:01 | 11 | 26 | 15 | 330 | 7911 | 46.04 | 2711.6641 | 31.8117 | 31.8117 | 2679.8525 | Heating | 2364.5757 | 8.5 | 2364.5757 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 472.9151 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2412.8323 | 0 | 482.5665 | 4.826% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 16:01 | 11 | 26 | 16 | 330 | 7912 | 44.96 | 2775.1332 | 23.5667 | 23.5667 | 2751.5666 | Heating | 2427.8528 | 8.5 | 2427.8528 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 485.5706 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2477.4009 | 0 | 495.4802 | 4.955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 17:01 | 11 | 26 | 17 | 330 | 7913 | 44.96 | 3123.0219 | 4.1758 | 4.1758 | 3118.8461 | Heating | 2751.9231 | 8.5 | 2751.9231 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.3846 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2808.0848 | 0 | 561.617 | 5.616% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 18:01 | 11 | 26 | 18 | 330 | 7914 | 37.94 | 3470.6767 | 0 | 0 | 3470.6767 | Heating | 3062.3618 | 8.5 | 3062.3618 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 612.4724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3124.859 | 0 | 624.9718 | 6.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 19:01 | 11 | 26 | 19 | 330 | 7915 | 35.96 | 3634.227 | 0 | 0 | 3634.227 | Heating | 3206.6709 | 8.5 | 3206.6709 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 641.3342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3272.1131 | 0 | 654.4226 | 6.544% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 20:01 | 11 | 26 | 20 | 330 | 7916 | 37.04 | 3722.1888 | 0 | 0 | 3722.1888 | Heating | 3284.2842 | 8.5 | 3284.2842 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 656.8568 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3351.3104 | 0 | 670.2621 | 6.703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 21:01 | 11 | 26 | 21 | 330 | 7917 | 37.04 | 3961.3464 | 0 | 0 | 3961.3464 | Heating | 3495.3057 | 8.5 | 3495.3057 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 699.0611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3566.6384 | 0 | 713.3277 | 7.133% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 22:01 | 11 | 26 | 22 | 330 | 7918 | 37.94 | 1110.2681 | 0 | 0 | 1110.2681 | Heating | 979.6483 | 8.5 | 979.6483 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.9297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 999.6412 | 0 | 199.9282 | 1.999% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-26 23:01 | 11 | 26 | 23 | 330 | 7919 | 39.02 | 977.4927 | 0 | 0 | 977.4927 | Heating | 862.4936 | 8.5 | 862.4936 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.4987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 880.0955 | 0 | 176.0191 | 1.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 00:01 | 11 | 27 | 0 | 331 | 7920 | 37.94 | 1020.1305 | 0 | 0 | 1020.1305 | Heating | 900.1152 | 8.5 | 900.1152 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 180.023 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 918.4849 | 0 | 183.697 | 1.837% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 01:01 | 11 | 27 | 1 | 331 | 7921 | 37.94 | 1176.9408 | 0 | 0 | 1176.9408 | Heating | 1038.4772 | 8.5 | 1038.4772 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 207.6954 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1059.6706 | 0 | 211.9341 | 2.119% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 02:01 | 11 | 27 | 2 | 331 | 7922 | 37.94 | 1309.3393 | 0 | 0 | 1309.3393 | Heating | 1155.2994 | 8.5 | 1155.2994 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.0599 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1178.877 | 0 | 235.7754 | 2.358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 03:01 | 11 | 27 | 3 | 331 | 7923 | 37.04 | 1387.8132 | 0 | 0 | 1387.8132 | Heating | 1224.5411 | 8.5 | 1224.5411 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 244.9082 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1249.5317 | 0 | 249.9063 | 2.499% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 04:01 | 11 | 27 | 4 | 331 | 7924 | 37.4 | 1457.3067 | 0 | 0 | 1457.3067 | Heating | 1285.8588 | 8.5 | 1285.8588 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 257.1718 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1312.1008 | 0 | 262.4202 | 2.624% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 05:01 | 11 | 27 | 5 | 331 | 7925 | 37.94 | 1538.3155 | 0 | 0 | 1538.3155 | Heating | 1357.3372 | 8.5 | 1357.3372 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 271.4674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1385.038 | 0 | 277.0076 | 2.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 06:01 | 11 | 27 | 6 | 331 | 7926 | 35.96 | 1548.8136 | 0 | 0 | 1548.8136 | Heating | 1366.6002 | 8.5 | 1366.6002 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 273.32 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1394.49 | 0 | 278.898 | 2.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 07:01 | 11 | 27 | 7 | 331 | 7927 | 37.04 | 10394.6046 | 0 | 0 | 10394.6046 | Heating | 9171.7099 | 8.5 | 9171.7099 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1834.342 | 36.69% | 1 | 73.37% | 0% | 0% | 0% | 39.984 | 0 | 0 | 0 | 39.984 | 9358.8877 | 0 | 1871.7775 | 18.72% | 1 | 37.44% | 0% | 0% | 4.2527 | 0 | 0 | 4.2527 | 44.2367
2007-11-27 08:01 | 11 | 27 | 8 | 331 | 7928 | 37.04 | 7745.4741 | 0 | 0 | 7745.4741 | Heating | 6834.2419 | 8.5 | 6834.2419 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1366.8484 | 30% | 1 | 54.67% | 0% | 0% | 0% | 20.3253 | 0 | 0 | 0 | 20.3253 | 6973.7162 | 0 | 1394.7432 | 13.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.5999
2007-11-27 09:01 | 11 | 27 | 9 | 331 | 7929 | 41 | 6292.4558 | 0 | 0 | 6292.4558 | Heating | 5552.1669 | 8.5 | 5552.1669 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1110.4334 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5665.4764 | 0 | 1133.0953 | 11.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 10:01 | 11 | 27 | 10 | 331 | 7930 | 42.08 | 5091.3114 | 0 | 0 | 5091.3114 | Heating | 4492.3336 | 8.5 | 4492.3336 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 898.4667 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4584.0139 | 0 | 916.8028 | 9.168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 11:01 | 11 | 27 | 11 | 331 | 7931 | 42.08 | 4274.6261 | 0 | 0 | 4274.6261 | Heating | 3771.7289 | 8.5 | 3771.7289 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 754.3458 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3848.703 | 0 | 769.7406 | 7.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 12:01 | 11 | 27 | 12 | 331 | 7932 | 42.08 | 3373.7017 | 0 | 0 | 3373.7017 | Heating | 2976.7956 | 8.5 | 2976.7956 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 595.3591 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3037.5466 | 0 | 607.5093 | 6.075% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 13:01 | 11 | 27 | 13 | 331 | 7933 | 42.08 | 2582.1524 | 0 | 0 | 2582.1524 | Heating | 2278.3698 | 8.5 | 2278.3698 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 455.674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2324.8671 | 0 | 464.9734 | 4.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 14:01 | 11 | 27 | 14 | 331 | 7934 | 42.08 | 2018.264 | 0 | 0 | 2018.264 | Heating | 1780.8211 | 8.5 | 1780.8211 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 356.1642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1817.1644 | 0 | 363.4329 | 3.634% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 15:01 | 11 | 27 | 15 | 331 | 7935 | 42.8 | 1816.1395 | 0 | 0 | 1816.1395 | Heating | 1602.4761 | 8.5 | 1602.4761 | 0 | 3.9261 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.4952 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1635.1797 | 0 | 327.0359 | 3.27% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 16:01 | 11 | 27 | 16 | 331 | 7936 | 39.92 | 1591.2495 | 0 | 0 | 1591.2495 | Heating | 1404.0437 | 8.5 | 1404.0437 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 280.8087 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1432.6976 | 0 | 286.5395 | 2.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 17:01 | 11 | 27 | 17 | 331 | 7937 | 39.92 | 1632.7884 | 0 | 0 | 1632.7884 | Heating | 1440.6956 | 8.5 | 1440.6956 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 288.1391 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1470.0976 | 0 | 294.0195 | 2.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 18:01 | 11 | 27 | 18 | 331 | 7938 | 39.02 | 1861.0922 | 0 | 0 | 1861.0922 | Heating | 1642.1402 | 8.5 | 1642.1402 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 328.428 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1675.6532 | 0 | 335.1306 | 3.351% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 19:01 | 11 | 27 | 19 | 331 | 7939 | 39.92 | 2117.6952 | 0 | 0 | 2117.6952 | Heating | 1868.5546 | 8.5 | 1868.5546 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.7109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1906.6883 | 0 | 381.3377 | 3.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 20:01 | 11 | 27 | 20 | 331 | 7940 | 39.92 | 2374.2283 | 0 | 0 | 2374.2283 | Heating | 2094.9074 | 8.5 | 2094.9074 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 418.9815 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2137.6606 | 0 | 427.5321 | 4.275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 21:01 | 11 | 27 | 21 | 331 | 7941 | 37.94 | 2580.2416 | 0 | 0 | 2580.2416 | Heating | 2276.6838 | 8.5 | 2276.6838 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 455.3368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2323.1467 | 0 | 464.6293 | 4.646% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 22:01 | 11 | 27 | 22 | 331 | 7942 | 37.94 | 734.2224 | 0 | 0 | 734.2224 | Heating | 647.8433 | 8.5 | 647.8433 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 129.5687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 661.0646 | 0 | 132.2129 | 1.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-27 23:01 | 11 | 27 | 23 | 331 | 7943 | 37.94 | 681.0749 | 0 | 0 | 681.0749 | Heating | 600.9485 | 8.5 | 600.9485 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.1897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 613.2127 | 0 | 122.6425 | 1.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 00:01 | 11 | 28 | 0 | 332 | 7944 | 37.94 | 682.1954 | 0 | 0 | 682.1954 | Heating | 601.9371 | 8.5 | 601.9371 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 120.3874 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 614.2215 | 0 | 122.8443 | 1.228% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 01:01 | 11 | 28 | 1 | 332 | 7945 | 37.94 | 671.6837 | 0 | 0 | 671.6837 | Heating | 592.6621 | 8.5 | 592.6621 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.5324 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 604.7572 | 0 | 120.9514 | 1.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 02:01 | 11 | 28 | 2 | 332 | 7946 | 37.94 | 669.5983 | 0 | 0 | 669.5983 | Heating | 590.822 | 8.5 | 590.822 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.1644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 602.8796 | 0 | 120.5759 | 1.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 03:01 | 11 | 28 | 3 | 332 | 7947 | 33.98 | 661.7692 | 0 | 0 | 661.7692 | Heating | 583.914 | 8.5 | 583.914 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 116.7828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 595.8306 | 0 | 119.1661 | 1.192% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 04:01 | 11 | 28 | 4 | 332 | 7948 | 35.06 | 655.5403 | 0 | 0 | 655.5403 | Heating | 578.4179 | 8.5 | 578.4179 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.6836 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 590.2223 | 0 | 118.0445 | 1.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 05:01 | 11 | 28 | 5 | 332 | 7949 | 35.06 | 652.7311 | 0 | 0 | 652.7311 | Heating | 575.9392 | 8.5 | 575.9392 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.1878 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 587.693 | 0 | 117.5386 | 1.175% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 06:01 | 11 | 28 | 6 | 332 | 7950 | 35.06 | 641.5285 | 0 | 0 | 641.5285 | Heating | 566.0546 | 8.5 | 566.0546 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 113.2109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 577.6067 | 0 | 115.5213 | 1.155% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 07:01 | 11 | 28 | 7 | 332 | 7951 | 33.98 | 6154.5839 | 18.993 | 18.993 | 6135.5908 | Heating | 5413.7566 | 8.5 | 5413.7566 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1082.7513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5524.2414 | 0 | 1104.8483 | 11.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 08:01 | 11 | 28 | 8 | 332 | 7952 | 33.98 | 4128.4235 | 0 | 0 | 4128.4235 | Heating | 3642.7266 | 8.5 | 3642.7266 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 728.5453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3717.0679 | 0 | 743.4136 | 7.434% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 09:01 | 11 | 28 | 9 | 332 | 7953 | 37.94 | 3004.8291 | 0 | 0 | 3004.8291 | Heating | 2651.3198 | 8.5 | 2651.3198 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 530.264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2705.4283 | 0 | 541.0857 | 5.411% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 10:01 | 11 | 28 | 10 | 332 | 7954 | 39.02 | 1880.9145 | 0 | 0 | 1880.9145 | Heating | 1659.6305 | 8.5 | 1659.6305 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 331.9261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1693.5005 | 0 | 338.7001 | 3.387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 11:01 | 11 | 28 | 11 | 332 | 7955 | 39.02 | 1493.7132 | 0 | 0 | 1493.7132 | Heating | 1317.9823 | 8.5 | 1317.9823 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 263.5965 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1344.8798 | 0 | 268.976 | 2.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 12:01 | 11 | 28 | 12 | 332 | 7956 | 41 | 1309.7621 | 0 | 0 | 1309.7621 | Heating | 1155.6724 | 8.5 | 1155.6724 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 231.1345 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1179.2576 | 0 | 235.8515 | 2.359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 13:01 | 11 | 28 | 13 | 332 | 7957 | 41 | 1172.8993 | 0 | 0 | 1172.8993 | Heating | 1034.9112 | 8.5 | 1034.9112 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.9822 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1056.0318 | 0 | 211.2064 | 2.112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 14:01 | 11 | 28 | 14 | 332 | 7958 | 41 | 1051.6964 | 0 | 0 | 1051.6964 | Heating | 927.9674 | 8.5 | 927.9674 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 185.5935 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 946.9055 | 0 | 189.3811 | 1.894% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 15:01 | 11 | 28 | 15 | 332 | 7959 | 41 | 988.4236 | 0 | 0 | 988.4236 | Heating | 872.1385 | 8.5 | 872.1385 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.4277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 889.9372 | 0 | 177.9874 | 1.78% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 16:01 | 11 | 28 | 16 | 332 | 7960 | 39.92 | 879.6191 | 0 | 0 | 879.6191 | Heating | 776.1345 | 8.5 | 776.1345 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.2269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 791.974 | 0 | 158.3948 | 1.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 17:01 | 11 | 28 | 17 | 332 | 7961 | 39.92 | 986.194 | 0 | 0 | 986.194 | Heating | 870.1712 | 8.5 | 870.1712 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.0342 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 887.9298 | 0 | 177.586 | 1.776% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 18:01 | 11 | 28 | 18 | 332 | 7962 | 35.96 | 1391.7286 | 0 | 0 | 1391.7286 | Heating | 1227.9958 | 8.5 | 1227.9958 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.5992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1253.057 | 0 | 250.6114 | 2.506% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 19:01 | 11 | 28 | 19 | 332 | 7963 | 33.98 | 1750.7855 | 0 | 0 | 1750.7855 | Heating | 1544.8107 | 8.5 | 1544.8107 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 308.9621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1576.3375 | 0 | 315.2675 | 3.153% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 20:01 | 11 | 28 | 20 | 332 | 7964 | 33.98 | 2177.0165 | 0 | 0 | 2177.0165 | Heating | 1920.8969 | 8.5 | 1920.8969 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.1794 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1960.0988 | 0 | 392.0198 | 3.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 21:01 | 11 | 28 | 21 | 332 | 7965 | 35.06 | 2432.7763 | 0 | 0 | 2432.7763 | Heating | 2146.5674 | 8.5 | 2146.5674 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 429.3135 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2190.3749 | 0 | 438.075 | 4.381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 22:01 | 11 | 28 | 22 | 332 | 7966 | 33.08 | 710.1379 | 0 | 0 | 710.1379 | Heating | 626.5922 | 8.5 | 626.5922 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 125.3184 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 639.3798 | 0 | 127.876 | 1.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-28 23:01 | 11 | 28 | 23 | 332 | 7967 | 33.08 | 670.1021 | 0 | 0 | 670.1021 | Heating | 591.2666 | 8.5 | 591.2666 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 118.2533 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 603.3332 | 0 | 120.6666 | 1.207% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 00:01 | 11 | 29 | 0 | 333 | 7968 | 30.02 | 706.0433 | 0 | 0 | 706.0433 | Heating | 622.9794 | 8.5 | 622.9794 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 124.5959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 635.6933 | 0 | 127.1387 | 1.271% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 01:01 | 11 | 29 | 1 | 333 | 7969 | 26.06 | 753.2071 | 0 | 0 | 753.2071 | Heating | 664.5945 | 8.5 | 664.5945 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 132.9189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 678.1576 | 0 | 135.6315 | 1.356% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 02:01 | 11 | 29 | 2 | 333 | 7970 | 26.06 | 767.4986 | 0 | 0 | 767.4986 | Heating | 677.2047 | 8.5 | 677.2047 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 135.4409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 691.0252 | 0 | 138.205 | 1.382% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 03:01 | 11 | 29 | 3 | 333 | 7971 | 24.98 | 779.2957 | 0 | 0 | 779.2957 | Heating | 687.6138 | 8.5 | 687.6138 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 137.5228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 701.6468 | 0 | 140.3294 | 1.403% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 04:01 | 11 | 29 | 4 | 333 | 7972 | 24.98 | 861.327 | 0 | 0 | 861.327 | Heating | 759.9944 | 8.5 | 759.9944 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 151.9989 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 775.5045 | 0 | 155.1009 | 1.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 05:01 | 11 | 29 | 5 | 333 | 7973 | 24.98 | 975.0505 | 0 | 0 | 975.0505 | Heating | 860.3387 | 8.5 | 860.3387 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.0677 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 877.8966 | 0 | 175.5793 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 06:01 | 11 | 29 | 6 | 333 | 7974 | 23 | 1041.9062 | 0 | 0 | 1041.9062 | Heating | 919.329 | 8.5 | 919.329 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.8658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 938.0908 | 0 | 187.6182 | 1.876% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 07:01 | 11 | 29 | 7 | 333 | 7975 | 23 | 8437.2902 | 0 | 0 | 8437.2902 | Heating | 7444.6678 | 8.5 | 7444.6678 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1488.9336 | 30% | 1 | 59.56% | 0% | 0% | 0% | 24.7454 | 0 | 0 | 0 | 24.7454 | 7596.5998 | 0 | 1519.32 | 15.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.0199
2007-11-29 08:01 | 11 | 29 | 8 | 333 | 7976 | 23 | 6396.1172 | 0 | 0 | 6396.1172 | Heating | 5643.6328 | 8.5 | 5643.6328 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1128.7266 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5758.809 | 0 | 1151.7618 | 11.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 09:01 | 11 | 29 | 9 | 333 | 7977 | 30.92 | 5056.1266 | 0 | 0 | 5056.1266 | Heating | 4461.2882 | 8.5 | 4461.2882 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 892.2576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4552.3349 | 0 | 910.467 | 9.105% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 10:01 | 11 | 29 | 10 | 333 | 7978 | 35.96 | 3711.8962 | 0 | 0 | 3711.8962 | Heating | 3275.2026 | 8.5 | 3275.2026 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 655.0405 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3342.0434 | 0 | 668.4087 | 6.684% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 11:01 | 11 | 29 | 11 | 333 | 7979 | 35.96 | 3117.8664 | 0 | 0 | 3117.8664 | Heating | 2751.0586 | 8.5 | 2751.0586 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 550.2117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2807.2026 | 0 | 561.4405 | 5.614% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 12:01 | 11 | 29 | 12 | 333 | 7980 | 41 | 2880.168 | 0 | 0 | 2880.168 | Heating | 2541.3247 | 8.5 | 2541.3247 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 508.2649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2593.1885 | 0 | 518.6377 | 5.186% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 13:01 | 11 | 29 | 13 | 333 | 7981 | 42.08 | 2670.3892 | 0 | 0 | 2670.3892 | Heating | 2356.2258 | 8.5 | 2356.2258 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.2452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2404.312 | 0 | 480.8624 | 4.809% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 14:01 | 11 | 29 | 14 | 333 | 7982 | 42.08 | 2403.2606 | 0 | 0 | 2403.2606 | Heating | 2120.524 | 8.5 | 2120.524 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.1048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2163.8 | 0 | 432.76 | 4.328% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 15:01 | 11 | 29 | 15 | 333 | 7983 | 44.06 | 2336.5972 | 0 | 0 | 2336.5972 | Heating | 2061.7034 | 8.5 | 2061.7034 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.3407 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2103.779 | 0 | 420.7558 | 4.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 16:01 | 11 | 29 | 16 | 333 | 7984 | 42.98 | 2409.0733 | 0 | 0 | 2409.0733 | Heating | 2125.6529 | 8.5 | 2125.6529 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 425.1306 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2169.0336 | 0 | 433.8067 | 4.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 17:01 | 11 | 29 | 17 | 333 | 7985 | 42.98 | 2830.5323 | 0 | 0 | 2830.5323 | Heating | 2497.5285 | 8.5 | 2497.5285 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 499.5057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2548.4985 | 0 | 509.6997 | 5.097% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 18:01 | 11 | 29 | 18 | 333 | 7986 | 35.06 | 3244.4697 | 0 | 0 | 3244.4697 | Heating | 2862.7674 | 8.5 | 2862.7674 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 572.5535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2921.1913 | 0 | 584.2383 | 5.842% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 19:01 | 11 | 29 | 19 | 333 | 7987 | 33.08 | 3479.8609 | 0 | 0 | 3479.8609 | Heating | 3070.4655 | 8.5 | 3070.4655 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 614.0931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3133.1281 | 0 | 626.6256 | 6.266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 20:01 | 11 | 29 | 20 | 333 | 7988 | 33.08 | 3695.3257 | 0 | 0 | 3695.3257 | Heating | 3260.5815 | 8.5 | 3260.5815 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 652.1163 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3327.124 | 0 | 665.4248 | 6.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 21:01 | 11 | 29 | 21 | 333 | 7989 | 30.02 | 3917.6728 | 0 | 0 | 3917.6728 | Heating | 3456.7701 | 8.5 | 3456.7701 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 691.354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3527.3164 | 0 | 705.4633 | 7.055% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 22:01 | 11 | 29 | 22 | 333 | 7990 | 28.04 | 1047.9141 | 0 | 0 | 1047.9141 | Heating | 924.6301 | 8.5 | 924.6301 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.926 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 943.5001 | 0 | 188.7 | 1.887% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-29 23:01 | 11 | 29 | 23 | 333 | 7991 | 28.04 | 975.2417 | 0 | 0 | 975.2417 | Heating | 860.5074 | 8.5 | 860.5074 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.1015 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 878.0688 | 0 | 175.6138 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 00:01 | 11 | 30 | 0 | 334 | 7992 | 30.92 | 1003.4005 | 0 | 0 | 1003.4005 | Heating | 885.3534 | 8.5 | 885.3534 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.0707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 903.4218 | 0 | 180.6844 | 1.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 01:01 | 11 | 30 | 1 | 334 | 7993 | 32 | 1046.5304 | 0 | 0 | 1046.5304 | Heating | 923.4092 | 8.5 | 923.4092 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 184.6818 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 942.2542 | 0 | 188.4508 | 1.885% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 02:01 | 11 | 30 | 2 | 334 | 7994 | 32 | 1109.1641 | 0 | 0 | 1109.1641 | Heating | 978.6742 | 8.5 | 978.6742 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.7348 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 998.6471 | 0 | 199.7294 | 1.997% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 03:01 | 11 | 30 | 3 | 334 | 7995 | 32 | 1167.4495 | 0 | 0 | 1167.4495 | Heating | 1030.1025 | 8.5 | 1030.1025 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.0205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1051.125 | 0 | 210.225 | 2.102% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 04:01 | 11 | 30 | 4 | 334 | 7996 | 33.08 | 1186.2158 | 0 | 0 | 1186.2158 | Heating | 1046.661 | 8.5 | 1046.661 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 209.3322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1068.0214 | 0 | 213.6043 | 2.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 05:01 | 11 | 30 | 5 | 334 | 7997 | 33.08 | 1227.6932 | 0 | 0 | 1227.6932 | Heating | 1083.2587 | 8.5 | 1083.2587 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 216.6517 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1105.3661 | 0 | 221.0732 | 2.211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 06:01 | 11 | 30 | 6 | 334 | 7998 | 44.96 | 1242.2089 | 0 | 0 | 1242.2089 | Heating | 1096.0667 | 8.5 | 1096.0667 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.2133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1118.4354 | 0 | 223.6871 | 2.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 07:01 | 11 | 30 | 7 | 334 | 7999 | 44.06 | 9078.2277 | 0 | 0 | 9078.2277 | Heating | 8010.2009 | 8.5 | 8010.2009 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1602.0402 | 32.04% | 1 | 64.08% | 0% | 0% | 0% | 29.284 | 0 | 0 | 0 | 29.284 | 8173.6744 | 0 | 1634.7349 | 16.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.5585
2007-11-30 08:01 | 11 | 30 | 8 | 334 | 8000 | 44.06 | 7019.0835 | 0 | 0 | 7019.0835 | Heating | 6193.309 | 8.5 | 6193.309 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1238.6618 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6319.7031 | 0 | 1263.9406 | 12.64% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 09:01 | 11 | 30 | 9 | 334 | 8001 | 46.04 | 5993.4393 | 0 | 0 | 5993.4393 | Heating | 5288.3288 | 8.5 | 5288.3288 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1057.6658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5396.2539 | 0 | 1079.2508 | 10.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 10:01 | 11 | 30 | 10 | 334 | 8002 | 46.04 | 4734.1865 | 0 | 0 | 4734.1865 | Heating | 4177.2234 | 8.5 | 4177.2234 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 835.4447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4262.4729 | 0 | 852.4946 | 8.525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 11:01 | 11 | 30 | 11 | 334 | 8003 | 46.04 | 3591.2337 | 0 | 0 | 3591.2337 | Heating | 3168.7357 | 8.5 | 3168.7357 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 633.7471 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3233.4037 | 0 | 646.6807 | 6.467% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 12:01 | 11 | 30 | 12 | 334 | 8004 | 48.92 | 2956.7718 | 0 | 0 | 2956.7718 | Heating | 2608.9163 | 8.5 | 2608.9163 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 521.7833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2662.1595 | 0 | 532.4319 | 5.324% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 13:01 | 11 | 30 | 13 | 334 | 8005 | 51.98 | 2550.9172 | 0 | 0 | 2550.9172 | Heating | 2250.8093 | 8.5 | 2250.8093 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 450.1619 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2296.7442 | 0 | 459.3488 | 4.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 14:01 | 11 | 30 | 14 | 334 | 8006 | 51.98 | 2261.1479 | 0 | 0 | 2261.1479 | Heating | 1995.1305 | 8.5 | 1995.1305 | 0 | 4.7043 | 0 | 0 | 0 | 0 | 8.5 | 0 | 399.0261 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2035.8474 | 0 | 407.1695 | 4.072% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 15:01 | 11 | 30 | 15 | 334 | 8007 | 53.06 | 2186.1299 | 0 | 0 | 2186.1299 | Heating | 1928.9381 | 8.5 | 1928.9381 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.7876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1968.3042 | 0 | 393.6608 | 3.937% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 16:01 | 11 | 30 | 16 | 334 | 8008 | 53.06 | 2228.0018 | 0 | 0 | 2228.0018 | Heating | 1965.884 | 8.5 | 1965.884 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 393.1768 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2006.004 | 0 | 401.2008 | 4.012% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 17:01 | 11 | 30 | 17 | 334 | 8009 | 53.06 | 2390.3246 | 0 | 0 | 2390.3246 | Heating | 2109.11 | 8.5 | 2109.11 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.822 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2152.153 | 0 | 430.4306 | 4.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 18:01 | 11 | 30 | 18 | 334 | 8010 | 53.06 | 2590.0975 | 0 | 0 | 2590.0975 | Heating | 2285.3801 | 8.5 | 2285.3801 | 0 | 4.8142 | 0 | 0 | 0 | 0 | 8.5 | 0 | 457.076 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2332.0205 | 0 | 466.4041 | 4.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 19:01 | 11 | 30 | 19 | 334 | 8011 | 52.7 | 2932.8391 | 0 | 0 | 2932.8391 | Heating | 2587.7992 | 8.5 | 2587.7992 | 0 | 4.7771 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.5598 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2640.6114 | 0 | 528.1223 | 5.281% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 20:01 | 11 | 30 | 20 | 334 | 8012 | 52.52 | 3352.8135 | 0 | 0 | 3352.8135 | Heating | 2958.3648 | 8.5 | 2958.3648 | 0 | 4.7587 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3018.7396 | 0 | 603.7479 | 6.037% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 21:01 | 11 | 30 | 21 | 334 | 8013 | 51.8 | 3511.3705 | 0 | 0 | 3511.3705 | Heating | 3098.2681 | 8.5 | 3098.2681 | 0 | 4.6864 | 0 | 0 | 0 | 0 | 8.5 | 0 | 619.6536 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3161.498 | 0 | 632.2996 | 6.323% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 22:01 | 11 | 30 | 22 | 334 | 8014 | 50.72 | 4008.0155 | 0 | 0 | 4008.0155 | Heating | 3536.4842 | 8.5 | 3536.4842 | 0 | 4.5813 | 0 | 0 | 0 | 0 | 8.5 | 0 | 707.2968 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3608.6574 | 0 | 721.7315 | 7.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-11-30 23:01 | 11 | 30 | 23 | 334 | 8015 | 49.82 | 989.9659 | 0 | 0 | 989.9659 | Heating | 873.4993 | 8.5 | 873.4993 | 0 | 4.4967 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.6999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 891.3258 | 0 | 178.2652 | 1.783% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 00:01 | 12 | 1 | 0 | 335 | 8016 | 47.84 | 1149.2696 | 0 | 0 | 1149.2696 | Heating | 1014.0615 | 8.5 | 1014.0615 | 0 | 4.3201 | 0 | 0 | 0 | 0 | 8.5 | 0 | 202.8123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1034.7566 | 0 | 206.9513 | 2.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 01:01 | 12 | 1 | 1 | 335 | 8017 | 46.58 | 1328.1019 | 0 | 0 | 1328.1019 | Heating | 1171.8546 | 8.5 | 1171.8546 | 0 | 4.2143 | 0 | 0 | 0 | 0 | 8.5 | 0 | 234.3709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1195.77 | 0 | 239.154 | 2.392% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 02:01 | 12 | 1 | 2 | 335 | 8018 | 45.5 | 1507.7315 | 0 | 0 | 1507.7315 | Heating | 1330.3513 | 8.5 | 1330.3513 | 0 | 4.1276 | 0 | 0 | 0 | 0 | 8.5 | 0 | 266.0703 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1357.5014 | 0 | 271.5003 | 2.715% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 03:01 | 12 | 1 | 3 | 335 | 8019 | 44.42 | 1685.015 | 0 | 0 | 1685.015 | Heating | 1486.778 | 8.5 | 1486.778 | 0 | 4.0444 | 0 | 0 | 0 | 0 | 8.5 | 0 | 297.3556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1517.1204 | 0 | 303.4241 | 3.034% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 04:01 | 12 | 1 | 4 | 335 | 8020 | 44.42 | 1868.5535 | 0 | 0 | 1868.5535 | Heating | 1648.7237 | 8.5 | 1648.7237 | 0 | 4.0444 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.7447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1682.3711 | 0 | 336.4742 | 3.365% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 05:01 | 12 | 1 | 5 | 335 | 8021 | 44.24 | 2010.3516 | 0 | 0 | 2010.3516 | Heating | 1773.8397 | 8.5 | 1773.8397 | 0 | 4.0309 | 0 | 0 | 0 | 0 | 8.5 | 0 | 354.7679 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1810.0405 | 0 | 362.0081 | 3.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 06:01 | 12 | 1 | 6 | 335 | 8022 | 44.6 | 2118.5099 | 0 | 0 | 2118.5099 | Heating | 1869.2734 | 8.5 | 1869.2734 | 0 | 4.058 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.8547 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1907.4219 | 0 | 381.4844 | 3.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 07:01 | 12 | 1 | 7 | 335 | 8023 | 44.06 | 2215.0424 | 0 | 0 | 2215.0424 | Heating | 1954.4492 | 8.5 | 1954.4492 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.8898 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1994.3359 | 0 | 398.8672 | 3.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 08:01 | 12 | 1 | 8 | 335 | 8024 | 44.06 | 2122.8068 | 0 | 0 | 2122.8068 | Heating | 1873.0648 | 8.5 | 1873.0648 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 374.613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1911.2906 | 0 | 382.2581 | 3.823% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 09:01 | 12 | 1 | 9 | 335 | 8025 | 46.04 | 10830.7574 | 0 | 0 | 10830.7574 | Heating | 9556.5507 | 8.5 | 9556.5507 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1911.3101 | 38.23% | 1 | 76.45% | 0% | 0% | 0% | 43.9484 | 0 | 0 | 0 | 43.9484 | 9751.5823 | 0 | 1950.3165 | 19.5% | 1 | 39.01% | 0% | 0% | 4.6744 | 0 | 0 | 4.6744 | 48.6227
2007-12-01 10:01 | 12 | 1 | 10 | 335 | 8026 | 48.02 | 7679.9211 | 0 | 0 | 7679.9211 | Heating | 6776.401 | 8.5 | 6776.401 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1355.2802 | 30% | 1 | 54.21% | 0% | 0% | 0% | 19.9319 | 0 | 0 | 0 | 19.9319 | 6914.6949 | 0 | 1382.939 | 13.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.2064
2007-12-01 11:01 | 12 | 1 | 11 | 335 | 8027 | 48.02 | 6032.3309 | 0 | 0 | 6032.3309 | Heating | 5322.6449 | 8.5 | 5322.6449 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1064.529 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5431.2703 | 0 | 1086.2541 | 10.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 12:01 | 12 | 1 | 12 | 335 | 8028 | 48.92 | 4992.2744 | 0 | 0 | 4992.2744 | Heating | 4404.948 | 8.5 | 4404.948 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 880.9896 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4494.8449 | 0 | 898.969 | 8.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 13:01 | 12 | 1 | 13 | 335 | 8029 | 51.08 | 3869.059 | 0 | 0 | 3869.059 | Heating | 3413.8756 | 8.5 | 3413.8756 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 682.7751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3483.5465 | 0 | 696.7093 | 6.967% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 14:01 | 12 | 1 | 14 | 335 | 8030 | 51.08 | 3451.0938 | 0 | 0 | 3451.0938 | Heating | 3045.0828 | 8.5 | 3045.0828 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 609.0166 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3107.2273 | 0 | 621.4455 | 6.214% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 15:01 | 12 | 1 | 15 | 335 | 8031 | 51.08 | 3401.8376 | 0 | 0 | 3401.8376 | Heating | 3001.6214 | 8.5 | 3001.6214 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 600.3243 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3062.879 | 0 | 612.5758 | 6.126% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 16:01 | 12 | 1 | 16 | 335 | 8032 | 51.08 | 3481.457 | 0 | 0 | 3481.457 | Heating | 3071.8738 | 8.5 | 3071.8738 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 614.3748 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3134.5651 | 0 | 626.913 | 6.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 17:01 | 12 | 1 | 17 | 335 | 8033 | 51.08 | 3597.5441 | 0 | 0 | 3597.5441 | Heating | 3174.3037 | 8.5 | 3174.3037 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 634.8607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3239.0854 | 0 | 647.8171 | 6.478% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 18:01 | 12 | 1 | 18 | 335 | 8034 | 51.08 | 5127.2276 | 0 | 0 | 5127.2276 | Heating | 4524.0243 | 8.5 | 4524.0243 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 904.8049 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4616.3514 | 0 | 923.2703 | 9.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 19:01 | 12 | 1 | 19 | 335 | 8035 | 50 | 5540.7215 | 0 | 0 | 5540.7215 | Heating | 4888.872 | 8.5 | 4888.872 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 977.7744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4988.6448 | 0 | 997.729 | 9.977% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 20:01 | 12 | 1 | 20 | 335 | 8036 | 50 | 1243.9621 | 0 | 0 | 1243.9621 | Heating | 1097.6136 | 8.5 | 1097.6136 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.5227 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1120.0139 | 0 | 224.0028 | 2.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 21:01 | 12 | 1 | 21 | 335 | 8037 | 51.8 | 1256.3989 | 0 | 0 | 1256.3989 | Heating | 1108.5873 | 8.5 | 1108.5873 | 0 | 4.6864 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.7175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1131.2115 | 0 | 226.2423 | 2.262% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 22:01 | 12 | 1 | 22 | 335 | 8038 | 51.08 | 1269.2067 | 0 | 0 | 1269.2067 | Heating | 1119.8883 | 8.5 | 1119.8883 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 223.9777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1142.7431 | 0 | 228.5486 | 2.285% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-01 23:01 | 12 | 1 | 23 | 335 | 8039 | 51.08 | 1333.7771 | 0 | 0 | 1333.7771 | Heating | 1176.8622 | 8.5 | 1176.8622 | 0 | 4.6159 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.3724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1200.8798 | 0 | 240.176 | 2.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 00:01 | 12 | 2 | 0 | 336 | 8040 | 50 | 1412.1918 | 0 | 0 | 1412.1918 | Heating | 1246.0516 | 8.5 | 1246.0516 | 0 | 4.5134 | 0 | 0 | 0 | 0 | 8.5 | 0 | 249.2103 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1271.4812 | 0 | 254.2962 | 2.543% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 01:01 | 12 | 2 | 1 | 336 | 8041 | 48.02 | 1485.1917 | 0 | 0 | 1485.1917 | Heating | 1310.4633 | 8.5 | 1310.4633 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 262.0927 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1337.2074 | 0 | 267.4415 | 2.674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 02:01 | 12 | 2 | 2 | 336 | 8042 | 48.02 | 1514.5125 | 0 | 0 | 1514.5125 | Heating | 1336.3346 | 8.5 | 1336.3346 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.2669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1363.6067 | 0 | 272.7213 | 2.727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 03:01 | 12 | 2 | 3 | 336 | 8043 | 46.94 | 1518.5396 | 0 | 0 | 1518.5396 | Heating | 1339.8879 | 8.5 | 1339.8879 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.9776 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1367.2325 | 0 | 273.4465 | 2.734% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 04:01 | 12 | 2 | 4 | 336 | 8044 | 46.94 | 1514.1553 | 0 | 0 | 1514.1553 | Heating | 1336.0194 | 8.5 | 1336.0194 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 267.2039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1363.2851 | 0 | 272.657 | 2.727% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 05:01 | 12 | 2 | 5 | 336 | 8045 | 48.92 | 1487.6504 | 0 | 0 | 1487.6504 | Heating | 1312.6327 | 8.5 | 1312.6327 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 262.5265 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1339.4212 | 0 | 267.8842 | 2.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 06:01 | 12 | 2 | 6 | 336 | 8046 | 48.02 | 1439.8367 | 0 | 0 | 1439.8367 | Heating | 1270.4442 | 8.5 | 1270.4442 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 254.0888 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1296.3716 | 0 | 259.2743 | 2.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 07:01 | 12 | 2 | 7 | 336 | 8047 | 44.96 | 9356.2214 | 0 | 0 | 9356.2214 | Heating | 8255.4895 | 8.5 | 8255.4895 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1651.0979 | 33.02% | 1 | 66.04% | 0% | 0% | 0% | 31.3876 | 0 | 0 | 0 | 31.3876 | 8423.9689 | 0 | 1684.7938 | 16.85% | 1 | 33.7% | 0% | 0% | 3.3384 | 0 | 0 | 3.3384 | 34.726
2007-12-02 08:01 | 12 | 2 | 8 | 336 | 8048 | 44.96 | 6929.96 | 0 | 0 | 6929.96 | Heating | 6114.6706 | 8.5 | 6114.6706 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1222.9341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6239.4598 | 0 | 1247.892 | 12.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 09:01 | 12 | 2 | 9 | 336 | 8049 | 48.92 | 5543.8427 | 0 | 0 | 5543.8427 | Heating | 4891.6259 | 8.5 | 4891.6259 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 978.3252 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4991.455 | 0 | 998.291 | 9.983% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 10:01 | 12 | 2 | 10 | 336 | 8050 | 48.02 | 4339.0397 | 0 | 0 | 4339.0397 | Heating | 3828.5644 | 8.5 | 3828.5644 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 765.7129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3906.6984 | 0 | 781.3397 | 7.813% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 11:01 | 12 | 2 | 11 | 336 | 8051 | 48.02 | 3775.8542 | 0 | 0 | 3775.8542 | Heating | 3331.636 | 8.5 | 3331.636 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 666.3272 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3399.6286 | 0 | 679.9257 | 6.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 12:01 | 12 | 2 | 12 | 336 | 8052 | 46.04 | 3362.8233 | 0 | 0 | 3362.8233 | Heating | 2967.197 | 8.5 | 2967.197 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 593.4394 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3027.7521 | 0 | 605.5504 | 6.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 13:01 | 12 | 2 | 13 | 336 | 8053 | 44.96 | 3206.9817 | 0 | 0 | 3206.9817 | Heating | 2829.6898 | 8.5 | 2829.6898 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 565.938 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2887.4385 | 0 | 577.4877 | 5.775% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 14:01 | 12 | 2 | 14 | 336 | 8054 | 44.96 | 3186.3415 | 0 | 0 | 3186.3415 | Heating | 2811.4778 | 8.5 | 2811.4778 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 562.2956 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2868.8549 | 0 | 573.771 | 5.738% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 15:01 | 12 | 2 | 15 | 336 | 8055 | 44.96 | 3314.3053 | 0 | 0 | 3314.3053 | Heating | 2924.3871 | 8.5 | 2924.3871 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 584.8774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2984.0684 | 0 | 596.8137 | 5.968% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 16:01 | 12 | 2 | 16 | 336 | 8056 | 44.06 | 3472.405 | 0 | 0 | 3472.405 | Heating | 3063.8867 | 8.5 | 3063.8867 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 612.7773 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3126.415 | 0 | 625.283 | 6.253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 17:01 | 12 | 2 | 17 | 336 | 8057 | 44.06 | 3727.7554 | 0 | 0 | 3727.7554 | Heating | 3289.1959 | 8.5 | 3289.1959 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 657.8392 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3356.3224 | 0 | 671.2645 | 6.713% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 18:01 | 12 | 2 | 18 | 336 | 8058 | 41 | 4040.7926 | 0 | 0 | 4040.7926 | Heating | 3565.4052 | 8.5 | 3565.4052 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 713.081 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3638.1686 | 0 | 727.6337 | 7.276% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 19:01 | 12 | 2 | 19 | 336 | 8059 | 37.04 | 4226.8578 | 0 | 0 | 4226.8578 | Heating | 3729.5804 | 8.5 | 3729.5804 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.9161 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3805.6943 | 0 | 761.1389 | 7.611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 20:01 | 12 | 2 | 20 | 336 | 8060 | 37.04 | 4530.4248 | 0 | 0 | 4530.4248 | Heating | 3997.4336 | 8.5 | 3997.4336 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 799.4867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4079.0139 | 0 | 815.8028 | 8.158% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 21:01 | 12 | 2 | 21 | 336 | 8061 | 39.92 | 4965.4486 | 0 | 0 | 4965.4486 | Heating | 4381.2782 | 8.5 | 4381.2782 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 876.2556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4470.6921 | 0 | 894.1384 | 8.941% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 22:01 | 12 | 2 | 22 | 336 | 8062 | 41 | 1538.9042 | 0 | 0 | 1538.9042 | Heating | 1357.8567 | 8.5 | 1357.8567 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 271.5713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1385.568 | 0 | 277.1136 | 2.771% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-02 23:01 | 12 | 2 | 23 | 336 | 8063 | 41 | 1479.58 | 0 | 0 | 1479.58 | Heating | 1305.5118 | 8.5 | 1305.5118 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.1024 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1332.1549 | 0 | 266.431 | 2.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 00:01 | 12 | 3 | 0 | 337 | 8064 | 39.92 | 1854.9815 | 0 | 0 | 1854.9815 | Heating | 1636.7484 | 8.5 | 1636.7484 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 327.3497 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1670.1515 | 0 | 334.0303 | 3.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 01:01 | 12 | 3 | 1 | 337 | 8065 | 41 | 2128.4499 | 0 | 0 | 2128.4499 | Heating | 1878.044 | 8.5 | 1878.044 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 375.6088 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1916.3714 | 0 | 383.2743 | 3.833% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 02:01 | 12 | 3 | 2 | 337 | 8066 | 41 | 2343.2658 | 0 | 0 | 2343.2658 | Heating | 2067.5875 | 8.5 | 2067.5875 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 413.5175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2109.7832 | 0 | 421.9566 | 4.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 03:01 | 12 | 3 | 3 | 337 | 8067 | 37.94 | 2527.2878 | 0 | 0 | 2527.2878 | Heating | 2229.9598 | 8.5 | 2229.9598 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 445.992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2275.4692 | 0 | 455.0938 | 4.551% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 04:01 | 12 | 3 | 4 | 337 | 8068 | 39.02 | 2701.5761 | 0 | 0 | 2701.5761 | Heating | 2383.7436 | 8.5 | 2383.7436 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.7487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2432.3914 | 0 | 486.4783 | 4.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 05:01 | 12 | 3 | 5 | 337 | 8069 | 39.02 | 2815.8907 | 0 | 0 | 2815.8907 | Heating | 2484.6094 | 8.5 | 2484.6094 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 496.9219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2535.3157 | 0 | 507.0631 | 5.071% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 06:01 | 12 | 3 | 6 | 337 | 8070 | 37.94 | 2867.7888 | 0 | 0 | 2867.7888 | Heating | 2530.4019 | 8.5 | 2530.4019 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 506.0804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2582.0428 | 0 | 516.4086 | 5.164% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 07:01 | 12 | 3 | 7 | 337 | 8071 | 39.92 | 13721.0807 | 0 | 0 | 13721.0807 | Heating | 12106.8359 | 8.5 | 12106.8359 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2421.3672 | 48.43% | 1 | 96.85% | 0% | 0% | 0% | 75.7217 | 0 | 0 | 0 | 75.7217 | 12353.9142 | 0 | 2470.7828 | 24.71% | 1 | 49.42% | 0% | 0% | 8.0538 | 0 | 0 | 8.0538 | 83.7755
2007-12-03 08:01 | 12 | 3 | 8 | 337 | 8072 | 39.92 | 11249.2365 | 0 | 0 | 11249.2365 | Heating | 9925.7969 | 8.5 | 9925.7969 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1985.1594 | 39.7% | 1 | 79.41% | 0% | 0% | 0% | 47.9524 | 0 | 0 | 0 | 47.9524 | 10128.3642 | 0 | 2025.6728 | 20.26% | 1 | 40.51% | 0% | 0% | 5.1002 | 0 | 0 | 5.1002 | 53.0527
2007-12-03 09:01 | 12 | 3 | 9 | 337 | 8073 | 44.96 | 9487.9287 | 0 | 0 | 9487.9287 | Heating | 8371.7018 | 8.5 | 8371.7018 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1674.3404 | 33.49% | 1 | 66.97% | 0% | 0% | 0% | 32.4132 | 0 | 0 | 0 | 32.4132 | 8542.5528 | 0 | 1708.5106 | 17.09% | 1 | 34.17% | 0% | 0% | 3.4475 | 0 | 0 | 3.4475 | 35.8607
2007-12-03 10:01 | 12 | 3 | 10 | 337 | 8074 | 44.96 | 8028.3208 | 0 | 0 | 8028.3208 | Heating | 7083.8125 | 8.5 | 7083.8125 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1416.7625 | 30% | 1 | 56.67% | 0% | 0% | 0% | 22.0731 | 0 | 0 | 0 | 22.0731 | 7228.3801 | 0 | 1445.676 | 14.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.3477
2007-12-03 11:01 | 12 | 3 | 11 | 337 | 8075 | 44.96 | 7279.5165 | 0 | 0 | 7279.5165 | Heating | 6423.1028 | 8.5 | 6423.1028 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1284.6206 | 30% | 1 | 51.38% | 0% | 0% | 0% | 17.6223 | 0 | 0 | 0 | 17.6223 | 6554.1865 | 0 | 1310.8373 | 13.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.8969
2007-12-03 12:01 | 12 | 3 | 12 | 337 | 8076 | 48.92 | 6729.464 | 0 | 0 | 6729.464 | Heating | 5937.7623 | 8.5 | 5937.7623 | 0 | 4.4149 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1187.5525 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6058.9412 | 0 | 1211.7882 | 12.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 13:01 | 12 | 3 | 13 | 337 | 8077 | 46.94 | 6411.8446 | 0 | 0 | 6411.8446 | Heating | 5657.51 | 8.5 | 5657.51 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1131.502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5772.9693 | 0 | 1154.5939 | 11.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 14:01 | 12 | 3 | 14 | 337 | 8078 | 46.94 | 6030.6781 | 0 | 0 | 6030.6781 | Heating | 5321.1866 | 8.5 | 5321.1866 | 0 | 4.2441 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1064.2373 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5429.7822 | 0 | 1085.9564 | 10.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 15:01 | 12 | 3 | 15 | 337 | 8079 | 46.04 | 5698.0946 | 0 | 0 | 5698.0946 | Heating | 5027.7306 | 8.5 | 5027.7306 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1005.5461 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5130.3373 | 0 | 1026.0675 | 10.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 16:01 | 12 | 3 | 16 | 337 | 8080 | 44.96 | 5420.4933 | 0 | 0 | 5420.4933 | Heating | 4782.7882 | 8.5 | 4782.7882 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 956.5576 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4880.3961 | 0 | 976.0792 | 9.761% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 17:01 | 12 | 3 | 17 | 337 | 8081 | 44.96 | 5309.0809 | 0 | 0 | 5309.0809 | Heating | 4684.4831 | 8.5 | 4684.4831 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 936.8966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4780.0848 | 0 | 956.017 | 9.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 18:01 | 12 | 3 | 18 | 337 | 8082 | 42.98 | 5268.7025 | 0 | 0 | 5268.7025 | Heating | 4648.8552 | 8.5 | 4648.8552 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 929.771 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4743.7297 | 0 | 948.7459 | 9.487% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 19:01 | 12 | 3 | 19 | 337 | 8083 | 42.08 | 5202.9001 | 0 | 0 | 5202.9001 | Heating | 4590.7942 | 8.5 | 4590.7942 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 918.1588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4684.4839 | 0 | 936.8968 | 9.369% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 20:01 | 12 | 3 | 20 | 337 | 8084 | 42.08 | 5125.9649 | 0 | 0 | 5125.9649 | Heating | 4522.9102 | 8.5 | 4522.9102 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 904.582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4615.2145 | 0 | 923.0429 | 9.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 21:01 | 12 | 3 | 21 | 337 | 8085 | 42.08 | 5082.1196 | 0 | 0 | 5082.1196 | Heating | 4484.2232 | 8.5 | 4484.2232 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 896.8446 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4575.738 | 0 | 915.1476 | 9.151% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 22:01 | 12 | 3 | 22 | 337 | 8086 | 39.02 | 1438.1239 | 0 | 0 | 1438.1239 | Heating | 1268.9329 | 8.5 | 1268.9329 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 253.7866 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1294.8295 | 0 | 258.9659 | 2.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-03 23:01 | 12 | 3 | 23 | 337 | 8087 | 39.02 | 1172.2456 | 0 | 0 | 1172.2456 | Heating | 1034.3343 | 8.5 | 1034.3343 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 206.8669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1055.4432 | 0 | 211.0886 | 2.111% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 00:01 | 12 | 4 | 0 | 338 | 8088 | 37.04 | 1271.35 | 0 | 0 | 1271.35 | Heating | 1121.7794 | 8.5 | 1121.7794 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 224.3559 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1144.6728 | 0 | 228.9346 | 2.289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 01:01 | 12 | 4 | 1 | 338 | 8089 | 37.04 | 1284.8336 | 0 | 0 | 1284.8336 | Heating | 1133.6767 | 8.5 | 1133.6767 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 226.7353 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1156.813 | 0 | 231.3626 | 2.314% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 02:01 | 12 | 4 | 2 | 338 | 8090 | 37.04 | 1275.3747 | 0 | 0 | 1275.3747 | Heating | 1125.3306 | 8.5 | 1125.3306 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.0661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1148.2966 | 0 | 229.6593 | 2.297% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 03:01 | 12 | 4 | 3 | 338 | 8091 | 37.04 | 1259.8157 | 0 | 0 | 1259.8157 | Heating | 1111.6021 | 8.5 | 1111.6021 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 222.3204 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1134.2878 | 0 | 226.8576 | 2.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 04:01 | 12 | 4 | 4 | 338 | 8092 | 37.04 | 1236.049 | 0 | 0 | 1236.049 | Heating | 1090.6315 | 8.5 | 1090.6315 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.1263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1112.8892 | 0 | 222.5778 | 2.226% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 05:01 | 12 | 4 | 5 | 338 | 8093 | 37.04 | 1202.7667 | 0 | 0 | 1202.7667 | Heating | 1061.2648 | 8.5 | 1061.2648 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.253 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1082.9232 | 0 | 216.5846 | 2.166% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 06:01 | 12 | 4 | 6 | 338 | 8094 | 37.04 | 1157.5393 | 0 | 0 | 1157.5393 | Heating | 1021.3582 | 8.5 | 1021.3582 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 204.2716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1042.2022 | 0 | 208.4404 | 2.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 07:01 | 12 | 4 | 7 | 338 | 8095 | 37.04 | 8436.9041 | 0 | 0 | 8436.9041 | Heating | 7444.3271 | 8.5 | 7444.3271 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1488.8654 | 30% | 1 | 59.55% | 0% | 0% | 0% | 24.7428 | 0 | 0 | 0 | 24.7428 | 7596.2522 | 0 | 1519.2504 | 15.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.0173
2007-12-04 08:01 | 12 | 4 | 8 | 338 | 8096 | 37.04 | 5957.035 | 0 | 0 | 5957.035 | Heating | 5256.2074 | 8.5 | 5256.2074 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1051.2415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5363.4769 | 0 | 1072.6954 | 10.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 09:01 | 12 | 4 | 9 | 338 | 8097 | 37.94 | 4435.7457 | 0 | 0 | 4435.7457 | Heating | 3913.8932 | 8.5 | 3913.8932 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 782.7786 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3993.7686 | 0 | 798.7537 | 7.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 10:01 | 12 | 4 | 10 | 338 | 8098 | 39.02 | 3059.6041 | 0 | 0 | 3059.6041 | Heating | 2699.6507 | 8.5 | 2699.6507 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 539.9301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2754.7456 | 0 | 550.9491 | 5.509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 11:01 | 12 | 4 | 11 | 338 | 8099 | 39.02 | 2335.5916 | 0 | 0 | 2335.5916 | Heating | 2060.8161 | 8.5 | 2060.8161 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.1632 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2102.8736 | 0 | 420.5747 | 4.206% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 12:01 | 12 | 4 | 12 | 338 | 8100 | 41 | 1779.6866 | 0 | 0 | 1779.6866 | Heating | 1570.3117 | 8.5 | 1570.3117 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 314.0623 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1602.3588 | 0 | 320.4718 | 3.205% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 13:01 | 12 | 4 | 13 | 338 | 8101 | 42.08 | 1466.3881 | 0 | 0 | 1466.3881 | Heating | 1293.8719 | 8.5 | 1293.8719 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 258.7744 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1320.2774 | 0 | 264.0555 | 2.641% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 14:01 | 12 | 4 | 14 | 338 | 8102 | 42.08 | 1391.0789 | 0 | 0 | 1391.0789 | Heating | 1227.4225 | 8.5 | 1227.4225 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 245.4845 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1252.472 | 0 | 250.4944 | 2.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 15:01 | 12 | 4 | 15 | 338 | 8103 | 37.94 | 1481.3143 | 0 | 0 | 1481.3143 | Heating | 1307.042 | 8.5 | 1307.042 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 261.4084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1333.7164 | 0 | 266.7433 | 2.667% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 16:01 | 12 | 4 | 16 | 338 | 8104 | 37.04 | 1588.9636 | 0 | 0 | 1588.9636 | Heating | 1402.0267 | 8.5 | 1402.0267 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 280.4053 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1430.6395 | 0 | 286.1279 | 2.861% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 17:01 | 12 | 4 | 17 | 338 | 8105 | 37.04 | 1905.0199 | 0 | 0 | 1905.0199 | Heating | 1680.8999 | 8.5 | 1680.8999 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.18 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1715.2039 | 0 | 343.0408 | 3.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 18:01 | 12 | 4 | 18 | 338 | 8106 | 37.04 | 2393.2511 | 0 | 0 | 2393.2511 | Heating | 2111.6922 | 8.5 | 2111.6922 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 422.3384 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2154.7879 | 0 | 430.9576 | 4.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 19:01 | 12 | 4 | 19 | 338 | 8107 | 35.96 | 2877.8278 | 0 | 0 | 2877.8278 | Heating | 2539.2598 | 8.5 | 2539.2598 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 507.852 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2591.0814 | 0 | 518.2163 | 5.182% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 20:01 | 12 | 4 | 20 | 338 | 8108 | 35.96 | 3216.2846 | 0 | 0 | 3216.2846 | Heating | 2837.8981 | 8.5 | 2837.8981 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 567.5796 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2895.8144 | 0 | 579.1629 | 5.792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 21:01 | 12 | 4 | 21 | 338 | 8109 | 35.96 | 3498.6873 | 0 | 0 | 3498.6873 | Heating | 3087.077 | 8.5 | 3087.077 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 617.4154 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3150.0786 | 0 | 630.0157 | 6.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 22:01 | 12 | 4 | 22 | 338 | 8110 | 35.96 | 1036.0304 | 0 | 0 | 1036.0304 | Heating | 914.1445 | 8.5 | 914.1445 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.8289 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 932.8005 | 0 | 186.5601 | 1.866% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-04 23:01 | 12 | 4 | 23 | 338 | 8111 | 35.96 | 891.926 | 0 | 0 | 891.926 | Heating | 786.9935 | 8.5 | 786.9935 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 157.3987 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 803.0546 | 0 | 160.6109 | 1.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 00:01 | 12 | 5 | 0 | 339 | 8112 | 35.06 | 1007.9721 | 0 | 0 | 1007.9721 | Heating | 889.3872 | 8.5 | 889.3872 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.8774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 907.5379 | 0 | 181.5076 | 1.815% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 01:01 | 12 | 5 | 1 | 339 | 8113 | 33.98 | 1122.7906 | 0 | 0 | 1122.7906 | Heating | 990.6976 | 8.5 | 990.6976 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 198.1395 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1010.916 | 0 | 202.1832 | 2.022% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 02:01 | 12 | 5 | 2 | 339 | 8114 | 33.98 | 1202.177 | 0 | 0 | 1202.177 | Heating | 1060.7444 | 8.5 | 1060.7444 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 212.1489 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1082.3923 | 0 | 216.4785 | 2.165% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 03:01 | 12 | 5 | 3 | 339 | 8115 | 33.98 | 1256.6381 | 0 | 0 | 1256.6381 | Heating | 1108.7983 | 8.5 | 1108.7983 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 221.7597 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1131.4268 | 0 | 226.2854 | 2.263% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 04:01 | 12 | 5 | 4 | 339 | 8116 | 33.08 | 1300.0288 | 0 | 0 | 1300.0288 | Heating | 1147.0843 | 8.5 | 1147.0843 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 229.4169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1170.4942 | 0 | 234.0988 | 2.341% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 05:01 | 12 | 5 | 5 | 339 | 8117 | 33.08 | 1445.7615 | 0 | 0 | 1445.7615 | Heating | 1275.6719 | 8.5 | 1275.6719 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 255.1344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1301.706 | 0 | 260.3412 | 2.603% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 06:01 | 12 | 5 | 6 | 339 | 8118 | 28.94 | 1645.5808 | 0 | 0 | 1645.5808 | Heating | 1451.9831 | 8.5 | 1451.9831 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.3966 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1481.6154 | 0 | 296.3231 | 2.963% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 07:01 | 12 | 5 | 7 | 339 | 8119 | 30.02 | 11029.5658 | 0 | 0 | 11029.5658 | Heating | 9731.9698 | 8.5 | 9731.9698 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1946.394 | 38.93% | 1 | 77.86% | 0% | 0% | 0% | 45.826 | 0 | 0 | 0 | 45.826 | 9930.5815 | 0 | 1986.1163 | 19.86% | 1 | 39.72% | 0% | 0% | 4.8741 | 0 | 0 | 4.8741 | 50.7001
2007-12-05 08:01 | 12 | 5 | 8 | 339 | 8120 | 30.02 | 8312.4007 | 0 | 0 | 8312.4007 | Heating | 7334.4712 | 8.5 | 7334.4712 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1466.8942 | 30% | 1 | 58.68% | 0% | 0% | 0% | 23.911 | 0 | 0 | 0 | 23.911 | 7484.1543 | 0 | 1496.8309 | 14.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.1856
2007-12-05 09:01 | 12 | 5 | 9 | 339 | 8121 | 32 | 6384.2747 | 0 | 0 | 6384.2747 | Heating | 5633.1836 | 8.5 | 5633.1836 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1126.6367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5748.1465 | 0 | 1149.6293 | 11.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 10:01 | 12 | 5 | 10 | 339 | 8122 | 32 | 4719.4902 | 0 | 0 | 4719.4902 | Heating | 4164.256 | 8.5 | 4164.256 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 832.8512 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4249.2409 | 0 | 849.8482 | 8.498% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 11:01 | 12 | 5 | 11 | 339 | 8123 | 32 | 3754.0252 | 0 | 0 | 3754.0252 | Heating | 3312.3752 | 8.5 | 3312.3752 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 662.475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3379.9747 | 0 | 675.9949 | 6.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 12:01 | 12 | 5 | 12 | 339 | 8124 | 33.98 | 2963.7122 | 0 | 0 | 2963.7122 | Heating | 2615.0402 | 8.5 | 2615.0402 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.008 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2668.4084 | 0 | 533.6817 | 5.337% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 13:01 | 12 | 5 | 13 | 339 | 8125 | 33.98 | 2404.8622 | 0 | 0 | 2404.8622 | Heating | 2121.9373 | 8.5 | 2121.9373 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.3875 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2165.2421 | 0 | 433.0484 | 4.33% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 14:01 | 12 | 5 | 14 | 339 | 8126 | 33.98 | 2175.5061 | 0 | 0 | 2175.5061 | Heating | 1919.5642 | 8.5 | 1919.5642 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 383.9128 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1958.739 | 0 | 391.7478 | 3.917% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 15:01 | 12 | 5 | 15 | 339 | 8127 | 35.06 | 2163.9146 | 0 | 0 | 2163.9146 | Heating | 1909.3364 | 8.5 | 1909.3364 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 381.8673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1948.3024 | 0 | 389.6605 | 3.897% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 16:01 | 12 | 5 | 16 | 339 | 8128 | 33.08 | 2187.0551 | 0 | 0 | 2187.0551 | Heating | 1929.7545 | 8.5 | 1929.7545 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 385.9509 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1969.1372 | 0 | 393.8274 | 3.938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 17:01 | 12 | 5 | 17 | 339 | 8129 | 33.08 | 2548.9612 | 0 | 0 | 2548.9612 | Heating | 2249.0834 | 8.5 | 2249.0834 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 449.8167 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2294.9831 | 0 | 458.9966 | 4.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 18:01 | 12 | 5 | 18 | 339 | 8130 | 28.94 | 3079.3284 | 0 | 0 | 3079.3284 | Heating | 2717.0545 | 8.5 | 2717.0545 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 543.4109 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2772.5046 | 0 | 554.5009 | 5.545% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 19:01 | 12 | 5 | 19 | 339 | 8131 | 26.96 | 3548.2484 | 0 | 0 | 3548.2484 | Heating | 3130.8074 | 8.5 | 3130.8074 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 626.1615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3194.7014 | 0 | 638.9403 | 6.389% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 20:01 | 12 | 5 | 20 | 339 | 8132 | 26.96 | 3723.1514 | 0 | 0 | 3723.1514 | Heating | 3285.1336 | 8.5 | 3285.1336 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 657.0267 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3352.1772 | 0 | 670.4354 | 6.704% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 21:01 | 12 | 5 | 21 | 339 | 8133 | 24.98 | 3750.4146 | 0 | 0 | 3750.4146 | Heating | 3309.1894 | 8.5 | 3309.1894 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 661.8379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3376.7239 | 0 | 675.3448 | 6.753% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 22:01 | 12 | 5 | 22 | 339 | 8134 | 24.98 | 1008.3006 | 0 | 0 | 1008.3006 | Heating | 889.677 | 8.5 | 889.677 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 177.9354 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 907.8337 | 0 | 181.5667 | 1.816% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-05 23:01 | 12 | 5 | 23 | 339 | 8135 | 24.98 | 879.6818 | 0 | 0 | 879.6818 | Heating | 776.1898 | 8.5 | 776.1898 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 155.238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 792.0304 | 0 | 158.4061 | 1.584% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 00:01 | 12 | 6 | 0 | 340 | 8136 | 26.06 | 941.5361 | 0 | 0 | 941.5361 | Heating | 830.7671 | 8.5 | 830.7671 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 166.1534 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 847.7215 | 0 | 169.5443 | 1.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 01:01 | 12 | 6 | 1 | 340 | 8137 | 26.06 | 1050.4645 | 0 | 0 | 1050.4645 | Heating | 926.8804 | 8.5 | 926.8804 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 185.3761 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 945.7963 | 0 | 189.1593 | 1.892% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 02:01 | 12 | 6 | 2 | 340 | 8138 | 26.06 | 1137.4382 | 0 | 0 | 1137.4382 | Heating | 1003.622 | 8.5 | 1003.622 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 200.7244 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1024.104 | 0 | 204.8208 | 2.048% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 03:01 | 12 | 6 | 3 | 340 | 8139 | 28.04 | 1198.4427 | 0 | 0 | 1198.4427 | Heating | 1057.4495 | 8.5 | 1057.4495 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.4899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1079.0301 | 0 | 215.806 | 2.158% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 04:01 | 12 | 6 | 4 | 340 | 8140 | 28.94 | 1245.0118 | 0 | 0 | 1245.0118 | Heating | 1098.5398 | 8.5 | 1098.5398 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1120.959 | 0 | 224.1918 | 2.242% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 05:01 | 12 | 6 | 5 | 340 | 8141 | 28.04 | 1335.8432 | 0 | 0 | 1335.8432 | Heating | 1178.6852 | 8.5 | 1178.6852 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.737 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1202.74 | 0 | 240.548 | 2.405% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 06:01 | 12 | 6 | 6 | 340 | 8142 | 28.04 | 1453.6769 | 0 | 0 | 1453.6769 | Heating | 1282.6561 | 8.5 | 1282.6561 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 256.5312 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1308.8327 | 0 | 261.7665 | 2.618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 07:01 | 12 | 6 | 7 | 340 | 8143 | 28.94 | 10056.5909 | 0 | 0 | 10056.5909 | Heating | 8873.4626 | 8.5 | 8873.4626 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1774.6925 | 35.49% | 1 | 70.99% | 0% | 0% | 0% | 37.0565 | 0 | 0 | 0 | 37.0565 | 9054.5537 | 0 | 1810.9107 | 18.11% | 1 | 36.22% | 0% | 0% | 3.9414 | 0 | 0 | 3.9414 | 40.9978
2007-12-06 08:01 | 12 | 6 | 8 | 340 | 8144 | 28.94 | 7291.167 | 0 | 0 | 7291.167 | Heating | 6433.3827 | 8.5 | 6433.3827 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1286.6765 | 30% | 1 | 51.47% | 0% | 0% | 0% | 17.6873 | 0 | 0 | 0 | 17.6873 | 6564.6762 | 0 | 1312.9352 | 13.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.9618
2007-12-06 09:01 | 12 | 6 | 9 | 340 | 8145 | 30.92 | 5274.3092 | 0 | 0 | 5274.3092 | Heating | 4653.8022 | 8.5 | 4653.8022 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 930.7604 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4748.7778 | 0 | 949.7556 | 9.498% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 10:01 | 12 | 6 | 10 | 340 | 8146 | 32 | 3463.8293 | 0 | 0 | 3463.8293 | Heating | 3056.32 | 8.5 | 3056.32 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 611.264 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3118.6939 | 0 | 623.7388 | 6.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 11:01 | 12 | 6 | 11 | 340 | 8147 | 32 | 2383.5492 | 9.7631 | 9.7631 | 2373.786 | Heating | 2094.5171 | 8.5 | 2094.5171 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 418.9034 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2137.2623 | 0 | 427.4525 | 4.275% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 12:01 | 12 | 6 | 12 | 340 | 8148 | 35.06 | 1488.0759 | 67.9264 | 67.9264 | 1420.1495 | Heating | 1253.0731 | 8.5 | 1253.0731 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 250.6146 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1278.646 | 0 | 255.7292 | 2.557% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 13:01 | 12 | 6 | 13 | 340 | 8149 | 37.94 | 880.7902 | 160.0989 | 160.0989 | 720.6914 | Heating | 635.9041 | 8.5 | 635.9041 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 127.1808 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 648.8818 | 0 | 129.7764 | 1.298% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 14:01 | 12 | 6 | 14 | 340 | 8150 | 37.94 | 712.3349 | 254.4989 | 254.4989 | 457.836 | Heating | 403.9729 | 8.5 | 403.9729 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 80.7946 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 412.2173 | 0 | 82.4435 | 0.8244% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 15:01 | 12 | 6 | 15 | 340 | 8151 | 42.08 | 885.7971 | 220.9216 | 220.9216 | 664.8755 | Heating | 586.6549 | 8.5 | 586.6549 | 0 | 3.8759 | 0 | 0 | 0 | 0 | 8.5 | 0 | 117.331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 598.6274 | 0 | 119.7255 | 1.197% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 16:01 | 12 | 6 | 16 | 340 | 8152 | 41 | 1143.9689 | 113.212 | 113.212 | 1030.7569 | Heating | 909.4914 | 8.5 | 909.4914 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 181.8983 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 928.0524 | 0 | 185.6105 | 1.856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 17:01 | 12 | 6 | 17 | 340 | 8153 | 41 | 1446.0378 | 74.7537 | 74.7537 | 1371.2841 | Heating | 1209.9566 | 8.5 | 1209.9566 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 241.9913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1234.6496 | 0 | 246.9299 | 2.469% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 18:01 | 12 | 6 | 18 | 340 | 8154 | 39.92 | 1808.9825 | 38.7823 | 38.7823 | 1770.2002 | Heating | 1561.9413 | 8.5 | 1561.9413 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 312.3883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1593.8177 | 0 | 318.7635 | 3.188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 19:01 | 12 | 6 | 19 | 340 | 8155 | 39.02 | 2138.4289 | 6.6822 | 6.6822 | 2131.7467 | Heating | 1880.953 | 8.5 | 1880.953 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.1906 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1919.3398 | 0 | 383.868 | 3.839% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 20:01 | 12 | 6 | 20 | 340 | 8156 | 39.02 | 2700.2235 | 0.079964 | 0.079964 | 2700.1436 | Heating | 2382.4796 | 8.5 | 2382.4796 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 476.4959 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2431.1017 | 0 | 486.2203 | 4.862% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 21:01 | 12 | 6 | 21 | 340 | 8157 | 39.02 | 3421.27 | 0 | 0 | 3421.27 | Heating | 3018.7676 | 8.5 | 3018.7676 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 603.7535 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3080.3751 | 0 | 616.075 | 6.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 22:01 | 12 | 6 | 22 | 340 | 8158 | 37.94 | 1019.2108 | 0 | 0 | 1019.2108 | Heating | 899.3036 | 8.5 | 899.3036 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 179.8607 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 917.6568 | 0 | 183.5314 | 1.835% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-06 23:01 | 12 | 6 | 23 | 340 | 8159 | 37.94 | 937.9572 | 0 | 0 | 937.9572 | Heating | 827.6093 | 8.5 | 827.6093 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.5219 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 844.4993 | 0 | 168.8999 | 1.689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 00:01 | 12 | 7 | 0 | 341 | 8160 | 39.02 | 938.7111 | 0 | 0 | 938.7111 | Heating | 828.2745 | 8.5 | 828.2745 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.6549 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 845.1781 | 0 | 169.0356 | 1.69% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 01:01 | 12 | 7 | 1 | 341 | 8161 | 37.04 | 936.6886 | 0 | 0 | 936.6886 | Heating | 826.4899 | 8.5 | 826.4899 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 165.298 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 843.3571 | 0 | 168.6714 | 1.687% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 02:01 | 12 | 7 | 2 | 341 | 8162 | 37.04 | 941.0405 | 0 | 0 | 941.0405 | Heating | 830.3299 | 8.5 | 830.3299 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 166.066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 847.2754 | 0 | 169.4551 | 1.695% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 03:01 | 12 | 7 | 3 | 341 | 8163 | 37.94 | 967.1836 | 0 | 0 | 967.1836 | Heating | 853.3973 | 8.5 | 853.3973 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 170.6795 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 870.8136 | 0 | 174.1627 | 1.742% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 04:01 | 12 | 7 | 4 | 341 | 8164 | 37.94 | 987.7094 | 0 | 0 | 987.7094 | Heating | 871.5083 | 8.5 | 871.5083 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 174.3017 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 889.2942 | 0 | 177.8588 | 1.779% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 05:01 | 12 | 7 | 5 | 341 | 8165 | 37.94 | 1037.6013 | 0 | 0 | 1037.6013 | Heating | 915.5305 | 8.5 | 915.5305 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 183.1061 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 934.2148 | 0 | 186.843 | 1.868% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 06:01 | 12 | 7 | 6 | 341 | 8166 | 33.98 | 1107.4326 | 0 | 0 | 1107.4326 | Heating | 977.1464 | 8.5 | 977.1464 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.4293 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 997.0882 | 0 | 199.4176 | 1.994% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 07:01 | 12 | 7 | 7 | 341 | 8167 | 30.02 | 8457.8627 | 0 | 0 | 8457.8627 | Heating | 7462.82 | 8.5 | 7462.82 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1492.564 | 30% | 1 | 59.7% | 0% | 0% | 0% | 24.8844 | 0 | 0 | 0 | 24.8844 | 7615.1225 | 0 | 1523.0245 | 15.23% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 33.1589
2007-12-07 08:01 | 12 | 7 | 8 | 341 | 8168 | 30.02 | 6285.1313 | 0 | 0 | 6285.1313 | Heating | 5545.7041 | 8.5 | 5545.7041 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1109.1408 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5658.8817 | 0 | 1131.7763 | 11.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 09:01 | 12 | 7 | 9 | 341 | 8169 | 37.04 | 5278.289 | 0 | 0 | 5278.289 | Heating | 4657.3138 | 8.5 | 4657.3138 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 931.4628 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4752.3611 | 0 | 950.4722 | 9.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 10:01 | 12 | 7 | 10 | 341 | 8170 | 39.02 | 4222.5118 | 0 | 0 | 4222.5118 | Heating | 3725.7457 | 8.5 | 3725.7457 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.1491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3801.7813 | 0 | 760.3563 | 7.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 11:01 | 12 | 7 | 11 | 341 | 8171 | 39.02 | 3360.3389 | 0 | 0 | 3360.3389 | Heating | 2965.0049 | 8.5 | 2965.0049 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 593.001 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3025.5152 | 0 | 605.103 | 6.051% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 12:01 | 12 | 7 | 12 | 341 | 8172 | 42.98 | 2796.5488 | 0 | 0 | 2796.5488 | Heating | 2467.5431 | 8.5 | 2467.5431 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 493.5086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2517.9011 | 0 | 503.5802 | 5.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 13:01 | 12 | 7 | 13 | 341 | 8173 | 42.98 | 2459.7887 | 0 | 0 | 2459.7887 | Heating | 2170.4018 | 8.5 | 2170.4018 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 434.0804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2214.6957 | 0 | 442.9391 | 4.429% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 14:01 | 12 | 7 | 14 | 341 | 8174 | 42.98 | 2283.4492 | 0 | 0 | 2283.4492 | Heating | 2014.8081 | 8.5 | 2014.8081 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.9616 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2055.9267 | 0 | 411.1853 | 4.112% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 15:01 | 12 | 7 | 15 | 341 | 8175 | 41 | 2257.8905 | 0 | 0 | 2257.8905 | Heating | 1992.2563 | 8.5 | 1992.2563 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 398.4513 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2032.9146 | 0 | 406.5829 | 4.066% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 16:01 | 12 | 7 | 16 | 341 | 8176 | 37.94 | 2222.1352 | 0 | 0 | 2222.1352 | Heating | 1960.7075 | 8.5 | 1960.7075 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 392.1415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2000.722 | 0 | 400.1444 | 4.001% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 17:01 | 12 | 7 | 17 | 341 | 8177 | 37.94 | 2290.8366 | 0 | 0 | 2290.8366 | Heating | 2021.3264 | 8.5 | 2021.3264 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.2653 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2062.578 | 0 | 412.5156 | 4.125% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 18:01 | 12 | 7 | 18 | 341 | 8178 | 35.06 | 2539.3157 | 0 | 0 | 2539.3157 | Heating | 2240.5727 | 8.5 | 2240.5727 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 448.1145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2286.2986 | 0 | 457.2597 | 4.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 19:01 | 12 | 7 | 19 | 341 | 8179 | 35.06 | 2963.5165 | 0 | 0 | 2963.5165 | Heating | 2614.8675 | 8.5 | 2614.8675 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 522.9735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2668.2322 | 0 | 533.6464 | 5.336% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 20:01 | 12 | 7 | 20 | 341 | 8180 | 35.06 | 3501.1806 | 0 | 0 | 3501.1806 | Heating | 3089.277 | 8.5 | 3089.277 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 617.8554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3152.3235 | 0 | 630.4647 | 6.305% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 21:01 | 12 | 7 | 21 | 341 | 8181 | 33.98 | 3993.2053 | 0 | 0 | 3993.2053 | Heating | 3523.4164 | 8.5 | 3523.4164 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 704.6833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3595.3229 | 0 | 719.0646 | 7.191% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 22:01 | 12 | 7 | 22 | 341 | 8182 | 33.98 | 4723.345 | 0 | 0 | 4723.345 | Heating | 4167.6573 | 8.5 | 4167.6573 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 833.5315 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4252.7116 | 0 | 850.5423 | 8.505% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-07 23:01 | 12 | 7 | 23 | 341 | 8183 | 33.98 | 1123.6012 | 0 | 0 | 1123.6012 | Heating | 991.4128 | 8.5 | 991.4128 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 198.2826 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1011.6457 | 0 | 202.3291 | 2.023% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 00:01 | 12 | 8 | 0 | 342 | 8184 | 33.8 | 1063.7785 | 0 | 0 | 1063.7785 | Heating | 938.6281 | 8.5 | 938.6281 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 187.7256 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 957.7838 | 0 | 191.5568 | 1.916% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 01:01 | 12 | 8 | 1 | 342 | 8185 | 33.08 | 975.167 | 0 | 0 | 975.167 | Heating | 860.4415 | 8.5 | 860.4415 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 172.0883 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 878.0015 | 0 | 175.6003 | 1.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 02:01 | 12 | 8 | 2 | 342 | 8186 | 33.08 | 921.5728 | 0 | 0 | 921.5728 | Heating | 813.1525 | 8.5 | 813.1525 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 162.6305 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 829.7474 | 0 | 165.9495 | 1.659% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 03:01 | 12 | 8 | 3 | 342 | 8187 | 32 | 904.7979 | 0 | 0 | 904.7979 | Heating | 798.3511 | 8.5 | 798.3511 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 159.6702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 814.644 | 0 | 162.9288 | 1.629% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 04:01 | 12 | 8 | 4 | 342 | 8188 | 32 | 884.7677 | 0 | 0 | 884.7677 | Heating | 780.6774 | 8.5 | 780.6774 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.1355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 796.6096 | 0 | 159.3219 | 1.593% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 05:01 | 12 | 8 | 5 | 342 | 8189 | 32 | 877.0029 | 0 | 0 | 877.0029 | Heating | 773.8261 | 8.5 | 773.8261 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.7652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 789.6185 | 0 | 157.9237 | 1.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 06:01 | 12 | 8 | 6 | 342 | 8190 | 33.08 | 873.7415 | 0 | 0 | 873.7415 | Heating | 770.9484 | 8.5 | 770.9484 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 154.1897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 786.682 | 0 | 157.3364 | 1.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 07:01 | 12 | 8 | 7 | 342 | 8191 | 33.08 | 866.628 | 0 | 0 | 866.628 | Heating | 764.6718 | 8.5 | 764.6718 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 152.9344 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 780.2774 | 0 | 156.0555 | 1.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 08:01 | 12 | 8 | 8 | 342 | 8192 | 33.08 | 838.6915 | 0 | 0 | 838.6915 | Heating | 740.0219 | 8.5 | 740.0219 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 148.0044 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 755.1244 | 0 | 151.0249 | 1.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 09:01 | 12 | 8 | 9 | 342 | 8193 | 33.98 | 6053.233 | 0 | 0 | 6053.233 | Heating | 5341.088 | 8.5 | 5341.088 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1068.2176 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5450.0898 | 0 | 1090.018 | 10.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 10:01 | 12 | 8 | 10 | 342 | 8194 | 33.98 | 4360.5152 | 0 | 0 | 4360.5152 | Heating | 3847.5134 | 8.5 | 3847.5134 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 769.5027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3926.0341 | 0 | 785.2068 | 7.852% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 11:01 | 12 | 8 | 11 | 342 | 8195 | 33.98 | 3494.9063 | 0 | 0 | 3494.9063 | Heating | 3083.7408 | 8.5 | 3083.7408 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 616.7482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3146.6743 | 0 | 629.3349 | 6.293% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 12:01 | 12 | 8 | 12 | 342 | 8196 | 35.96 | 3014.2421 | 0 | 0 | 3014.2421 | Heating | 2659.6254 | 8.5 | 2659.6254 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 531.9251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2713.9034 | 0 | 542.7807 | 5.428% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 13:01 | 12 | 8 | 13 | 342 | 8197 | 37.94 | 2397.248 | 0 | 0 | 2397.248 | Heating | 2115.2188 | 8.5 | 2115.2188 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 423.0438 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2158.3865 | 0 | 431.6773 | 4.317% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 14:01 | 12 | 8 | 14 | 342 | 8198 | 37.94 | 2146.2786 | 0 | 0 | 2146.2786 | Heating | 1893.7752 | 8.5 | 1893.7752 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.755 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1932.4237 | 0 | 386.4847 | 3.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 15:01 | 12 | 8 | 15 | 342 | 8199 | 39.92 | 2034.5151 | 0 | 0 | 2034.5151 | Heating | 1795.1604 | 8.5 | 1795.1604 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 359.0321 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1831.7963 | 0 | 366.3593 | 3.664% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 16:01 | 12 | 8 | 16 | 342 | 8200 | 37.94 | 1977.733 | 0 | 0 | 1977.733 | Heating | 1745.0585 | 8.5 | 1745.0585 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 349.0117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1780.6719 | 0 | 356.1344 | 3.561% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 17:01 | 12 | 8 | 17 | 342 | 8201 | 37.94 | 1996.5744 | 0 | 0 | 1996.5744 | Heating | 1761.6833 | 8.5 | 1761.6833 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 352.3367 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1797.636 | 0 | 359.5272 | 3.595% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 18:01 | 12 | 8 | 18 | 342 | 8202 | 33.08 | 3111.5533 | 0 | 0 | 3111.5533 | Heating | 2745.4882 | 8.5 | 2745.4882 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 549.0976 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2801.5185 | 0 | 560.3037 | 5.603% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 19:01 | 12 | 8 | 19 | 342 | 8203 | 33.98 | 3486.8604 | 0 | 0 | 3486.8604 | Heating | 3076.6415 | 8.5 | 3076.6415 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 615.3283 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3139.4301 | 0 | 627.886 | 6.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 20:01 | 12 | 8 | 20 | 342 | 8204 | 33.98 | 622.8981 | 0 | 0 | 622.8981 | Heating | 549.6159 | 8.5 | 549.6159 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 109.9232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 560.8326 | 0 | 112.1665 | 1.122% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 21:01 | 12 | 8 | 21 | 342 | 8205 | 33.98 | 654.9541 | 0 | 0 | 654.9541 | Heating | 577.9007 | 8.5 | 577.9007 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 115.5801 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 589.6946 | 0 | 117.9389 | 1.179% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 22:01 | 12 | 8 | 22 | 342 | 8206 | 33.98 | 691.3239 | 0 | 0 | 691.3239 | Heating | 609.9917 | 8.5 | 609.9917 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 121.9983 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 622.4405 | 0 | 124.4881 | 1.245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-08 23:01 | 12 | 8 | 23 | 342 | 8207 | 33.98 | 791.0182 | 0 | 0 | 791.0182 | Heating | 697.9573 | 8.5 | 697.9573 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 139.5915 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 712.2013 | 0 | 142.4403 | 1.424% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 00:01 | 12 | 9 | 0 | 343 | 8208 | 35.96 | 914.9569 | 0 | 0 | 914.9569 | Heating | 807.3149 | 8.5 | 807.3149 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 161.463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 823.7907 | 0 | 164.7581 | 1.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 01:01 | 12 | 9 | 1 | 343 | 8209 | 33.98 | 1036.7047 | 0 | 0 | 1036.7047 | Heating | 914.7394 | 8.5 | 914.7394 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 182.9479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 933.4076 | 0 | 186.6815 | 1.867% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 02:01 | 12 | 9 | 2 | 343 | 8210 | 33.98 | 1142.2256 | 0 | 0 | 1142.2256 | Heating | 1007.8462 | 8.5 | 1007.8462 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 201.5692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1028.4144 | 0 | 205.6829 | 2.057% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 03:01 | 12 | 9 | 3 | 343 | 8211 | 33.98 | 1239.6466 | 0 | 0 | 1239.6466 | Heating | 1093.8058 | 8.5 | 1093.8058 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 218.7612 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1116.1284 | 0 | 223.2257 | 2.232% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 04:01 | 12 | 9 | 4 | 343 | 8212 | 33.98 | 1333.7268 | 0 | 0 | 1333.7268 | Heating | 1176.8177 | 8.5 | 1176.8177 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 235.3635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1200.8344 | 0 | 240.1669 | 2.402% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 05:01 | 12 | 9 | 5 | 343 | 8213 | 33.98 | 1407.9298 | 0 | 0 | 1407.9298 | Heating | 1242.291 | 8.5 | 1242.291 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 248.4582 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1267.6439 | 0 | 253.5288 | 2.535% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 06:01 | 12 | 9 | 6 | 343 | 8214 | 32 | 1451.1094 | 0 | 0 | 1451.1094 | Heating | 1280.3906 | 8.5 | 1280.3906 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 256.0781 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1306.521 | 0 | 261.3042 | 2.613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 07:01 | 12 | 9 | 7 | 343 | 8215 | 32 | 9350.1923 | 0 | 0 | 9350.1923 | Heating | 8250.1697 | 8.5 | 8250.1697 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1650.0339 | 33% | 1 | 66% | 0% | 0% | 0% | 31.3411 | 0 | 0 | 0 | 31.3411 | 8418.5405 | 0 | 1683.7081 | 16.84% | 1 | 33.67% | 0% | 0% | 3.3335 | 0 | 0 | 3.3335 | 34.6746
2007-12-09 08:01 | 12 | 9 | 8 | 343 | 8216 | 32 | 7171.4395 | 0 | 0 | 7171.4395 | Heating | 6327.7408 | 8.5 | 6327.7408 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1265.5482 | 30% | 1 | 50.62% | 0% | 0% | 0% | 17.0264 | 0 | 0 | 0 | 17.0264 | 6456.8783 | 0 | 1291.3757 | 12.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3009
2007-12-09 09:01 | 12 | 9 | 9 | 343 | 8217 | 32 | 5914.9365 | 0 | 0 | 5914.9365 | Heating | 5219.0616 | 8.5 | 5219.0616 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1043.8123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5325.5731 | 0 | 1065.1146 | 10.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 10:01 | 12 | 9 | 10 | 343 | 8218 | 33.8 | 4957.6126 | 0 | 0 | 4957.6126 | Heating | 4374.364 | 8.5 | 4374.364 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 874.8728 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4463.6368 | 0 | 892.7274 | 8.927% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 11:01 | 12 | 9 | 11 | 343 | 8219 | 33.98 | 4538.0985 | 0 | 0 | 4538.0985 | Heating | 4004.2046 | 8.5 | 4004.2046 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 800.8409 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4085.923 | 0 | 817.1846 | 8.172% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 12:01 | 12 | 9 | 12 | 343 | 8220 | 39.02 | 4225.2817 | 0 | 0 | 4225.2817 | Heating | 3728.1898 | 8.5 | 3728.1898 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3804.2753 | 0 | 760.8551 | 7.609% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 13:01 | 12 | 9 | 13 | 343 | 8221 | 39.02 | 4114.2944 | 0 | 0 | 4114.2944 | Heating | 3630.2597 | 8.5 | 3630.2597 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 726.0519 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3704.3467 | 0 | 740.8693 | 7.409% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 14:01 | 12 | 9 | 14 | 343 | 8222 | 39.02 | 3983.1729 | 0 | 0 | 3983.1729 | Heating | 3514.5643 | 8.5 | 3514.5643 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 702.9129 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3586.2901 | 0 | 717.258 | 7.173% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 15:01 | 12 | 9 | 15 | 343 | 8223 | 37.04 | 3897.7897 | 0 | 0 | 3897.7897 | Heating | 3439.2262 | 8.5 | 3439.2262 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 687.8452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3509.4145 | 0 | 701.8829 | 7.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 16:01 | 12 | 9 | 16 | 343 | 8224 | 35.96 | 3840.7293 | 0 | 0 | 3840.7293 | Heating | 3388.8788 | 8.5 | 3388.8788 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 677.7758 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3458.0396 | 0 | 691.6079 | 6.916% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 17:01 | 12 | 9 | 17 | 343 | 8225 | 35.96 | 4025.0803 | 0 | 0 | 4025.0803 | Heating | 3551.5415 | 8.5 | 3551.5415 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 710.3083 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3624.0219 | 0 | 724.8044 | 7.248% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 18:01 | 12 | 9 | 18 | 343 | 8226 | 32 | 4393.7937 | 0 | 0 | 4393.7937 | Heating | 3876.8768 | 8.5 | 3876.8768 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 775.3754 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3955.9967 | 0 | 791.1993 | 7.912% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 19:01 | 12 | 9 | 19 | 343 | 8227 | 32 | 4635.4869 | 0 | 0 | 4635.4869 | Heating | 4090.1355 | 8.5 | 4090.1355 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 818.0271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4173.6076 | 0 | 834.7215 | 8.347% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 20:01 | 12 | 9 | 20 | 343 | 8228 | 32 | 4886.4364 | 0 | 0 | 4886.4364 | Heating | 4311.5615 | 8.5 | 4311.5615 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 862.3123 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4399.5526 | 0 | 879.9105 | 8.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 21:01 | 12 | 9 | 21 | 343 | 8229 | 32 | 5204.63 | 0 | 0 | 5204.63 | Heating | 4592.3206 | 8.5 | 4592.3206 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 918.4641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4686.0414 | 0 | 937.2083 | 9.372% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 22:01 | 12 | 9 | 22 | 343 | 8230 | 32 | 1586.0497 | 0 | 0 | 1586.0497 | Heating | 1399.4556 | 8.5 | 1399.4556 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 279.8911 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1428.0159 | 0 | 285.6032 | 2.856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-09 23:01 | 12 | 9 | 23 | 343 | 8231 | 32 | 1446.9128 | 0 | 0 | 1446.9128 | Heating | 1276.6877 | 8.5 | 1276.6877 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 255.3375 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1302.7426 | 0 | 260.5485 | 2.605% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 00:01 | 12 | 10 | 0 | 344 | 8232 | 30.92 | 1705.1906 | 0 | 0 | 1705.1906 | Heating | 1504.5799 | 8.5 | 1504.5799 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300.916 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1535.2856 | 0 | 307.0571 | 3.071% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 01:01 | 12 | 10 | 1 | 344 | 8233 | 32 | 1844.8746 | 0 | 0 | 1844.8746 | Heating | 1627.8305 | 8.5 | 1627.8305 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 325.5661 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1661.0516 | 0 | 332.2103 | 3.322% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 02:01 | 12 | 10 | 2 | 344 | 8234 | 32 | 2005.4616 | 0 | 0 | 2005.4616 | Heating | 1769.5249 | 8.5 | 1769.5249 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 353.905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1805.6377 | 0 | 361.1275 | 3.611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 03:01 | 12 | 10 | 3 | 344 | 8235 | 30.02 | 2178.9127 | 0 | 0 | 2178.9127 | Heating | 1922.57 | 8.5 | 1922.57 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.514 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1961.8062 | 0 | 392.3612 | 3.924% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 04:01 | 12 | 10 | 4 | 344 | 8236 | 30.92 | 2350.7042 | 0 | 0 | 2350.7042 | Heating | 2074.1507 | 8.5 | 2074.1507 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 414.8301 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2116.4803 | 0 | 423.2961 | 4.233% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 05:01 | 12 | 10 | 5 | 344 | 8237 | 30.92 | 2437.8869 | 0 | 0 | 2437.8869 | Heating | 2151.0767 | 8.5 | 2151.0767 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 430.2153 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2194.9762 | 0 | 438.9952 | 4.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 06:01 | 12 | 10 | 6 | 344 | 8238 | 28.04 | 2450.0989 | 0 | 0 | 2450.0989 | Heating | 2161.852 | 8.5 | 2161.852 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 432.3704 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2205.9714 | 0 | 441.1943 | 4.412% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 07:01 | 12 | 10 | 7 | 344 | 8239 | 26.96 | 12784.0661 | 0 | 0 | 12784.0661 | Heating | 11280.0584 | 8.5 | 11280.0584 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2256.0117 | 45.12% | 1 | 90.24% | 0% | 0% | 0% | 64.3526 | 0 | 0 | 0 | 64.3526 | 11510.2636 | 0 | 2302.0527 | 23.02% | 1 | 46.04% | 0% | 0% | 6.8446 | 0 | 0 | 6.8446 | 71.1972
2007-12-10 08:01 | 12 | 10 | 8 | 344 | 8240 | 26.96 | 9953.2195 | 0 | 0 | 9953.2195 | Heating | 8782.2525 | 8.5 | 8782.2525 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1756.4505 | 35.13% | 1 | 70.26% | 0% | 0% | 0% | 36.1863 | 0 | 0 | 0 | 36.1863 | 8961.4821 | 0 | 1792.2964 | 17.92% | 1 | 35.85% | 0% | 0% | 3.8488 | 0 | 0 | 3.8488 | 40.035
2007-12-10 09:01 | 12 | 10 | 9 | 344 | 8241 | 28.94 | 8366.9749 | 0 | 0 | 8366.9749 | Heating | 7382.6249 | 8.5 | 7382.6249 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1476.525 | 30% | 1 | 59.06% | 0% | 0% | 0% | 24.2736 | 0 | 0 | 0 | 24.2736 | 7533.2907 | 0 | 1506.6581 | 15.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.5482
2007-12-10 10:01 | 12 | 10 | 10 | 344 | 8242 | 30.02 | 7014.168 | 0 | 0 | 7014.168 | Heating | 6188.9718 | 8.5 | 6188.9718 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1237.7944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6315.2773 | 0 | 1263.0555 | 12.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 11:01 | 12 | 10 | 11 | 344 | 8243 | 30.02 | 6245.0408 | 0 | 0 | 6245.0408 | Heating | 5510.3301 | 8.5 | 5510.3301 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1102.066 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5622.7859 | 0 | 1124.5572 | 11.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 12:01 | 12 | 10 | 12 | 344 | 8244 | 32 | 5637.7102 | 0 | 0 | 5637.7102 | Heating | 4974.4502 | 8.5 | 4974.4502 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 994.89 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5075.9696 | 0 | 1015.1939 | 10.15% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 13:01 | 12 | 10 | 13 | 344 | 8245 | 30.02 | 5326.6213 | 0 | 0 | 5326.6213 | Heating | 4699.96 | 8.5 | 4699.96 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 939.992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4795.8775 | 0 | 959.1755 | 9.592% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 14:01 | 12 | 10 | 14 | 344 | 8246 | 30.02 | 5253.3692 | 0 | 0 | 5253.3692 | Heating | 4635.3258 | 8.5 | 4635.3258 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 927.0652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4729.9243 | 0 | 945.9849 | 9.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 15:01 | 12 | 10 | 15 | 344 | 8247 | 28.94 | 5291.6139 | 0 | 0 | 5291.6139 | Heating | 4669.0711 | 8.5 | 4669.0711 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 933.8142 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4764.3583 | 0 | 952.8717 | 9.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 16:01 | 12 | 10 | 16 | 344 | 8248 | 28.04 | 5392.8115 | 0 | 0 | 5392.8115 | Heating | 4758.3631 | 8.5 | 4758.3631 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 951.6726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4855.4726 | 0 | 971.0945 | 9.711% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 17:01 | 12 | 10 | 17 | 344 | 8249 | 28.04 | 5761.5992 | 0 | 0 | 5761.5992 | Heating | 5083.764 | 8.5 | 5083.764 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1016.7528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5187.5143 | 0 | 1037.5029 | 10.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 18:01 | 12 | 10 | 18 | 344 | 8250 | 26.96 | 6232.6671 | 0 | 0 | 6232.6671 | Heating | 5499.4121 | 8.5 | 5499.4121 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1099.8824 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5611.645 | 0 | 1122.329 | 11.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 19:01 | 12 | 10 | 19 | 344 | 8251 | 26.06 | 6572.3653 | 0 | 0 | 6572.3653 | Heating | 5799.1459 | 8.5 | 5799.1459 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1159.8292 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5917.4958 | 0 | 1183.4992 | 11.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 20:01 | 12 | 10 | 20 | 344 | 8252 | 26.06 | 6833.7251 | 0 | 0 | 6833.7251 | Heating | 6029.7575 | 8.5 | 6029.7575 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1205.9515 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6152.8137 | 0 | 1230.5627 | 12.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 21:01 | 12 | 10 | 21 | 344 | 8253 | 23 | 7029.1535 | 0 | 0 | 7029.1535 | Heating | 6202.1943 | 8.5 | 6202.1943 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1240.4389 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6328.7697 | 0 | 1265.7539 | 12.66% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 22:01 | 12 | 10 | 22 | 344 | 8254 | 21.92 | 2155.0976 | 0 | 0 | 2155.0976 | Heating | 1901.5567 | 8.5 | 1901.5567 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.3113 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1940.364 | 0 | 388.0728 | 3.881% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-10 23:01 | 12 | 10 | 23 | 344 | 8255 | 21.92 | 2144.8274 | 0 | 0 | 2144.8274 | Heating | 1892.4948 | 8.5 | 1892.4948 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.499 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1931.1171 | 0 | 386.2234 | 3.862% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 00:01 | 12 | 11 | 0 | 345 | 8256 | 19.04 | 2303.4933 | 0 | 0 | 2303.4933 | Heating | 2032.4941 | 8.5 | 2032.4941 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 406.4988 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2073.9735 | 0 | 414.7947 | 4.148% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 01:01 | 12 | 11 | 1 | 345 | 8257 | 19.04 | 2387.6719 | 0 | 0 | 2387.6719 | Heating | 2106.7693 | 8.5 | 2106.7693 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.3539 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2149.7646 | 0 | 429.9529 | 4.3% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 02:01 | 12 | 11 | 2 | 345 | 8258 | 19.04 | 2457.1175 | 0 | 0 | 2457.1175 | Heating | 2168.0448 | 8.5 | 2168.0448 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 433.609 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2212.2906 | 0 | 442.4581 | 4.425% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 03:01 | 12 | 11 | 3 | 345 | 8259 | 17.96 | 2517.1808 | 0 | 0 | 2517.1808 | Heating | 2221.0419 | 8.5 | 2221.0419 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 444.2084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2266.3693 | 0 | 453.2739 | 4.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 04:01 | 12 | 11 | 4 | 345 | 8260 | 17.96 | 2565.9732 | 0 | 0 | 2565.9732 | Heating | 2264.094 | 8.5 | 2264.094 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 452.8188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2310.3 | 0 | 462.06 | 4.621% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 05:01 | 12 | 11 | 5 | 345 | 8261 | 17.96 | 2646.2388 | 0 | 0 | 2646.2388 | Heating | 2334.9166 | 8.5 | 2334.9166 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 466.9833 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2382.5679 | 0 | 476.5136 | 4.765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 06:01 | 12 | 11 | 6 | 345 | 8262 | 19.94 | 2728.6522 | 0 | 0 | 2728.6522 | Heating | 2407.6343 | 8.5 | 2407.6343 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 481.5269 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2456.7697 | 0 | 491.3539 | 4.914% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 07:01 | 12 | 11 | 7 | 345 | 8263 | 19.94 | 13761.5236 | 0 | 0 | 13761.5236 | Heating | 12142.5208 | 8.5 | 12142.5208 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2428.5042 | 48.57% | 1 | 97.14% | 0% | 0% | 0% | 76.2361 | 0 | 0 | 0 | 76.2361 | 12390.3273 | 0 | 2478.0655 | 24.78% | 1 | 49.56% | 0% | 0% | 8.1085 | 0 | 0 | 8.1085 | 84.3446
2007-12-11 08:01 | 12 | 11 | 8 | 345 | 8264 | 19.94 | 11221.6755 | 0 | 0 | 11221.6755 | Heating | 9901.4784 | 8.5 | 9901.4784 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1980.2957 | 39.61% | 1 | 79.21% | 0% | 0% | 0% | 47.6826 | 0 | 0 | 0 | 47.6826 | 10103.5494 | 0 | 2020.7099 | 20.21% | 1 | 40.41% | 0% | 0% | 5.0716 | 0 | 0 | 5.0716 | 52.7542
2007-12-11 09:01 | 12 | 11 | 9 | 345 | 8265 | 21.92 | 9372.1441 | 0 | 0 | 9372.1441 | Heating | 8269.5389 | 8.5 | 8269.5389 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1653.9078 | 33.08% | 1 | 66.16% | 0% | 0% | 0% | 31.5106 | 0 | 0 | 0 | 31.5106 | 8438.305 | 0 | 1687.661 | 16.88% | 1 | 33.75% | 0% | 0% | 3.3515 | 0 | 0 | 3.3515 | 34.8621
2007-12-11 10:01 | 12 | 11 | 10 | 345 | 8266 | 24.08 | 7812.9004 | 0 | 0 | 7812.9004 | Heating | 6893.7356 | 8.5 | 6893.7356 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1378.7471 | 30% | 1 | 55.15% | 0% | 0% | 0% | 20.7346 | 0 | 0 | 0 | 20.7346 | 7034.4241 | 0 | 1406.8848 | 14.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.0091
2007-12-11 11:01 | 12 | 11 | 11 | 345 | 8267 | 24.08 | 6842.0679 | 0 | 0 | 6842.0679 | Heating | 6037.1188 | 8.5 | 6037.1188 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1207.4238 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6160.3253 | 0 | 1232.0651 | 12.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 12:01 | 12 | 11 | 12 | 345 | 8268 | 26.96 | 5956.0363 | 0 | 0 | 5956.0363 | Heating | 5255.3261 | 8.5 | 5255.3261 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1051.0652 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5362.5777 | 0 | 1072.5155 | 10.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 13:01 | 12 | 11 | 13 | 345 | 8269 | 26.06 | 5270.3409 | 0 | 0 | 5270.3409 | Heating | 4650.3008 | 8.5 | 4650.3008 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 930.0602 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4745.2049 | 0 | 949.041 | 9.49% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 14:01 | 12 | 11 | 14 | 345 | 8270 | 26.06 | 4945.7601 | 0 | 0 | 4945.7601 | Heating | 4363.906 | 8.5 | 4363.906 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 872.7812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4452.9653 | 0 | 890.5931 | 8.906% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 15:01 | 12 | 11 | 15 | 345 | 8271 | 26.96 | 4946.909 | 0 | 0 | 4946.909 | Heating | 4364.9197 | 8.5 | 4364.9197 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 872.9839 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4453.9997 | 0 | 890.7999 | 8.908% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 16:01 | 12 | 11 | 16 | 345 | 8272 | 26.96 | 4964.6338 | 0 | 0 | 4964.6338 | Heating | 4380.5593 | 8.5 | 4380.5593 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 876.1119 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4469.9584 | 0 | 893.9917 | 8.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 17:01 | 12 | 11 | 17 | 345 | 8273 | 26.96 | 5400.7398 | 0 | 0 | 5400.7398 | Heating | 4765.3586 | 8.5 | 4765.3586 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 953.0717 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4862.6108 | 0 | 972.5222 | 9.725% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 18:01 | 12 | 11 | 18 | 345 | 8274 | 23 | 6121.4023 | 0 | 0 | 6121.4023 | Heating | 5401.2374 | 8.5 | 5401.2374 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1080.2475 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5511.4667 | 0 | 1102.2933 | 11.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 19:01 | 12 | 11 | 19 | 345 | 8275 | 19.04 | 6649.9293 | 0 | 0 | 6649.9293 | Heating | 5867.5846 | 8.5 | 5867.5846 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1173.5169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5987.3313 | 0 | 1197.4663 | 11.97% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 20:01 | 12 | 11 | 20 | 345 | 8276 | 19.04 | 7178.738 | 0 | 0 | 7178.738 | Heating | 6334.1806 | 8.5 | 6334.1806 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1266.8361 | 30% | 1 | 50.67% | 0% | 0% | 0% | 17.0662 | 0 | 0 | 0 | 17.0662 | 6463.4496 | 0 | 1292.6899 | 12.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3408
2007-12-11 21:01 | 12 | 11 | 21 | 345 | 8277 | 19.04 | 7770.6468 | 0 | 0 | 7770.6468 | Heating | 6856.4531 | 8.5 | 6856.4531 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1371.2906 | 30% | 1 | 54.85% | 0% | 0% | 0% | 20.4776 | 0 | 0 | 0 | 20.4776 | 6996.3807 | 0 | 1399.2761 | 13.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 28.7521
2007-12-11 22:01 | 12 | 11 | 22 | 345 | 8278 | 17.06 | 2454.7601 | 0 | 0 | 2454.7601 | Heating | 2165.9648 | 8.5 | 2165.9648 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 433.193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2210.1682 | 0 | 442.0336 | 4.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-11 23:01 | 12 | 11 | 23 | 345 | 8279 | 17.06 | 2569.2987 | 0 | 0 | 2569.2987 | Heating | 2267.0283 | 8.5 | 2267.0283 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 453.4057 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2313.2942 | 0 | 462.6588 | 4.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 00:01 | 12 | 12 | 0 | 346 | 8280 | 17.96 | 2686.4833 | 0 | 0 | 2686.4833 | Heating | 2370.4265 | 8.5 | 2370.4265 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 474.0853 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2418.8025 | 0 | 483.7605 | 4.838% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 01:01 | 12 | 12 | 1 | 346 | 8281 | 17.96 | 2652.9822 | 0 | 0 | 2652.9822 | Heating | 2340.8667 | 8.5 | 2340.8667 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 468.1733 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2388.6395 | 0 | 477.7279 | 4.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 02:01 | 12 | 12 | 2 | 346 | 8282 | 17.96 | 2641.4917 | 0 | 0 | 2641.4917 | Heating | 2330.728 | 8.5 | 2330.728 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 466.1456 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2378.2939 | 0 | 475.6588 | 4.757% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 03:01 | 12 | 12 | 3 | 346 | 8283 | 17.06 | 2654.9546 | 0 | 0 | 2654.9546 | Heating | 2342.607 | 8.5 | 2342.607 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 468.5214 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2390.4153 | 0 | 478.0831 | 4.781% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 04:01 | 12 | 12 | 4 | 346 | 8284 | 15.08 | 2659.3001 | 0 | 0 | 2659.3001 | Heating | 2346.4412 | 8.5 | 2346.4412 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 469.2882 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2394.3278 | 0 | 478.8656 | 4.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 05:01 | 12 | 12 | 5 | 346 | 8285 | 15.08 | 2664.6264 | 0 | 0 | 2664.6264 | Heating | 2351.1409 | 8.5 | 2351.1409 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 470.2282 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2399.1234 | 0 | 479.8247 | 4.798% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 06:01 | 12 | 12 | 6 | 346 | 8286 | 15.98 | 2660.9429 | 0 | 0 | 2660.9429 | Heating | 2347.8908 | 8.5 | 2347.8908 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 469.5782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2395.8069 | 0 | 479.1614 | 4.792% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 07:01 | 12 | 12 | 7 | 346 | 8287 | 15.08 | 13434.5948 | 0 | 0 | 13434.5948 | Heating | 11854.0542 | 8.5 | 11854.0542 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2370.8108 | 47.42% | 1 | 94.83% | 0% | 0% | 0% | 72.1346 | 0 | 0 | 0 | 72.1346 | 12095.9737 | 0 | 2419.1947 | 24.19% | 1 | 48.38% | 0% | 0% | 7.6723 | 0 | 0 | 7.6723 | 79.8069
2007-12-12 08:01 | 12 | 12 | 8 | 346 | 8288 | 15.08 | 10755.5018 | 0 | 0 | 10755.5018 | Heating | 9490.1487 | 8.5 | 9490.1487 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1898.0297 | 37.96% | 1 | 75.92% | 0% | 0% | 0% | 43.2492 | 0 | 0 | 0 | 43.2492 | 9683.8252 | 0 | 1936.765 | 19.37% | 1 | 38.74% | 0% | 0% | 4.6 | 0 | 0 | 4.6 | 47.8492
2007-12-12 09:01 | 12 | 12 | 9 | 346 | 8289 | 21.92 | 8907.1286 | 0 | 0 | 8907.1286 | Heating | 7859.2312 | 8.5 | 7859.2312 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1571.8462 | 31.44% | 1 | 62.87% | 0% | 0% | 0% | 28.0301 | 0 | 0 | 0 | 28.0301 | 8019.6236 | 0 | 1603.9247 | 16.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.3046
2007-12-12 10:01 | 12 | 12 | 10 | 346 | 8290 | 24.98 | 7411.631 | 0 | 0 | 7411.631 | Heating | 6539.6744 | 8.5 | 6539.6744 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1307.9349 | 30% | 1 | 52.32% | 0% | 0% | 0% | 18.3666 | 0 | 0 | 0 | 18.3666 | 6673.1371 | 0 | 1334.6274 | 13.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.6412
2007-12-12 11:01 | 12 | 12 | 11 | 346 | 8291 | 24.98 | 6536.1516 | 0 | 0 | 6536.1516 | Heating | 5767.1926 | 8.5 | 5767.1926 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1153.4385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5884.8904 | 0 | 1176.9781 | 11.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 12:01 | 12 | 12 | 12 | 346 | 8292 | 30.02 | 5813.0362 | 0 | 0 | 5813.0362 | Heating | 5129.1496 | 8.5 | 5129.1496 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1025.8299 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5233.8261 | 0 | 1046.7652 | 10.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 13:01 | 12 | 12 | 13 | 346 | 8293 | 30.02 | 5346.2174 | 0 | 0 | 5346.2174 | Heating | 4717.2507 | 8.5 | 4717.2507 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 943.4501 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4813.5211 | 0 | 962.7042 | 9.627% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 14:01 | 12 | 12 | 14 | 346 | 8294 | 30.02 | 4990.8389 | 0 | 0 | 4990.8389 | Heating | 4403.6814 | 8.5 | 4403.6814 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 880.7363 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4493.5524 | 0 | 898.7105 | 8.987% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 15:01 | 12 | 12 | 15 | 346 | 8295 | 30.02 | 4776.2562 | 0 | 0 | 4776.2562 | Heating | 4214.3437 | 8.5 | 4214.3437 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 842.8687 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4300.3507 | 0 | 860.0701 | 8.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 16:01 | 12 | 12 | 16 | 346 | 8296 | 30.02 | 4622.153 | 0 | 0 | 4622.153 | Heating | 4078.3703 | 8.5 | 4078.3703 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 815.6741 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4161.6023 | 0 | 832.3205 | 8.323% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 17:01 | 12 | 12 | 17 | 346 | 8297 | 30.02 | 4630.1005 | 0 | 0 | 4630.1005 | Heating | 4085.3828 | 8.5 | 4085.3828 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 817.0766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4168.758 | 0 | 833.7516 | 8.338% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 18:01 | 12 | 12 | 18 | 346 | 8298 | 28.04 | 4690.5759 | 0 | 0 | 4690.5759 | Heating | 4138.7434 | 8.5 | 4138.7434 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 827.7487 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4223.2076 | 0 | 844.6415 | 8.446% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 19:01 | 12 | 12 | 19 | 346 | 8299 | 26.96 | 4736.0972 | 0 | 0 | 4736.0972 | Heating | 4178.9093 | 8.5 | 4178.9093 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 835.7819 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4264.1932 | 0 | 852.8386 | 8.528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 20:01 | 12 | 12 | 20 | 346 | 8300 | 26.96 | 4873.9991 | 0 | 0 | 4873.9991 | Heating | 4300.5874 | 8.5 | 4300.5874 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 860.1175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4388.3545 | 0 | 877.6709 | 8.777% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 21:01 | 12 | 12 | 21 | 346 | 8301 | 26.96 | 5129.5818 | 0 | 0 | 5129.5818 | Heating | 4526.1016 | 8.5 | 4526.1016 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 905.2203 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4618.471 | 0 | 923.6942 | 9.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 22:01 | 12 | 12 | 22 | 346 | 8302 | 26.96 | 1500.6825 | 0 | 0 | 1500.6825 | Heating | 1324.1316 | 8.5 | 1324.1316 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 264.8263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1351.1547 | 0 | 270.2309 | 2.702% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-12 23:01 | 12 | 12 | 23 | 346 | 8303 | 26.96 | 1284.4164 | 0 | 0 | 1284.4164 | Heating | 1133.3086 | 8.5 | 1133.3086 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 226.6617 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1156.4373 | 0 | 231.2875 | 2.313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 00:01 | 12 | 13 | 0 | 347 | 8304 | 28.4 | 1473.7253 | 0 | 0 | 1473.7253 | Heating | 1300.3459 | 8.5 | 1300.3459 | 0 | 3.1678 | 0 | 0 | 0 | 0 | 8.5 | 0 | 260.0692 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1326.8836 | 0 | 265.3767 | 2.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 01:01 | 12 | 13 | 1 | 347 | 8305 | 28.04 | 1577.8511 | 0 | 0 | 1577.8511 | Heating | 1392.2216 | 8.5 | 1392.2216 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 278.4443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1420.6342 | 0 | 284.1268 | 2.841% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 02:01 | 12 | 13 | 2 | 347 | 8306 | 28.04 | 1630.3862 | 0 | 0 | 1630.3862 | Heating | 1438.576 | 8.5 | 1438.576 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 287.7152 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1467.9347 | 0 | 293.5869 | 2.936% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 03:01 | 12 | 13 | 3 | 347 | 8307 | 28.94 | 1659.8579 | 0 | 0 | 1659.8579 | Heating | 1464.5805 | 8.5 | 1464.5805 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.9161 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1494.4699 | 0 | 298.894 | 2.989% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 04:01 | 12 | 13 | 4 | 347 | 8308 | 28.04 | 1675.2273 | 0 | 0 | 1675.2273 | Heating | 1478.1418 | 8.5 | 1478.1418 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 295.6284 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1508.3079 | 0 | 301.6616 | 3.017% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 05:01 | 12 | 13 | 5 | 347 | 8309 | 28.04 | 1695.2809 | 0 | 0 | 1695.2809 | Heating | 1495.8361 | 8.5 | 1495.8361 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 299.1672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1526.3634 | 0 | 305.2727 | 3.053% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 06:01 | 12 | 13 | 6 | 347 | 8310 | 30.02 | 1708.8668 | 0 | 0 | 1708.8668 | Heating | 1507.8237 | 8.5 | 1507.8237 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.5647 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1538.5956 | 0 | 307.7191 | 3.077% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 07:01 | 12 | 13 | 7 | 347 | 8311 | 30.92 | 10506.727 | 0 | 0 | 10506.727 | Heating | 9270.6414 | 8.5 | 9270.6414 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1854.1283 | 37.08% | 1 | 74.17% | 0% | 0% | 0% | 40.9829 | 0 | 0 | 0 | 40.9829 | 9459.8382 | 0 | 1891.9676 | 18.92% | 1 | 37.84% | 0% | 0% | 4.359 | 0 | 0 | 4.359 | 45.3419
2007-12-13 08:01 | 12 | 13 | 8 | 347 | 8312 | 32 | 7873.2674 | 0 | 0 | 7873.2674 | Heating | 6947.0007 | 8.5 | 6947.0007 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1389.4001 | 30% | 1 | 55.58% | 0% | 0% | 0% | 21.1049 | 0 | 0 | 0 | 21.1049 | 7088.7762 | 0 | 1417.7552 | 14.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.3795
2007-12-13 09:01 | 12 | 13 | 9 | 347 | 8313 | 33.98 | 6530.3544 | 0 | 0 | 6530.3544 | Heating | 5762.0774 | 8.5 | 5762.0774 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1152.4155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5879.6708 | 0 | 1175.9342 | 11.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 10:01 | 12 | 13 | 10 | 347 | 8314 | 35.6 | 5361.3773 | 0 | 0 | 5361.3773 | Heating | 4730.627 | 8.5 | 4730.627 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 946.1254 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4827.1704 | 0 | 965.4341 | 9.654% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 11:01 | 12 | 13 | 11 | 347 | 8315 | 35.06 | 4723.9987 | 0 | 0 | 4723.9987 | Heating | 4168.2341 | 8.5 | 4168.2341 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 833.6468 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4253.3001 | 0 | 850.66 | 8.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 12:01 | 12 | 13 | 12 | 347 | 8316 | 37.04 | 4222.4517 | 0 | 0 | 4222.4517 | Heating | 3725.6926 | 8.5 | 3725.6926 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 745.1385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3801.7272 | 0 | 760.3454 | 7.603% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 13:01 | 12 | 13 | 13 | 347 | 8317 | 37.04 | 3937.5791 | 0 | 0 | 3937.5791 | Heating | 3474.3345 | 8.5 | 3474.3345 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 694.8669 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3545.2393 | 0 | 709.0479 | 7.09% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 14:01 | 12 | 13 | 14 | 347 | 8318 | 37.04 | 3613.5381 | 0 | 0 | 3613.5381 | Heating | 3188.4159 | 8.5 | 3188.4159 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 637.6832 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3253.4857 | 0 | 650.6971 | 6.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 15:01 | 12 | 13 | 15 | 347 | 8319 | 37.94 | 3294.1948 | 0 | 0 | 3294.1948 | Heating | 2906.6425 | 8.5 | 2906.6425 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 581.3285 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2965.9617 | 0 | 593.1923 | 5.932% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 16:01 | 12 | 13 | 16 | 347 | 8320 | 39.02 | 3051.5206 | 0 | 0 | 3051.5206 | Heating | 2692.5182 | 8.5 | 2692.5182 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 538.5036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2747.4676 | 0 | 549.4935 | 5.495% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 17:01 | 12 | 13 | 17 | 347 | 8321 | 39.02 | 3068.5369 | 0 | 0 | 3068.5369 | Heating | 2707.5326 | 8.5 | 2707.5326 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 541.5065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2762.7884 | 0 | 552.5577 | 5.526% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 18:01 | 12 | 13 | 18 | 347 | 8322 | 37.04 | 3246.297 | 0 | 0 | 3246.297 | Heating | 2864.3797 | 8.5 | 2864.3797 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 572.8759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2922.8364 | 0 | 584.5673 | 5.846% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 19:01 | 12 | 13 | 19 | 347 | 8323 | 37.94 | 3350.4982 | 0 | 0 | 3350.4982 | Heating | 2956.3219 | 8.5 | 2956.3219 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 591.2644 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3016.655 | 0 | 603.331 | 6.033% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 20:01 | 12 | 13 | 20 | 347 | 8324 | 37.94 | 3580.1959 | 0 | 0 | 3580.1959 | Heating | 3158.9964 | 8.5 | 3158.9964 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 631.7993 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3223.4657 | 0 | 644.6931 | 6.447% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 21:01 | 12 | 13 | 21 | 347 | 8325 | 37.94 | 3934.0047 | 0 | 0 | 3934.0047 | Heating | 3471.1806 | 8.5 | 3471.1806 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 694.2361 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3542.021 | 0 | 708.4042 | 7.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 22:01 | 12 | 13 | 22 | 347 | 8326 | 37.04 | 1184.2182 | 0 | 0 | 1184.2182 | Heating | 1044.8985 | 8.5 | 1044.8985 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 208.9797 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1066.2229 | 0 | 213.2446 | 2.132% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-13 23:01 | 12 | 13 | 23 | 347 | 8327 | 37.04 | 992.8607 | 0 | 0 | 992.8607 | Heating | 876.0535 | 8.5 | 876.0535 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 175.2107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 893.9322 | 0 | 178.7864 | 1.788% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 00:01 | 12 | 14 | 0 | 348 | 8328 | 35.96 | 1102.1547 | 0 | 0 | 1102.1547 | Heating | 972.4894 | 8.5 | 972.4894 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 194.4979 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 992.3361 | 0 | 198.4672 | 1.985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 01:01 | 12 | 14 | 1 | 348 | 8329 | 35.96 | 1197.3873 | 0 | 0 | 1197.3873 | Heating | 1056.5182 | 8.5 | 1056.5182 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.3036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1078.0798 | 0 | 215.616 | 2.156% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 02:01 | 12 | 14 | 2 | 348 | 8330 | 35.96 | 1278.2349 | 0 | 0 | 1278.2349 | Heating | 1127.8543 | 8.5 | 1127.8543 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.5709 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1150.8717 | 0 | 230.1743 | 2.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 03:01 | 12 | 14 | 3 | 348 | 8331 | 35.06 | 1358.9625 | 0 | 0 | 1358.9625 | Heating | 1199.0846 | 8.5 | 1199.0846 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 239.8169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1223.5557 | 0 | 244.7111 | 2.447% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 04:01 | 12 | 14 | 4 | 348 | 8332 | 33.98 | 1430.8631 | 0 | 0 | 1430.8631 | Heating | 1262.5262 | 8.5 | 1262.5262 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.5052 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1288.2921 | 0 | 257.6584 | 2.577% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 05:01 | 12 | 14 | 5 | 348 | 8333 | 33.98 | 1495.5909 | 0 | 0 | 1495.5909 | Heating | 1319.639 | 8.5 | 1319.639 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 263.9278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1346.5704 | 0 | 269.3141 | 2.693% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 06:01 | 12 | 14 | 6 | 348 | 8334 | 32 | 1543.0904 | 0 | 0 | 1543.0904 | Heating | 1361.5503 | 8.5 | 1361.5503 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 272.3101 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1389.3371 | 0 | 277.8674 | 2.779% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 07:01 | 12 | 14 | 7 | 348 | 8335 | 32 | 9262.5735 | 0 | 0 | 9262.5735 | Heating | 8172.8589 | 8.5 | 8172.8589 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1634.5718 | 32.69% | 1 | 65.38% | 0% | 0% | 0% | 30.6697 | 0 | 0 | 0 | 30.6697 | 8339.652 | 0 | 1667.9304 | 16.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.9443
2007-12-14 08:01 | 12 | 14 | 8 | 348 | 8336 | 32 | 7174.1241 | 0 | 0 | 7174.1241 | Heating | 6330.1095 | 8.5 | 6330.1095 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1266.0219 | 30% | 1 | 50.64% | 0% | 0% | 0% | 17.041 | 0 | 0 | 0 | 17.041 | 6459.2954 | 0 | 1291.8591 | 12.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.3156
2007-12-14 09:01 | 12 | 14 | 9 | 348 | 8337 | 33.98 | 6432.1268 | 0 | 0 | 6432.1268 | Heating | 5675.406 | 8.5 | 5675.406 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1135.0812 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5791.2306 | 0 | 1158.2461 | 11.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 10:01 | 12 | 14 | 10 | 348 | 8338 | 35.96 | 5656.8277 | 0 | 0 | 5656.8277 | Heating | 4991.3185 | 8.5 | 4991.3185 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 998.2637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5093.1822 | 0 | 1018.6364 | 10.19% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 11:01 | 12 | 14 | 11 | 348 | 8339 | 35.96 | 5001.0369 | 0 | 0 | 5001.0369 | Heating | 4412.6796 | 8.5 | 4412.6796 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 882.5359 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4502.7343 | 0 | 900.5469 | 9.005% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 12:01 | 12 | 14 | 12 | 348 | 8340 | 37.94 | 4559.2244 | 0 | 0 | 4559.2244 | Heating | 4022.845 | 8.5 | 4022.845 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 804.569 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4104.9439 | 0 | 820.9888 | 8.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 13:01 | 12 | 14 | 13 | 348 | 8341 | 37.94 | 4391.6438 | 0 | 0 | 4391.6438 | Heating | 3874.9798 | 8.5 | 3874.9798 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 774.996 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3954.0611 | 0 | 790.8122 | 7.908% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 14:01 | 12 | 14 | 14 | 348 | 8342 | 37.94 | 4333.6518 | 0 | 0 | 4333.6518 | Heating | 3823.8105 | 8.5 | 3823.8105 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 764.7621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3901.8474 | 0 | 780.3695 | 7.804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 15:01 | 12 | 14 | 15 | 348 | 8343 | 37.94 | 4281.5553 | 0 | 0 | 4281.5553 | Heating | 3777.8429 | 8.5 | 3777.8429 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 755.5686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3854.9417 | 0 | 770.9883 | 7.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 16:01 | 12 | 14 | 16 | 348 | 8344 | 37.04 | 4321.0199 | 0 | 0 | 4321.0199 | Heating | 3812.6646 | 8.5 | 3812.6646 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 762.5329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3890.4741 | 0 | 778.0948 | 7.781% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 17:01 | 12 | 14 | 17 | 348 | 8345 | 35.96 | 4465.2057 | 0 | 0 | 4465.2057 | Heating | 3939.8873 | 8.5 | 3939.8873 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 787.9775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4020.2932 | 0 | 804.0586 | 8.041% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 18:01 | 12 | 14 | 18 | 348 | 8346 | 37.04 | 4723.8126 | 0 | 0 | 4723.8126 | Heating | 4168.07 | 8.5 | 4168.07 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 833.614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4253.1326 | 0 | 850.6265 | 8.506% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 19:01 | 12 | 14 | 19 | 348 | 8347 | 35.96 | 5083.7551 | 0 | 0 | 5083.7551 | Heating | 4485.6663 | 8.5 | 4485.6663 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 897.1333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4577.2105 | 0 | 915.4421 | 9.154% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 20:01 | 12 | 14 | 20 | 348 | 8348 | 35.96 | 5748.7846 | 0 | 0 | 5748.7846 | Heating | 5072.457 | 8.5 | 5072.457 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1014.4914 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5175.9766 | 0 | 1035.1953 | 10.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 21:01 | 12 | 14 | 21 | 348 | 8349 | 35.96 | 6244.641 | 0 | 0 | 6244.641 | Heating | 5509.9774 | 8.5 | 5509.9774 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1101.9955 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5622.4259 | 0 | 1124.4852 | 11.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 22:01 | 12 | 14 | 22 | 348 | 8350 | 35.06 | 6920.8092 | 0 | 0 | 6920.8092 | Heating | 6106.5964 | 8.5 | 6106.5964 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1221.3193 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6231.2208 | 0 | 1246.2442 | 12.46% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-14 23:01 | 12 | 14 | 23 | 348 | 8351 | 33.08 | 2104.2619 | 0 | 0 | 2104.2619 | Heating | 1856.7017 | 8.5 | 1856.7017 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 371.3403 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1894.5935 | 0 | 378.9187 | 3.789% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 00:01 | 12 | 15 | 0 | 349 | 8352 | 32 | 2196.2073 | 0 | 0 | 2196.2073 | Heating | 1937.83 | 8.5 | 1937.83 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1977.3776 | 0 | 395.4755 | 3.955% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 01:01 | 12 | 15 | 1 | 349 | 8353 | 30.92 | 2280.3867 | 0 | 0 | 2280.3867 | Heating | 2012.1059 | 8.5 | 2012.1059 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 402.4212 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2053.1693 | 0 | 410.6339 | 4.106% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 02:01 | 12 | 15 | 2 | 349 | 8354 | 30.92 | 2314.2997 | 0 | 0 | 2314.2997 | Heating | 2042.0292 | 8.5 | 2042.0292 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 408.4058 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2083.7032 | 0 | 416.7406 | 4.167% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 03:01 | 12 | 15 | 3 | 349 | 8355 | 32 | 2319.9166 | 0 | 0 | 2319.9166 | Heating | 2046.9852 | 8.5 | 2046.9852 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 409.397 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2088.7604 | 0 | 417.7521 | 4.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 04:01 | 12 | 15 | 4 | 349 | 8356 | 32 | 2316.1543 | 0 | 0 | 2316.1543 | Heating | 2043.6656 | 8.5 | 2043.6656 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 408.7331 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2085.373 | 0 | 417.0746 | 4.171% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 05:01 | 12 | 15 | 5 | 349 | 8357 | 32 | 2338.6884 | 0 | 0 | 2338.6884 | Heating | 2063.5486 | 8.5 | 2063.5486 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.7097 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2105.6618 | 0 | 421.1324 | 4.211% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 06:01 | 12 | 15 | 6 | 349 | 8358 | 30.02 | 2364.7258 | 0 | 0 | 2364.7258 | Heating | 2086.5228 | 8.5 | 2086.5228 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 417.3046 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2129.1049 | 0 | 425.821 | 4.258% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 07:01 | 12 | 15 | 7 | 349 | 8359 | 32 | 2388.251 | 0 | 0 | 2388.251 | Heating | 2107.2803 | 8.5 | 2107.2803 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 421.4561 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2150.286 | 0 | 430.0572 | 4.301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 08:01 | 12 | 15 | 8 | 349 | 8360 | 30.92 | 2344.1468 | 0 | 0 | 2344.1468 | Heating | 2068.3648 | 8.5 | 2068.3648 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 413.673 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2110.5763 | 0 | 422.1153 | 4.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 09:01 | 12 | 15 | 9 | 349 | 8361 | 30.02 | 11440.2627 | 0 | 0 | 11440.2627 | Heating | 10094.3494 | 8.5 | 10094.3494 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2018.8699 | 40.38% | 1 | 80.75% | 0% | 0% | 0% | 49.846 | 0 | 0 | 0 | 49.846 | 10300.3566 | 0 | 2060.0713 | 20.6% | 1 | 41.2% | 0% | 0% | 5.3017 | 0 | 0 | 5.3017 | 55.1476
2007-12-15 10:01 | 12 | 15 | 10 | 349 | 8362 | 28.94 | 8772.838 | 0 | 0 | 8772.838 | Heating | 7740.7394 | 8.5 | 7740.7394 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1548.1479 | 30.96% | 1 | 61.93% | 0% | 0% | 0% | 27.0676 | 0 | 0 | 0 | 27.0676 | 7898.7137 | 0 | 1579.7427 | 15.8% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.3421
2007-12-15 11:01 | 12 | 15 | 11 | 349 | 8363 | 28.94 | 7378.2849 | 0 | 0 | 7378.2849 | Heating | 6510.2514 | 8.5 | 6510.2514 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1302.0503 | 30% | 1 | 52.08% | 0% | 0% | 0% | 18.1771 | 0 | 0 | 0 | 18.1771 | 6643.1137 | 0 | 1328.6227 | 13.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.4517
2007-12-15 12:01 | 12 | 15 | 12 | 349 | 8364 | 28.94 | 6315.0647 | 0 | 0 | 6315.0647 | Heating | 5572.1159 | 8.5 | 5572.1159 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1114.4232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5685.8325 | 0 | 1137.1665 | 11.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 13:01 | 12 | 15 | 13 | 349 | 8365 | 28.94 | 5191.6736 | 0 | 0 | 5191.6736 | Heating | 4580.8884 | 8.5 | 4580.8884 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 916.1777 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4674.376 | 0 | 934.8752 | 9.349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 14:01 | 12 | 15 | 14 | 349 | 8366 | 28.94 | 4606.54 | 0 | 0 | 4606.54 | Heating | 4064.5941 | 8.5 | 4064.5941 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 812.9188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4147.545 | 0 | 829.509 | 8.295% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 15:01 | 12 | 15 | 15 | 349 | 8367 | 28.94 | 4301.1683 | 0 | 0 | 4301.1683 | Heating | 3795.1485 | 8.5 | 3795.1485 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 759.0297 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3872.6006 | 0 | 774.5201 | 7.745% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 16:01 | 12 | 15 | 16 | 349 | 8368 | 26.06 | 4122.3667 | 0 | 0 | 4122.3667 | Heating | 3637.3824 | 8.5 | 3637.3824 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.4765 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3711.6147 | 0 | 742.3229 | 7.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 17:01 | 12 | 15 | 17 | 349 | 8369 | 26.06 | 4309.6216 | 0 | 0 | 4309.6216 | Heating | 3802.6073 | 8.5 | 3802.6073 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 760.5215 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3880.2115 | 0 | 776.0423 | 7.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 18:01 | 12 | 15 | 18 | 349 | 8370 | 21.92 | 6252.568 | 0 | 0 | 6252.568 | Heating | 5516.9718 | 8.5 | 5516.9718 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1103.3944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5629.5631 | 0 | 1125.9126 | 11.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 19:01 | 12 | 15 | 19 | 349 | 8371 | 21.02 | 6973.6488 | 0 | 0 | 6973.6488 | Heating | 6153.2195 | 8.5 | 6153.2195 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1230.6439 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6278.7955 | 0 | 1255.7591 | 12.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 20:01 | 12 | 15 | 20 | 349 | 8372 | 21.02 | 1729.5547 | 0 | 0 | 1729.5547 | Heating | 1526.0777 | 8.5 | 1526.0777 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 305.2155 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1557.2221 | 0 | 311.4444 | 3.114% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 21:01 | 12 | 15 | 21 | 349 | 8373 | 24.08 | 1838.68 | 0 | 0 | 1838.68 | Heating | 1622.3647 | 8.5 | 1622.3647 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.4729 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1655.4742 | 0 | 331.0948 | 3.311% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 22:01 | 12 | 15 | 22 | 349 | 8374 | 24.08 | 1947.3992 | 0 | 0 | 1947.3992 | Heating | 1718.2934 | 8.5 | 1718.2934 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.6587 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1753.3606 | 0 | 350.6721 | 3.507% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-15 23:01 | 12 | 15 | 23 | 349 | 8375 | 24.08 | 1948.9288 | 0 | 0 | 1948.9288 | Heating | 1719.6431 | 8.5 | 1719.6431 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 343.9286 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1754.7378 | 0 | 350.9476 | 3.509% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 00:01 | 12 | 16 | 0 | 350 | 8376 | 24.08 | 1865.012 | 0 | 0 | 1865.012 | Heating | 1645.5988 | 8.5 | 1645.5988 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.1198 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1679.1824 | 0 | 335.8365 | 3.358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 01:01 | 12 | 16 | 1 | 350 | 8377 | 26.06 | 1765.0817 | 0 | 0 | 1765.0817 | Heating | 1557.425 | 8.5 | 1557.425 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 311.485 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1589.2092 | 0 | 317.8418 | 3.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 02:01 | 12 | 16 | 2 | 350 | 8378 | 26.06 | 1801.9654 | 0 | 0 | 1801.9654 | Heating | 1589.9695 | 8.5 | 1589.9695 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 317.9939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1622.4178 | 0 | 324.4836 | 3.245% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 03:01 | 12 | 16 | 3 | 350 | 8379 | 24.98 | 1933.4881 | 0 | 0 | 1933.4881 | Heating | 1706.0189 | 8.5 | 1706.0189 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 341.2038 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1740.8356 | 0 | 348.1671 | 3.482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 04:01 | 12 | 16 | 4 | 350 | 8380 | 24.08 | 2074.1468 | 0 | 0 | 2074.1468 | Heating | 1830.1295 | 8.5 | 1830.1295 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 366.0259 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1867.4791 | 0 | 373.4958 | 3.735% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 05:01 | 12 | 16 | 5 | 350 | 8381 | 24.08 | 2211.3199 | 0 | 0 | 2211.3199 | Heating | 1951.1646 | 8.5 | 1951.1646 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 390.2329 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1990.9843 | 0 | 398.1969 | 3.982% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 06:01 | 12 | 16 | 6 | 350 | 8382 | 19.94 | 2343.4448 | 0 | 0 | 2343.4448 | Heating | 2067.7454 | 8.5 | 2067.7454 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 413.5491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2109.9443 | 0 | 421.9889 | 4.22% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 07:01 | 12 | 16 | 7 | 350 | 8383 | 19.04 | 13176.6635 | 0 | 0 | 13176.6635 | Heating | 11626.4678 | 8.5 | 11626.4678 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2325.2936 | 46.51% | 1 | 93.01% | 0% | 0% | 0% | 68.989 | 0 | 0 | 0 | 68.989 | 11863.7426 | 0 | 2372.7485 | 23.73% | 1 | 47.45% | 0% | 0% | 7.3377 | 0 | 0 | 7.3377 | 76.3267
2007-12-16 08:01 | 12 | 16 | 8 | 350 | 8384 | 19.04 | 9886.0769 | 0 | 0 | 9886.0769 | Heating | 8723.009 | 8.5 | 8723.009 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1744.6018 | 34.89% | 1 | 69.78% | 0% | 0% | 0% | 35.6273 | 0 | 0 | 0 | 35.6273 | 8901.0296 | 0 | 1780.2059 | 17.8% | 1 | 35.6% | 0% | 0% | 3.7893 | 0 | 0 | 3.7893 | 39.4166
2007-12-16 09:01 | 12 | 16 | 9 | 350 | 8385 | 19.04 | 7237.4708 | 0 | 0 | 7237.4708 | Heating | 6386.0036 | 8.5 | 6386.0036 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1277.2007 | 30% | 1 | 51.09% | 0% | 0% | 0% | 17.3891 | 0 | 0 | 0 | 17.3891 | 6516.3302 | 0 | 1303.266 | 13.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.6636
2007-12-16 10:01 | 12 | 16 | 10 | 350 | 8386 | 17.96 | 4917.5561 | 0 | 0 | 4917.5561 | Heating | 4339.0201 | 8.5 | 4339.0201 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 867.804 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4427.5715 | 0 | 885.5143 | 8.855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 11:01 | 12 | 16 | 11 | 350 | 8387 | 17.96 | 3657.1473 | 0 | 0 | 3657.1473 | Heating | 3226.8947 | 8.5 | 3226.8947 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 645.3789 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3292.7497 | 0 | 658.5499 | 6.585% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 12:01 | 12 | 16 | 12 | 350 | 8388 | 17.96 | 2881.2936 | 0 | 0 | 2881.2936 | Heating | 2542.3179 | 8.5 | 2542.3179 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 508.4636 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2594.202 | 0 | 518.8404 | 5.188% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 13:01 | 12 | 16 | 13 | 350 | 8389 | 19.04 | 2362.0815 | 0 | 0 | 2362.0815 | Heating | 2084.1895 | 8.5 | 2084.1895 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 416.8379 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2126.724 | 0 | 425.3448 | 4.253% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 14:01 | 12 | 16 | 14 | 350 | 8390 | 19.04 | 2095.1575 | 2.5562 | 2.5562 | 2092.6013 | Heating | 1846.4129 | 8.5 | 1846.4129 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 369.2826 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1884.0948 | 0 | 376.819 | 3.768% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 15:01 | 12 | 16 | 15 | 350 | 8391 | 17.96 | 2014.8876 | 9.7939 | 9.7939 | 2005.0937 | Heating | 1769.2003 | 8.5 | 1769.2003 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 353.8401 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1805.3065 | 0 | 361.0613 | 3.611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 16:01 | 12 | 16 | 16 | 350 | 8392 | 17.06 | 1971.6811 | 12.288 | 12.288 | 1959.3931 | Heating | 1728.8762 | 8.5 | 1728.8762 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 345.7752 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1764.1594 | 0 | 352.8319 | 3.528% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 17:01 | 12 | 16 | 17 | 350 | 8393 | 15.98 | 2425.2488 | 0.9201 | 0.9201 | 2424.3287 | Heating | 2139.1136 | 8.5 | 2139.1136 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.8227 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2182.769 | 0 | 436.5538 | 4.366% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 18:01 | 12 | 16 | 18 | 350 | 8394 | 15.98 | 3183.3966 | 0 | 0 | 3183.3966 | Heating | 2808.8794 | 8.5 | 2808.8794 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 561.7759 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2866.2034 | 0 | 573.2407 | 5.732% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 19:01 | 12 | 16 | 19 | 350 | 8395 | 15.98 | 3884.4011 | 0 | 0 | 3884.4011 | Heating | 3427.4127 | 8.5 | 3427.4127 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 685.4825 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3497.3599 | 0 | 699.472 | 6.995% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 20:01 | 12 | 16 | 20 | 350 | 8396 | 17.96 | 4434.6007 | 0 | 0 | 4434.6007 | Heating | 3912.883 | 8.5 | 3912.883 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 782.5766 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3992.7378 | 0 | 798.5476 | 7.985% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 21:01 | 12 | 16 | 21 | 350 | 8397 | 17.06 | 4881.3731 | 0 | 0 | 4881.3731 | Heating | 4307.0939 | 8.5 | 4307.0939 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 861.4188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4394.9938 | 0 | 878.9988 | 8.79% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 22:01 | 12 | 16 | 22 | 350 | 8398 | 12.02 | 1460.8274 | 0 | 0 | 1460.8274 | Heating | 1288.9654 | 8.5 | 1288.9654 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 257.7931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1315.2708 | 0 | 263.0542 | 2.631% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-16 23:01 | 12 | 16 | 23 | 350 | 8399 | 12.02 | 1182.7694 | 0 | 0 | 1182.7694 | Heating | 1043.6201 | 8.5 | 1043.6201 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 208.724 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1064.9184 | 0 | 212.9837 | 2.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 00:01 | 12 | 17 | 0 | 351 | 8400 | 6.08 | 1200.2082 | 0 | 0 | 1200.2082 | Heating | 1059.0072 | 8.5 | 1059.0072 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 211.8014 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1080.6196 | 0 | 216.1239 | 2.161% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 01:01 | 12 | 17 | 1 | 351 | 8401 | 3.92 | 1119.7668 | 0 | 0 | 1119.7668 | Heating | 988.0296 | 8.5 | 988.0296 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 197.6059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1008.1934 | 0 | 201.6387 | 2.016% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 02:01 | 12 | 17 | 2 | 351 | 8402 | 3.92 | 1133.8266 | 0 | 0 | 1133.8266 | Heating | 1000.4353 | 8.5 | 1000.4353 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 200.0871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1020.8523 | 0 | 204.1705 | 2.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 03:01 | 12 | 17 | 3 | 351 | 8403 | 1.94 | 1243.5213 | 0 | 0 | 1243.5213 | Heating | 1097.2246 | 8.5 | 1097.2246 | 0 | 2.6096 | 0 | 0 | 0 | 0 | 8.5 | 0 | 219.4449 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1119.617 | 0 | 223.9234 | 2.239% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 04:01 | 12 | 17 | 4 | 351 | 8404 | 1.94 | 1352.9288 | 0 | 0 | 1352.9288 | Heating | 1193.7607 | 8.5 | 1193.7607 | 0 | 2.6096 | 0 | 0 | 0 | 0 | 8.5 | 0 | 238.7521 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1218.1232 | 0 | 243.6246 | 2.436% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 05:01 | 12 | 17 | 5 | 351 | 8405 | 1.94 | 1403.2957 | 0 | 0 | 1403.2957 | Heating | 1238.2021 | 8.5 | 1238.2021 | 0 | 2.6096 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.6404 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1263.4715 | 0 | 252.6943 | 2.527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 06:01 | 12 | 17 | 6 | 351 | 8406 | 1.94 | 1400.5819 | 0 | 0 | 1400.5819 | Heating | 1235.8075 | 8.5 | 1235.8075 | 0 | 2.6096 | 0 | 0 | 0 | 0 | 8.5 | 0 | 247.1615 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1261.0281 | 0 | 252.2056 | 2.522% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 07:01 | 12 | 17 | 7 | 351 | 8407 | 1.04 | 9509.1276 | 0 | 0 | 9509.1276 | Heating | 8390.4067 | 8.5 | 8390.4067 | 0 | 2.5975 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1678.0813 | 33.56% | 1 | 67.12% | 0% | 0% | 0% | 32.58 | 0 | 0 | 0 | 32.58 | 8561.6395 | 0 | 1712.3279 | 17.12% | 1 | 34.25% | 0% | 0% | 3.4652 | 0 | 0 | 3.4652 | 36.0452
2007-12-17 08:01 | 12 | 17 | 8 | 351 | 8408 | 1.04 | 7111.0914 | 0 | 0 | 7111.0914 | Heating | 6274.4924 | 8.5 | 6274.4924 | 0 | 2.5975 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1254.8985 | 30% | 1 | 50.2% | 0% | 0% | 0% | 16.6986 | 0 | 0 | 0 | 16.6986 | 6402.5433 | 0 | 1280.5087 | 12.81% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.9732
2007-12-17 09:01 | 12 | 17 | 9 | 351 | 8409 | 3.92 | 5741.1625 | 0 | 0 | 5741.1625 | Heating | 5065.7316 | 8.5 | 5065.7316 | 0 | 2.6361 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1013.1463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5169.1139 | 0 | 1033.8228 | 10.34% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 10:01 | 12 | 17 | 10 | 351 | 8410 | 6.08 | 4591.077 | 0 | 0 | 4591.077 | Heating | 4050.9503 | 8.5 | 4050.9503 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 810.1901 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4133.6228 | 0 | 826.7246 | 8.267% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 11:01 | 12 | 17 | 11 | 351 | 8411 | 6.08 | 4079.1444 | 0 | 0 | 4079.1444 | Heating | 3599.2451 | 8.5 | 3599.2451 | 0 | 2.6655 | 0 | 0 | 0 | 0 | 8.5 | 0 | 719.849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3672.699 | 0 | 734.5398 | 7.345% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 12:01 | 12 | 17 | 12 | 351 | 8412 | 10.04 | 3742.8648 | 0 | 0 | 3742.8648 | Heating | 3302.5278 | 8.5 | 3302.5278 | 0 | 2.723 | 0 | 0 | 0 | 0 | 8.5 | 0 | 660.5056 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3369.9263 | 0 | 673.9853 | 6.74% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 13:01 | 12 | 17 | 13 | 351 | 8413 | 12.02 | 3657.2571 | 0 | 0 | 3657.2571 | Heating | 3226.9916 | 8.5 | 3226.9916 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 645.3983 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3292.8485 | 0 | 658.5697 | 6.586% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 14:01 | 12 | 17 | 14 | 351 | 8414 | 12.02 | 3623.2093 | 0 | 0 | 3623.2093 | Heating | 3196.9494 | 8.5 | 3196.9494 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 639.3899 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3262.1932 | 0 | 652.4386 | 6.524% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 15:01 | 12 | 17 | 15 | 351 | 8415 | 15.08 | 3703.1334 | 0 | 0 | 3703.1334 | Heating | 3267.4706 | 8.5 | 3267.4706 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 653.4941 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3334.1537 | 0 | 666.8307 | 6.668% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 16:01 | 12 | 17 | 16 | 351 | 8416 | 15.08 | 3831.2105 | 0 | 0 | 3831.2105 | Heating | 3380.4798 | 8.5 | 3380.4798 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 676.096 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3449.4692 | 0 | 689.8938 | 6.899% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 17:01 | 12 | 17 | 17 | 351 | 8417 | 15.08 | 4055.1732 | 0 | 0 | 4055.1732 | Heating | 3578.094 | 8.5 | 3578.094 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 715.6188 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3651.1163 | 0 | 730.2233 | 7.302% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 18:01 | 12 | 17 | 18 | 351 | 8418 | 14 | 4361.9699 | 0 | 0 | 4361.9699 | Heating | 3848.7969 | 8.5 | 3848.7969 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 769.7594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3927.3438 | 0 | 785.4688 | 7.855% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 19:01 | 12 | 17 | 19 | 351 | 8419 | 12.92 | 4550.2159 | 0 | 0 | 4550.2159 | Heating | 4014.8964 | 8.5 | 4014.8964 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 802.9793 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4096.8331 | 0 | 819.3666 | 8.194% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 20:01 | 12 | 17 | 20 | 351 | 8420 | 12.92 | 4800.7442 | 0 | 0 | 4800.7442 | Heating | 4235.9508 | 8.5 | 4235.9508 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 847.1902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4322.3987 | 0 | 864.4797 | 8.645% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 21:01 | 12 | 17 | 21 | 351 | 8421 | 17.06 | 5118.5791 | 0 | 0 | 5118.5791 | Heating | 4516.3933 | 8.5 | 4516.3933 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 903.2787 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4608.5646 | 0 | 921.7129 | 9.217% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 22:01 | 12 | 17 | 22 | 351 | 8422 | 19.04 | 1616.3346 | 0 | 0 | 1616.3346 | Heating | 1426.1776 | 8.5 | 1426.1776 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 285.2355 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1455.2833 | 0 | 291.0567 | 2.911% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-17 23:01 | 12 | 17 | 23 | 351 | 8423 | 19.04 | 1664.2775 | 0 | 0 | 1664.2775 | Heating | 1468.4801 | 8.5 | 1468.4801 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 293.696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1498.4491 | 0 | 299.6898 | 2.997% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 00:01 | 12 | 18 | 0 | 352 | 8424 | 21.02 | 1932.2275 | 0 | 0 | 1932.2275 | Heating | 1704.9066 | 8.5 | 1704.9066 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.9813 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1739.7006 | 0 | 347.9401 | 3.479% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 01:01 | 12 | 18 | 1 | 352 | 8425 | 21.92 | 2085.5868 | 0 | 0 | 2085.5868 | Heating | 1840.2236 | 8.5 | 1840.2236 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.0447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1877.7792 | 0 | 375.5558 | 3.756% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 02:01 | 12 | 18 | 2 | 352 | 8426 | 21.02 | 2243.5673 | 0 | 0 | 2243.5673 | Heating | 1979.6182 | 8.5 | 1979.6182 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 395.9236 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2020.0186 | 0 | 404.0037 | 4.04% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 03:01 | 12 | 18 | 3 | 352 | 8427 | 19.94 | 2416.9793 | 0 | 0 | 2416.9793 | Heating | 2132.6288 | 8.5 | 2132.6288 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 426.5258 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2176.1519 | 0 | 435.2304 | 4.352% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 04:01 | 12 | 18 | 4 | 352 | 8428 | 19.94 | 2581.0414 | 0 | 0 | 2581.0414 | Heating | 2277.3894 | 8.5 | 2277.3894 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 455.4779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2323.8668 | 0 | 464.7734 | 4.648% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 05:01 | 12 | 18 | 5 | 352 | 8429 | 19.94 | 2694.4521 | 0 | 0 | 2694.4521 | Heating | 2377.4577 | 8.5 | 2377.4577 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 475.4915 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2425.9773 | 0 | 485.1955 | 4.852% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 06:01 | 12 | 18 | 6 | 352 | 8430 | 21.02 | 2750.4447 | 0 | 0 | 2750.4447 | Heating | 2426.863 | 8.5 | 2426.863 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 485.3726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2476.3908 | 0 | 495.2782 | 4.953% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 07:01 | 12 | 18 | 7 | 352 | 8431 | 21.02 | 13384.2253 | 0 | 0 | 13384.2253 | Heating | 11809.6105 | 8.5 | 11809.6105 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2361.9221 | 47.24% | 1 | 94.48% | 0% | 0% | 0% | 71.5141 | 0 | 0 | 0 | 71.5141 | 12050.623 | 0 | 2410.1246 | 24.1% | 1 | 48.2% | 0% | 0% | 7.6063 | 0 | 0 | 7.6063 | 79.1204
2007-12-18 08:01 | 12 | 18 | 8 | 352 | 8432 | 21.02 | 10330.6824 | 0 | 0 | 10330.6824 | Heating | 9115.308 | 8.5 | 9115.308 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1823.0616 | 36.46% | 1 | 72.92% | 0% | 0% | 0% | 39.4207 | 0 | 0 | 0 | 39.4207 | 9301.3347 | 0 | 1860.2669 | 18.6% | 1 | 37.21% | 0% | 0% | 4.1928 | 0 | 0 | 4.1928 | 43.6135
2007-12-18 09:01 | 12 | 18 | 9 | 352 | 8433 | 21.92 | 8367.2624 | 0 | 0 | 8367.2624 | Heating | 7382.8785 | 8.5 | 7382.8785 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1476.5757 | 30% | 1 | 59.06% | 0% | 0% | 0% | 24.2756 | 0 | 0 | 0 | 24.2756 | 7533.5495 | 0 | 1506.7099 | 15.07% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.5501
2007-12-18 10:01 | 12 | 18 | 10 | 352 | 8434 | 24.08 | 6772.723 | 0 | 0 | 6772.723 | Heating | 5975.932 | 8.5 | 5975.932 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1195.1864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6097.8898 | 0 | 1219.578 | 12.2% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 11:01 | 12 | 18 | 11 | 352 | 8435 | 24.08 | 5869.4505 | 0 | 0 | 5869.4505 | Heating | 5178.9269 | 8.5 | 5178.9269 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1035.7854 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5284.6193 | 0 | 1056.9239 | 10.57% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 12:01 | 12 | 18 | 12 | 352 | 8436 | 24.98 | 5131.1818 | 0 | 0 | 5131.1818 | Heating | 4527.5134 | 8.5 | 4527.5134 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 905.5027 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4619.9116 | 0 | 923.9823 | 9.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 13:01 | 12 | 18 | 13 | 352 | 8437 | 26.96 | 4734.1052 | 0 | 0 | 4734.1052 | Heating | 4177.1517 | 8.5 | 4177.1517 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 835.4303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4262.3997 | 0 | 852.4799 | 8.525% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 14:01 | 12 | 18 | 14 | 352 | 8438 | 28.04 | 4682.9703 | 0 | 0 | 4682.9703 | Heating | 4132.0326 | 8.5 | 4132.0326 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 826.4065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4216.3598 | 0 | 843.272 | 8.433% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 15:01 | 12 | 18 | 15 | 352 | 8439 | 30.02 | 4929.8745 | 0 | 0 | 4929.8745 | Heating | 4349.8893 | 8.5 | 4349.8893 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 869.9779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4438.6625 | 0 | 887.7325 | 8.877% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 16:01 | 12 | 18 | 16 | 352 | 8440 | 30.02 | 5219.4161 | 0 | 0 | 5219.4161 | Heating | 4605.3671 | 8.5 | 4605.3671 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 921.0734 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4699.3542 | 0 | 939.8708 | 9.399% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 17:01 | 12 | 18 | 17 | 352 | 8441 | 30.02 | 5647.8628 | 0 | 0 | 5647.8628 | Heating | 4983.4084 | 8.5 | 4983.4084 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 996.6817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5085.1106 | 0 | 1017.0221 | 10.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 18:01 | 12 | 18 | 18 | 352 | 8442 | 30.02 | 6179.7351 | 0 | 0 | 6179.7351 | Heating | 5452.7075 | 8.5 | 5452.7075 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1090.5415 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5563.9872 | 0 | 1112.7974 | 11.13% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 19:01 | 12 | 18 | 19 | 352 | 8443 | 30.2 | 6588.4185 | 0 | 0 | 6588.4185 | Heating | 5813.3105 | 8.5 | 5813.3105 | 0 | 3.2375 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1162.6621 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5931.9495 | 0 | 1186.3899 | 11.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 20:01 | 12 | 18 | 20 | 352 | 8444 | 30.92 | 6977.387 | 0 | 0 | 6977.387 | Heating | 6156.518 | 8.5 | 6156.518 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1231.3036 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6282.1612 | 0 | 1256.4322 | 12.56% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 21:01 | 12 | 18 | 21 | 352 | 8445 | 30.92 | 7313.7992 | 0 | 0 | 7313.7992 | Heating | 6453.3522 | 8.5 | 6453.3522 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1290.6704 | 30% | 1 | 51.63% | 0% | 0% | 0% | 17.8138 | 0 | 0 | 0 | 17.8138 | 6585.0533 | 0 | 1317.0107 | 13.17% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.0883
2007-12-18 22:01 | 12 | 18 | 22 | 352 | 8446 | 32 | 2355.1634 | 0 | 0 | 2355.1634 | Heating | 2078.0853 | 8.5 | 2078.0853 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 415.6171 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2120.4952 | 0 | 424.099 | 4.241% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-18 23:01 | 12 | 18 | 23 | 352 | 8447 | 32 | 2664.9885 | 0 | 0 | 2664.9885 | Heating | 2351.4605 | 8.5 | 2351.4605 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 470.2921 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2399.4495 | 0 | 479.8899 | 4.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 00:01 | 12 | 19 | 0 | 353 | 8448 | 33.98 | 2968.8882 | 0 | 0 | 2968.8882 | Heating | 2619.6073 | 8.5 | 2619.6073 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 523.9215 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2673.0686 | 0 | 534.6137 | 5.346% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 01:01 | 12 | 19 | 1 | 353 | 8449 | 35.06 | 3147.6147 | 0 | 0 | 3147.6147 | Heating | 2777.3071 | 8.5 | 2777.3071 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 555.4614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2833.9869 | 0 | 566.7974 | 5.668% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 02:01 | 12 | 19 | 2 | 353 | 8450 | 35.06 | 3170.5636 | 0 | 0 | 3170.5636 | Heating | 2797.5561 | 8.5 | 2797.5561 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 559.5112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2854.6491 | 0 | 570.9298 | 5.709% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 03:01 | 12 | 19 | 3 | 353 | 8451 | 37.04 | 3252.4267 | 0 | 0 | 3252.4267 | Heating | 2869.7883 | 8.5 | 2869.7883 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 573.9577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2928.3554 | 0 | 585.6711 | 5.857% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 04:01 | 12 | 19 | 4 | 353 | 8452 | 37.94 | 3313.1306 | 0 | 0 | 3313.1306 | Heating | 2923.3505 | 8.5 | 2923.3505 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 584.6701 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2983.0107 | 0 | 596.6021 | 5.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 05:01 | 12 | 19 | 5 | 353 | 8453 | 37.94 | 3331.9432 | 0 | 0 | 3331.9432 | Heating | 2939.9499 | 8.5 | 2939.9499 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 587.99 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2999.9489 | 0 | 599.9898 | 6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 06:01 | 12 | 19 | 6 | 353 | 8454 | 41 | 3313.2025 | 0 | 0 | 3313.2025 | Heating | 2923.4139 | 8.5 | 2923.4139 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 584.6828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2983.0754 | 0 | 596.6151 | 5.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 07:01 | 12 | 19 | 7 | 353 | 8455 | 41 | 14319.8191 | 0 | 0 | 14319.8191 | Heating | 12635.1345 | 8.5 | 12635.1345 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2527.0269 | 50.54% | 2 | 50.54% | 50.54% | 0% | 0% | 16.9635 | 16.9635 | 0 | 0 | 33.9269 | 12892.9944 | 0 | 2578.5989 | 25.79% | 1 | 51.57% | 0% | 0% | 8.8851 | 0 | 0 | 8.8851 | 42.8121
2007-12-19 08:01 | 12 | 19 | 8 | 353 | 8456 | 41 | 11709.5265 | 0 | 0 | 11709.5265 | Heating | 10331.9352 | 8.5 | 10331.9352 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2066.387 | 41.33% | 1 | 82.66% | 0% | 0% | 0% | 52.5857 | 0 | 0 | 0 | 52.5857 | 10542.791 | 0 | 2108.5582 | 21.09% | 1 | 42.17% | 0% | 0% | 5.5931 | 0 | 0 | 5.5931 | 58.1788
2007-12-19 09:01 | 12 | 19 | 9 | 353 | 8457 | 44.06 | 9697.2744 | 0 | 0 | 9697.2744 | Heating | 8556.4186 | 8.5 | 8556.4186 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1711.2837 | 34.23% | 1 | 68.45% | 0% | 0% | 0% | 34.0817 | 0 | 0 | 0 | 34.0817 | 8731.0394 | 0 | 1746.2079 | 17.46% | 1 | 34.92% | 0% | 0% | 3.625 | 0 | 0 | 3.625 | 37.7067
2007-12-19 10:01 | 12 | 19 | 10 | 353 | 8458 | 44.96 | 8011.5883 | 0 | 0 | 8011.5883 | Heating | 7069.0485 | 8.5 | 7069.0485 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1413.8097 | 30% | 1 | 56.55% | 0% | 0% | 0% | 21.9675 | 0 | 0 | 0 | 21.9675 | 7213.3148 | 0 | 1442.663 | 14.43% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.242
2007-12-19 11:01 | 12 | 19 | 11 | 353 | 8459 | 44.96 | 7035.2935 | 0 | 0 | 7035.2935 | Heating | 6207.612 | 8.5 | 6207.612 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1241.5224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6334.2979 | 0 | 1266.8596 | 12.67% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 12:01 | 12 | 19 | 12 | 353 | 8460 | 42.98 | 6172.052 | 0 | 0 | 6172.052 | Heating | 5445.9283 | 8.5 | 5445.9283 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1089.1857 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5557.0697 | 0 | 1111.4139 | 11.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 13:01 | 12 | 19 | 13 | 353 | 8461 | 37.4 | 5642.669 | 0 | 0 | 5642.669 | Heating | 4978.8256 | 8.5 | 4978.8256 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 995.7651 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5080.4343 | 0 | 1016.0869 | 10.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 14:01 | 12 | 19 | 14 | 353 | 8462 | 37.04 | 5358.2375 | 0 | 0 | 5358.2375 | Heating | 4727.8567 | 8.5 | 4727.8567 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 945.5713 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4824.3435 | 0 | 964.8687 | 9.649% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 15:01 | 12 | 19 | 15 | 353 | 8463 | 35.06 | 5280.2958 | 0 | 0 | 5280.2958 | Heating | 4659.0845 | 8.5 | 4659.0845 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 931.8169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4754.1679 | 0 | 950.8336 | 9.508% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 16:01 | 12 | 19 | 16 | 353 | 8464 | 33.08 | 5283.977 | 0 | 0 | 5283.977 | Heating | 4662.3327 | 8.5 | 4662.3327 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 932.4665 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4757.4823 | 0 | 951.4965 | 9.515% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 17:01 | 12 | 19 | 17 | 353 | 8465 | 33.08 | 5534.4493 | 0 | 0 | 5534.4493 | Heating | 4883.3377 | 8.5 | 4883.3377 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 976.6675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4982.9976 | 0 | 996.5995 | 9.966% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 18:01 | 12 | 19 | 18 | 353 | 8466 | 30.92 | 5876.678 | 0 | 0 | 5876.678 | Heating | 5185.3041 | 8.5 | 5185.3041 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1037.0608 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5291.1266 | 0 | 1058.2253 | 10.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 19:01 | 12 | 19 | 19 | 353 | 8467 | 28.94 | 6038.9893 | 0 | 0 | 6038.9893 | Heating | 5328.52 | 8.5 | 5328.52 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1065.704 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5437.2653 | 0 | 1087.4531 | 10.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 20:01 | 12 | 19 | 20 | 353 | 8468 | 28.94 | 6262.2809 | 0 | 0 | 6262.2809 | Heating | 5525.542 | 8.5 | 5525.542 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1105.1084 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5638.3081 | 0 | 1127.6616 | 11.28% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 21:01 | 12 | 19 | 21 | 353 | 8469 | 26.96 | 6513.0477 | 0 | 0 | 6513.0477 | Heating | 5746.8068 | 8.5 | 5746.8068 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1149.3614 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5864.0886 | 0 | 1172.8177 | 11.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 22:01 | 12 | 19 | 22 | 353 | 8470 | 24.08 | 1962.2655 | 0 | 0 | 1962.2655 | Heating | 1731.4107 | 8.5 | 1731.4107 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.2821 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1766.7457 | 0 | 353.3491 | 3.533% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-19 23:01 | 12 | 19 | 23 | 353 | 8471 | 24.08 | 1965.9242 | 0 | 0 | 1965.9242 | Heating | 1734.639 | 8.5 | 1734.639 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 346.9278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1770.0398 | 0 | 354.008 | 3.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 00:01 | 12 | 20 | 0 | 354 | 8472 | 19.94 | 2148.5749 | 0 | 0 | 2148.5749 | Heating | 1895.8014 | 8.5 | 1895.8014 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.1603 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1934.4912 | 0 | 386.8982 | 3.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 01:01 | 12 | 20 | 1 | 354 | 8473 | 19.04 | 2200.1567 | 0 | 0 | 2200.1567 | Heating | 1941.3148 | 8.5 | 1941.3148 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 388.263 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1980.9334 | 0 | 396.1867 | 3.962% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 02:01 | 12 | 20 | 2 | 354 | 8474 | 19.04 | 2231.6516 | 0 | 0 | 2231.6516 | Heating | 1969.1044 | 8.5 | 1969.1044 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 393.8209 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2009.2902 | 0 | 401.858 | 4.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 03:01 | 12 | 20 | 3 | 354 | 8475 | 17.06 | 2245.6901 | 0 | 0 | 2245.6901 | Heating | 1981.4913 | 8.5 | 1981.4913 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 396.2983 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2021.9299 | 0 | 404.386 | 4.044% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 04:01 | 12 | 20 | 4 | 354 | 8476 | 15.98 | 2240.8085 | 0 | 0 | 2240.8085 | Heating | 1977.1839 | 8.5 | 1977.1839 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 395.4368 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2017.5346 | 0 | 403.5069 | 4.035% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 05:01 | 12 | 20 | 5 | 354 | 8477 | 15.98 | 2289.4408 | 0 | 0 | 2289.4408 | Heating | 2020.0948 | 8.5 | 2020.0948 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 404.019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2061.3212 | 0 | 412.2642 | 4.123% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 06:01 | 12 | 20 | 6 | 354 | 8478 | 12.92 | 2351.2425 | 0 | 0 | 2351.2425 | Heating | 2074.6257 | 8.5 | 2074.6257 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 414.9251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2116.965 | 0 | 423.393 | 4.234% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 07:01 | 12 | 20 | 7 | 354 | 8479 | 12.92 | 13485.1146 | 0 | 0 | 13485.1146 | Heating | 11898.6305 | 8.5 | 11898.6305 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2379.7261 | 47.59% | 1 | 95.19% | 0% | 0% | 0% | 72.7601 | 0 | 0 | 0 | 72.7601 | 12141.4597 | 0 | 2428.2919 | 24.28% | 1 | 48.57% | 0% | 0% | 7.7388 | 0 | 0 | 7.7388 | 80.4989
2007-12-20 08:01 | 12 | 20 | 8 | 354 | 8480 | 12.92 | 10418.246 | 0 | 0 | 10418.246 | Heating | 9192.57 | 8.5 | 9192.57 | 0 | 2.7697 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1838.514 | 36.77% | 1 | 73.54% | 0% | 0% | 0% | 40.1934 | 0 | 0 | 0 | 40.1934 | 9380.1734 | 0 | 1876.0347 | 18.76% | 1 | 37.52% | 0% | 0% | 4.275 | 0 | 0 | 4.275 | 44.4684
2007-12-20 09:01 | 12 | 20 | 9 | 354 | 8481 | 14 | 8622.2509 | 0 | 0 | 8622.2509 | Heating | 7607.8684 | 8.5 | 7607.8684 | 0 | 2.7888 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1521.5737 | 30.43% | 1 | 60.86% | 0% | 0% | 0% | 26.0109 | 0 | 0 | 0 | 26.0109 | 7763.131 | 0 | 1552.6262 | 15.53% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.2854
2007-12-20 10:01 | 12 | 20 | 10 | 354 | 8482 | 15.98 | 7190.3294 | 0 | 0 | 7190.3294 | Heating | 6344.4083 | 8.5 | 6344.4083 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1268.8817 | 30% | 1 | 50.76% | 0% | 0% | 0% | 17.1297 | 0 | 0 | 0 | 17.1297 | 6473.886 | 0 | 1294.7772 | 12.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.4042
2007-12-20 11:01 | 12 | 20 | 11 | 354 | 8483 | 15.98 | 6458.2791 | 0 | 0 | 6458.2791 | Heating | 5698.4815 | 8.5 | 5698.4815 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1139.6963 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5814.7771 | 0 | 1162.9554 | 11.63% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 12:01 | 12 | 20 | 12 | 354 | 8484 | 19.94 | 5892.7174 | 0 | 0 | 5892.7174 | Heating | 5199.4565 | 8.5 | 5199.4565 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1039.8913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5305.5679 | 0 | 1061.1136 | 10.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 13:01 | 12 | 20 | 13 | 354 | 8485 | 21.02 | 5566.7958 | 0 | 0 | 5566.7958 | Heating | 4911.8786 | 8.5 | 4911.8786 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 982.3757 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5012.121 | 0 | 1002.4242 | 10.02% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 14:01 | 12 | 20 | 14 | 354 | 8486 | 21.02 | 5377.0214 | 0 | 0 | 5377.0214 | Heating | 4744.4307 | 8.5 | 4744.4307 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 948.8861 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4841.2558 | 0 | 968.2512 | 9.683% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 15:01 | 12 | 20 | 15 | 354 | 8487 | 21.92 | 5319.518 | 0 | 0 | 5319.518 | Heating | 4693.6924 | 8.5 | 4693.6924 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 938.7385 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4789.482 | 0 | 957.8964 | 9.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 16:01 | 12 | 20 | 16 | 354 | 8488 | 19.94 | 5302.7551 | 0 | 0 | 5302.7551 | Heating | 4678.9016 | 8.5 | 4678.9016 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 935.7803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4774.3894 | 0 | 954.8779 | 9.549% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 17:01 | 12 | 20 | 17 | 354 | 8489 | 19.94 | 5360.7485 | 0 | 0 | 5360.7485 | Heating | 4730.0722 | 8.5 | 4730.0722 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 946.0144 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4826.6043 | 0 | 965.3209 | 9.653% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 18:01 | 12 | 20 | 18 | 354 | 8490 | 15.98 | 5504.7931 | 0 | 0 | 5504.7931 | Heating | 4857.1704 | 8.5 | 4857.1704 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 971.4341 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4956.2964 | 0 | 991.2593 | 9.913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 19:01 | 12 | 20 | 19 | 354 | 8491 | 15.08 | 5556.5598 | 0 | 0 | 5556.5598 | Heating | 4902.8469 | 8.5 | 4902.8469 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 980.5694 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5002.905 | 0 | 1000.581 | 10.01% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 20:01 | 12 | 20 | 20 | 354 | 8492 | 15.08 | 5525.3461 | 0 | 0 | 5525.3461 | Heating | 4875.3054 | 8.5 | 4875.3054 | 0 | 2.8087 | 0 | 0 | 0 | 0 | 8.5 | 0 | 975.0611 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4974.8014 | 0 | 994.9603 | 9.95% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 21:01 | 12 | 20 | 21 | 354 | 8493 | 12.02 | 5500.594 | 0 | 0 | 5500.594 | Heating | 4853.4653 | 8.5 | 4853.4653 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 970.6931 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4952.5156 | 0 | 990.5031 | 9.905% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 22:01 | 12 | 20 | 22 | 354 | 8494 | 10.94 | 1571.8586 | 0 | 0 | 1571.8586 | Heating | 1386.934 | 8.5 | 1386.934 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 277.3868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1415.2388 | 0 | 283.0478 | 2.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-20 23:01 | 12 | 20 | 23 | 354 | 8495 | 10.94 | 1330.3628 | 0 | 0 | 1330.3628 | Heating | 1173.8496 | 8.5 | 1173.8496 | 0 | 2.737 | 0 | 0 | 0 | 0 | 8.5 | 0 | 234.7699 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1197.8057 | 0 | 239.5611 | 2.396% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 00:01 | 12 | 21 | 0 | 355 | 8496 | 8.96 | 1469.3937 | 0 | 0 | 1469.3937 | Heating | 1296.5239 | 8.5 | 1296.5239 | 0 | 2.7067 | 0 | 0 | 0 | 0 | 8.5 | 0 | 259.3048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1322.9835 | 0 | 264.5967 | 2.646% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 01:01 | 12 | 21 | 1 | 355 | 8497 | 8.06 | 1523.0063 | 0 | 0 | 1523.0063 | Heating | 1343.8291 | 8.5 | 1343.8291 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.7658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1371.2541 | 0 | 274.2508 | 2.743% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 02:01 | 12 | 21 | 2 | 355 | 8498 | 8.06 | 1535.419 | 0 | 0 | 1535.419 | Heating | 1354.7815 | 8.5 | 1354.7815 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 270.9563 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1382.4301 | 0 | 276.486 | 2.765% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 03:01 | 12 | 21 | 3 | 355 | 8499 | 8.06 | 1539.3199 | 0 | 0 | 1539.3199 | Heating | 1358.2234 | 8.5 | 1358.2234 | 0 | 2.6935 | 0 | 0 | 0 | 0 | 8.5 | 0 | 271.6447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1385.9423 | 0 | 277.1885 | 2.772% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 04:01 | 12 | 21 | 4 | 355 | 8500 | 6.98 | 1533.018 | 0 | 0 | 1533.018 | Heating | 1352.6629 | 8.5 | 1352.6629 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 270.5326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1380.2683 | 0 | 276.0537 | 2.761% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 05:01 | 12 | 21 | 5 | 355 | 8501 | 6.98 | 1523.3843 | 0 | 0 | 1523.3843 | Heating | 1344.1626 | 8.5 | 1344.1626 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.8325 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1371.5945 | 0 | 274.3189 | 2.743% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 06:01 | 12 | 21 | 6 | 355 | 8502 | 6.98 | 1505.1466 | 0 | 0 | 1505.1466 | Heating | 1328.0705 | 8.5 | 1328.0705 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 265.6141 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1355.174 | 0 | 271.0348 | 2.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 07:01 | 12 | 21 | 7 | 355 | 8503 | 6.98 | 9169.1006 | 0 | 0 | 9169.1006 | Heating | 8090.3829 | 8.5 | 8090.3829 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1618.0766 | 32.36% | 1 | 64.72% | 0% | 0% | 0% | 29.9626 | 0 | 0 | 0 | 29.9626 | 8255.4928 | 0 | 1651.0986 | 16.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 38.2371
2007-12-21 08:01 | 12 | 21 | 8 | 355 | 8504 | 6.98 | 6898.2399 | 0 | 0 | 6898.2399 | Heating | 6086.6823 | 8.5 | 6086.6823 | 0 | 2.6781 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1217.3365 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6210.9003 | 0 | 1242.1801 | 12.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 09:01 | 12 | 21 | 9 | 355 | 8505 | 12.02 | 5889.6459 | 0 | 0 | 5889.6459 | Heating | 5196.7464 | 8.5 | 5196.7464 | 0 | 2.7546 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1039.3493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5302.8025 | 0 | 1060.5605 | 10.61% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 10:01 | 12 | 21 | 10 | 355 | 8506 | 15.98 | 4890.9486 | 0 | 0 | 4890.9486 | Heating | 4315.5429 | 8.5 | 4315.5429 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 863.1086 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4403.6152 | 0 | 880.723 | 8.807% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 11:01 | 12 | 21 | 11 | 355 | 8507 | 15.98 | 4054.3603 | 0 | 0 | 4054.3603 | Heating | 3577.3767 | 8.5 | 3577.3767 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 715.4753 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3650.3844 | 0 | 730.0769 | 7.301% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 12:01 | 12 | 21 | 12 | 355 | 8508 | 21.02 | 3375.6554 | 0 | 0 | 3375.6554 | Heating | 2978.5195 | 8.5 | 2978.5195 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 595.7039 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3039.3056 | 0 | 607.8611 | 6.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 13:01 | 12 | 21 | 13 | 355 | 8509 | 24.08 | 2970.6251 | 0 | 0 | 2970.6251 | Heating | 2621.1398 | 8.5 | 2621.1398 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 524.228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2674.6324 | 0 | 534.9265 | 5.349% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 14:01 | 12 | 21 | 14 | 355 | 8510 | 24.08 | 3025.8741 | 0 | 0 | 3025.8741 | Heating | 2669.8889 | 8.5 | 2669.8889 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 533.9778 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2724.3764 | 0 | 544.8753 | 5.449% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 15:01 | 12 | 21 | 15 | 355 | 8511 | 26.06 | 3430.6609 | 0 | 0 | 3430.6609 | Heating | 3027.0537 | 8.5 | 3027.0537 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 605.4107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3088.8304 | 0 | 617.7661 | 6.178% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 16:01 | 12 | 21 | 16 | 355 | 8512 | 26.06 | 3853.1468 | 0 | 0 | 3853.1468 | Heating | 3399.8354 | 8.5 | 3399.8354 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 679.9671 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3469.2198 | 0 | 693.844 | 6.938% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 17:01 | 12 | 21 | 17 | 355 | 8513 | 26.06 | 4122.1133 | 0 | 0 | 4122.1133 | Heating | 3637.1588 | 8.5 | 3637.1588 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.4318 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3711.3866 | 0 | 742.2773 | 7.423% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 18:01 | 12 | 21 | 18 | 355 | 8514 | 26.96 | 4381.0904 | 0 | 0 | 4381.0904 | Heating | 3865.668 | 8.5 | 3865.668 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 773.1336 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3944.5592 | 0 | 788.9118 | 7.889% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 19:01 | 12 | 21 | 19 | 355 | 8515 | 26.96 | 4818.9604 | 0 | 0 | 4818.9604 | Heating | 4252.0239 | 8.5 | 4252.0239 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 850.4048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4338.7999 | 0 | 867.76 | 8.678% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 20:01 | 12 | 21 | 20 | 355 | 8516 | 26.96 | 5471.5608 | 0 | 0 | 5471.5608 | Heating | 4827.8478 | 8.5 | 4827.8478 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 965.5696 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4926.3753 | 0 | 985.2751 | 9.853% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 21:01 | 12 | 21 | 21 | 355 | 8517 | 26.96 | 5931.3335 | 0 | 0 | 5931.3335 | Heating | 5233.5296 | 8.5 | 5233.5296 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1046.7059 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5340.3363 | 0 | 1068.0673 | 10.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 22:01 | 12 | 21 | 22 | 355 | 8518 | 26.96 | 6572.2019 | 0 | 0 | 6572.2019 | Heating | 5799.0017 | 8.5 | 5799.0017 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1159.8003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5917.3486 | 0 | 1183.4697 | 11.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-21 23:01 | 12 | 21 | 23 | 355 | 8519 | 26.96 | 2013.1071 | 0 | 0 | 2013.1071 | Heating | 1776.271 | 8.5 | 1776.271 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 355.2542 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1812.5214 | 0 | 362.5043 | 3.625% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 00:01 | 12 | 22 | 0 | 356 | 8520 | 26.96 | 2049.5987 | 0 | 0 | 2049.5987 | Heating | 1808.4694 | 8.5 | 1808.4694 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 361.6939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1845.3769 | 0 | 369.0754 | 3.691% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 01:01 | 12 | 22 | 1 | 356 | 8521 | 26.96 | 2072.0116 | 0 | 0 | 2072.0116 | Heating | 1828.2455 | 8.5 | 1828.2455 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 365.6491 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1865.5566 | 0 | 373.1113 | 3.731% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 02:01 | 12 | 22 | 2 | 356 | 8522 | 26.96 | 2106.7256 | 0 | 0 | 2106.7256 | Heating | 1858.8755 | 8.5 | 1858.8755 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 371.7751 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1896.8118 | 0 | 379.3624 | 3.794% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 03:01 | 12 | 22 | 3 | 356 | 8523 | 23 | 2157.0605 | 0 | 0 | 2157.0605 | Heating | 1903.2887 | 8.5 | 1903.2887 | 0 | 2.9925 | 0 | 0 | 0 | 0 | 8.5 | 0 | 380.6577 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1942.1313 | 0 | 388.4263 | 3.884% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 04:01 | 12 | 22 | 4 | 356 | 8524 | 21.02 | 2201.9386 | 0 | 0 | 2201.9386 | Heating | 1942.887 | 8.5 | 1942.887 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 388.5774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1982.5378 | 0 | 396.5076 | 3.965% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 05:01 | 12 | 22 | 5 | 356 | 8525 | 21.02 | 2235.0925 | 0 | 0 | 2235.0925 | Heating | 1972.1404 | 8.5 | 1972.1404 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 394.4281 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2012.3882 | 0 | 402.4776 | 4.025% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 06:01 | 12 | 22 | 6 | 356 | 8526 | 24.08 | 2244.8498 | 0 | 0 | 2244.8498 | Heating | 1980.7498 | 8.5 | 1980.7498 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 396.15 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2021.1733 | 0 | 404.2347 | 4.042% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 07:01 | 12 | 22 | 7 | 356 | 8527 | 21.02 | 2248.2875 | 0 | 0 | 2248.2875 | Heating | 1983.7831 | 8.5 | 1983.7831 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 396.7566 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2024.2685 | 0 | 404.8537 | 4.049% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 08:01 | 12 | 22 | 8 | 356 | 8528 | 21.02 | 2181.6057 | 0 | 0 | 2181.6057 | Heating | 1924.9462 | 8.5 | 1924.9462 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 384.9892 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1964.2309 | 0 | 392.8462 | 3.928% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 09:01 | 12 | 22 | 9 | 356 | 8529 | 26.06 | 11121.5514 | 0 | 0 | 11121.5514 | Heating | 9813.1336 | 8.5 | 9813.1336 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1962.6267 | 39.25% | 1 | 78.51% | 0% | 0% | 0% | 46.7098 | 0 | 0 | 0 | 46.7098 | 10013.4016 | 0 | 2002.6803 | 20.03% | 1 | 40.05% | 0% | 0% | 4.9681 | 0 | 0 | 4.9681 | 51.6779
2007-12-22 10:01 | 12 | 22 | 10 | 356 | 8530 | 30.02 | 8393.0559 | 0 | 0 | 8393.0559 | Heating | 7405.6375 | 8.5 | 7405.6375 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1481.1275 | 30% | 1 | 59.25% | 0% | 0% | 0% | 24.448 | 0 | 0 | 0 | 24.448 | 7556.773 | 0 | 1511.3546 | 15.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.7226
2007-12-22 11:01 | 12 | 22 | 11 | 356 | 8531 | 30.02 | 7057.5006 | 0 | 0 | 7057.5006 | Heating | 6227.2064 | 8.5 | 6227.2064 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1245.4413 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6354.2922 | 0 | 1270.8584 | 12.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 12:01 | 12 | 22 | 12 | 356 | 8532 | 35.96 | 6144.2525 | 0 | 0 | 6144.2525 | Heating | 5421.3992 | 8.5 | 5421.3992 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1084.2798 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5532.04 | 0 | 1106.408 | 11.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 13:01 | 12 | 22 | 13 | 356 | 8533 | 37.04 | 5178.7781 | 0 | 0 | 5178.7781 | Heating | 4569.5101 | 8.5 | 4569.5101 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 913.902 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4662.7654 | 0 | 932.5531 | 9.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 14:01 | 12 | 22 | 14 | 356 | 8534 | 37.04 | 4804.6628 | 0 | 0 | 4804.6628 | Heating | 4239.4083 | 8.5 | 4239.4083 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 847.8817 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4325.9269 | 0 | 865.1854 | 8.652% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 15:01 | 12 | 22 | 15 | 356 | 8535 | 37.04 | 4597.4037 | 0 | 0 | 4597.4037 | Heating | 4056.5327 | 8.5 | 4056.5327 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 811.3065 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4139.3191 | 0 | 827.8638 | 8.279% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 16:01 | 12 | 22 | 16 | 356 | 8536 | 35.06 | 4453.1291 | 0 | 0 | 4453.1291 | Heating | 3929.2316 | 8.5 | 3929.2316 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 785.8463 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4009.42 | 0 | 801.884 | 8.019% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 17:01 | 12 | 22 | 17 | 356 | 8537 | 35.06 | 4574.9795 | 0 | 0 | 4574.9795 | Heating | 4036.7466 | 8.5 | 4036.7466 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 807.3493 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4119.1292 | 0 | 823.8258 | 8.238% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 18:01 | 12 | 22 | 18 | 356 | 8538 | 28.94 | 6391.0008 | 0 | 0 | 6391.0008 | Heating | 5639.1183 | 8.5 | 5639.1183 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1127.8237 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5754.2024 | 0 | 1150.8405 | 11.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 19:01 | 12 | 22 | 19 | 356 | 8539 | 26.96 | 6933.2025 | 0 | 0 | 6933.2025 | Heating | 6117.5316 | 8.5 | 6117.5316 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1223.5063 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6242.3792 | 0 | 1248.4758 | 12.48% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 20:01 | 12 | 22 | 20 | 356 | 8540 | 26.96 | 1706.6957 | 0 | 0 | 1706.6957 | Heating | 1505.908 | 8.5 | 1505.908 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 301.1816 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1536.6408 | 0 | 307.3282 | 3.073% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 21:01 | 12 | 22 | 21 | 356 | 8541 | 26.06 | 1776.5588 | 0 | 0 | 1776.5588 | Heating | 1567.5519 | 8.5 | 1567.5519 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 313.5104 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1599.5428 | 0 | 319.9086 | 3.199% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 22:01 | 12 | 22 | 22 | 356 | 8542 | 26.06 | 1847.126 | 0 | 0 | 1847.126 | Heating | 1629.8171 | 8.5 | 1629.8171 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 325.9634 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1663.0787 | 0 | 332.6157 | 3.326% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-22 23:01 | 12 | 22 | 23 | 356 | 8543 | 26.06 | 1909.3258 | 0 | 0 | 1909.3258 | Heating | 1684.6992 | 8.5 | 1684.6992 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 336.9398 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1719.0808 | 0 | 343.8162 | 3.438% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 00:01 | 12 | 23 | 0 | 357 | 8544 | 28.94 | 1959.8808 | 0 | 0 | 1959.8808 | Heating | 1729.3066 | 8.5 | 1729.3066 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 345.8613 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1764.5986 | 0 | 352.9197 | 3.529% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 01:01 | 12 | 23 | 1 | 357 | 8545 | 30.02 | 1993.4479 | 0 | 0 | 1993.4479 | Heating | 1758.9246 | 8.5 | 1758.9246 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 351.7849 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1794.8211 | 0 | 358.9642 | 3.59% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 02:01 | 12 | 23 | 2 | 357 | 8546 | 30.02 | 1993.3214 | 0 | 0 | 1993.3214 | Heating | 1758.813 | 8.5 | 1758.813 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 351.7626 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1794.7072 | 0 | 358.9414 | 3.589% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 03:01 | 12 | 23 | 3 | 357 | 8547 | 30.92 | 1976.5289 | 0 | 0 | 1976.5289 | Heating | 1743.9961 | 8.5 | 1743.9961 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 348.7992 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1779.5878 | 0 | 355.9176 | 3.559% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 04:01 | 12 | 23 | 4 | 357 | 8548 | 30.92 | 1952.5032 | 0 | 0 | 1952.5032 | Heating | 1722.797 | 8.5 | 1722.797 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 344.5594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1757.9561 | 0 | 351.5912 | 3.516% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 05:01 | 12 | 23 | 5 | 357 | 8549 | 30.02 | 1914.9183 | 0 | 0 | 1914.9183 | Heating | 1689.6338 | 8.5 | 1689.6338 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 337.9268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1724.1161 | 0 | 344.8232 | 3.448% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 06:01 | 12 | 23 | 6 | 357 | 8550 | 28.94 | 1865.2735 | 0 | 0 | 1865.2735 | Heating | 1645.8296 | 8.5 | 1645.8296 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 329.1659 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1679.4179 | 0 | 335.8836 | 3.359% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 07:01 | 12 | 23 | 7 | 357 | 8551 | 30.02 | 11158.2869 | 0 | 0 | 11158.2869 | Heating | 9845.5472 | 8.5 | 9845.5472 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1969.1094 | 39.38% | 1 | 78.76% | 0% | 0% | 0% | 47.0654 | 0 | 0 | 0 | 47.0654 | 10046.4768 | 0 | 2009.2954 | 20.09% | 1 | 40.19% | 0% | 0% | 5.0059 | 0 | 0 | 5.0059 | 52.0713
2007-12-23 08:01 | 12 | 23 | 8 | 357 | 8552 | 28.94 | 8393.0085 | 0 | 0 | 8393.0085 | Heating | 7405.5958 | 8.5 | 7405.5958 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1481.1192 | 30% | 1 | 59.24% | 0% | 0% | 0% | 24.4477 | 0 | 0 | 0 | 24.4477 | 7556.7304 | 0 | 1511.3461 | 15.11% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.7222
2007-12-23 09:01 | 12 | 23 | 9 | 357 | 8553 | 28.94 | 6711.1106 | 0 | 0 | 6711.1106 | Heating | 5921.5682 | 8.5 | 5921.5682 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1184.3136 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6042.4165 | 0 | 1208.4833 | 12.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 10:01 | 12 | 23 | 10 | 357 | 8554 | 28.94 | 5270.8793 | 0 | 0 | 5270.8793 | Heating | 4650.7759 | 8.5 | 4650.7759 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 930.1552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4745.6897 | 0 | 949.1379 | 9.491% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 11:01 | 12 | 23 | 11 | 357 | 8555 | 30.92 | 4302.9644 | 0 | 0 | 4302.9644 | Heating | 3796.7333 | 8.5 | 3796.7333 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 759.3467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3874.2176 | 0 | 774.8435 | 7.748% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 12:01 | 12 | 23 | 12 | 357 | 8556 | 33.08 | 3454.5572 | 0 | 0 | 3454.5572 | Heating | 3048.1387 | 8.5 | 3048.1387 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 609.6277 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3110.3457 | 0 | 622.0691 | 6.221% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 13:01 | 12 | 23 | 13 | 357 | 8557 | 35.06 | 2843.2255 | 0 | 0 | 2843.2255 | Heating | 2508.7284 | 8.5 | 2508.7284 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 501.7457 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2559.9269 | 0 | 511.9854 | 5.12% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 14:01 | 12 | 23 | 14 | 357 | 8558 | 35.06 | 2670.2404 | 0 | 0 | 2670.2404 | Heating | 2356.0945 | 8.5 | 2356.0945 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 471.2189 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2404.178 | 0 | 480.8356 | 4.808% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 15:01 | 12 | 23 | 15 | 357 | 8559 | 39.02 | 2738.045 | 0 | 0 | 2738.045 | Heating | 2415.9221 | 8.5 | 2415.9221 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 483.1844 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2465.2266 | 0 | 493.0453 | 4.93% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 16:01 | 12 | 23 | 16 | 357 | 8560 | 37.94 | 2876.7818 | 0 | 0 | 2876.7818 | Heating | 2538.3369 | 8.5 | 2538.3369 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 507.6674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2590.1397 | 0 | 518.0279 | 5.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 17:01 | 12 | 23 | 17 | 357 | 8561 | 37.94 | 3151.0834 | 0 | 0 | 3151.0834 | Heating | 2780.3677 | 8.5 | 2780.3677 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 556.0735 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2837.1099 | 0 | 567.422 | 5.674% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 18:01 | 12 | 23 | 18 | 357 | 8562 | 35.96 | 3491.9742 | 0 | 0 | 3491.9742 | Heating | 3081.1537 | 8.5 | 3081.1537 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 616.2307 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3144.0344 | 0 | 628.8069 | 6.288% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 19:01 | 12 | 23 | 19 | 357 | 8563 | 35.06 | 3709.1473 | 0 | 0 | 3709.1473 | Heating | 3272.777 | 8.5 | 3272.777 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 654.5554 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3339.5684 | 0 | 667.9137 | 6.679% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 20:01 | 12 | 23 | 20 | 357 | 8564 | 35.06 | 4084.1416 | 0 | 0 | 4084.1416 | Heating | 3603.6544 | 8.5 | 3603.6544 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 720.7309 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3677.1983 | 0 | 735.4397 | 7.354% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 21:01 | 12 | 23 | 21 | 357 | 8565 | 35.6 | 4586.3419 | 0 | 0 | 4586.3419 | Heating | 4046.7722 | 8.5 | 4046.7722 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 809.3544 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4129.3594 | 0 | 825.8719 | 8.259% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 22:01 | 12 | 23 | 22 | 357 | 8566 | 35.96 | 1432.0937 | 0 | 0 | 1432.0937 | Heating | 1263.6121 | 8.5 | 1263.6121 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 252.7224 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1289.4001 | 0 | 257.88 | 2.579% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-23 23:01 | 12 | 23 | 23 | 357 | 8567 | 35.06 | 1288.1238 | 0 | 0 | 1288.1238 | Heating | 1136.5798 | 8.5 | 1136.5798 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 227.316 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1159.7754 | 0 | 231.9551 | 2.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 00:01 | 12 | 24 | 0 | 358 | 8568 | 35.96 | 1522.418 | 0 | 0 | 1522.418 | Heating | 1343.31 | 8.5 | 1343.31 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 268.662 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1370.7245 | 0 | 274.1449 | 2.741% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 01:01 | 12 | 24 | 1 | 358 | 8569 | 35.96 | 1659.5888 | 0 | 0 | 1659.5888 | Heating | 1464.3431 | 8.5 | 1464.3431 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 292.8686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1494.2276 | 0 | 298.8455 | 2.988% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 02:01 | 12 | 24 | 2 | 358 | 8570 | 35.96 | 1813.5706 | 0 | 0 | 1813.5706 | Heating | 1600.2094 | 8.5 | 1600.2094 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 320.0419 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1632.8667 | 0 | 326.5733 | 3.266% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 03:01 | 12 | 24 | 3 | 358 | 8571 | 35.06 | 1985.3699 | 0 | 0 | 1985.3699 | Heating | 1751.797 | 8.5 | 1751.797 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 350.3594 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1787.5479 | 0 | 357.5096 | 3.575% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 04:01 | 12 | 24 | 4 | 358 | 8572 | 33.98 | 2148.9484 | 0 | 0 | 2148.9484 | Heating | 1896.131 | 8.5 | 1896.131 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.2262 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1934.8275 | 0 | 386.9655 | 3.87% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 05:01 | 12 | 24 | 5 | 358 | 8573 | 33.98 | 2268.028 | 0 | 0 | 2268.028 | Heating | 2001.2012 | 8.5 | 2001.2012 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 400.2402 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2042.0421 | 0 | 408.4084 | 4.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 06:01 | 12 | 24 | 6 | 358 | 8574 | 35.96 | 2336.935 | 0 | 0 | 2336.935 | Heating | 2062.0015 | 8.5 | 2062.0015 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.4003 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2104.0832 | 0 | 420.8166 | 4.208% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 07:01 | 12 | 24 | 7 | 358 | 8575 | 33.98 | 13230.1829 | 0 | 0 | 13230.1829 | Heating | 11673.6908 | 8.5 | 11673.6908 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2334.7382 | 46.69% | 1 | 93.39% | 0% | 0% | 0% | 69.6352 | 0 | 0 | 0 | 69.6352 | 11911.9294 | 0 | 2382.3859 | 23.82% | 1 | 47.65% | 0% | 0% | 7.4064 | 0 | 0 | 7.4064 | 77.0416
2007-12-24 08:01 | 12 | 24 | 8 | 358 | 8576 | 33.98 | 10151.6678 | 0 | 0 | 10151.6678 | Heating | 8957.354 | 8.5 | 8957.354 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1791.4708 | 35.83% | 1 | 71.66% | 0% | 0% | 0% | 37.8672 | 0 | 0 | 0 | 37.8672 | 9140.1571 | 0 | 1828.0314 | 18.28% | 1 | 36.56% | 0% | 0% | 4.0276 | 0 | 0 | 4.0276 | 41.8948
2007-12-24 09:01 | 12 | 24 | 9 | 358 | 8577 | 33.98 | 8079.8423 | 0 | 0 | 8079.8423 | Heating | 7129.2726 | 8.5 | 7129.2726 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1425.8545 | 30% | 1 | 57.03% | 0% | 0% | 0% | 22.4003 | 0 | 0 | 0 | 22.4003 | 7274.7679 | 0 | 1454.9536 | 14.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 30.6749
2007-12-24 10:01 | 12 | 24 | 10 | 358 | 8578 | 39.92 | 6281.3726 | 0 | 0 | 6281.3726 | Heating | 5542.3876 | 8.5 | 5542.3876 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1108.4775 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5655.4976 | 0 | 1131.0995 | 11.31% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 11:01 | 12 | 24 | 11 | 358 | 8579 | 39.92 | 5267.6357 | 0 | 0 | 5267.6357 | Heating | 4647.9138 | 8.5 | 4647.9138 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 929.5828 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4742.7692 | 0 | 948.5538 | 9.486% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 12:01 | 12 | 24 | 12 | 358 | 8580 | 42.98 | 4577.8624 | 0 | 0 | 4577.8624 | Heating | 4039.2903 | 8.5 | 4039.2903 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 807.8581 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4121.7248 | 0 | 824.345 | 8.243% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 13:01 | 12 | 24 | 13 | 358 | 8581 | 44.06 | 4165.2562 | 0 | 0 | 4165.2562 | Heating | 3675.2261 | 8.5 | 3675.2261 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 735.0452 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3750.2307 | 0 | 750.0461 | 7.5% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 14:01 | 12 | 24 | 14 | 358 | 8582 | 44.06 | 3958.2587 | 0 | 0 | 3958.2587 | Heating | 3492.5812 | 8.5 | 3492.5812 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 698.5162 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3563.8584 | 0 | 712.7717 | 7.128% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 15:01 | 12 | 24 | 15 | 358 | 8583 | 44.06 | 3927.7078 | 0 | 0 | 3927.7078 | Heating | 3465.6245 | 8.5 | 3465.6245 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 693.1249 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3536.3515 | 0 | 707.2703 | 7.073% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 16:01 | 12 | 24 | 16 | 358 | 8584 | 41 | 3933.8832 | 0 | 0 | 3933.8832 | Heating | 3471.0734 | 8.5 | 3471.0734 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 694.2147 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3541.9117 | 0 | 708.3823 | 7.084% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 17:01 | 12 | 24 | 17 | 358 | 8585 | 41 | 3943.0784 | 0 | 0 | 3943.0784 | Heating | 3479.1869 | 8.5 | 3479.1869 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 695.8374 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3550.1907 | 0 | 710.0381 | 7.1% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 18:01 | 12 | 24 | 18 | 358 | 8586 | 33.08 | 4011.049 | 0 | 0 | 4011.049 | Heating | 3539.1609 | 8.5 | 3539.1609 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 707.8322 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3611.3886 | 0 | 722.2777 | 7.223% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 19:01 | 12 | 24 | 19 | 358 | 8587 | 33.98 | 3966.866 | 0 | 0 | 3966.866 | Heating | 3500.1759 | 8.5 | 3500.1759 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 700.0352 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3571.608 | 0 | 714.3216 | 7.143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 20:01 | 12 | 24 | 20 | 358 | 8588 | 33.98 | 4094.5675 | 0 | 0 | 4094.5675 | Heating | 3612.8537 | 8.5 | 3612.8537 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 722.5707 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3686.5854 | 0 | 737.3171 | 7.373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 21:01 | 12 | 24 | 21 | 358 | 8589 | 32 | 4332.6099 | 0 | 0 | 4332.6099 | Heating | 3822.8911 | 8.5 | 3822.8911 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 764.5782 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3900.9093 | 0 | 780.1819 | 7.802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 22:01 | 12 | 24 | 22 | 358 | 8590 | 35.96 | 1278.8194 | 0 | 0 | 1278.8194 | Heating | 1128.37 | 8.5 | 1128.37 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 225.674 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1151.398 | 0 | 230.2796 | 2.303% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-24 23:01 | 12 | 24 | 23 | 358 | 8591 | 35.96 | 1101.4199 | 0 | 0 | 1101.4199 | Heating | 971.8411 | 8.5 | 971.8411 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 194.3682 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 991.6746 | 0 | 198.3349 | 1.983% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 00:01 | 12 | 25 | 0 | 359 | 8592 | 35.96 | 1322.1671 | 0 | 0 | 1322.1671 | Heating | 1166.618 | 8.5 | 1166.618 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 233.3236 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1190.4266 | 0 | 238.0853 | 2.381% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 01:01 | 12 | 25 | 1 | 359 | 8593 | 35.96 | 1493.5267 | 0 | 0 | 1493.5267 | Heating | 1317.8176 | 8.5 | 1317.8176 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 263.5635 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1344.7119 | 0 | 268.9424 | 2.689% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 02:01 | 12 | 25 | 2 | 359 | 8594 | 35.96 | 1571.1806 | 0 | 0 | 1571.1806 | Heating | 1386.3358 | 8.5 | 1386.3358 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 277.2672 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1414.6284 | 0 | 282.9257 | 2.829% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 03:01 | 12 | 25 | 3 | 359 | 8595 | 35.96 | 1598.9282 | 0 | 0 | 1598.9282 | Heating | 1410.819 | 8.5 | 1410.819 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 282.1638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1439.6112 | 0 | 287.9222 | 2.879% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 04:01 | 12 | 25 | 4 | 359 | 8596 | 35.96 | 1614.512 | 0 | 0 | 1614.512 | Heating | 1424.5694 | 8.5 | 1424.5694 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 284.9139 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1453.6423 | 0 | 290.7285 | 2.907% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 05:01 | 12 | 25 | 5 | 359 | 8597 | 35.96 | 1645.1805 | 0 | 0 | 1645.1805 | Heating | 1451.6299 | 8.5 | 1451.6299 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 290.326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1481.255 | 0 | 296.251 | 2.963% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 06:01 | 12 | 25 | 6 | 359 | 8598 | 37.94 | 1677.4372 | 0 | 0 | 1677.4372 | Heating | 1480.0916 | 8.5 | 1480.0916 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 296.0183 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1510.2976 | 0 | 302.0595 | 3.021% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 07:01 | 12 | 25 | 7 | 359 | 8599 | 39.02 | 9330.9475 | 0 | 0 | 9330.9475 | Heating | 8233.189 | 8.5 | 8233.189 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1646.6378 | 32.93% | 1 | 65.87% | 0% | 0% | 0% | 31.193 | 0 | 0 | 0 | 31.193 | 8401.2132 | 0 | 1680.2426 | 16.8% | 1 | 33.6% | 0% | 0% | 3.3177 | 0 | 0 | 3.3177 | 34.5107
2007-12-25 08:01 | 12 | 25 | 8 | 359 | 8600 | 39.02 | 7215.4152 | 0 | 0 | 7215.4152 | Heating | 6366.5429 | 8.5 | 6366.5429 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1273.3086 | 30% | 1 | 50.93% | 0% | 0% | 0% | 17.2675 | 0 | 0 | 0 | 17.2675 | 6496.4723 | 0 | 1299.2945 | 12.99% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.542
2007-12-25 09:01 | 12 | 25 | 9 | 359 | 8601 | 37.94 | 6283.9696 | 0 | 0 | 6283.9696 | Heating | 5544.6791 | 8.5 | 5544.6791 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1108.9358 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5657.8358 | 0 | 1131.5672 | 11.32% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 10:01 | 12 | 25 | 10 | 359 | 8602 | 37.04 | 5265.4175 | 0 | 0 | 5265.4175 | Heating | 4645.9566 | 8.5 | 4645.9566 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 929.1913 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4740.7721 | 0 | 948.1544 | 9.482% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 11:01 | 12 | 25 | 11 | 359 | 8603 | 37.04 | 4721.1533 | 0 | 0 | 4721.1533 | Heating | 4165.7235 | 8.5 | 4165.7235 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 833.1447 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4250.7382 | 0 | 850.1476 | 8.501% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 12:01 | 12 | 25 | 12 | 359 | 8604 | 35.96 | 4227.9663 | 0 | 0 | 4227.9663 | Heating | 3730.5585 | 8.5 | 3730.5585 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 746.1117 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3806.6924 | 0 | 761.3385 | 7.613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 13:01 | 12 | 25 | 13 | 359 | 8605 | 37.4 | 3931.6646 | 0 | 0 | 3931.6646 | Heating | 3469.1158 | 8.5 | 3469.1158 | 0 | 3.5838 | 0 | 0 | 0 | 0 | 8.5 | 0 | 693.8232 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3539.9141 | 0 | 707.9828 | 7.08% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 14:01 | 12 | 25 | 14 | 359 | 8606 | 37.94 | 3779.4632 | 0 | 0 | 3779.4632 | Heating | 3334.8204 | 8.5 | 3334.8204 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 666.9641 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3402.878 | 0 | 680.5756 | 6.806% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 15:01 | 12 | 25 | 15 | 359 | 8607 | 39.02 | 3725.098 | 0 | 0 | 3725.098 | Heating | 3286.8512 | 8.5 | 3286.8512 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 657.3702 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3353.9298 | 0 | 670.786 | 6.708% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 16:01 | 12 | 25 | 16 | 359 | 8608 | 39.02 | 3646.9757 | 0 | 0 | 3646.9757 | Heating | 3217.9198 | 8.5 | 3217.9198 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 643.584 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3283.5916 | 0 | 656.7183 | 6.567% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 17:01 | 12 | 25 | 17 | 359 | 8609 | 39.92 | 3842.7241 | 0 | 0 | 3842.7241 | Heating | 3390.6389 | 8.5 | 3390.6389 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 678.1278 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3459.8356 | 0 | 691.9671 | 6.92% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 18:01 | 12 | 25 | 18 | 359 | 8610 | 41 | 4156.8871 | 0 | 0 | 4156.8871 | Heating | 3667.8416 | 8.5 | 3667.8416 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 733.5683 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3742.6955 | 0 | 748.5391 | 7.485% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 19:01 | 12 | 25 | 19 | 359 | 8611 | 41 | 4593.7669 | 0 | 0 | 4593.7669 | Heating | 4053.3238 | 8.5 | 4053.3238 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 810.6648 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4136.0446 | 0 | 827.2089 | 8.272% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 20:01 | 12 | 25 | 20 | 359 | 8612 | 41 | 4886.2952 | 0 | 0 | 4886.2952 | Heating | 4311.437 | 8.5 | 4311.437 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 862.2874 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4399.4255 | 0 | 879.8851 | 8.799% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 21:01 | 12 | 25 | 21 | 359 | 8613 | 41 | 5014.5177 | 0 | 0 | 5014.5177 | Heating | 4424.5744 | 8.5 | 4424.5744 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 884.9149 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4514.8719 | 0 | 902.9744 | 9.03% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 22:01 | 12 | 25 | 22 | 359 | 8614 | 39.92 | 1759.3052 | 0 | 0 | 1759.3052 | Heating | 1552.3281 | 8.5 | 1552.3281 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 310.4656 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1584.0083 | 0 | 316.8017 | 3.168% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-25 23:01 | 12 | 25 | 23 | 359 | 8615 | 39.92 | 1834.6049 | 0 | 0 | 1834.6049 | Heating | 1618.769 | 8.5 | 1618.769 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 323.7538 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1651.8051 | 0 | 330.361 | 3.304% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 00:01 | 12 | 26 | 0 | 360 | 8616 | 39.02 | 1941.2448 | 0 | 0 | 1941.2448 | Heating | 1712.8631 | 8.5 | 1712.8631 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 342.5726 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1747.8194 | 0 | 349.5639 | 3.496% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 01:01 | 12 | 26 | 1 | 360 | 8617 | 39.92 | 2052.9231 | 0 | 0 | 2052.9231 | Heating | 1811.4027 | 8.5 | 1811.4027 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.2805 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1848.3701 | 0 | 369.674 | 3.697% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 02:01 | 12 | 26 | 2 | 360 | 8618 | 39.92 | 2116.5992 | 0 | 0 | 2116.5992 | Heating | 1867.5875 | 8.5 | 1867.5875 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 373.5175 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1905.7015 | 0 | 381.1403 | 3.811% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 03:01 | 12 | 26 | 3 | 360 | 8619 | 39.92 | 2146.5671 | 0 | 0 | 2146.5671 | Heating | 1894.0298 | 8.5 | 1894.0298 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 378.806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1932.6834 | 0 | 386.5367 | 3.865% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 04:01 | 12 | 26 | 4 | 360 | 8620 | 39.02 | 2173.0171 | 0 | 0 | 2173.0171 | Heating | 1917.3681 | 8.5 | 1917.3681 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 383.4736 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1956.498 | 0 | 391.2996 | 3.913% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 05:01 | 12 | 26 | 5 | 360 | 8621 | 39.02 | 2198.2159 | 0 | 0 | 2198.2159 | Heating | 1939.6023 | 8.5 | 1939.6023 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 387.9205 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1979.186 | 0 | 395.8372 | 3.958% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 06:01 | 12 | 26 | 6 | 360 | 8622 | 39.02 | 2206.5604 | 0 | 0 | 2206.5604 | Heating | 1946.9651 | 8.5 | 1946.9651 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 389.393 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1986.6991 | 0 | 397.3398 | 3.973% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 07:01 | 12 | 26 | 7 | 360 | 8623 | 37.94 | 10655.8188 | 0 | 0 | 10655.8188 | Heating | 9402.193 | 8.5 | 9402.193 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1880.4386 | 37.61% | 1 | 75.22% | 0% | 0% | 0% | 42.3328 | 0 | 0 | 0 | 42.3328 | 9594.0745 | 0 | 1918.8149 | 19.19% | 1 | 38.38% | 0% | 0% | 4.5025 | 0 | 0 | 4.5025 | 46.8354
2007-12-26 08:01 | 12 | 26 | 8 | 360 | 8624 | 37.94 | 8357.3532 | 0 | 0 | 8357.3532 | Heating | 7374.1352 | 8.5 | 7374.1352 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1474.827 | 30% | 1 | 58.99% | 0% | 0% | 0% | 24.2095 | 0 | 0 | 0 | 24.2095 | 7524.6277 | 0 | 1504.9255 | 15.05% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 32.484
2007-12-26 09:01 | 12 | 26 | 9 | 360 | 8625 | 39.92 | 7254.8168 | 0 | 0 | 7254.8168 | Heating | 6401.3089 | 8.5 | 6401.3089 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1280.2618 | 30% | 1 | 51.21% | 0% | 0% | 0% | 17.4851 | 0 | 0 | 0 | 17.4851 | 6531.9479 | 0 | 1306.3896 | 13.06% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 25.7596
2007-12-26 10:01 | 12 | 26 | 10 | 360 | 8626 | 41 | 5960.0221 | 0 | 0 | 5960.0221 | Heating | 5258.8431 | 8.5 | 5258.8431 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1051.7686 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5366.1664 | 0 | 1073.2333 | 10.73% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 11:01 | 12 | 26 | 11 | 360 | 8627 | 41 | 5182.8868 | 0 | 0 | 5182.8868 | Heating | 4573.1355 | 8.5 | 4573.1355 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 914.6271 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4666.4647 | 0 | 933.2929 | 9.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 12:01 | 12 | 26 | 12 | 360 | 8628 | 39.92 | 4518.0043 | 0 | 0 | 4518.0043 | Heating | 3986.4744 | 8.5 | 3986.4744 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 797.2949 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4067.831 | 0 | 813.5662 | 8.136% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 13:01 | 12 | 26 | 13 | 360 | 8629 | 39.92 | 4102.6323 | 0 | 0 | 4102.6323 | Heating | 3619.9697 | 8.5 | 3619.9697 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 723.9939 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3693.8466 | 0 | 738.7693 | 7.388% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 14:01 | 12 | 26 | 14 | 360 | 8630 | 39.92 | 4049.6432 | 0 | 0 | 4049.6432 | Heating | 3573.2146 | 8.5 | 3573.2146 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 714.6429 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3646.1373 | 0 | 729.2275 | 7.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 15:01 | 12 | 26 | 15 | 360 | 8631 | 37.94 | 4125.2587 | 0 | 0 | 4125.2587 | Heating | 3639.9342 | 8.5 | 3639.9342 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.9868 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3714.2185 | 0 | 742.8437 | 7.428% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 16:01 | 12 | 26 | 16 | 360 | 8632 | 35.06 | 4252.0165 | 0 | 0 | 4252.0165 | Heating | 3751.7792 | 8.5 | 3751.7792 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 750.3558 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3828.3462 | 0 | 765.6692 | 7.657% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 17:01 | 12 | 26 | 17 | 360 | 8633 | 35.06 | 4675.822 | 0 | 0 | 4675.822 | Heating | 4125.7253 | 8.5 | 4125.7253 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 825.1451 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4209.9238 | 0 | 841.9848 | 8.42% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 18:01 | 12 | 26 | 18 | 360 | 8634 | 28.94 | 5239.7966 | 0 | 0 | 5239.7966 | Heating | 4623.3499 | 8.5 | 4623.3499 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 924.67 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4717.704 | 0 | 943.5408 | 9.435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 19:01 | 12 | 26 | 19 | 360 | 8635 | 26.96 | 5928.7997 | 0 | 0 | 5928.7997 | Heating | 5231.2939 | 8.5 | 5231.2939 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1046.2588 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5338.055 | 0 | 1067.611 | 10.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 20:01 | 12 | 26 | 20 | 360 | 8636 | 26.96 | 6432.8632 | 0 | 0 | 6432.8632 | Heating | 5676.0558 | 8.5 | 5676.0558 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1135.2112 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5791.8936 | 0 | 1158.3787 | 11.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 21:01 | 12 | 26 | 21 | 360 | 8637 | 24.08 | 6741.5238 | 0 | 0 | 6741.5238 | Heating | 5948.4034 | 8.5 | 5948.4034 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1189.6807 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6069.7994 | 0 | 1213.9599 | 12.14% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 22:01 | 12 | 26 | 22 | 360 | 8638 | 21.92 | 2381.5819 | 0 | 0 | 2381.5819 | Heating | 2101.3958 | 8.5 | 2101.3958 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 420.2792 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2144.2814 | 0 | 428.8563 | 4.289% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-26 23:01 | 12 | 26 | 23 | 360 | 8639 | 21.92 | 2423.1892 | 0 | 0 | 2423.1892 | Heating | 2138.1081 | 8.5 | 2138.1081 | 0 | 2.9629 | 0 | 0 | 0 | 0 | 8.5 | 0 | 427.6216 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2181.743 | 0 | 436.3486 | 4.363% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 00:01 | 12 | 27 | 0 | 361 | 8640 | 21.02 | 2435.9711 | 0 | 0 | 2435.9711 | Heating | 2149.3862 | 8.5 | 2149.3862 | 0 | 2.9394 | 0 | 0 | 0 | 0 | 8.5 | 0 | 429.8772 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2193.2513 | 0 | 438.6503 | 4.387% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 01:01 | 12 | 27 | 1 | 361 | 8641 | 19.94 | 2429.1513 | 0 | 0 | 2429.1513 | Heating | 2143.3688 | 8.5 | 2143.3688 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 428.6738 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2187.111 | 0 | 437.4222 | 4.374% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 02:01 | 12 | 27 | 2 | 361 | 8642 | 19.94 | 2406.0494 | 0 | 0 | 2406.0494 | Heating | 2122.9847 | 8.5 | 2122.9847 | 0 | 2.9127 | 0 | 0 | 0 | 0 | 8.5 | 0 | 424.5969 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2166.311 | 0 | 433.2622 | 4.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 03:01 | 12 | 27 | 3 | 361 | 8643 | 19.04 | 2383.6511 | 0 | 0 | 2383.6511 | Heating | 2103.2215 | 8.5 | 2103.2215 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 420.6443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2146.1444 | 0 | 429.2289 | 4.292% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 04:01 | 12 | 27 | 4 | 361 | 8644 | 17.96 | 2352.9101 | 0 | 0 | 2352.9101 | Heating | 2076.0972 | 8.5 | 2076.0972 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 415.2194 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2118.4665 | 0 | 423.6933 | 4.237% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 05:01 | 12 | 27 | 5 | 361 | 8645 | 17.96 | 2337.8764 | 0 | 0 | 2337.8764 | Heating | 2062.8322 | 8.5 | 2062.8322 | 0 | 2.8673 | 0 | 0 | 0 | 0 | 8.5 | 0 | 412.5664 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2104.9308 | 0 | 420.9862 | 4.21% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 06:01 | 12 | 27 | 6 | 361 | 8646 | 17.06 | 2324.1568 | 0 | 0 | 2324.1568 | Heating | 2050.7266 | 8.5 | 2050.7266 | 0 | 2.8481 | 0 | 0 | 0 | 0 | 8.5 | 0 | 410.1453 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2092.5782 | 0 | 418.5156 | 4.185% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 07:01 | 12 | 27 | 7 | 361 | 8647 | 15.98 | 12475.7843 | 0 | 0 | 12475.7843 | Heating | 11008.045 | 8.5 | 11008.045 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2201.609 | 44.03% | 1 | 88.06% | 0% | 0% | 0% | 60.8392 | 0 | 0 | 0 | 60.8392 | 11232.6989 | 0 | 2246.5398 | 22.47% | 1 | 44.93% | 0% | 0% | 6.4709 | 0 | 0 | 6.4709 | 67.3101
2007-12-27 08:01 | 12 | 27 | 8 | 361 | 8648 | 15.98 | 9588.8323 | 0 | 0 | 9588.8323 | Heating | 8460.7344 | 8.5 | 8460.7344 | 0 | 2.8262 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1692.1469 | 33.84% | 1 | 67.69% | 0% | 0% | 0% | 33.2115 | 0 | 0 | 0 | 33.2115 | 8633.4025 | 0 | 1726.6805 | 17.27% | 1 | 34.53% | 0% | 0% | 3.5324 | 0 | 0 | 3.5324 | 36.7439
2007-12-27 09:01 | 12 | 27 | 9 | 361 | 8649 | 19.04 | 7937.9133 | 0 | 0 | 7937.9133 | Heating | 7004.0411 | 8.5 | 7004.0411 | 0 | 2.8915 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1400.8082 | 30% | 1 | 56.03% | 0% | 0% | 0% | 21.5056 | 0 | 0 | 0 | 21.5056 | 7146.9808 | 0 | 1429.3962 | 14.29% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 29.7802
2007-12-27 10:01 | 12 | 27 | 10 | 361 | 8650 | 24.98 | 6535.3738 | 0 | 0 | 6535.3738 | Heating | 5766.5063 | 8.5 | 5766.5063 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1153.3013 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5884.1901 | 0 | 1176.838 | 11.77% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 11:01 | 12 | 27 | 11 | 361 | 8651 | 24.98 | 5698.9128 | 0 | 0 | 5698.9128 | Heating | 5028.4525 | 8.5 | 5028.4525 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1005.6905 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5131.074 | 0 | 1026.2148 | 10.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 12:01 | 12 | 27 | 12 | 361 | 8652 | 28.94 | 5029.0291 | 0 | 0 | 5029.0291 | Heating | 4437.3786 | 8.5 | 4437.3786 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 887.4757 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4527.9374 | 0 | 905.5875 | 9.056% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 13:01 | 12 | 27 | 13 | 361 | 8653 | 28.04 | 4619.3825 | 0 | 0 | 4619.3825 | Heating | 4075.9257 | 8.5 | 4075.9257 | 0 | 3.1545 | 0 | 0 | 0 | 0 | 8.5 | 0 | 815.1851 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4159.1079 | 0 | 831.8216 | 8.318% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 14:01 | 12 | 27 | 14 | 361 | 8654 | 28.94 | 4450.0605 | 0 | 0 | 4450.0605 | Heating | 3926.524 | 8.5 | 3926.524 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 785.3048 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4006.6572 | 0 | 801.3314 | 8.013% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 15:01 | 12 | 27 | 15 | 361 | 8655 | 28.94 | 4507.2368 | 0 | 0 | 4507.2368 | Heating | 3976.9737 | 8.5 | 3976.9737 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 795.3947 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4058.1364 | 0 | 811.6273 | 8.116% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 16:01 | 12 | 27 | 16 | 361 | 8656 | 32 | 4625.254 | 0 | 0 | 4625.254 | Heating | 4081.1065 | 8.5 | 4081.1065 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 816.2213 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4164.3943 | 0 | 832.8789 | 8.329% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 17:01 | 12 | 27 | 17 | 361 | 8657 | 32 | 4894.7387 | 0 | 0 | 4894.7387 | Heating | 4318.8871 | 8.5 | 4318.8871 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 863.7774 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4407.0276 | 0 | 881.4055 | 8.814% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 18:01 | 12 | 27 | 18 | 361 | 8658 | 33.8 | 5259.5323 | 0 | 0 | 5259.5323 | Heating | 4640.7638 | 8.5 | 4640.7638 | 0 | 3.3963 | 0 | 0 | 0 | 0 | 8.5 | 0 | 928.1528 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4735.4733 | 0 | 947.0947 | 9.471% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 19:01 | 12 | 27 | 19 | 361 | 8659 | 33.98 | 5468.9959 | 0 | 0 | 5468.9959 | Heating | 4825.5846 | 8.5 | 4825.5846 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 965.1169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4924.0659 | 0 | 984.8132 | 9.848% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 20:01 | 12 | 27 | 20 | 361 | 8660 | 33.98 | 5698.902 | 0 | 0 | 5698.902 | Heating | 5028.4429 | 8.5 | 5028.4429 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1005.6886 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5131.0642 | 0 | 1026.2128 | 10.26% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 21:01 | 12 | 27 | 21 | 361 | 8661 | 35.96 | 6023.4127 | 0 | 0 | 6023.4127 | Heating | 5314.7759 | 8.5 | 5314.7759 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1062.9552 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5423.2407 | 0 | 1084.6481 | 10.85% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 22:01 | 12 | 27 | 22 | 361 | 8662 | 37.94 | 1872.9597 | 0 | 0 | 1872.9597 | Heating | 1652.6115 | 8.5 | 1652.6115 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 330.5223 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1686.3383 | 0 | 337.2677 | 3.373% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-27 23:01 | 12 | 27 | 23 | 361 | 8663 | 37.94 | 1928.0646 | 0 | 0 | 1928.0646 | Heating | 1701.2335 | 8.5 | 1701.2335 | 0 | 3.6146 | 0 | 0 | 0 | 0 | 8.5 | 0 | 340.2467 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1735.9525 | 0 | 347.1905 | 3.472% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 00:01 | 12 | 28 | 0 | 362 | 8664 | 39.92 | 2265.456 | 0 | 0 | 2265.456 | Heating | 1998.9318 | 8.5 | 1998.9318 | 0 | 3.7339 | 0 | 0 | 0 | 0 | 8.5 | 0 | 399.7864 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2039.7263 | 0 | 407.9453 | 4.079% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 01:01 | 12 | 28 | 1 | 362 | 8665 | 41 | 2485.5236 | 0 | 0 | 2485.5236 | Heating | 2193.109 | 8.5 | 2193.109 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 438.6218 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2237.8663 | 0 | 447.5733 | 4.476% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 02:01 | 12 | 28 | 2 | 362 | 8666 | 41 | 2650.2716 | 0 | 0 | 2650.2716 | Heating | 2338.4749 | 8.5 | 2338.4749 | 0 | 3.8033 | 0 | 0 | 0 | 0 | 8.5 | 0 | 467.695 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2386.1989 | 0 | 477.2398 | 4.772% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 03:01 | 12 | 28 | 3 | 362 | 8667 | 44.06 | 2796.9057 | 0 | 0 | 2796.9057 | Heating | 2467.8579 | 8.5 | 2467.8579 | 0 | 4.0174 | 0 | 0 | 0 | 0 | 8.5 | 0 | 493.5716 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2518.2224 | 0 | 503.6445 | 5.036% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 04:01 | 12 | 28 | 4 | 362 | 8668 | 44.96 | 2932.8729 | 0 | 0 | 2932.8729 | Heating | 2587.8291 | 8.5 | 2587.8291 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 517.5658 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2640.6419 | 0 | 528.1284 | 5.281% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 05:01 | 12 | 28 | 5 | 362 | 8669 | 44.96 | 3080.1973 | 0 | 0 | 3080.1973 | Heating | 2717.8211 | 8.5 | 2717.8211 | 0 | 4.0856 | 0 | 0 | 0 | 0 | 8.5 | 0 | 543.5642 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2773.2869 | 0 | 554.6574 | 5.547% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 06:01 | 12 | 28 | 6 | 362 | 8670 | 46.04 | 3223.2423 | 0 | 0 | 3223.2423 | Heating | 2844.0374 | 8.5 | 2844.0374 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 568.8075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2902.0789 | 0 | 580.4158 | 5.804% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 07:01 | 12 | 28 | 7 | 362 | 8671 | 46.04 | 13782.0687 | 0 | 0 | 13782.0687 | Heating | 12160.6489 | 8.5 | 12160.6489 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2432.1298 | 48.64% | 1 | 97.29% | 0% | 0% | 0% | 76.4981 | 0 | 0 | 0 | 76.4981 | 12408.8254 | 0 | 2481.7651 | 24.82% | 1 | 49.64% | 0% | 0% | 8.1364 | 0 | 0 | 8.1364 | 84.6345
2007-12-28 08:01 | 12 | 28 | 8 | 362 | 8672 | 46.04 | 11528.1345 | 0 | 0 | 11528.1345 | Heating | 10171.8834 | 8.5 | 10171.8834 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2034.3767 | 40.69% | 1 | 81.38% | 0% | 0% | 0% | 50.731 | 0 | 0 | 0 | 50.731 | 10379.4729 | 0 | 2075.8946 | 20.76% | 1 | 41.52% | 0% | 0% | 5.3958 | 0 | 0 | 5.3958 | 56.1268
2007-12-28 09:01 | 12 | 28 | 9 | 362 | 8673 | 42.98 | 9960.5426 | 0 | 0 | 9960.5426 | Heating | 8788.7141 | 8.5 | 8788.7141 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1757.7428 | 35.15% | 1 | 70.31% | 0% | 0% | 0% | 36.2475 | 0 | 0 | 0 | 36.2475 | 8968.0756 | 0 | 1793.6151 | 17.94% | 1 | 35.87% | 0% | 0% | 3.8553 | 0 | 0 | 3.8553 | 40.1028
2007-12-28 10:01 | 12 | 28 | 10 | 362 | 8674 | 48.02 | 8589.0378 | 0 | 0 | 8589.0378 | Heating | 7578.5628 | 8.5 | 7578.5628 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1515.7126 | 30.31% | 1 | 60.63% | 0% | 0% | 0% | 25.781 | 0 | 0 | 0 | 25.781 | 7733.2273 | 0 | 1546.6455 | 15.47% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.0555
2007-12-28 11:01 | 12 | 28 | 11 | 362 | 8675 | 48.02 | 7467.2141 | 0 | 0 | 7467.2141 | Heating | 6588.7183 | 8.5 | 6588.7183 | 0 | 4.3357 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1317.7437 | 30% | 1 | 52.71% | 0% | 0% | 0% | 18.685 | 0 | 0 | 0 | 18.685 | 6723.182 | 0 | 1344.6364 | 13.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.9595
2007-12-28 12:01 | 12 | 28 | 12 | 362 | 8676 | 46.04 | 6603.2053 | 0 | 0 | 6603.2053 | Heating | 5826.3576 | 8.5 | 5826.3576 | 0 | 4.1705 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1165.2715 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5945.2629 | 0 | 1189.0526 | 11.89% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 13:01 | 12 | 28 | 13 | 362 | 8677 | 42.98 | 6052.0133 | 0 | 0 | 6052.0133 | Heating | 5340.0117 | 8.5 | 5340.0117 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1068.0023 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5448.9916 | 0 | 1089.7983 | 10.9% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 14:01 | 12 | 28 | 14 | 362 | 8678 | 42.98 | 5856.3011 | 0 | 0 | 5856.3011 | Heating | 5167.3245 | 8.5 | 5167.3245 | 0 | 3.9388 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1033.4649 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5272.7801 | 0 | 1054.556 | 10.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 15:01 | 12 | 28 | 15 | 362 | 8679 | 39.02 | 5837.9869 | 0 | 0 | 5837.9869 | Heating | 5151.1649 | 8.5 | 5151.1649 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1030.233 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5256.2907 | 0 | 1051.2581 | 10.51% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 16:01 | 12 | 28 | 16 | 362 | 8680 | 39.02 | 5915.678 | 0 | 0 | 5915.678 | Heating | 5219.7159 | 8.5 | 5219.7159 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1043.9432 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5326.2407 | 0 | 1065.2481 | 10.65% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 17:01 | 12 | 28 | 17 | 362 | 8681 | 39.02 | 6206.3433 | 0 | 0 | 6206.3433 | Heating | 5476.1853 | 8.5 | 5476.1853 | 0 | 3.6785 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1095.2371 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5587.9441 | 0 | 1117.5888 | 11.18% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 18:01 | 12 | 28 | 18 | 362 | 8682 | 37.04 | 6632.1966 | 0 | 0 | 6632.1966 | Heating | 5851.9382 | 8.5 | 5851.9382 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1170.3876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5971.3655 | 0 | 1194.2731 | 11.94% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-28 19:01 | 12 | 28 | 19 | 362 | 8683 | 37.04 | 7422.9676 | 0 | 0 | 7422.9676 | Heating | 6549.6773 | 8.5 | 6549.6773 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1309.9355 | 30% | 1 | 52.4% | 0% | 0% | 0% | 18.4313 | 0 | 0 | 0 | 18.4313 | 6683.3442 | 0 | 1336.6688 | 13.37% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.7058
2007-12-28 20:01 | 12 | 28 | 20 | 362 | 8684 | 37.04 | 8232.9713 | 0 | 0 | 8232.9713 | Heating | 7264.3864 | 8.5 | 7264.3864 | 0 | 3.5637 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1452.8773 | 30% | 1 | 58.12% | 0% | 0% | 0% | 23.3888 | 0 | 0 | 0 | 23.3888 | 7412.6392 | 0 | 1482.5278 | 14.83% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 31.6633
2007-12-28 21:01 | 12 | 28 | 21 | 362 | 8685 | 35.96 | 8747.1823 | 0 | 0 | 8747.1823 | Heating | 7718.102 | 8.5 | 7718.102 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1543.6204 | 30.87% | 1 | 61.74% | 0% | 0% | 0% | 26.8859 | 0 | 0 | 0 | 26.8859 | 7875.6143 | 0 | 1575.1229 | 15.75% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 35.1604
2007-12-28 22:01 | 12 | 28 | 22 | 362 | 8686 | 35.96 | 9420.2002 | 0 | 0 | 9420.2002 | Heating | 8311.9414 | 8.5 | 8311.9414 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1662.3883 | 33.25% | 1 | 66.5% | 0% | 0% | 0% | 31.8835 | 0 | 0 | 0 | 31.8835 | 8481.5728 | 0 | 1696.3146 | 16.96% | 1 | 33.93% | 0% | 0% | 3.3911 | 0 | 0 | 3.3911 | 35.2746
2007-12-28 23:01 | 12 | 28 | 23 | 362 | 8687 | 35.06 | 3239.8234 | 0 | 0 | 3239.8234 | Heating | 2858.6677 | 8.5 | 2858.6677 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 571.7335 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2917.0079 | 0 | 583.4016 | 5.834% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 00:01 | 12 | 29 | 0 | 363 | 8688 | 35.6 | 3435.6348 | 0 | 0 | 3435.6348 | Heating | 3031.4425 | 8.5 | 3031.4425 | 0 | 3.4863 | 0 | 0 | 0 | 0 | 8.5 | 0 | 606.2885 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3093.3086 | 0 | 618.6617 | 6.187% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 01:01 | 12 | 29 | 1 | 363 | 8689 | 35.06 | 3624.6716 | 0 | 0 | 3624.6716 | Heating | 3198.2397 | 8.5 | 3198.2397 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 639.6479 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3263.5099 | 0 | 652.702 | 6.527% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 02:01 | 12 | 29 | 2 | 363 | 8690 | 35.06 | 3672.1521 | 0 | 0 | 3672.1521 | Heating | 3240.1342 | 8.5 | 3240.1342 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 648.0268 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3306.2594 | 0 | 661.2519 | 6.613% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 03:01 | 12 | 29 | 3 | 363 | 8691 | 35.06 | 3632.4291 | 0 | 0 | 3632.4291 | Heating | 3205.0845 | 8.5 | 3205.0845 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 641.0169 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3270.4944 | 0 | 654.0989 | 6.541% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 04:01 | 12 | 29 | 4 | 363 | 8692 | 35.06 | 3577.6178 | 0 | 0 | 3577.6178 | Heating | 3156.7216 | 8.5 | 3156.7216 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 631.3443 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3221.1445 | 0 | 644.2289 | 6.442% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 05:01 | 12 | 29 | 5 | 363 | 8693 | 33.98 | 3602.879 | 0 | 0 | 3602.879 | Heating | 3179.0109 | 8.5 | 3179.0109 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 635.8022 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3243.8886 | 0 | 648.7777 | 6.488% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 06:01 | 12 | 29 | 6 | 363 | 8694 | 33.08 | 3671.2564 | 0 | 0 | 3671.2564 | Heating | 3239.3439 | 8.5 | 3239.3439 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 647.8688 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3305.4529 | 0 | 661.0906 | 6.611% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 07:01 | 12 | 29 | 7 | 363 | 8695 | 33.08 | 3734.2604 | 0 | 0 | 3734.2604 | Heating | 3294.9356 | 8.5 | 3294.9356 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 658.9871 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3362.1792 | 0 | 672.4358 | 6.724% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 08:01 | 12 | 29 | 8 | 363 | 8696 | 33.08 | 3718.7539 | 0 | 0 | 3718.7539 | Heating | 3281.2534 | 8.5 | 3281.2534 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 656.2507 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3348.2178 | 0 | 669.6436 | 6.696% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 09:01 | 12 | 29 | 9 | 363 | 8697 | 30.92 | 15361.302 | 0 | 0 | 15361.302 | Heating | 13554.09 | 8.5 | 13554.09 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2710.818 | 54.22% | 2 | 54.22% | 54.22% | 0% | 0% | 19.9362 | 19.9362 | 0 | 0 | 39.8724 | 13830.7041 | 0 | 2766.1408 | 27.66% | 1 | 55.32% | 0% | 0% | 10.4422 | 0 | 0 | 10.4422 | 50.3147
2007-12-29 10:01 | 12 | 29 | 10 | 363 | 8698 | 32 | 12734.7286 | 0 | 0 | 12734.7286 | Heating | 11236.5252 | 8.5 | 11236.5252 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2247.305 | 44.95% | 1 | 89.89% | 0% | 0% | 0% | 63.7828 | 0 | 0 | 0 | 63.7828 | 11465.8421 | 0 | 2293.1684 | 22.93% | 1 | 45.86% | 0% | 0% | 6.784 | 0 | 0 | 6.784 | 70.5668
2007-12-29 11:01 | 12 | 29 | 11 | 363 | 8699 | 33.08 | 10652.4103 | 0 | 0 | 10652.4103 | Heating | 9399.1855 | 8.5 | 9399.1855 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1879.8371 | 37.6% | 1 | 75.19% | 0% | 0% | 0% | 42.3017 | 0 | 0 | 0 | 42.3017 | 9591.0056 | 0 | 1918.2011 | 19.18% | 1 | 38.36% | 0% | 0% | 4.4992 | 0 | 0 | 4.4992 | 46.8009
2007-12-29 12:01 | 12 | 29 | 12 | 363 | 8700 | 35.06 | 9093.7485 | 0 | 0 | 9093.7485 | Heating | 8023.8958 | 8.5 | 8023.8958 | 0 | 3.4585 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1604.7792 | 32.1% | 1 | 64.19% | 0% | 0% | 0% | 29.3992 | 0 | 0 | 0 | 29.3992 | 8187.6487 | 0 | 1637.5297 | 16.38% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 37.6738
2007-12-29 13:01 | 12 | 29 | 13 | 363 | 8701 | 35.96 | 7606.8393 | 0 | 0 | 7606.8393 | Heating | 6711.9171 | 8.5 | 6711.9171 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1342.3834 | 30% | 1 | 53.7% | 0% | 0% | 0% | 19.4983 | 0 | 0 | 0 | 19.4983 | 6848.895 | 0 | 1369.779 | 13.7% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.7729
2007-12-29 14:01 | 12 | 29 | 14 | 363 | 8702 | 35.96 | 7008.5033 | 0 | 0 | 7008.5033 | Heating | 6183.9735 | 8.5 | 6183.9735 | 0 | 3.5052 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1236.7947 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6310.177 | 0 | 1262.0354 | 12.62% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 15:01 | 12 | 29 | 15 | 363 | 8703 | 33.98 | 6879.3326 | 0 | 0 | 6879.3326 | Heating | 6069.9994 | 8.5 | 6069.9994 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1213.9999 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6193.8769 | 0 | 1238.7754 | 12.39% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 16:01 | 12 | 29 | 16 | 363 | 8704 | 33.08 | 6967.2975 | 0 | 0 | 6967.2975 | Heating | 6147.6155 | 8.5 | 6147.6155 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1229.5231 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6273.077 | 0 | 1254.6154 | 12.55% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 17:01 | 12 | 29 | 17 | 363 | 8705 | 33.08 | 7356.3628 | 0 | 0 | 7356.3628 | Heating | 6490.9084 | 8.5 | 6490.9084 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1298.1817 | 30% | 1 | 51.93% | 0% | 0% | 0% | 18.0531 | 0 | 0 | 0 | 18.0531 | 6623.3759 | 0 | 1324.6752 | 13.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 26.3277
2007-12-29 18:01 | 12 | 29 | 18 | 363 | 8706 | 32 | 10179.064 | 0 | 0 | 10179.064 | Heating | 8981.527 | 8.5 | 8981.527 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1796.3054 | 35.93% | 1 | 71.85% | 0% | 0% | 0% | 38.1027 | 0 | 0 | 0 | 38.1027 | 9164.8235 | 0 | 1832.9647 | 18.33% | 1 | 36.66% | 0% | 0% | 4.0526 | 0 | 0 | 4.0526 | 42.1553
2007-12-29 19:01 | 12 | 29 | 19 | 363 | 8707 | 32 | 11052.2221 | 0 | 0 | 11052.2221 | Heating | 9751.9607 | 8.5 | 9751.9607 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1950.3921 | 39.01% | 1 | 78.02% | 0% | 0% | 0% | 46.0428 | 0 | 0 | 0 | 46.0428 | 9950.9803 | 0 | 1990.1961 | 19.9% | 1 | 39.8% | 0% | 0% | 4.8971 | 0 | 0 | 4.8971 | 50.9399
2007-12-29 20:01 | 12 | 29 | 20 | 363 | 8708 | 32 | 3094.6048 | 0 | 0 | 3094.6048 | Heating | 2730.5337 | 8.5 | 2730.5337 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 546.1067 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2786.2588 | 0 | 557.2518 | 5.573% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 21:01 | 12 | 29 | 21 | 363 | 8709 | 32 | 3254.1151 | 0 | 0 | 3254.1151 | Heating | 2871.278 | 8.5 | 2871.278 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 574.2556 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 2929.8756 | 0 | 585.9751 | 5.86% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 22:01 | 12 | 29 | 22 | 363 | 8710 | 30.92 | 3411.518 | 0 | 0 | 3411.518 | Heating | 3010.1629 | 8.5 | 3010.1629 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 602.0326 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3071.5948 | 0 | 614.319 | 6.143% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-29 23:01 | 12 | 29 | 23 | 363 | 8711 | 30.92 | 3531.0294 | 0 | 0 | 3531.0294 | Heating | 3115.6142 | 8.5 | 3115.6142 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 623.1228 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3179.1982 | 0 | 635.8396 | 6.358% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 00:01 | 12 | 30 | 0 | 364 | 8712 | 30.92 | 3610.2941 | 0 | 0 | 3610.2941 | Heating | 3185.5536 | 8.5 | 3185.5536 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 637.1107 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3250.5649 | 0 | 650.113 | 6.501% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 01:01 | 12 | 30 | 1 | 364 | 8713 | 30.02 | 3668.2796 | 0 | 0 | 3668.2796 | Heating | 3236.7173 | 8.5 | 3236.7173 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 647.3435 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3302.7727 | 0 | 660.5545 | 6.606% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 02:01 | 12 | 30 | 2 | 364 | 8714 | 30.02 | 3667.1808 | 0 | 0 | 3667.1808 | Heating | 3235.7478 | 8.5 | 3235.7478 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 647.1496 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3301.7834 | 0 | 660.3567 | 6.604% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 03:01 | 12 | 30 | 3 | 364 | 8715 | 28.94 | 3621.0107 | 0 | 0 | 3621.0107 | Heating | 3195.0094 | 8.5 | 3195.0094 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 639.0019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3260.2137 | 0 | 652.0427 | 6.52% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 04:01 | 12 | 30 | 4 | 364 | 8716 | 28.94 | 3572.1964 | 0 | 0 | 3572.1964 | Heating | 3151.938 | 8.5 | 3151.938 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 630.3876 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3216.2632 | 0 | 643.2526 | 6.433% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 05:01 | 12 | 30 | 5 | 364 | 8717 | 28.94 | 3586.0383 | 0 | 0 | 3586.0383 | Heating | 3164.1514 | 8.5 | 3164.1514 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 632.8303 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3228.7259 | 0 | 645.7452 | 6.457% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 06:01 | 12 | 30 | 6 | 364 | 8718 | 28.94 | 3631.7558 | 0 | 0 | 3631.7558 | Heating | 3204.4904 | 8.5 | 3204.4904 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 640.8981 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3269.8882 | 0 | 653.9776 | 6.54% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 07:01 | 12 | 30 | 7 | 364 | 8719 | 30.02 | 16097.8568 | 0 | 0 | 16097.8568 | Heating | 14203.9913 | 8.5 | 14203.9913 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2840.7983 | 56.82% | 2 | 56.82% | 56.82% | 0% | 0% | 22.2037 | 22.2037 | 0 | 0 | 44.4074 | 14493.8687 | 0 | 2898.7737 | 28.99% | 1 | 57.98% | 0% | 0% | 11.6299 | 0 | 0 | 11.6299 | 56.0372
2007-12-30 08:01 | 12 | 30 | 8 | 364 | 8720 | 30.02 | 13514.4253 | 0 | 0 | 13514.4253 | Heating | 11924.4929 | 8.5 | 11924.4929 | 0 | 3.2302 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2384.8986 | 47.7% | 1 | 95.4% | 0% | 0% | 0% | 73.1243 | 0 | 0 | 0 | 73.1243 | 12167.8499 | 0 | 2433.57 | 24.34% | 1 | 48.67% | 0% | 0% | 7.7776 | 0 | 0 | 7.7776 | 80.9019
2007-12-30 09:01 | 12 | 30 | 9 | 364 | 8721 | 30.92 | 11408.4991 | 0 | 0 | 11408.4991 | Heating | 10066.3227 | 8.5 | 10066.3227 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2013.2645 | 40.27% | 1 | 80.53% | 0% | 0% | 0% | 49.5282 | 0 | 0 | 0 | 49.5282 | 10271.7579 | 0 | 2054.3516 | 20.54% | 1 | 41.09% | 0% | 0% | 5.2679 | 0 | 0 | 5.2679 | 54.7961
2007-12-30 10:01 | 12 | 30 | 10 | 364 | 8722 | 32 | 9778.3331 | 0 | 0 | 9778.3331 | Heating | 8627.941 | 8.5 | 8627.941 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1725.5882 | 34.51% | 1 | 69.02% | 0% | 0% | 0% | 34.7405 | 0 | 0 | 0 | 34.7405 | 8804.0214 | 0 | 1760.8043 | 17.61% | 1 | 35.22% | 0% | 0% | 3.695 | 0 | 0 | 3.695 | 38.4356
2007-12-30 11:01 | 12 | 30 | 11 | 364 | 8723 | 32 | 8652.2123 | 0 | 0 | 8652.2123 | Heating | 7634.305 | 8.5 | 7634.305 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1526.861 | 30.54% | 1 | 61.07% | 0% | 0% | 0% | 26.2192 | 0 | 0 | 0 | 26.2192 | 7790.1071 | 0 | 1558.0214 | 15.58% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 34.4938
2007-12-30 12:01 | 12 | 30 | 12 | 364 | 8724 | 32 | 7640.974 | 0 | 0 | 7640.974 | Heating | 6742.0359 | 8.5 | 6742.0359 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1348.4072 | 30% | 1 | 53.94% | 0% | 0% | 0% | 19.7001 | 0 | 0 | 0 | 19.7001 | 6879.6285 | 0 | 1375.9257 | 13.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 27.9747
2007-12-30 13:01 | 12 | 30 | 13 | 364 | 8725 | 30.92 | 6911.7088 | 0 | 0 | 6911.7088 | Heating | 6098.5666 | 8.5 | 6098.5666 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1219.7133 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6223.0272 | 0 | 1244.6054 | 12.45% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 14:01 | 12 | 30 | 14 | 364 | 8726 | 32 | 6245.0281 | 0 | 0 | 6245.0281 | Heating | 5510.3189 | 8.5 | 5510.3189 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1102.0638 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5622.7744 | 0 | 1124.5549 | 11.25% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 15:01 | 12 | 30 | 15 | 364 | 8727 | 33.08 | 5750.4216 | 0 | 0 | 5750.4216 | Heating | 5073.9014 | 8.5 | 5073.9014 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1014.7803 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5177.4504 | 0 | 1035.4901 | 10.35% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 16:01 | 12 | 30 | 16 | 364 | 8728 | 33.08 | 5341.3602 | 0 | 0 | 5341.3602 | Heating | 4712.9649 | 8.5 | 4712.9649 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 942.593 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4809.1478 | 0 | 961.8296 | 9.618% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 17:01 | 12 | 30 | 17 | 364 | 8729 | 33.08 | 5473.3749 | 0 | 0 | 5473.3749 | Heating | 4829.4485 | 8.5 | 4829.4485 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 965.8897 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4928.0086 | 0 | 985.6017 | 9.856% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 18:01 | 12 | 30 | 18 | 364 | 8730 | 33.08 | 5950.2688 | 0 | 0 | 5950.2688 | Heating | 5250.2372 | 8.5 | 5250.2372 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1050.0474 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5357.3849 | 0 | 1071.477 | 10.71% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 19:01 | 12 | 30 | 19 | 364 | 8731 | 33.08 | 6243.2087 | 0 | 0 | 6243.2087 | Heating | 5508.7136 | 8.5 | 5508.7136 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1101.7427 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5621.1363 | 0 | 1124.2273 | 11.24% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 20:01 | 12 | 30 | 20 | 364 | 8732 | 32 | 6444.1018 | 0 | 0 | 6444.1018 | Heating | 5685.9722 | 8.5 | 5685.9722 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1137.1944 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5802.0124 | 0 | 1160.4025 | 11.6% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 21:01 | 12 | 30 | 21 | 364 | 8733 | 24.8 | 6615.5121 | 0 | 0 | 6615.5121 | Heating | 5837.2165 | 8.5 | 5837.2165 | 0 | 3.0457 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1167.4433 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 5956.3434 | 0 | 1191.2687 | 11.91% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 22:01 | 12 | 30 | 22 | 364 | 8734 | 24.08 | 1970.7885 | 0 | 0 | 1970.7885 | Heating | 1738.931 | 8.5 | 1738.931 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 347.7862 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1774.4194 | 0 | 354.8839 | 3.549% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-30 23:01 | 12 | 30 | 23 | 364 | 8735 | 28.94 | 1839.8413 | 0 | 0 | 1839.8413 | Heating | 1623.3894 | 8.5 | 1623.3894 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 324.6779 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1656.5198 | 0 | 331.304 | 3.313% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 00:01 | 12 | 31 | 0 | 365 | 8736 | 30.92 | 2056.592 | 0 | 0 | 2056.592 | Heating | 1814.64 | 8.5 | 1814.64 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 362.928 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1851.6735 | 0 | 370.3347 | 3.703% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 01:01 | 12 | 31 | 1 | 365 | 8737 | 32 | 2132.0732 | 0 | 0 | 2132.0732 | Heating | 1881.241 | 8.5 | 1881.241 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.2482 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1919.6337 | 0 | 383.9267 | 3.839% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 02:01 | 12 | 31 | 2 | 365 | 8738 | 32 | 2148.8364 | 0 | 0 | 2148.8364 | Heating | 1896.0321 | 8.5 | 1896.0321 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 379.2064 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1934.7267 | 0 | 386.9453 | 3.869% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 03:01 | 12 | 31 | 3 | 365 | 8739 | 33.08 | 2136.1489 | 0 | 0 | 2136.1489 | Heating | 1884.8373 | 8.5 | 1884.8373 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 376.9675 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1923.3034 | 0 | 384.6607 | 3.847% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 04:01 | 12 | 31 | 4 | 365 | 8740 | 33.08 | 2111.2055 | 0 | 0 | 2111.2055 | Heating | 1862.8283 | 8.5 | 1862.8283 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 372.5657 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1900.8452 | 0 | 380.169 | 3.802% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 05:01 | 12 | 31 | 5 | 365 | 8741 | 33.08 | 2087.7885 | 0 | 0 | 2087.7885 | Heating | 1842.1664 | 8.5 | 1842.1664 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 368.4333 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1879.7616 | 0 | 375.9523 | 3.76% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 06:01 | 12 | 31 | 6 | 365 | 8742 | 32 | 2057.7088 | 0 | 0 | 2057.7088 | Heating | 1815.6254 | 8.5 | 1815.6254 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 363.1251 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 1852.679 | 0 | 370.5358 | 3.705% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 07:01 | 12 | 31 | 7 | 365 | 8743 | 30.92 | 12125.9161 | 0 | 0 | 12125.9161 | Heating | 10699.3377 | 8.5 | 10699.3377 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 2139.8675 | 42.8% | 1 | 85.59% | 0% | 0% | 0% | 56.9864 | 0 | 0 | 0 | 56.9864 | 10917.6916 | 0 | 2183.5383 | 21.84% | 1 | 43.67% | 0% | 0% | 6.0611 | 0 | 0 | 6.0611 | 63.0475
2007-12-31 08:01 | 12 | 31 | 8 | 365 | 8744 | 30.92 | 8972.05 | 0 | 0 | 8972.05 | Heating | 7916.5147 | 8.5 | 7916.5147 | 0 | 3.2671 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1583.3029 | 31.67% | 1 | 63.33% | 0% | 0% | 0% | 28.5022 | 0 | 0 | 0 | 28.5022 | 8078.0762 | 0 | 1615.6152 | 16.16% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 36.7767
2007-12-31 09:01 | 12 | 31 | 9 | 365 | 8745 | 33.08 | 7041.418 | 0 | 0 | 7041.418 | Heating | 6213.0159 | 8.5 | 6213.0159 | 0 | 3.3624 | 0 | 0 | 0 | 0 | 8.5 | 0 | 1242.6032 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 6339.8122 | 0 | 1267.9624 | 12.68% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 10:01 | 12 | 31 | 10 | 365 | 8746 | 33.98 | 5389.8423 | 0 | 0 | 5389.8423 | Heating | 4755.7432 | 8.5 | 4755.7432 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 951.1486 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4852.7992 | 0 | 970.5598 | 9.706% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 11:01 | 12 | 31 | 11 | 365 | 8747 | 33.98 | 4594.9901 | 0 | 0 | 4594.9901 | Heating | 4054.403 | 8.5 | 4054.403 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 810.8806 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 4137.1459 | 0 | 827.4292 | 8.274% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 12:01 | 12 | 31 | 12 | 365 | 8748 | 33.98 | 4119.6693 | 0 | 0 | 4119.6693 | Heating | 3635.0023 | 8.5 | 3635.0023 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 727.0005 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3709.186 | 0 | 741.8372 | 7.418% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 13:01 | 12 | 31 | 13 | 365 | 8749 | 33.98 | 3913.4824 | 0 | 0 | 3913.4824 | Heating | 3453.0727 | 8.5 | 3453.0727 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 690.6145 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3523.5436 | 0 | 704.7087 | 7.047% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 14:01 | 12 | 31 | 14 | 365 | 8750 | 33.98 | 3684.7512 | 0 | 0 | 3684.7512 | Heating | 3251.2511 | 8.5 | 3251.2511 | 0 | 3.405 | 0 | 0 | 0 | 0 | 8.5 | 0 | 650.2502 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3317.6031 | 0 | 663.5206 | 6.635% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 15:01 | 12 | 31 | 15 | 365 | 8751 | 32 | 3516.9431 | 0 | 0 | 3516.9431 | Heating | 3103.1851 | 8.5 | 3103.1851 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 620.637 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3166.5154 | 0 | 633.3031 | 6.333% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 16:01 | 12 | 31 | 16 | 365 | 8752 | 32 | 3384.9573 | 0 | 0 | 3384.9573 | Heating | 2986.727 | 8.5 | 2986.727 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 597.3454 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3047.6806 | 0 | 609.5361 | 6.095% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 17:01 | 12 | 31 | 17 | 365 | 8753 | 32 | 3369.5647 | 0 | 0 | 3369.5647 | Heating | 2973.1453 | 8.5 | 2973.1453 | 0 | 3.3135 | 0 | 0 | 0 | 0 | 8.5 | 0 | 594.6291 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3033.8217 | 0 | 606.7643 | 6.068% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 18:01 | 12 | 31 | 18 | 365 | 8754 | 28.94 | 3477.0776 | 0 | 0 | 3477.0776 | Heating | 3068.0097 | 8.5 | 3068.0097 | 0 | 3.188 | 0 | 0 | 0 | 0 | 8.5 | 0 | 613.6019 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3130.6221 | 0 | 626.1244 | 6.261% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 19:01 | 12 | 31 | 19 | 365 | 8755 | 26.96 | 3481.5248 | 0 | 0 | 3481.5248 | Heating | 3071.9337 | 8.5 | 3071.9337 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 614.3867 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3134.6262 | 0 | 626.9252 | 6.269% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 20:01 | 12 | 31 | 20 | 365 | 8756 | 26.96 | 3573.5765 | 0 | 0 | 3573.5765 | Heating | 3153.1557 | 8.5 | 3153.1557 | 0 | 3.1163 | 0 | 0 | 0 | 0 | 8.5 | 0 | 630.6311 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3217.5058 | 0 | 643.5012 | 6.435% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 21:01 | 12 | 31 | 21 | 365 | 8757 | 26.06 | 3741.7022 | 0 | 0 | 3741.7022 | Heating | 3301.502 | 8.5 | 3301.502 | 0 | 3.0859 | 0 | 0 | 0 | 0 | 8.5 | 0 | 660.3004 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 3368.8796 | 0 | 673.7759 | 6.738% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 22:01 | 12 | 31 | 22 | 365 | 8758 | 24.98 | 1109.3679 | 0 | 0 | 1109.3679 | Heating | 978.854 | 8.5 | 978.854 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 195.7708 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 998.8306 | 0 | 199.7661 | 1.998% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2007-12-31 23:01 | 12 | 31 | 23 | 365 | 8759 | 24.98 | 888.8904 | 0 | 0 | 888.8904 | Heating | 784.3151 | 8.5 | 784.3151 | 0 | 3.0513 | 0 | 0 | 0 | 0 | 8.5 | 0 | 156.863 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 800.3215 | 0 | 160.0643 | 1.601% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
2008-01-01 00:01 | 1 | 1 | 0 | 365 | 8760 | 24.08 | 973.5758 | 0 | 0 | 973.5758 | Heating | 859.0375 | 8.5 | 859.0375 | 0 | 3.0238 | 0 | 0 | 0 | 0 | 8.5 | 0 | 171.8075 | 30% | 1 | 50% | 0% | 0% | 0% | 16.5491 | 0 | 0 | 0 | 16.5491 | 876.5689 | 0 | 175.3138 | 1.753% | 1 | 50% | 0% | 0% | 8.2745 | 0 | 0 | 8.2745 | 24.8236
Formulas:
Day of Year = DAYS([DATE/TIME],A9)+1
Note on N8: Walck, Charles: Do we need to alter based on return temp?
Note on R8: Walck, Charles: Switch to Column Q after appropriate adjustment?

## Graphs
|  | Chiller |  |  | Loop Pumps | Outfall Pumps | Total
|  | Heating | Cooling | Total
1 | January | 0 | 0 | 0 | 15858.2892 | 6006.9589 | 21865.2481
2 | February | 0 | 0 | 0 | 13245.152 | 5450.5622 | 18695.7142
3 | March | 0 | 0 | 0 | 13389.4329 | 6067.7844 | 19457.2173
4 | April | 0 | 0 | 0 | 12074.9052 | 5931.8593 | 18006.7645
5 | May | 0 | 0 | 0 | 12709.1597 | 6102.6826 | 18811.8423
6 | June | 0 | 0 | 0 | 12901.0899 | 5799.8395 | 18700.9294
7 | July | 0 | 0 | 0 | 18492.7089 | 6068.5285 | 24561.2374
8 | August | 0 | 0 | 0 | 16139.214 | 6012.9963 | 22152.2103
9 | September | 0 | 0 | 0 | 13302.0043 | 5958.0809 | 19260.0852
10 | October | 0 | 0 | 0 | 12499.4972 | 6137.0731 | 18636.5703
11 | November | 0 | 0 | 0 | 12412.6587 | 5920.9865 | 18333.6452
12 | December | 0 | 0 | 0 | 14087.961 | 6018.3543 | 20106.3152
| Total | 0 | 0 | 0 | 167112.073 | 71475.7065 | 238587.7795
Central Plant Chiller |  | 0
Loop Pumps |  | 167112.073
Outfall Pumps |  | 71475.7065

## Inputs
Input Data
Load (Building) Side Information
| Heating Inputs |  |  |  | Cooling Inputs
| Cond LWT | 48 | °F |  | CWS Temp | 76 | °F
| Cond EWT | 38 | °F |  | CWR Temp | 88 | °F
| Cond Water ΔT | 10 | °F |  | ΔCW Temp | 12 | °F
| Eavp LWT | 25 | °F |  | Heat Exchanger Efficiency | 98%
| Eavp EWT | 35 | °F
| Eavp Water ΔT | 10 | °F
| Heating Capacity | 150000 | MBH
| Heat Pump Efficiency | 4 | COP
| Heat Input Ratio | 0.75
| Cooling Capacity | 345 | Tons
| Cooling Capacity | 90000 | MBH << heat pump buildings
| Compressor Heat Discount | 34.86%
| Cooling Capacity | 70000 | MBH << chiller buildings
| Compressor Heat Discount | 28.23%
| Chiller COP | 4.5
| Cooling Eff |  | EER
| Cooling Eff |  | kW/Ton
| Heating Capacity | 900 | MBH
| Heat Pump Efficiency |  | COP
| Cooling Capacity | 0 | Tons
| Cooling Capacity | 0 | MBH
| Cooling Eff | 15.22 | EER
| Cooling Eff | 0.7883 | kW/Ton
| Load Split | 0.67
| Loop Side Hydraulic Inputs |  |  |  | Loop Side Pump Inputs |  |  |  | Loop Side Heating Inputs |  |  | Loop Side Cooling Inputs
| Equivalent Linear Length | 1000 | Ft |  | Pump Qty | 2 |  |  | Heat Pump Efficiency | 8.5 | COP | Cooling Pump Efficiency | 7 | COP
| Hazen-Williams Coeff. (c) | 140 |  |  | Pump Efficiency | 85%
| Flow | #REF! | gpm |  | Motor HP per Pump | 100
| Flow velocity | 5 | ft/s |  | Duty Flow per Pump | 2500 | GPM
| Hydraulic Diameter | #REF! | in |  | Total Flow | 5000 | GPM | 5000
| Specific Gravity | 1 |  |  | Min Speed | 50%
[5 empty] | Min Flow Rate | 1250 | GPM
[5 empty] | Motor Efficiency | 91.5%
[5 empty] | Affinty Law Exponent | 2.3
| Wastewater Effluent Inputs |  |  |  | Outfall Pump Inputs
| Heating SWT | 50 | °F |  | Pump Qty | 2
| Heating RWT | 40 | °F |  | Pump Efficiency | 78.5%
| Cooling SWT | 75 | °F |  | Motor HP per Pump | 50
| Cooling RWT | 85 | °F |  | Duty Flow per Pump | 5000 | GPM
| Heating Capacity |  | MBH |  | Total Flow | 10000 | GPM
| Cooling Capacity |  | Tons |  | Min Speed | 50%
| Cooling Capacity |  | MBH |  | Min Flow Rate | 2500 | GPM
| Heating Capacity Limit | 30000 | MBH |  | Motor Efficiency | 91.5%
| Cooling Capacity Limit | 180000 | MBH |  | Affinty Law Exponent | 2.3
| Heating Load (MBH) |  |  |  |  | Cooling Load (MBH)
| Min | Max | Frequency |  |  | Min | Bin | Frequency
|  | 0 | 2930 | 8760 |  |  | 0 | 5830 | 8760
| 0 | 200 | 805 | 5830 |  | 0 | 400 | 1026 | 2930
| 200 | 400 | 628 | 5025 |  | 400 | 800 | 348 | 1904
| 400 | 600 | 614 | 4397 |  | 800 | 1200 | 255 | 1556
| 600 | 800 | 585 | 3783 |  | 1200 | 1600 | 175 | 1301
| 800 | 1000 | 472 | 3198 |  | 1600 | 2000 | 158 | 1126
| 1000 | 1200 | 467 | 2726 |  | 2000 | 2400 | 157 | 968
| 1200 | 1400 | 464 | 2259 |  | 2400 | 2800 | 136 | 811
| 1400 | 1600 | 399 | 1795 |  | 2800 | 3200 | 134 | 675
| 1600 | 1800 | 338 | 1396 |  | 3200 | 3600 | 134 | 541
| 1800 | 2000 | 254 | 1058 |  | 3600 | 4000 | 87 | 407
| 2000 | 2200 | 226 | 804 |  | 4000 | 4400 | 65 | 320
| 2200 | 2400 | 158 | 578 |  | 4400 | 4800 | 66 | 255
| 2400 | 2600 | 109 | 420 |  | 4800 | 5200 | 52 | 189
| 2600 | 2800 | 75 | 311 |  | 5200 | 5600 | 43 | 137
| 2800 | 3000 | 60 | 236 |  | 5600 | 6000 | 39 | 94
| 3000 | 3200 | 50 | 176 |  | 6000 | 6400 | 24 | 55
| 3200 | 3400 | 26 | 126 |  | 6400 | 6800 | 13 | 31
| 3400 | 3600 | 31 | 100 |  | 6800 | 7200 | 5 | 18
| 3600 | 3800 | 24 | 69 |  | 7200 | 7600 | 8 | 13
| 3800 | 4000 | 15 | 45 |  | 7600 | 8000 | 3 | 5
| 4000 | 4200 | 10 | 30 |  | 8000 | 8400 | 2 | 2
| 4200 | 4400 | 8 | 20 |  | 8400 | 8800 | 0 | 0
| 4400 | 4600 | 5 | 12 |  | 8800 | 9200 | 0 | 0
| 4600 | 4800 | 3 | 7 |  | 9200 | 9600 | 0 | 0
| 4800 | 5000 | 3 | 4 |  | 9600 | 10000 | 0 | 0
| 5000 | 5200 | 1 | 1 |  | 10000 | 10400 | 0 | 0
| 5200 | More | 0 | 0 |  | 10400 | More | 0 | 0

## Input Load Data
Input Load Data
| Max Load | 18348.4894
| GPM | 1834.8489
| Hour | Heating (MBH) | Cooling - Heat Pump (MBH) | Total Load (MBH)
2002-01-01 01:00 | 1 | 1256.981 | 0 | 1256.981
| 2 | 1668.0148 | 0 | 1668.0148
| 3 | 1766.93 | 0 | 1766.93
| 4 | 1881.2621 | 0 | 1881.2621
| 5 | 2019.8669 | 0 | 2019.8669
| 6 | 2105.5583 | 0 | 2105.5583
| 7 | 10111.2369 | 0 | 10111.2369
| 8 | 8091.3203 | 0 | 8091.3203
| 9 | 7307.0774 | 0 | 7307.0774
| 10 | 6316.7775 | 0 | 6316.7775
| 11 | 5764.988 | 0 | 5764.988
| 12 | 5222.0518 | 0 | 5222.0518
| 13 | 4591.8812 | 0 | 4591.8812
| 14 | 4103.5029 | 0 | 4103.5029
| 15 | 3756.724 | 0 | 3756.724
| 16 | 3341.8226 | 0 | 3341.8226
| 17 | 3118.5556 | 0 | 3118.5556
| 18 | 2989.2951 | 0 | 2989.2951
| 19 | 2894.043 | 0 | 2894.043
| 20 | 2700.6271 | 0 | 2700.6271
| 21 | 2483.4379 | 0 | 2483.4379
| 22 | 802.3528 | 0 | 802.3528
| 23 | 745.4465 | 0 | 745.4465
| 24 | 724.2447 | 0 | 724.2447
| 25 | 737.5426 | 0 | 737.5426
| 26 | 900.1883 | 0 | 900.1883
| 27 | 1104.4504 | 0 | 1104.4504
| 28 | 1237.0355 | 0 | 1237.0355
| 29 | 1337.4697 | 0 | 1337.4697
| 30 | 1416.6972 | 0 | 1416.6972
| 31 | 8939.3319 | 0 | 8939.3319
| 32 | 6978.6798 | 0 | 6978.6798
| 33 | 5874.0245 | 0 | 5874.0245
| 34 | 4825.3632 | 0 | 4825.3632
| 35 | 4386.015 | 0 | 4386.015
| 36 | 4113.5041 | 0 | 4113.5041
| 37 | 3996.4649 | 0 | 3996.4649
| 38 | 3854.2952 | 0 | 3854.2952
| 39 | 3800.5815 | 0 | 3800.5815
| 40 | 3755.7432 | 0 | 3755.7432
| 41 | 3907.4734 | 0 | 3907.4734
| 42 | 4114.6453 | 0 | 4114.6453
| 43 | 4124.4459 | 0 | 4124.4459
| 44 | 4251.3482 | 0 | 4251.3482
| 45 | 4660.704 | 0 | 4660.704
| 46 | 1520.0105 | 0 | 1520.0105
| 47 | 1422.2497 | 0 | 1422.2497
| 48 | 1677.5908 | 0 | 1677.5908
| 49 | 1838.8304 | 0 | 1838.8304
| 50 | 2051.6181 | 0 | 2051.6181
| 51 | 2138.5581 | 0 | 2138.5581
| 52 | 2183.8099 | 0 | 2183.8099
| 53 | 2280.5824 | 0 | 2280.5824
| 54 | 2329.3168 | 0 | 2329.3168
| 55 | 12745.9774 | 0 | 12745.9774
| 56 | 9897.8125 | 0 | 9897.8125
| 57 | 8216.0202 | 0 | 8216.0202
| 58 | 6950.0968 | 0 | 6950.0968
| 59 | 6183.6601 | 0 | 6183.6601
| 60 | 5598.4121 | 0 | 5598.4121
| 61 | 5121.3579 | 0 | 5121.3579
| 62 | 4715.1426 | 0 | 4715.1426
| 63 | 4453.9446 | 0 | 4453.9446
| 64 | 4758.2466 | 0 | 4758.2466
| 65 | 5152.0593 | 0 | 5152.0593
| 66 | 5504.9261 | 0 | 5504.9261
| 67 | 5671.0168 | 0 | 5671.0168
| 68 | 6096.2824 | 0 | 6096.2824
| 69 | 6554.6803 | 0 | 6554.6803
| 70 | 1999.6018 | 0 | 1999.6018
| 71 | 1917.1231 | 0 | 1917.1231
| 72 | 2197.806 | 0 | 2197.806
| 73 | 2551.9975 | 0 | 2551.9975
| 74 | 2681.7466 | 0 | 2681.7466
| 75 | 2695.0365 | 0 | 2695.0365
| 76 | 2751.4477 | 0 | 2751.4477
| 77 | 2840.9879 | 0 | 2840.9879
| 78 | 2892.2162 | 0 | 2892.2162
| 79 | 14462.4776 | 0 | 14462.4776
| 80 | 11935.9063 | 0 | 11935.9063
| 81 | 9692.7476 | 0 | 9692.7476
| 82 | 7843.3882 | 0 | 7843.3882
| 83 | 6756.3521 | 0 | 6756.3521
| 84 | 5658.8731 | 0 | 5658.8731
| 85 | 5239.1697 | 0 | 5239.1697
| 86 | 5060.4202 | 0 | 5060.4202
| 87 | 4879.0499 | 0 | 4879.0499
| 88 | 4804.8287 | 0 | 4804.8287
| 89 | 4960.0602 | 0 | 4960.0602
| 90 | 5079.3677 | 0 | 5079.3677
| 91 | 4979.138 | 0 | 4979.138
| 92 | 5039.2069 | 0 | 5039.2069
| 93 | 5347.897 | 0 | 5347.897
| 94 | 1562.0824 | 0 | 1562.0824
| 95 | 1345.1009 | 0 | 1345.1009
| 96 | 1559.8756 | 0 | 1559.8756
| 97 | 1680.6397 | 0 | 1680.6397
| 98 | 1685.8505 | 0 | 1685.8505
| 99 | 1813.1312 | 0 | 1813.1312
| 100 | 1993.4031 | 0 | 1993.4031
| 101 | 2072.5462 | 0 | 2072.5462
| 102 | 2099.62 | 0 | 2099.62
| 103 | 11280.8654 | 0 | 11280.8654
| 104 | 8726.8752 | 0 | 8726.8752
| 105 | 7688.6315 | 0 | 7688.6315
| 106 | 6643.107 | 0 | 6643.107
| 107 | 5555.1701 | 0 | 5555.1701
| 108 | 4754.4708 | 0 | 4754.4708
| 109 | 4581.637 | 0 | 4581.637
| 110 | 4618.2294 | 0 | 4618.2294
| 111 | 4690.1347 | 0 | 4690.1347
| 112 | 4838.0394 | 0 | 4838.0394
| 113 | 5385.7005 | 0 | 5385.7005
| 114 | 5964.391 | 0 | 5964.391
| 115 | 6626.0659 | 0 | 6626.0659
| 116 | 7224.7334 | 0 | 7224.7334
| 117 | 7657.1586 | 0 | 7657.1586
| 118 | 8189.6409 | 0 | 8189.6409
| 119 | 2479.29 | 0 | 2479.29
| 120 | 2463.554 | 0 | 2463.554
| 121 | 2490.5163 | 0 | 2490.5163
| 122 | 2569.6651 | 0 | 2569.6651
| 123 | 2699.4133 | 0 | 2699.4133
| 124 | 2673.1878 | 0 | 2673.1878
| 125 | 2499.6736 | 0 | 2499.6736
| 126 | 2374.5374 | 0 | 2374.5374
| 127 | 2295.5819 | 0 | 2295.5819
| 128 | 2250.0713 | 0 | 2250.0713
| 129 | 11684.1612 | 0 | 11684.1612
| 130 | 8987.2106 | 0 | 8987.2106
| 131 | 7914.5556 | 0 | 7914.5556
| 132 | 7691.7517 | 0 | 7691.7517
| 133 | 7339.4772 | 0 | 7339.4772
| 134 | 7054.1201 | 0 | 7054.1201
| 135 | 6747.7968 | 0 | 6747.7968
| 136 | 6696.6847 | 0 | 6696.6847
| 137 | 6718.9704 | 0 | 6718.9704
| 138 | 8871.0684 | 0 | 8871.0684
| 139 | 9315.2374 | 0 | 9315.2374
| 140 | 2438.8869 | 0 | 2438.8869
| 141 | 2455.9922 | 0 | 2455.9922
| 142 | 2573.4817 | 0 | 2573.4817
| 143 | 2658.4621 | 0 | 2658.4621
| 144 | 2745.0962 | 0 | 2745.0962
| 145 | 2781.7456 | 0 | 2781.7456
| 146 | 2822.1373 | 0 | 2822.1373
| 147 | 2888.0087 | 0 | 2888.0087
| 148 | 2998.3715 | 0 | 2998.3715
| 149 | 3057.8832 | 0 | 3057.8832
| 150 | 3143.3988 | 0 | 3143.3988
| 151 | 14470.1748 | 0 | 14470.1748
| 152 | 12030.3488 | 0 | 12030.3488
| 153 | 10403.5055 | 0 | 10403.5055
| 154 | 8955.3592 | 0 | 8955.3592
| 155 | 8109.7015 | 0 | 8109.7015
| 156 | 7483.7989 | 0 | 7483.7989
| 157 | 7175.2689 | 0 | 7175.2689
| 158 | 6844.281 | 0 | 6844.281
| 159 | 6582.0558 | 0 | 6582.0558
| 160 | 6563.2599 | 0 | 6563.2599
| 161 | 6618.2238 | 0 | 6618.2238
| 162 | 6763.0497 | 0 | 6763.0497
| 163 | 6786.8053 | 0 | 6786.8053
| 164 | 6934.587 | 0 | 6934.587
| 165 | 7087.7924 | 0 | 7087.7924
| 166 | 2249.4669 | 0 | 2249.4669
| 167 | 2293.8017 | 0 | 2293.8017
| 168 | 2564.0076 | 0 | 2564.0076
| 169 | 2541.3136 | 0 | 2541.3136
| 170 | 2522.22 | 0 | 2522.22
| 171 | 2677.608 | 0 | 2677.608
| 172 | 2824.2283 | 0 | 2824.2283
| 173 | 2921.1836 | 0 | 2921.1836
| 174 | 2838.4642 | 0 | 2838.4642
| 175 | 13594.6413 | 0 | 13594.6413
| 176 | 11457.2025 | 0 | 11457.2025
| 177 | 10676.814 | 0 | 10676.814
| 178 | 9725.9313 | 0 | 9725.9313
| 179 | 8926.5467 | 0 | 8926.5467
| 180 | 8197.6168 | 0 | 8197.6168
| 181 | 7697.8719 | 0 | 7697.8719
| 182 | 7259.2633 | 0 | 7259.2633
| 183 | 7092.0546 | 0 | 7092.0546
| 184 | 7266.6171 | 0 | 7266.6171
| 185 | 7798.629 | 0 | 7798.629
| 186 | 8244.1816 | 0 | 8244.1816
| 187 | 8334.1508 | 0 | 8334.1508
| 188 | 8726.6709 | 0 | 8726.6709
| 189 | 9141.0227 | 0 | 9141.0227
| 190 | 2997.8748 | 0 | 2997.8748
| 191 | 3562.7246 | 0 | 3562.7246
| 192 | 3703.6085 | 0 | 3703.6085
| 193 | 3804.183 | 0 | 3804.183
| 194 | 4042.6364 | 0 | 4042.6364
| 195 | 4206.3995 | 0 | 4206.3995
| 196 | 4372.4342 | 0 | 4372.4342
| 197 | 4628.7386 | 0 | 4628.7386
| 198 | 4750.4484 | 0 | 4750.4484
| 199 | 17930.9157 | 0 | 17930.9157
| 200 | 15217.6642 | 0 | 15217.6642
| 201 | 12929.3702 | 0 | 12929.3702
| 202 | 10916.8897 | 0 | 10916.8897
| 203 | 9577.212 | 0 | 9577.212
| 204 | 8506.29 | 0 | 8506.29
| 205 | 7844.9788 | 0 | 7844.9788
| 206 | 7418.803 | 0 | 7418.803
| 207 | 7238.5731 | 0 | 7238.5731
| 208 | 7119.7917 | 0 | 7119.7917
| 209 | 7399.7876 | 0 | 7399.7876
| 210 | 7718.4334 | 0 | 7718.4334
| 211 | 7699.8967 | 0 | 7699.8967
| 212 | 8013.189 | 0 | 8013.189
| 213 | 8359.0096 | 0 | 8359.0096
| 214 | 2663.5601 | 0 | 2663.5601
| 215 | 3015.3371 | 0 | 3015.3371
| 216 | 3267.5416 | 0 | 3267.5416
| 217 | 3411.7912 | 0 | 3411.7912
| 218 | 3550.975 | 0 | 3550.975
| 219 | 3614.8333 | 0 | 3614.8333
| 220 | 3673.3262 | 0 | 3673.3262
| 221 | 3835.5534 | 0 | 3835.5534
| 222 | 3945.8526 | 0 | 3945.8526
| 223 | 16203.0084 | 0 | 16203.0084
| 224 | 13587.7371 | 0 | 13587.7371
| 225 | 11580.4788 | 0 | 11580.4788
| 226 | 9864.7978 | 0 | 9864.7978
| 227 | 8922.8781 | 0 | 8922.8781
| 228 | 8119.0202 | 0 | 8119.0202
| 229 | 7606.1753 | 0 | 7606.1753
| 230 | 7232.5098 | 0 | 7232.5098
| 231 | 6948.7627 | 0 | 6948.7627
| 232 | 6901.2266 | 0 | 6901.2266
| 233 | 7113.288 | 0 | 7113.288
| 234 | 7328.776 | 0 | 7328.776
| 235 | 7470.3874 | 0 | 7470.3874
| 236 | 7979.9095 | 0 | 7979.9095
| 237 | 8625.327 | 0 | 8625.327
| 238 | 2808.4851 | 0 | 2808.4851
| 239 | 3089.6912 | 0 | 3089.6912
| 240 | 3476.5096 | 0 | 3476.5096
| 241 | 3700.8988 | 0 | 3700.8988
| 242 | 3714.8101 | 0 | 3714.8101
| 243 | 3757.9502 | 0 | 3757.9502
| 244 | 3827.0655 | 0 | 3827.0655
| 245 | 3886.5247 | 0 | 3886.5247
| 246 | 4037.7815 | 0 | 4037.7815
| 247 | 17266.2479 | 0 | 17266.2479
| 248 | 14305.6268 | 0 | 14305.6268
| 249 | 12053.4598 | 0 | 12053.4598
| 250 | 10219.2646 | 0 | 10219.2646
| 251 | 9016.5468 | 0 | 9016.5468
| 252 | 8117.2579 | 0 | 8117.2579
| 253 | 7470.6037 | 0 | 7470.6037
| 254 | 6985.9022 | 0 | 6985.9022
| 255 | 6306.7018 | 0 | 6306.7018
| 256 | 6244.3246 | 0 | 6244.3246
| 257 | 6684.1389 | 0 | 6684.1389
| 258 | 7128.1425 | 0 | 7128.1425
| 259 | 7113.7912 | 0 | 7113.7912
| 260 | 7383.0432 | 0 | 7383.0432
| 261 | 7779.6273 | 0 | 7779.6273
| 262 | 2517.7187 | 0 | 2517.7187
| 263 | 2840.243 | 0 | 2840.243
| 264 | 3096.6842 | 0 | 3096.6842
| 265 | 3121.3798 | 0 | 3121.3798
| 266 | 3281.4865 | 0 | 3281.4865
| 267 | 3293.2841 | 0 | 3293.2841
| 268 | 3309.2727 | 0 | 3309.2727
| 269 | 3465.028 | 0 | 3465.028
| 270 | 3600.463 | 0 | 3600.463
| 271 | 15921.0697 | 0 | 15921.0697
| 272 | 13744.007 | 0 | 13744.007
| 273 | 11886.9973 | 0 | 11886.9973
| 274 | 9730.6558 | 0 | 9730.6558
| 275 | 8044.6025 | 0 | 8044.6025
| 276 | 6999.5497 | 0 | 6999.5497
| 277 | 6493.3196 | 0 | 6493.3196
| 278 | 6004.2771 | 0 | 6004.2771
| 279 | 5721.8094 | 0 | 5721.8094
| 280 | 5764.2342 | 0 | 5764.2342
| 281 | 6020.3676 | 0 | 6020.3676
| 282 | 6343.9995 | 0 | 6343.9995
| 283 | 6571.8149 | 0 | 6571.8149
| 284 | 6915.3212 | 0 | 6915.3212
| 285 | 6884.1624 | 0 | 6884.1624
| 286 | 7170.6467 | 0 | 7170.6467
| 287 | 2142.3273 | 0 | 2142.3273
| 288 | 2139.8194 | 0 | 2139.8194
| 289 | 2124.2366 | 0 | 2124.2366
| 290 | 2093.5876 | 0 | 2093.5876
| 291 | 2118.5074 | 0 | 2118.5074
| 292 | 2109.7381 | 0 | 2109.7381
| 293 | 2067.9126 | 0 | 2067.9126
| 294 | 2049.943 | 0 | 2049.943
| 295 | 1984.2603 | 0 | 1984.2603
| 296 | 1955.3079 | 0 | 1955.3079
| 297 | 10382.4979 | 0 | 10382.4979
| 298 | 8272.4035 | 0 | 8272.4035
| 299 | 7146.4349 | 0 | 7146.4349
| 300 | 6433.1272 | 0 | 6433.1272
| 301 | 5784.7252 | 0 | 5784.7252
| 302 | 5483.3188 | 0 | 5483.3188
| 303 | 5279.6398 | 0 | 5279.6398
| 304 | 5272.6956 | 0 | 5272.6956
| 305 | 5352.2903 | 0 | 5352.2903
| 306 | 7387.2563 | 0 | 7387.2563
| 307 | 7874.0238 | 0 | 7874.0238
| 308 | 2047.9016 | 0 | 2047.9016
| 309 | 2050.7107 | 0 | 2050.7107
| 310 | 2061.6485 | 0 | 2061.6485
| 311 | 2273.0296 | 0 | 2273.0296
| 312 | 2533.0076 | 0 | 2533.0076
| 313 | 2766.5708 | 0 | 2766.5708
| 314 | 2973.8897 | 0 | 2973.8897
| 315 | 2775.9811 | 0 | 2775.9811
| 316 | 2610.6898 | 0 | 2610.6898
| 317 | 2648.6791 | 0 | 2648.6791
| 318 | 2704.1509 | 0 | 2704.1509
| 319 | 13845.8759 | 0 | 13845.8759
| 320 | 10971.0883 | 0 | 10971.0883
| 321 | 9273.8638 | 0 | 9273.8638
| 322 | 7772.7978 | 0 | 7772.7978
| 323 | 6907.8563 | 0 | 6907.8563
| 324 | 6135.2364 | 0 | 6135.2364
| 325 | 5481.1196 | 0 | 5481.1196
| 326 | 4788.4035 | 0 | 4788.4035
| 327 | 4403.0199 | 0 | 4403.0199
| 328 | 4213.7282 | 0 | 4213.7282
| 329 | 4202.6587 | 0 | 4202.6587
| 330 | 4329.5657 | 0 | 4329.5657
| 331 | 4578.8965 | 0 | 4578.8965
| 332 | 4878.8123 | 0 | 4878.8123
| 333 | 5139.8384 | 0 | 5139.8384
| 334 | 1555.0851 | 0 | 1555.0851
| 335 | 1404.4424 | 0 | 1404.4424
| 336 | 1672.9382 | 0 | 1672.9382
| 337 | 1694.7366 | 0 | 1694.7366
| 338 | 1794.2712 | 0 | 1794.2712
| 339 | 1835.5339 | 0 | 1835.5339
| 340 | 1835.4316 | 0 | 1835.4316
| 341 | 1862.1521 | 0 | 1862.1521
| 342 | 1870.4811 | 0 | 1870.4811
| 343 | 11700.8088 | 0 | 11700.8088
| 344 | 8734.8361 | 0 | 8734.8361
| 345 | 7325.0015 | 0 | 7325.0015
| 346 | 6722.7417 | 0 | 6722.7417
| 347 | 6652.6391 | 0 | 6652.6391
| 348 | 6385.0524 | 0 | 6385.0524
| 349 | 6320.1332 | 0 | 6320.1332
| 350 | 6358.2131 | 0 | 6358.2131
| 351 | 6496.3609 | 0 | 6496.3609
| 352 | 6972.3193 | 0 | 6972.3193
| 353 | 7661.4881 | 0 | 7661.4881
| 354 | 8190.011 | 0 | 8190.011
| 355 | 8352.0118 | 0 | 8352.0118
| 356 | 8759.058 | 0 | 8759.058
| 357 | 9138.1695 | 0 | 9138.1695
| 358 | 2978.8962 | 0 | 2978.8962
| 359 | 3469.7049 | 0 | 3469.7049
| 360 | 3995.0066 | 0 | 3995.0066
| 361 | 4181.4039 | 0 | 4181.4039
| 362 | 4260.4604 | 0 | 4260.4604
| 363 | 4468.0696 | 0 | 4468.0696
| 364 | 4658.4325 | 0 | 4658.4325
| 365 | 4839.4398 | 0 | 4839.4398
| 366 | 4853.0102 | 0 | 4853.0102
| 367 | 18348.4894 | 0 | 18348.4894
| 368 | 16076.582 | 0 | 16076.582
| 369 | 13843.4868 | 0 | 13843.4868
| 370 | 11752.0408 | 0 | 11752.0408
| 371 | 10211.8251 | 0 | 10211.8251
| 372 | 9165.8395 | 0 | 9165.8395
| 373 | 8447.6027 | 0 | 8447.6027
| 374 | 7777.7055 | 0 | 7777.7055
| 375 | 7437.339 | 0 | 7437.339
| 376 | 7257.5419 | 0 | 7257.5419
| 377 | 7661.5641 | 0 | 7661.5641
| 378 | 8142.7086 | 0 | 8142.7086
| 379 | 8229.0752 | 0 | 8229.0752
| 380 | 8581.3197 | 0 | 8581.3197
| 381 | 8703.0651 | 0 | 8703.0651
| 382 | 2701.8081 | 0 | 2701.8081
| 383 | 2841.9195 | 0 | 2841.9195
| 384 | 3005.5816 | 0 | 3005.5816
| 385 | 3089.0984 | 0 | 3089.0984
| 386 | 3174.0163 | 0 | 3174.0163
| 387 | 3220.563 | 0 | 3220.563
| 388 | 3147.9075 | 0 | 3147.9075
| 389 | 3114.8263 | 0 | 3114.8263
| 390 | 3221.0277 | 0 | 3221.0277
| 391 | 15307.3316 | 0 | 15307.3316
| 392 | 12665.8719 | 0 | 12665.8719
| 393 | 10815.859 | 0 | 10815.859
| 394 | 9464.9315 | 0 | 9464.9315
| 395 | 8288.516 | 0 | 8288.516
| 396 | 7219.6851 | 0 | 7219.6851
| 397 | 6651.0699 | 0 | 6651.0699
| 398 | 6318.2502 | 0 | 6318.2502
| 399 | 6183.8511 | 0 | 6183.8511
| 400 | 5986.9169 | 0 | 5986.9169
| 401 | 5957.7991 | 0 | 5957.7991
| 402 | 6012.4496 | 0 | 6012.4496
| 403 | 6026.9856 | 0 | 6026.9856
| 404 | 6141.7119 | 0 | 6141.7119
| 405 | 6418.0925 | 0 | 6418.0925
| 406 | 1925.7357 | 0 | 1925.7357
| 407 | 1812.8857 | 0 | 1812.8857
| 408 | 2122.3409 | 0 | 2122.3409
| 409 | 2204.5692 | 0 | 2204.5692
| 410 | 2181.1575 | 0 | 2181.1575
| 411 | 2261.9968 | 0 | 2261.9968
| 412 | 2331.7089 | 0 | 2331.7089
| 413 | 2371.3719 | 0 | 2371.3719
| 414 | 2345.9386 | 0 | 2345.9386
| 415 | 13229.3985 | 0 | 13229.3985
| 416 | 10842.0564 | 0 | 10842.0564
| 417 | 9402.2631 | 0 | 9402.2631
| 418 | 7220.4164 | 0 | 7220.4164
| 419 | 5983.4483 | 0 | 5983.4483
| 420 | 5138.813 | 0 | 5138.813
| 421 | 4448.8985 | 0 | 4448.8985
| 422 | 4028.4517 | 0 | 4028.4517
| 423 | 4081.3217 | 0 | 4081.3217
| 424 | 4216.3397 | 0 | 4216.3397
| 425 | 4366.9703 | 0 | 4366.9703
| 426 | 4649.4375 | 0 | 4649.4375
| 427 | 5172.2865 | 0 | 5172.2865
| 428 | 5885.2163 | 0 | 5885.2163
| 429 | 6426.5328 | 0 | 6426.5328
| 430 | 1990.6164 | 0 | 1990.6164
| 431 | 1918.1066 | 0 | 1918.1066
| 432 | 2188.7375 | 0 | 2188.7375
| 433 | 2323.2163 | 0 | 2323.2163
| 434 | 2436.8003 | 0 | 2436.8003
| 435 | 2527.3718 | 0 | 2527.3718
| 436 | 2461.5637 | 0 | 2461.5637
| 437 | 2415.5506 | 0 | 2415.5506
| 438 | 2405.6756 | 0 | 2405.6756
| 439 | 12560.1563 | 0 | 12560.1563
| 440 | 9785.0175 | 0 | 9785.0175
| 441 | 8107.8952 | 0 | 8107.8952
| 442 | 6932.7071 | 0 | 6932.7071
| 443 | 5904.0375 | 0 | 5904.0375
| 444 | 5134.324 | 0 | 5134.324
| 445 | 4775.6981 | 0 | 4775.6981
| 446 | 4581.8115 | 0 | 4581.8115
| 447 | 4814.6389 | 0 | 4814.6389
| 448 | 5009.8656 | 0 | 5009.8656
| 449 | 4912.8792 | 0 | 4912.8792
| 450 | 5122.6577 | 0 | 5122.6577
| 451 | 5527.3033 | 0 | 5527.3033
| 452 | 6283.8808 | 0 | 6283.8808
| 453 | 6594.8159 | 0 | 6594.8159
| 454 | 7256.2896 | 0 | 7256.2896
| 455 | 2407.7909 | 0 | 2407.7909
| 456 | 2473.831 | 0 | 2473.831
| 457 | 2608.3876 | 0 | 2608.3876
| 458 | 2872.9596 | 0 | 2872.9596
| 459 | 3079.1414 | 0 | 3079.1414
| 460 | 3277.8646 | 0 | 3277.8646
| 461 | 3382.2697 | 0 | 3382.2697
| 462 | 3488.2981 | 0 | 3488.2981
| 463 | 3493.5204 | 0 | 3493.5204
| 464 | 3508.6455 | 0 | 3508.6455
| 465 | 14589.4776 | 0 | 14589.4776
| 466 | 12455.3227 | 0 | 12455.3227
| 467 | 11142.1201 | 0 | 11142.1201
| 468 | 10281.0562 | 0 | 10281.0562
| 469 | 8996.6364 | 0 | 8996.6364
| 470 | 8503.6595 | 0 | 8503.6595
| 471 | 8476.6478 | 0 | 8476.6478
| 472 | 8711.9699 | 0 | 8711.9699
| 473 | 8842.7424 | 0 | 8842.7424
| 474 | 11697.6013 | 0 | 11697.6013
| 475 | 12366.4596 | 0 | 12366.4596
| 476 | 3613.9406 | 0 | 3613.9406
| 477 | 3800.0379 | 0 | 3800.0379
| 478 | 3764.072 | 0 | 3764.072
| 479 | 3722.8066 | 0 | 3722.8066
| 480 | 3963.7331 | 0 | 3963.7331
| 481 | 4156.9806 | 0 | 4156.9806
| 482 | 4126.6409 | 0 | 4126.6409
| 483 | 4264.2425 | 0 | 4264.2425
| 484 | 4463.7385 | 0 | 4463.7385
| 485 | 4593.181 | 0 | 4593.181
| 486 | 4693.1112 | 0 | 4693.1112
| 487 | 17933.7988 | 0 | 17933.7988
| 488 | 15510.575 | 0 | 15510.575
| 489 | 13535.2096 | 0 | 13535.2096
| 490 | 11817.1085 | 0 | 11817.1085
| 491 | 10706.1608 | 0 | 10706.1608
| 492 | 9798.6158 | 0 | 9798.6158
| 493 | 9211.0416 | 0 | 9211.0416
| 494 | 8527.3972 | 0 | 8527.3972
| 495 | 8351.6592 | 0 | 8351.6592
| 496 | 8420.0544 | 0 | 8420.0544
| 497 | 8510.3993 | 0 | 8510.3993
| 498 | 8671.0863 | 0 | 8671.0863
| 499 | 8647.8052 | 0 | 8647.8052
| 500 | 8858.4704 | 0 | 8858.4704
| 501 | 9159.6021 | 0 | 9159.6021
| 502 | 2934.2883 | 0 | 2934.2883
| 503 | 3195.3603 | 0 | 3195.3603
| 504 | 3458.7546 | 0 | 3458.7546
| 505 | 3524.7075 | 0 | 3524.7075
| 506 | 3489.4274 | 0 | 3489.4274
| 507 | 3436.3798 | 0 | 3436.3798
| 508 | 3433.1456 | 0 | 3433.1456
| 509 | 3635.7007 | 0 | 3635.7007
| 510 | 3792.9613 | 0 | 3792.9613
| 511 | 16104.6099 | 0 | 16104.6099
| 512 | 13647.0036 | 0 | 13647.0036
| 513 | 10835.7765 | 0 | 10835.7765
| 514 | 8205.3908 | 0 | 8205.3908
| 515 | 6853.3572 | 0 | 6853.3572
| 516 | 5848.8791 | 0 | 5848.8791
| 517 | 5204.3305 | 0 | 5204.3305
| 518 | 4701.0487 | 0 | 4701.0487
| 519 | 4688.8421 | 0 | 4688.8421
| 520 | 4699.5306 | 0 | 4699.5306
| 521 | 4886.1329 | 0 | 4886.1329
| 522 | 5251.3523 | 0 | 5251.3523
| 523 | 5298.4909 | 0 | 5298.4909
| 524 | 5546.7353 | 0 | 5546.7353
| 525 | 5843.4585 | 0 | 5843.4585
| 526 | 1774.7077 | 0 | 1774.7077
| 527 | 1648.017 | 0 | 1648.017
| 528 | 1836.0665 | 0 | 1836.0665
| 529 | 1922.1337 | 0 | 1922.1337
| 530 | 1931.0195 | 0 | 1931.0195
| 531 | 1947.6298 | 0 | 1947.6298
| 532 | 1944.9096 | 0 | 1944.9096
| 533 | 2035.3254 | 0 | 2035.3254
| 534 | 2109.7949 | 0 | 2109.7949
| 535 | 11863.5572 | 0 | 11863.5572
| 536 | 9131.6617 | 0 | 9131.6617
| 537 | 7659.7493 | 0 | 7659.7493
| 538 | 6490.5988 | 0 | 6490.5988
| 539 | 5768.4444 | 0 | 5768.4444
| 540 | 5151.1247 | 0 | 5151.1247
| 541 | 4913.0363 | 0 | 4913.0363
| 542 | 4835.3591 | 0 | 4835.3591
| 543 | 4877.4893 | 0 | 4877.4893
| 544 | 4749.2134 | 0 | 4749.2134
| 545 | 4932.6503 | 0 | 4932.6503
| 546 | 5308.5428 | 0 | 5308.5428
| 547 | 5415.7434 | 0 | 5415.7434
| 548 | 5543.5668 | 0 | 5543.5668
| 549 | 5678.3722 | 0 | 5678.3722
| 550 | 1668.2905 | 0 | 1668.2905
| 551 | 1501.151 | 0 | 1501.151
| 552 | 1731.6636 | 0 | 1731.6636
| 553 | 1846.7424 | 0 | 1846.7424
| 554 | 1964.3895 | 0 | 1964.3895
| 555 | 1963.4239 | 0 | 1963.4239
| 556 | 1970.3037 | 0 | 1970.3037
| 557 | 1981.6993 | 0 | 1981.6993
| 558 | 1966.91 | 0 | 1966.91
| 559 | 11752.5136 | 0 | 11752.5136
| 560 | 9017.046 | 0 | 9017.046
| 561 | 7439.5213 | 0 | 7439.5213
| 562 | 6142.6834 | 0 | 6142.6834
| 563 | 5423.0598 | 0 | 5423.0598
| 564 | 4794.8019 | 0 | 4794.8019
| 565 | 4282.2189 | 0 | 4282.2189
| 566 | 3909.7878 | 0 | 3909.7878
| 567 | 3731.6613 | 0 | 3731.6613
| 568 | 3702.7454 | 0 | 3702.7454
| 569 | 4036.4847 | 0 | 4036.4847
| 570 | 4542.7736 | 0 | 4542.7736
| 571 | 5186.1694 | 0 | 5186.1694
| 572 | 5699.1975 | 0 | 5699.1975
| 573 | 5935.3851 | 0 | 5935.3851
| 574 | 1713.2321 | 0 | 1713.2321
| 575 | 1454.7515 | 0 | 1454.7515
| 576 | 1709.2518 | 0 | 1709.2518
| 577 | 1823.9607 | 0 | 1823.9607
| 578 | 1872.5258 | 0 | 1872.5258
| 579 | 1940.4433 | 0 | 1940.4433
| 580 | 1931.0408 | 0 | 1931.0408
| 581 | 1957.6783 | 0 | 1957.6783
| 582 | 2008.1374 | 0 | 2008.1374
| 583 | 11618.2907 | 0 | 11618.2907
| 584 | 8782.2785 | 0 | 8782.2785
| 585 | 7303.7363 | 0 | 7303.7363
| 586 | 6185.3598 | 0 | 6185.3598
| 587 | 5559.3468 | 0 | 5559.3468
| 588 | 4904.6212 | 0 | 4904.6212
| 589 | 4372.264 | 0 | 4372.264
| 590 | 4040.7304 | 0 | 4040.7304
| 591 | 4002.3665 | 0 | 4002.3665
| 592 | 3986.2113 | 0 | 3986.2113
| 593 | 4160.197 | 0 | 4160.197
| 594 | 4519.9715 | 0 | 4519.9715
| 595 | 4934.5194 | 0 | 4934.5194
| 596 | 5394.0761 | 0 | 5394.0761
| 597 | 6174.4249 | 0 | 6174.4249
| 598 | 1899.7205 | 0 | 1899.7205
| 599 | 1838.3862 | 0 | 1838.3862
| 600 | 2185.8369 | 0 | 2185.8369
| 601 | 2554.695 | 0 | 2554.695
| 602 | 2452.9043 | 0 | 2452.9043
| 603 | 2281.1239 | 0 | 2281.1239
| 604 | 2333.1041 | 0 | 2333.1041
| 605 | 2404.8829 | 0 | 2404.8829
| 606 | 2489.8592 | 0 | 2489.8592
| 607 | 12709.7444 | 0 | 12709.7444
| 608 | 9983.3605 | 0 | 9983.3605
| 609 | 8535.004 | 0 | 8535.004
| 610 | 7182.8588 | 0 | 7182.8588
| 611 | 6264.0166 | 0 | 6264.0166
| 612 | 5564.573 | 0 | 5564.573
| 613 | 5320.0906 | 0 | 5320.0906
| 614 | 5316.7747 | 0 | 5316.7747
| 615 | 5358.2131 | 0 | 5358.2131
| 616 | 5413.9595 | 0 | 5413.9595
| 617 | 5850.6312 | 0 | 5850.6312
| 618 | 6340.1413 | 0 | 6340.1413
| 619 | 6889.7437 | 0 | 6889.7437
| 620 | 7320.9478 | 0 | 7320.9478
| 621 | 7718.2251 | 0 | 7718.2251
| 622 | 8226.6536 | 0 | 8226.6536
| 623 | 2628.7616 | 0 | 2628.7616
| 624 | 2702.9916 | 0 | 2702.9916
| 625 | 2889.1746 | 0 | 2889.1746
| 626 | 2934.371 | 0 | 2934.371
| 627 | 2939.6175 | 0 | 2939.6175
| 628 | 3016.7388 | 0 | 3016.7388
| 629 | 3006.9553 | 0 | 3006.9553
| 630 | 2931.4774 | 0 | 2931.4774
| 631 | 2892.754 | 0 | 2892.754
| 632 | 2866.1982 | 0 | 2866.1982
| 633 | 13049.3888 | 0 | 13049.3888
| 634 | 10651.0195 | 0 | 10651.0195
| 635 | 9176.3666 | 0 | 9176.3666
| 636 | 8341.749 | 0 | 8341.749
| 637 | 7395.93 | 0 | 7395.93
| 638 | 6896.9106 | 0 | 6896.9106
| 639 | 6645.5188 | 0 | 6645.5188
| 640 | 6436.1064 | 0 | 6436.1064
| 641 | 6493.5196 | 0 | 6493.5196
| 642 | 8992.4166 | 0 | 8992.4166
| 643 | 9860.7416 | 0 | 9860.7416
| 644 | 2522.0739 | 0 | 2522.0739
| 645 | 2684.2271 | 0 | 2684.2271
| 646 | 2669.3856 | 0 | 2669.3856
| 647 | 2598.5402 | 0 | 2598.5402
| 648 | 2627.2759 | 0 | 2627.2759
| 649 | 2675.7451 | 0 | 2675.7451
| 650 | 2673.559 | 0 | 2673.559
| 651 | 2643.2532 | 0 | 2643.2532
| 652 | 2632.9433 | 0 | 2632.9433
| 653 | 2650.6359 | 0 | 2650.6359
| 654 | 2585.5711 | 0 | 2585.5711
| 655 | 13603.0995 | 0 | 13603.0995
| 656 | 10740.3408 | 0 | 10740.3408
| 657 | 8953.6914 | 0 | 8953.6914
| 658 | 7004.2644 | 0 | 7004.2644
| 659 | 5773.5313 | 0 | 5773.5313
| 660 | 4756.0434 | 0 | 4756.0434
| 661 | 4058.7028 | 0 | 4058.7028
| 662 | 3837.8081 | 0 | 3837.8081
| 663 | 4010.892 | 0 | 4010.892
| 664 | 3943.5484 | 0 | 3943.5484
| 665 | 4163.0043 | 0 | 4163.0043
| 666 | 4754.0574 | 0 | 4754.0574
| 667 | 5012.5274 | 0 | 5012.5274
| 668 | 5330.4202 | 0 | 5330.4202
| 669 | 5738.081 | 0 | 5738.081
| 670 | 1795.7908 | 0 | 1795.7908
| 671 | 1809.3189 | 0 | 1809.3189
| 672 | 2114.0254 | 0 | 2114.0254
| 673 | 2374.9361 | 0 | 2374.9361
| 674 | 2688.0262 | 0 | 2688.0262
| 675 | 2803.9515 | 0 | 2803.9515
| 676 | 2834.1378 | 0 | 2834.1378
| 677 | 2801.2121 | 0 | 2801.2121
| 678 | 2909.5202 | 0 | 2909.5202
| 679 | 14595.2257 | 0 | 14595.2257
| 680 | 12111.014 | 0 | 12111.014
| 681 | 9910.654 | 0 | 9910.654
| 682 | 8113.926 | 0 | 8113.926
| 683 | 6447.9588 | 0 | 6447.9588
| 684 | 5278.2925 | 0 | 5278.2925
| 685 | 5074.0041 | 0 | 5074.0041
| 686 | 4965.6815 | 0 | 4965.6815
| 687 | 4652.8261 | 0 | 4652.8261
| 688 | 4514.3312 | 0 | 4514.3312
| 689 | 4905.6447 | 0 | 4905.6447
| 690 | 5489.7125 | 0 | 5489.7125
| 691 | 5637.8817 | 0 | 5637.8817
| 692 | 5814.1289 | 0 | 5814.1289
| 693 | 6342.8209 | 0 | 6342.8209
| 694 | 2033.4203 | 0 | 2033.4203
| 695 | 2184.4296 | 0 | 2184.4296
| 696 | 2547.022 | 0 | 2547.022
| 697 | 2762.2977 | 0 | 2762.2977
| 698 | 2939.5651 | 0 | 2939.5651
| 699 | 3097.8855 | 0 | 3097.8855
| 700 | 3248.9686 | 0 | 3248.9686
| 701 | 3384.8788 | 0 | 3384.8788
| 702 | 3451.118 | 0 | 3451.118
| 703 | 15898.1088 | 0 | 15898.1088
| 704 | 13498.1291 | 0 | 13498.1291
| 705 | 10995.8663 | 0 | 10995.8663
| 706 | 8749.8157 | 0 | 8749.8157
| 707 | 7245.6925 | 0 | 7245.6925
| 708 | 5874.2889 | 0 | 5874.2889
| 709 | 5050.1707 | 0 | 5050.1707
| 710 | 4322.1207 | 13.6347 | 4308.486
| 711 | 4083.3627 | 35.4253 | 4047.9374
| 712 | 3948.4687 | 34.9635 | 3913.5052
| 713 | 4182.5462 | 9.2592 | 4173.287
| 714 | 4790.1301 | 0 | 4790.1301
| 715 | 5446.7883 | 0 | 5446.7883
| 716 | 5952.7106 | 0 | 5952.7106
| 717 | 6548.3241 | 0 | 6548.3241
| 718 | 2037.554 | 0 | 2037.554
| 719 | 2032.1191 | 0 | 2032.1191
| 720 | 2400.3915 | 0 | 2400.3915
| 721 | 2695.1839 | 0 | 2695.1839
| 722 | 2911.7403 | 0 | 2911.7403
| 723 | 3237.9994 | 0 | 3237.9994
| 724 | 3336.4174 | 0 | 3336.4174
| 725 | 3380.5342 | 0 | 3380.5342
| 726 | 3402.414 | 0 | 3402.414
| 727 | 15709.5113 | 0 | 15709.5113
| 728 | 13193.2155 | 0 | 13193.2155
| 729 | 11328.8493 | 0 | 11328.8493
| 730 | 9628.7164 | 0 | 9628.7164
| 731 | 8672.537 | 0 | 8672.537
| 732 | 7787.0158 | 0 | 7787.0158
| 733 | 7141.9893 | 0 | 7141.9893
| 734 | 6589.8386 | 0 | 6589.8386
| 735 | 6315.1146 | 0 | 6315.1146
| 736 | 6215.4784 | 0 | 6215.4784
| 737 | 6275.2195 | 0 | 6275.2195
| 738 | 6442.4519 | 0 | 6442.4519
| 739 | 6377.5258 | 0 | 6377.5258
| 740 | 6547.868 | 0 | 6547.868
| 741 | 6775.1101 | 0 | 6775.1101
| 742 | 1843.6822 | 0 | 1843.6822
| 743 | 1480.7455 | 0 | 1480.7455
| 744 | 1497.6615 | 0 | 1497.6615
| 745 | 1400.2836 | 0 | 1400.2836
| 746 | 1261.9026 | 0 | 1261.9026
| 747 | 1109.6386 | 0 | 1109.6386
| 748 | 950.6362 | 0 | 950.6362
| 749 | 883.7069 | 0 | 883.7069
| 750 | 859.7209 | 0 | 859.7209
| 751 | 7615.7336 | 7.6312 | 7608.1024
| 752 | 5390.816 | 0 | 5390.816
| 753 | 4162.7614 | 0 | 4162.7614
| 754 | 3103.5633 | 0 | 3103.5633
| 755 | 2581.1997 | 0 | 2581.1997
| 756 | 2089.3772 | 0 | 2089.3772
| 757 | 1851.9088 | 0 | 1851.9088
| 758 | 1632.3596 | 0 | 1632.3596
| 759 | 1496.2981 | 0 | 1496.2981
| 760 | 1415.5709 | 0 | 1415.5709
| 761 | 1444.4412 | 0 | 1444.4412
| 762 | 1614.821 | 0 | 1614.821
| 763 | 1773.8943 | 0 | 1773.8943
| 764 | 1975.7546 | 0 | 1975.7546
| 765 | 2126.8035 | 0 | 2126.8035
| 766 | 588.8891 | 0 | 588.8891
| 767 | 548.554 | 0 | 548.554
| 768 | 572.5059 | 0 | 572.5059
| 769 | 581.4864 | 0 | 581.4864
| 770 | 570.2683 | 0 | 570.2683
| 771 | 566.6387 | 0 | 566.6387
| 772 | 569.9756 | 0 | 569.9756
| 773 | 568.1907 | 0 | 568.1907
| 774 | 543.532 | 0 | 543.532
| 775 | 5341.3411 | 20.059 | 5321.2822
| 776 | 4303.3275 | 0 | 4303.3275
| 777 | 4123.9278 | 0 | 4123.9278
| 778 | 3855.9078 | 0 | 3855.9078
| 779 | 3677.2428 | 0 | 3677.2428
| 780 | 3444.8834 | 0 | 3444.8834
| 781 | 3456.8867 | 0 | 3456.8867
| 782 | 3676.6092 | 0 | 3676.6092
| 783 | 3814.7087 | 0 | 3814.7087
| 784 | 3902.6514 | 0 | 3902.6514
| 785 | 4107.8379 | 0 | 4107.8379
| 786 | 4427.3197 | 0 | 4427.3197
| 787 | 4880.1145 | 0 | 4880.1145
| 788 | 5573.7946 | 0 | 5573.7946
| 789 | 6052.1788 | 0 | 6052.1788
| 790 | 6685.2243 | 0 | 6685.2243
| 791 | 2077.6786 | 0 | 2077.6786
| 792 | 2207.2702 | 0 | 2207.2702
| 793 | 2484.452 | 0 | 2484.452
| 794 | 2721.9951 | 0 | 2721.9951
| 795 | 2793.5219 | 0 | 2793.5219
| 796 | 2860.4004 | 0 | 2860.4004
| 797 | 2965.6629 | 0 | 2965.6629
| 798 | 3119.9856 | 0 | 3119.9856
| 799 | 3243.2101 | 0 | 3243.2101
| 800 | 3282.1666 | 0 | 3282.1666
| 801 | 13824.7162 | 0 | 13824.7162
| 802 | 11069.4307 | 0 | 11069.4307
| 803 | 9471.5727 | 0 | 9471.5727
| 804 | 8387.7408 | 0 | 8387.7408
| 805 | 7216.4697 | 0 | 7216.4697
| 806 | 6774.62 | 0 | 6774.62
| 807 | 6380.4926 | 0 | 6380.4926
| 808 | 6112.4953 | 0 | 6112.4953
| 809 | 6092.9273 | 0 | 6092.9273
| 810 | 8302.0198 | 0 | 8302.0198
| 811 | 8784.9295 | 0 | 8784.9295
| 812 | 2128.2712 | 0 | 2128.2712
| 813 | 2030.8168 | 0 | 2030.8168
| 814 | 1965.2883 | 0 | 1965.2883
| 815 | 2010.9728 | 0 | 2010.9728
| 816 | 2057.7055 | 0 | 2057.7055
| 817 | 2133.6685 | 0 | 2133.6685
| 818 | 2240.5811 | 0 | 2240.5811
| 819 | 2236.2402 | 0 | 2236.2402
| 820 | 2235.0706 | 0 | 2235.0706
| 821 | 2292.0132 | 0 | 2292.0132
| 822 | 2275.8189 | 0 | 2275.8189
| 823 | 12667.4131 | 0 | 12667.4131
| 824 | 9826.992 | 0 | 9826.992
| 825 | 8217.5937 | 0 | 8217.5937
| 826 | 6849.9038 | 0 | 6849.9038
| 827 | 6036.3277 | 0 | 6036.3277
| 828 | 5394.1328 | 0 | 5394.1328
| 829 | 4991.632 | 0 | 4991.632
| 830 | 4725.0088 | 0 | 4725.0088
| 831 | 4553.1608 | 0 | 4553.1608
| 832 | 4453.7311 | 0 | 4453.7311
| 833 | 5077.6401 | 0 | 5077.6401
| 834 | 5891.5552 | 0 | 5891.5552
| 835 | 6116.9172 | 0 | 6116.9172
| 836 | 6346.9333 | 0 | 6346.9333
| 837 | 6778.6411 | 0 | 6778.6411
| 838 | 2156.5158 | 0 | 2156.5158
| 839 | 2329.2044 | 0 | 2329.2044
| 840 | 2685.2428 | 0 | 2685.2428
| 841 | 2934.7496 | 0 | 2934.7496
| 842 | 3138.9027 | 0 | 3138.9027
| 843 | 3281.8554 | 0 | 3281.8554
| 844 | 3354.9169 | 0 | 3354.9169
| 845 | 3501.746 | 0 | 3501.746
| 846 | 3617.4648 | 0 | 3617.4648
| 847 | 15790.4714 | 0 | 15790.4714
| 848 | 13698.6437 | 0 | 13698.6437
| 849 | 11633.6661 | 0 | 11633.6661
| 850 | 9788.4115 | 0 | 9788.4115
| 851 | 8577.7923 | 0 | 8577.7923
| 852 | 7587.2712 | 0 | 7587.2712
| 853 | 7101.5728 | 0 | 7101.5728
| 854 | 6776.7851 | 0 | 6776.7851
| 855 | 6569.8711 | 0 | 6569.8711
| 856 | 6484.323 | 0 | 6484.323
| 857 | 6684.8524 | 0 | 6684.8524
| 858 | 7565.7547 | 0 | 7565.7547
| 859 | 8184.0099 | 0 | 8184.0099
| 860 | 9284.3241 | 0 | 9284.3241
| 861 | 9770.9356 | 0 | 9770.9356
| 862 | 2923.7318 | 0 | 2923.7318
| 863 | 3054.1304 | 0 | 3054.1304
| 864 | 3532.1643 | 0 | 3532.1643
| 865 | 3831.7737 | 0 | 3831.7737
| 866 | 3713.7947 | 0 | 3713.7947
| 867 | 3834.747 | 0 | 3834.747
| 868 | 3761.0241 | 0 | 3761.0241
| 869 | 3539.8389 | 0 | 3539.8389
| 870 | 3506.5083 | 0 | 3506.5083
| 871 | 16175.8339 | 0 | 16175.8339
| 872 | 13800.9973 | 0 | 13800.9973
| 873 | 11440.0215 | 0 | 11440.0215
| 874 | 9518.3842 | 0 | 9518.3842
| 875 | 8411.2487 | 0 | 8411.2487
| 876 | 7494.9777 | 0 | 7494.9777
| 877 | 6852.1701 | 0 | 6852.1701
| 878 | 6379.614 | 0 | 6379.614
| 879 | 6245.3069 | 0 | 6245.3069
| 880 | 6348.9269 | 0 | 6348.9269
| 881 | 6652.4896 | 0 | 6652.4896
| 882 | 7076.5474 | 0 | 7076.5474
| 883 | 7284.3901 | 0 | 7284.3901
| 884 | 7795.0123 | 0 | 7795.0123
| 885 | 8675.5644 | 0 | 8675.5644
| 886 | 2765.9058 | 0 | 2765.9058
| 887 | 3037.0975 | 0 | 3037.0975
| 888 | 3308.35 | 0 | 3308.35
| 889 | 3485.9212 | 0 | 3485.9212
| 890 | 3743.4275 | 0 | 3743.4275
| 891 | 3908.3508 | 0 | 3908.3508
| 892 | 3979.9279 | 0 | 3979.9279
| 893 | 4312.7143 | 0 | 4312.7143
| 894 | 4376.1303 | 0 | 4376.1303
| 895 | 17882.5674 | 0 | 17882.5674
| 896 | 15335.1095 | 0 | 15335.1095
| 897 | 12784.6773 | 0 | 12784.6773
| 898 | 10495.2559 | 0 | 10495.2559
| 899 | 9016.1043 | 0 | 9016.1043
| 900 | 7963.1059 | 0 | 7963.1059
| 901 | 7379.7005 | 0 | 7379.7005
| 902 | 7065.4368 | 0 | 7065.4368
| 903 | 6637.88 | 0 | 6637.88
| 904 | 6315.1512 | 0 | 6315.1512
| 905 | 6396.5807 | 0 | 6396.5807
| 906 | 6623.9004 | 0 | 6623.9004
| 907 | 6683.8342 | 0 | 6683.8342
| 908 | 6766.4075 | 0 | 6766.4075
| 909 | 6984.0398 | 0 | 6984.0398
| 910 | 2123.8993 | 0 | 2123.8993
| 911 | 2226.9403 | 0 | 2226.9403
| 912 | 2387.1617 | 0 | 2387.1617
| 913 | 2468.2964 | 0 | 2468.2964
| 914 | 2475.6565 | 0 | 2475.6565
| 915 | 2510.1311 | 0 | 2510.1311
| 916 | 2557.3122 | 0 | 2557.3122
| 917 | 2544.0992 | 0 | 2544.0992
| 918 | 2565.6505 | 0 | 2565.6505
| 919 | 13615.7263 | 0 | 13615.7263
| 920 | 10767.7917 | 0 | 10767.7917
| 921 | 8756.5624 | 0 | 8756.5624
| 922 | 6911.4061 | 0 | 6911.4061
| 923 | 6135.0144 | 0 | 6135.0144
| 924 | 5553.0072 | 0 | 5553.0072
| 925 | 5201.4422 | 0 | 5201.4422
| 926 | 5064.9625 | 0 | 5064.9625
| 927 | 5069.9492 | 0 | 5069.9492
| 928 | 5174.1875 | 0 | 5174.1875
| 929 | 5447.1774 | 0 | 5447.1774
| 930 | 5847.5159 | 0 | 5847.5159
| 931 | 6028.7403 | 0 | 6028.7403
| 932 | 6339.0979 | 0 | 6339.0979
| 933 | 6931.4033 | 0 | 6931.4033
| 934 | 2048.4018 | 0 | 2048.4018
| 935 | 1943.7464 | 0 | 1943.7464
| 936 | 2293.065 | 0 | 2293.065
| 937 | 2557.7058 | 0 | 2557.7058
| 938 | 2709.615 | 0 | 2709.615
| 939 | 2883.5731 | 0 | 2883.5731
| 940 | 3243.1617 | 0 | 3243.1617
| 941 | 3611.131 | 0 | 3611.131
| 942 | 3769.0847 | 0 | 3769.0847
| 943 | 16575.5607 | 0 | 16575.5607
| 944 | 13941.7555 | 0 | 13941.7555
| 945 | 11848.6113 | 0 | 11848.6113
| 946 | 9498.3403 | 0 | 9498.3403
| 947 | 7659.4214 | 0 | 7659.4214
| 948 | 6515.0799 | 0 | 6515.0799
| 949 | 6044.152 | 0 | 6044.152
| 950 | 5296.9404 | 0 | 5296.9404
| 951 | 4729.2978 | 0 | 4729.2978
| 952 | 4603.8174 | 0 | 4603.8174
| 953 | 4569.7461 | 0 | 4569.7461
| 954 | 4707.8357 | 0 | 4707.8357
| 955 | 4850.7865 | 0 | 4850.7865
| 956 | 5301.6631 | 0 | 5301.6631
| 957 | 5565.8412 | 0 | 5565.8412
| 958 | 5983.5449 | 0 | 5983.5449
| 959 | 1742.2006 | 0 | 1742.2006
| 960 | 1781.211 | 0 | 1781.211
| 961 | 1814.4899 | 0 | 1814.4899
| 962 | 1830.3218 | 0 | 1830.3218
| 963 | 1850.3151 | 0 | 1850.3151
| 964 | 1892.2241 | 0 | 1892.2241
| 965 | 2013.6068 | 0 | 2013.6068
| 966 | 2110.5107 | 0 | 2110.5107
| 967 | 2103.0012 | 0 | 2103.0012
| 968 | 2165.5454 | 0 | 2165.5454
| 969 | 11132.0724 | 0 | 11132.0724
| 970 | 8503.6186 | 0 | 8503.6186
| 971 | 7234.1321 | 0 | 7234.1321
| 972 | 6488.371 | 0 | 6488.371
| 973 | 5729.5581 | 0 | 5729.5581
| 974 | 5339.4674 | 0 | 5339.4674
| 975 | 5077.2247 | 0 | 5077.2247
| 976 | 5001.2339 | 0 | 5001.2339
| 977 | 5177.7743 | 0 | 5177.7743
| 978 | 7513.706 | 0 | 7513.706
| 979 | 8197.6052 | 0 | 8197.6052
| 980 | 2140.6252 | 0 | 2140.6252
| 981 | 2228.5271 | 0 | 2228.5271
| 982 | 2390.094 | 0 | 2390.094
| 983 | 2723.2865 | 0 | 2723.2865
| 984 | 3032.3466 | 0 | 3032.3466
| 985 | 3100.0753 | 0 | 3100.0753
| 986 | 3198.2022 | 0 | 3198.2022
| 987 | 3164.9321 | 0 | 3164.9321
| 988 | 3211.2226 | 0 | 3211.2226
| 989 | 3206.7495 | 0 | 3206.7495
| 990 | 3121.2883 | 0 | 3121.2883
| 991 | 15123.4562 | 0 | 15123.4562
| 992 | 12694.8127 | 0 | 12694.8127
| 993 | 10379.3509 | 0 | 10379.3509
| 994 | 8102.4149 | 0 | 8102.4149
| 995 | 7096.3031 | 0 | 7096.3031
| 996 | 6385.3194 | 0 | 6385.3194
| 997 | 5774.5931 | 0 | 5774.5931
| 998 | 5409.4539 | 0 | 5409.4539
| 999 | 5232.9887 | 0 | 5232.9887
| 1000 | 5105.7567 | 0 | 5105.7567
| 1001 | 5179.4936 | 0 | 5179.4936
| 1002 | 5460.0161 | 0 | 5460.0161
| 1003 | 5585.7289 | 0 | 5585.7289
| 1004 | 5853.3144 | 0 | 5853.3144
| 1005 | 6158.5244 | 0 | 6158.5244
| 1006 | 1848.2959 | 0 | 1848.2959
| 1007 | 1763.8421 | 0 | 1763.8421
| 1008 | 2028.4332 | 0 | 2028.4332
| 1009 | 2141.83 | 0 | 2141.83
| 1010 | 2320.6169 | 0 | 2320.6169
| 1011 | 2416.7074 | 0 | 2416.7074
| 1012 | 2384.2601 | 0 | 2384.2601
| 1013 | 2258.7097 | 0 | 2258.7097
| 1014 | 2188.6116 | 0 | 2188.6116
| 1015 | 12461.9378 | 0 | 12461.9378
| 1016 | 9335.1869 | 0 | 9335.1869
| 1017 | 7531.3295 | 0 | 7531.3295
| 1018 | 6156.144 | 0 | 6156.144
| 1019 | 5392.0037 | 0 | 5392.0037
| 1020 | 4640.986 | 0 | 4640.986
| 1021 | 4114.9369 | 0 | 4114.9369
| 1022 | 3684.7404 | 0 | 3684.7404
| 1023 | 3447.73 | 0 | 3447.73
| 1024 | 3514.5177 | 0 | 3514.5177
| 1025 | 3859.3191 | 0 | 3859.3191
| 1026 | 4167.6906 | 0 | 4167.6906
| 1027 | 4252.5693 | 0 | 4252.5693
| 1028 | 4377.1928 | 0 | 4377.1928
| 1029 | 4616.4992 | 0 | 4616.4992
| 1030 | 1521.1056 | 0 | 1521.1056
| 1031 | 1682.9003 | 0 | 1682.9003
| 1032 | 2119.9615 | 0 | 2119.9615
| 1033 | 2417.0521 | 0 | 2417.0521
| 1034 | 2571.6307 | 0 | 2571.6307
| 1035 | 2720.0259 | 0 | 2720.0259
| 1036 | 2770.9305 | 0 | 2770.9305
| 1037 | 2686.7567 | 0 | 2686.7567
| 1038 | 2649.4557 | 0 | 2649.4557
| 1039 | 13384.1385 | 0 | 13384.1385
| 1040 | 10463.3673 | 0 | 10463.3673
| 1041 | 8728.5892 | 0 | 8728.5892
| 1042 | 7345.8717 | 0 | 7345.8717
| 1043 | 6615.6836 | 0 | 6615.6836
| 1044 | 6158.0374 | 0 | 6158.0374
| 1045 | 5903.2362 | 0 | 5903.2362
| 1046 | 5646.5809 | 0 | 5646.5809
| 1047 | 5598.5324 | 0 | 5598.5324
| 1048 | 5556.971 | 0 | 5556.971
| 1049 | 5713.343 | 0 | 5713.343
| 1050 | 6101.1259 | 0 | 6101.1259
| 1051 | 6239.4378 | 0 | 6239.4378
| 1052 | 6418.8312 | 0 | 6418.8312
| 1053 | 6797.7287 | 0 | 6797.7287
| 1054 | 2158.016 | 0 | 2158.016
| 1055 | 2478.3242 | 0 | 2478.3242
| 1056 | 2966.5476 | 0 | 2966.5476
| 1057 | 3001.2679 | 0 | 3001.2679
| 1058 | 2942.4344 | 0 | 2942.4344
| 1059 | 2963.3672 | 0 | 2963.3672
| 1060 | 2899.9512 | 0 | 2899.9512
| 1061 | 2885.992 | 0 | 2885.992
| 1062 | 2961.1526 | 0 | 2961.1526
| 1063 | 13972.319 | 0 | 13972.319
| 1064 | 11350.7491 | 0 | 11350.7491
| 1065 | 9328.9747 | 0 | 9328.9747
| 1066 | 7582.9789 | 0 | 7582.9789
| 1067 | 6398.2884 | 0 | 6398.2884
| 1068 | 5409.7041 | 0 | 5409.7041
| 1069 | 4896.5451 | 0 | 4896.5451
| 1070 | 4440.4285 | 0 | 4440.4285
| 1071 | 4186.7199 | 0 | 4186.7199
| 1072 | 4110.8723 | 0 | 4110.8723
| 1073 | 4091.2743 | 0 | 4091.2743
| 1074 | 4543.5215 | 0 | 4543.5215
| 1075 | 5094.2994 | 0 | 5094.2994
| 1076 | 6060.2266 | 0 | 6060.2266
| 1077 | 6726.4037 | 0 | 6726.4037
| 1078 | 2021.3851 | 0 | 2021.3851
| 1079 | 1807.3577 | 0 | 1807.3577
| 1080 | 1983.2644 | 0 | 1983.2644
| 1081 | 1952.9301 | 0 | 1952.9301
| 1082 | 1918.0978 | 0 | 1918.0978
| 1083 | 1997.1753 | 0 | 1997.1753
| 1084 | 2055.4505 | 0 | 2055.4505
| 1085 | 2104.8544 | 0 | 2104.8544
| 1086 | 2096.0812 | 0 | 2096.0812
| 1087 | 11734.3261 | 0 | 11734.3261
| 1088 | 8707.7501 | 0 | 8707.7501
| 1089 | 6952.1728 | 0 | 6952.1728
| 1090 | 5384.1607 | 0 | 5384.1607
| 1091 | 4476.9427 | 0 | 4476.9427
| 1092 | 3855.1575 | 0 | 3855.1575
| 1093 | 3590.5243 | 0 | 3590.5243
| 1094 | 3281.2694 | 0 | 3281.2694
| 1095 | 3088.2031 | 0 | 3088.2031
| 1096 | 3015.7196 | 0 | 3015.7196
| 1097 | 2956.4094 | 0 | 2956.4094
| 1098 | 3034.2443 | 0 | 3034.2443
| 1099 | 3107.3402 | 0 | 3107.3402
| 1100 | 3221.5559 | 0 | 3221.5559
| 1101 | 3391.8319 | 0 | 3391.8319
| 1102 | 952.9596 | 0 | 952.9596
| 1103 | 826.2335 | 0 | 826.2335
| 1104 | 886.4532 | 0 | 886.4532
| 1105 | 923.4813 | 0 | 923.4813
| 1106 | 986.996 | 0 | 986.996
| 1107 | 1100.8907 | 0 | 1100.8907
| 1108 | 1214.4476 | 0 | 1214.4476
| 1109 | 1261.3103 | 0 | 1261.3103
| 1110 | 1310.9346 | 0 | 1310.9346
| 1111 | 8611.5007 | 0 | 8611.5007
| 1112 | 6615.8303 | 0 | 6615.8303
| 1113 | 5948.2103 | 0 | 5948.2103
| 1114 | 5083.8997 | 0 | 5083.8997
| 1115 | 4435.7839 | 0 | 4435.7839
| 1116 | 3977.6794 | 0 | 3977.6794
| 1117 | 3807.828 | 0 | 3807.828
| 1118 | 3691.5725 | 0 | 3691.5725
| 1119 | 3595.5151 | 0 | 3595.5151
| 1120 | 3761.5495 | 0 | 3761.5495
| 1121 | 4026.4376 | 0 | 4026.4376
| 1122 | 4482.385 | 0 | 4482.385
| 1123 | 5061.0237 | 0 | 5061.0237
| 1124 | 5744.4134 | 0 | 5744.4134
| 1125 | 6098.5532 | 0 | 6098.5532
| 1126 | 6623.9762 | 0 | 6623.9762
| 1127 | 1968.9996 | 0 | 1968.9996
| 1128 | 2033.7032 | 0 | 2033.7032
| 1129 | 2054.6209 | 0 | 2054.6209
| 1130 | 2125.2793 | 0 | 2125.2793
| 1131 | 2138.0988 | 0 | 2138.0988
| 1132 | 2133.7732 | 0 | 2133.7732
| 1133 | 2273.4319 | 0 | 2273.4319
| 1134 | 2414.2774 | 0 | 2414.2774
| 1135 | 2496.0501 | 0 | 2496.0501
| 1136 | 2483.9371 | 0 | 2483.9371
| 1137 | 11970.2726 | 0 | 11970.2726
| 1138 | 8579.8891 | 0 | 8579.8891
| 1139 | 6988.5379 | 0 | 6988.5379
| 1140 | 6077.1653 | 0 | 6077.1653
| 1141 | 5179.1253 | 0 | 5179.1253
| 1142 | 4738.4492 | 0 | 4738.4492
| 1143 | 4305.4163 | 0 | 4305.4163
| 1144 | 3891.6819 | 0 | 3891.6819
| 1145 | 3690.9839 | 0 | 3690.9839
| 1146 | 5354.1959 | 0 | 5354.1959
| 1147 | 5978.4271 | 0 | 5978.4271
| 1148 | 1336.0828 | 0 | 1336.0828
| 1149 | 1434.2795 | 0 | 1434.2795
| 1150 | 1542.8396 | 0 | 1542.8396
| 1151 | 1672.8476 | 0 | 1672.8476
| 1152 | 1726.8894 | 0 | 1726.8894
| 1153 | 1771.3055 | 0 | 1771.3055
| 1154 | 1791.2743 | 0 | 1791.2743
| 1155 | 1753.8663 | 0 | 1753.8663
| 1156 | 1673.9605 | 0 | 1673.9605
| 1157 | 1647.6912 | 0 | 1647.6912
| 1158 | 1666.3913 | 0 | 1666.3913
| 1159 | 10453.0955 | 0 | 10453.0955
| 1160 | 7903.1132 | 0 | 7903.1132
| 1161 | 6291.5509 | 0 | 6291.5509
| 1162 | 4771.1398 | 0 | 4771.1398
| 1163 | 3934.2018 | 0 | 3934.2018
| 1164 | 3188.6426 | 0 | 3188.6426
| 1165 | 2817.6771 | 5.6124 | 2812.0647
| 1166 | 2433.9141 | 46.1521 | 2387.762
| 1167 | 2168.553 | 69.7866 | 2098.7664
| 1168 | 2084.0127 | 65.4893 | 2018.5234
| 1169 | 2096.9096 | 41.0781 | 2055.8315
| 1170 | 2679.3797 | 9.4339 | 2669.9458
| 1171 | 3227.0475 | 0 | 3227.0475
| 1172 | 3539.6165 | 0 | 3539.6165
| 1173 | 3954.1444 | 0 | 3954.1444
| 1174 | 1169.518 | 0 | 1169.518
| 1175 | 1175.666 | 0 | 1175.666
| 1176 | 1479.5466 | 0 | 1479.5466
| 1177 | 1689.3431 | 0 | 1689.3431
| 1178 | 1908.9672 | 0 | 1908.9672
| 1179 | 2183.6157 | 0 | 2183.6157
| 1180 | 2352.2609 | 0 | 2352.2609
| 1181 | 2429.3487 | 0 | 2429.3487
| 1182 | 2480.9478 | 0 | 2480.9478
| 1183 | 13482.2921 | 0 | 13482.2921
| 1184 | 10798.5624 | 0 | 10798.5624
| 1185 | 8392.3212 | 0 | 8392.3212
| 1186 | 6073.0527 | 0 | 6073.0527
| 1187 | 4597.5246 | 0 | 4597.5246
| 1188 | 3442.6213 | 0 | 3442.6213
| 1189 | 2857.8644 | 0 | 2857.8644
| 1190 | 2629.5435 | 0 | 2629.5435
| 1191 | 2473.1876 | 0 | 2473.1876
| 1192 | 2442.5512 | 0 | 2442.5512
| 1193 | 2626.2182 | 0 | 2626.2182
| 1194 | 2899.3142 | 0 | 2899.3142
| 1195 | 2969.3538 | 0 | 2969.3538
| 1196 | 3151.1357 | 0 | 3151.1357
| 1197 | 3635.4842 | 0 | 3635.4842
| 1198 | 1087.8725 | 0 | 1087.8725
| 1199 | 945.1855 | 0 | 945.1855
| 1200 | 1018.7032 | 0 | 1018.7032
| 1201 | 1099.1653 | 0 | 1099.1653
| 1202 | 1162.6101 | 0 | 1162.6101
| 1203 | 1206.0399 | 0 | 1206.0399
| 1204 | 1202.5388 | 0 | 1202.5388
| 1205 | 1220.7245 | 0 | 1220.7245
| 1206 | 1231.5165 | 0 | 1231.5165
| 1207 | 9179.3131 | 0 | 9179.3131
| 1208 | 6673.5791 | 0 | 6673.5791
| 1209 | 5313.5912 | 0 | 5313.5912
| 1210 | 4154.6543 | 0 | 4154.6543
| 1211 | 3569.2242 | 0 | 3569.2242
| 1212 | 3047.6203 | 0 | 3047.6203
| 1213 | 2784.5241 | 0 | 2784.5241
| 1214 | 2711.5759 | 0 | 2711.5759
| 1215 | 2119.5945 | 0 | 2119.5945
| 1216 | 1827.9639 | 0 | 1827.9639
| 1217 | 2076.3038 | 0 | 2076.3038
| 1218 | 2537.9681 | 0 | 2537.9681
| 1219 | 2825.063 | 0 | 2825.063
| 1220 | 3214.1789 | 0 | 3214.1789
| 1221 | 3580.5116 | 0 | 3580.5116
| 1222 | 994.4378 | 0 | 994.4378
| 1223 | 879.6135 | 0 | 879.6135
| 1224 | 918.5894 | 0 | 918.5894
| 1225 | 1136.7246 | 0 | 1136.7246
| 1226 | 1444.3097 | 0 | 1444.3097
| 1227 | 1731.5404 | 0 | 1731.5404
| 1228 | 1985.7136 | 0 | 1985.7136
| 1229 | 2193.7463 | 0 | 2193.7463
| 1230 | 2422.8841 | 0 | 2422.8841
| 1231 | 12691.6284 | 0 | 12691.6284
| 1232 | 10161.3273 | 0 | 10161.3273
| 1233 | 8865.8553 | 0 | 8865.8553
| 1234 | 7854.5052 | 0 | 7854.5052
| 1235 | 7525.1747 | 0 | 7525.1747
| 1236 | 7153.3402 | 0 | 7153.3402
| 1237 | 6934.8358 | 0 | 6934.8358
| 1238 | 6740.5367 | 0 | 6740.5367
| 1239 | 6659.8676 | 0 | 6659.8676
| 1240 | 6533.7 | 0 | 6533.7
| 1241 | 6640.5447 | 0 | 6640.5447
| 1242 | 7001.499 | 0 | 7001.499
| 1243 | 7211.2033 | 0 | 7211.2033
| 1244 | 7522.3139 | 0 | 7522.3139
| 1245 | 8137.446 | 0 | 8137.446
| 1246 | 2571.7703 | 0 | 2571.7703
| 1247 | 2728.0171 | 0 | 2728.0171
| 1248 | 3041.8659 | 0 | 3041.8659
| 1249 | 3254.8878 | 0 | 3254.8878
| 1250 | 3372.1883 | 0 | 3372.1883
| 1251 | 3515.895 | 0 | 3515.895
| 1252 | 3472.0559 | 0 | 3472.0559
| 1253 | 3436.1709 | 0 | 3436.1709
| 1254 | 3404.8302 | 0 | 3404.8302
| 1255 | 15229.5754 | 0 | 15229.5754
| 1256 | 12269.3903 | 0 | 12269.3903
| 1257 | 9919.6666 | 0 | 9919.6666
| 1258 | 7644.8915 | 0 | 7644.8915
| 1259 | 6319.4864 | 0 | 6319.4864
| 1260 | 5186.9818 | 0 | 5186.9818
| 1261 | 4484.6746 | 0 | 4484.6746
| 1262 | 3918.3425 | 0 | 3918.3425
| 1263 | 3555.1079 | 0 | 3555.1079
| 1264 | 3232.1168 | 0 | 3232.1168
| 1265 | 3070.7132 | 0 | 3070.7132
| 1266 | 3088.1112 | 0 | 3088.1112
| 1267 | 3270.5343 | 0 | 3270.5343
| 1268 | 3360.6627 | 0 | 3360.6627
| 1269 | 3492.3207 | 0 | 3492.3207
| 1270 | 1007.4861 | 0 | 1007.4861
| 1271 | 870.6016 | 0 | 870.6016
| 1272 | 961.9287 | 0 | 961.9287
| 1273 | 1041.1474 | 0 | 1041.1474
| 1274 | 1056.6028 | 0 | 1056.6028
| 1275 | 1067.5955 | 0 | 1067.5955
| 1276 | 1083.4722 | 0 | 1083.4722
| 1277 | 1081.0991 | 0 | 1081.0991
| 1278 | 1081.1066 | 0 | 1081.1066
| 1279 | 7760.7272 | 0 | 7760.7272
| 1280 | 5757.5683 | 0 | 5757.5683
| 1281 | 4793.0431 | 0 | 4793.0431
| 1282 | 3802.4663 | 0 | 3802.4663
| 1283 | 3037.9384 | 0 | 3037.9384
| 1284 | 2845.1472 | 0 | 2845.1472
| 1285 | 2807.1521 | 0 | 2807.1521
| 1286 | 2618.2831 | 0 | 2618.2831
| 1287 | 2485.2366 | 0 | 2485.2366
| 1288 | 2471.5969 | 0 | 2471.5969
| 1289 | 2695.4714 | 0 | 2695.4714
| 1290 | 3009.7288 | 0 | 3009.7288
| 1291 | 3394.1812 | 0 | 3394.1812
| 1292 | 4007.8665 | 0 | 4007.8665
| 1293 | 4551.1893 | 0 | 4551.1893
| 1294 | 5101.4791 | 0 | 5101.4791
| 1295 | 1405.2211 | 0 | 1405.2211
| 1296 | 1549.2666 | 0 | 1549.2666
| 1297 | 1604.6018 | 0 | 1604.6018
| 1298 | 1648.2573 | 0 | 1648.2573
| 1299 | 1839.7136 | 0 | 1839.7136
| 1300 | 1943.9152 | 0 | 1943.9152
| 1301 | 1962.5616 | 0 | 1962.5616
| 1302 | 2027.057 | 0 | 2027.057
| 1303 | 2150.6784 | 0 | 2150.6784
| 1304 | 2128.3578 | 0 | 2128.3578
| 1305 | 10825.3495 | 0 | 10825.3495
| 1306 | 8135.1006 | 0 | 8135.1006
| 1307 | 6902.8331 | 0 | 6902.8331
| 1308 | 6163.7678 | 0 | 6163.7678
| 1309 | 5409.9292 | 0 | 5409.9292
| 1310 | 5055.1029 | 0 | 5055.1029
| 1311 | 4806.5908 | 0 | 4806.5908
| 1312 | 4779.6836 | 0 | 4779.6836
| 1313 | 4847.4341 | 0 | 4847.4341
| 1314 | 6927.614 | 0 | 6927.614
| 1315 | 7670.3738 | 0 | 7670.3738
| 1316 | 1968.0893 | 0 | 1968.0893
| 1317 | 2115.2578 | 0 | 2115.2578
| 1318 | 2209.6317 | 0 | 2209.6317
| 1319 | 2265.0147 | 0 | 2265.0147
| 1320 | 2321.9431 | 0 | 2321.9431
| 1321 | 2440.6079 | 0 | 2440.6079
| 1322 | 2514.4646 | 0 | 2514.4646
| 1323 | 2591.8247 | 0 | 2591.8247
| 1324 | 2760.0025 | 0 | 2760.0025
| 1325 | 2816.0696 | 0 | 2816.0696
| 1326 | 2929.4413 | 0 | 2929.4413
| 1327 | 14310.5189 | 0 | 14310.5189
| 1328 | 11363.4479 | 0 | 11363.4479
| 1329 | 9048.4686 | 0 | 9048.4686
| 1330 | 7125.064 | 0 | 7125.064
| 1331 | 5820.2966 | 0 | 5820.2966
| 1332 | 4942.0488 | 0 | 4942.0488
| 1333 | 4539.9276 | 0 | 4539.9276
| 1334 | 4376.2208 | 0 | 4376.2208
| 1335 | 4164.322 | 0 | 4164.322
| 1336 | 4081.312 | 0 | 4081.312
| 1337 | 4319.1352 | 0 | 4319.1352
| 1338 | 4704.9543 | 0 | 4704.9543
| 1339 | 5074.9937 | 0 | 5074.9937
| 1340 | 5490.5866 | 0 | 5490.5866
| 1341 | 5986.836 | 0 | 5986.836
| 1342 | 1855.4421 | 0 | 1855.4421
| 1343 | 1862.0095 | 0 | 1862.0095
| 1344 | 2275.3215 | 0 | 2275.3215
| 1345 | 2490.8704 | 0 | 2490.8704
| 1346 | 2688.9867 | 0 | 2688.9867
| 1347 | 2876.384 | 0 | 2876.384
| 1348 | 2939.3091 | 0 | 2939.3091
| 1349 | 2887.5495 | 0 | 2887.5495
| 1350 | 2867.5537 | 0 | 2867.5537
| 1351 | 14555.0251 | 0 | 14555.0251
| 1352 | 11946.7614 | 0 | 11946.7614
| 1353 | 9341.1414 | 0 | 9341.1414
| 1354 | 7128.1624 | 0 | 7128.1624
| 1355 | 5733.347 | 0 | 5733.347
| 1356 | 4614.8115 | 0 | 4614.8115
| 1357 | 4213.4078 | 0 | 4213.4078
| 1358 | 4047.2092 | 0 | 4047.2092
| 1359 | 3806.676 | 3.4998 | 3803.1761
| 1360 | 3777.2144 | 1.4395 | 3775.775
| 1361 | 3915.1941 | 0 | 3915.1941
| 1362 | 4305.9615 | 0 | 4305.9615
| 1363 | 4638.8992 | 0 | 4638.8992
| 1364 | 5080.2261 | 0 | 5080.2261
| 1365 | 5364.6554 | 0 | 5364.6554
| 1366 | 1509.4923 | 0 | 1509.4923
| 1367 | 1302.0678 | 0 | 1302.0678
| 1368 | 1505.6261 | 0 | 1505.6261
| 1369 | 1681.6023 | 0 | 1681.6023
| 1370 | 1833.2935 | 0 | 1833.2935
| 1371 | 1916.5602 | 0 | 1916.5602
| 1372 | 2050.5006 | 0 | 2050.5006
| 1373 | 2093.897 | 0 | 2093.897
| 1374 | 2099.9163 | 0 | 2099.9163
| 1375 | 12444.3697 | 0 | 12444.3697
| 1376 | 9658.7919 | 0 | 9658.7919
| 1377 | 7960.0094 | 0 | 7960.0094
| 1378 | 6480.843 | 0 | 6480.843
| 1379 | 5608.7691 | 0 | 5608.7691
| 1380 | 4949.9509 | 0 | 4949.9509
| 1381 | 4677.784 | 0 | 4677.784
| 1382 | 4479.2447 | 0 | 4479.2447
| 1383 | 4222.6655 | 0 | 4222.6655
| 1384 | 4219.0346 | 0 | 4219.0346
| 1385 | 4246.3819 | 0 | 4246.3819
| 1386 | 4459.5902 | 0 | 4459.5902
| 1387 | 4688.3986 | 0 | 4688.3986
| 1388 | 4861.8273 | 0 | 4861.8273
| 1389 | 5221.3503 | 0 | 5221.3503
| 1390 | 1548.0194 | 0 | 1548.0194
| 1391 | 1412.4262 | 0 | 1412.4262
| 1392 | 1690.4162 | 0 | 1690.4162
| 1393 | 1838.0132 | 0 | 1838.0132
| 1394 | 1949.7373 | 0 | 1949.7373
| 1395 | 2120.8585 | 0 | 2120.8585
| 1396 | 2218.4503 | 0 | 2218.4503
| 1397 | 2367.093 | 0 | 2367.093
| 1398 | 2545.8776 | 0 | 2545.8776
| 1399 | 13759.6708 | 0 | 13759.6708
| 1400 | 10464.7557 | 0 | 10464.7557
| 1401 | 8112.4462 | 0 | 8112.4462
| 1402 | 6060.2039 | 0 | 6060.2039
| 1403 | 4924.5667 | 0 | 4924.5667
| 1404 | 4169.0705 | 0 | 4169.0705
| 1405 | 3546.3854 | 8.8784 | 3537.507
| 1406 | 3159.8948 | 53.8481 | 3106.0467
| 1407 | 2925.1039 | 63.2578 | 2861.8461
| 1408 | 2703.4773 | 67.9281 | 2635.5492
| 1409 | 2907.6395 | 41.3467 | 2866.2928
| 1410 | 3363.8136 | 11.8341 | 3351.9796
| 1411 | 3784.8135 | 0 | 3784.8135
| 1412 | 4657.0021 | 0 | 4657.0021
| 1413 | 5436.6105 | 0 | 5436.6105
| 1414 | 1434.9871 | 0 | 1434.9871
| 1415 | 1197.4085 | 0 | 1197.4085
| 1416 | 1232.9262 | 0 | 1232.9262
| 1417 | 1218.7616 | 0 | 1218.7616
| 1418 | 1164.2235 | 0 | 1164.2235
| 1419 | 1087.0862 | 0 | 1087.0862
| 1420 | 994.4072 | 0 | 994.4072
| 1421 | 991.3152 | 0 | 991.3152
| 1422 | 1041.8635 | 0 | 1041.8635
| 1423 | 8542.5347 | 0 | 8542.5347
| 1424 | 6332.8049 | 0 | 6332.8049
| 1425 | 5144.2525 | 0 | 5144.2525
| 1426 | 4065.7887 | 0 | 4065.7887
| 1427 | 3565.1609 | 0 | 3565.1609
| 1428 | 3173.5449 | 0 | 3173.5449
| 1429 | 3013.9594 | 0 | 3013.9594
| 1430 | 2911.9509 | 0 | 2911.9509
| 1431 | 2871.8516 | 0 | 2871.8516
| 1432 | 2848.1652 | 0 | 2848.1652
| 1433 | 3100.7272 | 0 | 3100.7272
| 1434 | 3565.3225 | 0 | 3565.3225
| 1435 | 3979.8635 | 0 | 3979.8635
| 1436 | 4340.5763 | 0 | 4340.5763
| 1437 | 4735.6308 | 0 | 4735.6308
| 1438 | 1456.1364 | 0 | 1456.1364
| 1439 | 1380.9972 | 0 | 1380.9972
| 1440 | 1655.1816 | 0 | 1655.1816
| 1441 | 1842.096 | 0 | 1842.096
| 1442 | 2012.8014 | 0 | 2012.8014
| 1443 | 2197.8051 | 0 | 2197.8051
| 1444 | 2372.3491 | 0 | 2372.3491
| 1445 | 2522.7305 | 0 | 2522.7305
| 1446 | 2649.6643 | 0 | 2649.6643
| 1447 | 12837.5941 | 0 | 12837.5941
| 1448 | 10152.8053 | 0 | 10152.8053
| 1449 | 9093.6217 | 0 | 9093.6217
| 1450 | 8105.0517 | 0 | 8105.0517
| 1451 | 7261.7971 | 0 | 7261.7971
| 1452 | 6708.2401 | 0 | 6708.2401
| 1453 | 6426.7506 | 0 | 6426.7506
| 1454 | 6349.5091 | 0 | 6349.5091
| 1455 | 6351.2717 | 0 | 6351.2717
| 1456 | 6379.4863 | 0 | 6379.4863
| 1457 | 6427.3635 | 0 | 6427.3635
| 1458 | 6614.3537 | 0 | 6614.3537
| 1459 | 7105.0454 | 0 | 7105.0454
| 1460 | 7634.3163 | 0 | 7634.3163
| 1461 | 7847.9462 | 0 | 7847.9462
| 1462 | 8220.3501 | 0 | 8220.3501
| 1463 | 2552.9814 | 0 | 2552.9814
| 1464 | 2646.367 | 0 | 2646.367
| 1465 | 2735.6698 | 0 | 2735.6698
| 1466 | 2802.8043 | 0 | 2802.8043
| 1467 | 2852.4761 | 0 | 2852.4761
| 1468 | 2899.6072 | 0 | 2899.6072
| 1469 | 2883.0535 | 0 | 2883.0535
| 1470 | 2821.0937 | 0 | 2821.0937
| 1471 | 2739.2171 | 0 | 2739.2171
| 1472 | 2602.7148 | 0 | 2602.7148
| 1473 | 12611.257 | 0 | 12611.257
| 1474 | 9629.6974 | 0 | 9629.6974
| 1475 | 8030.6308 | 0 | 8030.6308
| 1476 | 7049.7769 | 0 | 7049.7769
| 1477 | 6087.3066 | 0 | 6087.3066
| 1478 | 5641.2898 | 0 | 5641.2898
| 1479 | 5446.5239 | 0 | 5446.5239
| 1480 | 5382.3863 | 0 | 5382.3863
| 1481 | 5275.4532 | 0 | 5275.4532
| 1482 | 6922.9808 | 0 | 6922.9808
| 1483 | 7164.7488 | 0 | 7164.7488
| 1484 | 1708.2105 | 0 | 1708.2105
| 1485 | 1703.7441 | 0 | 1703.7441
| 1486 | 1700.9185 | 0 | 1700.9185
| 1487 | 1731.2116 | 0 | 1731.2116
| 1488 | 1769.6802 | 0 | 1769.6802
| 1489 | 1798.5511 | 0 | 1798.5511
| 1490 | 1798.0234 | 0 | 1798.0234
| 1491 | 1784.651 | 0 | 1784.651
| 1492 | 1762.9972 | 0 | 1762.9972
| 1493 | 1741.6473 | 0 | 1741.6473
| 1494 | 1714.0937 | 0 | 1714.0937
| 1495 | 10256.8564 | 0 | 10256.8564
| 1496 | 7617.1127 | 0 | 7617.1127
| 1497 | 6062.5069 | 0 | 6062.5069
| 1498 | 4786.5982 | 0 | 4786.5982
| 1499 | 4093.1056 | 0 | 4093.1056
| 1500 | 3546.5748 | 0 | 3546.5748
| 1501 | 3239.3348 | 0 | 3239.3348
| 1502 | 2949.3541 | 0 | 2949.3541
| 1503 | 2743.3319 | 0 | 2743.3319
| 1504 | 2549.1533 | 0 | 2549.1533
| 1505 | 2621.8355 | 0 | 2621.8355
| 1506 | 2906.6193 | 0 | 2906.6193
| 1507 | 3116.9366 | 0 | 3116.9366
| 1508 | 3188.9522 | 0 | 3188.9522
| 1509 | 3177.2013 | 0 | 3177.2013
| 1510 | 879.2517 | 0 | 879.2517
| 1511 | 725.0516 | 0 | 725.0516
| 1512 | 749.7898 | 0 | 749.7898
| 1513 | 783.7238 | 0 | 783.7238
| 1514 | 815.0487 | 0 | 815.0487
| 1515 | 839.2634 | 0 | 839.2634
| 1516 | 856.0134 | 0 | 856.0134
| 1517 | 871.8687 | 0 | 871.8687
| 1518 | 876.6518 | 0 | 876.6518
| 1519 | 7350.631 | 0 | 7350.631
| 1520 | 5196.2801 | 0 | 5196.2801
| 1521 | 3912.494 | 0 | 3912.494
| 1522 | 2733.4278 | 0 | 2733.4278
| 1523 | 1728.358 | 0 | 1728.358
| 1524 | 689.7337 | 5.1139 | 684.6198
| 1525 | 209.3615 | 45.3058 | 164.0557
| 1526 | 121.9252 | 146.9366 | -25.0114
| 1527 | 95.2526 | 205.5003 | -110.2476
| 1528 | 79.5381 | 188.8867 | -109.3486
| 1529 | 91.1188 | 155.4189 | -64.3001
| 1530 | 125.856 | 80.6044 | 45.2516
| 1531 | 160.7808 | 21.6975 | 139.0833
| 1532 | 494.5562 | 6.8545 | 487.7017
| 1533 | 1027.0262 | 0 | 1027.0262
| 1534 | 362.4685 | 0 | 362.4685
| 1535 | 452.6636 | 0 | 452.6636
| 1536 | 569.534 | 0 | 569.534
| 1537 | 688.2002 | 0 | 688.2002
| 1538 | 758.4743 | 0 | 758.4743
| 1539 | 799.2264 | 0 | 799.2264
| 1540 | 861.5093 | 0 | 861.5093
| 1541 | 957.2026 | 0 | 957.2026
| 1542 | 1063.4177 | 0 | 1063.4177
| 1543 | 8448.0378 | 0 | 8448.0378
| 1544 | 6280.8524 | 0 | 6280.8524
| 1545 | 5064.7453 | 0 | 5064.7453
| 1546 | 3932.2009 | 0 | 3932.2009
| 1547 | 3351.564 | 0 | 3351.564
| 1548 | 2813.9428 | 0 | 2813.9428
| 1549 | 2548.5639 | 0 | 2548.5639
| 1550 | 2480.3424 | 0 | 2480.3424
| 1551 | 2549.109 | 0 | 2549.109
| 1552 | 2622.5357 | 0 | 2622.5357
| 1553 | 2927.2529 | 0 | 2927.2529
| 1554 | 3389.012 | 0 | 3389.012
| 1555 | 3805.5259 | 0 | 3805.5259
| 1556 | 4224.2392 | 0 | 4224.2392
| 1557 | 4705.0415 | 0 | 4705.0415
| 1558 | 1396.7092 | 0 | 1396.7092
| 1559 | 1231.0063 | 0 | 1231.0063
| 1560 | 1412.4103 | 0 | 1412.4103
| 1561 | 1552.9311 | 0 | 1552.9311
| 1562 | 1631.8581 | 0 | 1631.8581
| 1563 | 1678.5054 | 0 | 1678.5054
| 1564 | 1705.4765 | 0 | 1705.4765
| 1565 | 1758.0375 | 0 | 1758.0375
| 1566 | 1816.8235 | 0 | 1816.8235
| 1567 | 11319.4631 | 0 | 11319.4631
| 1568 | 8271.4156 | 0 | 8271.4156
| 1569 | 6349.7673 | 0 | 6349.7673
| 1570 | 4583.6561 | 0 | 4583.6561
| 1571 | 3799.7239 | 0 | 3799.7239
| 1572 | 3279.3856 | 0 | 3279.3856
| 1573 | 3006.6523 | 0 | 3006.6523
| 1574 | 2884.4456 | 0 | 2884.4456
| 1575 | 2881.6896 | 0 | 2881.6896
| 1576 | 2938.7362 | 0 | 2938.7362
| 1577 | 3239.5852 | 0 | 3239.5852
| 1578 | 3721.9968 | 0 | 3721.9968
| 1579 | 4172.7589 | 0 | 4172.7589
| 1580 | 4546.1697 | 0 | 4546.1697
| 1581 | 4936.5592 | 0 | 4936.5592
| 1582 | 1468.8562 | 0 | 1468.8562
| 1583 | 1318.0155 | 0 | 1318.0155
| 1584 | 1529.8976 | 0 | 1529.8976
| 1585 | 1682.8945 | 0 | 1682.8945
| 1586 | 1846.9369 | 0 | 1846.9369
| 1587 | 2023.7721 | 0 | 2023.7721
| 1588 | 2194.0856 | 0 | 2194.0856
| 1589 | 2294.0434 | 0 | 2294.0434
| 1590 | 2331.6064 | 0 | 2331.6064
| 1591 | 12572.8095 | 0 | 12572.8095
| 1592 | 9506.0336 | 0 | 9506.0336
| 1593 | 7654.0034 | 0 | 7654.0034
| 1594 | 6045.0674 | 0 | 6045.0674
| 1595 | 5191.1593 | 0 | 5191.1593
| 1596 | 4604.5645 | 0 | 4604.5645
| 1597 | 4319.7963 | 0 | 4319.7963
| 1598 | 4113.0854 | 0 | 4113.0854
| 1599 | 3987.2502 | 0 | 3987.2502
| 1600 | 3925.6278 | 0 | 3925.6278
| 1601 | 4176.2555 | 0 | 4176.2555
| 1602 | 4668.3074 | 0 | 4668.3074
| 1603 | 5112.6018 | 0 | 5112.6018
| 1604 | 5559.3759 | 0 | 5559.3759
| 1605 | 6146.2162 | 0 | 6146.2162
| 1606 | 1900.8041 | 0 | 1900.8041
| 1607 | 1905.8986 | 0 | 1905.8986
| 1608 | 2270.494 | 0 | 2270.494
| 1609 | 2528.7876 | 0 | 2528.7876
| 1610 | 2659.2942 | 0 | 2659.2942
| 1611 | 2720.7158 | 0 | 2720.7158
| 1612 | 2765.1195 | 0 | 2765.1195
| 1613 | 2791.0694 | 0 | 2791.0694
| 1614 | 2801.8688 | 0 | 2801.8688
| 1615 | 13455.5081 | 0 | 13455.5081
| 1616 | 10669.986 | 0 | 10669.986
| 1617 | 8800.028 | 0 | 8800.028
| 1618 | 7146.011 | 0 | 7146.011
| 1619 | 5853.3318 | 0 | 5853.3318
| 1620 | 4903.8253 | 0 | 4903.8253
| 1621 | 4253.802 | 0 | 4253.802
| 1622 | 4006.1407 | 0 | 4006.1407
| 1623 | 4016.0215 | 0 | 4016.0215
| 1624 | 4022.4277 | 0 | 4022.4277
| 1625 | 4198.8898 | 0 | 4198.8898
| 1626 | 4607.1163 | 0 | 4607.1163
| 1627 | 5189.6839 | 0 | 5189.6839
| 1628 | 5878.0526 | 0 | 5878.0526
| 1629 | 6235.8393 | 0 | 6235.8393
| 1630 | 6779.3416 | 0 | 6779.3416
| 1631 | 2029.9433 | 0 | 2029.9433
| 1632 | 2058.642 | 0 | 2058.642
| 1633 | 2076.1962 | 0 | 2076.1962
| 1634 | 2167.2783 | 0 | 2167.2783
| 1635 | 2302.3365 | 0 | 2302.3365
| 1636 | 2444.4043 | 0 | 2444.4043
| 1637 | 2494.695 | 0 | 2494.695
| 1638 | 2472.2927 | 0 | 2472.2927
| 1639 | 2416.9847 | 0 | 2416.9847
| 1640 | 2172.1889 | 0 | 2172.1889
| 1641 | 10986.5189 | 0 | 10986.5189
| 1642 | 7372.8595 | 0 | 7372.8595
| 1643 | 5455.2876 | 0 | 5455.2876
| 1644 | 4338.1103 | 0 | 4338.1103
| 1645 | 3292.8026 | 0 | 3292.8026
| 1646 | 2952.856 | 0 | 2952.856
| 1647 | 2916.1847 | 0 | 2916.1847
| 1648 | 2956.7034 | 0 | 2956.7034
| 1649 | 3148.6695 | 0 | 3148.6695
| 1650 | 4872.5563 | 0 | 4872.5563
| 1651 | 5545.3553 | 0 | 5545.3553
| 1652 | 1308.9625 | 0 | 1308.9625
| 1653 | 1373.4526 | 0 | 1373.4526
| 1654 | 1433.6085 | 0 | 1433.6085
| 1655 | 1505.9816 | 0 | 1505.9816
| 1656 | 1568.838 | 0 | 1568.838
| 1657 | 1621.3719 | 0 | 1621.3719
| 1658 | 1659.2216 | 0 | 1659.2216
| 1659 | 1683.4981 | 0 | 1683.4981
| 1660 | 1704.1676 | 0 | 1704.1676
| 1661 | 1710.6618 | 0 | 1710.6618
| 1662 | 1694.6478 | 0 | 1694.6478
| 1663 | 10255.5179 | 0 | 10255.5179
| 1664 | 7665.1953 | 0 | 7665.1953
| 1665 | 6156.309 | 0 | 6156.309
| 1666 | 4750.078 | 0 | 4750.078
| 1667 | 4025.6283 | 0 | 4025.6283
| 1668 | 3395.4222 | 0 | 3395.4222
| 1669 | 3019.4781 | 0 | 3019.4781
| 1670 | 2809.2455 | 0 | 2809.2455
| 1671 | 2710.3889 | 0 | 2710.3889
| 1672 | 2707.8915 | 0 | 2707.8915
| 1673 | 3017.5191 | 0 | 3017.5191
| 1674 | 3532.1644 | 0 | 3532.1644
| 1675 | 3990.7333 | 0 | 3990.7333
| 1676 | 4511.9623 | 0 | 4511.9623
| 1677 | 5025.0409 | 0 | 5025.0409
| 1678 | 1543.1895 | 0 | 1543.1895
| 1679 | 1509.4055 | 0 | 1509.4055
| 1680 | 1868.3866 | 0 | 1868.3866
| 1681 | 2120.3079 | 0 | 2120.3079
| 1682 | 2288.0072 | 0 | 2288.0072
| 1683 | 2418.6477 | 0 | 2418.6477
| 1684 | 2527.5915 | 0 | 2527.5915
| 1685 | 2586.4676 | 0 | 2586.4676
| 1686 | 2606.9039 | 0 | 2606.9039
| 1687 | 13310.8284 | 0 | 13310.8284
| 1688 | 10487.3595 | 0 | 10487.3595
| 1689 | 8194.0143 | 0 | 8194.0143
| 1690 | 6228.6301 | 0 | 6228.6301
| 1691 | 4997.1853 | 0 | 4997.1853
| 1692 | 4076.2805 | 0 | 4076.2805
| 1693 | 3499.7891 | 0 | 3499.7891
| 1694 | 3226.7501 | 0 | 3226.7501
| 1695 | 3177.8718 | 0 | 3177.8718
| 1696 | 3135.6466 | 0 | 3135.6466
| 1697 | 3320.4706 | 0 | 3320.4706
| 1698 | 3645.5417 | 0 | 3645.5417
| 1699 | 3916.2856 | 0 | 3916.2856
| 1700 | 4262.1484 | 0 | 4262.1484
| 1701 | 4693.0344 | 0 | 4693.0344
| 1702 | 1463.4964 | 0 | 1463.4964
| 1703 | 1353.215 | 0 | 1353.215
| 1704 | 1497.8487 | 0 | 1497.8487
| 1705 | 1538.5218 | 0 | 1538.5218
| 1706 | 1538.9507 | 0 | 1538.9507
| 1707 | 1513.674 | 0 | 1513.674
| 1708 | 1476.4952 | 0 | 1476.4952
| 1709 | 1410.471 | 0 | 1410.471
| 1710 | 1305.5724 | 0 | 1305.5724
| 1711 | 8930.1937 | 0 | 8930.1937
| 1712 | 6148.2195 | 0 | 6148.2195
| 1713 | 4314.9067 | 0 | 4314.9067
| 1714 | 2653.1095 | 0 | 2653.1095
| 1715 | 1996.2869 | 0 | 1996.2869
| 1716 | 1684.5185 | 0 | 1684.5185
| 1717 | 1626.2558 | 0 | 1626.2558
| 1718 | 1739.8214 | 0 | 1739.8214
| 1719 | 1984.8678 | 0 | 1984.8678
| 1720 | 2199.7079 | 0 | 2199.7079
| 1721 | 2495.3756 | 0 | 2495.3756
| 1722 | 2862.15 | 0 | 2862.15
| 1723 | 3179.392 | 0 | 3179.392
| 1724 | 3571.3937 | 0 | 3571.3937
| 1725 | 4073.1385 | 0 | 4073.1385
| 1726 | 1272.8703 | 0 | 1272.8703
| 1727 | 1160.9718 | 0 | 1160.9718
| 1728 | 1372.3088 | 0 | 1372.3088
| 1729 | 1512.5299 | 0 | 1512.5299
| 1730 | 1624.3292 | 0 | 1624.3292
| 1731 | 1725.5173 | 0 | 1725.5173
| 1732 | 1815.5532 | 0 | 1815.5532
| 1733 | 1893.5246 | 0 | 1893.5246
| 1734 | 1953.7608 | 0 | 1953.7608
| 1735 | 11170.6408 | 0 | 11170.6408
| 1736 | 8377.731 | 0 | 8377.731
| 1737 | 6585.991 | 0 | 6585.991
| 1738 | 5006.727 | 0 | 5006.727
| 1739 | 4112.214 | 0 | 4112.214
| 1740 | 3399.1767 | 0 | 3399.1767
| 1741 | 2958.3137 | 0 | 2958.3137
| 1742 | 2532.6404 | 8.067 | 2524.5734
| 1743 | 2163.4784 | 20.9095 | 2142.5689
| 1744 | 1859.2299 | 26.1367 | 1833.0932
| 1745 | 2047.2957 | 17.1768 | 2030.1189
| 1746 | 2520.1902 | 0.59613 | 2519.594
| 1747 | 3002.872 | 0 | 3002.872
| 1748 | 3593.9127 | 0 | 3593.9127
| 1749 | 4223.9934 | 0 | 4223.9934
| 1750 | 1271.5641 | 0 | 1271.5641
| 1751 | 1148.8221 | 0 | 1148.8221
| 1752 | 1268.9567 | 0 | 1268.9567
| 1753 | 1369.1143 | 0 | 1369.1143
| 1754 | 1344.4219 | 0 | 1344.4219
| 1755 | 1234.4968 | 0 | 1234.4968
| 1756 | 1105.6315 | 0 | 1105.6315
| 1757 | 1088.2003 | 0 | 1088.2003
| 1758 | 1134.2375 | 0 | 1134.2375
| 1759 | 8812.5788 | 0 | 8812.5788
| 1760 | 6429.3568 | 0 | 6429.3568
| 1761 | 5134.8616 | 0 | 5134.8616
| 1762 | 4005.2907 | 0 | 4005.2907
| 1763 | 3381.4941 | 0 | 3381.4941
| 1764 | 2794.708 | 0 | 2794.708
| 1765 | 2375.9951 | 0 | 2375.9951
| 1766 | 2201.3558 | 0 | 2201.3558
| 1767 | 2167.2553 | 1.0925 | 2166.1628
| 1768 | 2181.389 | 0.23588 | 2181.1531
| 1769 | 2487.4644 | 0 | 2487.4644
| 1770 | 2960.1412 | 0 | 2960.1412
| 1771 | 3401.3655 | 0 | 3401.3655
| 1772 | 3837.1536 | 0 | 3837.1536
| 1773 | 4280.2708 | 0 | 4280.2708
| 1774 | 1264.2323 | 0 | 1264.2323
| 1775 | 1145.2042 | 0 | 1145.2042
| 1776 | 1324.6125 | 0 | 1324.6125
| 1777 | 1491.8501 | 0 | 1491.8501
| 1778 | 1624.2064 | 0 | 1624.2064
| 1779 | 1740.3865 | 0 | 1740.3865
| 1780 | 1839.4202 | 0 | 1839.4202
| 1781 | 1961.9909 | 0 | 1961.9909
| 1782 | 2103.0215 | 0 | 2103.0215
| 1783 | 11826.736 | 0 | 11826.736
| 1784 | 9326.4489 | 0 | 9326.4489
| 1785 | 8373.8655 | 0 | 8373.8655
| 1786 | 7443.2074 | 0 | 7443.2074
| 1787 | 6548.1073 | 0 | 6548.1073
| 1788 | 5882.8376 | 0 | 5882.8376
| 1789 | 5489.2642 | 0 | 5489.2642
| 1790 | 5337.7555 | 0 | 5337.7555
| 1791 | 5313.0708 | 0 | 5313.0708
| 1792 | 5278.6935 | 0 | 5278.6935
| 1793 | 5255.0922 | 0 | 5255.0922
| 1794 | 5363.1493 | 0 | 5363.1493
| 1795 | 5695.5112 | 0 | 5695.5112
| 1796 | 6364.2972 | 0 | 6364.2972
| 1797 | 6865.5497 | 0 | 6865.5497
| 1798 | 7559.2886 | 0 | 7559.2886
| 1799 | 2414.5219 | 0 | 2414.5219
| 1800 | 2436.5978 | 0 | 2436.5978
| 1801 | 2450.42 | 0 | 2450.42
| 1802 | 2573.0352 | 0 | 2573.0352
| 1803 | 2781.0418 | 0 | 2781.0418
| 1804 | 2994.8087 | 0 | 2994.8087
| 1805 | 3128.5724 | 0 | 3128.5724
| 1806 | 3197.9115 | 0 | 3197.9115
| 1807 | 3223.3236 | 0 | 3223.3236
| 1808 | 3083.007 | 0 | 3083.007
| 1809 | 12889.3763 | 0 | 12889.3763
| 1810 | 10020.8009 | 0 | 10020.8009
| 1811 | 8411.896 | 0 | 8411.896
| 1812 | 7564.1218 | 0 | 7564.1218
| 1813 | 6667.2578 | 0 | 6667.2578
| 1814 | 6502.4893 | 0 | 6502.4893
| 1815 | 6574.1434 | 0 | 6574.1434
| 1816 | 6716.5548 | 0 | 6716.5548
| 1817 | 6958.2129 | 0 | 6958.2129
| 1818 | 9398.219 | 0 | 9398.219
| 1819 | 10100.5168 | 0 | 10100.5168
| 1820 | 2866.6603 | 0 | 2866.6603
| 1821 | 2941.6368 | 0 | 2941.6368
| 1822 | 3016.3301 | 0 | 3016.3301
| 1823 | 3108.8591 | 0 | 3108.8591
| 1824 | 3197.374 | 0 | 3197.374
| 1825 | 3265.8478 | 0 | 3265.8478
| 1826 | 3326.124 | 0 | 3326.124
| 1827 | 3371.0002 | 0 | 3371.0002
| 1828 | 3411.2226 | 0 | 3411.2226
| 1829 | 3478.9464 | 0 | 3478.9464
| 1830 | 3541.0681 | 0 | 3541.0681
| 1831 | 15635.3609 | 0 | 15635.3609
| 1832 | 12827.5198 | 0 | 12827.5198
| 1833 | 10485.0064 | 0 | 10485.0064
| 1834 | 8330.4833 | 0 | 8330.4833
| 1835 | 6951.5607 | 0 | 6951.5607
| 1836 | 5676.7596 | 0 | 5676.7596
| 1837 | 4776.6171 | 0 | 4776.6171
| 1838 | 4170.8656 | 0 | 4170.8656
| 1839 | 3809.452 | 0 | 3809.452
| 1840 | 3502.1901 | 0 | 3502.1901
| 1841 | 3706.9072 | 0 | 3706.9072
| 1842 | 4235.6799 | 0 | 4235.6799
| 1843 | 4733.4501 | 0 | 4733.4501
| 1844 | 5326.428 | 0 | 5326.428
| 1845 | 5957.1017 | 0 | 5957.1017
| 1846 | 1865.4476 | 0 | 1865.4476
| 1847 | 1591.1031 | 0 | 1591.1031
| 1848 | 1700.1914 | 0 | 1700.1914
| 1849 | 1683.5074 | 0 | 1683.5074
| 1850 | 1688.4498 | 0 | 1688.4498
| 1851 | 1706.2443 | 0 | 1706.2443
| 1852 | 1706.8629 | 0 | 1706.8629
| 1853 | 1663.9561 | 0 | 1663.9561
| 1854 | 1571.912 | 0 | 1571.912
| 1855 | 9863.4101 | 0 | 9863.4101
| 1856 | 7163.2664 | 0 | 7163.2664
| 1857 | 5583.8354 | 0 | 5583.8354
| 1858 | 4274.6696 | 0 | 4274.6696
| 1859 | 3316.2791 | 0 | 3316.2791
| 1860 | 2347.7467 | 0 | 2347.7467
| 1861 | 1652.5319 | 0 | 1652.5319
| 1862 | 1129.644 | 0 | 1129.644
| 1863 | 700.8483 | 10.6389 | 690.2095
| 1864 | 346.8341 | 29.2017 | 317.6324
| 1865 | 319.629 | 39.1063 | 280.5228
| 1866 | 585.4385 | 11.75 | 573.6884
| 1867 | 1007.1585 | 0 | 1007.1585
| 1868 | 1518.4034 | 0 | 1518.4034
| 1869 | 2030.8369 | 0 | 2030.8369
| 1870 | 577.9616 | 0 | 577.9616
| 1871 | 636.1837 | 0 | 636.1837
| 1872 | 695.7375 | 0 | 695.7375
| 1873 | 755.5632 | 0 | 755.5632
| 1874 | 811.3782 | 0 | 811.3782
| 1875 | 865.0367 | 0 | 865.0367
| 1876 | 922.7256 | 0 | 922.7256
| 1877 | 964.5681 | 0 | 964.5681
| 1878 | 975.0142 | 0 | 975.0142
| 1879 | 8302.0242 | 0 | 8302.0242
| 1880 | 5348.9755 | 0 | 5348.9755
| 1881 | 3055.5768 | 0 | 3055.5768
| 1882 | 1021.933 | 3.3237 | 1018.6093
| 1883 | 152.5602 | 60.3676 | 92.1926
| 1884 | 59.0109 | 200.3819 | -141.371
| 1885 | 15.9659 | 1019.0188 | -1003.0529
| 1886 | 1.7452 | 2213.2302 | -2211.4851
| 1887 | 0.004391 | 3052.3069 | -3052.3025
| 1888 | 0 | 3478.3561 | -3478.3561
| 1889 | 0 | 3198.1214 | -3198.1214
| 1890 | 0 | 2156.6352 | -2156.6352
| 1891 | 0 | 685.8365 | -685.8365
| 1892 | 0.13917 | 202.1137 | -201.9745
| 1893 | 3.6747 | 109.5803 | -105.9057
| 1894 | 12.2491 | 72.2074 | -59.9583
| 1895 | 25.6731 | 0 | 25.6731
| 1896 | 40.6803 | 0 | 40.6803
| 1897 | 54.6468 | 0 | 54.6468
| 1898 | 70.486 | 0 | 70.486
| 1899 | 92.8493 | 0 | 92.8493
| 1900 | 115.9792 | 0 | 115.9792
| 1901 | 128.6022 | 0 | 128.6022
| 1902 | 129.0721 | 0 | 129.0721
| 1903 | 1930.3351 | 81.1224 | 1849.2127
| 1904 | 1390.0364 | 0 | 1390.0364
| 1905 | 763.4996 | 65.6838 | 697.8158
| 1906 | 77.6824 | 173.0086 | -95.3263
| 1907 | 46.9755 | 342.1707 | -295.1952
| 1908 | 34.675 | 504.1927 | -469.5177
| 1909 | 28.5435 | 602.3941 | -573.8506
| 1910 | 70.8937 | 670.0563 | -599.1626
| 1911 | 177.5831 | 549.3504 | -371.7673
| 1912 | 444.4767 | 223.5847 | 220.892
| 1913 | 753.265 | 154.6033 | 598.6617
| 1914 | 967.7536 | 68.1057 | 899.6479
| 1915 | 1279.9614 | 1.455 | 1278.5064
| 1916 | 1674.316 | 0 | 1674.316
| 1917 | 2145.3706 | 0 | 2145.3706
| 1918 | 531.2143 | 0 | 531.2143
| 1919 | 638.3324 | 0 | 638.3324
| 1920 | 758.9907 | 0 | 758.9907
| 1921 | 899.1042 | 0 | 899.1042
| 1922 | 1124.6804 | 0 | 1124.6804
| 1923 | 1393.5522 | 0 | 1393.5522
| 1924 | 1690.9588 | 0 | 1690.9588
| 1925 | 1924.6473 | 0 | 1924.6473
| 1926 | 2081.4172 | 0 | 2081.4172
| 1927 | 11837.8775 | 0 | 11837.8775
| 1928 | 9056.0736 | 0 | 9056.0736
| 1929 | 7357.6458 | 0 | 7357.6458
| 1930 | 5860.6305 | 0 | 5860.6305
| 1931 | 5010.974 | 0 | 5010.974
| 1932 | 4314.6037 | 0 | 4314.6037
| 1933 | 3907.5184 | 0 | 3907.5184
| 1934 | 3644.9543 | 0 | 3644.9543
| 1935 | 3501.0828 | 0 | 3501.0828
| 1936 | 3396.9855 | 0 | 3396.9855
| 1937 | 3651.7174 | 0 | 3651.7174
| 1938 | 4138.322 | 0 | 4138.322
| 1939 | 4649.442 | 0 | 4649.442
| 1940 | 5175.9076 | 0 | 5175.9076
| 1941 | 5699.4597 | 0 | 5699.4597
| 1942 | 1701.737 | 0 | 1701.737
| 1943 | 1563.301 | 0 | 1563.301
| 1944 | 1861.1417 | 0 | 1861.1417
| 1945 | 2054.2154 | 0 | 2054.2154
| 1946 | 2224.323 | 0 | 2224.323
| 1947 | 2351.2364 | 0 | 2351.2364
| 1948 | 2459.7648 | 0 | 2459.7648
| 1949 | 2522.8621 | 0 | 2522.8621
| 1950 | 2536.9053 | 0 | 2536.9053
| 1951 | 12718.4435 | 0 | 12718.4435
| 1952 | 9737.4897 | 0 | 9737.4897
| 1953 | 7697.4879 | 0 | 7697.4879
| 1954 | 5651.9277 | 0 | 5651.9277
| 1955 | 3941.108 | 0 | 3941.108
| 1956 | 2679.0783 | 0 | 2679.0783
| 1957 | 1819.1388 | 0 | 1819.1388
| 1958 | 1236.8749 | 0.02258 | 1236.8524
| 1959 | 836.9127 | 0 | 836.9127
| 1960 | 518.3046 | 0 | 518.3046
| 1961 | 616.0652 | 0 | 616.0652
| 1962 | 1152.2135 | 0 | 1152.2135
| 1963 | 2082.6734 | 0 | 2082.6734
| 1964 | 2879.5149 | 0 | 2879.5149
| 1965 | 3535.4371 | 0 | 3535.4371
| 1966 | 4449.9947 | 0 | 4449.9947
| 1967 | 1054.8794 | 0 | 1054.8794
| 1968 | 1088.1094 | 0 | 1088.1094
| 1969 | 1102.6968 | 0 | 1102.6968
| 1970 | 1132.1102 | 0 | 1132.1102
| 1971 | 1177.5751 | 0 | 1177.5751
| 1972 | 1218.5243 | 0 | 1218.5243
| 1973 | 1236.064 | 0 | 1236.064
| 1974 | 1234.6546 | 0 | 1234.6546
| 1975 | 1174.0065 | 0 | 1174.0065
| 1976 | 971.7511 | 0 | 971.7511
| 1977 | 6345.6013 | 0 | 6345.6013
| 1978 | 3702.3879 | 0 | 3702.3879
| 1979 | 2169.2604 | 0 | 2169.2604
| 1980 | 1149.2731 | 0 | 1149.2731
| 1981 | 181.124 | 0 | 181.124
| 1982 | 50.7459 | 0 | 50.7459
| 1983 | 24.763 | 0 | 24.763
| 1984 | 8.0268 | 0 | 8.0268
| 1985 | 6.2711 | 0 | 6.2711
| 1986 | 12.3567 | 0 | 12.3567
| 1987 | 488.782 | 0 | 488.782
| 1988 | 66.9915 | 0 | 66.9915
| 1989 | 125.073 | 0 | 125.073
| 1990 | 194.782 | 0 | 194.782
| 1991 | 279.6767 | 0 | 279.6767
| 1992 | 357.5831 | 0 | 357.5831
| 1993 | 433.237 | 0 | 433.237
| 1994 | 486.532 | 0 | 486.532
| 1995 | 529.3181 | 0 | 529.3181
| 1996 | 578.4552 | 0 | 578.4552
| 1997 | 604.1378 | 0 | 604.1378
| 1998 | 600.5792 | 0 | 600.5792
| 1999 | 6221.1354 | 0 | 6221.1354
| 2000 | 4156.4148 | 0 | 4156.4148
| 2001 | 2855.499 | 0 | 2855.499
| 2002 | 1672.8285 | 0 | 1672.8285
| 2003 | 976.161 | 0 | 976.161
| 2004 | 354.4948 | 0 | 354.4948
| 2005 | 177.8443 | 0 | 177.8443
| 2006 | 150.1637 | 18.5248 | 131.6389
| 2007 | 170.8011 | 40.2047 | 130.5965
| 2008 | 197.8224 | 48.4432 | 149.3792
| 2009 | 208.333 | 60.0689 | 148.264
| 2010 | 220.2331 | 26.5346 | 193.6985
| 2011 | 325.6904 | 0.29953 | 325.3909
| 2012 | 881.611 | 0 | 881.611
| 2013 | 1516.7623 | 0 | 1516.7623
| 2014 | 467.1884 | 0 | 467.1884
| 2015 | 542.3986 | 0 | 542.3986
| 2016 | 595.0999 | 0 | 595.0999
| 2017 | 642.4565 | 0 | 642.4565
| 2018 | 671.667 | 0 | 671.667
| 2019 | 692.6904 | 0 | 692.6904
| 2020 | 711.3459 | 0 | 711.3459
| 2021 | 739.3534 | 0 | 739.3534
| 2022 | 778.9394 | 0 | 778.9394
| 2023 | 7418.521 | 0 | 7418.521
| 2024 | 5003.3421 | 0 | 5003.3421
| 2025 | 3313.0602 | 0 | 3313.0602
| 2026 | 1720.9188 | 5.3597 | 1715.5592
| 2027 | 921.6753 | 22.9343 | 898.741
| 2028 | 323.7464 | 98.9258 | 224.8206
| 2029 | 157.253 | 241.3748 | -84.1218
| 2030 | 106.1782 | 416.6799 | -310.5017
| 2031 | 70.6516 | 568.5861 | -497.9345
| 2032 | 40.0968 | 658.2533 | -618.1565
| 2033 | 40.0399 | 492.4459 | -452.406
| 2034 | 77.1121 | 289.8294 | -212.7173
| 2035 | 131.8118 | 122.3659 | 9.4459
| 2036 | 607.8547 | 73.3329 | 534.5218
| 2037 | 1414.128 | 15.495 | 1398.633
| 2038 | 432.0914 | 0.23293 | 431.8585
| 2039 | 476.7601 | 0 | 476.7601
| 2040 | 458.0697 | 0 | 458.0697
| 2041 | 422.6858 | 0 | 422.6858
| 2042 | 416.2665 | 0 | 416.2665
| 2043 | 442.1682 | 0 | 442.1682
| 2044 | 469.2893 | 0 | 469.2893
| 2045 | 473.7345 | 0 | 473.7345
| 2046 | 453.6193 | 0 | 453.6193
| 2047 | 4763.743 | 34.2358 | 4729.5072
| 2048 | 2818.8051 | 0 | 2818.8051
| 2049 | 1681.0982 | 0 | 1681.0982
| 2050 | 461.3745 | 20.2169 | 441.1576
| 2051 | 115.1371 | 87.7713 | 27.3659
| 2052 | 49.2519 | 270.571 | -221.3191
| 2053 | 14.2531 | 585.2788 | -571.0257
| 2054 | 3.9306 | 1410.3212 | -1406.3906
| 2055 | 0.66351 | 2003.5023 | -2002.8388
| 2056 | 0 | 2334.6578 | -2334.6578
| 2057 | 0 | 1989.5473 | -1989.5473
| 2058 | 1.3255 | 912.3345 | -911.0091
| 2059 | 7.943 | 218.6124 | -210.6694
| 2060 | 24.365 | 174.57 | -150.205
| 2061 | 46.1316 | 85.8524 | -39.7208
| 2062 | 68.2557 | 54.1429 | 14.1128
| 2063 | 112.6651 | 0 | 112.6651
| 2064 | 153.9325 | 0 | 153.9325
| 2065 | 198.572 | 0 | 198.572
| 2066 | 261.9549 | 0 | 261.9549
| 2067 | 343.3945 | 0 | 343.3945
| 2068 | 428.3387 | 0 | 428.3387
| 2069 | 489.7777 | 0 | 489.7777
| 2070 | 523.0506 | 0 | 523.0506
| 2071 | 5573.2778 | 0 | 5573.2778
| 2072 | 4178.6668 | 0 | 4178.6668
| 2073 | 3643.3434 | 0 | 3643.3434
| 2074 | 3076.2037 | 0 | 3076.2037
| 2075 | 2742.7811 | 0 | 2742.7811
| 2076 | 2282.5017 | 0 | 2282.5017
| 2077 | 1950.2572 | 0 | 1950.2572
| 2078 | 1822.9352 | 7.4727 | 1815.4626
| 2079 | 1828.8683 | 7.4856 | 1821.3827
| 2080 | 1902.4817 | 5.5372 | 1896.9444
| 2081 | 2070.364 | 15.5476 | 2054.8164
| 2082 | 2346.5813 | 9.8031 | 2336.7782
| 2083 | 2655.956 | 0 | 2655.956
| 2084 | 2898.9915 | 0 | 2898.9915
| 2085 | 3113.4099 | 0 | 3113.4099
| 2086 | 778.6228 | 0 | 778.6228
| 2087 | 776.6101 | 0 | 776.6101
| 2088 | 843.596 | 0 | 843.596
| 2089 | 918.4051 | 0 | 918.4051
| 2090 | 1009.9811 | 0 | 1009.9811
| 2091 | 1129.6362 | 0 | 1129.6362
| 2092 | 1265.3401 | 0 | 1265.3401
| 2093 | 1345.1579 | 0 | 1345.1579
| 2094 | 1355.1532 | 0 | 1355.1532
| 2095 | 9718.3175 | 0 | 9718.3175
| 2096 | 6994.2046 | 0 | 6994.2046
| 2097 | 5285.9339 | 0 | 5285.9339
| 2098 | 3710.3643 | 0 | 3710.3643
| 2099 | 2631.344 | 0 | 2631.344
| 2100 | 1642.9356 | 16.4268 | 1626.5088
| 2101 | 842.8215 | 64.3813 | 778.4402
| 2102 | 446.5227 | 173.9045 | 272.6182
| 2103 | 364.6797 | 210.6993 | 153.9803
| 2104 | 302.3968 | 156.4911 | 145.9057
| 2105 | 364.8105 | 121.2891 | 243.5213
| 2106 | 652.2648 | 61.8244 | 590.4404
| 2107 | 1203.6037 | 10.7606 | 1192.843
| 2108 | 1726.7568 | 0.53507 | 1726.2217
| 2109 | 2210.41 | 0 | 2210.41
| 2110 | 610.1889 | 0 | 610.1889
| 2111 | 670.2495 | 0 | 670.2495
| 2112 | 737.2743 | 0 | 737.2743
| 2113 | 802.6648 | 0 | 802.6648
| 2114 | 866.0999 | 0 | 866.0999
| 2115 | 947.5998 | 0 | 947.5998
| 2116 | 1058.9183 | 0 | 1058.9183
| 2117 | 1129.6885 | 0 | 1129.6885
| 2118 | 1148.1837 | 0 | 1148.1837
| 2119 | 8776.1824 | 0 | 8776.1824
| 2120 | 6058.756 | 0 | 6058.756
| 2121 | 4413.9414 | 0 | 4413.9414
| 2122 | 2592.1644 | 0 | 2592.1644
| 2123 | 1173.857 | 0 | 1173.857
| 2124 | 317.9375 | 23.2015 | 294.736
| 2125 | 128.7654 | 67.3877 | 61.3776
| 2126 | 86.9699 | 91.3202 | -4.3503
| 2127 | 78.012 | 52.4423 | 25.5698
| 2128 | 72.226 | 48.9358 | 23.2902
| 2129 | 70.3402 | 44.0997 | 26.2405
| 2130 | 67.8495 | 20.5403 | 47.3092
| 2131 | 91.7599 | 0 | 91.7599
| 2132 | 389.4251 | 0 | 389.4251
| 2133 | 854.391 | 0 | 854.391
| 2134 | 1406.3847 | 0 | 1406.3847
| 2135 | 298.3762 | 0 | 298.3762
| 2136 | 388.5388 | 0 | 388.5388
| 2137 | 480.2326 | 0 | 480.2326
| 2138 | 542.8054 | 0 | 542.8054
| 2139 | 590.0779 | 0 | 590.0779
| 2140 | 633.8342 | 0 | 633.8342
| 2141 | 656.3643 | 0 | 656.3643
| 2142 | 662.5148 | 0 | 662.5148
| 2143 | 656.5908 | 0 | 656.5908
| 2144 | 630.5947 | 0 | 630.5947
| 2145 | 5659.1408 | 0 | 5659.1408
| 2146 | 3914.123 | 0 | 3914.123
| 2147 | 2892.9679 | 0 | 2892.9679
| 2148 | 2091.146 | 0 | 2091.146
| 2149 | 1200.254 | 0 | 1200.254
| 2150 | 956.1315 | 0 | 956.1315
| 2151 | 1025.1602 | 0 | 1025.1602
| 2152 | 1118.6049 | 0 | 1118.6049
| 2153 | 1223.3106 | 0 | 1223.3106
| 2154 | 2315.9774 | 0 | 2315.9774
| 2155 | 2773.2603 | 0 | 2773.2603
| 2156 | 393.0292 | 0 | 393.0292
| 2157 | 413.461 | 0 | 413.461
| 2158 | 464.0584 | 0 | 464.0584
| 2159 | 575.451 | 0 | 575.451
| 2160 | 721.3784 | 0 | 721.3784
| 2161 | 889.5648 | 0 | 889.5648
| 2162 | 1069.1522 | 0 | 1069.1522
| 2163 | 1236.095 | 0 | 1236.095
| 2164 | 1411.963 | 0 | 1411.963
| 2165 | 1582.3884 | 0 | 1582.3884
| 2166 | 1738.2037 | 0 | 1738.2037
| 2167 | 10347.4273 | 0 | 10347.4273
| 2168 | 6731.7947 | 0 | 6731.7947
| 2169 | 4384.8011 | 0 | 4384.8011
| 2170 | 2634.1165 | 0 | 2634.1165
| 2171 | 1628.4777 | 0 | 1628.4777
| 2172 | 858.902 | 10.1444 | 848.7576
| 2173 | 485.7437 | 37.2792 | 448.4645
| 2174 | 327.4361 | 117.3149 | 210.1212
| 2175 | 230.7803 | 178.9575 | 51.8227
| 2176 | 215.7945 | 165.5933 | 50.2012
| 2177 | 245.2691 | 128.9372 | 116.332
| 2178 | 379.3842 | 78.2016 | 301.1826
| 2179 | 1503.9893 | 7.3361 | 1496.6532
| 2180 | 2684.968 | 0 | 2684.968
| 2181 | 3330.183 | 0 | 3330.183
| 2182 | 928.9518 | 0 | 928.9518
| 2183 | 901.1142 | 0 | 901.1142
| 2184 | 1009.003 | 0 | 1009.003
| 2185 | 1141.882 | 0 | 1141.882
| 2186 | 1350.4244 | 0 | 1350.4244
| 2187 | 1541.6811 | 0 | 1541.6811
| 2188 | 1639.3552 | 0 | 1639.3552
| 2189 | 1615.665 | 0 | 1615.665
| 2190 | 9687.8874 | 0 | 9687.8874
| 2191 | 7905.0303 | 0 | 7905.0303
| 2192 | 6539.1123 | 0 | 6539.1123
| 2193 | 4918.4493 | 0 | 4918.4493
| 2194 | 3614.5036 | 0 | 3614.5036
| 2195 | 2501.2957 | 0 | 2501.2957
| 2196 | 1614.3485 | 0 | 1614.3485
| 2197 | 1022.7288 | 0 | 1022.7288
| 2198 | 654.0519 | 0 | 654.0519
| 2199 | 418.2408 | 0 | 418.2408
| 2200 | 346.5074 | 0 | 346.5074
| 2201 | 354.1241 | 0 | 354.1241
| 2202 | 827.1635 | 0 | 827.1635
| 2203 | 1361.4243 | 0 | 1361.4243
| 2204 | 1866.776 | 0 | 1866.776
| 2205 | 619.1237 | 0 | 619.1237
| 2206 | 808.8199 | 0 | 808.8199
| 2207 | 897.3762 | 0 | 897.3762
| 2208 | 946.9521 | 0 | 946.9521
| 2209 | 991.7454 | 0 | 991.7454
| 2210 | 1009.1745 | 0 | 1009.1745
| 2211 | 996.514 | 0 | 996.514
| 2212 | 959.2745 | 0 | 959.2745
| 2213 | 890.8472 | 0 | 890.8472
| 2214 | 6701.0412 | 0 | 6701.0412
| 2215 | 5004.9232 | 0 | 5004.9232
| 2216 | 3688.6261 | 0 | 3688.6261
| 2217 | 2452.0914 | 0 | 2452.0914
| 2218 | 1767.2281 | 0 | 1767.2281
| 2219 | 1170.1562 | 0 | 1170.1562
| 2220 | 799.2194 | 0 | 799.2194
| 2221 | 354.7054 | 0 | 354.7054
| 2222 | 253.6926 | 0 | 253.6926
| 2223 | 346.5702 | 0 | 346.5702
| 2224 | 1049.1055 | 0 | 1049.1055
| 2225 | 1765.3944 | 0 | 1765.3944
| 2226 | 2389.8034 | 0 | 2389.8034
| 2227 | 2646.5831 | 0 | 2646.5831
| 2228 | 3081.2306 | 0 | 3081.2306
| 2229 | 882.945 | 0 | 882.945
| 2230 | 820.3468 | 0 | 820.3468
| 2231 | 924.1412 | 0 | 924.1412
| 2232 | 1106.8104 | 0 | 1106.8104
| 2233 | 1192.2984 | 0 | 1192.2984
| 2234 | 1250.58 | 0 | 1250.58
| 2235 | 1266.0794 | 0 | 1266.0794
| 2236 | 1277.1235 | 0 | 1277.1235
| 2237 | 1289.0331 | 0 | 1289.0331
| 2238 | 8865.2316 | 0 | 8865.2316
| 2239 | 7165.8865 | 0 | 7165.8865
| 2240 | 5648.466 | 0 | 5648.466
| 2241 | 4367.9553 | 0 | 4367.9553
| 2242 | 3668.9366 | 0 | 3668.9366
| 2243 | 2850.8432 | 0 | 2850.8432
| 2244 | 2183.8607 | 0 | 2183.8607
| 2245 | 1731.6372 | 10.5537 | 1721.0835
| 2246 | 1338.9816 | 38.297 | 1300.6846
| 2247 | 882.925 | 83.6862 | 799.2388
| 2248 | 767.143 | 85.5265 | 681.6165
| 2249 | 807.7763 | 85.0435 | 722.7328
| 2250 | 1221.5224 | 46.3372 | 1175.1853
| 2251 | 1822.9701 | 6.5213 | 1816.4488
| 2252 | 2519.7852 | 0 | 2519.7852
| 2253 | 715.5001 | 0 | 715.5001
| 2254 | 738.3318 | 0 | 738.3318
| 2255 | 847.8991 | 0 | 847.8991
| 2256 | 980.5029 | 0 | 980.5029
| 2257 | 1140.5245 | 0 | 1140.5245
| 2258 | 1300.6617 | 0 | 1300.6617
| 2259 | 1390.2206 | 0 | 1390.2206
| 2260 | 1486.0883 | 0 | 1486.0883
| 2261 | 1656.4006 | 0 | 1656.4006
| 2262 | 10595.056 | 0 | 10595.056
| 2263 | 8158.734 | 0 | 8158.734
| 2264 | 5701.3267 | 0 | 5701.3267
| 2265 | 3521.3478 | 0 | 3521.3478
| 2266 | 2389.6768 | 0 | 2389.6768
| 2267 | 1355.9113 | 0 | 1355.9113
| 2268 | 803.3397 | 6.7758 | 796.5639
| 2269 | 414.8851 | 50.441 | 364.444
| 2270 | 215.9214 | 132.4138 | 83.5075
| 2271 | 102.3612 | 280.5819 | -178.2207
| 2272 | 47.7787 | 275.4571 | -227.6784
| 2273 | 29.6229 | 188.5553 | -158.9324
| 2274 | 24.1304 | 108.9245 | -84.794
| 2275 | 47.3327 | 87.0362 | -39.7035
| 2276 | 105.3501 | 24.9441 | 80.406
| 2277 | 125.9439 | 9.7962 | 116.1477
| 2278 | 187.8664 | 0 | 187.8664
| 2279 | 284.9584 | 0 | 284.9584
| 2280 | 351.2847 | 0 | 351.2847
| 2281 | 386.5276 | 0 | 386.5276
| 2282 | 413.3624 | 0 | 413.3624
| 2283 | 441.9258 | 0 | 441.9258
| 2284 | 461.0831 | 0 | 461.0831
| 2285 | 471.574 | 0 | 471.574
| 2286 | 4883.1354 | 14.226 | 4868.9093
| 2287 | 3548.208 | 0 | 3548.208
| 2288 | 2967.8725 | 0 | 2967.8725
| 2289 | 2319.6872 | 0 | 2319.6872
| 2290 | 1887.7422 | 0 | 1887.7422
| 2291 | 1603.3701 | 0 | 1603.3701
| 2292 | 1478.5327 | 0 | 1478.5327
| 2293 | 1531.0876 | 0 | 1531.0876
| 2294 | 1757.4292 | 0 | 1757.4292
| 2295 | 1839.106 | 0 | 1839.106
| 2296 | 2010.7903 | 0 | 2010.7903
| 2297 | 2240.2584 | 0 | 2240.2584
| 2298 | 2797.0262 | 0 | 2797.0262
| 2299 | 3272.1191 | 0 | 3272.1191
| 2300 | 3493.4376 | 0 | 3493.4376
| 2301 | 3979.4968 | 0 | 3979.4968
| 2302 | 969.5612 | 0 | 969.5612
| 2303 | 1067.6986 | 0 | 1067.6986
| 2304 | 1178.4329 | 0 | 1178.4329
| 2305 | 1271.702 | 0 | 1271.702
| 2306 | 1383.0748 | 0 | 1383.0748
| 2307 | 1436.8893 | 0 | 1436.8893
| 2308 | 1445.4681 | 0 | 1445.4681
| 2309 | 1447.6564 | 0 | 1447.6564
| 2310 | 1431.2172 | 0 | 1431.2172
| 2311 | 1429.3838 | 0 | 1429.3838
| 2312 | 8613.9587 | 0 | 8613.9587
| 2313 | 6450.2669 | 0 | 6450.2669
| 2314 | 5396.6616 | 0 | 5396.6616
| 2315 | 4918.8142 | 0 | 4918.8142
| 2316 | 4383.3803 | 0 | 4383.3803
| 2317 | 4081.9014 | 0 | 4081.9014
| 2318 | 3907.6404 | 0 | 3907.6404
| 2319 | 3740.5782 | 0 | 3740.5782
| 2320 | 3638.7603 | 0 | 3638.7603
| 2321 | 4956.9204 | 0 | 4956.9204
| 2322 | 5343.212 | 0 | 5343.212
| 2323 | 1238.7072 | 0 | 1238.7072
| 2324 | 1299.1618 | 0 | 1299.1618
| 2325 | 1358.4059 | 0 | 1358.4059
| 2326 | 1424.2218 | 0 | 1424.2218
| 2327 | 1522.2123 | 0 | 1522.2123
| 2328 | 1606.1786 | 0 | 1606.1786
| 2329 | 1668.4567 | 0 | 1668.4567
| 2330 | 1756.1576 | 0 | 1756.1576
| 2331 | 1819.3817 | 0 | 1819.3817
| 2332 | 1860.2784 | 0 | 1860.2784
| 2333 | 1905.5485 | 0 | 1905.5485
| 2334 | 10247.9329 | 0 | 10247.9329
| 2335 | 7566.0506 | 0 | 7566.0506
| 2336 | 5875.4838 | 0 | 5875.4838
| 2337 | 4251.4459 | 0 | 4251.4459
| 2338 | 3115.2136 | 0 | 3115.2136
| 2339 | 2304.1705 | 0 | 2304.1705
| 2340 | 1714.3543 | 0 | 1714.3543
| 2341 | 1206.4924 | 19.8373 | 1186.6551
| 2342 | 800.2651 | 49.6875 | 750.5775
| 2343 | 523.8555 | 57.0591 | 466.7964
| 2344 | 527.8001 | 75.8961 | 451.904
| 2345 | 562.301 | 86.0322 | 476.2688
| 2346 | 914.7083 | 55.334 | 859.3743
| 2347 | 1500.8039 | 17.5763 | 1483.2276
| 2348 | 2336.4418 | 0.033397 | 2336.4084
| 2349 | 730.065 | 0 | 730.065
| 2350 | 837.4115 | 0 | 837.4115
| 2351 | 964.6776 | 0 | 964.6776
| 2352 | 1071.2399 | 0 | 1071.2399
| 2353 | 1186.1079 | 0 | 1186.1079
| 2354 | 1277.3011 | 0 | 1277.3011
| 2355 | 1291.1076 | 0 | 1291.1076
| 2356 | 1311.6702 | 0 | 1311.6702
| 2357 | 1382.0956 | 0 | 1382.0956
| 2358 | 10119.2715 | 0 | 10119.2715
| 2359 | 7244.6812 | 0 | 7244.6812
| 2360 | 5105.6313 | 0 | 5105.6313
| 2361 | 3038.8355 | 0 | 3038.8355
| 2362 | 1812.0012 | 0 | 1812.0012
| 2363 | 1112.9545 | 0 | 1112.9545
| 2364 | 747.3537 | 5.4295 | 741.9242
| 2365 | 409.6393 | 50.4976 | 359.1416
| 2366 | 267.8045 | 77.7911 | 190.0134
| 2367 | 224.7085 | 117.3906 | 107.3179
| 2368 | 179.6741 | 155.4804 | 24.1938
| 2369 | 174.0397 | 115.7011 | 58.3386
| 2370 | 176.5761 | 47.6822 | 128.8939
| 2371 | 499.6761 | 21.2956 | 478.3805
| 2372 | 997.8126 | 0 | 997.8126
| 2373 | 314.3336 | 0 | 314.3336
| 2374 | 343.5688 | 0 | 343.5688
| 2375 | 364.3706 | 0 | 364.3706
| 2376 | 390.804 | 0 | 390.804
| 2377 | 405.7525 | 0 | 405.7525
| 2378 | 405.6409 | 0 | 405.6409
| 2379 | 406.4807 | 0 | 406.4807
| 2380 | 409.233 | 0 | 409.233
| 2381 | 414.0427 | 0 | 414.0427
| 2382 | 4497.4539 | 0 | 4497.4539
| 2383 | 3124.4265 | 0 | 3124.4265
| 2384 | 2463.6326 | 0 | 2463.6326
| 2385 | 1694.442 | 0 | 1694.442
| 2386 | 1348.4269 | 0 | 1348.4269
| 2387 | 1044.6289 | 0 | 1044.6289
| 2388 | 918.6958 | 0 | 918.6958
| 2389 | 1037.1749 | 0 | 1037.1749
| 2390 | 862.1756 | 0 | 862.1756
| 2391 | 597.0458 | 0 | 597.0458
| 2392 | 521.4184 | 0 | 521.4184
| 2393 | 603.0222 | 0 | 603.0222
| 2394 | 931.1129 | 0 | 931.1129
| 2395 | 1297.8756 | 0 | 1297.8756
| 2396 | 1664.567 | 0 | 1664.567
| 2397 | 481.2312 | 0 | 481.2312
| 2398 | 538.9354 | 0 | 538.9354
| 2399 | 596.9458 | 0 | 596.9458
| 2400 | 665.0611 | 0 | 665.0611
| 2401 | 742.6902 | 0 | 742.6902
| 2402 | 848.8855 | 0 | 848.8855
| 2403 | 936.4597 | 0 | 936.4597
| 2404 | 1078.5672 | 0 | 1078.5672
| 2405 | 1184.6537 | 0 | 1184.6537
| 2406 | 8424.1885 | 0 | 8424.1885
| 2407 | 5864.4622 | 0 | 5864.4622
| 2408 | 4289.3318 | 0 | 4289.3318
| 2409 | 2919.9262 | 0 | 2919.9262
| 2410 | 2118.8353 | 0 | 2118.8353
| 2411 | 1344.3381 | 0 | 1344.3381
| 2412 | 807.6696 | 1.147 | 806.5226
| 2413 | 462.767 | 27.2992 | 435.4678
| 2414 | 330.8517 | 103.2236 | 227.6281
| 2415 | 256.7492 | 110.7311 | 146.018
| 2416 | 216.0236 | 114.8196 | 101.204
| 2417 | 245.0689 | 68.5704 | 176.4985
| 2418 | 493.3315 | 18.0523 | 475.2792
| 2419 | 1034.5258 | 2.2209 | 1032.305
| 2420 | 1422.6183 | 0 | 1422.6183
| 2421 | 407.645 | 0 | 407.645
| 2422 | 473.3342 | 0 | 473.3342
| 2423 | 532.1812 | 0 | 532.1812
| 2424 | 594.2015 | 0 | 594.2015
| 2425 | 698.9733 | 0 | 698.9733
| 2426 | 825.1496 | 0 | 825.1496
| 2427 | 910.4415 | 0 | 910.4415
| 2428 | 991.1796 | 0 | 991.1796
| 2429 | 1071.5683 | 0 | 1071.5683
| 2430 | 8885.8408 | 0 | 8885.8408
| 2431 | 6226.8364 | 0 | 6226.8364
| 2432 | 4672.2024 | 0 | 4672.2024
| 2433 | 3271.5164 | 0 | 3271.5164
| 2434 | 2378.5332 | 0 | 2378.5332
| 2435 | 1622.6423 | 0 | 1622.6423
| 2436 | 1087.4115 | 0 | 1087.4115
| 2437 | 897.0168 | 1.5032 | 895.5136
| 2438 | 722.2465 | 11.7493 | 710.4972
| 2439 | 668.3582 | 17.0037 | 651.3546
| 2440 | 944.5725 | 12.128 | 932.4446
| 2441 | 1406.2336 | 0 | 1406.2336
| 2442 | 1722.9449 | 0 | 1722.9449
| 2443 | 1977.0554 | 0 | 1977.0554
| 2444 | 2196.4589 | 0 | 2196.4589
| 2445 | 549.4328 | 0 | 549.4328
| 2446 | 588.4545 | 0 | 588.4545
| 2447 | 632.017 | 0 | 632.017
| 2448 | 664.254 | 0 | 664.254
| 2449 | 683.5529 | 0 | 683.5529
| 2450 | 699.7479 | 0 | 699.7479
| 2451 | 712.925 | 0 | 712.925
| 2452 | 718.8742 | 0 | 718.8742
| 2453 | 713.62 | 0 | 713.62
| 2454 | 6555.1865 | 0 | 6555.1865
| 2455 | 4757.2457 | 0 | 4757.2457
| 2456 | 4022.7034 | 0 | 4022.7034
| 2457 | 3136.3013 | 0 | 3136.3013
| 2458 | 2384.7392 | 0 | 2384.7392
| 2459 | 1929.9303 | 0 | 1929.9303
| 2460 | 1756.5413 | 0 | 1756.5413
| 2461 | 1652.6421 | 0 | 1652.6421
| 2462 | 1553.1161 | 0 | 1553.1161
| 2463 | 1332.5313 | 0 | 1332.5313
| 2464 | 1148.7335 | 0 | 1148.7335
| 2465 | 1170.8187 | 0 | 1170.8187
| 2466 | 1562.262 | 0 | 1562.262
| 2467 | 1756.1523 | 0 | 1756.1523
| 2468 | 1837.9317 | 0 | 1837.9317
| 2469 | 2137.2744 | 0 | 2137.2744
| 2470 | 419.6952 | 0 | 419.6952
| 2471 | 464.6814 | 0 | 464.6814
| 2472 | 545.8045 | 0 | 545.8045
| 2473 | 646.0792 | 0 | 646.0792
| 2474 | 693.9317 | 0 | 693.9317
| 2475 | 727.6635 | 0 | 727.6635
| 2476 | 738.9757 | 0 | 738.9757
| 2477 | 737.2355 | 0 | 737.2355
| 2478 | 679.7368 | 0 | 679.7368
| 2479 | 621.1942 | 0 | 621.1942
| 2480 | 5252.6125 | 0 | 5252.6125
| 2481 | 3495.4954 | 0 | 3495.4954
| 2482 | 2546.7631 | 0 | 2546.7631
| 2483 | 1857.5517 | 0 | 1857.5517
| 2484 | 1114.6302 | 0 | 1114.6302
| 2485 | 774.8372 | 0 | 774.8372
| 2486 | 612.386 | 0 | 612.386
| 2487 | 374.01 | 0 | 374.01
| 2488 | 147.6873 | 0 | 147.6873
| 2489 | 339.208 | 0 | 339.208
| 2490 | 616.9243 | 0 | 616.9243
| 2491 | 107.9824 | 0 | 107.9824
| 2492 | 216.6064 | 0 | 216.6064
| 2493 | 328.5447 | 0 | 328.5447
| 2494 | 443.0621 | 0 | 443.0621
| 2495 | 557.1537 | 0 | 557.1537
| 2496 | 674.1424 | 0 | 674.1424
| 2497 | 779.75 | 0 | 779.75
| 2498 | 858.0508 | 0 | 858.0508
| 2499 | 939.0537 | 0 | 939.0537
| 2500 | 979.6671 | 0 | 979.6671
| 2501 | 1049.707 | 0 | 1049.707
| 2502 | 8677.4208 | 0 | 8677.4208
| 2503 | 5971.8752 | 0 | 5971.8752
| 2504 | 3921.5962 | 0 | 3921.5962
| 2505 | 1887.0163 | 0 | 1887.0163
| 2506 | 508.5777 | 10.9113 | 497.6664
| 2507 | 68.7412 | 52.1221 | 16.6191
| 2508 | 7.0344 | 924.9303 | -917.8959
| 2509 | 0 | 2354.6805 | -2354.6805
| 2510 | 0 | 3706.2001 | -3706.2001
| 2511 | 0 | 4872.3198 | -4872.3198
| 2512 | 0 | 5356.6016 | -5356.6016
| 2513 | 0 | 5349.8087 | -5349.8087
| 2514 | 0 | 3659.4704 | -3659.4704
| 2515 | 0 | 2677.7349 | -2677.7349
| 2516 | 0 | 1754.2483 | -1754.2483
| 2517 | 0 | 461.204 | -461.204
| 2518 | 0 | 2.813 | -2.813
| 2519 | 0 | 0 | 0
| 2520 | 0.15932 | 0 | 0.15932
| 2521 | 2.3543 | 0 | 2.3543
| 2522 | 7.8801 | 0 | 7.8801
| 2523 | 11.7746 | 0 | 11.7746
| 2524 | 15.9156 | 0 | 15.9156
| 2525 | 14.6578 | 0 | 14.6578
| 2526 | 1028.092 | 117.4784 | 910.6137
| 2527 | 654.1987 | 0 | 654.1987
| 2528 | 421.9497 | 133.6853 | 288.2645
| 2529 | 628.709 | 107.1615 | 521.5475
| 2530 | 951.2372 | 96.2286 | 855.0086
| 2531 | 834.4176 | 167.3943 | 667.0233
| 2532 | 723.773 | 224.7789 | 498.9942
| 2533 | 383.3724 | 462.4699 | -79.0974
| 2534 | 136.5191 | 749.0692 | -612.55
| 2535 | 59.0058 | 707.8627 | -648.8569
| 2536 | 62.3527 | 483.0391 | -420.6864
| 2537 | 83.0304 | 365.5095 | -282.4791
| 2538 | 125.6333 | 206.2153 | -80.582
| 2539 | 432.0637 | 151.264 | 280.7997
| 2540 | 980.0397 | 39.6332 | 940.4064
| 2541 | 208.0256 | 12.6038 | 195.4218
| 2542 | 306.4868 | 0 | 306.4868
| 2543 | 400.4235 | 0 | 400.4235
| 2544 | 433.7504 | 0 | 433.7504
| 2545 | 521.5356 | 0 | 521.5356
| 2546 | 611.2673 | 0 | 611.2673
| 2547 | 678.4022 | 0 | 678.4022
| 2548 | 681.8747 | 0 | 681.8747
| 2549 | 677.043 | 0 | 677.043
| 2550 | 6772.5018 | 0 | 6772.5018
| 2551 | 4564.5861 | 0 | 4564.5861
| 2552 | 3279.6616 | 0 | 3279.6616
| 2553 | 2213.4853 | 0.26234 | 2213.223
| 2554 | 1942.3952 | 0.85514 | 1941.54
| 2555 | 1925.3392 | 0 | 1925.3392
| 2556 | 1632.8627 | 0 | 1632.8627
| 2557 | 992.4407 | 17.5303 | 974.9104
| 2558 | 811.5115 | 61.7289 | 749.7826
| 2559 | 614.0556 | 94.3698 | 519.6858
| 2560 | 598.0586 | 99.3047 | 498.7539
| 2561 | 883.54 | 58.996 | 824.544
| 2562 | 1121.9997 | 12.1597 | 1109.8401
| 2563 | 1598.7605 | 1.9847 | 1596.7758
| 2564 | 1961.5358 | 0 | 1961.5358
| 2565 | 498.1788 | 0 | 498.1788
| 2566 | 580.0858 | 0 | 580.0858
| 2567 | 669.8999 | 0 | 669.8999
| 2568 | 745.8375 | 0 | 745.8375
| 2569 | 770.8671 | 0 | 770.8671
| 2570 | 801.1628 | 0 | 801.1628
| 2571 | 845.3757 | 0 | 845.3757
| 2572 | 874.1647 | 0 | 874.1647
| 2573 | 907.446 | 0 | 907.446
| 2574 | 8111.2284 | 0 | 8111.2284
| 2575 | 5872.7099 | 0 | 5872.7099
| 2576 | 4172.7606 | 0 | 4172.7606
| 2577 | 2620.135 | 1.9074 | 2618.2277
| 2578 | 1883.3535 | 6.2968 | 1877.0567
| 2579 | 1294.2314 | 5.4542 | 1288.7773
| 2580 | 990.8401 | 13.7133 | 977.1267
| 2581 | 541.05 | 69.8644 | 471.1856
| 2582 | 296.2548 | 158.8721 | 137.3827
| 2583 | 240.9549 | 181.0085 | 59.9464
| 2584 | 198.5117 | 207.9172 | -9.4055
| 2585 | 172.4781 | 189.4274 | -16.9493
| 2586 | 177.852 | 127.1514 | 50.7006
| 2587 | 701.7594 | 78.0806 | 623.6788
| 2588 | 1535.7529 | 13.9037 | 1521.8492
| 2589 | 449.9401 | 3.2196 | 446.7205
| 2590 | 532.6091 | 0 | 532.6091
| 2591 | 616.448 | 0 | 616.448
| 2592 | 677.1933 | 0 | 677.1933
| 2593 | 620.2518 | 0 | 620.2518
| 2594 | 533.6341 | 0 | 533.6341
| 2595 | 545.1116 | 0 | 545.1116
| 2596 | 569.6687 | 0 | 569.6687
| 2597 | 536.8663 | 0 | 536.8663
| 2598 | 5222.3628 | 31.9927 | 5190.3702
| 2599 | 3257.946 | 0 | 3257.946
| 2600 | 2200.4153 | 1.9288 | 2198.4864
| 2601 | 947.2426 | 24.994 | 922.2486
| 2602 | 553.5929 | 43.8572 | 509.7357
| 2603 | 165.1119 | 156.8401 | 8.2717
| 2604 | 59.0053 | 370.7296 | -311.7243
| 2605 | 20.016 | 928.1391 | -908.1231
| 2606 | 40.273 | 737.2062 | -696.9332
| 2607 | 47.1794 | 551.7551 | -504.5757
| 2608 | 36.4557 | 399.5495 | -363.0938
| 2609 | 43.4624 | 281.189 | -237.7266
| 2610 | 26.7284 | 182.3427 | -155.6143
| 2611 | 38.4248 | 148.5042 | -110.0794
| 2612 | 137.5876 | 48.0854 | 89.5022
| 2613 | 155.3466 | 10.8518 | 144.4948
| 2614 | 234.9703 | 0 | 234.9703
| 2615 | 302.1112 | 0 | 302.1112
| 2616 | 374.076 | 0 | 374.076
| 2617 | 443.7461 | 0 | 443.7461
| 2618 | 497.1193 | 0 | 497.1193
| 2619 | 606.7373 | 0 | 606.7373
| 2620 | 647.1103 | 0 | 647.1103
| 2621 | 618.4969 | 0 | 618.4969
| 2622 | 5885.7924 | 0 | 5885.7924
| 2623 | 4169.1032 | 0 | 4169.1032
| 2624 | 3567.1241 | 0 | 3567.1241
| 2625 | 2635.9228 | 0.22311 | 2635.6997
| 2626 | 1778.761 | 2.4718 | 1776.2892
| 2627 | 1253.4103 | 0.44543 | 1252.9649
| 2628 | 910.7995 | 3.817 | 906.9825
| 2629 | 676.17 | 3.2871 | 672.8829
| 2630 | 549.7808 | 0 | 549.7808
| 2631 | 486.4015 | 0 | 486.4015
| 2632 | 525.9501 | 0 | 525.9501
| 2633 | 661.0097 | 2.097 | 658.9127
| 2634 | 1352.8901 | 0 | 1352.8901
| 2635 | 1948.1649 | 0 | 1948.1649
| 2636 | 2369.7517 | 0 | 2369.7517
| 2637 | 2947.5806 | 0 | 2947.5806
| 2638 | 637.7336 | 0 | 637.7336
| 2639 | 743.4437 | 0 | 743.4437
| 2640 | 891.7306 | 0 | 891.7306
| 2641 | 1067.8919 | 0 | 1067.8919
| 2642 | 1130.7997 | 0 | 1130.7997
| 2643 | 1147.8424 | 0 | 1147.8424
| 2644 | 1118.7006 | 0 | 1118.7006
| 2645 | 1123.8293 | 0 | 1123.8293
| 2646 | 1117.6403 | 0 | 1117.6403
| 2647 | 1015.6317 | 0 | 1015.6317
| 2648 | 7295.1091 | 0 | 7295.1091
| 2649 | 4948.3311 | 0 | 4948.3311
| 2650 | 3539.1919 | 0 | 3539.1919
| 2651 | 2661.976 | 0 | 2661.976
| 2652 | 1908.7436 | 0 | 1908.7436
| 2653 | 1508.2351 | 0 | 1508.2351
| 2654 | 1369.5953 | 0 | 1369.5953
| 2655 | 1427.4319 | 0 | 1427.4319
| 2656 | 1426.0647 | 0 | 1426.0647
| 2657 | 2472.6573 | 0 | 2472.6573
| 2658 | 2776.4501 | 0 | 2776.4501
| 2659 | 429.3928 | 0 | 429.3928
| 2660 | 530.7911 | 0 | 530.7911
| 2661 | 605.8637 | 0 | 605.8637
| 2662 | 728.092 | 0 | 728.092
| 2663 | 885.3022 | 0 | 885.3022
| 2664 | 1068.1191 | 0 | 1068.1191
| 2665 | 1294.7405 | 0 | 1294.7405
| 2666 | 1355.2255 | 0 | 1355.2255
| 2667 | 1353.9153 | 0 | 1353.9153
| 2668 | 1410.4275 | 0 | 1410.4275
| 2669 | 1440.6814 | 0 | 1440.6814
| 2670 | 9493.1625 | 0 | 9493.1625
| 2671 | 6682.7125 | 0 | 6682.7125
| 2672 | 4910.3003 | 0 | 4910.3003
| 2673 | 3333.6585 | 0 | 3333.6585
| 2674 | 2501.3356 | 0 | 2501.3356
| 2675 | 1955.1599 | 0 | 1955.1599
| 2676 | 1382.4657 | 0.53805 | 1381.9277
| 2677 | 977.8822 | 7.6586 | 970.2236
| 2678 | 727.8 | 20.9026 | 706.8974
| 2679 | 548.3925 | 24.8645 | 523.528
| 2680 | 571.9324 | 43.7226 | 528.2098
| 2681 | 775.914 | 21.4609 | 754.4531
| 2682 | 1156.6442 | 9.6071 | 1147.0371
| 2683 | 1560.0841 | 2.9908 | 1557.0932
| 2684 | 1965.0601 | 0 | 1965.0601
| 2685 | 564.6138 | 0 | 564.6138
| 2686 | 641.6356 | 0 | 641.6356
| 2687 | 708.2964 | 0 | 708.2964
| 2688 | 793.6207 | 0 | 793.6207
| 2689 | 845.776 | 0 | 845.776
| 2690 | 911.8416 | 0 | 911.8416
| 2691 | 1005.7088 | 0 | 1005.7088
| 2692 | 1160.5843 | 0 | 1160.5843
| 2693 | 1216.4575 | 0 | 1216.4575
| 2694 | 9003.8033 | 0 | 9003.8033
| 2695 | 6111.4236 | 0 | 6111.4236
| 2696 | 4261.034 | 0 | 4261.034
| 2697 | 2602.6951 | 13.9974 | 2588.6976
| 2698 | 1499.8844 | 38.9434 | 1460.941
| 2699 | 658.1587 | 52.8925 | 605.2661
| 2700 | 271.8958 | 82.2367 | 189.6592
| 2701 | 204.0025 | 162.3513 | 41.6513
| 2702 | 168.5956 | 254.9547 | -86.3591
| 2703 | 114.4486 | 289.0753 | -174.6267
| 2704 | 64.901 | 304.4384 | -239.5374
| 2705 | 40.13 | 252.5157 | -212.3857
| 2706 | 37.1097 | 153.5759 | -116.4662
| 2707 | 72.9006 | 112.144 | -39.2434
| 2708 | 237.7028 | 41.8071 | 195.8957
| 2709 | 208.7898 | 13.4389 | 195.351
| 2710 | 361.8147 | 0 | 361.8147
| 2711 | 448.5786 | 0 | 448.5786
| 2712 | 481.6067 | 0 | 481.6067
| 2713 | 524.0452 | 0 | 524.0452
| 2714 | 529.8052 | 0 | 529.8052
| 2715 | 552.0363 | 0 | 552.0363
| 2716 | 567.3548 | 0 | 567.3548
| 2717 | 573.4063 | 0 | 573.4063
| 2718 | 5660.3673 | 11.6677 | 5648.6995
| 2719 | 3487.05 | 0 | 3487.05
| 2720 | 2093.1592 | 33.0318 | 2060.1274
| 2721 | 553.2714 | 93.2918 | 459.9795
| 2722 | 54.3558 | 401.1099 | -346.754
| 2723 | 2.4862 | 1274.2937 | -1271.8075
| 2724 | 0 | 2494.004 | -2494.004
| 2725 | 0 | 3659.6061 | -3659.6061
| 2726 | 0 | 4616.1764 | -4616.1764
| 2727 | 0 | 4747.8187 | -4747.8187
| 2728 | 0 | 4506.6345 | -4506.6345
| 2729 | 0 | 4329.515 | -4329.515
| 2730 | 0 | 3064.1482 | -3064.1482
| 2731 | 0 | 2370.2095 | -2370.2095
| 2732 | 0 | 1689.7745 | -1689.7745
| 2733 | 0 | 765.662 | -765.662
| 2734 | 0 | 6.9693 | -6.9693
| 2735 | 0 | 2.3504 | -2.3504
| 2736 | 0 | 0.058398 | -0.058398
| 2737 | 0 | 0 | 0
| 2738 | 0 | 0 | 0
| 2739 | 1.1611 | 0 | 1.1611
| 2740 | 6.5322 | 0 | 6.5322
| 2741 | 10.1243 | 0 | 10.1243
| 2742 | 955.6046 | 181.0328 | 774.5719
| 2743 | 611.4753 | 54.4115 | 557.0638
| 2744 | 148.9825 | 660.3675 | -511.385
| 2745 | 21.179 | 714.7053 | -693.5264
| 2746 | 31.2616 | 798.9772 | -767.7156
| 2747 | 30.4844 | 863.3676 | -832.8832
| 2748 | 11.0796 | 1251.6929 | -1240.6132
| 2749 | 0.16521 | 2822.7802 | -2822.615
| 2750 | 0 | 3076.0466 | -3076.0466
| 2751 | 0.17531 | 2119.8635 | -2119.6882
| 2752 | 4.0796 | 1118.744 | -1114.6645
| 2753 | 5.415 | 667.059 | -661.644
| 2754 | 5.0617 | 305.9736 | -300.912
| 2755 | 13.4959 | 244.7324 | -231.2365
| 2756 | 59.4551 | 137.8872 | -78.4322
| 2757 | 23.7197 | 112.6051 | -88.8854
| 2758 | 39.0235 | 0 | 39.0235
| 2759 | 91.2297 | 0 | 91.2297
| 2760 | 158.6291 | 0 | 158.6291
| 2761 | 216.3396 | 0 | 216.3396
| 2762 | 271.135 | 0 | 271.135
| 2763 | 311.4562 | 0 | 311.4562
| 2764 | 347.8534 | 0 | 347.8534
| 2765 | 369.3455 | 0 | 369.3455
| 2766 | 4657.5927 | 36.2298 | 4621.363
| 2767 | 3229.8567 | 0 | 3229.8567
| 2768 | 2494.3222 | 0 | 2494.3222
| 2769 | 1647.5263 | 0.080255 | 1647.4461
| 2770 | 1256.5985 | 8.0999 | 1248.4986
| 2771 | 707.8218 | 62.9302 | 644.8916
| 2772 | 203.0788 | 278.7632 | -75.6843
| 2773 | 86.5635 | 618.3027 | -531.7392
| 2774 | 29.2289 | 1073.3294 | -1044.1006
| 2775 | 5.7441 | 1702.2805 | -1696.5364
| 2776 | 0.10267 | 2374.8575 | -2374.7548
| 2777 | 0 | 2427.4867 | -2427.4867
| 2778 | 0 | 1086.0023 | -1086.0023
| 2779 | 0.71837 | 312.7473 | -312.0289
| 2780 | 9.4304 | 180.4981 | -171.0678
| 2781 | 25.7322 | 123.8747 | -98.1425
| 2782 | 49.9208 | 0 | 49.9208
| 2783 | 78.7053 | 0 | 78.7053
| 2784 | 106.0286 | 0 | 106.0286
| 2785 | 137.9471 | 0 | 137.9471
| 2786 | 164.3776 | 0 | 164.3776
| 2787 | 180.7075 | 0 | 180.7075
| 2788 | 191.1233 | 0 | 191.1233
| 2789 | 203.2189 | 0 | 203.2189
| 2790 | 2947.612 | 81.1224 | 2866.4896
| 2791 | 1921.85 | 0 | 1921.85
| 2792 | 1225.1103 | 20.8768 | 1204.2335
| 2793 | 203.7283 | 80.7027 | 123.0256
| 2794 | 4.1957 | 476.0063 | -471.8106
| 2795 | 0 | 1766.6185 | -1766.6185
| 2796 | 0 | 3349.4708 | -3349.4708
| 2797 | 0 | 4828.9097 | -4828.9097
| 2798 | 0 | 5795.8126 | -5795.8126
| 2799 | 0 | 4516.864 | -4516.864
| 2800 | 0 | 4216.0054 | -4216.0054
| 2801 | 0 | 4921.6721 | -4921.6721
| 2802 | 0 | 2819.3172 | -2819.3172
| 2803 | 0 | 1486.1367 | -1486.1367
| 2804 | 0 | 929.7813 | -929.7813
| 2805 | 0 | 211.1293 | -211.1293
| 2806 | 0 | 40.2532 | -40.2532
| 2807 | 0 | 2.2337 | -2.2337
| 2808 | 1.4385 | 0 | 1.4385
| 2809 | 14.9204 | 0 | 14.9204
| 2810 | 46.6486 | 0 | 46.6486
| 2811 | 89.3852 | 0 | 89.3852
| 2812 | 135.1877 | 0 | 135.1877
| 2813 | 176.3321 | 0 | 176.3321
| 2814 | 199.1311 | 0 | 199.1311
| 2815 | 202.3044 | 0 | 202.3044
| 2816 | 3855.0492 | 0 | 3855.0492
| 2817 | 2729.2229 | 0 | 2729.2229
| 2818 | 2160.0479 | 0 | 2160.0479
| 2819 | 1787.0035 | 0 | 1787.0035
| 2820 | 1162.1742 | 0 | 1162.1742
| 2821 | 706.6165 | 0 | 706.6165
| 2822 | 523.8162 | 0 | 523.8162
| 2823 | 279.4789 | 0 | 279.4789
| 2824 | 112.4198 | 0 | 112.4198
| 2825 | 865.0218 | 0 | 865.0218
| 2826 | 1301.336 | 0 | 1301.336
| 2827 | 82.5157 | 0 | 82.5157
| 2828 | 147.532 | 0 | 147.532
| 2829 | 204.9074 | 0 | 204.9074
| 2830 | 273.3268 | 0 | 273.3268
| 2831 | 344.5627 | 0 | 344.5627
| 2832 | 409.9443 | 0 | 409.9443
| 2833 | 462.0366 | 0 | 462.0366
| 2834 | 536.1198 | 0 | 536.1198
| 2835 | 562.6474 | 0 | 562.6474
| 2836 | 561.3126 | 0 | 561.3126
| 2837 | 564.1251 | 0 | 564.1251
| 2838 | 6270.7923 | 0 | 6270.7923
| 2839 | 4460.167 | 0 | 4460.167
| 2840 | 3376.4735 | 0 | 3376.4735
| 2841 | 2230.4341 | 0 | 2230.4341
| 2842 | 1611.122 | 0 | 1611.122
| 2843 | 1003.7509 | 0 | 1003.7509
| 2844 | 814.4222 | 0 | 814.4222
| 2845 | 487.8058 | 12.6518 | 475.1539
| 2846 | 217.105 | 52.2626 | 164.8424
| 2847 | 148.4064 | 121.3129 | 27.0936
| 2848 | 113.7038 | 154.9361 | -41.2323
| 2849 | 88.8859 | 118.4657 | -29.5798
| 2850 | 84.6495 | 35.137 | 49.5124
| 2851 | 144.3057 | 19.6092 | 124.6966
| 2852 | 415.2648 | 0 | 415.2648
| 2853 | 177.3105 | 0 | 177.3105
| 2854 | 229.742 | 0 | 229.742
| 2855 | 268.6754 | 0 | 268.6754
| 2856 | 280.0595 | 0 | 280.0595
| 2857 | 282.2744 | 0 | 282.2744
| 2858 | 289.3054 | 0 | 289.3054
| 2859 | 298.6416 | 0 | 298.6416
| 2860 | 318.9627 | 0 | 318.9627
| 2861 | 363.3765 | 0 | 363.3765
| 2862 | 4132.6877 | 48.8955 | 4083.7922
| 2863 | 3038.6693 | 0 | 3038.6693
| 2864 | 2341.838 | 11.1467 | 2330.6913
| 2865 | 1392.3485 | 53.0295 | 1339.319
| 2866 | 838.9593 | 129.7901 | 709.1692
| 2867 | 298.9338 | 227.512 | 71.4218
| 2868 | 142.2735 | 370.5 | -228.2264
| 2869 | 81.4135 | 613.8323 | -532.4188
| 2870 | 53.3179 | 784.5792 | -731.2613
| 2871 | 19.6569 | 1007.7001 | -988.0433
| 2872 | 5.8047 | 1185.2965 | -1179.4918
| 2873 | 0.75813 | 1071.2547 | -1070.4966
| 2874 | 0.43807 | 326.067 | -325.6289
| 2875 | 6.1245 | 236.5588 | -230.4343
| 2876 | 15.2591 | 148.19 | -132.9309
| 2877 | 26.2748 | 112.0289 | -85.7541
| 2878 | 43.2998 | 0 | 43.2998
| 2879 | 53.9823 | 0 | 53.9823
| 2880 | 66.256 | 0 | 66.256
| 2881 | 72.6534 | 0 | 72.6534
| 2882 | 76.6424 | 0 | 76.6424
| 2883 | 77.2687 | 0 | 77.2687
| 2884 | 73.187 | 0 | 73.187
| 2885 | 85.9298 | 0 | 85.9298
| 2886 | 1639.5631 | 93.0554 | 1546.5077
| 2887 | 1310.5766 | 1.6114 | 1308.9651
| 2888 | 712.1073 | 201.5389 | 510.5684
| 2889 | 51.3115 | 471.2271 | -419.9155
| 2890 | 30.1148 | 731.2593 | -701.1445
| 2891 | 53.7959 | 817.9397 | -764.1438
| 2892 | 78.6245 | 858.3884 | -779.7639
| 2893 | 86.4646 | 930.8957 | -844.4311
| 2894 | 82.8298 | 1068.7389 | -985.9092
| 2895 | 56.4188 | 961.74 | -905.3212
| 2896 | 33.0207 | 820.5366 | -787.5159
| 2897 | 29.3786 | 624.716 | -595.3374
| 2898 | 24.3717 | 298.4105 | -274.0387
| 2899 | 49.3758 | 238.7601 | -189.3843
| 2900 | 238.1701 | 132.2099 | 105.9602
| 2901 | 96.7079 | 93.2118 | 3.4961
| 2902 | 122.7539 | 0 | 122.7539
| 2903 | 191.3105 | 0 | 191.3105
| 2904 | 279.3831 | 0 | 279.3831
| 2905 | 339.339 | 0 | 339.339
| 2906 | 400.5476 | 0 | 400.5476
| 2907 | 425.3217 | 0 | 425.3217
| 2908 | 444.4919 | 0 | 444.4919
| 2909 | 462.7503 | 0 | 462.7503
| 2910 | 4906.6432 | 26.9375 | 4879.7058
| 2911 | 3259.0992 | 0 | 3259.0992
| 2912 | 2330.9817 | 11.4535 | 2319.5281
| 2913 | 1075.736 | 88.7106 | 987.0254
| 2914 | 283.0764 | 309.66 | -26.5835
| 2915 | 79.6045 | 586.4419 | -506.8374
| 2916 | 31.7683 | 801.359 | -769.5907
| 2917 | 14.2824 | 1123.7177 | -1109.4353
| 2918 | 8.1964 | 1509.3789 | -1501.1825
| 2919 | 6.8748 | 1583.3821 | -1576.5073
| 2920 | 9.0342 | 1167.5999 | -1158.5657
| 2921 | 14.5089 | 542.8243 | -528.3155
| 2922 | 28.4609 | 225.6224 | -197.1615
| 2923 | 59.919 | 175.0691 | -115.1501
| 2924 | 222.126 | 77.8357 | 144.2903
| 2925 | 125.8062 | 43.5281 | 82.2781
| 2926 | 179.9715 | 0 | 179.9715
| 2927 | 239.3047 | 0 | 239.3047
| 2928 | 296.2793 | 0 | 296.2793
| 2929 | 344.2421 | 0 | 344.2421
| 2930 | 388.1328 | 0 | 388.1328
| 2931 | 430.8686 | 0 | 430.8686
| 2932 | 459.3663 | 0 | 459.3663
| 2933 | 449.604 | 0 | 449.604
| 2934 | 4694.4703 | 37.7671 | 4656.7032
| 2935 | 3349.1373 | 0 | 3349.1373
| 2936 | 2721.3965 | 0 | 2721.3965
| 2937 | 2012.8374 | 1.5797 | 2011.2577
| 2938 | 1704.4936 | 14.5279 | 1689.9657
| 2939 | 1300.9736 | 51.8472 | 1249.1264
| 2940 | 1032.9894 | 80.4117 | 952.5778
| 2941 | 790.6229 | 227.6168 | 563.0061
| 2942 | 504.7863 | 414.5665 | 90.2199
| 2943 | 260.1247 | 418.6512 | -158.5265
| 2944 | 175.5979 | 422.7961 | -247.1982
| 2945 | 138.9671 | 398.7839 | -259.8167
| 2946 | 123.6903 | 213.153 | -89.4627
| 2947 | 492.0437 | 161.821 | 330.2227
| 2948 | 1014.5094 | 63.8801 | 950.6293
| 2949 | 318.2497 | 38.8544 | 279.3953
| 2950 | 465.9358 | 0 | 465.9358
| 2951 | 620.9175 | 0 | 620.9175
| 2952 | 754.1939 | 0 | 754.1939
| 2953 | 842.1496 | 0 | 842.1496
| 2954 | 922.6516 | 0 | 922.6516
| 2955 | 993.9917 | 0 | 993.9917
| 2956 | 1070.9577 | 0 | 1070.9577
| 2957 | 1111.1328 | 0 | 1111.1328
| 2958 | 8259.1432 | 0 | 8259.1432
| 2959 | 4909.6016 | 0 | 4909.6016
| 2960 | 3230.7308 | 1.4209 | 3229.3099
| 2961 | 1700.4339 | 17.1463 | 1683.2876
| 2962 | 731.4325 | 22.1683 | 709.2641
| 2963 | 228.9769 | 26.4113 | 202.5656
| 2964 | 140.7468 | 35.5892 | 105.1576
| 2965 | 81.0766 | 48.5586 | 32.518
| 2966 | 40.0979 | 63.8846 | -23.7867
| 2967 | 12.788 | 320.6566 | -307.8686
| 2968 | 3.7017 | 550.1561 | -546.4543
| 2969 | 1.6165 | 345.1986 | -343.5821
| 2970 | 2.5667 | 0 | 2.5667
| 2971 | 15.6509 | 0 | 15.6509
| 2972 | 137.0263 | 0 | 137.0263
| 2973 | 619.5444 | 0 | 619.5444
| 2974 | 122.3687 | 0 | 122.3687
| 2975 | 205.0217 | 0 | 205.0217
| 2976 | 262.7885 | 0 | 262.7885
| 2977 | 286.0765 | 0 | 286.0765
| 2978 | 291.7305 | 0 | 291.7305
| 2979 | 282.5466 | 0 | 282.5466
| 2980 | 316.6485 | 0 | 316.6485
| 2981 | 341.0237 | 0 | 341.0237
| 2982 | 332.3309 | 0 | 332.3309
| 2983 | 299.1007 | 0 | 299.1007
| 2984 | 3241.6165 | 0 | 3241.6165
| 2985 | 2001.5892 | 0 | 2001.5892
| 2986 | 1152.2221 | 0 | 1152.2221
| 2987 | 469.4617 | 0 | 469.4617
| 2988 | 21.5868 | 0 | 21.5868
| 2989 | 4.9336 | 0 | 4.9336
| 2990 | 1.4687 | 0 | 1.4687
| 2991 | 6.7933 | 0 | 6.7933
| 2992 | 15.4734 | 0 | 15.4734
| 2993 | 162.7566 | 0 | 162.7566
| 2994 | 575.4656 | 0 | 575.4656
| 2995 | 22.4012 | 0 | 22.4012
| 2996 | 38.34 | 0 | 38.34
| 2997 | 36.1028 | 0 | 36.1028
| 2998 | 52.1352 | 0 | 52.1352
| 2999 | 120.82 | 0 | 120.82
| 3000 | 147.3924 | 0 | 147.3924
| 3001 | 130.1933 | 0 | 130.1933
| 3002 | 155.7583 | 0 | 155.7583
| 3003 | 206.135 | 0 | 206.135
| 3004 | 246.6082 | 0 | 246.6082
| 3005 | 309.6596 | 0 | 309.6596
| 3006 | 4099.2758 | 35.7438 | 4063.532
| 3007 | 3041.9785 | 0 | 3041.9785
| 3008 | 2354.9409 | 0 | 2354.9409
| 3009 | 1672.6366 | 0 | 1672.6366
| 3010 | 1395.972 | 0.57142 | 1395.4006
| 3011 | 1087.2835 | 10.4077 | 1076.8759
| 3012 | 873.8172 | 18.2167 | 855.6006
| 3013 | 722.2124 | 99.7299 | 622.4824
| 3014 | 562.9208 | 152.788 | 410.1328
| 3015 | 467.6088 | 177.7019 | 289.9069
| 3016 | 432.3766 | 182.2567 | 250.1199
| 3017 | 479.3252 | 112.8847 | 366.4405
| 3018 | 785.1158 | 13.0848 | 772.0311
| 3019 | 1045.2193 | 3.2065 | 1042.0128
| 3020 | 1229.6967 | 0 | 1229.6967
| 3021 | 288.5082 | 0 | 288.5082
| 3022 | 300.2602 | 0 | 300.2602
| 3023 | 307.1437 | 0 | 307.1437
| 3024 | 309.8321 | 0 | 309.8321
| 3025 | 299.4007 | 0 | 299.4007
| 3026 | 296.3681 | 0 | 296.3681
| 3027 | 302.7448 | 0 | 302.7448
| 3028 | 307.2278 | 0 | 307.2278
| 3029 | 327.6728 | 0 | 327.6728
| 3030 | 3812.2905 | 49.8539 | 3762.4366
| 3031 | 2683.6365 | 0 | 2683.6365
| 3032 | 1961.4098 | 0.45065 | 1960.9591
| 3033 | 1008.1296 | 36.0881 | 972.0415
| 3034 | 370.9303 | 130.2752 | 240.6551
| 3035 | 115.3482 | 285.1913 | -169.8431
| 3036 | 57.2241 | 436.9403 | -379.7162
| 3037 | 32.719 | 732.3869 | -699.6679
| 3038 | 20.9317 | 1005.2101 | -984.2784
| 3039 | 14.0102 | 1142.9575 | -1128.9473
| 3040 | 6.5921 | 1112.1413 | -1105.5492
| 3041 | 2.0186 | 906.4347 | -904.4161
| 3042 | 1.2905 | 295.7795 | -294.4891
| 3043 | 12.2077 | 241.2738 | -229.0661
| 3044 | 37.8595 | 129.6344 | -91.7749
| 3045 | 77.7849 | 75.1187 | 2.6663
| 3046 | 149.6038 | 0 | 149.6038
| 3047 | 195.9436 | 0 | 195.9436
| 3048 | 237.0441 | 0 | 237.0441
| 3049 | 293.0082 | 0 | 293.0082
| 3050 | 345.8141 | 0 | 345.8141
| 3051 | 390.6521 | 0 | 390.6521
| 3052 | 454.5448 | 0 | 454.5448
| 3053 | 542.1014 | 0 | 542.1014
| 3054 | 5678.3645 | 0 | 5678.3645
| 3055 | 4035.4434 | 0 | 4035.4434
| 3056 | 3138.2387 | 42.1254 | 3096.1133
| 3057 | 2151.6865 | 114.5681 | 2037.1183
| 3058 | 1608.5522 | 157.8325 | 1450.7197
| 3059 | 1031.5488 | 156.9997 | 874.5491
| 3060 | 517.1488 | 238.4561 | 278.6927
| 3061 | 299.1847 | 390.5321 | -91.3474
| 3062 | 220.6741 | 495.3731 | -274.699
| 3063 | 181.2423 | 483.2479 | -302.0056
| 3064 | 142.7556 | 457.9126 | -315.157
| 3065 | 132.2657 | 414.1876 | -281.9219
| 3066 | 171.9058 | 223.9231 | -52.0173
| 3067 | 523.8816 | 166.385 | 357.4965
| 3068 | 1122.2505 | 60.7385 | 1061.5121
| 3069 | 342.2715 | 32.9904 | 309.2811
| 3070 | 448.665 | 0 | 448.665
| 3071 | 551.0888 | 0 | 551.0888
| 3072 | 670.8113 | 0 | 670.8113
| 3073 | 784.2144 | 0 | 784.2144
| 3074 | 862.7829 | 0 | 862.7829
| 3075 | 968.6142 | 0 | 968.6142
| 3076 | 1037.5075 | 0 | 1037.5075
| 3077 | 1090.1034 | 0 | 1090.1034
| 3078 | 9185.5084 | 0 | 9185.5084
| 3079 | 6003.8559 | 0 | 6003.8559
| 3080 | 3803.0629 | 2.1456 | 3800.9173
| 3081 | 2075.044 | 21.477 | 2053.567
| 3082 | 1249.2109 | 68.8811 | 1180.3298
| 3083 | 448.1497 | 119.5057 | 328.644
| 3084 | 174.6056 | 210.4102 | -35.8046
| 3085 | 109.7488 | 418.6565 | -308.9076
| 3086 | 70.364 | 603.4694 | -533.1054
| 3087 | 21.2321 | 993.8444 | -972.6123
| 3088 | 1.7862 | 1645.4091 | -1643.6229
| 3089 | 0 | 1796.5272 | -1796.5272
| 3090 | 0 | 1044.5392 | -1044.5392
| 3091 | 0 | 471.5215 | -471.5215
| 3092 | 0.61674 | 179.8001 | -179.1834
| 3093 | 8.0576 | 124.8127 | -116.7551
| 3094 | 31.0722 | 0 | 31.0722
| 3095 | 78.2459 | 0 | 78.2459
| 3096 | 124.9394 | 0 | 124.9394
| 3097 | 149.4944 | 0 | 149.4944
| 3098 | 181.036 | 0 | 181.036
| 3099 | 206.3791 | 0 | 206.3791
| 3100 | 217.4393 | 0 | 217.4393
| 3101 | 216.1996 | 0 | 216.1996
| 3102 | 2726.5175 | 81.1224 | 2645.3951
| 3103 | 1509.2589 | 20.6585 | 1488.6004
| 3104 | 559.3458 | 371.8084 | 187.5374
| 3105 | 8.5057 | 1286.7854 | -1278.2797
| 3106 | 0 | 3027.2113 | -3027.2113
| 3107 | 0 | 5025.997 | -5025.997
| 3108 | 0 | 6212.1608 | -6212.1608
| 3109 | 0 | 7288.4527 | -7288.4527
| 3110 | 0 | 8078.9359 | -8078.9359
| 3111 | 0 | 8358.0198 | -8358.0198
| 3112 | 0 | 8123.7729 | -8123.7729
| 3113 | 0 | 7326.2356 | -7326.2356
| 3114 | 0 | 4840.6763 | -4840.6763
| 3115 | 0 | 4118.6063 | -4118.6063
| 3116 | 0 | 3241.7378 | -3241.7378
| 3117 | 0 | 1430.5719 | -1430.5719
| 3118 | 0 | 245.3439 | -245.3439
| 3119 | 0 | 129.5086 | -129.5086
| 3120 | 0 | 17.4463 | -17.4463
| 3121 | 0 | 0.078906 | -0.078906
| 3122 | 0.66111 | 0 | 0.66111
| 3123 | 7.5526 | 0 | 7.5526
| 3124 | 17.1675 | 0 | 17.1675
| 3125 | 26.3077 | 0 | 26.3077
| 3126 | 1355.6215 | 149.6541 | 1205.9674
| 3127 | 602.979 | 130.8423 | 472.1367
| 3128 | 14.9845 | 635.8492 | -620.8648
| 3129 | 0 | 1382.2042 | -1382.2042
| 3130 | 0 | 3359.1448 | -3359.1448
| 3131 | 0 | 4894.747 | -4894.747
| 3132 | 0 | 5903.1011 | -5903.1011
| 3133 | 0 | 6573.3594 | -6573.3594
| 3134 | 0 | 6826.4083 | -6826.4083
| 3135 | 0 | 7128.7143 | -7128.7143
| 3136 | 0 | 7553.9651 | -7553.9651
| 3137 | 0 | 7323.5025 | -7323.5025
| 3138 | 0 | 4895.6198 | -4895.6198
| 3139 | 0 | 3529.3801 | -3529.3801
| 3140 | 0 | 2028.3736 | -2028.3736
| 3141 | 0 | 717.9491 | -717.9491
| 3142 | 0 | 308.2009 | -308.2009
| 3143 | 0 | 102.7826 | -102.7826
| 3144 | 0 | 21.5624 | -21.5624
| 3145 | 1.9453 | 0.4949 | 1.4504
| 3146 | 7.2912 | 0 | 7.2912
| 3147 | 8.8503 | 0 | 8.8503
| 3148 | 23.3675 | 0 | 23.3675
| 3149 | 34.4519 | 0 | 34.4519
| 3150 | 33.3747 | 0 | 33.3747
| 3151 | 24.1632 | 0 | 24.1632
| 3152 | 1832.6209 | 0 | 1832.6209
| 3153 | 814.0774 | 0 | 814.0774
| 3154 | 60.6363 | 0 | 60.6363
| 3155 | 0 | 163.5914 | -163.5914
| 3156 | 0 | 1237.209 | -1237.209
| 3157 | 0 | 2171.5199 | -2171.5199
| 3158 | 0 | 3461.6972 | -3461.6972
| 3159 | 0 | 4135.1541 | -4135.1541
| 3160 | 0 | 4486.9726 | -4486.9726
| 3161 | 0 | 4843.1945 | -4843.1945
| 3162 | 0 | 3225.1494 | -3225.1494
| 3163 | 0 | 1119.6555 | -1119.6555
| 3164 | 0 | 843.7119 | -843.7119
| 3165 | 0 | 478.27 | -478.27
| 3166 | 0 | 263.0048 | -263.0048
| 3167 | 0 | 135.9424 | -135.9424
| 3168 | 0 | 53.4091 | -53.4091
| 3169 | 0 | 21.351 | -21.351
| 3170 | 0 | 13.0074 | -13.0074
| 3171 | 0 | 6.4457 | -6.4457
| 3172 | 0 | 0.37171 | -0.37171
| 3173 | 0 | 0 | 0
| 3174 | 675.0887 | 396.865 | 278.2237
| 3175 | 236.1535 | 326.9201 | -90.7667
| 3176 | 0 | 2689.1051 | -2689.1051
| 3177 | 0 | 3963.9398 | -3963.9398
| 3178 | 0 | 6727.176 | -6727.176
| 3179 | 0 | 9366.818 | -9366.818
| 3180 | 0 | 11130.2518 | -11130.2518
| 3181 | 0 | 12488.3864 | -12488.3864
| 3182 | 0 | 13480.5017 | -13480.5017
| 3183 | 0 | 13801.0861 | -13801.0861
| 3184 | 0 | 13278.0252 | -13278.0252
| 3185 | 0 | 12748.8459 | -12748.8459
| 3186 | 0 | 8214.3479 | -8214.3479
| 3187 | 0 | 6344.638 | -6344.638
| 3188 | 0 | 4467.8203 | -4467.8203
| 3189 | 0 | 1920.8804 | -1920.8804
| 3190 | 0 | 487.1268 | -487.1268
| 3191 | 0 | 267.8724 | -267.8724
| 3192 | 0 | 135.898 | -135.898
| 3193 | 0 | 51.9308 | -51.9308
| 3194 | 0.18115 | 4.4845 | -4.3033
| 3195 | 5.2295 | 0 | 5.2295
| 3196 | 12.1313 | 0 | 12.1313
| 3197 | 18.8372 | 0 | 18.8372
| 3198 | 1559.5233 | 206.8217 | 1352.7016
| 3199 | 1026.2902 | 199.2546 | 827.0356
| 3200 | 326.3937 | 997.5816 | -671.1878
| 3201 | 1.1304 | 1990.5845 | -1989.454
| 3202 | 0 | 2977.4726 | -2977.4726
| 3203 | 0 | 3607.2769 | -3607.2769
| 3204 | 0 | 4509.8681 | -4509.8681
| 3205 | 0 | 5464.9198 | -5464.9198
| 3206 | 0 | 5995.7794 | -5995.7794
| 3207 | 0 | 6010.258 | -6010.258
| 3208 | 0 | 5467.4581 | -5467.4581
| 3209 | 0 | 4609.2861 | -4609.2861
| 3210 | 0 | 1811.9643 | -1811.9643
| 3211 | 0 | 654.4076 | -654.4076
| 3212 | 0 | 380.4787 | -380.4787
| 3213 | 1.68 | 267.1847 | -265.5048
| 3214 | 12.1472 | 0 | 12.1472
| 3215 | 25.6432 | 0 | 25.6432
| 3216 | 38.3881 | 0 | 38.3881
| 3217 | 48.1636 | 0 | 48.1636
| 3218 | 52.6928 | 0 | 52.6928
| 3219 | 74.6858 | 0 | 74.6858
| 3220 | 101.6215 | 0 | 101.6215
| 3221 | 115.3196 | 0 | 115.3196
| 3222 | 3080.194 | 109.8875 | 2970.3065
| 3223 | 2089.423 | 1.6595 | 2087.7635
| 3224 | 1372.8135 | 189.666 | 1183.1475
| 3225 | 285.2527 | 611.9657 | -326.713
| 3226 | 30.2935 | 928.2941 | -898.0006
| 3227 | 16.0495 | 1067.1832 | -1051.1337
| 3228 | 5.1599 | 1465.7636 | -1460.6037
| 3229 | 0.67302 | 2315.3819 | -2314.7088
| 3230 | 0 | 3018.8829 | -3018.8829
| 3231 | 0 | 3138.8457 | -3138.8457
| 3232 | 0 | 2683.0716 | -2683.0716
| 3233 | 0 | 2341.4502 | -2341.4502
| 3234 | 0 | 856.3211 | -856.3211
| 3235 | 0 | 413.5995 | -413.5995
| 3236 | 0.63082 | 276.8397 | -276.2089
| 3237 | 4.5736 | 211.2884 | -206.7148
| 3238 | 13.7766 | 0 | 13.7766
| 3239 | 25.6827 | 0 | 25.6827
| 3240 | 45.127 | 0 | 45.127
| 3241 | 70.7581 | 0 | 70.7581
| 3242 | 94.6356 | 0 | 94.6356
| 3243 | 123.9144 | 0 | 123.9144
| 3244 | 148.9285 | 0 | 148.9285
| 3245 | 158.0775 | 0 | 158.0775
| 3246 | 2987.3364 | 97.3243 | 2890.0121
| 3247 | 2038.5776 | 0.1052 | 2038.4724
| 3248 | 1454.94 | 116.3932 | 1338.5469
| 3249 | 589.5678 | 411.9619 | 177.6058
| 3250 | 166.2537 | 738.7136 | -572.4599
| 3251 | 42.8952 | 985.5052 | -942.6099
| 3252 | 20.4219 | 1060.821 | -1040.3991
| 3253 | 16.2957 | 1278.8811 | -1262.5854
| 3254 | 12.4527 | 1533.4141 | -1520.9614
| 3255 | 2.4884 | 2342.0375 | -2339.5491
| 3256 | 0.60666 | 2063.9075 | -2063.3009
| 3257 | 4.7835 | 848.3009 | -843.5174
| 3258 | 8.4424 | 320.3603 | -311.9179
| 3259 | 10.7726 | 295.476 | -284.7034
| 3260 | 17.0727 | 188.3956 | -171.3229
| 3261 | 19.2111 | 154.9302 | -135.7192
| 3262 | 25.7454 | 0 | 25.7454
| 3263 | 37.3362 | 0 | 37.3362
| 3264 | 62.4882 | 0 | 62.4882
| 3265 | 89.3312 | 0 | 89.3312
| 3266 | 97.5582 | 0 | 97.5582
| 3267 | 111.8323 | 0 | 111.8323
| 3268 | 126.9452 | 0 | 126.9452
| 3269 | 114.9304 | 0 | 114.9304
| 3270 | 1860.6377 | 85.4432 | 1775.1945
| 3271 | 1406.5327 | 4.8314 | 1401.7013
| 3272 | 800.3056 | 388.6497 | 411.6559
| 3273 | 101.749 | 876.8296 | -775.0806
| 3274 | 44.1859 | 1129.6919 | -1085.5059
| 3275 | 23.2959 | 1186.1573 | -1162.8614
| 3276 | 6.5091 | 1959.9577 | -1953.4486
| 3277 | 0.032579 | 3236.3142 | -3236.2816
| 3278 | 0 | 4272.4078 | -4272.4078
| 3279 | 0 | 4960.6308 | -4960.6308
| 3280 | 0 | 5433.3608 | -5433.3608
| 3281 | 0 | 5020.4646 | -5020.4646
| 3282 | 0 | 2979.2504 | -2979.2504
| 3283 | 0 | 1913.112 | -1913.112
| 3284 | 0 | 599.9376 | -599.9376
| 3285 | 0 | 312.0491 | -312.0491
| 3286 | 3.2691 | 0 | 3.2691
| 3287 | 14.3606 | 0 | 14.3606
| 3288 | 24.962 | 0 | 24.962
| 3289 | 34.1905 | 0 | 34.1905
| 3290 | 52.9657 | 0 | 52.9657
| 3291 | 82.6569 | 0 | 82.6569
| 3292 | 134.9192 | 0 | 134.9192
| 3293 | 179.8322 | 0 | 179.8322
| 3294 | 3180.3294 | 78.2099 | 3102.1195
| 3295 | 2489.8572 | 0 | 2489.8572
| 3296 | 2281.4611 | 0 | 2281.4611
| 3297 | 1798.3612 | 0 | 1798.3612
| 3298 | 1172.0702 | 1.5395 | 1170.5307
| 3299 | 382.1977 | 28.7363 | 353.4614
| 3300 | 105.0951 | 86.169 | 18.9261
| 3301 | 52.1932 | 147.6479 | -95.4548
| 3302 | 29.7 | 101.8425 | -72.1425
| 3303 | 15.2852 | 139.2017 | -123.9165
| 3304 | 4.84 | 393.6825 | -388.8424
| 3305 | 2.0171 | 278.4649 | -276.4478
| 3306 | 3.279 | 0 | 3.279
| 3307 | 32.7556 | 0 | 32.7556
| 3308 | 358.9722 | 0 | 358.9722
| 3309 | 1091.7726 | 0 | 1091.7726
| 3310 | 171.1924 | 0 | 171.1924
| 3311 | 236.2896 | 0 | 236.2896
| 3312 | 295.0564 | 0 | 295.0564
| 3313 | 335.1551 | 0 | 335.1551
| 3314 | 386.2552 | 0 | 386.2552
| 3315 | 437.0638 | 0 | 437.0638
| 3316 | 464.2755 | 0 | 464.2755
| 3317 | 472.7927 | 0 | 472.7927
| 3318 | 484.9229 | 0 | 484.9229
| 3319 | 479.3565 | 0 | 479.3565
| 3320 | 4978.7997 | 0 | 4978.7997
| 3321 | 3171.7298 | 0 | 3171.7298
| 3322 | 2335.8118 | 0 | 2335.8118
| 3323 | 1698.6157 | 0 | 1698.6157
| 3324 | 954.0147 | 0 | 954.0147
| 3325 | 700.2609 | 0 | 700.2609
| 3326 | 407.4348 | 0 | 407.4348
| 3327 | 181.2216 | 0 | 181.2216
| 3328 | 161.6977 | 0 | 161.6977
| 3329 | 896.1534 | 0 | 896.1534
| 3330 | 1206.9665 | 0 | 1206.9665
| 3331 | 100.0763 | 0 | 100.0763
| 3332 | 152.9127 | 0 | 152.9127
| 3333 | 189.2853 | 0 | 189.2853
| 3334 | 222.917 | 0 | 222.917
| 3335 | 284.4058 | 0 | 284.4058
| 3336 | 353.246 | 0 | 353.246
| 3337 | 374.9414 | 0 | 374.9414
| 3338 | 397.7985 | 0 | 397.7985
| 3339 | 408.7747 | 0 | 408.7747
| 3340 | 382.3656 | 0 | 382.3656
| 3341 | 356.8738 | 0 | 356.8738
| 3342 | 3975.0054 | 31.4202 | 3943.5852
| 3343 | 2223.6924 | 0 | 2223.6924
| 3344 | 1015.3431 | 47.7283 | 967.6148
| 3345 | 44.2467 | 156.9228 | -112.6761
| 3346 | 2.3304 | 962.3947 | -960.0642
| 3347 | 0 | 2962.311 | -2962.311
| 3348 | 0 | 5038.2202 | -5038.2202
| 3349 | 0 | 6760.4248 | -6760.4248
| 3350 | 0 | 7585.8904 | -7585.8904
| 3351 | 0 | 7495.6588 | -7495.6588
| 3352 | 0 | 7337.2844 | -7337.2844
| 3353 | 0 | 6884.8697 | -6884.8697
| 3354 | 0 | 4654.8368 | -4654.8368
| 3355 | 0 | 3778.2368 | -3778.2368
| 3356 | 0 | 2749.4106 | -2749.4106
| 3357 | 0 | 1220.2749 | -1220.2749
| 3358 | 0 | 127.0122 | -127.0122
| 3359 | 0 | 43.3967 | -43.3967
| 3360 | 0 | 2.1484 | -2.1484
| 3361 | 0 | 0 | 0
| 3362 | 2.3087 | 0 | 2.3087
| 3363 | 14.0594 | 0 | 14.0594
| 3364 | 21.7911 | 0 | 21.7911
| 3365 | 23.0203 | 0 | 23.0203
| 3366 | 1511.5679 | 115.2655 | 1396.3024
| 3367 | 551.2063 | 113.2145 | 437.9918
| 3368 | 8.743 | 1440.6997 | -1431.9568
| 3369 | 0 | 2158.79 | -2158.79
| 3370 | 0 | 2886.0509 | -2886.0509
| 3371 | 0 | 3035.3204 | -3035.3204
| 3372 | 0 | 2350.4661 | -2350.4661
| 3373 | 0.15776 | 1825.4312 | -1825.2734
| 3374 | 0.43675 | 1886.4151 | -1885.9784
| 3375 | 0 | 2556.9975 | -2556.9975
| 3376 | 0 | 2706.949 | -2706.949
| 3377 | 0 | 2710.0143 | -2710.0143
| 3378 | 0 | 1837.6285 | -1837.6285
| 3379 | 0 | 1039.8327 | -1039.8327
| 3380 | 0.035931 | 284.6563 | -284.6203
| 3381 | 0.52689 | 219.0374 | -218.5105
| 3382 | 5.7771 | 0 | 5.7771
| 3383 | 26.5005 | 0 | 26.5005
| 3384 | 58.3768 | 0 | 58.3768
| 3385 | 90.9659 | 0 | 90.9659
| 3386 | 139.0068 | 0 | 139.0068
| 3387 | 207.2088 | 0 | 207.2088
| 3388 | 271.8441 | 0 | 271.8441
| 3389 | 318.2876 | 0 | 318.2876
| 3390 | 4406.316 | 24.4289 | 4381.8871
| 3391 | 2428.415 | 19.2319 | 2409.1831
| 3392 | 1314.7831 | 239.0846 | 1075.6985
| 3393 | 207.6277 | 611.6894 | -404.0616
| 3394 | 22.0731 | 1062.0099 | -1039.9369
| 3395 | 3.545 | 1590.4576 | -1586.9126
| 3396 | 0.11331 | 2793.5864 | -2793.4731
| 3397 | 0 | 3885.7393 | -3885.7393
| 3398 | 0 | 5225.8647 | -5225.8647
| 3399 | 0 | 5542.3394 | -5542.3394
| 3400 | 0 | 5267.8701 | -5267.8701
| 3401 | 0 | 4976.0735 | -4976.0735
| 3402 | 0 | 2587.1494 | -2587.1494
| 3403 | 0 | 1154.6712 | -1154.6712
| 3404 | 0.41506 | 314.5704 | -314.1553
| 3405 | 4.3829 | 230.9038 | -226.5209
| 3406 | 15.8749 | 0 | 15.8749
| 3407 | 40.1959 | 0 | 40.1959
| 3408 | 70.3826 | 0 | 70.3826
| 3409 | 100.4389 | 0 | 100.4389
| 3410 | 163.0271 | 0 | 163.0271
| 3411 | 231.9254 | 0 | 231.9254
| 3412 | 301.2968 | 0 | 301.2968
| 3413 | 341.412 | 0 | 341.412
| 3414 | 4409.8677 | 39.1432 | 4370.7245
| 3415 | 2651.1126 | 1.8574 | 2649.2552
| 3416 | 1643.2605 | 164.0319 | 1479.2286
| 3417 | 352.8738 | 584.1211 | -231.2473
| 3418 | 22.8043 | 1100.2555 | -1077.4513
| 3419 | 1.4331 | 2016.8999 | -2015.4668
| 3420 | 0 | 3349.2154 | -3349.2154
| 3421 | 0 | 4846.4957 | -4846.4957
| 3422 | 0 | 5763.1145 | -5763.1145
| 3423 | 0 | 6099.1993 | -6099.1993
| 3424 | 0 | 5923.3496 | -5923.3496
| 3425 | 0 | 5524.5721 | -5524.5721
| 3426 | 0 | 3627.9914 | -3627.9914
| 3427 | 0 | 2435.1596 | -2435.1596
| 3428 | 0 | 713.5052 | -713.5052
| 3429 | 0.80397 | 289.3728 | -288.5688
| 3430 | 11.5217 | 0 | 11.5217
| 3431 | 31.6397 | 0 | 31.6397
| 3432 | 55.7072 | 0 | 55.7072
| 3433 | 84.7375 | 0 | 84.7375
| 3434 | 141.1636 | 0 | 141.1636
| 3435 | 194.1385 | 0 | 194.1385
| 3436 | 256.0177 | 0 | 256.0177
| 3437 | 307.4677 | 0 | 307.4677
| 3438 | 4115.2352 | 77.3411 | 4037.8941
| 3439 | 2152.0782 | 60.9143 | 2091.1639
| 3440 | 699.7498 | 640.7979 | 58.9519
| 3441 | 8.7814 | 1432.5804 | -1423.799
| 3442 | 0.68006 | 2572.4262 | -2571.7461
| 3443 | 0 | 4416.6655 | -4416.6655
| 3444 | 0 | 5339.0072 | -5339.0072
| 3445 | 0 | 6099.366 | -6099.366
| 3446 | 0 | 6778.3557 | -6778.3557
| 3447 | 0 | 7027.4155 | -7027.4155
| 3448 | 0 | 7146.1968 | -7146.1968
| 3449 | 0 | 6937.3617 | -6937.3617
| 3450 | 0 | 4571.6449 | -4571.6449
| 3451 | 0 | 3637.8609 | -3637.8609
| 3452 | 0 | 1186.0756 | -1186.0756
| 3453 | 0 | 379.1588 | -379.1588
| 3454 | 2.7513 | 0 | 2.7513
| 3455 | 21.4278 | 0 | 21.4278
| 3456 | 38.2718 | 0 | 38.2718
| 3457 | 57.6601 | 0 | 57.6601
| 3458 | 101.579 | 0 | 101.579
| 3459 | 169.2447 | 0 | 169.2447
| 3460 | 235.1664 | 0 | 235.1664
| 3461 | 284.6173 | 0 | 284.6173
| 3462 | 4080.016 | 27.1281 | 4052.8879
| 3463 | 1961.62 | 13.2766 | 1948.3435
| 3464 | 873.4096 | 104.7355 | 768.6741
| 3465 | 10.743 | 264.5668 | -253.8238
| 3466 | 0 | 963.9544 | -963.9544
| 3467 | 0 | 2442.7897 | -2442.7897
| 3468 | 0 | 3345.9505 | -3345.9505
| 3469 | 0 | 4101.9712 | -4101.9712
| 3470 | 0 | 4468.5035 | -4468.5035
| 3471 | 0 | 5042.5334 | -5042.5334
| 3472 | 0 | 5456.7943 | -5456.7943
| 3473 | 0 | 5240.8541 | -5240.8541
| 3474 | 0 | 3192.1974 | -3192.1974
| 3475 | 0 | 2424.2539 | -2424.2539
| 3476 | 0 | 1606.622 | -1606.622
| 3477 | 0 | 588.6929 | -588.6929
| 3478 | 0 | 304.575 | -304.575
| 3479 | 0 | 111.531 | -111.531
| 3480 | 0 | 26.0318 | -26.0318
| 3481 | 0 | 1.1103 | -1.1103
| 3482 | 5.0564 | 0 | 5.0564
| 3483 | 8.9204 | 0 | 8.9204
| 3484 | 9.3179 | 0 | 9.3179
| 3485 | 11.9855 | 0 | 11.9855
| 3486 | 9.336 | 0 | 9.336
| 3487 | 7.2535 | 0 | 7.2535
| 3488 | 1333.8993 | 0 | 1333.8993
| 3489 | 681.2468 | 0 | 681.2468
| 3490 | 199.7657 | 0 | 199.7657
| 3491 | 1.68 | 0 | 1.68
| 3492 | 0 | 1.1432 | -1.1432
| 3493 | 0 | 19.4089 | -19.4089
| 3494 | 0 | 100.7866 | -100.7866
| 3495 | 0 | 243.1556 | -243.1556
| 3496 | 0 | 734.0392 | -734.0392
| 3497 | 0 | 348.928 | -348.928
| 3498 | 0 | 149.4206 | -149.4206
| 3499 | 0 | 76.2748 | -76.2748
| 3500 | 0 | 43.7167 | -43.7167
| 3501 | 0 | 30.7887 | -30.7887
| 3502 | 0 | 6.5144 | -6.5144
| 3503 | 0 | 0 | 0
| 3504 | 0.41311 | 0 | 0.41311
| 3505 | 1.7435 | 0 | 1.7435
| 3506 | 3.02 | 0 | 3.02
| 3507 | 4.0419 | 0 | 4.0419
| 3508 | 4.5417 | 0 | 4.5417
| 3509 | 5.4527 | 0 | 5.4527
| 3510 | 958.5693 | 222.7147 | 735.8546
| 3511 | 402.2067 | 149.6502 | 252.5565
| 3512 | 0 | 1779.9743 | -1779.9743
| 3513 | 0 | 3668.8739 | -3668.8739
| 3514 | 0 | 5965.1989 | -5965.1989
| 3515 | 0 | 7570.2224 | -7570.2224
| 3516 | 0 | 8674.8654 | -8674.8654
| 3517 | 0 | 9837.8058 | -9837.8058
| 3518 | 0 | 7358.734 | -7358.734
| 3519 | 0 | 4605.8346 | -4605.8346
| 3520 | 0 | 4413.8896 | -4413.8896
| 3521 | 0 | 4740.2076 | -4740.2076
| 3522 | 0 | 3479.8157 | -3479.8157
| 3523 | 0 | 2742.681 | -2742.681
| 3524 | 0 | 1363.6954 | -1363.6954
| 3525 | 0 | 528.2643 | -528.2643
| 3526 | 0 | 80.529 | -80.529
| 3527 | 0 | 25.3132 | -25.3132
| 3528 | 0 | 0.13381 | -0.13381
| 3529 | 5.3959 | 0 | 5.3959
| 3530 | 12.4652 | 0 | 12.4652
| 3531 | 19.1818 | 0 | 19.1818
| 3532 | 25.5134 | 0 | 25.5134
| 3533 | 28.1699 | 0 | 28.1699
| 3534 | 1587.0916 | 162.3004 | 1424.7912
| 3535 | 1277.7087 | 11.9834 | 1265.7253
| 3536 | 838.9819 | 415.3938 | 423.5881
| 3537 | 262.2679 | 742.3303 | -480.0624
| 3538 | 165.9836 | 817.7629 | -651.7792
| 3539 | 72.4976 | 816.145 | -743.6475
| 3540 | 69.4971 | 888.2921 | -818.795
| 3541 | 74.9942 | 973.5594 | -898.5652
| 3542 | 87.2283 | 1001.739 | -914.5108
| 3543 | 81.8442 | 848.0439 | -766.1997
| 3544 | 57.8557 | 680.7384 | -622.8827
| 3545 | 37.7009 | 553.8257 | -516.1248
| 3546 | 12.8583 | 284.401 | -271.5427
| 3547 | 13.2287 | 253.4833 | -240.2546
| 3548 | 53.2133 | 133.2722 | -80.0589
| 3549 | 58.1089 | 74.784 | -16.6751
| 3550 | 109.1138 | 0 | 109.1138
| 3551 | 189.1421 | 0 | 189.1421
| 3552 | 276.8938 | 0 | 276.8938
| 3553 | 385.9024 | 0 | 385.9024
| 3554 | 440.0901 | 0 | 440.0901
| 3555 | 453.5827 | 0 | 453.5827
| 3556 | 499.0622 | 0 | 499.0622
| 3557 | 485.5879 | 0 | 485.5879
| 3558 | 5068.6798 | 26.7379 | 5041.9419
| 3559 | 3184.2076 | 0 | 3184.2076
| 3560 | 1969.6365 | 52.8754 | 1916.7612
| 3561 | 728.1635 | 205.4797 | 522.6838
| 3562 | 165.9148 | 412.7793 | -246.8645
| 3563 | 55.5558 | 670.448 | -614.8922
| 3564 | 21.6777 | 930.6901 | -909.0124
| 3565 | 8.6433 | 1680.3795 | -1671.7361
| 3566 | 1.3822 | 2781.2727 | -2779.8904
| 3567 | 0 | 3058.0443 | -3058.0443
| 3568 | 0 | 3062.7008 | -3062.7008
| 3569 | 0 | 3106.0862 | -3106.0862
| 3570 | 0 | 1859.2222 | -1859.2222
| 3571 | 0 | 898.272 | -898.272
| 3572 | 3.6216 | 299.3776 | -295.756
| 3573 | 26.8091 | 203.1958 | -176.3867
| 3574 | 72.498 | 0 | 72.498
| 3575 | 151.1734 | 0 | 151.1734
| 3576 | 225.2875 | 0 | 225.2875
| 3577 | 301.6711 | 0 | 301.6711
| 3578 | 376.2987 | 0 | 376.2987
| 3579 | 453.918 | 0 | 453.918
| 3580 | 507.3338 | 0 | 507.3338
| 3581 | 524.6614 | 0 | 524.6614
| 3582 | 5106.9369 | 0 | 5106.9369
| 3583 | 2921.3552 | 0 | 2921.3552
| 3584 | 1663.171 | 81.1152 | 1582.0557
| 3585 | 351.5176 | 392.7571 | -41.2395
| 3586 | 27.649 | 1152.8218 | -1125.1727
| 3587 | 0.42875 | 2478.0246 | -2477.5959
| 3588 | 0 | 4274.0238 | -4274.0238
| 3589 | 0 | 5193.7403 | -5193.7403
| 3590 | 0 | 5625.1229 | -5625.1229
| 3591 | 0 | 5557.8396 | -5557.8396
| 3592 | 0 | 5288.6972 | -5288.6972
| 3593 | 0 | 4886.8412 | -4886.8412
| 3594 | 0 | 2928.4662 | -2928.4662
| 3595 | 0 | 1961.6786 | -1961.6786
| 3596 | 0 | 629.6669 | -629.6669
| 3597 | 0 | 273.0596 | -273.0596
| 3598 | 0 | 0 | 0
| 3599 | 6.3199 | 0 | 6.3199
| 3600 | 20.4484 | 0 | 20.4484
| 3601 | 31.412 | 0 | 31.412
| 3602 | 39.4339 | 0 | 39.4339
| 3603 | 50.9323 | 0 | 50.9323
| 3604 | 65.6338 | 0 | 65.6338
| 3605 | 64.3399 | 0 | 64.3399
| 3606 | 1706.4389 | 157.3338 | 1549.1051
| 3607 | 1040.8069 | 44.017 | 996.7899
| 3608 | 203.8195 | 974.9072 | -771.0877
| 3609 | 0.53779 | 2116.7523 | -2116.2145
| 3610 | 0 | 3395.5295 | -3395.5295
| 3611 | 0 | 5179.7933 | -5179.7933
| 3612 | 0 | 5703.6783 | -5703.6783
| 3613 | 0 | 6198.2542 | -6198.2542
| 3614 | 0 | 6457.1257 | -6457.1257
| 3615 | 0 | 6164.3059 | -6164.3059
| 3616 | 0 | 6305.0525 | -6305.0525
| 3617 | 0 | 6425.9182 | -6425.9182
| 3618 | 0 | 3973.4043 | -3973.4043
| 3619 | 0 | 3167.9885 | -3167.9885
| 3620 | 0 | 2265.3162 | -2265.3162
| 3621 | 0 | 1165.0618 | -1165.0618
| 3622 | 0 | 99.7789 | -99.7789
| 3623 | 0 | 22.3486 | -22.3486
| 3624 | 0 | 0.28117 | -0.28117
| 3625 | 0 | 0 | 0
| 3626 | 0.08027 | 0 | 0.08027
| 3627 | 3.9831 | 0 | 3.9831
| 3628 | 9.2526 | 0 | 9.2526
| 3629 | 13.8814 | 0 | 13.8814
| 3630 | 1147.2804 | 158.6593 | 988.6211
| 3631 | 741.603 | 87.8935 | 653.7095
| 3632 | 193.8722 | 281.9313 | -88.0592
| 3633 | 0 | 1323.6455 | -1323.6455
| 3634 | 0 | 2986.6495 | -2986.6495
| 3635 | 0 | 6040.9374 | -6040.9374
| 3636 | 0 | 7598.4386 | -7598.4386
| 3637 | 0 | 9126.3604 | -9126.3604
| 3638 | 0 | 9343.8251 | -9343.8251
| 3639 | 0 | 9010.7111 | -9010.7111
| 3640 | 0 | 8576.6155 | -8576.6155
| 3641 | 0 | 8319.333 | -8319.333
| 3642 | 0 | 5639.0753 | -5639.0753
| 3643 | 0 | 2431.8375 | -2431.8375
| 3644 | 0 | 563.4222 | -563.4222
| 3645 | 0 | 440.7053 | -440.7053
| 3646 | 0 | 335.9253 | -335.9253
| 3647 | 0 | 82.0647 | -82.0647
| 3648 | 12.4963 | 0 | 12.4963
| 3649 | 29.7761 | 0 | 29.7761
| 3650 | 45.5433 | 0 | 45.5433
| 3651 | 60.9048 | 0 | 60.9048
| 3652 | 86.0713 | 0 | 86.0713
| 3653 | 111.5136 | 0 | 111.5136
| 3654 | 133.8783 | 0 | 133.8783
| 3655 | 145.3997 | 0 | 145.3997
| 3656 | 3518.7606 | 0 | 3518.7606
| 3657 | 2451.5604 | 0 | 2451.5604
| 3658 | 1824.3046 | 0 | 1824.3046
| 3659 | 1545.7941 | 0 | 1545.7941
| 3660 | 925.052 | 0 | 925.052
| 3661 | 459.9106 | 0 | 459.9106
| 3662 | 73.332 | 0 | 73.332
| 3663 | 17.9764 | 0 | 17.9764
| 3664 | 11.1317 | 0 | 11.1317
| 3665 | 263.5794 | 0 | 263.5794
| 3666 | 705.5649 | 0 | 705.5649
| 3667 | 20.6616 | 0 | 20.6616
| 3668 | 68.2125 | 0 | 68.2125
| 3669 | 134.7016 | 0 | 134.7016
| 3670 | 212.7598 | 0 | 212.7598
| 3671 | 303.671 | 0 | 303.671
| 3672 | 389.8611 | 0 | 389.8611
| 3673 | 465.8307 | 0 | 465.8307
| 3674 | 533.745 | 0 | 533.745
| 3675 | 602.4789 | 0 | 602.4789
| 3676 | 683.5078 | 0 | 683.5078
| 3677 | 734.0735 | 0 | 734.0735
| 3678 | 6904.7187 | 0 | 6904.7187
| 3679 | 4145.8246 | 0 | 4145.8246
| 3680 | 2746.1153 | 27.2284 | 2718.8869
| 3681 | 1416.2792 | 116.2726 | 1300.0066
| 3682 | 822.0353 | 183.9061 | 638.1292
| 3683 | 244.1306 | 195.385 | 48.7456
| 3684 | 120.7831 | 261.8678 | -141.0848
| 3685 | 75.5711 | 511.3889 | -435.8179
| 3686 | 30.9118 | 904.0369 | -873.1251
| 3687 | 7.1876 | 1424.5056 | -1417.318
| 3688 | 1.5238 | 1830.6298 | -1829.106
| 3689 | 0 | 1890.6122 | -1890.6122
| 3690 | 0 | 731.4416 | -731.4416
| 3691 | 0.074092 | 314.9796 | -314.9055
| 3692 | 7.164 | 193.579 | -186.415
| 3693 | 46.5432 | 121.9406 | -75.3974
| 3694 | 114.508 | 0 | 114.508
| 3695 | 172.5213 | 0 | 172.5213
| 3696 | 203.7939 | 0 | 203.7939
| 3697 | 221.284 | 0 | 221.284
| 3698 | 258.337 | 0 | 258.337
| 3699 | 300.7862 | 0 | 300.7862
| 3700 | 340.9679 | 0 | 340.9679
| 3701 | 353.8118 | 0 | 353.8118
| 3702 | 3867.7976 | 59.3425 | 3808.4551
| 3703 | 2095.3482 | 8.5821 | 2086.7661
| 3704 | 1098.6766 | 188.0146 | 910.662
| 3705 | 91.8377 | 538.1727 | -446.335
| 3706 | 11.0137 | 1297.8399 | -1286.8262
| 3707 | 0.24937 | 2523.3038 | -2523.0544
| 3708 | 0 | 4466.7248 | -4466.7248
| 3709 | 0 | 5746.2056 | -5746.2056
| 3710 | 0 | 6796.3345 | -6796.3345
| 3711 | 0 | 7382.3894 | -7382.3894
| 3712 | 0 | 7662.9449 | -7662.9449
| 3713 | 0 | 7692.6481 | -7692.6481
| 3714 | 0 | 5259.2371 | -5259.2371
| 3715 | 0 | 4591.1026 | -4591.1026
| 3716 | 0 | 3435.2876 | -3435.2876
| 3717 | 0 | 1391.5125 | -1391.5125
| 3718 | 0 | 97.4155 | -97.4155
| 3719 | 0 | 16.2471 | -16.2471
| 3720 | 0 | 0 | 0
| 3721 | 0 | 0 | 0
| 3722 | 0 | 0 | 0
| 3723 | 0.73808 | 0 | 0.73808
| 3724 | 2.156 | 0 | 2.156
| 3725 | 0.74826 | 0 | 0.74826
| 3726 | 692.5766 | 414.972 | 277.6046
| 3727 | 316.7965 | 306.4747 | 10.3218
| 3728 | 25.0154 | 1813.2198 | -1788.2044
| 3729 | 0.60285 | 2913.63 | -2913.0272
| 3730 | 0 | 4084.3973 | -4084.3973
| 3731 | 0 | 6639.7524 | -6639.7524
| 3732 | 0 | 7805.9909 | -7805.9909
| 3733 | 0 | 8038.3448 | -8038.3448
| 3734 | 0 | 8696.4451 | -8696.4451
| 3735 | 0 | 8458.2761 | -8458.2761
| 3736 | 0 | 8048.5389 | -8048.5389
| 3737 | 0 | 7643.5457 | -7643.5457
| 3738 | 0 | 4799.339 | -4799.339
| 3739 | 0 | 2160.5158 | -2160.5158
| 3740 | 0 | 412.9227 | -412.9227
| 3741 | 0 | 285.8642 | -285.8642
| 3742 | 2.7881 | 0 | 2.7881
| 3743 | 8.5471 | 0 | 8.5471
| 3744 | 15.2667 | 0 | 15.2667
| 3745 | 20.9347 | 0 | 20.9347
| 3746 | 24.9573 | 0 | 24.9573
| 3747 | 28.22 | 0 | 28.22
| 3748 | 30.2145 | 0 | 30.2145
| 3749 | 29.4361 | 0 | 29.4361
| 3750 | 1569.8091 | 148.1481 | 1421.661
| 3751 | 1171.842 | 23.6454 | 1148.1966
| 3752 | 713.1001 | 634.4669 | 78.6332
| 3753 | 109.9441 | 937.4605 | -827.5163
| 3754 | 25.7113 | 1173.9859 | -1148.2746
| 3755 | 19.3895 | 1255.2578 | -1235.8683
| 3756 | 18.2989 | 1286.0652 | -1267.7663
| 3757 | 15.0351 | 1445.5019 | -1430.4668
| 3758 | 12.6888 | 1528.2859 | -1515.5971
| 3759 | 11.8336 | 1302.8624 | -1291.0288
| 3760 | 6.1509 | 1569.1848 | -1563.0339
| 3761 | 2.4147 | 1273.2723 | -1270.8576
| 3762 | 0.20841 | 383.6829 | -383.4745
| 3763 | 1.9155 | 346.0588 | -344.1433
| 3764 | 5.3358 | 239.5595 | -234.2237
| 3765 | 7.5733 | 203.6379 | -196.0646
| 3766 | 11.9612 | 0 | 11.9612
| 3767 | 18.518 | 0 | 18.518
| 3768 | 25.6009 | 0 | 25.6009
| 3769 | 34.5675 | 0 | 34.5675
| 3770 | 43.951 | 0 | 43.951
| 3771 | 52.3256 | 0 | 52.3256
| 3772 | 67.366 | 0 | 67.366
| 3773 | 63.3362 | 0 | 63.3362
| 3774 | 1527.6193 | 215.9968 | 1311.6225
| 3775 | 1113.6603 | 56.6003 | 1057.0601
| 3776 | 566.3589 | 819.7402 | -253.3813
| 3777 | 22.1986 | 1247.3983 | -1225.1998
| 3778 | 6.5245 | 1876.7259 | -1870.2014
| 3779 | 0.34623 | 2425.1469 | -2424.8007
| 3780 | 0 | 3215.1361 | -3215.1361
| 3781 | 0 | 4683.0983 | -4683.0983
| 3782 | 0 | 5717.7989 | -5717.7989
| 3783 | 0 | 6874.8269 | -6874.8269
| 3784 | 0 | 6670.3916 | -6670.3916
| 3785 | 0 | 6212.0217 | -6212.0217
| 3786 | 0 | 3812.9952 | -3812.9952
| 3787 | 0 | 2497.0024 | -2497.0024
| 3788 | 0 | 1115.9672 | -1115.9672
| 3789 | 0 | 393.0478 | -393.0478
| 3790 | 0 | 13.5534 | -13.5534
| 3791 | 0 | 0.13246 | -0.13246
| 3792 | 0 | 0 | 0
| 3793 | 0 | 0 | 0
| 3794 | 0.82582 | 0 | 0.82582
| 3795 | 1.9674 | 0 | 1.9674
| 3796 | 2.4657 | 0 | 2.4657
| 3797 | 1.8108 | 0 | 1.8108
| 3798 | 695.8636 | 354.5524 | 341.3112
| 3799 | 282.7307 | 155.7034 | 127.0273
| 3800 | 1.8721 | 579.7266 | -577.8545
| 3801 | 0 | 906.8741 | -906.8741
| 3802 | 0 | 2186.1841 | -2186.1841
| 3803 | 0 | 4440.7297 | -4440.7297
| 3804 | 0 | 6460.1237 | -6460.1237
| 3805 | 0 | 7010.334 | -7010.334
| 3806 | 0 | 7571.7238 | -7571.7238
| 3807 | 0 | 8160.748 | -8160.748
| 3808 | 0 | 7460.9782 | -7460.9782
| 3809 | 0 | 6177.921 | -6177.921
| 3810 | 0 | 3345.6705 | -3345.6705
| 3811 | 0 | 2031.7648 | -2031.7648
| 3812 | 0 | 1070.3456 | -1070.3456
| 3813 | 0 | 361.8745 | -361.8745
| 3814 | 0 | 261.4436 | -261.4436
| 3815 | 0 | 158.6694 | -158.6694
| 3816 | 0 | 43.67 | -43.67
| 3817 | 0 | 2.0751 | -2.0751
| 3818 | 1.4489 | 0 | 1.4489
| 3819 | 8.6145 | 0 | 8.6145
| 3820 | 19.1711 | 0 | 19.1711
| 3821 | 27.4512 | 0 | 27.4512
| 3822 | 22.9623 | 0 | 22.9623
| 3823 | 11.5865 | 0 | 11.5865
| 3824 | 1603.4762 | 0 | 1603.4762
| 3825 | 701.1421 | 0 | 701.1421
| 3826 | 84.0908 | 0 | 84.0908
| 3827 | 0 | 0.40709 | -0.40709
| 3828 | 0 | 143.3594 | -143.3594
| 3829 | 0 | 592.6223 | -592.6223
| 3830 | 0 | 1123.9598 | -1123.9598
| 3831 | 0 | 1469.398 | -1469.398
| 3832 | 0 | 1668.2046 | -1668.2046
| 3833 | 0 | 1183.1293 | -1183.1293
| 3834 | 0 | 717.8941 | -717.8941
| 3835 | 0 | 442.4052 | -442.4052
| 3836 | 0 | 190.8018 | -190.8018
| 3837 | 0 | 71.3015 | -71.3015
| 3838 | 0 | 9.8532 | -9.8532
| 3839 | 3.509 | 0 | 3.509
| 3840 | 13.4432 | 0 | 13.4432
| 3841 | 24.0825 | 0 | 24.0825
| 3842 | 37.4288 | 0 | 37.4288
| 3843 | 81.4999 | 0 | 81.4999
| 3844 | 154.1898 | 0 | 154.1898
| 3845 | 189.8889 | 0 | 189.8889
| 3846 | 3892.928 | 56.2063 | 3836.7218
| 3847 | 1844.4168 | 101.8458 | 1742.5709
| 3848 | 642.5273 | 542.0965 | 100.4308
| 3849 | 2.8197 | 1529.3504 | -1526.5306
| 3850 | 0 | 3021.0696 | -3021.0696
| 3851 | 0 | 4734.1798 | -4734.1798
| 3852 | 0 | 5872.6108 | -5872.6108
| 3853 | 0 | 7048.2687 | -7048.2687
| 3854 | 0 | 7902.9425 | -7902.9425
| 3855 | 0 | 8235.27 | -8235.27
| 3856 | 0 | 8106.1801 | -8106.1801
| 3857 | 0 | 8011.703 | -8011.703
| 3858 | 0 | 5573.7643 | -5573.7643
| 3859 | 0 | 4683.6366 | -4683.6366
| 3860 | 0 | 3352.8639 | -3352.8639
| 3861 | 0 | 1620.1582 | -1620.1582
| 3862 | 0 | 309.061 | -309.061
| 3863 | 0 | 199.0743 | -199.0743
| 3864 | 0 | 102.6693 | -102.6693
| 3865 | 0 | 59.7659 | -59.7659
| 3866 | 0 | 26.9876 | -26.9876
| 3867 | 0 | 11.6756 | -11.6756
| 3868 | 0 | 5.6222 | -5.6222
| 3869 | 0 | 14.981 | -14.981
| 3870 | 297.8924 | 687.8279 | -389.9354
| 3871 | 71.6045 | 539.9427 | -468.3381
| 3872 | 0 | 2565.9438 | -2565.9438
| 3873 | 0 | 3014.8986 | -3014.8986
| 3874 | 0 | 3273.4315 | -3273.4315
| 3875 | 0 | 4151.4423 | -4151.4423
| 3876 | 0 | 4840.9751 | -4840.9751
| 3877 | 0 | 4891.1909 | -4891.1909
| 3878 | 0 | 4601.1521 | -4601.1521
| 3879 | 0 | 3688.4048 | -3688.4048
| 3880 | 0 | 3492.3929 | -3492.3929
| 3881 | 0 | 2864.1543 | -2864.1543
| 3882 | 0 | 856.0065 | -856.0065
| 3883 | 0 | 550.8633 | -550.8633
| 3884 | 0 | 420.8363 | -420.8363
| 3885 | 0 | 349.3101 | -349.3101
| 3886 | 0 | 5.7056 | -5.7056
| 3887 | 0.94795 | 0 | 0.94795
| 3888 | 4.7451 | 0 | 4.7451
| 3889 | 6.8197 | 0 | 6.8197
| 3890 | 10.6317 | 0 | 10.6317
| 3891 | 15.2149 | 0 | 15.2149
| 3892 | 16.9674 | 0 | 16.9674
| 3893 | 16.314 | 0 | 16.314
| 3894 | 1266.6153 | 360.672 | 905.9434
| 3895 | 910.7931 | 109.2438 | 801.5493
| 3896 | 471.4142 | 954.2057 | -482.7916
| 3897 | 19.2339 | 1202.6746 | -1183.4408
| 3898 | 16.8921 | 1337.6342 | -1320.7421
| 3899 | 17.5432 | 1356.549 | -1339.0058
| 3900 | 21.7615 | 1312.7699 | -1291.0084
| 3901 | 24.8253 | 1384.6215 | -1359.7962
| 3902 | 23.2171 | 1415.7564 | -1392.5393
| 3903 | 24.5655 | 1157.5718 | -1133.0063
| 3904 | 27.7 | 860.4881 | -832.7881
| 3905 | 30.1007 | 658.7091 | -628.6084
| 3906 | 28.9333 | 281.3537 | -252.4204
| 3907 | 39.7884 | 241.4932 | -201.7048
| 3908 | 140.969 | 138.7299 | 2.2392
| 3909 | 56.451 | 98.0065 | -41.5555
| 3910 | 95.8024 | 0 | 95.8024
| 3911 | 128.4882 | 0 | 128.4882
| 3912 | 166.0039 | 0 | 166.0039
| 3913 | 196.5204 | 0 | 196.5204
| 3914 | 233.2388 | 0 | 233.2388
| 3915 | 263.909 | 0 | 263.909
| 3916 | 279.2894 | 0 | 279.2894
| 3917 | 281.9727 | 0 | 281.9727
| 3918 | 3545.4174 | 64.8979 | 3480.5195
| 3919 | 2310.1982 | 0 | 2310.1982
| 3920 | 1679.7449 | 42.2828 | 1637.4621
| 3921 | 796.2753 | 244.3675 | 551.9078
| 3922 | 311.5791 | 616.8436 | -305.2645
| 3923 | 125.1507 | 795.4855 | -670.3348
| 3924 | 57.4003 | 1017.0399 | -959.6396
| 3925 | 5.9507 | 2184.4785 | -2178.5278
| 3926 | 5.4811 | 2009.0053 | -2003.5243
| 3927 | 4.9054 | 2077.2096 | -2072.3042
| 3928 | 0 | 2364.1971 | -2364.1971
| 3929 | 0 | 1774.1142 | -1774.1142
| 3930 | 0 | 413.5432 | -413.5432
| 3931 | 0 | 361.2318 | -361.2318
| 3932 | 0.71032 | 249.6156 | -248.9053
| 3933 | 7.9438 | 202.8261 | -194.8824
| 3934 | 39.4196 | 0 | 39.4196
| 3935 | 101.5165 | 0 | 101.5165
| 3936 | 138.0835 | 0 | 138.0835
| 3937 | 185.8563 | 0 | 185.8563
| 3938 | 245.0258 | 0 | 245.0258
| 3939 | 309.0816 | 0 | 309.0816
| 3940 | 324.8318 | 0 | 324.8318
| 3941 | 268.8484 | 0 | 268.8484
| 3942 | 2890.6143 | 87.9493 | 2802.6651
| 3943 | 1399.4434 | 100.8293 | 1298.6141
| 3944 | 512.0743 | 749.9305 | -237.8563
| 3945 | 16.4342 | 1516.7466 | -1500.3124
| 3946 | 1.7691 | 2494.093 | -2492.3239
| 3947 | 0 | 3957.4735 | -3957.4735
| 3948 | 0 | 5268.8935 | -5268.8935
| 3949 | 0 | 6592.2606 | -6592.2606
| 3950 | 0 | 7389.3456 | -7389.3456
| 3951 | 0 | 7720.4653 | -7720.4653
| 3952 | 0 | 7841.2754 | -7841.2754
| 3953 | 0 | 7658.6477 | -7658.6477
| 3954 | 0 | 5142.0229 | -5142.0229
| 3955 | 0 | 4435.8587 | -4435.8587
| 3956 | 0 | 2623.0303 | -2623.0303
| 3957 | 0 | 914.7421 | -914.7421
| 3958 | 0 | 20.7224 | -20.7224
| 3959 | 2.6595 | 0 | 2.6595
| 3960 | 21.0308 | 0 | 21.0308
| 3961 | 36.2583 | 0 | 36.2583
| 3962 | 49.1436 | 0 | 49.1436
| 3963 | 53.6896 | 0 | 53.6896
| 3964 | 64.5359 | 0 | 64.5359
| 3965 | 77.6335 | 0 | 77.6335
| 3966 | 2297.1505 | 120.0368 | 2177.1137
| 3967 | 1134.0969 | 47.0938 | 1087.0031
| 3968 | 314.9352 | 224.2821 | 90.6531
| 3969 | 0 | 1010.1539 | -1010.1539
| 3970 | 0 | 1847.0774 | -1847.0774
| 3971 | 0 | 3412.868 | -3412.868
| 3972 | 0 | 4471.4206 | -4471.4206
| 3973 | 0 | 5015.2131 | -5015.2131
| 3974 | 0 | 5537.3158 | -5537.3158
| 3975 | 0 | 6237.6927 | -6237.6927
| 3976 | 0 | 6947.8511 | -6947.8511
| 3977 | 0 | 7217.0884 | -7217.0884
| 3978 | 0 | 5184.4735 | -5184.4735
| 3979 | 0 | 4520.239 | -4520.239
| 3980 | 0 | 3508.4917 | -3508.4917
| 3981 | 0 | 1991.6956 | -1991.6956
| 3982 | 0 | 877.9363 | -877.9363
| 3983 | 0 | 803.5361 | -803.5361
| 3984 | 0 | 670.8181 | -670.8181
| 3985 | 0 | 570.2737 | -570.2737
| 3986 | 0 | 299.6803 | -299.6803
| 3987 | 0 | 224.3603 | -224.3603
| 3988 | 0 | 194.5132 | -194.5132
| 3989 | 0 | 200.183 | -200.183
| 3990 | 0 | 574.3059 | -574.3059
| 3991 | 0 | 552.2503 | -552.2503
| 3992 | 0 | 679.6353 | -679.6353
| 3993 | 0 | 907.23 | -907.23
| 3994 | 0 | 706.2439 | -706.2439
| 3995 | 0 | 2481.5723 | -2481.5723
| 3996 | 0 | 5510.0185 | -5510.0185
| 3997 | 0 | 6747.3724 | -6747.3724
| 3998 | 0 | 7316.2965 | -7316.2965
| 3999 | 0 | 7094.2481 | -7094.2481
| 4000 | 0 | 7374.2194 | -7374.2194
| 4001 | 0 | 7567.4801 | -7567.4801
| 4002 | 0 | 6603.2234 | -6603.2234
| 4003 | 0 | 2440.4229 | -2440.4229
| 4004 | 0 | 1933.4375 | -1933.4375
| 4005 | 0 | 1867.8457 | -1867.8457
| 4006 | 0 | 1162.8387 | -1162.8387
| 4007 | 0 | 651.9328 | -651.9328
| 4008 | 0 | 502.4191 | -502.4191
| 4009 | 0 | 215.6235 | -215.6235
| 4010 | 0 | 49.5881 | -49.5881
| 4011 | 0 | 9.2495 | -9.2495
| 4012 | 4.6881 | 0 | 4.6881
| 4013 | 18.9202 | 0 | 18.9202
| 4014 | 1744.886 | 215.146 | 1529.74
| 4015 | 1235.8584 | 227.3021 | 1008.5563
| 4016 | 719.9749 | 836.8092 | -116.8343
| 4017 | 51.2806 | 1156.1882 | -1104.9076
| 4018 | 3.5108 | 1464.3469 | -1460.8361
| 4019 | 0.15145 | 1893.9318 | -1893.7803
| 4020 | 0 | 2508.0652 | -2508.0652
| 4021 | 0 | 3067.139 | -3067.139
| 4022 | 0 | 3587.2841 | -3587.2841
| 4023 | 0 | 3549.0128 | -3549.0128
| 4024 | 0 | 2992.1386 | -2992.1386
| 4025 | 0 | 2307.6009 | -2307.6009
| 4026 | 0 | 659.1364 | -659.1364
| 4027 | 0 | 479.4987 | -479.4987
| 4028 | 1.2272 | 308.631 | -307.4038
| 4029 | 7.7174 | 226.8634 | -219.146
| 4030 | 25.2007 | 0 | 25.2007
| 4031 | 43.5644 | 0 | 43.5644
| 4032 | 69.7668 | 0 | 69.7668
| 4033 | 112.529 | 0 | 112.529
| 4034 | 160.4406 | 0 | 160.4406
| 4035 | 205.4586 | 0 | 205.4586
| 4036 | 252.1844 | 0 | 252.1844
| 4037 | 275.3428 | 0 | 275.3428
| 4038 | 4100.0051 | 34.6488 | 4065.3562
| 4039 | 2223.8094 | 49.4085 | 2174.4009
| 4040 | 1197.9614 | 366.706 | 831.2555
| 4041 | 136.7973 | 796.9915 | -660.1941
| 4042 | 12.5581 | 1321.0735 | -1308.5154
| 4043 | 2.2715 | 1761.6839 | -1759.4124
| 4044 | 0.68108 | 2082.1041 | -2081.423
| 4045 | 0.022481 | 3185.9418 | -3185.9193
| 4046 | 0 | 3663.2144 | -3663.2144
| 4047 | 0 | 3780.4057 | -3780.4057
| 4048 | 0 | 3691.8386 | -3691.8386
| 4049 | 0 | 3382.8306 | -3382.8306
| 4050 | 0 | 1873.0723 | -1873.0723
| 4051 | 0 | 1142.4667 | -1142.4667
| 4052 | 0 | 357.5577 | -357.5577
| 4053 | 0 | 273.2193 | -273.2193
| 4054 | 4.2939 | 0 | 4.2939
| 4055 | 22.8568 | 0 | 22.8568
| 4056 | 36.6022 | 0 | 36.6022
| 4057 | 49.822 | 0 | 49.822
| 4058 | 67.7114 | 0 | 67.7114
| 4059 | 86.3976 | 0 | 86.3976
| 4060 | 102.9353 | 0 | 102.9353
| 4061 | 167.8836 | 0 | 167.8836
| 4062 | 3065.7747 | 113.9435 | 2951.8312
| 4063 | 1561.869 | 88.7279 | 1473.1412
| 4064 | 521.7851 | 751.5107 | -229.7256
| 4065 | 3.6803 | 1965.7508 | -1962.0706
| 4066 | 0 | 3356.2922 | -3356.2922
| 4067 | 0 | 4951.4189 | -4951.4189
| 4068 | 0 | 5921.9923 | -5921.9923
| 4069 | 0 | 6937.8886 | -6937.8886
| 4070 | 0 | 7097.5645 | -7097.5645
| 4071 | 0 | 6143.7775 | -6143.7775
| 4072 | 0 | 4613.2434 | -4613.2434
| 4073 | 0 | 2891.1441 | -2891.1441
| 4074 | 0 | 683.1838 | -683.1838
| 4075 | 0.38007 | 387.8559 | -387.4758
| 4076 | 3.7055 | 276.1175 | -272.412
| 4077 | 6.2427 | 235.5953 | -229.3526
| 4078 | 14.3637 | 0 | 14.3637
| 4079 | 24.861 | 0 | 24.861
| 4080 | 32.7225 | 0 | 32.7225
| 4081 | 38.4912 | 0 | 38.4912
| 4082 | 44.2844 | 0 | 44.2844
| 4083 | 45.4199 | 0 | 45.4199
| 4084 | 46.425 | 0 | 46.425
| 4085 | 46.83 | 0 | 46.83
| 4086 | 1636.3117 | 199.8504 | 1436.4613
| 4087 | 1227.5662 | 21.8273 | 1205.7388
| 4088 | 758.8279 | 549.9319 | 208.896
| 4089 | 76.2131 | 966.0141 | -889.801
| 4090 | 18.6419 | 1248.2759 | -1229.634
| 4091 | 7.5718 | 1816.7329 | -1809.1611
| 4092 | 0.78173 | 2798.2489 | -2797.4672
| 4093 | 0 | 4368.755 | -4368.755
| 4094 | 0 | 5676.5497 | -5676.5497
| 4095 | 0 | 5985.174 | -5985.174
| 4096 | 0 | 5867.6529 | -5867.6529
| 4097 | 0 | 5628.2964 | -5628.2964
| 4098 | 0 | 3411.6587 | -3411.6587
| 4099 | 0 | 2473.2044 | -2473.2044
| 4100 | 0 | 870.8124 | -870.8124
| 4101 | 0 | 328.2693 | -328.2693
| 4102 | 0.31223 | 0 | 0.31223
| 4103 | 23.3993 | 0 | 23.3993
| 4104 | 48.6546 | 0 | 48.6546
| 4105 | 97.3713 | 0 | 97.3713
| 4106 | 157.5857 | 0 | 157.5857
| 4107 | 222.0434 | 0 | 222.0434
| 4108 | 291.3509 | 0 | 291.3509
| 4109 | 323.2171 | 0 | 323.2171
| 4110 | 4221.2732 | 79.0745 | 4142.1987
| 4111 | 2142.5504 | 57.3593 | 2085.1911
| 4112 | 968.2555 | 507.5697 | 460.6858
| 4113 | 26.3892 | 1214.3367 | -1187.9475
| 4114 | 1.3578 | 2411.1512 | -2409.7934
| 4115 | 0 | 3837.2519 | -3837.2519
| 4116 | 0 | 4866.1391 | -4866.1391
| 4117 | 0 | 5577.3217 | -5577.3217
| 4118 | 0 | 6333.3162 | -6333.3162
| 4119 | 0 | 6794.3959 | -6794.3959
| 4120 | 0 | 6850.2281 | -6850.2281
| 4121 | 0 | 6695.8599 | -6695.8599
| 4122 | 0 | 4454.5955 | -4454.5955
| 4123 | 0 | 3773.2475 | -3773.2475
| 4124 | 0 | 1695.1132 | -1695.1132
| 4125 | 0 | 415.766 | -415.766
| 4126 | 0.062374 | 0.56502 | -0.50264
| 4127 | 10.9065 | 0 | 10.9065
| 4128 | 19.5584 | 0 | 19.5584
| 4129 | 21.5789 | 0 | 21.5789
| 4130 | 26.3712 | 0 | 26.3712
| 4131 | 39.117 | 0 | 39.117
| 4132 | 52.9637 | 0 | 52.9637
| 4133 | 59.4412 | 0 | 59.4412
| 4134 | 2055.3352 | 90.0427 | 1965.2925
| 4135 | 969.7109 | 32.2783 | 937.4327
| 4136 | 332.958 | 195.2349 | 137.7231
| 4137 | 0 | 548.7466 | -548.7466
| 4138 | 0 | 1297.9508 | -1297.9508
| 4139 | 0 | 3120.0285 | -3120.0285
| 4140 | 0 | 4371.4809 | -4371.4809
| 4141 | 0 | 5441.8013 | -5441.8013
| 4142 | 0 | 6195.5019 | -6195.5019
| 4143 | 0 | 6589.0246 | -6589.0246
| 4144 | 0 | 6697.7133 | -6697.7133
| 4145 | 0 | 6272.9394 | -6272.9394
| 4146 | 0 | 4145.7624 | -4145.7624
| 4147 | 0 | 3103.6761 | -3103.6761
| 4148 | 0 | 2045.3749 | -2045.3749
| 4149 | 0 | 854.8328 | -854.8328
| 4150 | 0 | 406.7123 | -406.7123
| 4151 | 0 | 311.928 | -311.928
| 4152 | 0 | 226.0762 | -226.0762
| 4153 | 0 | 132.1741 | -132.1741
| 4154 | 0 | 69.9674 | -69.9674
| 4155 | 0 | 46.5968 | -46.5968
| 4156 | 0 | 28.7174 | -28.7174
| 4157 | 0 | 8.5851 | -8.5851
| 4158 | 0 | 2.4015 | -2.4015
| 4159 | 0 | 11.4807 | -11.4807
| 4160 | 448.0484 | 23.867 | 424.1813
| 4161 | 0 | 244.4217 | -244.4217
| 4162 | 0 | 648.3471 | -648.3471
| 4163 | 0 | 1073.5737 | -1073.5737
| 4164 | 0 | 2790.7724 | -2790.7724
| 4165 | 0 | 3446.9183 | -3446.9183
| 4166 | 0 | 3378.3814 | -3378.3814
| 4167 | 0 | 3505.2398 | -3505.2398
| 4168 | 0 | 3609.2857 | -3609.2857
| 4169 | 0 | 3579.5027 | -3579.5027
| 4170 | 0 | 3132.9953 | -3132.9953
| 4171 | 0 | 1421.473 | -1421.473
| 4172 | 0 | 1214.2788 | -1214.2788
| 4173 | 0 | 552.9746 | -552.9746
| 4174 | 0 | 277.0561 | -277.0561
| 4175 | 0 | 110.4154 | -110.4154
| 4176 | 0 | 21.5786 | -21.5786
| 4177 | 2.2183 | 0 | 2.2183
| 4178 | 8.7897 | 0 | 8.7897
| 4179 | 18.1365 | 0 | 18.1365
| 4180 | 25.0453 | 0 | 25.0453
| 4181 | 23.6707 | 0 | 23.6707
| 4182 | 1696.9179 | 264.5961 | 1432.3219
| 4183 | 492.4131 | 428.7386 | 63.6745
| 4184 | 0 | 3007.662 | -3007.662
| 4185 | 0 | 4139.7296 | -4139.7296
| 4186 | 0 | 5240.5529 | -5240.5529
| 4187 | 0 | 6601.0358 | -6601.0358
| 4188 | 0 | 7514.1043 | -7514.1043
| 4189 | 0 | 7479.9139 | -7479.9139
| 4190 | 0 | 7148.5149 | -7148.5149
| 4191 | 0 | 7241.4099 | -7241.4099
| 4192 | 0 | 6548.4915 | -6548.4915
| 4193 | 0 | 5272.1153 | -5272.1153
| 4194 | 0 | 2610.1372 | -2610.1372
| 4195 | 0 | 1311.6932 | -1311.6932
| 4196 | 0 | 507.1971 | -507.1971
| 4197 | 0 | 349.4148 | -349.4148
| 4198 | 1.256 | 1.1826 | 0.073405
| 4199 | 13.6853 | 0 | 13.6853
| 4200 | 28.779 | 0 | 28.779
| 4201 | 39.5394 | 0 | 39.5394
| 4202 | 52.5149 | 0 | 52.5149
| 4203 | 70.8329 | 0 | 70.8329
| 4204 | 99.2133 | 0 | 99.2133
| 4205 | 134.0034 | 0 | 134.0034
| 4206 | 3183.4532 | 118.3005 | 3065.1526
| 4207 | 1752.5194 | 61.832 | 1690.6874
| 4208 | 949.3872 | 411.2151 | 538.1721
| 4209 | 124.7628 | 857.6724 | -732.9096
| 4210 | 15.2579 | 1114.3712 | -1099.1133
| 4211 | 5.0796 | 1460.9111 | -1455.8314
| 4212 | 2.8433 | 1641.527 | -1638.6837
| 4213 | 1.6505 | 2046.8247 | -2045.1742
| 4214 | 0.68154 | 2427.8442 | -2427.1627
| 4215 | 0 | 2418.3082 | -2418.3082
| 4216 | 0 | 2265.5122 | -2265.5122
| 4217 | 0 | 1921.7714 | -1921.7714
| 4218 | 0 | 648.8376 | -648.8376
| 4219 | 0 | 427.1135 | -427.1135
| 4220 | 0.97089 | 300.6342 | -299.6633
| 4221 | 9.3317 | 220.0178 | -210.6862
| 4222 | 29.9886 | 0 | 29.9886
| 4223 | 57.4627 | 0 | 57.4627
| 4224 | 95.5705 | 0 | 95.5705
| 4225 | 136.4389 | 0 | 136.4389
| 4226 | 230.0499 | 0 | 230.0499
| 4227 | 308.0016 | 0 | 308.0016
| 4228 | 306.4423 | 0 | 306.4423
| 4229 | 297.071 | 0 | 297.071
| 4230 | 3968.4865 | 56.0687 | 3912.4178
| 4231 | 2177.8228 | 2.4889 | 2175.3339
| 4232 | 971.9706 | 281.2853 | 690.6853
| 4233 | 30.6519 | 802.1304 | -771.4785
| 4234 | 3.9522 | 1731.0686 | -1727.1164
| 4235 | 0 | 3106.035 | -3106.035
| 4236 | 0 | 4060.7119 | -4060.7119
| 4237 | 0 | 4778.7506 | -4778.7506
| 4238 | 0 | 5157.9171 | -5157.9171
| 4239 | 0 | 5098.1061 | -5098.1061
| 4240 | 0 | 4789.92 | -4789.92
| 4241 | 0 | 4162.5568 | -4162.5568
| 4242 | 0 | 2293.2277 | -2293.2277
| 4243 | 0 | 1584.9524 | -1584.9524
| 4244 | 0 | 599.3874 | -599.3874
| 4245 | 0 | 287.7384 | -287.7384
| 4246 | 0 | 0 | 0
| 4247 | 2.1168 | 0 | 2.1168
| 4248 | 4.6544 | 0 | 4.6544
| 4249 | 9.272 | 0 | 9.272
| 4250 | 16.8514 | 0 | 16.8514
| 4251 | 24.1423 | 0 | 24.1423
| 4252 | 31.3957 | 0 | 31.3957
| 4253 | 29.7427 | 0 | 29.7427
| 4254 | 1501.3761 | 229.479 | 1271.8971
| 4255 | 505.0837 | 318.9988 | 186.0849
| 4256 | 0.16285 | 2509.9064 | -2509.7436
| 4257 | 0 | 3915.5754 | -3915.5754
| 4258 | 0 | 6036.2459 | -6036.2459
| 4259 | 0 | 8012.9981 | -8012.9981
| 4260 | 0 | 8977.9139 | -8977.9139
| 4261 | 0 | 9645.3492 | -9645.3492
| 4262 | 0 | 10689.2838 | -10689.2838
| 4263 | 0 | 11592.8487 | -11592.8487
| 4264 | 0 | 11972.0873 | -11972.0873
| 4265 | 0 | 10636.1917 | -10636.1917
| 4266 | 0 | 6241.5728 | -6241.5728
| 4267 | 0 | 5079.8255 | -5079.8255
| 4268 | 0 | 4115.621 | -4115.621
| 4269 | 0 | 1974.0202 | -1974.0202
| 4270 | 0 | 600.1472 | -600.1472
| 4271 | 0 | 661.0786 | -661.0786
| 4272 | 0 | 570.7843 | -570.7843
| 4273 | 0 | 412.0556 | -412.0556
| 4274 | 0 | 465.2652 | -465.2652
| 4275 | 0 | 500.731 | -500.731
| 4276 | 0 | 363.33 | -363.33
| 4277 | 0 | 165.9646 | -165.9646
| 4278 | 38.6985 | 2223.5 | -2184.8015
| 4279 | 0 | 3269.3551 | -3269.3551
| 4280 | 0 | 5300.1368 | -5300.1368
| 4281 | 0 | 7301.8188 | -7301.8188
| 4282 | 0 | 9657.2461 | -9657.2461
| 4283 | 0 | 11446.7831 | -11446.7831
| 4284 | 0 | 12664.5441 | -12664.5441
| 4285 | 0 | 13631.119 | -13631.119
| 4286 | 0 | 14362.8101 | -14362.8101
| 4287 | 0 | 14675.655 | -14675.655
| 4288 | 0 | 14433.014 | -14433.014
| 4289 | 0 | 13899.0703 | -13899.0703
| 4290 | 0 | 8890.5276 | -8890.5276
| 4291 | 0 | 7446.4406 | -7446.4406
| 4292 | 0 | 6215.6148 | -6215.6148
| 4293 | 0 | 2851.5347 | -2851.5347
| 4294 | 0 | 952.9505 | -952.9505
| 4295 | 0 | 799.9094 | -799.9094
| 4296 | 0 | 667.9509 | -667.9509
| 4297 | 0 | 631.5466 | -631.5466
| 4298 | 0 | 342.2445 | -342.2445
| 4299 | 0 | 229.8001 | -229.8001
| 4300 | 0 | 99.0104 | -99.0104
| 4301 | 0 | 21.0367 | -21.0367
| 4302 | 625.3875 | 623.1905 | 2.1971
| 4303 | 3.4685 | 872.2324 | -868.7639
| 4304 | 0 | 1849.3243 | -1849.3243
| 4305 | 0 | 2283.2584 | -2283.2584
| 4306 | 0 | 3918.0838 | -3918.0838
| 4307 | 0 | 5018.874 | -5018.874
| 4308 | 0 | 5419.1471 | -5419.1471
| 4309 | 0 | 5667.3796 | -5667.3796
| 4310 | 0 | 5759.913 | -5759.913
| 4311 | 0 | 5985.3486 | -5985.3486
| 4312 | 0 | 6087.5749 | -6087.5749
| 4313 | 0 | 5533.4064 | -5533.4064
| 4314 | 0 | 3258.9085 | -3258.9085
| 4315 | 0 | 2221.858 | -2221.858
| 4316 | 0 | 616.6877 | -616.6877
| 4317 | 0 | 222.5972 | -222.5972
| 4318 | 0 | 67.55 | -67.55
| 4319 | 3.6178 | 2.0686 | 1.5492
| 4320 | 8.1924 | 0 | 8.1924
| 4321 | 12.5795 | 0 | 12.5795
| 4322 | 25.9986 | 0 | 25.9986
| 4323 | 41.008 | 0 | 41.008
| 4324 | 55.3838 | 0 | 55.3838
| 4325 | 62.7453 | 0 | 62.7453
| 4326 | 30.8994 | 0 | 30.8994
| 4327 | 6.729 | 0 | 6.729
| 4328 | 1385.8402 | 0 | 1385.8402
| 4329 | 437.2543 | 5.5217 | 431.7327
| 4330 | 0 | 20.5285 | -20.5285
| 4331 | 0 | 141.7293 | -141.7293
| 4332 | 0 | 550.6436 | -550.6436
| 4333 | 0 | 1333.2809 | -1333.2809
| 4334 | 0 | 1733.515 | -1733.515
| 4335 | 0 | 1594.4873 | -1594.4873
| 4336 | 0 | 2128.5702 | -2128.5702
| 4337 | 0 | 1949.5429 | -1949.5429
| 4338 | 0 | 934.2691 | -934.2691
| 4339 | 0 | 386.7399 | -386.7399
| 4340 | 0 | 298.2561 | -298.2561
| 4341 | 0 | 167.7209 | -167.7209
| 4342 | 0 | 80.7587 | -80.7587
| 4343 | 0 | 57.6132 | -57.6132
| 4344 | 0 | 45.1262 | -45.1262
| 4345 | 0 | 100.0019 | -100.0019
| 4346 | 0 | 199.0938 | -199.0938
| 4347 | 0 | 338.8691 | -338.8691
| 4348 | 0 | 272.2512 | -272.2512
| 4349 | 0 | 436.2485 | -436.2485
| 4350 | 0 | 1803.2991 | -1803.2991
| 4351 | 0 | 2453.6952 | -2453.6952
| 4352 | 0 | 4483.9777 | -4483.9777
| 4353 | 0 | 6223.7041 | -6223.7041
| 4354 | 0 | 7829.8417 | -7829.8417
| 4355 | 0 | 9662.4367 | -9662.4367
| 4356 | 0 | 11264.1903 | -11264.1903
| 4357 | 0 | 12654.1674 | -12654.1674
| 4358 | 0 | 13576.3882 | -13576.3882
| 4359 | 0 | 13739.8337 | -13739.8337
| 4360 | 0 | 13345.4433 | -13345.4433
| 4361 | 0 | 12588.6571 | -12588.6571
| 4362 | 0 | 8498.7962 | -8498.7962
| 4363 | 0 | 7524.5594 | -7524.5594
| 4364 | 0 | 5908.7324 | -5908.7324
| 4365 | 0 | 2483.9931 | -2483.9931
| 4366 | 0 | 589.3424 | -589.3424
| 4367 | 0 | 306.149 | -306.149
| 4368 | 0 | 132.2943 | -132.2943
| 4369 | 0 | 45.2083 | -45.2083
| 4370 | 0 | 15.0564 | -15.0564
| 4371 | 0 | 3.9969 | -3.9969
| 4372 | 0 | 1.263 | -1.263
| 4373 | 0 | 8.9052 | -8.9052
| 4374 | 542.75 | 951.6361 | -408.8861
| 4375 | 0 | 1972.1939 | -1972.1939
| 4376 | 0 | 4025.1178 | -4025.1178
| 4377 | 0 | 5094.1905 | -5094.1905
| 4378 | 0 | 6356.9763 | -6356.9763
| 4379 | 0 | 7050.5489 | -7050.5489
| 4380 | 0 | 7474.0119 | -7474.0119
| 4381 | 0 | 7952.0065 | -7952.0065
| 4382 | 0 | 8067.569 | -8067.569
| 4383 | 0 | 7546.6093 | -7546.6093
| 4384 | 0 | 6687.6972 | -6687.6972
| 4385 | 0 | 5576.4358 | -5576.4358
| 4386 | 0 | 2773.568 | -2773.568
| 4387 | 0 | 1707.7269 | -1707.7269
| 4388 | 0 | 698.8673 | -698.8673
| 4389 | 0 | 459.5697 | -459.5697
| 4390 | 0 | 38.7957 | -38.7957
| 4391 | 0.25781 | 1.9868 | -1.729
| 4392 | 7.1269 | 0 | 7.1269
| 4393 | 16.0827 | 0 | 16.0827
| 4394 | 28.1565 | 0 | 28.1565
| 4395 | 38.6966 | 0 | 38.6966
| 4396 | 50.0078 | 0 | 50.0078
| 4397 | 42.4846 | 0 | 42.4846
| 4398 | 2067.4925 | 154.8679 | 1912.6246
| 4399 | 835.2634 | 197.3976 | 637.8657
| 4400 | 106.2717 | 1845.8625 | -1739.5909
| 4401 | 0 | 2774.5293 | -2774.5293
| 4402 | 0 | 3401.5273 | -3401.5273
| 4403 | 0 | 5142.3853 | -5142.3853
| 4404 | 0 | 6651.0789 | -6651.0789
| 4405 | 0 | 8188.8406 | -8188.8406
| 4406 | 0 | 9194.5705 | -9194.5705
| 4407 | 0 | 9411.5344 | -9411.5344
| 4408 | 0 | 9340.9544 | -9340.9544
| 4409 | 0 | 8753.3099 | -8753.3099
| 4410 | 0 | 5485.1802 | -5485.1802
| 4411 | 0 | 4558.1126 | -4558.1126
| 4412 | 0 | 3291.6519 | -3291.6519
| 4413 | 0 | 1287.3827 | -1287.3827
| 4414 | 0 | 233.7405 | -233.7405
| 4415 | 0 | 91.3667 | -91.3667
| 4416 | 0 | 26.4827 | -26.4827
| 4417 | 0 | 2.4795 | -2.4795
| 4418 | 0 | 0 | 0
| 4419 | 0 | 0 | 0
| 4420 | 0 | 0 | 0
| 4421 | 0 | 0 | 0
| 4422 | 596.0559 | 519.482 | 76.5739
| 4423 | 181.2175 | 575.1365 | -393.919
| 4424 | 0 | 3259.4581 | -3259.4581
| 4425 | 0 | 4939.7059 | -4939.7059
| 4426 | 0 | 7417.2661 | -7417.2661
| 4427 | 0 | 9220.255 | -9220.255
| 4428 | 0 | 10659.6966 | -10659.6966
| 4429 | 0 | 12025.0429 | -12025.0429
| 4430 | 0 | 12914.2679 | -12914.2679
| 4431 | 0 | 13294.6208 | -13294.6208
| 4432 | 0 | 13412.0894 | -13412.0894
| 4433 | 0 | 13054.408 | -13054.408
| 4434 | 0 | 8695.4429 | -8695.4429
| 4435 | 0 | 7799.0652 | -7799.0652
| 4436 | 0 | 6562.3903 | -6562.3903
| 4437 | 0 | 2881.3026 | -2881.3026
| 4438 | 0 | 933.139 | -933.139
| 4439 | 0 | 937.5524 | -937.5524
| 4440 | 0 | 763.3838 | -763.3838
| 4441 | 0 | 689.3127 | -689.3127
| 4442 | 0 | 598.9387 | -598.9387
| 4443 | 0 | 484.8651 | -484.8651
| 4444 | 0 | 246.0191 | -246.0191
| 4445 | 0 | 240.7528 | -240.7528
| 4446 | 33.3211 | 3096.3478 | -3063.0267
| 4447 | 0 | 3527.8809 | -3527.8809
| 4448 | 0 | 6048.1517 | -6048.1517
| 4449 | 0 | 8975.6293 | -8975.6293
| 4450 | 0 | 11436.1405 | -11436.1405
| 4451 | 0 | 13105.4778 | -13105.4778
| 4452 | 0 | 14071.2556 | -14071.2556
| 4453 | 0 | 15051.4587 | -15051.4587
| 4454 | 0 | 15162.7293 | -15162.7293
| 4455 | 0 | 14651.0631 | -14651.0631
| 4456 | 0 | 13777.4927 | -13777.4927
| 4457 | 0 | 12769.1188 | -12769.1188
| 4458 | 0 | 8102.2016 | -8102.2016
| 4459 | 0 | 6977.1173 | -6977.1173
| 4460 | 0 | 5305.9344 | -5305.9344
| 4461 | 0 | 2325.1184 | -2325.1184
| 4462 | 0 | 540.9978 | -540.9978
| 4463 | 0 | 282.344 | -282.344
| 4464 | 0 | 107.3835 | -107.3835
| 4465 | 0 | 29.285 | -29.285
| 4466 | 1.1305 | 0.84619 | 0.28435
| 4467 | 7.1663 | 0 | 7.1663
| 4468 | 14.6285 | 0 | 14.6285
| 4469 | 11.9083 | 0 | 11.9083
| 4470 | 1416.6524 | 185.2455 | 1231.4069
| 4471 | 539.4533 | 149.3153 | 390.138
| 4472 | 57.5898 | 467.8038 | -410.2139
| 4473 | 0 | 649.4701 | -649.4701
| 4474 | 0 | 803.739 | -803.739
| 4475 | 0 | 1553.9107 | -1553.9107
| 4476 | 0 | 2004.6893 | -2004.6893
| 4477 | 0 | 2316.8332 | -2316.8332
| 4478 | 0 | 2177.9386 | -2177.9386
| 4479 | 0 | 2025.1428 | -2025.1428
| 4480 | 0 | 2049.4378 | -2049.4378
| 4481 | 0 | 1776.8598 | -1776.8598
| 4482 | 0 | 332.9721 | -332.9721
| 4483 | 0 | 129.0341 | -129.0341
| 4484 | 0 | 87.7301 | -87.7301
| 4485 | 0 | 58.199 | -58.199
| 4486 | 0 | 24.4793 | -24.4793
| 4487 | 0 | 0.57192 | -0.57192
| 4488 | 1.3313 | 0 | 1.3313
| 4489 | 4.3045 | 0 | 4.3045
| 4490 | 7.4284 | 0 | 7.4284
| 4491 | 11.4271 | 0 | 11.4271
| 4492 | 16.7802 | 0 | 16.7802
| 4493 | 17.9512 | 0 | 17.9512
| 4494 | 15.4576 | 0 | 15.4576
| 4495 | 13.9959 | 0 | 13.9959
| 4496 | 1508.9185 | 0 | 1508.9185
| 4497 | 493.1772 | 0 | 493.1772
| 4498 | 0 | 0 | 0
| 4499 | 0 | 161.9902 | -161.9902
| 4500 | 0 | 1190.0105 | -1190.0105
| 4501 | 0 | 2678.6887 | -2678.6887
| 4502 | 0 | 3539.1373 | -3539.1373
| 4503 | 0 | 4094.2199 | -4094.2199
| 4504 | 0 | 4753.6474 | -4753.6474
| 4505 | 0 | 4582.9558 | -4582.9558
| 4506 | 0 | 3582.4661 | -3582.4661
| 4507 | 0 | 1357.0372 | -1357.0372
| 4508 | 0 | 1054.1909 | -1054.1909
| 4509 | 0 | 841.0381 | -841.0381
| 4510 | 0 | 726.485 | -726.485
| 4511 | 0 | 393.2431 | -393.2431
| 4512 | 0 | 264.4756 | -264.4756
| 4513 | 0 | 175.6958 | -175.6958
| 4514 | 0 | 126.7774 | -126.7774
| 4515 | 0 | 107.8966 | -107.8966
| 4516 | 0 | 104.7802 | -104.7802
| 4517 | 0 | 199.0783 | -199.0783
| 4518 | 103.2717 | 1532.2457 | -1428.974
| 4519 | 0 | 1735.0365 | -1735.0365
| 4520 | 0 | 4309.0861 | -4309.0861
| 4521 | 0 | 5016.3756 | -5016.3756
| 4522 | 0 | 6213.3229 | -6213.3229
| 4523 | 0 | 7866.3962 | -7866.3962
| 4524 | 0 | 9584.2099 | -9584.2099
| 4525 | 0 | 11261.4665 | -11261.4665
| 4526 | 0 | 11813.9291 | -11813.9291
| 4527 | 0 | 11046.6537 | -11046.6537
| 4528 | 0 | 9962.3871 | -9962.3871
| 4529 | 0 | 9006.5331 | -9006.5331
| 4530 | 0 | 5808.5427 | -5808.5427
| 4531 | 0 | 4914.1653 | -4914.1653
| 4532 | 0 | 3851.6835 | -3851.6835
| 4533 | 0 | 2034.4915 | -2034.4915
| 4534 | 0 | 501.5829 | -501.5829
| 4535 | 0 | 363.1482 | -363.1482
| 4536 | 0 | 260.9932 | -260.9932
| 4537 | 0 | 202.3384 | -202.3384
| 4538 | 0 | 89.9158 | -89.9158
| 4539 | 0 | 14.8202 | -14.8202
| 4540 | 1.0801 | 0 | 1.0801
| 4541 | 0.29885 | 0 | 0.29885
| 4542 | 652.7433 | 903.0301 | -250.2869
| 4543 | 0 | 2473.6512 | -2473.6512
| 4544 | 0 | 5250.1862 | -5250.1862
| 4545 | 0 | 7676.6869 | -7676.6869
| 4546 | 0 | 9894.2853 | -9894.2853
| 4547 | 0 | 10942.6892 | -10942.6892
| 4548 | 0 | 11353.5786 | -11353.5786
| 4549 | 0 | 11706.1894 | -11706.1894
| 4550 | 0 | 12243.7881 | -12243.7881
| 4551 | 0 | 12812.0489 | -12812.0489
| 4552 | 0 | 12872.4565 | -12872.4565
| 4553 | 0 | 12215.3782 | -12215.3782
| 4554 | 0 | 7921.826 | -7921.826
| 4555 | 0 | 6883.2167 | -6883.2167
| 4556 | 0 | 5489.6536 | -5489.6536
| 4557 | 0 | 2502.0202 | -2502.0202
| 4558 | 0 | 709.3038 | -709.3038
| 4559 | 0 | 484.5534 | -484.5534
| 4560 | 0 | 282.0776 | -282.0776
| 4561 | 0 | 129.2889 | -129.2889
| 4562 | 0 | 50.2504 | -50.2504
| 4563 | 0 | 18.4279 | -18.4279
| 4564 | 0 | 1.7554 | -1.7554
| 4565 | 0 | 0.83236 | -0.83236
| 4566 | 620.5668 | 620.5897 | -0.022914
| 4567 | 203.3437 | 831.5163 | -628.1726
| 4568 | 0 | 3355.8923 | -3355.8923
| 4569 | 0 | 4438.5067 | -4438.5067
| 4570 | 0 | 5854.0253 | -5854.0253
| 4571 | 0 | 6798.7175 | -6798.7175
| 4572 | 0 | 7474.4427 | -7474.4427
| 4573 | 0 | 8226.4123 | -8226.4123
| 4574 | 0 | 8833.9659 | -8833.9659
| 4575 | 0 | 9023.6008 | -9023.6008
| 4576 | 0 | 9020.8369 | -9020.8369
| 4577 | 0 | 8446.8323 | -8446.8323
| 4578 | 0 | 5152.6327 | -5152.6327
| 4579 | 0 | 4176.9054 | -4176.9054
| 4580 | 0 | 2131.5138 | -2131.5138
| 4581 | 0 | 741.9784 | -741.9784
| 4582 | 0 | 36.9378 | -36.9378
| 4583 | 6.6247 | 0 | 6.6247
| 4584 | 21.7293 | 0 | 21.7293
| 4585 | 38.5559 | 0 | 38.5559
| 4586 | 52.0584 | 0 | 52.0584
| 4587 | 72.4162 | 0 | 72.4162
| 4588 | 104.6535 | 0 | 104.6535
| 4589 | 94.7757 | 0 | 94.7757
| 4590 | 2675.1216 | 198.6386 | 2476.483
| 4591 | 1233.362 | 225.3155 | 1008.0465
| 4592 | 292.8971 | 1749.0576 | -1456.1606
| 4593 | 0 | 3072.0372 | -3072.0372
| 4594 | 0 | 4419.0042 | -4419.0042
| 4595 | 0 | 6324.5018 | -6324.5018
| 4596 | 0 | 7666.9506 | -7666.9506
| 4597 | 0 | 8993.1421 | -8993.1421
| 4598 | 0 | 9619.8083 | -9619.8083
| 4599 | 0 | 9337.9978 | -9337.9978
| 4600 | 0 | 8813.5803 | -8813.5803
| 4601 | 0 | 8192.0109 | -8192.0109
| 4602 | 0 | 5114.7141 | -5114.7141
| 4603 | 0 | 4360.9947 | -4360.9947
| 4604 | 0 | 3238.1658 | -3238.1658
| 4605 | 0 | 1422.4019 | -1422.4019
| 4606 | 0 | 162.1993 | -162.1993
| 4607 | 0 | 48.3143 | -48.3143
| 4608 | 0 | 10.6702 | -10.6702
| 4609 | 0 | 0.063666 | -0.063666
| 4610 | 0 | 0 | 0
| 4611 | 0 | 0 | 0
| 4612 | 0.073801 | 0 | 0.073801
| 4613 | 0 | 0 | 0
| 4614 | 592.2372 | 533.8245 | 58.4127
| 4615 | 152.7591 | 528.6794 | -375.9203
| 4616 | 0 | 3225.3472 | -3225.3472
| 4617 | 0 | 3979.1679 | -3979.1679
| 4618 | 0 | 4556.0177 | -4556.0177
| 4619 | 0 | 5949.25 | -5949.25
| 4620 | 0 | 7121.9335 | -7121.9335
| 4621 | 0 | 8020.3488 | -8020.3488
| 4622 | 0 | 9071.1622 | -9071.1622
| 4623 | 0 | 9608.5469 | -9608.5469
| 4624 | 0 | 9885.1194 | -9885.1194
| 4625 | 0 | 9914.2851 | -9914.2851
| 4626 | 0 | 6518.697 | -6518.697
| 4627 | 0 | 6020.3154 | -6020.3154
| 4628 | 0 | 5300.4988 | -5300.4988
| 4629 | 0 | 2537.5133 | -2537.5133
| 4630 | 0 | 880.1815 | -880.1815
| 4631 | 0 | 990.5597 | -990.5597
| 4632 | 0 | 919.4087 | -919.4087
| 4633 | 0 | 804.2362 | -804.2362
| 4634 | 0 | 733.1047 | -733.1047
| 4635 | 0 | 830.9262 | -830.9262
| 4636 | 0 | 824.031 | -824.031
| 4637 | 0 | 880.1956 | -880.1956
| 4638 | 0 | 2667.8385 | -2667.8385
| 4639 | 0 | 2376.0908 | -2376.0908
| 4640 | 0 | 3139.3288 | -3139.3288
| 4641 | 0 | 6054.5396 | -6054.5396
| 4642 | 0 | 8035.0626 | -8035.0626
| 4643 | 0 | 9553.226 | -9553.226
| 4644 | 0 | 11037.7091 | -11037.7091
| 4645 | 0 | 11424.0858 | -11424.0858
| 4646 | 0 | 11244.6906 | -11244.6906
| 4647 | 0 | 10976.5541 | -10976.5541
| 4648 | 0 | 10744.1801 | -10744.1801
| 4649 | 0 | 9846.457 | -9846.457
| 4650 | 0 | 6160.6014 | -6160.6014
| 4651 | 0 | 4643.5369 | -4643.5369
| 4652 | 0 | 3197.8344 | -3197.8344
| 4653 | 0 | 1597.8636 | -1597.8636
| 4654 | 0 | 917.6578 | -917.6578
| 4655 | 0 | 498.2983 | -498.2983
| 4656 | 0 | 275.8649 | -275.8649
| 4657 | 0 | 112.6106 | -112.6106
| 4658 | 0 | 45.5541 | -45.5541
| 4659 | 0 | 19.5693 | -19.5693
| 4660 | 0 | 9.2233 | -9.2233
| 4661 | 0 | 14.821 | -14.821
| 4662 | 0 | 47.4975 | -47.4975
| 4663 | 0 | 161.5949 | -161.5949
| 4664 | 187.9063 | 527.6522 | -339.7459
| 4665 | 0 | 705.7267 | -705.7267
| 4666 | 0 | 889.5619 | -889.5619
| 4667 | 0 | 1582.8806 | -1582.8806
| 4668 | 0 | 3355.4808 | -3355.4808
| 4669 | 0 | 4244.267 | -4244.267
| 4670 | 0 | 4867.5576 | -4867.5576
| 4671 | 0 | 5539.8253 | -5539.8253
| 4672 | 0 | 6014.018 | -6014.018
| 4673 | 0 | 5846.7401 | -5846.7401
| 4674 | 0 | 4769.8998 | -4769.8998
| 4675 | 0 | 1972.1518 | -1972.1518
| 4676 | 0 | 1492.9527 | -1492.9527
| 4677 | 0 | 1215.1852 | -1215.1852
| 4678 | 0 | 571.8136 | -571.8136
| 4679 | 0 | 297.5612 | -297.5612
| 4680 | 0 | 104.2802 | -104.2802
| 4681 | 0 | 20.3533 | -20.3533
| 4682 | 2.1381 | 0 | 2.1381
| 4683 | 9.4743 | 0 | 9.4743
| 4684 | 21.4774 | 0 | 21.4774
| 4685 | 15.5733 | 0 | 15.5733
| 4686 | 1429.563 | 638.9831 | 790.5798
| 4687 | 281.6607 | 1221.3581 | -939.6974
| 4688 | 0 | 4351.4105 | -4351.4105
| 4689 | 0 | 5884.192 | -5884.192
| 4690 | 0 | 8644.0156 | -8644.0156
| 4691 | 0 | 10429.7469 | -10429.7469
| 4692 | 0 | 11798.3117 | -11798.3117
| 4693 | 0 | 13067.8464 | -13067.8464
| 4694 | 0 | 14081.2945 | -14081.2945
| 4695 | 0 | 14920.8083 | -14920.8083
| 4696 | 0 | 15499.2852 | -15499.2852
| 4697 | 0 | 15276.4032 | -15276.4032
| 4698 | 0 | 10669.4829 | -10669.4829
| 4699 | 0 | 9504.2958 | -9504.2958
| 4700 | 0 | 7846.0764 | -7846.0764
| 4701 | 0 | 3333.2056 | -3333.2056
| 4702 | 0 | 1190.8747 | -1190.8747
| 4703 | 0 | 1104.1454 | -1104.1454
| 4704 | 0 | 859.3387 | -859.3387
| 4705 | 0 | 851.3806 | -851.3806
| 4706 | 0 | 874.0729 | -874.0729
| 4707 | 0 | 758.7498 | -758.7498
| 4708 | 0 | 601.0482 | -601.0482
| 4709 | 0 | 701.713 | -701.713
| 4710 | 0 | 3773.4288 | -3773.4288
| 4711 | 0 | 4009.1475 | -4009.1475
| 4712 | 0 | 6461.4195 | -6461.4195
| 4713 | 0 | 9807.799 | -9807.799
| 4714 | 0 | 11961.5693 | -11961.5693
| 4715 | 0 | 13536.0501 | -13536.0501
| 4716 | 0 | 14776.6979 | -14776.6979
| 4717 | 0 | 16081.545 | -16081.545
| 4718 | 0 | 16520.1972 | -16520.1972
| 4719 | 0 | 15932.4487 | -15932.4487
| 4720 | 0 | 14677.0822 | -14677.0822
| 4721 | 0 | 13733.0686 | -13733.0686
| 4722 | 0 | 9066.5305 | -9066.5305
| 4723 | 0 | 8240.8496 | -8240.8496
| 4724 | 0 | 7170.3149 | -7170.3149
| 4725 | 0 | 3375.9817 | -3375.9817
| 4726 | 0 | 1368.641 | -1368.641
| 4727 | 0 | 1379.8254 | -1379.8254
| 4728 | 0 | 1183.3226 | -1183.3226
| 4729 | 0 | 920.9002 | -920.9002
| 4730 | 0 | 927.2457 | -927.2457
| 4731 | 0 | 835.3881 | -835.3881
| 4732 | 0 | 720.2652 | -720.2652
| 4733 | 0 | 834.9659 | -834.9659
| 4734 | 0 | 4386.9741 | -4386.9741
| 4735 | 0 | 4443.4162 | -4443.4162
| 4736 | 0 | 6587.2607 | -6587.2607
| 4737 | 0 | 9484.693 | -9484.693
| 4738 | 0 | 11427.4664 | -11427.4664
| 4739 | 0 | 12773.5312 | -12773.5312
| 4740 | 0 | 13593.2299 | -13593.2299
| 4741 | 0 | 14273.566 | -14273.566
| 4742 | 0 | 14885.7168 | -14885.7168
| 4743 | 0 | 15299.989 | -15299.989
| 4744 | 0 | 15352.5756 | -15352.5756
| 4745 | 0 | 14921.6707 | -14921.6707
| 4746 | 0 | 10090.3107 | -10090.3107
| 4747 | 0 | 9084.1103 | -9084.1103
| 4748 | 0 | 7785.4282 | -7785.4282
| 4749 | 0 | 3406.9624 | -3406.9624
| 4750 | 0 | 1449.3908 | -1449.3908
| 4751 | 0 | 1402.7068 | -1402.7068
| 4752 | 0 | 1211.5125 | -1211.5125
| 4753 | 0 | 1295.1522 | -1295.1522
| 4754 | 0 | 1125.9026 | -1125.9026
| 4755 | 0 | 813.6379 | -813.6379
| 4756 | 0 | 491.4865 | -491.4865
| 4757 | 0 | 631.0961 | -631.0961
| 4758 | 0 | 4627.9094 | -4627.9094
| 4759 | 0 | 5665.2014 | -5665.2014
| 4760 | 0 | 8394.1918 | -8394.1918
| 4761 | 0 | 11519.0878 | -11519.0878
| 4762 | 0 | 12880.2462 | -12880.2462
| 4763 | 0 | 14107.9638 | -14107.9638
| 4764 | 0 | 14922.8311 | -14922.8311
| 4765 | 0 | 15577.9721 | -15577.9721
| 4766 | 0 | 16104.4376 | -16104.4376
| 4767 | 0 | 16457.0778 | -16457.0778
| 4768 | 0 | 16466.9039 | -16466.9039
| 4769 | 0 | 16006.5994 | -16006.5994
| 4770 | 0 | 11173.0344 | -11173.0344
| 4771 | 0 | 10090.7619 | -10090.7619
| 4772 | 0 | 8538.8002 | -8538.8002
| 4773 | 0 | 3758.8198 | -3758.8198
| 4774 | 0 | 1576.5226 | -1576.5226
| 4775 | 0 | 1398.7441 | -1398.7441
| 4776 | 0 | 1000.2674 | -1000.2674
| 4777 | 0 | 847.3123 | -847.3123
| 4778 | 0 | 490.6475 | -490.6475
| 4779 | 0 | 365.072 | -365.072
| 4780 | 0 | 259.4119 | -259.4119
| 4781 | 0 | 470.6525 | -470.6525
| 4782 | 14.8894 | 4782.0137 | -4767.1243
| 4783 | 0 | 5345.9629 | -5345.9629
| 4784 | 0 | 7721.8064 | -7721.8064
| 4785 | 0 | 11648.1906 | -11648.1906
| 4786 | 0 | 13859.0458 | -13859.0458
| 4787 | 0 | 15657.2751 | -15657.2751
| 4788 | 0 | 17055.2342 | -17055.2342
| 4789 | 0 | 18415.1509 | -18415.1509
| 4790 | 0 | 19184.7204 | -19184.7204
| 4791 | 0 | 19398.9563 | -19398.9563
| 4792 | 0 | 19184.6422 | -19184.6422
| 4793 | 0 | 18116.202 | -18116.202
| 4794 | 0 | 11910.2792 | -11910.2792
| 4795 | 0 | 9324.7886 | -9324.7886
| 4796 | 0 | 7226.3261 | -7226.3261
| 4797 | 0 | 3336.0202 | -3336.0202
| 4798 | 0 | 1346.4365 | -1346.4365
| 4799 | 0 | 1039.1006 | -1039.1006
| 4800 | 0 | 849.8597 | -849.8597
| 4801 | 0 | 527.8053 | -527.8053
| 4802 | 0 | 373.869 | -373.869
| 4803 | 0 | 246.8977 | -246.8977
| 4804 | 0 | 147.2396 | -147.2396
| 4805 | 0 | 173.4608 | -173.4608
| 4806 | 142.2081 | 2069.0465 | -1926.8385
| 4807 | 0 | 2238.6927 | -2238.6927
| 4808 | 0 | 2740.0224 | -2740.0224
| 4809 | 0 | 4962.3645 | -4962.3645
| 4810 | 0 | 8062.6757 | -8062.6757
| 4811 | 0 | 10032.7316 | -10032.7316
| 4812 | 0 | 11891.2202 | -11891.2202
| 4813 | 0 | 12855.952 | -12855.952
| 4814 | 0 | 13760.3608 | -13760.3608
| 4815 | 0 | 14625.5632 | -14625.5632
| 4816 | 0 | 15530.7099 | -15530.7099
| 4817 | 0 | 15037.2799 | -15037.2799
| 4818 | 0 | 10671.7022 | -10671.7022
| 4819 | 0 | 9107.4373 | -9107.4373
| 4820 | 0 | 7768.7866 | -7768.7866
| 4821 | 0 | 6113.8374 | -6113.8374
| 4822 | 0 | 2482.1414 | -2482.1414
| 4823 | 0 | 2071.1967 | -2071.1967
| 4824 | 0 | 1758.8405 | -1758.8405
| 4825 | 0 | 1571.6787 | -1571.6787
| 4826 | 0 | 1318.9312 | -1318.9312
| 4827 | 0 | 1121.209 | -1121.209
| 4828 | 0 | 909.4857 | -909.4857
| 4829 | 0 | 1016.7512 | -1016.7512
| 4830 | 0 | 1361.267 | -1361.267
| 4831 | 0 | 1969.8395 | -1969.8395
| 4832 | 0 | 3326.9956 | -3326.9956
| 4833 | 0 | 5565.2594 | -5565.2594
| 4834 | 0 | 8077.0494 | -8077.0494
| 4835 | 0 | 9291.3455 | -9291.3455
| 4836 | 0 | 10653.119 | -10653.119
| 4837 | 0 | 11481.5383 | -11481.5383
| 4838 | 0 | 11139.0835 | -11139.0835
| 4839 | 0 | 10295.4219 | -10295.4219
| 4840 | 0 | 9361.3272 | -9361.3272
| 4841 | 0 | 8451.0776 | -8451.0776
| 4842 | 0 | 6838.1586 | -6838.1586
| 4843 | 0 | 2868.4489 | -2868.4489
| 4844 | 0 | 2501.8786 | -2501.8786
| 4845 | 0 | 2180.8916 | -2180.8916
| 4846 | 0 | 2023.2636 | -2023.2636
| 4847 | 0 | 1635.6143 | -1635.6143
| 4848 | 0 | 1135.0993 | -1135.0993
| 4849 | 0 | 835.9788 | -835.9788
| 4850 | 0 | 421.0413 | -421.0413
| 4851 | 0 | 235.9722 | -235.9722
| 4852 | 0 | 104.6611 | -104.6611
| 4853 | 0 | 59.9498 | -59.9498
| 4854 | 454.9272 | 1482.2933 | -1027.3661
| 4855 | 159.3436 | 1170.3967 | -1011.0531
| 4856 | 0 | 3292.2701 | -3292.2701
| 4857 | 0 | 4086.2828 | -4086.2828
| 4858 | 0 | 4995.539 | -4995.539
| 4859 | 0 | 6527.4051 | -6527.4051
| 4860 | 0 | 7462.6899 | -7462.6899
| 4861 | 0 | 8360.1604 | -8360.1604
| 4862 | 0 | 8668.307 | -8668.307
| 4863 | 0 | 8379.2001 | -8379.2001
| 4864 | 0 | 7939.7739 | -7939.7739
| 4865 | 0 | 6984.9268 | -6984.9268
| 4866 | 0 | 3723.2377 | -3723.2377
| 4867 | 0 | 2294.1416 | -2294.1416
| 4868 | 0 | 896.1526 | -896.1526
| 4869 | 0 | 493.7836 | -493.7836
| 4870 | 0.76187 | 11.1908 | -10.429
| 4871 | 8.2238 | 0 | 8.2238
| 4872 | 16.4404 | 0 | 16.4404
| 4873 | 25.3671 | 0 | 25.3671
| 4874 | 34.4866 | 0 | 34.4866
| 4875 | 45.0033 | 0 | 45.0033
| 4876 | 61.4419 | 0 | 61.4419
| 4877 | 57.7882 | 0 | 57.7882
| 4878 | 2419.5935 | 204.611 | 2214.9825
| 4879 | 1187.9199 | 269.6265 | 918.2934
| 4880 | 286.5924 | 1723.1378 | -1436.5453
| 4881 | 0 | 2923.9896 | -2923.9896
| 4882 | 0 | 4229.732 | -4229.732
| 4883 | 0 | 5486.7639 | -5486.7639
| 4884 | 0 | 6445.1308 | -6445.1308
| 4885 | 0 | 7530.8014 | -7530.8014
| 4886 | 0 | 8305.0745 | -8305.0745
| 4887 | 0 | 8541.5379 | -8541.5379
| 4888 | 0 | 8533.1059 | -8533.1059
| 4889 | 0 | 8159.7769 | -8159.7769
| 4890 | 0 | 5222.9393 | -5222.9393
| 4891 | 0 | 4573.9984 | -4573.9984
| 4892 | 0 | 3419.3364 | -3419.3364
| 4893 | 0 | 1360.019 | -1360.019
| 4894 | 0 | 170.6124 | -170.6124
| 4895 | 0 | 35.4048 | -35.4048
| 4896 | 0.040862 | 1.1062 | -1.0654
| 4897 | 5.4073 | 0 | 5.4073
| 4898 | 15.3232 | 0 | 15.3232
| 4899 | 29.6522 | 0 | 29.6522
| 4900 | 42.6616 | 0 | 42.6616
| 4901 | 38.191 | 0 | 38.191
| 4902 | 1907.5749 | 298.7832 | 1608.7917
| 4903 | 729.4852 | 424.3957 | 305.0895
| 4904 | 28.9821 | 2891.2124 | -2862.2303
| 4905 | 0 | 4563.426 | -4563.426
| 4906 | 0 | 7121.2396 | -7121.2396
| 4907 | 0 | 9085.344 | -9085.344
| 4908 | 0 | 10116.3094 | -10116.3094
| 4909 | 0 | 11013.9553 | -11013.9553
| 4910 | 0 | 11417.7006 | -11417.7006
| 4911 | 0 | 11524.3864 | -11524.3864
| 4912 | 0 | 11363.2967 | -11363.2967
| 4913 | 0 | 10772.3361 | -10772.3361
| 4914 | 0 | 6777.2558 | -6777.2558
| 4915 | 0 | 5625.287 | -5625.287
| 4916 | 0 | 4677.4195 | -4677.4195
| 4917 | 0 | 2256.7027 | -2256.7027
| 4918 | 0 | 736.1042 | -736.1042
| 4919 | 0 | 777.4939 | -777.4939
| 4920 | 0 | 642.0509 | -642.0509
| 4921 | 0 | 598.4579 | -598.4579
| 4922 | 0 | 548.7504 | -548.7504
| 4923 | 0 | 488.5413 | -488.5413
| 4924 | 0 | 431.5228 | -431.5228
| 4925 | 0 | 362.8889 | -362.8889
| 4926 | 19.9639 | 1691.7687 | -1671.8048
| 4927 | 23.2365 | 1139.1447 | -1115.9082
| 4928 | 0 | 3402.8674 | -3402.8674
| 4929 | 0 | 4048.991 | -4048.991
| 4930 | 0 | 4372.714 | -4372.714
| 4931 | 0 | 5374.3752 | -5374.3752
| 4932 | 0 | 6817.1026 | -6817.1026
| 4933 | 0 | 8235.2352 | -8235.2352
| 4934 | 0 | 9078.8735 | -9078.8735
| 4935 | 0 | 9165.7242 | -9165.7242
| 4936 | 0 | 9105.4001 | -9105.4001
| 4937 | 0 | 8755.8541 | -8755.8541
| 4938 | 0 | 5466.0176 | -5466.0176
| 4939 | 0 | 4678.0103 | -4678.0103
| 4940 | 0 | 3578.3553 | -3578.3553
| 4941 | 0 | 1867.9408 | -1867.9408
| 4942 | 0 | 397.7124 | -397.7124
| 4943 | 0 | 192.7293 | -192.7293
| 4944 | 0 | 42.5311 | -42.5311
| 4945 | 0.3757 | 0.65012 | -0.27443
| 4946 | 6.8564 | 0 | 6.8564
| 4947 | 15.5121 | 0 | 15.5121
| 4948 | 27.3005 | 0 | 27.3005
| 4949 | 26.3248 | 0 | 26.3248
| 4950 | 1463.8279 | 252.7814 | 1211.0465
| 4951 | 831.9683 | 283.9132 | 548.0551
| 4952 | 170.6771 | 1833.381 | -1662.7038
| 4953 | 0 | 2807.4567 | -2807.4567
| 4954 | 0 | 3375.8046 | -3375.8046
| 4955 | 0 | 4559.3948 | -4559.3948
| 4956 | 0 | 5602.5827 | -5602.5827
| 4957 | 0 | 6490.2125 | -6490.2125
| 4958 | 0 | 7027.1106 | -7027.1106
| 4959 | 0 | 6888.6806 | -6888.6806
| 4960 | 0 | 6529.4534 | -6529.4534
| 4961 | 0 | 5748.4658 | -5748.4658
| 4962 | 0 | 2815.9879 | -2815.9879
| 4963 | 0 | 1581.699 | -1581.699
| 4964 | 0 | 538.6428 | -538.6428
| 4965 | 0 | 346.1895 | -346.1895
| 4966 | 1.362 | 0.77323 | 0.58877
| 4967 | 9.8633 | 0 | 9.8633
| 4968 | 22.9544 | 0 | 22.9544
| 4969 | 34.7479 | 0 | 34.7479
| 4970 | 49.534 | 0 | 49.534
| 4971 | 84.1825 | 0 | 84.1825
| 4972 | 136.8396 | 0 | 136.8396
| 4973 | 142.5074 | 0 | 142.5074
| 4974 | 3090.2265 | 84.2075 | 3006.019
| 4975 | 1788.8986 | 50.7669 | 1738.1317
| 4976 | 999.8738 | 148.6847 | 851.1891
| 4977 | 82.0599 | 220.1189 | -138.059
| 4978 | 0.93023 | 378.723 | -377.7928
| 4979 | 0 | 954.9462 | -954.9462
| 4980 | 0 | 1687.7895 | -1687.7895
| 4981 | 0 | 2626.7676 | -2626.7676
| 4982 | 0 | 2896.1735 | -2896.1735
| 4983 | 0 | 3324.1012 | -3324.1012
| 4984 | 0 | 3744.762 | -3744.762
| 4985 | 0 | 3663.8246 | -3663.8246
| 4986 | 0 | 1763.8685 | -1763.8685
| 4987 | 0 | 979.932 | -979.932
| 4988 | 0 | 214.953 | -214.953
| 4989 | 0 | 32.9752 | -32.9752
| 4990 | 4.8171 | 0 | 4.8171
| 4991 | 27.2402 | 0 | 27.2402
| 4992 | 48.907 | 0 | 48.907
| 4993 | 79.794 | 0 | 79.794
| 4994 | 129.9307 | 0 | 129.9307
| 4995 | 190.2186 | 0 | 190.2186
| 4996 | 254.895 | 0 | 254.895
| 4997 | 248.2523 | 0 | 248.2523
| 4998 | 177.4221 | 0 | 177.4221
| 4999 | 94.6183 | 0 | 94.6183
| 5000 | 2293.2837 | 0 | 2293.2837
| 5001 | 730.1225 | 0 | 730.1225
| 5002 | 0 | 8.5611 | -8.5611
| 5003 | 0 | 47.717 | -47.717
| 5004 | 0 | 1024.5079 | -1024.5079
| 5005 | 0 | 1963.3363 | -1963.3363
| 5006 | 0 | 2424.3568 | -2424.3568
| 5007 | 0 | 2829.6378 | -2829.6378
| 5008 | 0 | 3131.2414 | -3131.2414
| 5009 | 0 | 2844.7472 | -2844.7472
| 5010 | 0 | 1887.2116 | -1887.2116
| 5011 | 0 | 660.3239 | -660.3239
| 5012 | 0 | 491.095 | -491.095
| 5013 | 0 | 244.0302 | -244.0302
| 5014 | 0 | 103.5537 | -103.5537
| 5015 | 0 | 21.0449 | -21.0449
| 5016 | 0 | 0.44665 | -0.44665
| 5017 | 1.9734 | 0 | 1.9734
| 5018 | 7.0282 | 0 | 7.0282
| 5019 | 11.9087 | 0 | 11.9087
| 5020 | 16.3301 | 0 | 16.3301
| 5021 | 13.8591 | 0 | 13.8591
| 5022 | 1400.2109 | 289.8224 | 1110.3885
| 5023 | 624.9843 | 156.0435 | 468.9408
| 5024 | 44.0377 | 1418.8722 | -1374.8346
| 5025 | 0 | 2999.32 | -2999.32
| 5026 | 0 | 4672.2076 | -4672.2076
| 5027 | 0 | 6623.9672 | -6623.9672
| 5028 | 0 | 7928.5019 | -7928.5019
| 5029 | 0 | 9114.7093 | -9114.7093
| 5030 | 0 | 9821.8813 | -9821.8813
| 5031 | 0 | 9721.7277 | -9721.7277
| 5032 | 0 | 9342.4649 | -9342.4649
| 5033 | 0 | 8529.386 | -8529.386
| 5034 | 0 | 5325.3 | -5325.3
| 5035 | 0 | 4278.1619 | -4278.1619
| 5036 | 0 | 3294.7428 | -3294.7428
| 5037 | 0 | 1772.5398 | -1772.5398
| 5038 | 0 | 397.9206 | -397.9206
| 5039 | 0 | 269.1663 | -269.1663
| 5040 | 0 | 152.3384 | -152.3384
| 5041 | 0 | 75.4124 | -75.4124
| 5042 | 0 | 34.3956 | -34.3956
| 5043 | 0 | 12.5941 | -12.5941
| 5044 | 0 | 1.2531 | -1.2531
| 5045 | 0 | 0 | 0
| 5046 | 548.1487 | 475.0422 | 73.1064
| 5047 | 158.6657 | 438.6709 | -280.0052
| 5048 | 0 | 2579.6704 | -2579.6704
| 5049 | 0 | 3194.2169 | -3194.2169
| 5050 | 0 | 3516.3496 | -3516.3496
| 5051 | 0 | 4530.8072 | -4530.8072
| 5052 | 0 | 6110.6659 | -6110.6659
| 5053 | 0 | 7542.1019 | -7542.1019
| 5054 | 0 | 8657.4364 | -8657.4364
| 5055 | 0 | 9386.0122 | -9386.0122
| 5056 | 0 | 9863.0683 | -9863.0683
| 5057 | 0 | 9537.2217 | -9537.2217
| 5058 | 0 | 5973.1126 | -5973.1126
| 5059 | 0 | 4936.8237 | -4936.8237
| 5060 | 0 | 3347.6048 | -3347.6048
| 5061 | 0 | 1077.4748 | -1077.4748
| 5062 | 0 | 143.7391 | -143.7391
| 5063 | 0 | 27.0988 | -27.0988
| 5064 | 1.6869 | 0 | 1.6869
| 5065 | 7.6473 | 0 | 7.6473
| 5066 | 11.8811 | 0 | 11.8811
| 5067 | 15.6416 | 0 | 15.6416
| 5068 | 17.3325 | 0 | 17.3325
| 5069 | 12.7444 | 0 | 12.7444
| 5070 | 1442.2907 | 387.3714 | 1054.9193
| 5071 | 617.383 | 330.8967 | 286.4862
| 5072 | 30.9597 | 2924.4273 | -2893.4676
| 5073 | 0 | 4374.1454 | -4374.1454
| 5074 | 0 | 6002.7034 | -6002.7034
| 5075 | 0 | 8168.7768 | -8168.7768
| 5076 | 0 | 9833.8969 | -9833.8969
| 5077 | 0 | 11362.8003 | -11362.8003
| 5078 | 0 | 12452.0075 | -12452.0075
| 5079 | 0 | 13117.9249 | -13117.9249
| 5080 | 0 | 13349.6895 | -13349.6895
| 5081 | 0 | 12994.8631 | -12994.8631
| 5082 | 0 | 8818.4368 | -8818.4368
| 5083 | 0 | 7978.5755 | -7978.5755
| 5084 | 0 | 6906.1182 | -6906.1182
| 5085 | 0 | 3006.7903 | -3006.7903
| 5086 | 0 | 1072.5716 | -1072.5716
| 5087 | 0 | 943.4427 | -943.4427
| 5088 | 0 | 661.983 | -661.983
| 5089 | 0 | 257.5273 | -257.5273
| 5090 | 0 | 96.691 | -96.691
| 5091 | 0 | 11.6524 | -11.6524
| 5092 | 5.0306 | 0 | 5.0306
| 5093 | 11.7241 | 0 | 11.7241
| 5094 | 1278.7391 | 341.2254 | 937.5137
| 5095 | 776.4139 | 496.1464 | 280.2675
| 5096 | 144.3352 | 2044.8986 | -1900.5634
| 5097 | 0 | 3106.0417 | -3106.0417
| 5098 | 0 | 3857.1083 | -3857.1083
| 5099 | 0 | 5478.3231 | -5478.3231
| 5100 | 0 | 6569.4986 | -6569.4986
| 5101 | 0 | 7478.4238 | -7478.4238
| 5102 | 0 | 8139.5731 | -8139.5731
| 5103 | 0 | 8282.5966 | -8282.5966
| 5104 | 0 | 7694.9805 | -7694.9805
| 5105 | 0 | 7002.2557 | -7002.2557
| 5106 | 0 | 4355.8646 | -4355.8646
| 5107 | 0 | 2994.217 | -2994.217
| 5108 | 0 | 1086.1019 | -1086.1019
| 5109 | 0 | 476.8853 | -476.8853
| 5110 | 0 | 14.3449 | -14.3449
| 5111 | 3.9728 | 0 | 3.9728
| 5112 | 15.5063 | 0 | 15.5063
| 5113 | 32.7934 | 0 | 32.7934
| 5114 | 46.8106 | 0 | 46.8106
| 5115 | 60.903 | 0 | 60.903
| 5116 | 88.0858 | 0 | 88.0858
| 5117 | 117.5206 | 0 | 117.5206
| 5118 | 3207.7457 | 170.9567 | 3036.789
| 5119 | 1695.6094 | 170.7786 | 1524.8309
| 5120 | 628.4694 | 1004.8756 | -376.4062
| 5121 | 3.9159 | 2464.0192 | -2460.1032
| 5122 | 0 | 3395.9782 | -3395.9782
| 5123 | 0 | 4983.2386 | -4983.2386
| 5124 | 0 | 6036.3546 | -6036.3546
| 5125 | 0 | 6956.7556 | -6956.7556
| 5126 | 0 | 7551.3099 | -7551.3099
| 5127 | 0 | 7634.2862 | -7634.2862
| 5128 | 0 | 7401.1092 | -7401.1092
| 5129 | 0 | 6842.2304 | -6842.2304
| 5130 | 0 | 4296.9334 | -4296.9334
| 5131 | 0 | 3282.3469 | -3282.3469
| 5132 | 0 | 983.599 | -983.599
| 5133 | 0 | 418.9131 | -418.9131
| 5134 | 0.6301 | 0.018452 | 0.61164
| 5135 | 8.177 | 0 | 8.177
| 5136 | 23.0925 | 0 | 23.0925
| 5137 | 33.3318 | 0 | 33.3318
| 5138 | 46.3009 | 0 | 46.3009
| 5139 | 71.7185 | 0 | 71.7185
| 5140 | 112.7543 | 0 | 112.7543
| 5141 | 155.3413 | 0 | 155.3413
| 5142 | 3278.8243 | 84.388 | 3194.4363
| 5143 | 1841.3163 | 63.4181 | 1777.8982
| 5144 | 800.6695 | 197.6174 | 603.052
| 5145 | 3.8137 | 282.39 | -278.5762
| 5146 | 0 | 616.1331 | -616.1331
| 5147 | 0 | 2440.3536 | -2440.3536
| 5148 | 0 | 3567.3808 | -3567.3808
| 5149 | 0 | 4393.6506 | -4393.6506
| 5150 | 0 | 4731.6092 | -4731.6092
| 5151 | 0 | 5117.219 | -5117.219
| 5152 | 0 | 5448.4863 | -5448.4863
| 5153 | 0 | 5383.9858 | -5383.9858
| 5154 | 0 | 3287.8165 | -3287.8165
| 5155 | 0 | 2271.2267 | -2271.2267
| 5156 | 0 | 1070.712 | -1070.712
| 5157 | 0 | 194.0428 | -194.0428
| 5158 | 0 | 45.1354 | -45.1354
| 5159 | 0 | 2.298 | -2.298
| 5160 | 2.8335 | 0 | 2.8335
| 5161 | 10.1553 | 0 | 10.1553
| 5162 | 26.5581 | 0 | 26.5581
| 5163 | 38.0814 | 0 | 38.0814
| 5164 | 46.2783 | 0 | 46.2783
| 5165 | 62.2575 | 0 | 62.2575
| 5166 | 48.405 | 0 | 48.405
| 5167 | 17.9586 | 0 | 17.9586
| 5168 | 1241.7967 | 2.9412 | 1238.8555
| 5169 | 146.7232 | 152.084 | -5.3609
| 5170 | 0 | 299.6162 | -299.6162
| 5171 | 0 | 579.7575 | -579.7575
| 5172 | 0 | 2864.4449 | -2864.4449
| 5173 | 0 | 3639.0037 | -3639.0037
| 5174 | 0 | 4487.9929 | -4487.9929
| 5175 | 0 | 4558.5158 | -4558.5158
| 5176 | 0 | 4868.8695 | -4868.8695
| 5177 | 0 | 4949.7735 | -4949.7735
| 5178 | 0 | 4208.0637 | -4208.0637
| 5179 | 0 | 1629.5329 | -1629.5329
| 5180 | 0 | 1108.8306 | -1108.8306
| 5181 | 0 | 506.353 | -506.353
| 5182 | 0 | 224.1633 | -224.1633
| 5183 | 0 | 75.604 | -75.604
| 5184 | 0.081586 | 4.8268 | -4.7452
| 5185 | 3.4204 | 0 | 3.4204
| 5186 | 8.8918 | 0 | 8.8918
| 5187 | 18.59 | 0 | 18.59
| 5188 | 27.7969 | 0 | 27.7969
| 5189 | 34.2097 | 0 | 34.2097
| 5190 | 1814.0775 | 228.5195 | 1585.558
| 5191 | 999.038 | 384.7117 | 614.3263
| 5192 | 58.9551 | 2497.4166 | -2438.4615
| 5193 | 0 | 4426.7125 | -4426.7125
| 5194 | 0 | 7197.8932 | -7197.8932
| 5195 | 0 | 9286.733 | -9286.733
| 5196 | 0 | 10744.4921 | -10744.4921
| 5197 | 0 | 11607.2159 | -11607.2159
| 5198 | 0 | 12016.0625 | -12016.0625
| 5199 | 0 | 11943.831 | -11943.831
| 5200 | 0 | 11450.2833 | -11450.2833
| 5201 | 0 | 10955.9844 | -10955.9844
| 5202 | 0 | 7338.5354 | -7338.5354
| 5203 | 0 | 6134.5336 | -6134.5336
| 5204 | 0 | 4906.252 | -4906.252
| 5205 | 0 | 2369.1298 | -2369.1298
| 5206 | 0 | 716.9627 | -716.9627
| 5207 | 0 | 730.9207 | -730.9207
| 5208 | 0 | 515.5069 | -515.5069
| 5209 | 0 | 289.2878 | -289.2878
| 5210 | 0 | 134.9269 | -134.9269
| 5211 | 0 | 46.3876 | -46.3876
| 5212 | 0 | 5.9357 | -5.9357
| 5213 | 0 | 0 | 0
| 5214 | 729.6055 | 709.252 | 20.3535
| 5215 | 186.7696 | 999.8679 | -813.0983
| 5216 | 0 | 3924.7217 | -3924.7217
| 5217 | 0 | 5657.0732 | -5657.0732
| 5218 | 0 | 7962.5068 | -7962.5068
| 5219 | 0 | 9850.2341 | -9850.2341
| 5220 | 0 | 11153.4025 | -11153.4025
| 5221 | 0 | 11890.7512 | -11890.7512
| 5222 | 0 | 11802.5082 | -11802.5082
| 5223 | 0 | 11138.1481 | -11138.1481
| 5224 | 0 | 10626.6037 | -10626.6037
| 5225 | 0 | 9975.5511 | -9975.5511
| 5226 | 0 | 6464.7804 | -6464.7804
| 5227 | 0 | 5462.5301 | -5462.5301
| 5228 | 0 | 4217.8573 | -4217.8573
| 5229 | 0 | 2113.5723 | -2113.5723
| 5230 | 0 | 579.8942 | -579.8942
| 5231 | 0 | 408.5683 | -408.5683
| 5232 | 0 | 227.2224 | -227.2224
| 5233 | 0 | 124.8543 | -124.8543
| 5234 | 0 | 61.0103 | -61.0103
| 5235 | 0 | 30.9873 | -30.9873
| 5236 | 0 | 16.5543 | -16.5543
| 5237 | 0 | 7.3339 | -7.3339
| 5238 | 508.6221 | 690.1378 | -181.5157
| 5239 | 19.1177 | 1535.4514 | -1516.3337
| 5240 | 0 | 4388.9473 | -4388.9473
| 5241 | 0 | 5752.5528 | -5752.5528
| 5242 | 0 | 7942.1515 | -7942.1515
| 5243 | 0 | 9892.9492 | -9892.9492
| 5244 | 0 | 11011.9865 | -11011.9865
| 5245 | 0 | 11466.6578 | -11466.6578
| 5246 | 0 | 11693.5635 | -11693.5635
| 5247 | 0 | 11666.5414 | -11666.5414
| 5248 | 0 | 11523.671 | -11523.671
| 5249 | 0 | 11443.8936 | -11443.8936
| 5250 | 0 | 6748.6496 | -6748.6496
| 5251 | 0 | 5399.497 | -5399.497
| 5252 | 0 | 4980.8806 | -4980.8806
| 5253 | 0 | 2558.7415 | -2558.7415
| 5254 | 0 | 808.7022 | -808.7022
| 5255 | 0 | 527.9048 | -527.9048
| 5256 | 0 | 263.8264 | -263.8264
| 5257 | 0 | 160.1572 | -160.1572
| 5258 | 0 | 104.7286 | -104.7286
| 5259 | 0 | 73.2057 | -73.2057
| 5260 | 0 | 60.3623 | -60.3623
| 5261 | 0 | 59.5646 | -59.5646
| 5262 | 353.042 | 1169.4292 | -816.3871
| 5263 | 26.4255 | 1248.989 | -1222.5636
| 5264 | 0 | 4621.8845 | -4621.8845
| 5265 | 0 | 6048.4205 | -6048.4205
| 5266 | 0 | 8459.4181 | -8459.4181
| 5267 | 0 | 10029.9771 | -10029.9771
| 5268 | 0 | 11142.5296 | -11142.5296
| 5269 | 0 | 12555.9055 | -12555.9055
| 5270 | 0 | 13883.421 | -13883.421
| 5271 | 0 | 14346.3807 | -14346.3807
| 5272 | 0 | 13982.4171 | -13982.4171
| 5273 | 0 | 13434.0299 | -13434.0299
| 5274 | 0 | 9115.8568 | -9115.8568
| 5275 | 0 | 7675.9643 | -7675.9643
| 5276 | 0 | 5450.8515 | -5450.8515
| 5277 | 0 | 2640.4532 | -2640.4532
| 5278 | 0 | 636.298 | -636.298
| 5279 | 0 | 296.9461 | -296.9461
| 5280 | 0 | 95.5718 | -95.5718
| 5281 | 0.46597 | 12.1937 | -11.7278
| 5282 | 6.474 | 0 | 6.474
| 5283 | 11.4849 | 0 | 11.4849
| 5284 | 19.4221 | 0 | 19.4221
| 5285 | 21.5549 | 0 | 21.5549
| 5286 | 1533.1177 | 330.6184 | 1202.4992
| 5287 | 696.1191 | 629.7435 | 66.3756
| 5288 | 3.3662 | 3650.0625 | -3646.6963
| 5289 | 0 | 5211.2602 | -5211.2602
| 5290 | 0 | 7656.0024 | -7656.0024
| 5291 | 0 | 10222.2039 | -10222.2039
| 5292 | 0 | 11611.4207 | -11611.4207
| 5293 | 0 | 12502.1173 | -12502.1173
| 5294 | 0 | 13224.3374 | -13224.3374
| 5295 | 0 | 13088.5597 | -13088.5597
| 5296 | 0 | 12530.8518 | -12530.8518
| 5297 | 0 | 12000.0543 | -12000.0543
| 5298 | 0 | 8045.5139 | -8045.5139
| 5299 | 0 | 6891.1877 | -6891.1877
| 5300 | 0 | 4878.9052 | -4878.9052
| 5301 | 0 | 2053.4579 | -2053.4579
| 5302 | 0 | 625.0974 | -625.0974
| 5303 | 0 | 349.9482 | -349.9482
| 5304 | 0 | 114.3002 | -114.3002
| 5305 | 0 | 33.2258 | -33.2258
| 5306 | 0.93061 | 3.2578 | -2.3272
| 5307 | 3.52 | 0 | 3.52
| 5308 | 8.0574 | 0 | 8.0574
| 5309 | 14.5326 | 0 | 14.5326
| 5310 | 1331.7378 | 263.5509 | 1068.1869
| 5311 | 696.1851 | 232.8263 | 463.3588
| 5312 | 33.5888 | 1108.903 | -1075.3142
| 5313 | 0 | 1974.8116 | -1974.8116
| 5314 | 0 | 4827.9838 | -4827.9838
| 5315 | 0 | 6833.762 | -6833.762
| 5316 | 0 | 8530.7635 | -8530.7635
| 5317 | 0 | 9109.4466 | -9109.4466
| 5318 | 0 | 8825.0541 | -8825.0541
| 5319 | 0 | 8371.8511 | -8371.8511
| 5320 | 0 | 8275.0799 | -8275.0799
| 5321 | 0 | 8109.4699 | -8109.4699
| 5322 | 0 | 5706.0014 | -5706.0014
| 5323 | 0 | 4879.725 | -4879.725
| 5324 | 0 | 3953.0745 | -3953.0745
| 5325 | 0 | 2643.2325 | -2643.2325
| 5326 | 0 | 1197.7888 | -1197.7888
| 5327 | 0 | 1036.8613 | -1036.8613
| 5328 | 0 | 847.5891 | -847.5891
| 5329 | 0 | 755.9333 | -755.9333
| 5330 | 0 | 613.2428 | -613.2428
| 5331 | 0 | 501.5147 | -501.5147
| 5332 | 0 | 343.8764 | -343.8764
| 5333 | 0 | 294.5444 | -294.5444
| 5334 | 0 | 289.9868 | -289.9868
| 5335 | 0 | 550.4287 | -550.4287
| 5336 | 28.9415 | 745.5402 | -716.5987
| 5337 | 0 | 692.3749 | -692.3749
| 5338 | 0 | 1707.2466 | -1707.2466
| 5339 | 0 | 3269.1727 | -3269.1727
| 5340 | 0 | 4855.8311 | -4855.8311
| 5341 | 0 | 5338.2462 | -5338.2462
| 5342 | 0 | 5852.5454 | -5852.5454
| 5343 | 0 | 5475.6895 | -5475.6895
| 5344 | 0 | 6087.4976 | -6087.4976
| 5345 | 0 | 6025.1523 | -6025.1523
| 5346 | 0 | 4619.3913 | -4619.3913
| 5347 | 0 | 1827.3247 | -1827.3247
| 5348 | 0 | 1387.8098 | -1387.8098
| 5349 | 0 | 1006.9034 | -1006.9034
| 5350 | 0 | 790.8403 | -790.8403
| 5351 | 0 | 381.6285 | -381.6285
| 5352 | 0 | 217.3658 | -217.3658
| 5353 | 0 | 91.1804 | -91.1804
| 5354 | 0 | 32.679 | -32.679
| 5355 | 0 | 4.1166 | -4.1166
| 5356 | 0.34858 | 0 | 0.34858
| 5357 | 4.1127 | 0 | 4.1127
| 5358 | 1187.4076 | 495.4339 | 691.9737
| 5359 | 758.5279 | 513.8225 | 244.7055
| 5360 | 131.4117 | 2051.6834 | -1920.2717
| 5361 | 0 | 2866.5157 | -2866.5157
| 5362 | 0 | 3619.2099 | -3619.2099
| 5363 | 0 | 5409.7274 | -5409.7274
| 5364 | 0 | 6686.068 | -6686.068
| 5365 | 0 | 7666.2353 | -7666.2353
| 5366 | 0 | 8304.531 | -8304.531
| 5367 | 0 | 8278.5635 | -8278.5635
| 5368 | 0 | 7762.4729 | -7762.4729
| 5369 | 0 | 7120.0471 | -7120.0471
| 5370 | 0 | 4295.6548 | -4295.6548
| 5371 | 0 | 2843.8183 | -2843.8183
| 5372 | 0 | 862.6211 | -862.6211
| 5373 | 0 | 482.1231 | -482.1231
| 5374 | 0 | 44.3178 | -44.3178
| 5375 | 0.93152 | 7.9744 | -7.0429
| 5376 | 13.4929 | 0 | 13.4929
| 5377 | 28.0247 | 0 | 28.0247
| 5378 | 44.5892 | 0 | 44.5892
| 5379 | 67.8234 | 0 | 67.8234
| 5380 | 101.9541 | 0 | 101.9541
| 5381 | 138.9301 | 0 | 138.9301
| 5382 | 3489.4049 | 120.6044 | 3368.8005
| 5383 | 1936.7424 | 97.6561 | 1839.0863
| 5384 | 745.6659 | 845.9687 | -100.3028
| 5385 | 2.9258 | 2263.2187 | -2260.2929
| 5386 | 0 | 3550.0966 | -3550.0966
| 5387 | 0 | 5493.8208 | -5493.8208
| 5388 | 0 | 6974.833 | -6974.833
| 5389 | 0 | 8652.3808 | -8652.3808
| 5390 | 0 | 10204.0887 | -10204.0887
| 5391 | 0 | 10843.1244 | -10843.1244
| 5392 | 0 | 10263.6666 | -10263.6666
| 5393 | 0 | 9823.4526 | -9823.4526
| 5394 | 0 | 6600.6824 | -6600.6824
| 5395 | 0 | 5911.3811 | -5911.3811
| 5396 | 0 | 4763.9605 | -4763.9605
| 5397 | 0 | 2201.0473 | -2201.0473
| 5398 | 0 | 707.3883 | -707.3883
| 5399 | 0 | 754.3315 | -754.3315
| 5400 | 0 | 717.8604 | -717.8604
| 5401 | 0 | 637.0785 | -637.0785
| 5402 | 0 | 632.4571 | -632.4571
| 5403 | 0 | 464.7968 | -464.7968
| 5404 | 0 | 358.139 | -358.139
| 5405 | 0 | 386.8978 | -386.8978
| 5406 | 0 | 2954.4311 | -2954.4311
| 5407 | 0 | 3816.1974 | -3816.1974
| 5408 | 0 | 6722.1898 | -6722.1898
| 5409 | 0 | 10587.2583 | -10587.2583
| 5410 | 0 | 12601.9964 | -12601.9964
| 5411 | 0 | 13518.6181 | -13518.6181
| 5412 | 0 | 14169.4612 | -14169.4612
| 5413 | 0 | 14602.0655 | -14602.0655
| 5414 | 0 | 14013.8935 | -14013.8935
| 5415 | 0 | 13488.5956 | -13488.5956
| 5416 | 0 | 13972.3387 | -13972.3387
| 5417 | 0 | 13668.4438 | -13668.4438
| 5418 | 0 | 9012.3045 | -9012.3045
| 5419 | 0 | 8665.7992 | -8665.7992
| 5420 | 0 | 8938.6529 | -8938.6529
| 5421 | 0 | 3976.4685 | -3976.4685
| 5422 | 0 | 1790.7932 | -1790.7932
| 5423 | 0 | 2001.9388 | -2001.9388
| 5424 | 0 | 1551.8147 | -1551.8147
| 5425 | 0 | 1314.3246 | -1314.3246
| 5426 | 0 | 1304.2589 | -1304.2589
| 5427 | 0 | 1190.6838 | -1190.6838
| 5428 | 0 | 911.6048 | -911.6048
| 5429 | 0 | 953.9911 | -953.9911
| 5430 | 0 | 5283.7926 | -5283.7926
| 5431 | 0 | 5583.1055 | -5583.1055
| 5432 | 0 | 7651.5548 | -7651.5548
| 5433 | 0 | 11071.991 | -11071.991
| 5434 | 0 | 12961.8621 | -12961.8621
| 5435 | 0 | 14936.7155 | -14936.7155
| 5436 | 0 | 16257.1701 | -16257.1701
| 5437 | 0 | 17544.33 | -17544.33
| 5438 | 0 | 18460.3406 | -18460.3406
| 5439 | 0 | 17645.1644 | -17645.1644
| 5440 | 0 | 17927.4435 | -17927.4435
| 5441 | 0 | 17847.0444 | -17847.0444
| 5442 | 0 | 10572.8479 | -10572.8479
| 5443 | 0 | 7889.7848 | -7889.7848
| 5444 | 0 | 6604.3525 | -6604.3525
| 5445 | 0 | 3288.1017 | -3288.1017
| 5446 | 0 | 1471.9269 | -1471.9269
| 5447 | 0 | 1256.7242 | -1256.7242
| 5448 | 0 | 1207.0382 | -1207.0382
| 5449 | 0 | 1128.9992 | -1128.9992
| 5450 | 0 | 920.9188 | -920.9188
| 5451 | 0 | 883.4823 | -883.4823
| 5452 | 0 | 643.5283 | -643.5283
| 5453 | 0 | 321.1914 | -321.1914
| 5454 | 64.231 | 2998.5136 | -2934.2826
| 5455 | 0 | 2994.1598 | -2994.1598
| 5456 | 0 | 4619.3479 | -4619.3479
| 5457 | 0 | 5028.5905 | -5028.5905
| 5458 | 0 | 5779.7142 | -5779.7142
| 5459 | 0 | 7060.3625 | -7060.3625
| 5460 | 0 | 7432.5337 | -7432.5337
| 5461 | 0 | 8298.9842 | -8298.9842
| 5462 | 0 | 8826.6093 | -8826.6093
| 5463 | 0 | 9010.8996 | -9010.8996
| 5464 | 0 | 8621.7441 | -8621.7441
| 5465 | 0 | 7879.7828 | -7879.7828
| 5466 | 0 | 4893.0201 | -4893.0201
| 5467 | 0 | 3871.2434 | -3871.2434
| 5468 | 0 | 2448.7884 | -2448.7884
| 5469 | 0 | 1116.4941 | -1116.4941
| 5470 | 0 | 206.9333 | -206.9333
| 5471 | 0 | 67.7432 | -67.7432
| 5472 | 0.17704 | 6.3641 | -6.1871
| 5473 | 6.6701 | 0 | 6.6701
| 5474 | 23.3219 | 0 | 23.3219
| 5475 | 35.7202 | 0 | 35.7202
| 5476 | 45.5884 | 0 | 45.5884
| 5477 | 59.8804 | 0 | 59.8804
| 5478 | 2834.3394 | 89.2366 | 2745.1027
| 5479 | 1511.5715 | 80.4339 | 1431.1376
| 5480 | 524.2609 | 266.1039 | 258.157
| 5481 | 0 | 908.7717 | -908.7717
| 5482 | 0 | 1798.1689 | -1798.1689
| 5483 | 0 | 3668.8998 | -3668.8998
| 5484 | 0 | 4942.4504 | -4942.4504
| 5485 | 0 | 5572.0127 | -5572.0127
| 5486 | 0 | 5819.6225 | -5819.6225
| 5487 | 0 | 6069.4727 | -6069.4727
| 5488 | 0 | 6376.6486 | -6376.6486
| 5489 | 0 | 6156.1566 | -6156.1566
| 5490 | 0 | 3828.908 | -3828.908
| 5491 | 0 | 2673.6647 | -2673.6647
| 5492 | 0 | 998.8343 | -998.8343
| 5493 | 0 | 249.8505 | -249.8505
| 5494 | 0 | 89.6028 | -89.6028
| 5495 | 0.19478 | 13.0226 | -12.8278
| 5496 | 7.5477 | 0 | 7.5477
| 5497 | 19.3854 | 0 | 19.3854
| 5498 | 31.7388 | 0 | 31.7388
| 5499 | 43.5646 | 0 | 43.5646
| 5500 | 58.2001 | 0 | 58.2001
| 5501 | 74.1103 | 0 | 74.1103
| 5502 | 79.8744 | 0 | 79.8744
| 5503 | 49.1175 | 0 | 49.1175
| 5504 | 2014.2541 | 0 | 2014.2541
| 5505 | 544.7988 | 0.36087 | 544.4379
| 5506 | 0 | 270.573 | -270.573
| 5507 | 0 | 645.3489 | -645.3489
| 5508 | 0 | 2674.691 | -2674.691
| 5509 | 0 | 3548.9991 | -3548.9991
| 5510 | 0 | 3880.6554 | -3880.6554
| 5511 | 0 | 3897.7003 | -3897.7003
| 5512 | 0 | 3774.739 | -3774.739
| 5513 | 0 | 3006.6039 | -3006.6039
| 5514 | 0 | 1926.8929 | -1926.8929
| 5515 | 0 | 828.0247 | -828.0247
| 5516 | 0 | 609.6325 | -609.6325
| 5517 | 0 | 347.3959 | -347.3959
| 5518 | 0 | 173.9876 | -173.9876
| 5519 | 0 | 56.3156 | -56.3156
| 5520 | 0 | 6.3609 | -6.3609
| 5521 | 4.1525 | 0 | 4.1525
| 5522 | 18.4718 | 0 | 18.4718
| 5523 | 33.4102 | 0 | 33.4102
| 5524 | 40.5839 | 0 | 40.5839
| 5525 | 34.6259 | 0 | 34.6259
| 5526 | 1646.4346 | 250.1585 | 1396.2761
| 5527 | 1069.5943 | 165.9006 | 903.6936
| 5528 | 158.2476 | 1810.742 | -1652.4943
| 5529 | 0 | 3178.2763 | -3178.2763
| 5530 | 0 | 3933.4207 | -3933.4207
| 5531 | 0 | 6159.5486 | -6159.5486
| 5532 | 0 | 7445.2111 | -7445.2111
| 5533 | 0 | 8831.3699 | -8831.3699
| 5534 | 0 | 9834.8756 | -9834.8756
| 5535 | 0 | 9516.3728 | -9516.3728
| 5536 | 0 | 8991.7695 | -8991.7695
| 5537 | 0 | 8550.5565 | -8550.5565
| 5538 | 0 | 5565.4433 | -5565.4433
| 5539 | 0 | 4558.6564 | -4558.6564
| 5540 | 0 | 3068.9467 | -3068.9467
| 5541 | 0 | 1545.5383 | -1545.5383
| 5542 | 0 | 320.8342 | -320.8342
| 5543 | 0 | 241.0418 | -241.0418
| 5544 | 0 | 144.4631 | -144.4631
| 5545 | 0 | 95.8372 | -95.8372
| 5546 | 0 | 55.0655 | -55.0655
| 5547 | 0 | 13.7359 | -13.7359
| 5548 | 0 | 0 | 0
| 5549 | 0 | 0 | 0
| 5550 | 630.1852 | 528.1643 | 102.0209
| 5551 | 285.0181 | 492.768 | -207.75
| 5552 | 0 | 2589.6108 | -2589.6108
| 5553 | 0 | 3593.5055 | -3593.5055
| 5554 | 0 | 4870.5878 | -4870.5878
| 5555 | 0 | 6297.6482 | -6297.6482
| 5556 | 0 | 7218.2723 | -7218.2723
| 5557 | 0 | 7983.705 | -7983.705
| 5558 | 0 | 9104.0286 | -9104.0286
| 5559 | 0 | 9499.8836 | -9499.8836
| 5560 | 0 | 8797.8095 | -8797.8095
| 5561 | 0 | 8088.9895 | -8088.9895
| 5562 | 0 | 4787.5684 | -4787.5684
| 5563 | 0 | 3697.5056 | -3697.5056
| 5564 | 0 | 2598.2635 | -2598.2635
| 5565 | 0 | 841.6373 | -841.6373
| 5566 | 0 | 119.0776 | -119.0776
| 5567 | 0 | 59.9494 | -59.9494
| 5568 | 0.28356 | 10.9317 | -10.6481
| 5569 | 2.7905 | 0 | 2.7905
| 5570 | 4.8437 | 0 | 4.8437
| 5571 | 7.1917 | 0 | 7.1917
| 5572 | 7.0062 | 0 | 7.0062
| 5573 | 7.5582 | 0 | 7.5582
| 5574 | 1184.1499 | 374.7042 | 809.4457
| 5575 | 726.4262 | 368.9758 | 357.4504
| 5576 | 84.9422 | 2045.8097 | -1960.8675
| 5577 | 0 | 3352.7742 | -3352.7742
| 5578 | 0 | 4128.9408 | -4128.9408
| 5579 | 0 | 5936.0352 | -5936.0352
| 5580 | 0 | 6709.6928 | -6709.6928
| 5581 | 0 | 7348.2602 | -7348.2602
| 5582 | 0 | 7646.6199 | -7646.6199
| 5583 | 0 | 7330.608 | -7330.608
| 5584 | 0 | 6920.3778 | -6920.3778
| 5585 | 0 | 6288.4859 | -6288.4859
| 5586 | 0 | 3743.7917 | -3743.7917
| 5587 | 0 | 2738.4078 | -2738.4078
| 5588 | 0 | 1572.2431 | -1572.2431
| 5589 | 0 | 839.31 | -839.31
| 5590 | 0 | 129.7608 | -129.7608
| 5591 | 0 | 43.8227 | -43.8227
| 5592 | 0 | 9.2811 | -9.2811
| 5593 | 0 | 0.67821 | -0.67821
| 5594 | 0.4619 | 0 | 0.4619
| 5595 | 3.7238 | 0 | 3.7238
| 5596 | 5.9112 | 0 | 5.9112
| 5597 | 6.2247 | 0 | 6.2247
| 5598 | 1004.8876 | 332.3253 | 672.5623
| 5599 | 618.0049 | 247.3446 | 370.6603
| 5600 | 95.7833 | 1670.2316 | -1574.4484
| 5601 | 0.13888 | 2555.0631 | -2554.9242
| 5602 | 0 | 3192.719 | -3192.719
| 5603 | 0 | 4681.9504 | -4681.9504
| 5604 | 0 | 6293.1011 | -6293.1011
| 5605 | 0 | 6614.231 | -6614.231
| 5606 | 0 | 6899.7436 | -6899.7436
| 5607 | 0 | 6675.603 | -6675.603
| 5608 | 0 | 6236.7176 | -6236.7176
| 5609 | 0 | 5822.2787 | -5822.2787
| 5610 | 0 | 3445.2544 | -3445.2544
| 5611 | 0 | 2200.644 | -2200.644
| 5612 | 0 | 1095.9809 | -1095.9809
| 5613 | 0 | 474.5358 | -474.5358
| 5614 | 0 | 65.328 | -65.328
| 5615 | 0 | 25.9251 | -25.9251
| 5616 | 0.13627 | 2.0844 | -1.9482
| 5617 | 6.9734 | 0 | 6.9734
| 5618 | 20.0966 | 0 | 20.0966
| 5619 | 38.6255 | 0 | 38.6255
| 5620 | 62.7866 | 0 | 62.7866
| 5621 | 110.0054 | 0 | 110.0054
| 5622 | 3404.0357 | 147.989 | 3256.0467
| 5623 | 1842.1369 | 89.3002 | 1752.8367
| 5624 | 697.9031 | 813.2884 | -115.3853
| 5625 | 5.9411 | 1957.9994 | -1952.0583
| 5626 | 0.022232 | 3197.7223 | -3197.7001
| 5627 | 0 | 5238.6168 | -5238.6168
| 5628 | 0 | 6198.9346 | -6198.9346
| 5629 | 0 | 7088.2693 | -7088.2693
| 5630 | 0 | 7797.384 | -7797.384
| 5631 | 0 | 8067.251 | -8067.251
| 5632 | 0 | 7527.0693 | -7527.0693
| 5633 | 0 | 6621.8178 | -6621.8178
| 5634 | 0 | 4078.7479 | -4078.7479
| 5635 | 0 | 2392.8213 | -2392.8213
| 5636 | 0 | 644.9124 | -644.9124
| 5637 | 0 | 377.0997 | -377.0997
| 5638 | 2.3308 | 1.5351 | 0.79572
| 5639 | 13.6196 | 0 | 13.6196
| 5640 | 29.3716 | 0 | 29.3716
| 5641 | 45.4138 | 0 | 45.4138
| 5642 | 66.3318 | 0 | 66.3318
| 5643 | 93.1912 | 0 | 93.1912
| 5644 | 116.668 | 0 | 116.668
| 5645 | 164.0572 | 0 | 164.0572
| 5646 | 3504.8118 | 64.2617 | 3440.5501
| 5647 | 2034.7219 | 1.5561 | 2033.1657
| 5648 | 1033.7144 | 70.8499 | 962.8645
| 5649 | 80.0763 | 134.274 | -54.1978
| 5650 | 1.1179 | 323.2737 | -322.1558
| 5651 | 0 | 639.5029 | -639.5029
| 5652 | 0 | 1484.7807 | -1484.7807
| 5653 | 0 | 2545.9844 | -2545.9844
| 5654 | 0 | 2870.3166 | -2870.3166
| 5655 | 0 | 3159.0414 | -3159.0414
| 5656 | 0 | 3345.681 | -3345.681
| 5657 | 0 | 2392.0955 | -2392.0955
| 5658 | 0 | 501.1962 | -501.1962
| 5659 | 0 | 22.8027 | -22.8027
| 5660 | 0 | 3.7454 | -3.7454
| 5661 | 0 | 12.7261 | -12.7261
| 5662 | 0 | 21.7227 | -21.7227
| 5663 | 0 | 11.683 | -11.683
| 5664 | 0 | 0.49135 | -0.49135
| 5665 | 0 | 0 | 0
| 5666 | 3.9303 | 0 | 3.9303
| 5667 | 6.5884 | 0 | 6.5884
| 5668 | 8.0259 | 0 | 8.0259
| 5669 | 7.7442 | 0 | 7.7442
| 5670 | 10.9921 | 0 | 10.9921
| 5671 | 14.6065 | 0 | 14.6065
| 5672 | 1425.385 | 0 | 1425.385
| 5673 | 814.8872 | 0 | 814.8872
| 5674 | 330.1649 | 0 | 330.1649
| 5675 | 39.5939 | 0 | 39.5939
| 5676 | 0 | 0 | 0
| 5677 | 0 | 0 | 0
| 5678 | 0 | 0 | 0
| 5679 | 0 | 122.7328 | -122.7328
| 5680 | 0 | 1001.3126 | -1001.3126
| 5681 | 0 | 234.2973 | -234.2973
| 5682 | 0 | 143.8576 | -143.8576
| 5683 | 0 | 98.6048 | -98.6048
| 5684 | 0 | 71.7812 | -71.7812
| 5685 | 0 | 59.5235 | -59.5235
| 5686 | 0 | 21.4603 | -21.4603
| 5687 | 0 | 1.2229 | -1.2229
| 5688 | 0 | 0 | 0
| 5689 | 0 | 0 | 0
| 5690 | 0.37072 | 0 | 0.37072
| 5691 | 1.5011 | 0 | 1.5011
| 5692 | 2.0864 | 0 | 2.0864
| 5693 | 1.6828 | 0 | 1.6828
| 5694 | 740.4839 | 387.2192 | 353.2648
| 5695 | 336.618 | 173.1443 | 163.4736
| 5696 | 0.40787 | 1674.7045 | -1674.2967
| 5697 | 0 | 2771.6159 | -2771.6159
| 5698 | 0 | 3559.0946 | -3559.0946
| 5699 | 0 | 4837.7119 | -4837.7119
| 5700 | 0 | 7023.1881 | -7023.1881
| 5701 | 0 | 8525.8503 | -8525.8503
| 5702 | 0 | 10228.5506 | -10228.5506
| 5703 | 0 | 11801.9348 | -11801.9348
| 5704 | 0 | 12573.2503 | -12573.2503
| 5705 | 0 | 12433.9474 | -12433.9474
| 5706 | 0 | 8497.3114 | -8497.3114
| 5707 | 0 | 6887.5327 | -6887.5327
| 5708 | 0 | 4817.0901 | -4817.0901
| 5709 | 0 | 2125.6042 | -2125.6042
| 5710 | 0 | 465.3966 | -465.3966
| 5711 | 0 | 683.3288 | -683.3288
| 5712 | 0 | 810.6786 | -810.6786
| 5713 | 0 | 722.7389 | -722.7389
| 5714 | 0 | 722.1609 | -722.1609
| 5715 | 0 | 588.2966 | -588.2966
| 5716 | 0 | 581.865 | -581.865
| 5717 | 0 | 493.6567 | -493.6567
| 5718 | 8.3327 | 1575.6829 | -1567.3503
| 5719 | 0 | 2471.2878 | -2471.2878
| 5720 | 0 | 5335.4888 | -5335.4888
| 5721 | 0 | 6816.8603 | -6816.8603
| 5722 | 0 | 8062.2742 | -8062.2742
| 5723 | 0 | 9111.0132 | -9111.0132
| 5724 | 0 | 9400.3292 | -9400.3292
| 5725 | 0 | 9654.3963 | -9654.3963
| 5726 | 0 | 10057.3958 | -10057.3958
| 5727 | 0 | 10401.0655 | -10401.0655
| 5728 | 0 | 10388.9404 | -10388.9404
| 5729 | 0 | 9562.2941 | -9562.2941
| 5730 | 0 | 5887.1786 | -5887.1786
| 5731 | 0 | 4763.5348 | -4763.5348
| 5732 | 0 | 3559.3979 | -3559.3979
| 5733 | 0 | 1747.5035 | -1747.5035
| 5734 | 0 | 427.1844 | -427.1844
| 5735 | 0 | 214.2895 | -214.2895
| 5736 | 0 | 116.2453 | -116.2453
| 5737 | 0.12074 | 21.8009 | -21.6801
| 5738 | 4.7676 | 0 | 4.7676
| 5739 | 6.239 | 0 | 6.239
| 5740 | 2.4212 | 0 | 2.4212
| 5741 | 0.29058 | 0 | 0.29058
| 5742 | 784.2022 | 502.9464 | 281.2557
| 5743 | 303.3599 | 579.3761 | -276.0162
| 5744 | 0 | 3517.5169 | -3517.5169
| 5745 | 0 | 4566.1533 | -4566.1533
| 5746 | 0 | 6067.1774 | -6067.1774
| 5747 | 0 | 7414.102 | -7414.102
| 5748 | 0 | 7807.0522 | -7807.0522
| 5749 | 0 | 8943.9885 | -8943.9885
| 5750 | 0 | 9978.6953 | -9978.6953
| 5751 | 0 | 10428.4365 | -10428.4365
| 5752 | 0 | 9960.0031 | -9960.0031
| 5753 | 0 | 9250.5718 | -9250.5718
| 5754 | 0 | 5585.7362 | -5585.7362
| 5755 | 0 | 4202.2765 | -4202.2765
| 5756 | 0 | 2994.1265 | -2994.1265
| 5757 | 0 | 1240.9257 | -1240.9257
| 5758 | 0 | 259.125 | -259.125
| 5759 | 0 | 84.1808 | -84.1808
| 5760 | 0 | 50.4803 | -50.4803
| 5761 | 0 | 23.7165 | -23.7165
| 5762 | 0.17082 | 0.039411 | 0.13141
| 5763 | 2.6984 | 0 | 2.6984
| 5764 | 4.407 | 0 | 4.407
| 5765 | 9.707 | 0 | 9.707
| 5766 | 1349.7759 | 318.3193 | 1031.4567
| 5767 | 965.9113 | 259.6408 | 706.2705
| 5768 | 398.8944 | 1123.0731 | -724.1787
| 5769 | 3.3519 | 1832.8705 | -1829.5186
| 5770 | 0.47979 | 2500.7732 | -2500.2934
| 5771 | 0 | 2630.5932 | -2630.5932
| 5772 | 0 | 3120.1053 | -3120.1053
| 5773 | 0 | 3845.4389 | -3845.4389
| 5774 | 0 | 4460.87 | -4460.87
| 5775 | 0 | 4432.7931 | -4432.7931
| 5776 | 0 | 3936.5214 | -3936.5214
| 5777 | 0 | 2997.7398 | -2997.7398
| 5778 | 0 | 1186.1386 | -1186.1386
| 5779 | 0 | 495.6702 | -495.6702
| 5780 | 0 | 366.1109 | -366.1109
| 5781 | 0 | 307.1761 | -307.1761
| 5782 | 0.50191 | 0 | 0.50191
| 5783 | 5.3267 | 0 | 5.3267
| 5784 | 11.6663 | 0 | 11.6663
| 5785 | 16.0075 | 0 | 16.0075
| 5786 | 25.7546 | 0 | 25.7546
| 5787 | 33.5457 | 0 | 33.5457
| 5788 | 41.2107 | 0 | 41.2107
| 5789 | 46.5138 | 0 | 46.5138
| 5790 | 1829.9014 | 148.4793 | 1681.4222
| 5791 | 1371.0408 | 32.8837 | 1338.1571
| 5792 | 687.0604 | 712.5474 | -25.487
| 5793 | 20.0493 | 1107.34 | -1087.2907
| 5794 | 4.0923 | 2500.2416 | -2496.1494
| 5795 | 0 | 3266.4904 | -3266.4904
| 5796 | 0 | 4357.0138 | -4357.0138
| 5797 | 0 | 5039.8627 | -5039.8627
| 5798 | 0 | 5621.3363 | -5621.3363
| 5799 | 0 | 5572.5279 | -5572.5279
| 5800 | 0 | 4894.0438 | -4894.0438
| 5801 | 0 | 2655.3451 | -2655.3451
| 5802 | 0 | 409.3551 | -409.3551
| 5803 | 1.5516 | 353.6665 | -352.1148
| 5804 | 5.6631 | 230.4402 | -224.7771
| 5805 | 8.1328 | 190.8915 | -182.7587
| 5806 | 12.6116 | 0 | 12.6116
| 5807 | 22.5844 | 0 | 22.5844
| 5808 | 38.2205 | 0 | 38.2205
| 5809 | 49.9133 | 0 | 49.9133
| 5810 | 63.1084 | 0 | 63.1084
| 5811 | 82.6111 | 0 | 82.6111
| 5812 | 97.322 | 0 | 97.322
| 5813 | 110.5965 | 0 | 110.5965
| 5814 | 2594.6963 | 108.6033 | 2486.093
| 5815 | 1864.9332 | 0 | 1864.9332
| 5816 | 1490.5881 | 17.814 | 1472.774
| 5817 | 777.726 | 46.7932 | 730.9328
| 5818 | 173.3616 | 104.9275 | 68.4341
| 5819 | 51.9969 | 160.9406 | -108.9438
| 5820 | 32.2876 | 199.6139 | -167.3263
| 5821 | 27.5501 | 233.0633 | -205.5131
| 5822 | 29.9765 | 142.1944 | -112.2179
| 5823 | 31.6012 | 140.1039 | -108.5027
| 5824 | 21.4269 | 134.2416 | -112.8148
| 5825 | 13.7282 | 81.9846 | -68.2564
| 5826 | 14.837 | 0 | 14.837
| 5827 | 72.2525 | 0 | 72.2525
| 5828 | 272.8468 | 0 | 272.8468
| 5829 | 727.0869 | 0 | 727.0869
| 5830 | 86.1759 | 0 | 86.1759
| 5831 | 117.4983 | 0 | 117.4983
| 5832 | 153.7609 | 0 | 153.7609
| 5833 | 190.2507 | 0 | 190.2507
| 5834 | 225.1553 | 0 | 225.1553
| 5835 | 256.1161 | 0 | 256.1161
| 5836 | 283.5925 | 0 | 283.5925
| 5837 | 310.1439 | 0 | 310.1439
| 5838 | 318.7203 | 0 | 318.7203
| 5839 | 229.6894 | 0 | 229.6894
| 5840 | 2485.5569 | 0 | 2485.5569
| 5841 | 927.2418 | 0 | 927.2418
| 5842 | 33.5659 | 0 | 33.5659
| 5843 | 0 | 0.21004 | -0.21004
| 5844 | 0 | 825.5511 | -825.5511
| 5845 | 0 | 2240.6553 | -2240.6553
| 5846 | 0 | 3159.5946 | -3159.5946
| 5847 | 0 | 3663.6571 | -3663.6571
| 5848 | 0 | 3843.2698 | -3843.2698
| 5849 | 0 | 3483.846 | -3483.846
| 5850 | 0 | 2545.6202 | -2545.6202
| 5851 | 0 | 726.4237 | -726.4237
| 5852 | 0 | 564.4714 | -564.4714
| 5853 | 0 | 511.8142 | -511.8142
| 5854 | 0 | 408.5143 | -408.5143
| 5855 | 0 | 94.3843 | -94.3843
| 5856 | 0 | 46.4326 | -46.4326
| 5857 | 0 | 24.6256 | -24.6256
| 5858 | 0 | 11.3775 | -11.3775
| 5859 | 0 | 2.5569 | -2.5569
| 5860 | 0 | 0 | 0
| 5861 | 0 | 0 | 0
| 5862 | 487.7828 | 526.2817 | -38.4989
| 5863 | 46.3603 | 635.5677 | -589.2074
| 5864 | 0 | 2160.7979 | -2160.7979
| 5865 | 0 | 3785.4938 | -3785.4938
| 5866 | 0 | 7179.9918 | -7179.9918
| 5867 | 0 | 9903.3305 | -9903.3305
| 5868 | 0 | 11316.6646 | -11316.6646
| 5869 | 0 | 12689.4147 | -12689.4147
| 5870 | 0 | 14003.8478 | -14003.8478
| 5871 | 0 | 13920.5598 | -13920.5598
| 5872 | 0 | 13002.653 | -13002.653
| 5873 | 0 | 11789.5236 | -11789.5236
| 5874 | 0 | 7955.179 | -7955.179
| 5875 | 0 | 6139.1722 | -6139.1722
| 5876 | 0 | 4045.5414 | -4045.5414
| 5877 | 0 | 1847.4529 | -1847.4529
| 5878 | 0 | 551.8596 | -551.8596
| 5879 | 0 | 395.326 | -395.326
| 5880 | 0 | 260.4976 | -260.4976
| 5881 | 0 | 142.7368 | -142.7368
| 5882 | 0 | 43.6835 | -43.6835
| 5883 | 0 | 5.6617 | -5.6617
| 5884 | 4.6169 | 0 | 4.6169
| 5885 | 11.4351 | 0 | 11.4351
| 5886 | 1339.067 | 188.3438 | 1150.7232
| 5887 | 1051.2799 | 73.5627 | 977.7172
| 5888 | 697.4408 | 634.5656 | 62.8751
| 5889 | 35.8965 | 1199.397 | -1163.5005
| 5890 | 1.2614 | 1916.9743 | -1915.7129
| 5891 | 0.058509 | 2650.5688 | -2650.5103
| 5892 | 0 | 3866.2534 | -3866.2534
| 5893 | 0 | 5118.06 | -5118.06
| 5894 | 0 | 6428.253 | -6428.253
| 5895 | 0 | 6851.4163 | -6851.4163
| 5896 | 0 | 6763.8813 | -6763.8813
| 5897 | 0 | 6128.9801 | -6128.9801
| 5898 | 0 | 3490.6608 | -3490.6608
| 5899 | 0 | 1316.5632 | -1316.5632
| 5900 | 0 | 436.8821 | -436.8821
| 5901 | 3.0155 | 306.8525 | -303.837
| 5902 | 8.8648 | 0 | 8.8648
| 5903 | 19.4778 | 0 | 19.4778
| 5904 | 33.3217 | 0 | 33.3217
| 5905 | 52.0998 | 0 | 52.0998
| 5906 | 86.7994 | 0 | 86.7994
| 5907 | 121.671 | 0 | 121.671
| 5908 | 159.8104 | 0 | 159.8104
| 5909 | 199.7712 | 0 | 199.7712
| 5910 | 4020.79 | 84.5398 | 3936.2502
| 5911 | 2556.2865 | 4.0321 | 2552.2544
| 5912 | 1578.5089 | 356.5214 | 1221.9875
| 5913 | 199.895 | 1044.3749 | -844.4799
| 5914 | 1.713 | 2656.0881 | -2654.3752
| 5915 | 0 | 4514.6185 | -4514.6185
| 5916 | 0 | 5480.7661 | -5480.7661
| 5917 | 0 | 6447.0174 | -6447.0174
| 5918 | 0 | 7249.2956 | -7249.2956
| 5919 | 0 | 7365.9827 | -7365.9827
| 5920 | 0 | 7169.0983 | -7169.0983
| 5921 | 0 | 6629.9237 | -6629.9237
| 5922 | 0 | 3838.1116 | -3838.1116
| 5923 | 0 | 2378.5429 | -2378.5429
| 5924 | 0 | 1096.124 | -1096.124
| 5925 | 0 | 443.6128 | -443.6128
| 5926 | 0 | 28.5959 | -28.5959
| 5927 | 0 | 12.5694 | -12.5694
| 5928 | 0 | 0.49713 | -0.49713
| 5929 | 0.584 | 0 | 0.584
| 5930 | 2.6455 | 0 | 2.6455
| 5931 | 5.2569 | 0 | 5.2569
| 5932 | 8.5529 | 0 | 8.5529
| 5933 | 12.1612 | 0 | 12.1612
| 5934 | 1147.3596 | 207.8781 | 939.4815
| 5935 | 699.9698 | 201.1527 | 498.8171
| 5936 | 167.1299 | 1374.9768 | -1207.8469
| 5937 | 3.5735 | 2173.444 | -2169.8704
| 5938 | 0.50324 | 2607.3225 | -2606.8193
| 5939 | 0 | 3681.1636 | -3681.1636
| 5940 | 0 | 4846.9238 | -4846.9238
| 5941 | 0 | 5516.1456 | -5516.1456
| 5942 | 0 | 6458.4586 | -6458.4586
| 5943 | 0 | 7332.4071 | -7332.4071
| 5944 | 0 | 7885.1283 | -7885.1283
| 5945 | 0 | 7676.769 | -7676.769
| 5946 | 0 | 4812.712 | -4812.712
| 5947 | 0 | 3869.2387 | -3869.2387
| 5948 | 0 | 3059.9423 | -3059.9423
| 5949 | 0 | 1590.1849 | -1590.1849
| 5950 | 0 | 248.4177 | -248.4177
| 5951 | 0 | 107.377 | -107.377
| 5952 | 0 | 26.1152 | -26.1152
| 5953 | 0 | 2.2719 | -2.2719
| 5954 | 0.42276 | 0 | 0.42276
| 5955 | 2.3668 | 0 | 2.3668
| 5956 | 2.1583 | 0 | 2.1583
| 5957 | 0.38924 | 0 | 0.38924
| 5958 | 751.6946 | 514.302 | 237.3926
| 5959 | 304.3989 | 493.347 | -188.9481
| 5960 | 0 | 3182.8125 | -3182.8125
| 5961 | 0 | 4703.0477 | -4703.0477
| 5962 | 0 | 6738.5243 | -6738.5243
| 5963 | 0 | 9183.3056 | -9183.3056
| 5964 | 0 | 10797.4025 | -10797.4025
| 5965 | 0 | 12127.3633 | -12127.3633
| 5966 | 0 | 12555.0097 | -12555.0097
| 5967 | 0 | 13044.9885 | -13044.9885
| 5968 | 0 | 12628.8828 | -12628.8828
| 5969 | 0 | 11345.664 | -11345.664
| 5970 | 0 | 6925.7211 | -6925.7211
| 5971 | 0 | 5617.6835 | -5617.6835
| 5972 | 0 | 4191.1445 | -4191.1445
| 5973 | 0 | 2140.6005 | -2140.6005
| 5974 | 0 | 644.1325 | -644.1325
| 5975 | 0 | 723.0787 | -723.0787
| 5976 | 0 | 585.7362 | -585.7362
| 5977 | 0 | 525.5203 | -525.5203
| 5978 | 0 | 282.4643 | -282.4643
| 5979 | 0 | 427.3206 | -427.3206
| 5980 | 0 | 501.6169 | -501.6169
| 5981 | 0 | 340.395 | -340.395
| 5982 | 13.0899 | 1431.0249 | -1417.935
| 5983 | 0 | 1054.4264 | -1054.4264
| 5984 | 0 | 1482.1798 | -1482.1798
| 5985 | 0 | 1919.479 | -1919.479
| 5986 | 0 | 2504.1105 | -2504.1105
| 5987 | 0 | 3468.3971 | -3468.3971
| 5988 | 0 | 4212.3907 | -4212.3907
| 5989 | 0 | 5132.2985 | -5132.2985
| 5990 | 0 | 5293.8233 | -5293.8233
| 5991 | 0 | 5348.9755 | -5348.9755
| 5992 | 0 | 5876.1296 | -5876.1296
| 5993 | 0 | 6082.61 | -6082.61
| 5994 | 0 | 1702.3928 | -1702.3928
| 5995 | 0 | 283.462 | -283.462
| 5996 | 0 | 138.639 | -138.639
| 5997 | 42.7088 | 50.8041 | -8.0953
| 5998 | 1.5613 | 2.2307 | -0.66939
| 5999 | 9.3999 | 0 | 9.3999
| 6000 | 18.1439 | 0 | 18.1439
| 6001 | 30.9814 | 0 | 30.9814
| 6002 | 48.0814 | 0 | 48.0814
| 6003 | 89.1218 | 0 | 89.1218
| 6004 | 132.4451 | 0 | 132.4451
| 6005 | 182.4196 | 0 | 182.4196
| 6006 | 212.8986 | 0 | 212.8986
| 6007 | 186.5224 | 0 | 186.5224
| 6008 | 3656.4597 | 0 | 3656.4597
| 6009 | 2113.1161 | 0 | 2113.1161
| 6010 | 1263.7858 | 0 | 1263.7858
| 6011 | 647.7117 | 0 | 647.7117
| 6012 | 42.1383 | 0 | 42.1383
| 6013 | 8.2557 | 0 | 8.2557
| 6014 | 1.1733 | 3.5113 | -2.3379
| 6015 | 0 | 18.757 | -18.757
| 6016 | 0 | 113.4783 | -113.4783
| 6017 | 0 | 97.5198 | -97.5198
| 6018 | 0 | 75.0519 | -75.0519
| 6019 | 6.7734 | 5.8803 | 0.89312
| 6020 | 23.2661 | 0 | 23.2661
| 6021 | 52.6269 | 0 | 52.6269
| 6022 | 100.7948 | 0 | 100.7948
| 6023 | 159.0225 | 0 | 159.0225
| 6024 | 251.5173 | 0 | 251.5173
| 6025 | 310.8832 | 0 | 310.8832
| 6026 | 362.548 | 0 | 362.548
| 6027 | 427.4781 | 0 | 427.4781
| 6028 | 484.6347 | 0 | 484.6347
| 6029 | 542.1278 | 0 | 542.1278
| 6030 | 6109.1826 | 0 | 6109.1826
| 6031 | 3776.7948 | 0 | 3776.7948
| 6032 | 2291.9286 | 24.0423 | 2267.8863
| 6033 | 687.1634 | 145.8297 | 541.3337
| 6034 | 57.8968 | 431.6561 | -373.7593
| 6035 | 11.4728 | 928.65 | -917.1772
| 6036 | 1.4925 | 1606.7235 | -1605.231
| 6037 | 0 | 2552.3481 | -2552.3481
| 6038 | 1.8978 | 2305.1038 | -2303.206
| 6039 | 14.4863 | 1190.5522 | -1176.0659
| 6040 | 38.2038 | 565.8568 | -527.653
| 6041 | 68.8028 | 361.573 | -292.7702
| 6042 | 72.2907 | 188.0639 | -115.7733
| 6043 | 136.6917 | 163.3314 | -26.6397
| 6044 | 202.8182 | 96.3186 | 106.4996
| 6045 | 82.8829 | 84.129 | -1.2462
| 6046 | 98.2836 | 0 | 98.2836
| 6047 | 129.0287 | 0 | 129.0287
| 6048 | 175.1818 | 0 | 175.1818
| 6049 | 191.2152 | 0 | 191.2152
| 6050 | 199.3025 | 0 | 199.3025
| 6051 | 197.7594 | 0 | 197.7594
| 6052 | 193.1198 | 0 | 193.1198
| 6053 | 188.3675 | 0 | 188.3675
| 6054 | 2677.7316 | 83.0277 | 2594.7039
| 6055 | 1775.8438 | 0.76996 | 1775.0738
| 6056 | 1019.3046 | 208.6226 | 810.682
| 6057 | 131.959 | 473.9655 | -342.0065
| 6058 | 38.959 | 1016.1685 | -977.2096
| 6059 | 8.6307 | 1650.6192 | -1641.9885
| 6060 | 0.49421 | 2965.9788 | -2965.4845
| 6061 | 0 | 5250.9282 | -5250.9282
| 6062 | 0 | 6835.0458 | -6835.0458
| 6063 | 0 | 7355.975 | -7355.975
| 6064 | 0 | 7532.882 | -7532.882
| 6065 | 0 | 7358.0164 | -7358.0164
| 6066 | 0 | 4359.5101 | -4359.5101
| 6067 | 0 | 2351.5111 | -2351.5111
| 6068 | 0 | 803.9574 | -803.9574
| 6069 | 0 | 355.3719 | -355.3719
| 6070 | 0 | 0 | 0
| 6071 | 1.5628 | 0 | 1.5628
| 6072 | 7.5595 | 0 | 7.5595
| 6073 | 12.5933 | 0 | 12.5933
| 6074 | 13.1106 | 0 | 13.1106
| 6075 | 10.8888 | 0 | 10.8888
| 6076 | 12.5545 | 0 | 12.5545
| 6077 | 19.255 | 0 | 19.255
| 6078 | 1280.2875 | 286.8911 | 993.3963
| 6079 | 751.6699 | 174.3947 | 577.2752
| 6080 | 38.9524 | 2540.0318 | -2501.0794
| 6081 | 0 | 4424.7503 | -4424.7503
| 6082 | 0 | 6886.6931 | -6886.6931
| 6083 | 0 | 9038.5818 | -9038.5818
| 6084 | 0 | 10233.839 | -10233.839
| 6085 | 0 | 11433.5111 | -11433.5111
| 6086 | 0 | 11776.1257 | -11776.1257
| 6087 | 0 | 10794.9148 | -10794.9148
| 6088 | 0 | 10078.4024 | -10078.4024
| 6089 | 0 | 9490.4424 | -9490.4424
| 6090 | 0 | 5576.6872 | -5576.6872
| 6091 | 0 | 3873.5401 | -3873.5401
| 6092 | 0 | 1771.7807 | -1771.7807
| 6093 | 0 | 623.9695 | -623.9695
| 6094 | 0 | 80.0066 | -80.0066
| 6095 | 0 | 20.0371 | -20.0371
| 6096 | 0.51276 | 1.5546 | -1.0419
| 6097 | 6.9196 | 0 | 6.9196
| 6098 | 17.5476 | 0 | 17.5476
| 6099 | 27.7622 | 0 | 27.7622
| 6100 | 36.9381 | 0 | 36.9381
| 6101 | 38.0066 | 0 | 38.0066
| 6102 | 1784.1285 | 177.4706 | 1606.6579
| 6103 | 1206.0664 | 100.9899 | 1105.0765
| 6104 | 449.715 | 1021.4937 | -571.7787
| 6105 | 2.4162 | 2519.6912 | -2517.275
| 6106 | 0 | 4783.1411 | -4783.1411
| 6107 | 0 | 7634.5368 | -7634.5368
| 6108 | 0 | 9795.2888 | -9795.2888
| 6109 | 0 | 11651.8755 | -11651.8755
| 6110 | 0 | 12503.3171 | -12503.3171
| 6111 | 0 | 13010.5167 | -13010.5167
| 6112 | 0 | 12078.4671 | -12078.4671
| 6113 | 0 | 10919.3229 | -10919.3229
| 6114 | 0 | 6911.8092 | -6911.8092
| 6115 | 0 | 5472.4384 | -5472.4384
| 6116 | 0 | 3880.248 | -3880.248
| 6117 | 0 | 1786.397 | -1786.397
| 6118 | 0 | 342.3238 | -342.3238
| 6119 | 0 | 166.385 | -166.385
| 6120 | 0 | 41.2648 | -41.2648
| 6121 | 0 | 4.5461 | -4.5461
| 6122 | 4.3508 | 0 | 4.3508
| 6123 | 11.8679 | 0 | 11.8679
| 6124 | 20.6893 | 0 | 20.6893
| 6125 | 22.3116 | 0 | 22.3116
| 6126 | 1529.2332 | 329.1438 | 1200.0895
| 6127 | 1040.715 | 293.0056 | 747.7094
| 6128 | 128.7583 | 2517.9498 | -2389.1915
| 6129 | 0 | 4595.2795 | -4595.2795
| 6130 | 0 | 6945.8614 | -6945.8614
| 6131 | 0 | 8826.7417 | -8826.7417
| 6132 | 0 | 10510.086 | -10510.086
| 6133 | 0 | 12156.0916 | -12156.0916
| 6134 | 0 | 12920.0245 | -12920.0245
| 6135 | 0 | 13173.511 | -13173.511
| 6136 | 0 | 12711.6997 | -12711.6997
| 6137 | 0 | 11734.3355 | -11734.3355
| 6138 | 0 | 7193.6948 | -7193.6948
| 6139 | 0 | 5218.9402 | -5218.9402
| 6140 | 0 | 3187.8403 | -3187.8403
| 6141 | 0 | 1405.2075 | -1405.2075
| 6142 | 0 | 312.5538 | -312.5538
| 6143 | 0 | 269.4114 | -269.4114
| 6144 | 0 | 217.1442 | -217.1442
| 6145 | 0 | 113.1199 | -113.1199
| 6146 | 0 | 48.4553 | -48.4553
| 6147 | 0 | 19.3724 | -19.3724
| 6148 | 0 | 8.3177 | -8.3177
| 6149 | 0 | 10.2249 | -10.2249
| 6150 | 481.1041 | 494.3466 | -13.2425
| 6151 | 159.1702 | 251.5405 | -92.3703
| 6152 | 0 | 920.1092 | -920.1092
| 6153 | 0 | 1573.4346 | -1573.4346
| 6154 | 0 | 2951.3253 | -2951.3253
| 6155 | 0 | 4619.0225 | -4619.0225
| 6156 | 0 | 5469.2199 | -5469.2199
| 6157 | 0 | 6158.2979 | -6158.2979
| 6158 | 0 | 6384.6159 | -6384.6159
| 6159 | 0 | 6621.909 | -6621.909
| 6160 | 0 | 6602.5035 | -6602.5035
| 6161 | 0 | 6077.1206 | -6077.1206
| 6162 | 0 | 3426.6693 | -3426.6693
| 6163 | 0 | 2403.1098 | -2403.1098
| 6164 | 0 | 1590.1407 | -1590.1407
| 6165 | 0 | 875.7151 | -875.7151
| 6166 | 0 | 688.2416 | -688.2416
| 6167 | 0 | 537.7274 | -537.7274
| 6168 | 0 | 513.0323 | -513.0323
| 6169 | 0 | 265.6721 | -265.6721
| 6170 | 0 | 461.9643 | -461.9643
| 6171 | 0 | 373.9462 | -373.9462
| 6172 | 0 | 256.3575 | -256.3575
| 6173 | 0 | 93.0709 | -93.0709
| 6174 | 0 | 57.9704 | -57.9704
| 6175 | 0 | 38.1008 | -38.1008
| 6176 | 549.6752 | 5.5956 | 544.0796
| 6177 | 153.3653 | 15.1323 | 138.233
| 6178 | 0 | 120.037 | -120.037
| 6179 | 0 | 82.9448 | -82.9448
| 6180 | 0 | 66.0681 | -66.0681
| 6181 | 0 | 75.0743 | -75.0743
| 6182 | 0 | 61.3817 | -61.3817
| 6183 | 0 | 67.5925 | -67.5925
| 6184 | 0 | 87.6159 | -87.6159
| 6185 | 0 | 115.5897 | -115.5897
| 6186 | 46.4345 | 78.8628 | -32.4282
| 6187 | 0 | 23.7669 | -23.7669
| 6188 | 1.1295 | 5.0934 | -3.9638
| 6189 | 3.3195 | 0 | 3.3195
| 6190 | 8.8438 | 0 | 8.8438
| 6191 | 18.4186 | 0 | 18.4186
| 6192 | 31.2188 | 0 | 31.2188
| 6193 | 43.2724 | 0 | 43.2724
| 6194 | 61.3377 | 0 | 61.3377
| 6195 | 107.5658 | 0 | 107.5658
| 6196 | 192.9817 | 0 | 192.9817
| 6197 | 246.3682 | 0 | 246.3682
| 6198 | 4315.5162 | 42.4901 | 4273.0261
| 6199 | 2643.0031 | 2.7149 | 2640.2882
| 6200 | 1703.4746 | 86.3035 | 1617.1712
| 6201 | 707.2529 | 258.9627 | 448.2902
| 6202 | 214.509 | 547.614 | -333.105
| 6203 | 42.1901 | 738.9889 | -696.7988
| 6204 | 27.9502 | 927.6716 | -899.7214
| 6205 | 15.935 | 1262.159 | -1246.224
| 6206 | 13.7841 | 1228.3609 | -1214.5768
| 6207 | 10.5954 | 1300.846 | -1290.2507
| 6208 | 11.3924 | 996.7386 | -985.3463
| 6209 | 16.4186 | 586.7707 | -570.352
| 6210 | 26.7866 | 266.181 | -239.3944
| 6211 | 77.8239 | 211.9267 | -134.1028
| 6212 | 377.1328 | 105.0658 | 272.0671
| 6213 | 121.2071 | 57.3609 | 63.8462
| 6214 | 147.2953 | 0 | 147.2953
| 6215 | 187.4123 | 0 | 187.4123
| 6216 | 231.8848 | 0 | 231.8848
| 6217 | 282.7773 | 0 | 282.7773
| 6218 | 337.4411 | 0 | 337.4411
| 6219 | 425.2794 | 0 | 425.2794
| 6220 | 473.0582 | 0 | 473.0582
| 6221 | 502.9638 | 0 | 502.9638
| 6222 | 5516.1723 | 0 | 5516.1723
| 6223 | 3801.4495 | 0 | 3801.4495
| 6224 | 2714.2639 | 30.7204 | 2683.5435
| 6225 | 1527.29 | 123.1268 | 1404.1632
| 6226 | 807.1054 | 271.3349 | 535.7705
| 6227 | 424.4606 | 320.26 | 104.2006
| 6228 | 256.6832 | 377.5425 | -120.8594
| 6229 | 203.4734 | 538.8722 | -335.3988
| 6230 | 173.991 | 729.4515 | -555.4605
| 6231 | 162.675 | 643.4155 | -480.7405
| 6232 | 158.4722 | 469.6097 | -311.1375
| 6233 | 163.6782 | 357.0765 | -193.3983
| 6234 | 300.6769 | 152.3976 | 148.2793
| 6235 | 811.3558 | 86.8665 | 724.4893
| 6236 | 1279.1586 | 20.3081 | 1258.8505
| 6237 | 347.5271 | 2.5821 | 344.945
| 6238 | 437.2266 | 0 | 437.2266
| 6239 | 496.3622 | 0 | 496.3622
| 6240 | 556.4579 | 0 | 556.4579
| 6241 | 614.1085 | 0 | 614.1085
| 6242 | 648.0322 | 0 | 648.0322
| 6243 | 684.6157 | 0 | 684.6157
| 6244 | 723.7444 | 0 | 723.7444
| 6245 | 766.2068 | 0 | 766.2068
| 6246 | 7428.9658 | 0 | 7428.9658
| 6247 | 5028.1387 | 0 | 5028.1387
| 6248 | 3352.6206 | 8.6164 | 3344.0042
| 6249 | 1881.688 | 47.58 | 1834.108
| 6250 | 1113.4394 | 140.6316 | 972.8078
| 6251 | 498.7231 | 292.3475 | 206.3756
| 6252 | 221.1167 | 441.0557 | -219.939
| 6253 | 143.5775 | 633.4323 | -489.8549
| 6254 | 94.3952 | 858.2303 | -763.8351
| 6255 | 71.1947 | 863.9289 | -792.7342
| 6256 | 53.3281 | 778.7627 | -725.4347
| 6257 | 40.8796 | 641.1303 | -600.2507
| 6258 | 61.2385 | 251.1929 | -189.9544
| 6259 | 172.7931 | 176.0382 | -3.2451
| 6260 | 594.5602 | 89.7604 | 504.7997
| 6261 | 254.7212 | 44.3069 | 210.4143
| 6262 | 350.8679 | 0 | 350.8679
| 6263 | 467.763 | 0 | 467.763
| 6264 | 587.8082 | 0 | 587.8082
| 6265 | 659.1678 | 0 | 659.1678
| 6266 | 718.2381 | 0 | 718.2381
| 6267 | 788.2792 | 0 | 788.2792
| 6268 | 801.4624 | 0 | 801.4624
| 6269 | 791.9879 | 0 | 791.9879
| 6270 | 7402.2432 | 0 | 7402.2432
| 6271 | 5052.857 | 0 | 5052.857
| 6272 | 3542.7009 | 0 | 3542.7009
| 6273 | 2076.5238 | 1.8946 | 2074.6292
| 6274 | 1107.1328 | 41.1783 | 1065.9544
| 6275 | 302.4141 | 207.2383 | 95.1758
| 6276 | 175.314 | 301.5931 | -126.2791
| 6277 | 179.1476 | 386.1127 | -206.9651
| 6278 | 183.5908 | 473.618 | -290.0272
| 6279 | 174.3229 | 362.7665 | -188.4436
| 6280 | 164.8331 | 247.6286 | -82.7955
| 6281 | 214.3634 | 148.2982 | 66.0652
| 6282 | 433.0144 | 59.2375 | 373.7769
| 6283 | 766.7871 | 40.2851 | 726.502
| 6284 | 897.1302 | 6.66 | 890.4702
| 6285 | 244.9527 | 2.2589 | 242.6938
| 6286 | 272.3394 | 0 | 272.3394
| 6287 | 288.4065 | 0 | 288.4065
| 6288 | 303.9213 | 0 | 303.9213
| 6289 | 315.618 | 0 | 315.618
| 6290 | 325.1448 | 0 | 325.1448
| 6291 | 333.5284 | 0 | 333.5284
| 6292 | 337.0251 | 0 | 337.0251
| 6293 | 342.5715 | 0 | 342.5715
| 6294 | 3732.181 | 50.7474 | 3681.4336
| 6295 | 2432.2546 | 0 | 2432.2546
| 6296 | 1414.5198 | 36.0647 | 1378.4551
| 6297 | 457.3365 | 144.5647 | 312.7718
| 6298 | 123.6711 | 401.1087 | -277.4376
| 6299 | 72.002 | 583.7346 | -511.7326
| 6300 | 61.5382 | 750.6102 | -689.072
| 6301 | 31.2703 | 1244.9724 | -1213.7021
| 6302 | 12.662 | 1753.9715 | -1741.3096
| 6303 | 11.3408 | 1711.0659 | -1699.7252
| 6304 | 5.3743 | 1641.9591 | -1636.5848
| 6305 | 3.5718 | 1088.6235 | -1085.0516
| 6306 | 11.1787 | 305.5177 | -294.3389
| 6307 | 40.2515 | 238.1702 | -197.9187
| 6308 | 76.7993 | 144.0067 | -67.2074
| 6309 | 102.7437 | 88.3154 | 14.4283
| 6310 | 183.5291 | 0 | 183.5291
| 6311 | 268.6245 | 0 | 268.6245
| 6312 | 354.3693 | 0 | 354.3693
| 6313 | 430.0956 | 0 | 430.0956
| 6314 | 502.4726 | 0 | 502.4726
| 6315 | 562.9178 | 0 | 562.9178
| 6316 | 578.3735 | 0 | 578.3735
| 6317 | 603.0082 | 0 | 603.0082
| 6318 | 6137.5903 | 0 | 6137.5903
| 6319 | 4276.8248 | 0 | 4276.8248
| 6320 | 3041.1363 | 10.1582 | 3030.9781
| 6321 | 1592.5717 | 36.8883 | 1555.6834
| 6322 | 460.8349 | 77.0525 | 383.7823
| 6323 | 88.1628 | 129.8507 | -41.6879
| 6324 | 28.9481 | 183.7441 | -154.796
| 6325 | 10.0998 | 683.4291 | -673.3293
| 6326 | 5.3831 | 968.4859 | -963.1028
| 6327 | 3.9764 | 1090.2484 | -1086.272
| 6328 | 1.2784 | 1262.4107 | -1261.1323
| 6329 | 1.6227 | 787.7791 | -786.1565
| 6330 | 10.6369 | 0 | 10.6369
| 6331 | 71.0075 | 0 | 71.0075
| 6332 | 500.2419 | 0 | 500.2419
| 6333 | 1207.3563 | 0 | 1207.3563
| 6334 | 164.454 | 0 | 164.454
| 6335 | 163.5683 | 0 | 163.5683
| 6336 | 167.3795 | 0 | 167.3795
| 6337 | 186.2138 | 0 | 186.2138
| 6338 | 214.6788 | 0 | 214.6788
| 6339 | 215.5983 | 0 | 215.5983
| 6340 | 195.3992 | 0 | 195.3992
| 6341 | 207.8867 | 0 | 207.8867
| 6342 | 193.7163 | 0 | 193.7163
| 6343 | 174.9602 | 0 | 174.9602
| 6344 | 2714.1699 | 0 | 2714.1699
| 6345 | 1799.7614 | 0 | 1799.7614
| 6346 | 1145.3706 | 0 | 1145.3706
| 6347 | 763.7924 | 0 | 763.7924
| 6348 | 398.3499 | 0 | 398.3499
| 6349 | 339.9431 | 0 | 339.9431
| 6350 | 257.6972 | 0 | 257.6972
| 6351 | 130.6119 | 0 | 130.6119
| 6352 | 72.1542 | 0 | 72.1542
| 6353 | 502.7172 | 0 | 502.7172
| 6354 | 780.2206 | 0 | 780.2206
| 6355 | 38.4682 | 0 | 38.4682
| 6356 | 41.4165 | 0 | 41.4165
| 6357 | 53.7075 | 0 | 53.7075
| 6358 | 69.0787 | 0 | 69.0787
| 6359 | 152.5143 | 0 | 152.5143
| 6360 | 270.2567 | 0 | 270.2567
| 6361 | 348.6131 | 0 | 348.6131
| 6362 | 429.6487 | 0 | 429.6487
| 6363 | 507.0813 | 0 | 507.0813
| 6364 | 521.9022 | 0 | 521.9022
| 6365 | 514.6693 | 0 | 514.6693
| 6366 | 5751.002 | 20.6965 | 5730.3055
| 6367 | 3962.0998 | 0 | 3962.0998
| 6368 | 2394.8143 | 1.0688 | 2393.7455
| 6369 | 817.272 | 31.3411 | 785.9309
| 6370 | 152.3836 | 87.0279 | 65.3557
| 6371 | 85.7868 | 147.5332 | -61.7464
| 6372 | 105.0991 | 186.5044 | -81.4053
| 6373 | 142.7965 | 288.1883 | -145.3918
| 6374 | 109.0771 | 474.1112 | -365.0342
| 6375 | 98.7741 | 357.1572 | -258.3831
| 6376 | 92.9102 | 318.1735 | -225.2633
| 6377 | 63.8516 | 251.4661 | -187.6145
| 6378 | 76.795 | 121.0265 | -44.2315
| 6379 | 285.2868 | 69.0627 | 216.2241
| 6380 | 874.9267 | 5.0377 | 869.889
| 6381 | 263.2483 | 0 | 263.2483
| 6382 | 292.6942 | 0 | 292.6942
| 6383 | 365.4361 | 0 | 365.4361
| 6384 | 424.0997 | 0 | 424.0997
| 6385 | 434.3451 | 0 | 434.3451
| 6386 | 428.9395 | 0 | 428.9395
| 6387 | 430.2166 | 0 | 430.2166
| 6388 | 448.6464 | 0 | 448.6464
| 6389 | 441.4639 | 0 | 441.4639
| 6390 | 4716.1386 | 46.4427 | 4669.696
| 6391 | 3301.9613 | 0 | 3301.9613
| 6392 | 2502.3195 | 0 | 2502.3195
| 6393 | 1588.7718 | 2.8694 | 1585.9024
| 6394 | 1195.4358 | 7.2128 | 1188.223
| 6395 | 803.5649 | 31.1205 | 772.4444
| 6396 | 529.3372 | 54.959 | 474.3781
| 6397 | 252.6841 | 294.1734 | -41.4893
| 6398 | 184.0616 | 528.4623 | -344.4007
| 6399 | 135.714 | 474.8889 | -339.1748
| 6400 | 61.3394 | 488.989 | -427.6496
| 6401 | 22.2622 | 456.687 | -434.4248
| 6402 | 90.3634 | 198.7221 | -108.3587
| 6403 | 757.1865 | 106.9564 | 650.2301
| 6404 | 1436.1507 | 21.6259 | 1414.5248
| 6405 | 322.4646 | 6.0558 | 316.4088
| 6406 | 358.3598 | 0 | 358.3598
| 6407 | 465.7742 | 0 | 465.7742
| 6408 | 502.5168 | 0 | 502.5168
| 6409 | 487.715 | 0 | 487.715
| 6410 | 508.3308 | 0 | 508.3308
| 6411 | 542.6933 | 0 | 542.6933
| 6412 | 574.1289 | 0 | 574.1289
| 6413 | 586.0411 | 0 | 586.0411
| 6414 | 5786.5569 | 15.4881 | 5771.0688
| 6415 | 3871.7684 | 0 | 3871.7684
| 6416 | 2734.1525 | 0 | 2734.1525
| 6417 | 1468.5847 | 16.3254 | 1452.2593
| 6418 | 529.6529 | 130.2921 | 399.3608
| 6419 | 139.3305 | 405.7387 | -266.4082
| 6420 | 47.7635 | 830.5436 | -782.7801
| 6421 | 12.2059 | 1709.4895 | -1697.2837
| 6422 | 5.8105 | 2258.9629 | -2253.1525
| 6423 | 1.1371 | 2827.5203 | -2826.3833
| 6424 | 0 | 2640.8026 | -2640.8026
| 6425 | 0.089966 | 1806.2207 | -1806.1307
| 6426 | 0.82484 | 391.5813 | -390.7565
| 6427 | 4.4778 | 285.4466 | -280.9688
| 6428 | 10.3253 | 175.1193 | -164.7941
| 6429 | 18.5609 | 134.0667 | -115.5058
| 6430 | 46.7664 | 0 | 46.7664
| 6431 | 94.3319 | 0 | 94.3319
| 6432 | 117.5836 | 0 | 117.5836
| 6433 | 132.1597 | 0 | 132.1597
| 6434 | 167.0378 | 0 | 167.0378
| 6435 | 191.5964 | 0 | 191.5964
| 6436 | 203.2912 | 0 | 203.2912
| 6437 | 215.5641 | 0 | 215.5641
| 6438 | 2943.4211 | 81.1224 | 2862.2988
| 6439 | 2022.6358 | 0 | 2022.6358
| 6440 | 1229.3555 | 79.6538 | 1149.7017
| 6441 | 172.4469 | 325.4963 | -153.0494
| 6442 | 74.9332 | 507.7751 | -432.8419
| 6443 | 85.8054 | 644.4638 | -558.6584
| 6444 | 54.2786 | 944.3878 | -890.1092
| 6445 | 13.2162 | 1724.5142 | -1711.298
| 6446 | 1.5537 | 2908.1041 | -2906.5504
| 6447 | 2.8841 | 2184.9167 | -2182.0326
| 6448 | 3.2763 | 1753.5429 | -1750.2666
| 6449 | 1.8006 | 1217.7802 | -1215.9796
| 6450 | 1.884 | 321.3785 | -319.4944
| 6451 | 5.4682 | 283.0216 | -277.5534
| 6452 | 14.2452 | 167.6338 | -153.3886
| 6453 | 47.7205 | 122.7931 | -75.0726
| 6454 | 92.5096 | 0 | 92.5096
| 6455 | 157.2916 | 0 | 157.2916
| 6456 | 218.0181 | 0 | 218.0181
| 6457 | 270.6024 | 0 | 270.6024
| 6458 | 368.0407 | 0 | 368.0407
| 6459 | 407.852 | 0 | 407.852
| 6460 | 409.1872 | 0 | 409.1872
| 6461 | 425.1926 | 0 | 425.1926
| 6462 | 4583.686 | 51.9418 | 4531.7442
| 6463 | 3175.0209 | 0 | 3175.0209
| 6464 | 2182.8296 | 28.5631 | 2154.2665
| 6465 | 873.8935 | 294.617 | 579.2764
| 6466 | 97.6358 | 856.0796 | -758.4438
| 6467 | 13.172 | 1652.7474 | -1639.5754
| 6468 | 1.1119 | 3941.2486 | -3940.1367
| 6469 | 0 | 5708.6526 | -5708.6526
| 6470 | 0 | 6795.0903 | -6795.0903
| 6471 | 0 | 6989.3731 | -6989.3731
| 6472 | 0 | 6376.5423 | -6376.5423
| 6473 | 0 | 5624.6602 | -5624.6602
| 6474 | 0 | 2298.0556 | -2298.0556
| 6475 | 0.82867 | 507.3571 | -506.5284
| 6476 | 7.1736 | 321.0597 | -313.8861
| 6477 | 20.4739 | 240.5505 | -220.0767
| 6478 | 39.8155 | 0 | 39.8155
| 6479 | 80.664 | 0 | 80.664
| 6480 | 129.3721 | 0 | 129.3721
| 6481 | 184.8354 | 0 | 184.8354
| 6482 | 231.1024 | 0 | 231.1024
| 6483 | 278.4785 | 0 | 278.4785
| 6484 | 317.2035 | 0 | 317.2035
| 6485 | 356.0864 | 0 | 356.0864
| 6486 | 4248.0477 | 31.4636 | 4216.5841
| 6487 | 2711.0286 | 0 | 2711.0286
| 6488 | 2162.6257 | 3.1645 | 2159.4612
| 6489 | 1311.8776 | 8.4535 | 1303.4241
| 6490 | 542.8441 | 27.1054 | 515.7387
| 6491 | 76.9566 | 127.5697 | -50.613
| 6492 | 5.1388 | 748.2988 | -743.16
| 6493 | 0 | 2715.8323 | -2715.8323
| 6494 | 0 | 3353.6351 | -3353.6351
| 6495 | 0 | 3754.4249 | -3754.4249
| 6496 | 0 | 3870.1526 | -3870.1526
| 6497 | 0 | 3544.0338 | -3544.0338
| 6498 | 0 | 977.8193 | -977.8193
| 6499 | 0 | 19.1764 | -19.1764
| 6500 | 1.7939 | 0.4847 | 1.3092
| 6501 | 191.1493 | 0 | 191.1493
| 6502 | 21.0911 | 0 | 21.0911
| 6503 | 47.697 | 0 | 47.697
| 6504 | 86.1495 | 0 | 86.1495
| 6505 | 126.0995 | 0 | 126.0995
| 6506 | 151.7778 | 0 | 151.7778
| 6507 | 130.0508 | 0 | 130.0508
| 6508 | 135.2439 | 0 | 135.2439
| 6509 | 139.8801 | 0 | 139.8801
| 6510 | 130.1218 | 0 | 130.1218
| 6511 | 130.2951 | 0 | 130.2951
| 6512 | 2531.103 | 0 | 2531.103
| 6513 | 1584.3164 | 0 | 1584.3164
| 6514 | 843.6304 | 0 | 843.6304
| 6515 | 128.7607 | 0 | 128.7607
| 6516 | 0.074425 | 0 | 0.074425
| 6517 | 0 | 320.4925 | -320.4925
| 6518 | 0 | 1417.0956 | -1417.0956
| 6519 | 0 | 1392.9238 | -1392.9238
| 6520 | 0 | 1336.7519 | -1336.7519
| 6521 | 0 | 502.9262 | -502.9262
| 6522 | 0 | 159.4029 | -159.4029
| 6523 | 0 | 25.1248 | -25.1248
| 6524 | 0 | 11.5069 | -11.5069
| 6525 | 0.9141 | 0.88188 | 0.032213
| 6526 | 7.0397 | 0 | 7.0397
| 6527 | 16.8218 | 0 | 16.8218
| 6528 | 27.1079 | 0 | 27.1079
| 6529 | 37.9843 | 0 | 37.9843
| 6530 | 49.65 | 0 | 49.65
| 6531 | 58.9381 | 0 | 58.9381
| 6532 | 66.9584 | 0 | 66.9584
| 6533 | 62.2439 | 0 | 62.2439
| 6534 | 1743.5412 | 88.3994 | 1655.1418
| 6535 | 1126.4116 | 16.0425 | 1110.369
| 6536 | 339.5704 | 472.1773 | -132.6069
| 6537 | 7.0159 | 978.0828 | -971.067
| 6538 | 0.16603 | 1716.048 | -1715.8819
| 6539 | 0 | 4142.0979 | -4142.0979
| 6540 | 0 | 5640.319 | -5640.319
| 6541 | 0 | 6498.1532 | -6498.1532
| 6542 | 0 | 6404.5567 | -6404.5567
| 6543 | 0 | 5853.3854 | -5853.3854
| 6544 | 0 | 4615.8115 | -4615.8115
| 6545 | 0.86193 | 1547.3173 | -1546.4554
| 6546 | 6.0725 | 320.5762 | -314.5037
| 6547 | 11.9561 | 267.5343 | -255.5782
| 6548 | 25.0391 | 160.1147 | -135.0756
| 6549 | 36.4663 | 111.5883 | -75.122
| 6550 | 54.3417 | 0 | 54.3417
| 6551 | 50.0727 | 0 | 50.0727
| 6552 | 41.7264 | 0 | 41.7264
| 6553 | 26.4253 | 0 | 26.4253
| 6554 | 12.4973 | 0 | 12.4973
| 6555 | 3.3041 | 0 | 3.3041
| 6556 | 0 | 138.8102 | -138.8102
| 6557 | 0 | 88.9855 | -88.9855
| 6558 | 515.4188 | 380.8602 | 134.5586
| 6559 | 302.6191 | 116.6298 | 185.9893
| 6560 | 13.501 | 1397.4703 | -1383.9692
| 6561 | 0.92987 | 2164.6724 | -2163.7425
| 6562 | 0.13162 | 2498.8477 | -2498.7161
| 6563 | 0 | 3233.5937 | -3233.5937
| 6564 | 0 | 3877.1947 | -3877.1947
| 6565 | 0 | 4380.1358 | -4380.1358
| 6566 | 0 | 4621.1925 | -4621.1925
| 6567 | 0 | 4721.6738 | -4721.6738
| 6568 | 0 | 3982.8471 | -3982.8471
| 6569 | 0 | 2785.3744 | -2785.3744
| 6570 | 0 | 780.7326 | -780.7326
| 6571 | 0 | 418.5733 | -418.5733
| 6572 | 1.3547 | 293.2044 | -291.8497
| 6573 | 3.8828 | 249.2334 | -245.3506
| 6574 | 8.8644 | 0 | 8.8644
| 6575 | 14.3696 | 0 | 14.3696
| 6576 | 22.5223 | 0 | 22.5223
| 6577 | 30.5155 | 0 | 30.5155
| 6578 | 35.6231 | 0 | 35.6231
| 6579 | 41.4249 | 0 | 41.4249
| 6580 | 47.3664 | 0 | 47.3664
| 6581 | 48.9183 | 0 | 48.9183
| 6582 | 1625.9579 | 152.5863 | 1473.3716
| 6583 | 1240.4092 | 34.3016 | 1206.1076
| 6584 | 811.03 | 466.2177 | 344.8123
| 6585 | 186.4756 | 798.3525 | -611.8769
| 6586 | 75.0103 | 1011.7515 | -936.7412
| 6587 | 58.2662 | 1065.9154 | -1007.6492
| 6588 | 39.3752 | 1177.4287 | -1138.0535
| 6589 | 32.2517 | 1271.1356 | -1238.8839
| 6590 | 30.6455 | 1290.6233 | -1259.9778
| 6591 | 22.4753 | 1150.8956 | -1128.4203
| 6592 | 10.1315 | 1220.1026 | -1209.9711
| 6593 | 4.1571 | 968.2207 | -964.0636
| 6594 | 3.6416 | 326.8217 | -323.1801
| 6595 | 7.6057 | 282.9197 | -275.314
| 6596 | 11.1418 | 176.3736 | -165.2317
| 6597 | 16.7438 | 134.9251 | -118.1813
| 6598 | 57.01 | 0 | 57.01
| 6599 | 104.109 | 0 | 104.109
| 6600 | 162.1743 | 0 | 162.1743
| 6601 | 250.6731 | 0 | 250.6731
| 6602 | 307.0317 | 0 | 307.0317
| 6603 | 360.5818 | 0 | 360.5818
| 6604 | 418.0292 | 0 | 418.0292
| 6605 | 386.1311 | 0 | 386.1311
| 6606 | 4161.2541 | 78.8288 | 4082.4253
| 6607 | 2822.8197 | 0 | 2822.8197
| 6608 | 2070.2192 | 17.0867 | 2053.1324
| 6609 | 1136.6038 | 97.2335 | 1039.3703
| 6610 | 718.8703 | 323.9193 | 394.9509
| 6611 | 312.6718 | 511.9977 | -199.3259
| 6612 | 158.4788 | 711.7069 | -553.228
| 6613 | 121.561 | 835.9986 | -714.4376
| 6614 | 126.9298 | 870.7233 | -743.7935
| 6615 | 170.2413 | 507.8523 | -337.611
| 6616 | 181.6573 | 282.0698 | -100.4125
| 6617 | 171.2441 | 209.2203 | -37.9762
| 6618 | 131.7014 | 108.6075 | 23.0939
| 6619 | 183.4863 | 91.5561 | 91.9302
| 6620 | 286.2547 | 18.3679 | 267.8868
| 6621 | 93.2242 | 20.7581 | 72.4661
| 6622 | 93.081 | 0 | 93.081
| 6623 | 93.9366 | 0 | 93.9366
| 6624 | 92.0978 | 0 | 92.0978
| 6625 | 89.3023 | 0 | 89.3023
| 6626 | 92.9497 | 0 | 92.9497
| 6627 | 95.3352 | 0 | 95.3352
| 6628 | 106.955 | 0 | 106.955
| 6629 | 131.3607 | 0 | 131.3607
| 6630 | 1747.5849 | 86.7298 | 1660.8551
| 6631 | 1383.6733 | 0.18521 | 1383.4881
| 6632 | 541.603 | 582.6238 | -41.0207
| 6633 | 19.3139 | 1710.5246 | -1691.2107
| 6634 | 2.9964 | 2429.679 | -2426.6826
| 6635 | 0.070519 | 3197.8117 | -3197.7412
| 6636 | 0 | 4300.3767 | -4300.3767
| 6637 | 0 | 4546.9594 | -4546.9594
| 6638 | 0 | 4273.8726 | -4273.8726
| 6639 | 0 | 3151.0974 | -3151.0974
| 6640 | 1.9639 | 2290.3828 | -2288.4189
| 6641 | 6.5638 | 941.0403 | -934.4765
| 6642 | 13.0644 | 310.9955 | -297.9311
| 6643 | 27.9462 | 247.8416 | -219.8954
| 6644 | 87.3643 | 124.5288 | -37.1645
| 6645 | 78.5451 | 77.7202 | 0.82494
| 6646 | 118.8728 | 0 | 118.8728
| 6647 | 153.3956 | 0 | 153.3956
| 6648 | 197.5654 | 0 | 197.5654
| 6649 | 229.0193 | 0 | 229.0193
| 6650 | 274.8485 | 0 | 274.8485
| 6651 | 326.1467 | 0 | 326.1467
| 6652 | 337.1714 | 0 | 337.1714
| 6653 | 329.6804 | 0 | 329.6804
| 6654 | 3881.9198 | 59.3226 | 3822.5973
| 6655 | 2912.833 | 0 | 2912.833
| 6656 | 2420.7718 | 0 | 2420.7718
| 6657 | 1497.9457 | 0 | 1497.9457
| 6658 | 827.0618 | 6.0154 | 821.0464
| 6659 | 295.8138 | 24.3187 | 271.495
| 6660 | 191.0328 | 30.2112 | 160.8217
| 6661 | 200.9365 | 33.9199 | 167.0166
| 6662 | 197.9385 | 13.5632 | 184.3753
| 6663 | 188.0595 | 17.1341 | 170.9253
| 6664 | 182.7273 | 7.7712 | 174.9561
| 6665 | 177.3603 | 0 | 177.3603
| 6666 | 625.3425 | 0 | 625.3425
| 6667 | 1188.1906 | 0 | 1188.1906
| 6668 | 1777.0361 | 0 | 1777.0361
| 6669 | 2549.6984 | 0 | 2549.6984
| 6670 | 502.5858 | 0 | 502.5858
| 6671 | 553.2972 | 0 | 553.2972
| 6672 | 596.3186 | 0 | 596.3186
| 6673 | 595.1149 | 0 | 595.1149
| 6674 | 577.3181 | 0 | 577.3181
| 6675 | 562.0823 | 0 | 562.0823
| 6676 | 517.742 | 0 | 517.742
| 6677 | 495.7021 | 0 | 495.7021
| 6678 | 502.2546 | 0 | 502.2546
| 6679 | 493.0638 | 0 | 493.0638
| 6680 | 4971.3852 | 0 | 4971.3852
| 6681 | 3501.657 | 0 | 3501.657
| 6682 | 2937.8187 | 0 | 2937.8187
| 6683 | 2422.7287 | 0 | 2422.7287
| 6684 | 1828.7433 | 0 | 1828.7433
| 6685 | 1763.9057 | 0 | 1763.9057
| 6686 | 1698.1648 | 0 | 1698.1648
| 6687 | 1802.4728 | 0 | 1802.4728
| 6688 | 1952.7183 | 0 | 1952.7183
| 6689 | 3210.0244 | 0 | 3210.0244
| 6690 | 3661.49 | 0 | 3661.49
| 6691 | 600.9418 | 0 | 600.9418
| 6692 | 645.0029 | 0 | 645.0029
| 6693 | 702.0164 | 0 | 702.0164
| 6694 | 767.3124 | 0 | 767.3124
| 6695 | 857.6235 | 0 | 857.6235
| 6696 | 997.3917 | 0 | 997.3917
| 6697 | 1166.0205 | 0 | 1166.0205
| 6698 | 1262.4944 | 0 | 1262.4944
| 6699 | 1308.5299 | 0 | 1308.5299
| 6700 | 1426.6871 | 0 | 1426.6871
| 6701 | 1532.0789 | 0 | 1532.0789
| 6702 | 10250.1297 | 0 | 10250.1297
| 6703 | 7601.7665 | 0 | 7601.7665
| 6704 | 5693.8635 | 0 | 5693.8635
| 6705 | 3705.5905 | 0 | 3705.5905
| 6706 | 2445.6653 | 0 | 2445.6653
| 6707 | 1587.9058 | 0 | 1587.9058
| 6708 | 1022.2513 | 3.6075 | 1018.6438
| 6709 | 641.2486 | 49.5307 | 591.7179
| 6710 | 345.7762 | 125.235 | 220.5411
| 6711 | 233.9212 | 154.8159 | 79.1053
| 6712 | 187.744 | 160.5892 | 27.1547
| 6713 | 216.4822 | 115.5818 | 100.9004
| 6714 | 749.8871 | 47.8616 | 702.0255
| 6715 | 1667.8041 | 17.1471 | 1650.657
| 6716 | 2438.3991 | 0 | 2438.3991
| 6717 | 602.8612 | 0 | 602.8612
| 6718 | 626.3946 | 0 | 626.3946
| 6719 | 683.1019 | 0 | 683.1019
| 6720 | 696.033 | 0 | 696.033
| 6721 | 727.3095 | 0 | 727.3095
| 6722 | 736.3703 | 0 | 736.3703
| 6723 | 749.7648 | 0 | 749.7648
| 6724 | 775.5721 | 0 | 775.5721
| 6725 | 766.3436 | 0 | 766.3436
| 6726 | 7265.6588 | 0 | 7265.6588
| 6727 | 5243.1886 | 0 | 5243.1886
| 6728 | 3715.5096 | 0 | 3715.5096
| 6729 | 2132.4268 | 0 | 2132.4268
| 6730 | 1023.1971 | 28.8695 | 994.3276
| 6731 | 225.2475 | 144.7227 | 80.5249
| 6732 | 115.0686 | 383.8176 | -268.749
| 6733 | 71.0519 | 608.6778 | -537.6259
| 6734 | 24.789 | 1645.8186 | -1621.0297
| 6735 | 4.0074 | 2443.6566 | -2439.6492
| 6736 | 0.91797 | 2398.7646 | -2397.8466
| 6737 | 0.50964 | 1689.415 | -1688.9054
| 6738 | 0.55794 | 342.4087 | -341.8508
| 6739 | 3.8241 | 236.4756 | -232.6515
| 6740 | 7.5905 | 150.4991 | -142.9085
| 6741 | 11.1517 | 120.6842 | -109.5325
| 6742 | 27.3722 | 0 | 27.3722
| 6743 | 44.5686 | 0 | 44.5686
| 6744 | 65.647 | 0 | 65.647
| 6745 | 79.1758 | 0 | 79.1758
| 6746 | 99.6104 | 0 | 99.6104
| 6747 | 129.1197 | 0 | 129.1197
| 6748 | 155.5818 | 0 | 155.5818
| 6749 | 187.7838 | 0 | 187.7838
| 6750 | 2786.9855 | 81.1224 | 2705.8632
| 6751 | 1925.5642 | 0 | 1925.5642
| 6752 | 1161.7387 | 100.0015 | 1061.7373
| 6753 | 147.3048 | 364.8575 | -217.5528
| 6754 | 38.4652 | 668.2223 | -629.7571
| 6755 | 19.9752 | 1042.3483 | -1022.3731
| 6756 | 62.7315 | 706.8567 | -644.1252
| 6757 | 109.4348 | 750.6176 | -641.1828
| 6758 | 192.2212 | 621.6373 | -429.4161
| 6759 | 360.0785 | 252.2182 | 107.8603
| 6760 | 619.6142 | 160.7631 | 458.8511
| 6761 | 999.0874 | 66.2719 | 932.8156
| 6762 | 1343.9291 | 9.1977 | 1334.7314
| 6763 | 1584.1941 | 2.9253 | 1581.2687
| 6764 | 1872.1185 | 0 | 1872.1185
| 6765 | 483.4319 | 0 | 483.4319
| 6766 | 538.1503 | 0 | 538.1503
| 6767 | 581.8801 | 0 | 581.8801
| 6768 | 627.7485 | 0 | 627.7485
| 6769 | 665.4901 | 0 | 665.4901
| 6770 | 709.5187 | 0 | 709.5187
| 6771 | 755.1311 | 0 | 755.1311
| 6772 | 843.1058 | 0 | 843.1058
| 6773 | 924.9176 | 0 | 924.9176
| 6774 | 8335.2651 | 0 | 8335.2651
| 6775 | 6408.0103 | 0 | 6408.0103
| 6776 | 4904.2572 | 0 | 4904.2572
| 6777 | 3354.1373 | 0 | 3354.1373
| 6778 | 2603.0309 | 2.6751 | 2600.3558
| 6779 | 1981.8464 | 29.5986 | 1952.2478
| 6780 | 1509.2204 | 134.1828 | 1375.0376
| 6781 | 1092.5808 | 283.8118 | 808.7689
| 6782 | 851.2998 | 381.4576 | 469.8422
| 6783 | 718.0727 | 349.4953 | 368.5774
| 6784 | 867.5231 | 288.8483 | 578.6749
| 6785 | 1252.0495 | 185.6152 | 1066.4343
| 6786 | 1953.3662 | 61.9272 | 1891.439
| 6787 | 2817.0601 | 22.4957 | 2794.5644
| 6788 | 3407.9584 | 0 | 3407.9584
| 6789 | 875.8852 | 0 | 875.8852
| 6790 | 900.9779 | 0 | 900.9779
| 6791 | 991.4672 | 0 | 991.4672
| 6792 | 1111.5039 | 0 | 1111.5039
| 6793 | 1209.7317 | 0 | 1209.7317
| 6794 | 1352.6503 | 0 | 1352.6503
| 6795 | 1441.9513 | 0 | 1441.9513
| 6796 | 1527.3843 | 0 | 1527.3843
| 6797 | 1605.0509 | 0 | 1605.0509
| 6798 | 11462.047 | 0 | 11462.047
| 6799 | 8677.0938 | 0 | 8677.0938
| 6800 | 6683.2129 | 0 | 6683.2129
| 6801 | 4460.1516 | 0 | 4460.1516
| 6802 | 2717.9051 | 1.8974 | 2716.0077
| 6803 | 1451.5989 | 37.3512 | 1414.2477
| 6804 | 733.1319 | 167.2062 | 565.9256
| 6805 | 395.4311 | 327.6778 | 67.7534
| 6806 | 269.1658 | 420.6956 | -151.5298
| 6807 | 206.3328 | 419.6042 | -213.2714
| 6808 | 166.1644 | 391.4625 | -225.2982
| 6809 | 175.9513 | 272.4538 | -96.5025
| 6810 | 525.1575 | 113.8199 | 411.3376
| 6811 | 1605.3613 | 66.9801 | 1538.3812
| 6812 | 2275.7666 | 17.2514 | 2258.5152
| 6813 | 599.8214 | 1.257 | 598.5645
| 6814 | 690.139 | 0 | 690.139
| 6815 | 768.494 | 0 | 768.494
| 6816 | 841.2305 | 0 | 841.2305
| 6817 | 903.7818 | 0 | 903.7818
| 6818 | 963.3505 | 0 | 963.3505
| 6819 | 1013.7873 | 0 | 1013.7873
| 6820 | 1035.1161 | 0 | 1035.1161
| 6821 | 1029.9242 | 0 | 1029.9242
| 6822 | 8361.0796 | 0 | 8361.0796
| 6823 | 6281.0638 | 0 | 6281.0638
| 6824 | 5025.8576 | 0 | 5025.8576
| 6825 | 3322.253 | 0 | 3322.253
| 6826 | 1762.3942 | 0 | 1762.3942
| 6827 | 774.4719 | 8.4733 | 765.9987
| 6828 | 304.1361 | 43.7204 | 260.4157
| 6829 | 199.0183 | 94.5406 | 104.4777
| 6830 | 143.22 | 90.2804 | 52.9396
| 6831 | 104.8503 | 81.4532 | 23.3971
| 6832 | 92.7228 | 66.4123 | 26.3106
| 6833 | 94.4733 | 40.8812 | 53.5921
| 6834 | 121.0378 | 0 | 121.0378
| 6835 | 387.9399 | 0 | 387.9399
| 6836 | 701.4391 | 0 | 701.4391
| 6837 | 1148.0007 | 0 | 1148.0007
| 6838 | 210.8034 | 0 | 210.8034
| 6839 | 254.5457 | 0 | 254.5457
| 6840 | 303.175 | 0 | 303.175
| 6841 | 328.4356 | 0 | 328.4356
| 6842 | 329.7938 | 0 | 329.7938
| 6843 | 330.4839 | 0 | 330.4839
| 6844 | 344.6614 | 0 | 344.6614
| 6845 | 321.9633 | 0 | 321.9633
| 6846 | 292.5723 | 0 | 292.5723
| 6847 | 287.2659 | 0 | 287.2659
| 6848 | 3179.6105 | 0 | 3179.6105
| 6849 | 1989.8116 | 0 | 1989.8116
| 6850 | 1245.4924 | 0 | 1245.4924
| 6851 | 996.1095 | 0 | 996.1095
| 6852 | 602.8827 | 0 | 602.8827
| 6853 | 442.4903 | 0 | 442.4903
| 6854 | 275.285 | 0 | 275.285
| 6855 | 131.7714 | 0 | 131.7714
| 6856 | 93.8476 | 0 | 93.8476
| 6857 | 450.8841 | 0 | 450.8841
| 6858 | 717.0656 | 0 | 717.0656
| 6859 | 46.7948 | 0 | 46.7948
| 6860 | 48.4608 | 0 | 48.4608
| 6861 | 49.7452 | 0 | 49.7452
| 6862 | 64.8238 | 0 | 64.8238
| 6863 | 84.018 | 0 | 84.018
| 6864 | 103.7622 | 0 | 103.7622
| 6865 | 112.6843 | 0 | 112.6843
| 6866 | 118.484 | 0 | 118.484
| 6867 | 123.0119 | 0 | 123.0119
| 6868 | 123.3982 | 0 | 123.3982
| 6869 | 115.3443 | 0 | 115.3443
| 6870 | 1810.0701 | 88.2426 | 1721.8275
| 6871 | 1345.2195 | 0 | 1345.2195
| 6872 | 803.1581 | 0 | 803.1581
| 6873 | 153.9359 | 17.0273 | 136.9086
| 6874 | 105.8577 | 74.2888 | 31.5689
| 6875 | 69.7409 | 196.0912 | -126.3503
| 6876 | 38.9118 | 223.4936 | -184.5818
| 6877 | 19.7167 | 415.8299 | -396.1132
| 6878 | 4.2327 | 1771.7593 | -1767.5267
| 6879 | 5.3579 | 1773.4218 | -1768.0639
| 6880 | 6.1564 | 1433.2489 | -1427.0925
| 6881 | 2.2657 | 1045.7504 | -1043.4846
| 6882 | 2.9466 | 182.8747 | -179.928
| 6883 | 19.5767 | 118.1649 | -98.5882
| 6884 | 67.6426 | 15.4852 | 52.1574
| 6885 | 88.0236 | 1.9829 | 86.0408
| 6886 | 148.5434 | 0 | 148.5434
| 6887 | 226.483 | 0 | 226.483
| 6888 | 307.4104 | 0 | 307.4104
| 6889 | 366.9929 | 0 | 366.9929
| 6890 | 425.9403 | 0 | 425.9403
| 6891 | 515.7743 | 0 | 515.7743
| 6892 | 597.9663 | 0 | 597.9663
| 6893 | 635.0044 | 0 | 635.0044
| 6894 | 6244.8968 | 0 | 6244.8968
| 6895 | 4251.64 | 0 | 4251.64
| 6896 | 2981.1981 | 0 | 2981.1981
| 6897 | 1809.4272 | 1.8379 | 1807.5893
| 6898 | 1200.5705 | 25.8025 | 1174.768
| 6899 | 744.3166 | 82.0987 | 662.2179
| 6900 | 434.768 | 164.8439 | 269.9241
| 6901 | 317.9212 | 264.9058 | 53.0154
| 6902 | 363.4932 | 253.4892 | 110.004
| 6903 | 321.8382 | 216.3756 | 105.4626
| 6904 | 303.4012 | 177.3928 | 126.0084
| 6905 | 380.5921 | 112.7169 | 267.8752
| 6906 | 811.5658 | 34.2377 | 777.3281
| 6907 | 1345.4636 | 19.6899 | 1325.7737
| 6908 | 2113.4618 | 0.022598 | 2113.4392
| 6909 | 565.31 | 0 | 565.31
| 6910 | 634.2989 | 0 | 634.2989
| 6911 | 737.8329 | 0 | 737.8329
| 6912 | 824.6215 | 0 | 824.6215
| 6913 | 862.9948 | 0 | 862.9948
| 6914 | 895.1233 | 0 | 895.1233
| 6915 | 914.7754 | 0 | 914.7754
| 6916 | 876.1792 | 0 | 876.1792
| 6917 | 836.6672 | 0 | 836.6672
| 6918 | 7572.5214 | 0 | 7572.5214
| 6919 | 5450.1219 | 0 | 5450.1219
| 6920 | 4223.0019 | 0 | 4223.0019
| 6921 | 3004.9648 | 0 | 3004.9648
| 6922 | 2184.3662 | 0 | 2184.3662
| 6923 | 1531.9217 | 0.87933 | 1531.0423
| 6924 | 1284.4636 | 1.7059 | 1282.7578
| 6925 | 1077.6548 | 12.3767 | 1065.2781
| 6926 | 917.5237 | 32.0958 | 885.4279
| 6927 | 779.4674 | 38.9586 | 740.5088
| 6928 | 765.4178 | 63.4352 | 701.9826
| 6929 | 865.8958 | 20.502 | 845.3939
| 6930 | 1228.4985 | 0 | 1228.4985
| 6931 | 1582.0797 | 0 | 1582.0797
| 6932 | 1863.473 | 0 | 1863.473
| 6933 | 493.8404 | 0 | 493.8404
| 6934 | 590.3081 | 0 | 590.3081
| 6935 | 703.0044 | 0 | 703.0044
| 6936 | 775.6257 | 0 | 775.6257
| 6937 | 765.7676 | 0 | 765.7676
| 6938 | 757.3076 | 0 | 757.3076
| 6939 | 768.8216 | 0 | 768.8216
| 6940 | 759.5785 | 0 | 759.5785
| 6941 | 747.1304 | 0 | 747.1304
| 6942 | 6976.0606 | 0 | 6976.0606
| 6943 | 4989.4597 | 0 | 4989.4597
| 6944 | 3804.5323 | 0 | 3804.5323
| 6945 | 2640.4199 | 0 | 2640.4199
| 6946 | 1907.6501 | 0 | 1907.6501
| 6947 | 1112.2193 | 1.3312 | 1110.8881
| 6948 | 686.5211 | 12.4113 | 674.1097
| 6949 | 433.0859 | 38.3288 | 394.7571
| 6950 | 329.0727 | 61.2243 | 267.8483
| 6951 | 312.2998 | 86.2584 | 226.0413
| 6952 | 345.1592 | 97.2574 | 247.9018
| 6953 | 635.3484 | 31.3487 | 603.9996
| 6954 | 1097.3996 | 0.093915 | 1097.3057
| 6955 | 1373.8567 | 0 | 1373.8567
| 6956 | 1608.3261 | 0 | 1608.3261
| 6957 | 433.7415 | 0 | 433.7415
| 6958 | 475.8101 | 0 | 475.8101
| 6959 | 521.3212 | 0 | 521.3212
| 6960 | 574.3412 | 0 | 574.3412
| 6961 | 656.9022 | 0 | 656.9022
| 6962 | 743.1838 | 0 | 743.1838
| 6963 | 818.6122 | 0 | 818.6122
| 6964 | 868.2401 | 0 | 868.2401
| 6965 | 892.1645 | 0 | 892.1645
| 6966 | 8074.3054 | 0 | 8074.3054
| 6967 | 5782.7444 | 0 | 5782.7444
| 6968 | 4161.7829 | 0 | 4161.7829
| 6969 | 2656.7854 | 0 | 2656.7854
| 6970 | 1925.5395 | 4.0724 | 1921.4671
| 6971 | 1352.8989 | 39.2133 | 1313.6856
| 6972 | 836.8509 | 189.0299 | 647.821
| 6973 | 448.2867 | 362.6261 | 85.6605
| 6974 | 283.8872 | 453.6346 | -169.7474
| 6975 | 214.8729 | 460.1582 | -245.2853
| 6976 | 235.4049 | 380.8754 | -145.4705
| 6977 | 543.8686 | 231.6088 | 312.2599
| 6978 | 1306.5354 | 95.1312 | 1211.4042
| 6979 | 2143.6706 | 52.2878 | 2091.3828
| 6980 | 2772.1454 | 6.9991 | 2765.1463
| 6981 | 681.1622 | 0 | 681.1622
| 6982 | 741.0623 | 0 | 741.0623
| 6983 | 802.7521 | 0 | 802.7521
| 6984 | 873.0839 | 0 | 873.0839
| 6985 | 950.2782 | 0 | 950.2782
| 6986 | 1048.1323 | 0 | 1048.1323
| 6987 | 1157.1877 | 0 | 1157.1877
| 6988 | 1243.1781 | 0 | 1243.1781
| 6989 | 1329.6213 | 0 | 1329.6213
| 6990 | 9892.9017 | 0 | 9892.9017
| 6991 | 7541.0555 | 0 | 7541.0555
| 6992 | 6127.7356 | 0 | 6127.7356
| 6993 | 4126.4472 | 0 | 4126.4472
| 6994 | 2410.2406 | 1.1006 | 2409.14
| 6995 | 1192.5139 | 33.1061 | 1159.4078
| 6996 | 379.8692 | 90.8953 | 288.9739
| 6997 | 184.0959 | 145.0843 | 39.0115
| 6998 | 136.7507 | 156.8745 | -20.1239
| 6999 | 101.4983 | 161.2877 | -59.7894
| 7000 | 81.4859 | 150.513 | -69.0271
| 7001 | 85.8791 | 104.8637 | -18.9846
| 7002 | 154.4104 | 0 | 154.4104
| 7003 | 746.2729 | 0 | 746.2729
| 7004 | 1185.9631 | 0 | 1185.9631
| 7005 | 1683.2404 | 0 | 1683.2404
| 7006 | 370.9219 | 0 | 370.9219
| 7007 | 473.7564 | 0 | 473.7564
| 7008 | 544.8246 | 0 | 544.8246
| 7009 | 656.7077 | 0 | 656.7077
| 7010 | 701.3934 | 0 | 701.3934
| 7011 | 832.8888 | 0 | 832.8888
| 7012 | 972.3274 | 0 | 972.3274
| 7013 | 1020.9702 | 0 | 1020.9702
| 7014 | 1093.3685 | 0 | 1093.3685
| 7015 | 1136.2948 | 0 | 1136.2948
| 7016 | 7603.9479 | 0 | 7603.9479
| 7017 | 4412.9843 | 0 | 4412.9843
| 7018 | 2645.8145 | 0 | 2645.8145
| 7019 | 1572.4176 | 0 | 1572.4176
| 7020 | 486.5674 | 0 | 486.5674
| 7021 | 110.7237 | 0 | 110.7237
| 7022 | 75.8696 | 0 | 75.8696
| 7023 | 48.6011 | 0 | 48.6011
| 7024 | 43.2239 | 0 | 43.2239
| 7025 | 587.658 | 0 | 587.658
| 7026 | 1474.4327 | 0 | 1474.4327
| 7027 | 166.4957 | 0 | 166.4957
| 7028 | 236.6622 | 0 | 236.6622
| 7029 | 299.5753 | 0 | 299.5753
| 7030 | 392.0183 | 0 | 392.0183
| 7031 | 500.9308 | 0 | 500.9308
| 7032 | 630.9573 | 0 | 630.9573
| 7033 | 678.0648 | 0 | 678.0648
| 7034 | 713.9466 | 0 | 713.9466
| 7035 | 743.636 | 0 | 743.636
| 7036 | 799.6838 | 0 | 799.6838
| 7037 | 887.5326 | 0 | 887.5326
| 7038 | 8359.7069 | 0 | 8359.7069
| 7039 | 5927.2956 | 0 | 5927.2956
| 7040 | 4205.0033 | 0 | 4205.0033
| 7041 | 2556.3688 | 0 | 2556.3688
| 7042 | 1651.6279 | 0.069464 | 1651.5585
| 7043 | 686.7543 | 13.1208 | 673.6335
| 7044 | 204.2957 | 44.4466 | 159.8491
| 7045 | 103.7752 | 105.8317 | -2.0565
| 7046 | 84.0138 | 147.7916 | -63.7778
| 7047 | 95.5345 | 153.8487 | -58.3141
| 7048 | 95.0207 | 168.1811 | -73.1604
| 7049 | 90.1144 | 112.3345 | -22.2201
| 7050 | 94.7929 | 47.1043 | 47.6886
| 7051 | 147.9308 | 36.8969 | 111.0339
| 7052 | 360.8847 | 8.8214 | 352.0633
| 7053 | 169.3602 | 1.382 | 167.9782
| 7054 | 223.9115 | 0 | 223.9115
| 7055 | 297.3108 | 0 | 297.3108
| 7056 | 372.5396 | 0 | 372.5396
| 7057 | 461.9282 | 0 | 461.9282
| 7058 | 519.8533 | 0 | 519.8533
| 7059 | 596.3689 | 0 | 596.3689
| 7060 | 653.8036 | 0 | 653.8036
| 7061 | 679.7016 | 0 | 679.7016
| 7062 | 6584.2037 | 0 | 6584.2037
| 7063 | 4436.5191 | 0 | 4436.5191
| 7064 | 2928.955 | 0 | 2928.955
| 7065 | 1579.3057 | 21.7573 | 1557.5485
| 7066 | 680.5372 | 120.7982 | 559.739
| 7067 | 151.288 | 400.4935 | -249.2055
| 7068 | 72.1971 | 635.2196 | -563.0225
| 7069 | 36.6501 | 1323.2126 | -1286.5624
| 7070 | 10.8896 | 2270.4544 | -2259.5648
| 7071 | 2.3682 | 2843.0697 | -2840.7015
| 7072 | 0.25621 | 2651.9026 | -2651.6463
| 7073 | 3.1693 | 1427.6198 | -1424.4506
| 7074 | 46.3819 | 268.8458 | -222.4639
| 7075 | 184.2742 | 186.3014 | -2.0271
| 7076 | 760.7602 | 91.4786 | 669.2816
| 7077 | 241.2713 | 51.3789 | 189.8925
| 7078 | 296.9412 | 0 | 296.9412
| 7079 | 296.7281 | 0 | 296.7281
| 7080 | 273.9043 | 0 | 273.9043
| 7081 | 265.7045 | 0 | 265.7045
| 7082 | 277.8875 | 0 | 277.8875
| 7083 | 290.2465 | 0 | 290.2465
| 7084 | 297.9329 | 0 | 297.9329
| 7085 | 307.4674 | 0 | 307.4674
| 7086 | 3582.4886 | 76.8101 | 3505.6784
| 7087 | 2391.501 | 0 | 2391.501
| 7088 | 1722.0986 | 18.5087 | 1703.5898
| 7089 | 752.4026 | 106.912 | 645.4906
| 7090 | 159.096 | 393.3452 | -234.2492
| 7091 | 37.3265 | 769.9045 | -732.578
| 7092 | 6.4746 | 1449.1495 | -1442.6749
| 7093 | 0.93034 | 2422.1469 | -2421.2165
| 7094 | 14.378 | 1703.7211 | -1689.3431
| 7095 | 78.4868 | 548.9267 | -470.44
| 7096 | 78.5878 | 487.3952 | -408.8075
| 7097 | 72.7937 | 339.3623 | -266.5686
| 7098 | 79.0486 | 156.3771 | -77.3285
| 7099 | 136.0162 | 115.8365 | 20.1797
| 7100 | 354.1094 | 37.2999 | 316.8095
| 7101 | 180.6112 | 15.7626 | 164.8486
| 7102 | 269.6192 | 0 | 269.6192
| 7103 | 351.6823 | 0 | 351.6823
| 7104 | 420.9402 | 0 | 420.9402
| 7105 | 492.6705 | 0 | 492.6705
| 7106 | 557.4797 | 0 | 557.4797
| 7107 | 597.4966 | 0 | 597.4966
| 7108 | 629.956 | 0 | 629.956
| 7109 | 686.8037 | 0 | 686.8037
| 7110 | 6991.7124 | 0 | 6991.7124
| 7111 | 5139.358 | 0 | 5139.358
| 7112 | 3629.3868 | 0 | 3629.3868
| 7113 | 2173.3335 | 22.1888 | 2151.1447
| 7114 | 1438.6333 | 106.6347 | 1331.9986
| 7115 | 908.6784 | 164.1596 | 744.5188
| 7116 | 518.5623 | 349.8725 | 168.6898
| 7117 | 255.7384 | 518.8769 | -263.1385
| 7118 | 157.5945 | 703.9693 | -546.3748
| 7119 | 122.8975 | 694.5894 | -571.6919
| 7120 | 117.5437 | 591.3933 | -473.8496
| 7121 | 188.4092 | 370.0799 | -181.6707
| 7122 | 805.3183 | 114.0922 | 691.2261
| 7123 | 1543.6167 | 62.4108 | 1481.2058
| 7124 | 2208.4242 | 8.965 | 2199.4592
| 7125 | 576.3677 | 0 | 576.3677
| 7126 | 649.3966 | 0 | 649.3966
| 7127 | 730.4442 | 0 | 730.4442
| 7128 | 826.687 | 0 | 826.687
| 7129 | 863.2846 | 0 | 863.2846
| 7130 | 924.9899 | 0 | 924.9899
| 7131 | 1032.4932 | 0 | 1032.4932
| 7132 | 1157.7847 | 0 | 1157.7847
| 7133 | 1244.2331 | 0 | 1244.2331
| 7134 | 10003.3765 | 0 | 10003.3765
| 7135 | 7813.6665 | 0 | 7813.6665
| 7136 | 6140.3049 | 0 | 6140.3049
| 7137 | 4101.3213 | 0 | 4101.3213
| 7138 | 2707.5306 | 7.7498 | 2699.7808
| 7139 | 1623.1201 | 81.251 | 1541.8691
| 7140 | 1070.3805 | 246.4427 | 823.9378
| 7141 | 619.8895 | 376.9948 | 242.8947
| 7142 | 301.0395 | 438.7251 | -137.6856
| 7143 | 268.9492 | 308.7435 | -39.7943
| 7144 | 380.2561 | 213.8733 | 166.3828
| 7145 | 707.5189 | 104.2161 | 603.3028
| 7146 | 1100.0113 | 51.7794 | 1048.2319
| 7147 | 1427.0682 | 35.8279 | 1391.2403
| 7148 | 1745.9105 | 7.1673 | 1738.7433
| 7149 | 480.943 | 0.3029 | 480.6401
| 7150 | 568.7074 | 0 | 568.7074
| 7151 | 606.9293 | 0 | 606.9293
| 7152 | 649.4709 | 0 | 649.4709
| 7153 | 683.5383 | 0 | 683.5383
| 7154 | 703.2658 | 0 | 703.2658
| 7155 | 719.5988 | 0 | 719.5988
| 7156 | 731.1084 | 0 | 731.1084
| 7157 | 717.4258 | 0 | 717.4258
| 7158 | 6496.4659 | 0 | 6496.4659
| 7159 | 4689.8292 | 0 | 4689.8292
| 7160 | 3972.6727 | 0 | 3972.6727
| 7161 | 3097.6232 | 0 | 3097.6232
| 7162 | 2430.2698 | 0 | 2430.2698
| 7163 | 1931.5144 | 0 | 1931.5144
| 7164 | 1635.3618 | 0 | 1635.3618
| 7165 | 1406.8978 | 0 | 1406.8978
| 7166 | 1302.3722 | 0 | 1302.3722
| 7167 | 1237.7484 | 0 | 1237.7484
| 7168 | 1253.894 | 0 | 1253.894
| 7169 | 1376.587 | 0 | 1376.587
| 7170 | 1812.4252 | 0 | 1812.4252
| 7171 | 2013.6029 | 0 | 2013.6029
| 7172 | 2178.4596 | 0 | 2178.4596
| 7173 | 2546.1047 | 0 | 2546.1047
| 7174 | 513.2371 | 0 | 513.2371
| 7175 | 541.4775 | 0 | 541.4775
| 7176 | 567.3702 | 0 | 567.3702
| 7177 | 581.0759 | 0 | 581.0759
| 7178 | 602.8373 | 0 | 602.8373
| 7179 | 607.9864 | 0 | 607.9864
| 7180 | 602.9011 | 0 | 602.9011
| 7181 | 606.1612 | 0 | 606.1612
| 7182 | 600.3748 | 0 | 600.3748
| 7183 | 597.8989 | 0 | 597.8989
| 7184 | 5437.5823 | 0 | 5437.5823
| 7185 | 3877.8858 | 0 | 3877.8858
| 7186 | 3049.9025 | 0 | 3049.9025
| 7187 | 2539.5644 | 0 | 2539.5644
| 7188 | 1890.8618 | 0 | 1890.8618
| 7189 | 1561.575 | 0 | 1561.575
| 7190 | 1414.8767 | 0 | 1414.8767
| 7191 | 1351.8216 | 0 | 1351.8216
| 7192 | 1304.1275 | 0 | 1304.1275
| 7193 | 2090.5263 | 0 | 2090.5263
| 7194 | 2366.5061 | 0 | 2366.5061
| 7195 | 338.3604 | 0 | 338.3604
| 7196 | 358.1824 | 0 | 358.1824
| 7197 | 372.8797 | 0 | 372.8797
| 7198 | 401.9675 | 0 | 401.9675
| 7199 | 416.9335 | 0 | 416.9335
| 7200 | 445.7937 | 0 | 445.7937
| 7201 | 469.0908 | 0 | 469.0908
| 7202 | 465.6541 | 0 | 465.6541
| 7203 | 462.5019 | 0 | 462.5019
| 7204 | 463.1469 | 0 | 463.1469
| 7205 | 454.2387 | 0 | 454.2387
| 7206 | 4872.9491 | 24.2853 | 4848.6638
| 7207 | 3695.7626 | 0 | 3695.7626
| 7208 | 2507.2538 | 0 | 2507.2538
| 7209 | 1203.0033 | 0 | 1203.0033
| 7210 | 642.3061 | 0 | 642.3061
| 7211 | 392.15 | 0 | 392.15
| 7212 | 284.217 | 0 | 284.217
| 7213 | 229.5611 | 0.76865 | 228.7924
| 7214 | 226.7745 | 6.36 | 220.4145
| 7215 | 231.719 | 22.6264 | 209.0927
| 7216 | 216.1134 | 57.6606 | 158.4528
| 7217 | 252.1957 | 11.2464 | 240.9493
| 7218 | 461.5095 | 0 | 461.5095
| 7219 | 770.4167 | 0 | 770.4167
| 7220 | 1099.2394 | 0 | 1099.2394
| 7221 | 317.6938 | 0 | 317.6938
| 7222 | 492.474 | 0 | 492.474
| 7223 | 610.1176 | 0 | 610.1176
| 7224 | 700.5533 | 0 | 700.5533
| 7225 | 758.4674 | 0 | 758.4674
| 7226 | 760.1151 | 0 | 760.1151
| 7227 | 771.9774 | 0 | 771.9774
| 7228 | 780.3071 | 0 | 780.3071
| 7229 | 766.9643 | 0 | 766.9643
| 7230 | 6916.2815 | 0 | 6916.2815
| 7231 | 5317.1409 | 0 | 5317.1409
| 7232 | 3923.9066 | 0 | 3923.9066
| 7233 | 2515.3177 | 0 | 2515.3177
| 7234 | 1575.3076 | 4.831 | 1570.4766
| 7235 | 612.5699 | 70.0869 | 542.4829
| 7236 | 196.6145 | 198.0193 | -1.4048
| 7237 | 99.3421 | 466.3534 | -367.0114
| 7238 | 41.3326 | 1318.0258 | -1276.6932
| 7239 | 12.1495 | 2039.7816 | -2027.6321
| 7240 | 4.428 | 2053.3588 | -2048.9308
| 7241 | 3.9773 | 1167.043 | -1163.0657
| 7242 | 10.0941 | 272.8512 | -262.7571
| 7243 | 35.6791 | 154.1209 | -118.4418
| 7244 | 104.9912 | 78.0989 | 26.8922
| 7245 | 92.5263 | 57.6546 | 34.8717
| 7246 | 91.9428 | 0 | 91.9428
| 7247 | 81.2114 | 0 | 81.2114
| 7248 | 93.2771 | 0 | 93.2771
| 7249 | 129.1499 | 0 | 129.1499
| 7250 | 154.4534 | 0 | 154.4534
| 7251 | 176.7848 | 0 | 176.7848
| 7252 | 207.0636 | 0 | 207.0636
| 7253 | 243.8825 | 0 | 243.8825
| 7254 | 3179.7063 | 59.4651 | 3120.2412
| 7255 | 2332.9071 | 0 | 2332.9071
| 7256 | 1877.792 | 8.1768 | 1869.6152
| 7257 | 1236.2844 | 34.473 | 1201.8114
| 7258 | 959.0967 | 84.5807 | 874.516
| 7259 | 640.222 | 202.554 | 437.668
| 7260 | 431.2294 | 282.5474 | 148.682
| 7261 | 306.8562 | 434.853 | -127.9968
| 7262 | 302.896 | 513.4714 | -210.5754
| 7263 | 348.8872 | 458.7151 | -109.8279
| 7264 | 562.1829 | 325.6491 | 236.5338
| 7265 | 1000.7524 | 143.0946 | 857.6578
| 7266 | 1619.5545 | 51.1763 | 1568.3782
| 7267 | 2238.6637 | 23.0809 | 2215.5828
| 7268 | 2889.4872 | 0 | 2889.4872
| 7269 | 692.7485 | 0 | 692.7485
| 7270 | 788.2375 | 0 | 788.2375
| 7271 | 880.3861 | 0 | 880.3861
| 7272 | 975.9348 | 0 | 975.9348
| 7273 | 1078.3619 | 0 | 1078.3619
| 7274 | 1153.072 | 0 | 1153.072
| 7275 | 1324.9289 | 0 | 1324.9289
| 7276 | 1412.8309 | 0 | 1412.8309
| 7277 | 1565.0885 | 0 | 1565.0885
| 7278 | 1569.9025 | 0 | 1569.9025
| 7279 | 11204.1342 | 0 | 11204.1342
| 7280 | 8142.6432 | 0 | 8142.6432
| 7281 | 5886.4663 | 0 | 5886.4663
| 7282 | 4096.8299 | 1.061 | 4095.7689
| 7283 | 2769.3866 | 41.5723 | 2727.8143
| 7284 | 1915.2366 | 160.0013 | 1755.2353
| 7285 | 1554.9356 | 284.6504 | 1270.2852
| 7286 | 1135.6756 | 383.6172 | 752.0584
| 7287 | 880.2867 | 409.0172 | 471.2695
| 7288 | 770.8473 | 343.9463 | 426.901
| 7289 | 1246.1479 | 185.4527 | 1060.6952
| 7290 | 1811.4192 | 87.4672 | 1723.952
| 7291 | 2102.1313 | 41.1707 | 2060.9606
| 7292 | 2408.2245 | 20.1376 | 2388.0869
| 7293 | 2588.577 | 0 | 2588.577
| 7294 | 635.7804 | 0 | 635.7804
| 7295 | 613.3283 | 0 | 613.3283
| 7296 | 628.8738 | 0 | 628.8738
| 7297 | 633.722 | 0 | 633.722
| 7298 | 627.0649 | 0 | 627.0649
| 7299 | 620.7897 | 0 | 620.7897
| 7300 | 612.9325 | 0 | 612.9325
| 7301 | 608.1528 | 0 | 608.1528
| 7302 | 613.9449 | 0 | 613.9449
| 7303 | 6273.5277 | 18.97 | 6254.5576
| 7304 | 4427.2131 | 0 | 4427.2131
| 7305 | 3217.7634 | 0.15816 | 3217.6052
| 7306 | 2157.774 | 10.7405 | 2147.0335
| 7307 | 1569.7498 | 57.2501 | 1512.4997
| 7308 | 1086.4936 | 125.9839 | 960.5097
| 7309 | 877.402 | 194.6384 | 682.7636
| 7310 | 666.8572 | 268.4293 | 398.4279
| 7311 | 618.8315 | 294.8206 | 324.0109
| 7312 | 668.9272 | 226.4893 | 442.4378
| 7313 | 994.5278 | 120.5875 | 873.9403
| 7314 | 1416.8023 | 66.8327 | 1349.9697
| 7315 | 1708.4803 | 39.702 | 1668.7783
| 7316 | 1973.9518 | 24.7361 | 1949.2158
| 7317 | 2196.4894 | 0.34842 | 2196.141
| 7318 | 559.2747 | 0 | 559.2747
| 7319 | 615.5984 | 0 | 615.5984
| 7320 | 705.4178 | 0 | 705.4178
| 7321 | 804.4478 | 0 | 804.4478
| 7322 | 888.536 | 0 | 888.536
| 7323 | 924.7684 | 0 | 924.7684
| 7324 | 931.5982 | 0 | 931.5982
| 7325 | 910.7561 | 0 | 910.7561
| 7326 | 883.1461 | 0 | 883.1461
| 7327 | 7583.9485 | 0 | 7583.9485
| 7328 | 5359.2826 | 0 | 5359.2826
| 7329 | 4428.6082 | 0 | 4428.6082
| 7330 | 3481.5564 | 0 | 3481.5564
| 7331 | 2541.6732 | 0 | 2541.6732
| 7332 | 1897.234 | 0 | 1897.234
| 7333 | 1645.005 | 0 | 1645.005
| 7334 | 1376.7425 | 0 | 1376.7425
| 7335 | 1011.8885 | 0 | 1011.8885
| 7336 | 730.2786 | 0 | 730.2786
| 7337 | 625.5443 | 0 | 625.5443
| 7338 | 677.8662 | 0 | 677.8662
| 7339 | 1119.1596 | 0 | 1119.1596
| 7340 | 1407.8078 | 0 | 1407.8078
| 7341 | 1512.54 | 0 | 1512.54
| 7342 | 1792.6786 | 0 | 1792.6786
| 7343 | 373.6125 | 0 | 373.6125
| 7344 | 416.2677 | 0 | 416.2677
| 7345 | 461.5264 | 0 | 461.5264
| 7346 | 462.3395 | 0 | 462.3395
| 7347 | 495.8897 | 0 | 495.8897
| 7348 | 557.8803 | 0 | 557.8803
| 7349 | 614.1402 | 0 | 614.1402
| 7350 | 666.1421 | 0 | 666.1421
| 7351 | 734.3505 | 0 | 734.3505
| 7352 | 750.0805 | 0 | 750.0805
| 7353 | 5952.7991 | 0 | 5952.7991
| 7354 | 4039.2475 | 0 | 4039.2475
| 7355 | 2979.934 | 0 | 2979.934
| 7356 | 2404.5356 | 0 | 2404.5356
| 7357 | 1757.5065 | 0 | 1757.5065
| 7358 | 1553.3579 | 0 | 1553.3579
| 7359 | 1642.1542 | 0 | 1642.1542
| 7360 | 1804.3344 | 0 | 1804.3344
| 7361 | 2200.1002 | 0 | 2200.1002
| 7362 | 3690.8657 | 0 | 3690.8657
| 7363 | 4338.5413 | 0 | 4338.5413
| 7364 | 842.3468 | 0 | 842.3468
| 7365 | 894.4101 | 0 | 894.4101
| 7366 | 982.1802 | 0 | 982.1802
| 7367 | 1084.6502 | 0 | 1084.6502
| 7368 | 1288.0641 | 0 | 1288.0641
| 7369 | 1462.2122 | 0 | 1462.2122
| 7370 | 1566.3382 | 0 | 1566.3382
| 7371 | 1638.8576 | 0 | 1638.8576
| 7372 | 1655.8985 | 0 | 1655.8985
| 7373 | 1807.8451 | 0 | 1807.8451
| 7374 | 1840.7535 | 0 | 1840.7535
| 7375 | 11545.5822 | 0 | 11545.5822
| 7376 | 8558.6675 | 0 | 8558.6675
| 7377 | 6531.6385 | 0 | 6531.6385
| 7378 | 4914.4185 | 0 | 4914.4185
| 7379 | 3853.309 | 0 | 3853.309
| 7380 | 3128.3103 | 0 | 3128.3103
| 7381 | 2818.2947 | 0 | 2818.2947
| 7382 | 2603.24 | 0 | 2603.24
| 7383 | 2594.4707 | 0 | 2594.4707
| 7384 | 2834.7373 | 0 | 2834.7373
| 7385 | 3014.5456 | 0 | 3014.5456
| 7386 | 3092.221 | 0 | 3092.221
| 7387 | 3128.2796 | 0 | 3128.2796
| 7388 | 3100.0186 | 0 | 3100.0186
| 7389 | 3109.1134 | 0 | 3109.1134
| 7390 | 865.6478 | 0 | 865.6478
| 7391 | 712.2605 | 0 | 712.2605
| 7392 | 709.7752 | 0 | 709.7752
| 7393 | 718.3018 | 0 | 718.3018
| 7394 | 723.0084 | 0 | 723.0084
| 7395 | 700.5833 | 0 | 700.5833
| 7396 | 687.3826 | 0 | 687.3826
| 7397 | 714.2358 | 0 | 714.2358
| 7398 | 771.8419 | 0 | 771.8419
| 7399 | 7356.4203 | 0 | 7356.4203
| 7400 | 5630.8325 | 0 | 5630.8325
| 7401 | 4562.694 | 0 | 4562.694
| 7402 | 3254.0546 | 0 | 3254.0546
| 7403 | 2736.7982 | 0 | 2736.7982
| 7404 | 2362.6162 | 0 | 2362.6162
| 7405 | 2151.9878 | 0 | 2151.9878
| 7406 | 2029.7362 | 1.4223 | 2028.3139
| 7407 | 2134.8508 | 4.935 | 2129.9158
| 7408 | 2119.805 | 4.4327 | 2115.3724
| 7409 | 2275.3579 | 0.15365 | 2275.2043
| 7410 | 2523.843 | 0 | 2523.843
| 7411 | 2673.404 | 0 | 2673.404
| 7412 | 2834.7138 | 0 | 2834.7138
| 7413 | 2932.6323 | 0 | 2932.6323
| 7414 | 797.9863 | 0 | 797.9863
| 7415 | 728.4973 | 0 | 728.4973
| 7416 | 748.3174 | 0 | 748.3174
| 7417 | 788.1127 | 0 | 788.1127
| 7418 | 899.7473 | 0 | 899.7473
| 7419 | 959.129 | 0 | 959.129
| 7420 | 956.064 | 0 | 956.064
| 7421 | 1013.5331 | 0 | 1013.5331
| 7422 | 1053.9157 | 0 | 1053.9157
| 7423 | 8332.1062 | 0 | 8332.1062
| 7424 | 6036.2566 | 0 | 6036.2566
| 7425 | 4535.5573 | 0 | 4535.5573
| 7426 | 2957.3235 | 0 | 2957.3235
| 7427 | 1874.7499 | 0.33651 | 1874.4134
| 7428 | 964.4547 | 43.2418 | 921.2129
| 7429 | 534.3721 | 109.5112 | 424.8609
| 7430 | 268.5804 | 229.7098 | 38.8706
| 7431 | 219.4808 | 301.4863 | -82.0055
| 7432 | 228.9366 | 238.7662 | -9.8296
| 7433 | 303.1233 | 131.0516 | 172.0717
| 7434 | 572.6941 | 75.508 | 497.1861
| 7435 | 971.8962 | 36.1668 | 935.7293
| 7436 | 1241.5954 | 23.5277 | 1218.0677
| 7437 | 1561.5432 | 1.9545 | 1559.5887
| 7438 | 508.3579 | 0 | 508.3579
| 7439 | 627.9421 | 0 | 627.9421
| 7440 | 698.9563 | 0 | 698.9563
| 7441 | 708.1864 | 0 | 708.1864
| 7442 | 783.5986 | 0 | 783.5986
| 7443 | 836.9961 | 0 | 836.9961
| 7444 | 761.7353 | 0 | 761.7353
| 7445 | 708.8639 | 0 | 708.8639
| 7446 | 697.0925 | 0 | 697.0925
| 7447 | 6676.6849 | 0 | 6676.6849
| 7448 | 4637.1036 | 0 | 4637.1036
| 7449 | 3312.8948 | 0 | 3312.8948
| 7450 | 2062.5771 | 0 | 2062.5771
| 7451 | 992.7268 | 20.4908 | 972.236
| 7452 | 231.0792 | 68.4158 | 162.6634
| 7453 | 146.6525 | 172.8223 | -26.1698
| 7454 | 81.8362 | 421.8246 | -339.9884
| 7455 | 62.3334 | 389.5869 | -327.2536
| 7456 | 71.4373 | 337.0956 | -265.6583
| 7457 | 94.8982 | 250.623 | -155.7248
| 7458 | 58.8608 | 191.3603 | -132.4995
| 7459 | 26.2552 | 114.4 | -88.1448
| 7460 | 74.6372 | 66.3965 | 8.2407
| 7461 | 264.4227 | 18.7432 | 245.6795
| 7462 | 197.3095 | 2.6422 | 194.6673
| 7463 | 297.6476 | 0 | 297.6476
| 7464 | 375.8744 | 0 | 375.8744
| 7465 | 445.8737 | 0 | 445.8737
| 7466 | 526.0067 | 0 | 526.0067
| 7467 | 634.4661 | 0 | 634.4661
| 7468 | 742.9958 | 0 | 742.9958
| 7469 | 842.1059 | 0 | 842.1059
| 7470 | 901.0094 | 0 | 901.0094
| 7471 | 8271.8111 | 0 | 8271.8111
| 7472 | 5962.6366 | 0 | 5962.6366
| 7473 | 4295.3451 | 0 | 4295.3451
| 7474 | 2970.374 | 3.397 | 2966.9771
| 7475 | 2350.4112 | 29.7046 | 2320.7066
| 7476 | 1820.3641 | 113.8556 | 1706.5085
| 7477 | 1479.4507 | 205.7933 | 1273.6574
| 7478 | 2019.1698 | 89.0669 | 1930.1029
| 7479 | 2199.3883 | 42.9314 | 2156.4568
| 7480 | 2163.2476 | 43.4254 | 2119.8222
| 7481 | 2590.5836 | 18.9653 | 2571.6183
| 7482 | 3117.8516 | 0 | 3117.8516
| 7483 | 3468.4036 | 0 | 3468.4036
| 7484 | 3976.4593 | 0 | 3976.4593
| 7485 | 4344.2486 | 0 | 4344.2486
| 7486 | 1150.0535 | 0 | 1150.0535
| 7487 | 1098.2669 | 0 | 1098.2669
| 7488 | 1250.5121 | 0 | 1250.5121
| 7489 | 1324.7874 | 0 | 1324.7874
| 7490 | 1462.6945 | 0 | 1462.6945
| 7491 | 1621.1728 | 0 | 1621.1728
| 7492 | 1676.4252 | 0 | 1676.4252
| 7493 | 1764.4632 | 0 | 1764.4632
| 7494 | 1872.5412 | 0 | 1872.5412
| 7495 | 11261.2291 | 0 | 11261.2291
| 7496 | 8281.3946 | 0 | 8281.3946
| 7497 | 6779.8888 | 0 | 6779.8888
| 7498 | 5348.1003 | 0 | 5348.1003
| 7499 | 4383.96 | 0 | 4383.96
| 7500 | 3708.963 | 0 | 3708.963
| 7501 | 3275.2816 | 0 | 3275.2816
| 7502 | 3225.4858 | 0 | 3225.4858
| 7503 | 3370.9128 | 0 | 3370.9128
| 7504 | 3488.1468 | 0 | 3488.1468
| 7505 | 3855.2153 | 0 | 3855.2153
| 7506 | 4273.3857 | 0 | 4273.3857
| 7507 | 4660.3892 | 0 | 4660.3892
| 7508 | 5355.1775 | 0 | 5355.1775
| 7509 | 5614.225 | 0 | 5614.225
| 7510 | 6290.9768 | 0 | 6290.9768
| 7511 | 1933.4267 | 0 | 1933.4267
| 7512 | 2050.3988 | 0 | 2050.3988
| 7513 | 2121.0443 | 0 | 2121.0443
| 7514 | 2280.7672 | 0 | 2280.7672
| 7515 | 2427.0397 | 0 | 2427.0397
| 7516 | 2424.6183 | 0 | 2424.6183
| 7517 | 2444.41 | 0 | 2444.41
| 7518 | 2368.4811 | 0 | 2368.4811
| 7519 | 2248.9151 | 0 | 2248.9151
| 7520 | 2158.4481 | 0 | 2158.4481
| 7521 | 11556.5563 | 0 | 11556.5563
| 7522 | 8687.1776 | 0 | 8687.1776
| 7523 | 7390.3228 | 0 | 7390.3228
| 7524 | 6679.5404 | 0 | 6679.5404
| 7525 | 5694.0728 | 0 | 5694.0728
| 7526 | 4974.5429 | 0 | 4974.5429
| 7527 | 4415.6549 | 0 | 4415.6549
| 7528 | 4205.5427 | 0 | 4205.5427
| 7529 | 4190.24 | 0 | 4190.24
| 7530 | 5689.4149 | 0 | 5689.4149
| 7531 | 5811.7445 | 0 | 5811.7445
| 7532 | 1253.5096 | 0 | 1253.5096
| 7533 | 1227.1627 | 0 | 1227.1627
| 7534 | 1223.7035 | 0 | 1223.7035
| 7535 | 1253.9037 | 0 | 1253.9037
| 7536 | 1275.2519 | 0 | 1275.2519
| 7537 | 1309.4101 | 0 | 1309.4101
| 7538 | 1325.518 | 0 | 1325.518
| 7539 | 1371.1745 | 0 | 1371.1745
| 7540 | 1392.9838 | 0 | 1392.9838
| 7541 | 1345.8861 | 0 | 1345.8861
| 7542 | 1335.0761 | 0 | 1335.0761
| 7543 | 8964.4798 | 0 | 8964.4798
| 7544 | 6450.7585 | 0 | 6450.7585
| 7545 | 4959.9743 | 0 | 4959.9743
| 7546 | 3634.3699 | 0 | 3634.3699
| 7547 | 2819.2778 | 0 | 2819.2778
| 7548 | 1860.6533 | 0 | 1860.6533
| 7549 | 1437.0286 | 0 | 1437.0286
| 7550 | 1056.8101 | 0 | 1056.8101
| 7551 | 910.3719 | 0 | 910.3719
| 7552 | 889.5937 | 0 | 889.5937
| 7553 | 1176.8139 | 0 | 1176.8139
| 7554 | 1599.8074 | 0 | 1599.8074
| 7555 | 2089.1311 | 0 | 2089.1311
| 7556 | 2708.5251 | 0 | 2708.5251
| 7557 | 3180.284 | 0 | 3180.284
| 7558 | 956.1117 | 0 | 956.1117
| 7559 | 876.6589 | 0 | 876.6589
| 7560 | 1034.3582 | 0 | 1034.3582
| 7561 | 1166.3932 | 0 | 1166.3932
| 7562 | 1262.3049 | 0 | 1262.3049
| 7563 | 1345.689 | 0 | 1345.689
| 7564 | 1457.8824 | 0 | 1457.8824
| 7565 | 1523.7074 | 0 | 1523.7074
| 7566 | 1530.1977 | 0 | 1530.1977
| 7567 | 10003.1403 | 0 | 10003.1403
| 7568 | 7596.4662 | 0 | 7596.4662
| 7569 | 6493.8705 | 0 | 6493.8705
| 7570 | 5629.5003 | 0 | 5629.5003
| 7571 | 5306.7932 | 0 | 5306.7932
| 7572 | 4952.7759 | 0 | 4952.7759
| 7573 | 4646.9674 | 0 | 4646.9674
| 7574 | 4370.2541 | 0 | 4370.2541
| 7575 | 4271.611 | 0 | 4271.611
| 7576 | 4121.3471 | 0 | 4121.3471
| 7577 | 4106.2032 | 0 | 4106.2032
| 7578 | 4226.0247 | 0 | 4226.0247
| 7579 | 4306.1207 | 0 | 4306.1207
| 7580 | 4538.6182 | 0 | 4538.6182
| 7581 | 4694.4858 | 0 | 4694.4858
| 7582 | 1324.6344 | 0 | 1324.6344
| 7583 | 1131.8003 | 0 | 1131.8003
| 7584 | 1327.9546 | 0 | 1327.9546
| 7585 | 1459.878 | 0 | 1459.878
| 7586 | 1584.1871 | 0 | 1584.1871
| 7587 | 1715.0243 | 0 | 1715.0243
| 7588 | 1798.9025 | 0 | 1798.9025
| 7589 | 1879.8835 | 0 | 1879.8835
| 7590 | 2001.6644 | 0 | 2001.6644
| 7591 | 11874.4625 | 0 | 11874.4625
| 7592 | 8931.2054 | 0 | 8931.2054
| 7593 | 7033.1278 | 0 | 7033.1278
| 7594 | 5340.2998 | 0 | 5340.2998
| 7595 | 4251.1921 | 0 | 4251.1921
| 7596 | 3412.2592 | 0 | 3412.2592
| 7597 | 2998.4458 | 1.5059 | 2996.9399
| 7598 | 2763.8199 | 30.247 | 2733.5729
| 7599 | 2737.7188 | 42.9782 | 2694.7407
| 7600 | 2853.5455 | 26.0451 | 2827.5003
| 7601 | 3292.2749 | 3.9814 | 3288.2934
| 7602 | 3829.2429 | 0 | 3829.2429
| 7603 | 4355.9465 | 0 | 4355.9465
| 7604 | 4776.1436 | 0 | 4776.1436
| 7605 | 5164.2114 | 0 | 5164.2114
| 7606 | 1546.7448 | 0 | 1546.7448
| 7607 | 1444.256 | 0 | 1444.256
| 7608 | 1667.4513 | 0 | 1667.4513
| 7609 | 1821.2121 | 0 | 1821.2121
| 7610 | 2062.0007 | 0 | 2062.0007
| 7611 | 2093.4749 | 0 | 2093.4749
| 7612 | 2154.9456 | 0 | 2154.9456
| 7613 | 2299.6716 | 0 | 2299.6716
| 7614 | 2407.8462 | 0 | 2407.8462
| 7615 | 12970.6837 | 0 | 12970.6837
| 7616 | 9955.7697 | 0 | 9955.7697
| 7617 | 7721.0758 | 0 | 7721.0758
| 7618 | 5576.6213 | 0 | 5576.6213
| 7619 | 3892.9534 | 0 | 3892.9534
| 7620 | 2684.5407 | 20.6534 | 2663.8872
| 7621 | 2040.1667 | 55.8393 | 1984.3274
| 7622 | 1613.9021 | 115.8655 | 1498.0365
| 7623 | 1474.3477 | 147.8494 | 1326.4983
| 7624 | 1595.6425 | 81.9326 | 1513.7099
| 7625 | 1955.4623 | 52.8366 | 1902.6256
| 7626 | 2225.8558 | 19.9588 | 2205.897
| 7627 | 2561.9908 | 0.13595 | 2561.8549
| 7628 | 2907.8969 | 0 | 2907.8969
| 7629 | 3154.7513 | 0 | 3154.7513
| 7630 | 850.2636 | 0 | 850.2636
| 7631 | 777.7622 | 0 | 777.7622
| 7632 | 854.2291 | 0 | 854.2291
| 7633 | 1031.2458 | 0 | 1031.2458
| 7634 | 1110.8787 | 0 | 1110.8787
| 7635 | 1152.6029 | 0 | 1152.6029
| 7636 | 1237.9179 | 0 | 1237.9179
| 7637 | 1223.1827 | 0 | 1223.1827
| 7638 | 1235.2405 | 0 | 1235.2405
| 7639 | 9328.9789 | 0 | 9328.9789
| 7640 | 6756.2535 | 0 | 6756.2535
| 7641 | 4866.5107 | 0 | 4866.5107
| 7642 | 3215.2316 | 0 | 3215.2316
| 7643 | 2229.102 | 15.1922 | 2213.9098
| 7644 | 1443.8015 | 71.0831 | 1372.7185
| 7645 | 959.9696 | 209.0156 | 750.954
| 7646 | 617.9173 | 313.2931 | 304.6242
| 7647 | 547.2415 | 328.3429 | 218.8985
| 7648 | 591.3562 | 240.6535 | 350.7027
| 7649 | 1081.1802 | 111.1103 | 970.0699
| 7650 | 1466.3151 | 65.7837 | 1400.5314
| 7651 | 1729.2548 | 25.8099 | 1703.445
| 7652 | 2052.591 | 8.5467 | 2044.0443
| 7653 | 2216.1611 | 0 | 2216.1611
| 7654 | 619.1626 | 0 | 619.1626
| 7655 | 731.697 | 0 | 731.697
| 7656 | 894.6743 | 0 | 894.6743
| 7657 | 1001.2801 | 0 | 1001.2801
| 7658 | 1118.64 | 0 | 1118.64
| 7659 | 1195.3971 | 0 | 1195.3971
| 7660 | 1046.0083 | 0 | 1046.0083
| 7661 | 979.7065 | 0 | 979.7065
| 7662 | 1078.2623 | 0 | 1078.2623
| 7663 | 8860.1685 | 0 | 8860.1685
| 7664 | 6229.4246 | 0 | 6229.4246
| 7665 | 4899.6062 | 0 | 4899.6062
| 7666 | 3829.4729 | 0 | 3829.4729
| 7667 | 2911.0456 | 0 | 2911.0456
| 7668 | 2147.7811 | 0 | 2147.7811
| 7669 | 1514.5165 | 0 | 1514.5165
| 7670 | 1081.4065 | 1.2028 | 1080.2037
| 7671 | 827.0003 | 0 | 827.0003
| 7672 | 875.7852 | 0 | 875.7852
| 7673 | 1273.3964 | 0 | 1273.3964
| 7674 | 2124.5087 | 0 | 2124.5087
| 7675 | 2905.9827 | 0 | 2905.9827
| 7676 | 3481.1156 | 0 | 3481.1156
| 7677 | 3996.107 | 0 | 3996.107
| 7678 | 4635.5857 | 0 | 4635.5857
| 7679 | 1084.6872 | 0 | 1084.6872
| 7680 | 1169.0999 | 0 | 1169.0999
| 7681 | 1307.5265 | 0 | 1307.5265
| 7682 | 1380.7639 | 0 | 1380.7639
| 7683 | 1440.3292 | 0 | 1440.3292
| 7684 | 1506.0724 | 0 | 1506.0724
| 7685 | 1475.5141 | 0 | 1475.5141
| 7686 | 1449.2809 | 0 | 1449.2809
| 7687 | 1417.6719 | 0 | 1417.6719
| 7688 | 1339.4766 | 0 | 1339.4766
| 7689 | 8364.3197 | 0 | 8364.3197
| 7690 | 5947.2055 | 0 | 5947.2055
| 7691 | 4595.6299 | 0 | 4595.6299
| 7692 | 3660.981 | 0 | 3660.981
| 7693 | 2806.3103 | 0 | 2806.3103
| 7694 | 2382.7001 | 0 | 2382.7001
| 7695 | 2174.2779 | 0 | 2174.2779
| 7696 | 2097.7742 | 0 | 2097.7742
| 7697 | 2133.6363 | 0 | 2133.6363
| 7698 | 3334.2761 | 0 | 3334.2761
| 7699 | 3753.4025 | 0 | 3753.4025
| 7700 | 650.0102 | 0 | 650.0102
| 7701 | 657.4579 | 0 | 657.4579
| 7702 | 687.6193 | 0 | 687.6193
| 7703 | 733.3068 | 0 | 733.3068
| 7704 | 783.5093 | 0 | 783.5093
| 7705 | 845.9624 | 0 | 845.9624
| 7706 | 855.64 | 0 | 855.64
| 7707 | 893.74 | 0 | 893.74
| 7708 | 932.3988 | 0 | 932.3988
| 7709 | 1053.5842 | 0 | 1053.5842
| 7710 | 1205.6064 | 0 | 1205.6064
| 7711 | 8628.2731 | 0 | 8628.2731
| 7712 | 5958.6679 | 0 | 5958.6679
| 7713 | 4456.7364 | 0 | 4456.7364
| 7714 | 3067.2919 | 0 | 3067.2919
| 7715 | 2133.1443 | 0 | 2133.1443
| 7716 | 1374.309 | 0 | 1374.309
| 7717 | 1065.5689 | 0 | 1065.5689
| 7718 | 975.4233 | 0 | 975.4233
| 7719 | 960.3932 | 0 | 960.3932
| 7720 | 869.8784 | 0 | 869.8784
| 7721 | 984.4474 | 0 | 984.4474
| 7722 | 1213.2663 | 0 | 1213.2663
| 7723 | 1397.2229 | 0 | 1397.2229
| 7724 | 1622.1791 | 0 | 1622.1791
| 7725 | 1835.3393 | 0 | 1835.3393
| 7726 | 524.5764 | 0 | 524.5764
| 7727 | 516.8489 | 0 | 516.8489
| 7728 | 543.2681 | 0 | 543.2681
| 7729 | 553.6714 | 0 | 553.6714
| 7730 | 546.9237 | 0 | 546.9237
| 7731 | 545.4578 | 0 | 545.4578
| 7732 | 562.3235 | 0 | 562.3235
| 7733 | 520.9827 | 0 | 520.9827
| 7734 | 484.2693 | 0 | 484.2693
| 7735 | 5102.602 | 23.8211 | 5078.7809
| 7736 | 3350.6051 | 0 | 3350.6051
| 7737 | 2291.6946 | 0 | 2291.6946
| 7738 | 1262.4123 | 0 | 1262.4123
| 7739 | 823.2921 | 0 | 823.2921
| 7740 | 358.0426 | 20.0912 | 337.9514
| 7741 | 282.7714 | 32.3453 | 250.4262
| 7742 | 245.5474 | 98.403 | 147.1443
| 7743 | 259.3707 | 102.6823 | 156.6884
| 7744 | 324.7675 | 92.2179 | 232.5496
| 7745 | 512.02 | 73.0408 | 438.9792
| 7746 | 1347.4629 | 17.3571 | 1330.1058
| 7747 | 1802.5294 | 0 | 1802.5294
| 7748 | 2113.4799 | 0 | 2113.4799
| 7749 | 2478.4945 | 0 | 2478.4945
| 7750 | 615.4792 | 0 | 615.4792
| 7751 | 641.3458 | 0 | 641.3458
| 7752 | 681.2698 | 0 | 681.2698
| 7753 | 730.0919 | 0 | 730.0919
| 7754 | 788.9685 | 0 | 788.9685
| 7755 | 845.6219 | 0 | 845.6219
| 7756 | 852.9717 | 0 | 852.9717
| 7757 | 871.0312 | 0 | 871.0312
| 7758 | 906.9278 | 0 | 906.9278
| 7759 | 8143.1372 | 0 | 8143.1372
| 7760 | 6100.1726 | 0 | 6100.1726
| 7761 | 4870.0487 | 0 | 4870.0487
| 7762 | 3653.5851 | 0 | 3653.5851
| 7763 | 2978.1545 | 0 | 2978.1545
| 7764 | 2422.7415 | 0 | 2422.7415
| 7765 | 2146.098 | 0 | 2146.098
| 7766 | 1976.0647 | 0 | 1976.0647
| 7767 | 1965.1039 | 0 | 1965.1039
| 7768 | 2117.2912 | 0 | 2117.2912
| 7769 | 2300.3975 | 0 | 2300.3975
| 7770 | 2425.4507 | 0 | 2425.4507
| 7771 | 2566.587 | 0 | 2566.587
| 7772 | 2623.8877 | 0 | 2623.8877
| 7773 | 2760.7509 | 0 | 2760.7509
| 7774 | 751.5313 | 0 | 751.5313
| 7775 | 694.643 | 0 | 694.643
| 7776 | 724.8892 | 0 | 724.8892
| 7777 | 739.4831 | 0 | 739.4831
| 7778 | 743.9344 | 0 | 743.9344
| 7779 | 751.9405 | 0 | 751.9405
| 7780 | 744.1613 | 0 | 744.1613
| 7781 | 736.5731 | 0 | 736.5731
| 7782 | 726.3998 | 0 | 726.3998
| 7783 | 6794.0744 | 0 | 6794.0744
| 7784 | 4801.7292 | 0 | 4801.7292
| 7785 | 3759.9913 | 0 | 3759.9913
| 7786 | 2757.6476 | 0 | 2757.6476
| 7787 | 2334.1146 | 0 | 2334.1146
| 7788 | 1951.3431 | 0 | 1951.3431
| 7789 | 1687.7088 | 0 | 1687.7088
| 7790 | 1526.1392 | 0 | 1526.1392
| 7791 | 1437.7371 | 0 | 1437.7371
| 7792 | 1385.9265 | 0 | 1385.9265
| 7793 | 1406.0283 | 0 | 1406.0283
| 7794 | 1587.6093 | 0 | 1587.6093
| 7795 | 1821.2561 | 0 | 1821.2561
| 7796 | 2010.5246 | 0 | 2010.5246
| 7797 | 2274.7893 | 0 | 2274.7893
| 7798 | 657.268 | 0 | 657.268
| 7799 | 684.964 | 0 | 684.964
| 7800 | 784.3593 | 0 | 784.3593
| 7801 | 884.5812 | 0 | 884.5812
| 7802 | 960.1267 | 0 | 960.1267
| 7803 | 1038.764 | 0 | 1038.764
| 7804 | 1109.3858 | 0 | 1109.3858
| 7805 | 1162.0868 | 0 | 1162.0868
| 7806 | 1196.8424 | 0 | 1196.8424
| 7807 | 9245.0616 | 0 | 9245.0616
| 7808 | 6632.4538 | 0 | 6632.4538
| 7809 | 4998.5491 | 0 | 4998.5491
| 7810 | 3279.2255 | 0 | 3279.2255
| 7811 | 2415.8295 | 0 | 2415.8295
| 7812 | 1860.5489 | 0 | 1860.5489
| 7813 | 1642.1213 | 0 | 1642.1213
| 7814 | 1304.2726 | 8.6357 | 1295.6369
| 7815 | 1142.9575 | 31.2114 | 1111.746
| 7816 | 1356.7608 | 20.1682 | 1336.5925
| 7817 | 1590.8713 | 14.5568 | 1576.3145
| 7818 | 2208.2687 | 0.36542 | 2207.9032
| 7819 | 2804.395 | 0 | 2804.395
| 7820 | 3238.3297 | 0 | 3238.3297
| 7821 | 3725.8706 | 0 | 3725.8706
| 7822 | 1034.3374 | 0 | 1034.3374
| 7823 | 993.3926 | 0 | 993.3926
| 7824 | 1068.8501 | 0 | 1068.8501
| 7825 | 1208.7741 | 0 | 1208.7741
| 7826 | 1337.3125 | 0 | 1337.3125
| 7827 | 1472.8185 | 0 | 1472.8185
| 7828 | 1565.4952 | 0 | 1565.4952
| 7829 | 1626.8375 | 0 | 1626.8375
| 7830 | 1725.7292 | 0 | 1725.7292
| 7831 | 10945.9805 | 0 | 10945.9805
| 7832 | 8340.6568 | 0 | 8340.6568
| 7833 | 6846.338 | 0 | 6846.338
| 7834 | 5057.9409 | 0 | 5057.9409
| 7835 | 3418.0681 | 0 | 3418.0681
| 7836 | 2159.7833 | 2.1094 | 2157.6739
| 7837 | 1453.5315 | 35.6995 | 1417.832
| 7838 | 979.3213 | 63.1698 | 916.1515
| 7839 | 734.0972 | 47.8583 | 686.2389
| 7840 | 734.6618 | 34.8657 | 699.7961
| 7841 | 972.7418 | 6.6968 | 966.045
| 7842 | 1284.0414 | 0 | 1284.0414
| 7843 | 1924.5456 | 0 | 1924.5456
| 7844 | 2336.1427 | 0 | 2336.1427
| 7845 | 2787.381 | 0 | 2787.381
| 7846 | 3408.8843 | 0 | 3408.8843
| 7847 | 686.3708 | 0 | 686.3708
| 7848 | 772.3332 | 0 | 772.3332
| 7849 | 819.1824 | 0 | 819.1824
| 7850 | 824.0818 | 0 | 824.0818
| 7851 | 825.0386 | 0 | 825.0386
| 7852 | 806.4979 | 0 | 806.4979
| 7853 | 739.1744 | 0 | 739.1744
| 7854 | 680.6118 | 0 | 680.6118
| 7855 | 659.2396 | 0 | 659.2396
| 7856 | 626.6964 | 0 | 626.6964
| 7857 | 5388.649 | 0 | 5388.649
| 7858 | 3846.2324 | 0 | 3846.2324
| 7859 | 3195.8806 | 0 | 3195.8806
| 7860 | 2820.7233 | 0 | 2820.7233
| 7861 | 2186.06 | 0 | 2186.06
| 7862 | 1833.1189 | 0 | 1833.1189
| 7863 | 1655.437 | 0 | 1655.437
| 7864 | 1654.9519 | 0 | 1654.9519
| 7865 | 1729.4478 | 0 | 1729.4478
| 7866 | 2728.7312 | 0 | 2728.7312
| 7867 | 2968.4922 | 0 | 2968.4922
| 7868 | 436.3177 | 0 | 436.3177
| 7869 | 436.2774 | 0 | 436.2774
| 7870 | 406.3668 | 0 | 406.3668
| 7871 | 385.3147 | 0 | 385.3147
| 7872 | 365.6043 | 0 | 365.6043
| 7873 | 338.2653 | 0 | 338.2653
| 7874 | 310.5861 | 0 | 310.5861
| 7875 | 285.7481 | 0 | 285.7481
| 7876 | 258.1538 | 0 | 258.1538
| 7877 | 227.9798 | 0 | 227.9798
| 7878 | 201.4649 | 0 | 201.4649
| 7879 | 2616.8824 | 0 | 2616.8824
| 7880 | 1798.5927 | 0 | 1798.5927
| 7881 | 785.6495 | 0 | 785.6495
| 7882 | 118.0073 | 0 | 118.0073
| 7883 | 447.1423 | 0 | 447.1423
| 7884 | 531.558 | 0 | 531.558
| 7885 | 787.0049 | 0 | 787.0049
| 7886 | 1425.9835 | 0 | 1425.9835
| 7887 | 1757.0915 | 0 | 1757.0915
| 7888 | 2000.5087 | 0 | 2000.5087
| 7889 | 2490.8118 | 0 | 2490.8118
| 7890 | 2948.9939 | 0 | 2948.9939
| 7891 | 3220.0782 | 0 | 3220.0782
| 7892 | 3535.3363 | 0 | 3535.3363
| 7893 | 3827.1403 | 0 | 3827.1403
| 7894 | 1130.9333 | 0 | 1130.9333
| 7895 | 1042.9284 | 0 | 1042.9284
| 7896 | 1325.4197 | 0 | 1325.4197
| 7897 | 1470.5794 | 0 | 1470.5794
| 7898 | 1583.2123 | 0 | 1583.2123
| 7899 | 1709.6442 | 0 | 1709.6442
| 7900 | 1783.9297 | 0 | 1783.9297
| 7901 | 1839.7294 | 0 | 1839.7294
| 7902 | 1929.6979 | 0 | 1929.6979
| 7903 | 11556.054 | 0 | 11556.054
| 7904 | 8823.4793 | 0 | 8823.4793
| 7905 | 7025.9707 | 0 | 7025.9707
| 7906 | 5382.8651 | 0 | 5382.8651
| 7907 | 4480.481 | 0 | 4480.481
| 7908 | 3861.6578 | 0 | 3861.6578
| 7909 | 3195.9886 | 0 | 3195.9886
| 7910 | 2816.2407 | 13.7649 | 2802.4758
| 7911 | 2711.6641 | 31.8117 | 2679.8525
| 7912 | 2775.1332 | 23.5667 | 2751.5666
| 7913 | 3123.0219 | 4.1758 | 3118.8461
| 7914 | 3470.6767 | 0 | 3470.6767
| 7915 | 3634.227 | 0 | 3634.227
| 7916 | 3722.1888 | 0 | 3722.1888
| 7917 | 3961.3464 | 0 | 3961.3464
| 7918 | 1110.2681 | 0 | 1110.2681
| 7919 | 977.4927 | 0 | 977.4927
| 7920 | 1020.1305 | 0 | 1020.1305
| 7921 | 1176.9408 | 0 | 1176.9408
| 7922 | 1309.3393 | 0 | 1309.3393
| 7923 | 1387.8132 | 0 | 1387.8132
| 7924 | 1457.3067 | 0 | 1457.3067
| 7925 | 1538.3155 | 0 | 1538.3155
| 7926 | 1548.8136 | 0 | 1548.8136
| 7927 | 10394.6046 | 0 | 10394.6046
| 7928 | 7745.4741 | 0 | 7745.4741
| 7929 | 6292.4558 | 0 | 6292.4558
| 7930 | 5091.3114 | 0 | 5091.3114
| 7931 | 4274.6261 | 0 | 4274.6261
| 7932 | 3373.7017 | 0 | 3373.7017
| 7933 | 2582.1524 | 0 | 2582.1524
| 7934 | 2018.264 | 0 | 2018.264
| 7935 | 1816.1395 | 0 | 1816.1395
| 7936 | 1591.2495 | 0 | 1591.2495
| 7937 | 1632.7884 | 0 | 1632.7884
| 7938 | 1861.0922 | 0 | 1861.0922
| 7939 | 2117.6952 | 0 | 2117.6952
| 7940 | 2374.2283 | 0 | 2374.2283
| 7941 | 2580.2416 | 0 | 2580.2416
| 7942 | 734.2224 | 0 | 734.2224
| 7943 | 681.0749 | 0 | 681.0749
| 7944 | 682.1954 | 0 | 682.1954
| 7945 | 671.6837 | 0 | 671.6837
| 7946 | 669.5983 | 0 | 669.5983
| 7947 | 661.7692 | 0 | 661.7692
| 7948 | 655.5403 | 0 | 655.5403
| 7949 | 652.7311 | 0 | 652.7311
| 7950 | 641.5285 | 0 | 641.5285
| 7951 | 6154.5839 | 18.993 | 6135.5908
| 7952 | 4128.4235 | 0 | 4128.4235
| 7953 | 3004.8291 | 0 | 3004.8291
| 7954 | 1880.9145 | 0 | 1880.9145
| 7955 | 1493.7132 | 0 | 1493.7132
| 7956 | 1309.7621 | 0 | 1309.7621
| 7957 | 1172.8993 | 0 | 1172.8993
| 7958 | 1051.6964 | 0 | 1051.6964
| 7959 | 988.4236 | 0 | 988.4236
| 7960 | 879.6191 | 0 | 879.6191
| 7961 | 986.194 | 0 | 986.194
| 7962 | 1391.7286 | 0 | 1391.7286
| 7963 | 1750.7855 | 0 | 1750.7855
| 7964 | 2177.0165 | 0 | 2177.0165
| 7965 | 2432.7763 | 0 | 2432.7763
| 7966 | 710.1379 | 0 | 710.1379
| 7967 | 670.1021 | 0 | 670.1021
| 7968 | 706.0433 | 0 | 706.0433
| 7969 | 753.2071 | 0 | 753.2071
| 7970 | 767.4986 | 0 | 767.4986
| 7971 | 779.2957 | 0 | 779.2957
| 7972 | 861.327 | 0 | 861.327
| 7973 | 975.0505 | 0 | 975.0505
| 7974 | 1041.9062 | 0 | 1041.9062
| 7975 | 8437.2902 | 0 | 8437.2902
| 7976 | 6396.1172 | 0 | 6396.1172
| 7977 | 5056.1266 | 0 | 5056.1266
| 7978 | 3711.8962 | 0 | 3711.8962
| 7979 | 3117.8664 | 0 | 3117.8664
| 7980 | 2880.168 | 0 | 2880.168
| 7981 | 2670.3892 | 0 | 2670.3892
| 7982 | 2403.2606 | 0 | 2403.2606
| 7983 | 2336.5972 | 0 | 2336.5972
| 7984 | 2409.0733 | 0 | 2409.0733
| 7985 | 2830.5323 | 0 | 2830.5323
| 7986 | 3244.4697 | 0 | 3244.4697
| 7987 | 3479.8609 | 0 | 3479.8609
| 7988 | 3695.3257 | 0 | 3695.3257
| 7989 | 3917.6728 | 0 | 3917.6728
| 7990 | 1047.9141 | 0 | 1047.9141
| 7991 | 975.2417 | 0 | 975.2417
| 7992 | 1003.4005 | 0 | 1003.4005
| 7993 | 1046.5304 | 0 | 1046.5304
| 7994 | 1109.1641 | 0 | 1109.1641
| 7995 | 1167.4495 | 0 | 1167.4495
| 7996 | 1186.2158 | 0 | 1186.2158
| 7997 | 1227.6932 | 0 | 1227.6932
| 7998 | 1242.2089 | 0 | 1242.2089
| 7999 | 9078.2277 | 0 | 9078.2277
| 8000 | 7019.0835 | 0 | 7019.0835
| 8001 | 5993.4393 | 0 | 5993.4393
| 8002 | 4734.1865 | 0 | 4734.1865
| 8003 | 3591.2337 | 0 | 3591.2337
| 8004 | 2956.7718 | 0 | 2956.7718
| 8005 | 2550.9172 | 0 | 2550.9172
| 8006 | 2261.1479 | 0 | 2261.1479
| 8007 | 2186.1299 | 0 | 2186.1299
| 8008 | 2228.0018 | 0 | 2228.0018
| 8009 | 2390.3246 | 0 | 2390.3246
| 8010 | 2590.0975 | 0 | 2590.0975
| 8011 | 2932.8391 | 0 | 2932.8391
| 8012 | 3352.8135 | 0 | 3352.8135
| 8013 | 3511.3705 | 0 | 3511.3705
| 8014 | 4008.0155 | 0 | 4008.0155
| 8015 | 989.9659 | 0 | 989.9659
| 8016 | 1149.2696 | 0 | 1149.2696
| 8017 | 1328.1019 | 0 | 1328.1019
| 8018 | 1507.7315 | 0 | 1507.7315
| 8019 | 1685.015 | 0 | 1685.015
| 8020 | 1868.5535 | 0 | 1868.5535
| 8021 | 2010.3516 | 0 | 2010.3516
| 8022 | 2118.5099 | 0 | 2118.5099
| 8023 | 2215.0424 | 0 | 2215.0424
| 8024 | 2122.8068 | 0 | 2122.8068
| 8025 | 10830.7574 | 0 | 10830.7574
| 8026 | 7679.9211 | 0 | 7679.9211
| 8027 | 6032.3309 | 0 | 6032.3309
| 8028 | 4992.2744 | 0 | 4992.2744
| 8029 | 3869.059 | 0 | 3869.059
| 8030 | 3451.0938 | 0 | 3451.0938
| 8031 | 3401.8376 | 0 | 3401.8376
| 8032 | 3481.457 | 0 | 3481.457
| 8033 | 3597.5441 | 0 | 3597.5441
| 8034 | 5127.2276 | 0 | 5127.2276
| 8035 | 5540.7215 | 0 | 5540.7215
| 8036 | 1243.9621 | 0 | 1243.9621
| 8037 | 1256.3989 | 0 | 1256.3989
| 8038 | 1269.2067 | 0 | 1269.2067
| 8039 | 1333.7771 | 0 | 1333.7771
| 8040 | 1412.1918 | 0 | 1412.1918
| 8041 | 1485.1917 | 0 | 1485.1917
| 8042 | 1514.5125 | 0 | 1514.5125
| 8043 | 1518.5396 | 0 | 1518.5396
| 8044 | 1514.1553 | 0 | 1514.1553
| 8045 | 1487.6504 | 0 | 1487.6504
| 8046 | 1439.8367 | 0 | 1439.8367
| 8047 | 9356.2214 | 0 | 9356.2214
| 8048 | 6929.96 | 0 | 6929.96
| 8049 | 5543.8427 | 0 | 5543.8427
| 8050 | 4339.0397 | 0 | 4339.0397
| 8051 | 3775.8542 | 0 | 3775.8542
| 8052 | 3362.8233 | 0 | 3362.8233
| 8053 | 3206.9817 | 0 | 3206.9817
| 8054 | 3186.3415 | 0 | 3186.3415
| 8055 | 3314.3053 | 0 | 3314.3053
| 8056 | 3472.405 | 0 | 3472.405
| 8057 | 3727.7554 | 0 | 3727.7554
| 8058 | 4040.7926 | 0 | 4040.7926
| 8059 | 4226.8578 | 0 | 4226.8578
| 8060 | 4530.4248 | 0 | 4530.4248
| 8061 | 4965.4486 | 0 | 4965.4486
| 8062 | 1538.9042 | 0 | 1538.9042
| 8063 | 1479.58 | 0 | 1479.58
| 8064 | 1854.9815 | 0 | 1854.9815
| 8065 | 2128.4499 | 0 | 2128.4499
| 8066 | 2343.2658 | 0 | 2343.2658
| 8067 | 2527.2878 | 0 | 2527.2878
| 8068 | 2701.5761 | 0 | 2701.5761
| 8069 | 2815.8907 | 0 | 2815.8907
| 8070 | 2867.7888 | 0 | 2867.7888
| 8071 | 13721.0807 | 0 | 13721.0807
| 8072 | 11249.2365 | 0 | 11249.2365
| 8073 | 9487.9287 | 0 | 9487.9287
| 8074 | 8028.3208 | 0 | 8028.3208
| 8075 | 7279.5165 | 0 | 7279.5165
| 8076 | 6729.464 | 0 | 6729.464
| 8077 | 6411.8446 | 0 | 6411.8446
| 8078 | 6030.6781 | 0 | 6030.6781
| 8079 | 5698.0946 | 0 | 5698.0946
| 8080 | 5420.4933 | 0 | 5420.4933
| 8081 | 5309.0809 | 0 | 5309.0809
| 8082 | 5268.7025 | 0 | 5268.7025
| 8083 | 5202.9001 | 0 | 5202.9001
| 8084 | 5125.9649 | 0 | 5125.9649
| 8085 | 5082.1196 | 0 | 5082.1196
| 8086 | 1438.1239 | 0 | 1438.1239
| 8087 | 1172.2456 | 0 | 1172.2456
| 8088 | 1271.35 | 0 | 1271.35
| 8089 | 1284.8336 | 0 | 1284.8336
| 8090 | 1275.3747 | 0 | 1275.3747
| 8091 | 1259.8157 | 0 | 1259.8157
| 8092 | 1236.049 | 0 | 1236.049
| 8093 | 1202.7667 | 0 | 1202.7667
| 8094 | 1157.5393 | 0 | 1157.5393
| 8095 | 8436.9041 | 0 | 8436.9041
| 8096 | 5957.035 | 0 | 5957.035
| 8097 | 4435.7457 | 0 | 4435.7457
| 8098 | 3059.6041 | 0 | 3059.6041
| 8099 | 2335.5916 | 0 | 2335.5916
| 8100 | 1779.6866 | 0 | 1779.6866
| 8101 | 1466.3881 | 0 | 1466.3881
| 8102 | 1391.0789 | 0 | 1391.0789
| 8103 | 1481.3143 | 0 | 1481.3143
| 8104 | 1588.9636 | 0 | 1588.9636
| 8105 | 1905.0199 | 0 | 1905.0199
| 8106 | 2393.2511 | 0 | 2393.2511
| 8107 | 2877.8278 | 0 | 2877.8278
| 8108 | 3216.2846 | 0 | 3216.2846
| 8109 | 3498.6873 | 0 | 3498.6873
| 8110 | 1036.0304 | 0 | 1036.0304
| 8111 | 891.926 | 0 | 891.926
| 8112 | 1007.9721 | 0 | 1007.9721
| 8113 | 1122.7906 | 0 | 1122.7906
| 8114 | 1202.177 | 0 | 1202.177
| 8115 | 1256.6381 | 0 | 1256.6381
| 8116 | 1300.0288 | 0 | 1300.0288
| 8117 | 1445.7615 | 0 | 1445.7615
| 8118 | 1645.5808 | 0 | 1645.5808
| 8119 | 11029.5658 | 0 | 11029.5658
| 8120 | 8312.4007 | 0 | 8312.4007
| 8121 | 6384.2747 | 0 | 6384.2747
| 8122 | 4719.4902 | 0 | 4719.4902
| 8123 | 3754.0252 | 0 | 3754.0252
| 8124 | 2963.7122 | 0 | 2963.7122
| 8125 | 2404.8622 | 0 | 2404.8622
| 8126 | 2175.5061 | 0 | 2175.5061
| 8127 | 2163.9146 | 0 | 2163.9146
| 8128 | 2187.0551 | 0 | 2187.0551
| 8129 | 2548.9612 | 0 | 2548.9612
| 8130 | 3079.3284 | 0 | 3079.3284
| 8131 | 3548.2484 | 0 | 3548.2484
| 8132 | 3723.1514 | 0 | 3723.1514
| 8133 | 3750.4146 | 0 | 3750.4146
| 8134 | 1008.3006 | 0 | 1008.3006
| 8135 | 879.6818 | 0 | 879.6818
| 8136 | 941.5361 | 0 | 941.5361
| 8137 | 1050.4645 | 0 | 1050.4645
| 8138 | 1137.4382 | 0 | 1137.4382
| 8139 | 1198.4427 | 0 | 1198.4427
| 8140 | 1245.0118 | 0 | 1245.0118
| 8141 | 1335.8432 | 0 | 1335.8432
| 8142 | 1453.6769 | 0 | 1453.6769
| 8143 | 10056.5909 | 0 | 10056.5909
| 8144 | 7291.167 | 0 | 7291.167
| 8145 | 5274.3092 | 0 | 5274.3092
| 8146 | 3463.8293 | 0 | 3463.8293
| 8147 | 2383.5492 | 9.7631 | 2373.786
| 8148 | 1488.0759 | 67.9264 | 1420.1495
| 8149 | 880.7902 | 160.0989 | 720.6914
| 8150 | 712.3349 | 254.4989 | 457.836
| 8151 | 885.7971 | 220.9216 | 664.8755
| 8152 | 1143.9689 | 113.212 | 1030.7569
| 8153 | 1446.0378 | 74.7537 | 1371.2841
| 8154 | 1808.9825 | 38.7823 | 1770.2002
| 8155 | 2138.4289 | 6.6822 | 2131.7467
| 8156 | 2700.2235 | 0.079964 | 2700.1436
| 8157 | 3421.27 | 0 | 3421.27
| 8158 | 1019.2108 | 0 | 1019.2108
| 8159 | 937.9572 | 0 | 937.9572
| 8160 | 938.7111 | 0 | 938.7111
| 8161 | 936.6886 | 0 | 936.6886
| 8162 | 941.0405 | 0 | 941.0405
| 8163 | 967.1836 | 0 | 967.1836
| 8164 | 987.7094 | 0 | 987.7094
| 8165 | 1037.6013 | 0 | 1037.6013
| 8166 | 1107.4326 | 0 | 1107.4326
| 8167 | 8457.8627 | 0 | 8457.8627
| 8168 | 6285.1313 | 0 | 6285.1313
| 8169 | 5278.289 | 0 | 5278.289
| 8170 | 4222.5118 | 0 | 4222.5118
| 8171 | 3360.3389 | 0 | 3360.3389
| 8172 | 2796.5488 | 0 | 2796.5488
| 8173 | 2459.7887 | 0 | 2459.7887
| 8174 | 2283.4492 | 0 | 2283.4492
| 8175 | 2257.8905 | 0 | 2257.8905
| 8176 | 2222.1352 | 0 | 2222.1352
| 8177 | 2290.8366 | 0 | 2290.8366
| 8178 | 2539.3157 | 0 | 2539.3157
| 8179 | 2963.5165 | 0 | 2963.5165
| 8180 | 3501.1806 | 0 | 3501.1806
| 8181 | 3993.2053 | 0 | 3993.2053
| 8182 | 4723.345 | 0 | 4723.345
| 8183 | 1123.6012 | 0 | 1123.6012
| 8184 | 1063.7785 | 0 | 1063.7785
| 8185 | 975.167 | 0 | 975.167
| 8186 | 921.5728 | 0 | 921.5728
| 8187 | 904.7979 | 0 | 904.7979
| 8188 | 884.7677 | 0 | 884.7677
| 8189 | 877.0029 | 0 | 877.0029
| 8190 | 873.7415 | 0 | 873.7415
| 8191 | 866.628 | 0 | 866.628
| 8192 | 838.6915 | 0 | 838.6915
| 8193 | 6053.233 | 0 | 6053.233
| 8194 | 4360.5152 | 0 | 4360.5152
| 8195 | 3494.9063 | 0 | 3494.9063
| 8196 | 3014.2421 | 0 | 3014.2421
| 8197 | 2397.248 | 0 | 2397.248
| 8198 | 2146.2786 | 0 | 2146.2786
| 8199 | 2034.5151 | 0 | 2034.5151
| 8200 | 1977.733 | 0 | 1977.733
| 8201 | 1996.5744 | 0 | 1996.5744
| 8202 | 3111.5533 | 0 | 3111.5533
| 8203 | 3486.8604 | 0 | 3486.8604
| 8204 | 622.8981 | 0 | 622.8981
| 8205 | 654.9541 | 0 | 654.9541
| 8206 | 691.3239 | 0 | 691.3239
| 8207 | 791.0182 | 0 | 791.0182
| 8208 | 914.9569 | 0 | 914.9569
| 8209 | 1036.7047 | 0 | 1036.7047
| 8210 | 1142.2256 | 0 | 1142.2256
| 8211 | 1239.6466 | 0 | 1239.6466
| 8212 | 1333.7268 | 0 | 1333.7268
| 8213 | 1407.9298 | 0 | 1407.9298
| 8214 | 1451.1094 | 0 | 1451.1094
| 8215 | 9350.1923 | 0 | 9350.1923
| 8216 | 7171.4395 | 0 | 7171.4395
| 8217 | 5914.9365 | 0 | 5914.9365
| 8218 | 4957.6126 | 0 | 4957.6126
| 8219 | 4538.0985 | 0 | 4538.0985
| 8220 | 4225.2817 | 0 | 4225.2817
| 8221 | 4114.2944 | 0 | 4114.2944
| 8222 | 3983.1729 | 0 | 3983.1729
| 8223 | 3897.7897 | 0 | 3897.7897
| 8224 | 3840.7293 | 0 | 3840.7293
| 8225 | 4025.0803 | 0 | 4025.0803
| 8226 | 4393.7937 | 0 | 4393.7937
| 8227 | 4635.4869 | 0 | 4635.4869
| 8228 | 4886.4364 | 0 | 4886.4364
| 8229 | 5204.63 | 0 | 5204.63
| 8230 | 1586.0497 | 0 | 1586.0497
| 8231 | 1446.9128 | 0 | 1446.9128
| 8232 | 1705.1906 | 0 | 1705.1906
| 8233 | 1844.8746 | 0 | 1844.8746
| 8234 | 2005.4616 | 0 | 2005.4616
| 8235 | 2178.9127 | 0 | 2178.9127
| 8236 | 2350.7042 | 0 | 2350.7042
| 8237 | 2437.8869 | 0 | 2437.8869
| 8238 | 2450.0989 | 0 | 2450.0989
| 8239 | 12784.0661 | 0 | 12784.0661
| 8240 | 9953.2195 | 0 | 9953.2195
| 8241 | 8366.9749 | 0 | 8366.9749
| 8242 | 7014.168 | 0 | 7014.168
| 8243 | 6245.0408 | 0 | 6245.0408
| 8244 | 5637.7102 | 0 | 5637.7102
| 8245 | 5326.6213 | 0 | 5326.6213
| 8246 | 5253.3692 | 0 | 5253.3692
| 8247 | 5291.6139 | 0 | 5291.6139
| 8248 | 5392.8115 | 0 | 5392.8115
| 8249 | 5761.5992 | 0 | 5761.5992
| 8250 | 6232.6671 | 0 | 6232.6671
| 8251 | 6572.3653 | 0 | 6572.3653
| 8252 | 6833.7251 | 0 | 6833.7251
| 8253 | 7029.1535 | 0 | 7029.1535
| 8254 | 2155.0976 | 0 | 2155.0976
| 8255 | 2144.8274 | 0 | 2144.8274
| 8256 | 2303.4933 | 0 | 2303.4933
| 8257 | 2387.6719 | 0 | 2387.6719
| 8258 | 2457.1175 | 0 | 2457.1175
| 8259 | 2517.1808 | 0 | 2517.1808
| 8260 | 2565.9732 | 0 | 2565.9732
| 8261 | 2646.2388 | 0 | 2646.2388
| 8262 | 2728.6522 | 0 | 2728.6522
| 8263 | 13761.5236 | 0 | 13761.5236
| 8264 | 11221.6755 | 0 | 11221.6755
| 8265 | 9372.1441 | 0 | 9372.1441
| 8266 | 7812.9004 | 0 | 7812.9004
| 8267 | 6842.0679 | 0 | 6842.0679
| 8268 | 5956.0363 | 0 | 5956.0363
| 8269 | 5270.3409 | 0 | 5270.3409
| 8270 | 4945.7601 | 0 | 4945.7601
| 8271 | 4946.909 | 0 | 4946.909
| 8272 | 4964.6338 | 0 | 4964.6338
| 8273 | 5400.7398 | 0 | 5400.7398
| 8274 | 6121.4023 | 0 | 6121.4023
| 8275 | 6649.9293 | 0 | 6649.9293
| 8276 | 7178.738 | 0 | 7178.738
| 8277 | 7770.6468 | 0 | 7770.6468
| 8278 | 2454.7601 | 0 | 2454.7601
| 8279 | 2569.2987 | 0 | 2569.2987
| 8280 | 2686.4833 | 0 | 2686.4833
| 8281 | 2652.9822 | 0 | 2652.9822
| 8282 | 2641.4917 | 0 | 2641.4917
| 8283 | 2654.9546 | 0 | 2654.9546
| 8284 | 2659.3001 | 0 | 2659.3001
| 8285 | 2664.6264 | 0 | 2664.6264
| 8286 | 2660.9429 | 0 | 2660.9429
| 8287 | 13434.5948 | 0 | 13434.5948
| 8288 | 10755.5018 | 0 | 10755.5018
| 8289 | 8907.1286 | 0 | 8907.1286
| 8290 | 7411.631 | 0 | 7411.631
| 8291 | 6536.1516 | 0 | 6536.1516
| 8292 | 5813.0362 | 0 | 5813.0362
| 8293 | 5346.2174 | 0 | 5346.2174
| 8294 | 4990.8389 | 0 | 4990.8389
| 8295 | 4776.2562 | 0 | 4776.2562
| 8296 | 4622.153 | 0 | 4622.153
| 8297 | 4630.1005 | 0 | 4630.1005
| 8298 | 4690.5759 | 0 | 4690.5759
| 8299 | 4736.0972 | 0 | 4736.0972
| 8300 | 4873.9991 | 0 | 4873.9991
| 8301 | 5129.5818 | 0 | 5129.5818
| 8302 | 1500.6825 | 0 | 1500.6825
| 8303 | 1284.4164 | 0 | 1284.4164
| 8304 | 1473.7253 | 0 | 1473.7253
| 8305 | 1577.8511 | 0 | 1577.8511
| 8306 | 1630.3862 | 0 | 1630.3862
| 8307 | 1659.8579 | 0 | 1659.8579
| 8308 | 1675.2273 | 0 | 1675.2273
| 8309 | 1695.2809 | 0 | 1695.2809
| 8310 | 1708.8668 | 0 | 1708.8668
| 8311 | 10506.727 | 0 | 10506.727
| 8312 | 7873.2674 | 0 | 7873.2674
| 8313 | 6530.3544 | 0 | 6530.3544
| 8314 | 5361.3773 | 0 | 5361.3773
| 8315 | 4723.9987 | 0 | 4723.9987
| 8316 | 4222.4517 | 0 | 4222.4517
| 8317 | 3937.5791 | 0 | 3937.5791
| 8318 | 3613.5381 | 0 | 3613.5381
| 8319 | 3294.1948 | 0 | 3294.1948
| 8320 | 3051.5206 | 0 | 3051.5206
| 8321 | 3068.5369 | 0 | 3068.5369
| 8322 | 3246.297 | 0 | 3246.297
| 8323 | 3350.4982 | 0 | 3350.4982
| 8324 | 3580.1959 | 0 | 3580.1959
| 8325 | 3934.0047 | 0 | 3934.0047
| 8326 | 1184.2182 | 0 | 1184.2182
| 8327 | 992.8607 | 0 | 992.8607
| 8328 | 1102.1547 | 0 | 1102.1547
| 8329 | 1197.3873 | 0 | 1197.3873
| 8330 | 1278.2349 | 0 | 1278.2349
| 8331 | 1358.9625 | 0 | 1358.9625
| 8332 | 1430.8631 | 0 | 1430.8631
| 8333 | 1495.5909 | 0 | 1495.5909
| 8334 | 1543.0904 | 0 | 1543.0904
| 8335 | 9262.5735 | 0 | 9262.5735
| 8336 | 7174.1241 | 0 | 7174.1241
| 8337 | 6432.1268 | 0 | 6432.1268
| 8338 | 5656.8277 | 0 | 5656.8277
| 8339 | 5001.0369 | 0 | 5001.0369
| 8340 | 4559.2244 | 0 | 4559.2244
| 8341 | 4391.6438 | 0 | 4391.6438
| 8342 | 4333.6518 | 0 | 4333.6518
| 8343 | 4281.5553 | 0 | 4281.5553
| 8344 | 4321.0199 | 0 | 4321.0199
| 8345 | 4465.2057 | 0 | 4465.2057
| 8346 | 4723.8126 | 0 | 4723.8126
| 8347 | 5083.7551 | 0 | 5083.7551
| 8348 | 5748.7846 | 0 | 5748.7846
| 8349 | 6244.641 | 0 | 6244.641
| 8350 | 6920.8092 | 0 | 6920.8092
| 8351 | 2104.2619 | 0 | 2104.2619
| 8352 | 2196.2073 | 0 | 2196.2073
| 8353 | 2280.3867 | 0 | 2280.3867
| 8354 | 2314.2997 | 0 | 2314.2997
| 8355 | 2319.9166 | 0 | 2319.9166
| 8356 | 2316.1543 | 0 | 2316.1543
| 8357 | 2338.6884 | 0 | 2338.6884
| 8358 | 2364.7258 | 0 | 2364.7258
| 8359 | 2388.251 | 0 | 2388.251
| 8360 | 2344.1468 | 0 | 2344.1468
| 8361 | 11440.2627 | 0 | 11440.2627
| 8362 | 8772.838 | 0 | 8772.838
| 8363 | 7378.2849 | 0 | 7378.2849
| 8364 | 6315.0647 | 0 | 6315.0647
| 8365 | 5191.6736 | 0 | 5191.6736
| 8366 | 4606.54 | 0 | 4606.54
| 8367 | 4301.1683 | 0 | 4301.1683
| 8368 | 4122.3667 | 0 | 4122.3667
| 8369 | 4309.6216 | 0 | 4309.6216
| 8370 | 6252.568 | 0 | 6252.568
| 8371 | 6973.6488 | 0 | 6973.6488
| 8372 | 1729.5547 | 0 | 1729.5547
| 8373 | 1838.68 | 0 | 1838.68
| 8374 | 1947.3992 | 0 | 1947.3992
| 8375 | 1948.9288 | 0 | 1948.9288
| 8376 | 1865.012 | 0 | 1865.012
| 8377 | 1765.0817 | 0 | 1765.0817
| 8378 | 1801.9654 | 0 | 1801.9654
| 8379 | 1933.4881 | 0 | 1933.4881
| 8380 | 2074.1468 | 0 | 2074.1468
| 8381 | 2211.3199 | 0 | 2211.3199
| 8382 | 2343.4448 | 0 | 2343.4448
| 8383 | 13176.6635 | 0 | 13176.6635
| 8384 | 9886.0769 | 0 | 9886.0769
| 8385 | 7237.4708 | 0 | 7237.4708
| 8386 | 4917.5561 | 0 | 4917.5561
| 8387 | 3657.1473 | 0 | 3657.1473
| 8388 | 2881.2936 | 0 | 2881.2936
| 8389 | 2362.0815 | 0 | 2362.0815
| 8390 | 2095.1575 | 2.5562 | 2092.6013
| 8391 | 2014.8876 | 9.7939 | 2005.0937
| 8392 | 1971.6811 | 12.288 | 1959.3931
| 8393 | 2425.2488 | 0.9201 | 2424.3287
| 8394 | 3183.3966 | 0 | 3183.3966
| 8395 | 3884.4011 | 0 | 3884.4011
| 8396 | 4434.6007 | 0 | 4434.6007
| 8397 | 4881.3731 | 0 | 4881.3731
| 8398 | 1460.8274 | 0 | 1460.8274
| 8399 | 1182.7694 | 0 | 1182.7694
| 8400 | 1200.2082 | 0 | 1200.2082
| 8401 | 1119.7668 | 0 | 1119.7668
| 8402 | 1133.8266 | 0 | 1133.8266
| 8403 | 1243.5213 | 0 | 1243.5213
| 8404 | 1352.9288 | 0 | 1352.9288
| 8405 | 1403.2957 | 0 | 1403.2957
| 8406 | 1400.5819 | 0 | 1400.5819
| 8407 | 9509.1276 | 0 | 9509.1276
| 8408 | 7111.0914 | 0 | 7111.0914
| 8409 | 5741.1625 | 0 | 5741.1625
| 8410 | 4591.077 | 0 | 4591.077
| 8411 | 4079.1444 | 0 | 4079.1444
| 8412 | 3742.8648 | 0 | 3742.8648
| 8413 | 3657.2571 | 0 | 3657.2571
| 8414 | 3623.2093 | 0 | 3623.2093
| 8415 | 3703.1334 | 0 | 3703.1334
| 8416 | 3831.2105 | 0 | 3831.2105
| 8417 | 4055.1732 | 0 | 4055.1732
| 8418 | 4361.9699 | 0 | 4361.9699
| 8419 | 4550.2159 | 0 | 4550.2159
| 8420 | 4800.7442 | 0 | 4800.7442
| 8421 | 5118.5791 | 0 | 5118.5791
| 8422 | 1616.3346 | 0 | 1616.3346
| 8423 | 1664.2775 | 0 | 1664.2775
| 8424 | 1932.2275 | 0 | 1932.2275
| 8425 | 2085.5868 | 0 | 2085.5868
| 8426 | 2243.5673 | 0 | 2243.5673
| 8427 | 2416.9793 | 0 | 2416.9793
| 8428 | 2581.0414 | 0 | 2581.0414
| 8429 | 2694.4521 | 0 | 2694.4521
| 8430 | 2750.4447 | 0 | 2750.4447
| 8431 | 13384.2253 | 0 | 13384.2253
| 8432 | 10330.6824 | 0 | 10330.6824
| 8433 | 8367.2624 | 0 | 8367.2624
| 8434 | 6772.723 | 0 | 6772.723
| 8435 | 5869.4505 | 0 | 5869.4505
| 8436 | 5131.1818 | 0 | 5131.1818
| 8437 | 4734.1052 | 0 | 4734.1052
| 8438 | 4682.9703 | 0 | 4682.9703
| 8439 | 4929.8745 | 0 | 4929.8745
| 8440 | 5219.4161 | 0 | 5219.4161
| 8441 | 5647.8628 | 0 | 5647.8628
| 8442 | 6179.7351 | 0 | 6179.7351
| 8443 | 6588.4185 | 0 | 6588.4185
| 8444 | 6977.387 | 0 | 6977.387
| 8445 | 7313.7992 | 0 | 7313.7992
| 8446 | 2355.1634 | 0 | 2355.1634
| 8447 | 2664.9885 | 0 | 2664.9885
| 8448 | 2968.8882 | 0 | 2968.8882
| 8449 | 3147.6147 | 0 | 3147.6147
| 8450 | 3170.5636 | 0 | 3170.5636
| 8451 | 3252.4267 | 0 | 3252.4267
| 8452 | 3313.1306 | 0 | 3313.1306
| 8453 | 3331.9432 | 0 | 3331.9432
| 8454 | 3313.2025 | 0 | 3313.2025
| 8455 | 14319.8191 | 0 | 14319.8191
| 8456 | 11709.5265 | 0 | 11709.5265
| 8457 | 9697.2744 | 0 | 9697.2744
| 8458 | 8011.5883 | 0 | 8011.5883
| 8459 | 7035.2935 | 0 | 7035.2935
| 8460 | 6172.052 | 0 | 6172.052
| 8461 | 5642.669 | 0 | 5642.669
| 8462 | 5358.2375 | 0 | 5358.2375
| 8463 | 5280.2958 | 0 | 5280.2958
| 8464 | 5283.977 | 0 | 5283.977
| 8465 | 5534.4493 | 0 | 5534.4493
| 8466 | 5876.678 | 0 | 5876.678
| 8467 | 6038.9893 | 0 | 6038.9893
| 8468 | 6262.2809 | 0 | 6262.2809
| 8469 | 6513.0477 | 0 | 6513.0477
| 8470 | 1962.2655 | 0 | 1962.2655
| 8471 | 1965.9242 | 0 | 1965.9242
| 8472 | 2148.5749 | 0 | 2148.5749
| 8473 | 2200.1567 | 0 | 2200.1567
| 8474 | 2231.6516 | 0 | 2231.6516
| 8475 | 2245.6901 | 0 | 2245.6901
| 8476 | 2240.8085 | 0 | 2240.8085
| 8477 | 2289.4408 | 0 | 2289.4408
| 8478 | 2351.2425 | 0 | 2351.2425
| 8479 | 13485.1146 | 0 | 13485.1146
| 8480 | 10418.246 | 0 | 10418.246
| 8481 | 8622.2509 | 0 | 8622.2509
| 8482 | 7190.3294 | 0 | 7190.3294
| 8483 | 6458.2791 | 0 | 6458.2791
| 8484 | 5892.7174 | 0 | 5892.7174
| 8485 | 5566.7958 | 0 | 5566.7958
| 8486 | 5377.0214 | 0 | 5377.0214
| 8487 | 5319.518 | 0 | 5319.518
| 8488 | 5302.7551 | 0 | 5302.7551
| 8489 | 5360.7485 | 0 | 5360.7485
| 8490 | 5504.7931 | 0 | 5504.7931
| 8491 | 5556.5598 | 0 | 5556.5598
| 8492 | 5525.3461 | 0 | 5525.3461
| 8493 | 5500.594 | 0 | 5500.594
| 8494 | 1571.8586 | 0 | 1571.8586
| 8495 | 1330.3628 | 0 | 1330.3628
| 8496 | 1469.3937 | 0 | 1469.3937
| 8497 | 1523.0063 | 0 | 1523.0063
| 8498 | 1535.419 | 0 | 1535.419
| 8499 | 1539.3199 | 0 | 1539.3199
| 8500 | 1533.018 | 0 | 1533.018
| 8501 | 1523.3843 | 0 | 1523.3843
| 8502 | 1505.1466 | 0 | 1505.1466
| 8503 | 9169.1006 | 0 | 9169.1006
| 8504 | 6898.2399 | 0 | 6898.2399
| 8505 | 5889.6459 | 0 | 5889.6459
| 8506 | 4890.9486 | 0 | 4890.9486
| 8507 | 4054.3603 | 0 | 4054.3603
| 8508 | 3375.6554 | 0 | 3375.6554
| 8509 | 2970.6251 | 0 | 2970.6251
| 8510 | 3025.8741 | 0 | 3025.8741
| 8511 | 3430.6609 | 0 | 3430.6609
| 8512 | 3853.1468 | 0 | 3853.1468
| 8513 | 4122.1133 | 0 | 4122.1133
| 8514 | 4381.0904 | 0 | 4381.0904
| 8515 | 4818.9604 | 0 | 4818.9604
| 8516 | 5471.5608 | 0 | 5471.5608
| 8517 | 5931.3335 | 0 | 5931.3335
| 8518 | 6572.2019 | 0 | 6572.2019
| 8519 | 2013.1071 | 0 | 2013.1071
| 8520 | 2049.5987 | 0 | 2049.5987
| 8521 | 2072.0116 | 0 | 2072.0116
| 8522 | 2106.7256 | 0 | 2106.7256
| 8523 | 2157.0605 | 0 | 2157.0605
| 8524 | 2201.9386 | 0 | 2201.9386
| 8525 | 2235.0925 | 0 | 2235.0925
| 8526 | 2244.8498 | 0 | 2244.8498
| 8527 | 2248.2875 | 0 | 2248.2875
| 8528 | 2181.6057 | 0 | 2181.6057
| 8529 | 11121.5514 | 0 | 11121.5514
| 8530 | 8393.0559 | 0 | 8393.0559
| 8531 | 7057.5006 | 0 | 7057.5006
| 8532 | 6144.2525 | 0 | 6144.2525
| 8533 | 5178.7781 | 0 | 5178.7781
| 8534 | 4804.6628 | 0 | 4804.6628
| 8535 | 4597.4037 | 0 | 4597.4037
| 8536 | 4453.1291 | 0 | 4453.1291
| 8537 | 4574.9795 | 0 | 4574.9795
| 8538 | 6391.0008 | 0 | 6391.0008
| 8539 | 6933.2025 | 0 | 6933.2025
| 8540 | 1706.6957 | 0 | 1706.6957
| 8541 | 1776.5588 | 0 | 1776.5588
| 8542 | 1847.126 | 0 | 1847.126
| 8543 | 1909.3258 | 0 | 1909.3258
| 8544 | 1959.8808 | 0 | 1959.8808
| 8545 | 1993.4479 | 0 | 1993.4479
| 8546 | 1993.3214 | 0 | 1993.3214
| 8547 | 1976.5289 | 0 | 1976.5289
| 8548 | 1952.5032 | 0 | 1952.5032
| 8549 | 1914.9183 | 0 | 1914.9183
| 8550 | 1865.2735 | 0 | 1865.2735
| 8551 | 11158.2869 | 0 | 11158.2869
| 8552 | 8393.0085 | 0 | 8393.0085
| 8553 | 6711.1106 | 0 | 6711.1106
| 8554 | 5270.8793 | 0 | 5270.8793
| 8555 | 4302.9644 | 0 | 4302.9644
| 8556 | 3454.5572 | 0 | 3454.5572
| 8557 | 2843.2255 | 0 | 2843.2255
| 8558 | 2670.2404 | 0 | 2670.2404
| 8559 | 2738.045 | 0 | 2738.045
| 8560 | 2876.7818 | 0 | 2876.7818
| 8561 | 3151.0834 | 0 | 3151.0834
| 8562 | 3491.9742 | 0 | 3491.9742
| 8563 | 3709.1473 | 0 | 3709.1473
| 8564 | 4084.1416 | 0 | 4084.1416
| 8565 | 4586.3419 | 0 | 4586.3419
| 8566 | 1432.0937 | 0 | 1432.0937
| 8567 | 1288.1238 | 0 | 1288.1238
| 8568 | 1522.418 | 0 | 1522.418
| 8569 | 1659.5888 | 0 | 1659.5888
| 8570 | 1813.5706 | 0 | 1813.5706
| 8571 | 1985.3699 | 0 | 1985.3699
| 8572 | 2148.9484 | 0 | 2148.9484
| 8573 | 2268.028 | 0 | 2268.028
| 8574 | 2336.935 | 0 | 2336.935
| 8575 | 13230.1829 | 0 | 13230.1829
| 8576 | 10151.6678 | 0 | 10151.6678
| 8577 | 8079.8423 | 0 | 8079.8423
| 8578 | 6281.3726 | 0 | 6281.3726
| 8579 | 5267.6357 | 0 | 5267.6357
| 8580 | 4577.8624 | 0 | 4577.8624
| 8581 | 4165.2562 | 0 | 4165.2562
| 8582 | 3958.2587 | 0 | 3958.2587
| 8583 | 3927.7078 | 0 | 3927.7078
| 8584 | 3933.8832 | 0 | 3933.8832
| 8585 | 3943.0784 | 0 | 3943.0784
| 8586 | 4011.049 | 0 | 4011.049
| 8587 | 3966.866 | 0 | 3966.866
| 8588 | 4094.5675 | 0 | 4094.5675
| 8589 | 4332.6099 | 0 | 4332.6099
| 8590 | 1278.8194 | 0 | 1278.8194
| 8591 | 1101.4199 | 0 | 1101.4199
| 8592 | 1322.1671 | 0 | 1322.1671
| 8593 | 1493.5267 | 0 | 1493.5267
| 8594 | 1571.1806 | 0 | 1571.1806
| 8595 | 1598.9282 | 0 | 1598.9282
| 8596 | 1614.512 | 0 | 1614.512
| 8597 | 1645.1805 | 0 | 1645.1805
| 8598 | 1677.4372 | 0 | 1677.4372
| 8599 | 9330.9475 | 0 | 9330.9475
| 8600 | 7215.4152 | 0 | 7215.4152
| 8601 | 6283.9696 | 0 | 6283.9696
| 8602 | 5265.4175 | 0 | 5265.4175
| 8603 | 4721.1533 | 0 | 4721.1533
| 8604 | 4227.9663 | 0 | 4227.9663
| 8605 | 3931.6646 | 0 | 3931.6646
| 8606 | 3779.4632 | 0 | 3779.4632
| 8607 | 3725.098 | 0 | 3725.098
| 8608 | 3646.9757 | 0 | 3646.9757
| 8609 | 3842.7241 | 0 | 3842.7241
| 8610 | 4156.8871 | 0 | 4156.8871
| 8611 | 4593.7669 | 0 | 4593.7669
| 8612 | 4886.2952 | 0 | 4886.2952
| 8613 | 5014.5177 | 0 | 5014.5177
| 8614 | 1759.3052 | 0 | 1759.3052
| 8615 | 1834.6049 | 0 | 1834.6049
| 8616 | 1941.2448 | 0 | 1941.2448
| 8617 | 2052.9231 | 0 | 2052.9231
| 8618 | 2116.5992 | 0 | 2116.5992
| 8619 | 2146.5671 | 0 | 2146.5671
| 8620 | 2173.0171 | 0 | 2173.0171
| 8621 | 2198.2159 | 0 | 2198.2159
| 8622 | 2206.5604 | 0 | 2206.5604
| 8623 | 10655.8188 | 0 | 10655.8188
| 8624 | 8357.3532 | 0 | 8357.3532
| 8625 | 7254.8168 | 0 | 7254.8168
| 8626 | 5960.0221 | 0 | 5960.0221
| 8627 | 5182.8868 | 0 | 5182.8868
| 8628 | 4518.0043 | 0 | 4518.0043
| 8629 | 4102.6323 | 0 | 4102.6323
| 8630 | 4049.6432 | 0 | 4049.6432
| 8631 | 4125.2587 | 0 | 4125.2587
| 8632 | 4252.0165 | 0 | 4252.0165
| 8633 | 4675.822 | 0 | 4675.822
| 8634 | 5239.7966 | 0 | 5239.7966
| 8635 | 5928.7997 | 0 | 5928.7997
| 8636 | 6432.8632 | 0 | 6432.8632
| 8637 | 6741.5238 | 0 | 6741.5238
| 8638 | 2381.5819 | 0 | 2381.5819
| 8639 | 2423.1892 | 0 | 2423.1892
| 8640 | 2435.9711 | 0 | 2435.9711
| 8641 | 2429.1513 | 0 | 2429.1513
| 8642 | 2406.0494 | 0 | 2406.0494
| 8643 | 2383.6511 | 0 | 2383.6511
| 8644 | 2352.9101 | 0 | 2352.9101
| 8645 | 2337.8764 | 0 | 2337.8764
| 8646 | 2324.1568 | 0 | 2324.1568
| 8647 | 12475.7843 | 0 | 12475.7843
| 8648 | 9588.8323 | 0 | 9588.8323
| 8649 | 7937.9133 | 0 | 7937.9133
| 8650 | 6535.3738 | 0 | 6535.3738
| 8651 | 5698.9128 | 0 | 5698.9128
| 8652 | 5029.0291 | 0 | 5029.0291
| 8653 | 4619.3825 | 0 | 4619.3825
| 8654 | 4450.0605 | 0 | 4450.0605
| 8655 | 4507.2368 | 0 | 4507.2368
| 8656 | 4625.254 | 0 | 4625.254
| 8657 | 4894.7387 | 0 | 4894.7387
| 8658 | 5259.5323 | 0 | 5259.5323
| 8659 | 5468.9959 | 0 | 5468.9959
| 8660 | 5698.902 | 0 | 5698.902
| 8661 | 6023.4127 | 0 | 6023.4127
| 8662 | 1872.9597 | 0 | 1872.9597
| 8663 | 1928.0646 | 0 | 1928.0646
| 8664 | 2265.456 | 0 | 2265.456
| 8665 | 2485.5236 | 0 | 2485.5236
| 8666 | 2650.2716 | 0 | 2650.2716
| 8667 | 2796.9057 | 0 | 2796.9057
| 8668 | 2932.8729 | 0 | 2932.8729
| 8669 | 3080.1973 | 0 | 3080.1973
| 8670 | 3223.2423 | 0 | 3223.2423
| 8671 | 13782.0687 | 0 | 13782.0687
| 8672 | 11528.1345 | 0 | 11528.1345
| 8673 | 9960.5426 | 0 | 9960.5426
| 8674 | 8589.0378 | 0 | 8589.0378
| 8675 | 7467.2141 | 0 | 7467.2141
| 8676 | 6603.2053 | 0 | 6603.2053
| 8677 | 6052.0133 | 0 | 6052.0133
| 8678 | 5856.3011 | 0 | 5856.3011
| 8679 | 5837.9869 | 0 | 5837.9869
| 8680 | 5915.678 | 0 | 5915.678
| 8681 | 6206.3433 | 0 | 6206.3433
| 8682 | 6632.1966 | 0 | 6632.1966
| 8683 | 7422.9676 | 0 | 7422.9676
| 8684 | 8232.9713 | 0 | 8232.9713
| 8685 | 8747.1823 | 0 | 8747.1823
| 8686 | 9420.2002 | 0 | 9420.2002
| 8687 | 3239.8234 | 0 | 3239.8234
| 8688 | 3435.6348 | 0 | 3435.6348
| 8689 | 3624.6716 | 0 | 3624.6716
| 8690 | 3672.1521 | 0 | 3672.1521
| 8691 | 3632.4291 | 0 | 3632.4291
| 8692 | 3577.6178 | 0 | 3577.6178
| 8693 | 3602.879 | 0 | 3602.879
| 8694 | 3671.2564 | 0 | 3671.2564
| 8695 | 3734.2604 | 0 | 3734.2604
| 8696 | 3718.7539 | 0 | 3718.7539
| 8697 | 15361.302 | 0 | 15361.302
| 8698 | 12734.7286 | 0 | 12734.7286
| 8699 | 10652.4103 | 0 | 10652.4103
| 8700 | 9093.7485 | 0 | 9093.7485
| 8701 | 7606.8393 | 0 | 7606.8393
| 8702 | 7008.5033 | 0 | 7008.5033
| 8703 | 6879.3326 | 0 | 6879.3326
| 8704 | 6967.2975 | 0 | 6967.2975
| 8705 | 7356.3628 | 0 | 7356.3628
| 8706 | 10179.064 | 0 | 10179.064
| 8707 | 11052.2221 | 0 | 11052.2221
| 8708 | 3094.6048 | 0 | 3094.6048
| 8709 | 3254.1151 | 0 | 3254.1151
| 8710 | 3411.518 | 0 | 3411.518
| 8711 | 3531.0294 | 0 | 3531.0294
| 8712 | 3610.2941 | 0 | 3610.2941
| 8713 | 3668.2796 | 0 | 3668.2796
| 8714 | 3667.1808 | 0 | 3667.1808
| 8715 | 3621.0107 | 0 | 3621.0107
| 8716 | 3572.1964 | 0 | 3572.1964
| 8717 | 3586.0383 | 0 | 3586.0383
| 8718 | 3631.7558 | 0 | 3631.7558
| 8719 | 16097.8568 | 0 | 16097.8568
| 8720 | 13514.4253 | 0 | 13514.4253
| 8721 | 11408.4991 | 0 | 11408.4991
| 8722 | 9778.3331 | 0 | 9778.3331
| 8723 | 8652.2123 | 0 | 8652.2123
| 8724 | 7640.974 | 0 | 7640.974
| 8725 | 6911.7088 | 0 | 6911.7088
| 8726 | 6245.0281 | 0 | 6245.0281
| 8727 | 5750.4216 | 0 | 5750.4216
| 8728 | 5341.3602 | 0 | 5341.3602
| 8729 | 5473.3749 | 0 | 5473.3749
| 8730 | 5950.2688 | 0 | 5950.2688
| 8731 | 6243.2087 | 0 | 6243.2087
| 8732 | 6444.1018 | 0 | 6444.1018
| 8733 | 6615.5121 | 0 | 6615.5121
| 8734 | 1970.7885 | 0 | 1970.7885
| 8735 | 1839.8413 | 0 | 1839.8413
| 8736 | 2056.592 | 0 | 2056.592
| 8737 | 2132.0732 | 0 | 2132.0732
| 8738 | 2148.8364 | 0 | 2148.8364
| 8739 | 2136.1489 | 0 | 2136.1489
| 8740 | 2111.2055 | 0 | 2111.2055
| 8741 | 2087.7885 | 0 | 2087.7885
| 8742 | 2057.7088 | 0 | 2057.7088
| 8743 | 12125.9161 | 0 | 12125.9161
| 8744 | 8972.05 | 0 | 8972.05
| 8745 | 7041.418 | 0 | 7041.418
| 8746 | 5389.8423 | 0 | 5389.8423
| 8747 | 4594.9901 | 0 | 4594.9901
| 8748 | 4119.6693 | 0 | 4119.6693
| 8749 | 3913.4824 | 0 | 3913.4824
| 8750 | 3684.7512 | 0 | 3684.7512
| 8751 | 3516.9431 | 0 | 3516.9431
| 8752 | 3384.9573 | 0 | 3384.9573
| 8753 | 3369.5647 | 0 | 3369.5647
| 8754 | 3477.0776 | 0 | 3477.0776
| 8755 | 3481.5248 | 0 | 3481.5248
| 8756 | 3573.5765 | 0 | 3573.5765
| 8757 | 3741.7022 | 0 | 3741.7022
| 8758 | 1109.3679 | 0 | 1109.3679
| 8759 | 888.8904 | 0 | 888.8904
| 8760 | 973.5758 | 0 | 973.5758

## Pivot Tables (hidden)
Monthy Peak Electric Demand (kW) | [5 empty] | Monthly Peak Heat Pump Loop Energy Demand (MBH) |  | Monthly Total Heat Pump Loop Energy Consumption (MMBtu) |  |  | Peak Daily Heat Absorbed from Geo-Loop (MBH) | [32 empty] | Peak Hourly Heat Absorbed from Geo-Loop (MBH) | [26 empty] | Peak Hourly Heat Rejected to Geo-Loop (MBH)
Months | Max of Total Electric Demand |  | Total Peak Demand (kW) | Electric Cost ($) |  | Months | Max of Heating Load (MBH) | Months |  |  |  | Hours | [33 empty] | Column Labels | [26 empty] | Column Labels
1 | 85.5384 |  | 85.5384 | 1598.457 |  | 1 | 18348.4894 | 1 |  |  | Months | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Grand Total | Row Labels | Day | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Grand Total | Row Labels | Day | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Grand Total
2 | 87.3457 |  | 87.3457 | 1619.0243 |  | 2 | 17882.5674 | 2 |  |  | 1 | [32 empty] | 1 | 1 | [25 empty] | 1 | 1
3 | 80.093 |  | 80.093 | 1536.4879 |  | 3 | 15635.3609 | 3 |  |  | 2 | [32 empty] | 1 | 2 | [25 empty] | 1 | 2
4 | 46.2234 |  | 46.2234 | 1151.052 |  | 4 | 10595.056 | 4 |  |  | 3 | [32 empty] | 1 | 3 | [25 empty] | 1 | 3
5 | 74.6896 |  | 74.6896 | 1474.9975 |  | 5 | 9185.5084 | 5 |  |  | 4 | [32 empty] | 1 | 4 | [25 empty] | 1 | 4
6 | 88.3262 |  | 88.3262 | 1630.1816 |  | 6 | 6904.7187 | 6 |  |  | 5 | [32 empty] | 1 | 5 | [25 empty] | 1 | 5
7 | 108.8554 |  | 108.8554 | 1863.804 |  | 7 | 3090.2265 | 7 |  |  | 6 | [32 empty] | 1 | 6 | [25 empty] | 1 | 6
8 | 97.1205 |  | 97.1205 | 1730.2613 |  | 8 | 3504.8118 | 8 |  |  | 7 | [32 empty] | 1 | 7 | [25 empty] | 1 | 7
9 | 91.4797 |  | 91.4797 | 1666.0689 |  | 9 | 7428.9658 | 9 |  |  | 8 | [32 empty] | 1 | 8 | [25 empty] | 1 | 8
10 | 55.3895 |  | 55.3895 | 1255.3621 |  | 10 | 11462.047 | 10 |  |  | 9 | [32 empty] | 1 | 9 | [25 empty] | 1 | 9
11 | 73.6103 |  | 73.6103 | 1462.7155 |  | 11 | 12970.6837 | 11 |  |  | 10 | [32 empty] | 1 | 10 | [25 empty] | 1 | 10
12 | 84.6345 |  | 84.6345 | 1588.1702 |  | 12 | 16097.8568 | 12 |  |  | 11 | [32 empty] | 1 | 11 | [25 empty] | 1 | 11
Grand Total | 108.8554 |  | 108.8554 | 18576.5824 |  | Grand Total | 18348.4894 | Grand Total |  |  | 12 | [32 empty] | 1 | 12 | [25 empty] | 1 | 12
|  |  | 0.07786 | [7 empty] | Grand Total | [32 empty] | 1 | 13 | [25 empty] | 1 | 13
[6 empty] | Monthly Peak Geo-Loop Energy Demand (MBH) |  | Monthly Total Geo-Loop Energy Consumption (MMBtu) | [35 empty] | 1 | 14 | [25 empty] | 1 | 14
Monthy Electric Consumption (kWh) | [5 empty] | Months |  | Months | Sum of Heat Absorbed from WWTP Outfall (MBH) | Sum of Heat Rejected to WWTP Outfall (MBH) | Peak Daily Heat Rejected to Geo-Loop (MBH) | [32 empty] | 1 | 15 | [25 empty] | 1 | 15
Months | Sum of Total Electric Demand | 2021 SC3 Supply Price | Total Consumption (kWh) | Electric Cost ($) |  | 1 |  | 1 | 3703039.0643 | 0 |  | Hours | [31 empty] | 1 | 16 | [25 empty] | 1 | 16
1 | 21865.2481 | 0.069488 | 21865.3176 | 1519.3857 |  | 2 |  | 2 | 2742803.9291 | 0 | Months | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Grand Total | 1 | 17 | [25 empty] | 1 | 17
2 | 18695.7142 | 0.11856 | 18695.8328 | 2216.5846 |  | 3 |  | 3 | 1940488.1146 | 39929.3167 | 1 | [32 empty] | 1 | 18 | [25 empty] | 1 | 18
3 | 19457.2173 | 0.066042 | 19457.2834 | 1284.9904 |  | 4 |  | 4 | 898733.9042 | 172197.7781 | 2 | [32 empty] | 1 | 19 | [25 empty] | 1 | 19
4 | 18006.7645 | 0.046219 | 18006.8107 | 832.2628 |  | 5 |  | 5 | 274106.3416 | 1077193.5292 | 3 | [32 empty] | 1 | 20 | [25 empty] | 1 | 20
5 | 18811.8423 | 0.043677 | 18811.886 | 821.6486 |  | 6 |  | 6 | 114611.2452 | 1690644.3902 | 4 | [32 empty] | 1 | 21 | [25 empty] | 1 | 21
6 | 18700.9294 | 0.069524 | 18700.9989 | 1300.162 |  | 7 |  | 7 | 28685.7536 | 3924336.8093 | 5 | [32 empty] | 1 | 22 | [25 empty] | 1 | 22
7 | 24561.2374 | 0.085452 | 24561.3229 | 2098.8205 |  | 8 |  | 8 | 59748.2516 | 2942682.1583 | 6 | [32 empty] | 1 | 23 | [25 empty] | 1 | 23
8 | 22152.2103 | 0.10853 | 22152.3188 | 2404.1411 |  | 9 |  | 9 | 246419.7697 | 1321263.4058 | 7 | [32 empty] | 1 | 24 | [25 empty] | 1 | 24
9 | 19260.0852 | 0.10085 | 19260.1861 | 1942.3063 |  | 10 |  | 10 | 775951.2087 | 167348.5398 | 8 | [32 empty] | 1 | 25 | [25 empty] | 1 | 25
10 | 18636.5703 | 0.068858 | 18636.6392 | 1283.2829 |  | 11 |  | 11 | 1539240.6294 | 2955.2909 | 9 | [32 empty] | 1 | 26 | [25 empty] | 1 | 26
11 | 18333.6452 | 0.047086 | 18333.6923 | 863.2663 |  | 12 |  | 12 | 2774159.3902 | 0 | 10 | [32 empty] | 1 | 27 | [25 empty] | 1 | 27
12 | 20106.3152 | 0.053532 | 20106.3687 | 1170.4844 |  | Grand Total |  | Grand Total | 15097987.6021 | 11338551.2183 | 11 | [32 empty] | 1 | 28 | [25 empty] | 1 | 28
Grand Total | 238587.7795 |  | 238588.6573 | 17737.3356 | 0.074343 | [5 empty] | 12 | [32 empty] | 1 | 29 | [25 empty] | 1 | 29
|  |  | 0.1522 | [7 empty] | Grand Total | [32 empty] | 1 | 30 | [25 empty] | 1 | 30
[44 empty] | 1 | 31 | [25 empty] | 1 | 31
[44 empty] | 2 | 1 | [25 empty] | 2 | 1
[44 empty] | 2 | 2 | [25 empty] | 2 | 2
[44 empty] | 2 | 3 | [25 empty] | 2 | 3
[44 empty] | 2 | 4 | [25 empty] | 2 | 4
[44 empty] | 2 | 5 | [25 empty] | 2 | 5
[44 empty] | 2 | 6 | [25 empty] | 2 | 6
[44 empty] | 2 | 7 | [25 empty] | 2 | 7
[44 empty] | 2 | 8 | [25 empty] | 2 | 8
[44 empty] | 2 | 9 | [25 empty] | 2 | 9
[44 empty] | 2 | 10 | [25 empty] | 2 | 10
[44 empty] | 2 | 11 | [25 empty] | 2 | 11
[44 empty] | 2 | 12 | [25 empty] | 2 | 12
[44 empty] | 2 | 13 | [25 empty] | 2 | 13
[44 empty] | 2 | 14 | [25 empty] | 2 | 14
[44 empty] | 2 | 15 | [25 empty] | 2 | 15
[44 empty] | 2 | 16 | [25 empty] | 2 | 16
[44 empty] | 2 | 17 | [25 empty] | 2 | 17
[44 empty] | 2 | 18 | [25 empty] | 2 | 18
[44 empty] | 2 | 19 | [25 empty] | 2 | 19
[44 empty] | 2 | 20 | [25 empty] | 2 | 20
[44 empty] | 2 | 21 | [25 empty] | 2 | 21
[44 empty] | 2 | 22 | [25 empty] | 2 | 22
[44 empty] | 2 | 23 | [25 empty] | 2 | 23
[44 empty] | 2 | 24 | [25 empty] | 2 | 24
[44 empty] | 2 | 25 | [25 empty] | 2 | 25
[44 empty] | 2 | 26 | [25 empty] | 2 | 26
[44 empty] | 2 | 27 | [25 empty] | 2 | 27
[44 empty] | 2 | 28 | [25 empty] | 2 | 28
[44 empty] | 3 | 1 | [25 empty] | 3 | 1
[44 empty] | 3 | 2 | [25 empty] | 3 | 2
[44 empty] | 3 | 3 | [25 empty] | 3 | 3
[44 empty] | 3 | 4 | [25 empty] | 3 | 4
[44 empty] | 3 | 5 | [25 empty] | 3 | 5
[44 empty] | 3 | 6 | [25 empty] | 3 | 6
[44 empty] | 3 | 7 | [25 empty] | 3 | 7
[44 empty] | 3 | 8 | [25 empty] | 3 | 8
[44 empty] | 3 | 9 | [25 empty] | 3 | 9
[44 empty] | 3 | 10 | [25 empty] | 3 | 10
[44 empty] | 3 | 11 | [25 empty] | 3 | 11
[44 empty] | 3 | 12 | [25 empty] | 3 | 12
[44 empty] | 3 | 13 | [25 empty] | 3 | 13
[44 empty] | 3 | 14 | [25 empty] | 3 | 14
[44 empty] | 3 | 15 | [25 empty] | 3 | 15
[44 empty] | 3 | 16 | [25 empty] | 3 | 16
[44 empty] | 3 | 17 | [25 empty] | 3 | 17
[44 empty] | 3 | 18 | [25 empty] | 3 | 18
[44 empty] | 3 | 19 | [25 empty] | 3 | 19
[44 empty] | 3 | 20 | [25 empty] | 3 | 20
[44 empty] | 3 | 21 | [25 empty] | 3 | 21
[44 empty] | 3 | 22 | [25 empty] | 3 | 22
[44 empty] | 3 | 23 | [25 empty] | 3 | 23
[44 empty] | 3 | 24 | [25 empty] | 3 | 24
[44 empty] | 3 | 25 | [25 empty] | 3 | 25
[44 empty] | 3 | 26 | [25 empty] | 3 | 26
[44 empty] | 3 | 27 | [25 empty] | 3 | 27
[44 empty] | 3 | 28 | [25 empty] | 3 | 28
[44 empty] | 3 | 29 | [25 empty] | 3 | 29
[44 empty] | 3 | 30 | [25 empty] | 3 | 30
[44 empty] | 3 | 31 | [25 empty] | 3 | 31
[44 empty] | 4 | 1 | [25 empty] | 4 | 1
[44 empty] | 4 | 2 | [25 empty] | 4 | 2
[44 empty] | 4 | 3 | [25 empty] | 4 | 3
[44 empty] | 4 | 4 | [25 empty] | 4 | 4
[44 empty] | 4 | 5 | [25 empty] | 4 | 5
[44 empty] | 4 | 6 | [25 empty] | 4 | 6
[44 empty] | 4 | 7 | [25 empty] | 4 | 7
[44 empty] | 4 | 8 | [25 empty] | 4 | 8
[44 empty] | 4 | 9 | [25 empty] | 4 | 9
[44 empty] | 4 | 10 | [25 empty] | 4 | 10
[44 empty] | 4 | 11 | [25 empty] | 4 | 11
[44 empty] | 4 | 12 | [25 empty] | 4 | 12
[44 empty] | 4 | 13 | [25 empty] | 4 | 13
[44 empty] | 4 | 14 | [25 empty] | 4 | 14
[44 empty] | 4 | 15 | [25 empty] | 4 | 15
[44 empty] | 4 | 16 | [25 empty] | 4 | 16
[44 empty] | 4 | 17 | [25 empty] | 4 | 17
[44 empty] | 4 | 18 | [25 empty] | 4 | 18
[44 empty] | 4 | 19 | [25 empty] | 4 | 19
[44 empty] | 4 | 20 | [25 empty] | 4 | 20
[44 empty] | 4 | 21 | [25 empty] | 4 | 21
[44 empty] | 4 | 22 | [25 empty] | 4 | 22
[44 empty] | 4 | 23 | [25 empty] | 4 | 23
[44 empty] | 4 | 24 | [25 empty] | 4 | 24
[44 empty] | 4 | 25 | [25 empty] | 4 | 25
[44 empty] | 4 | 26 | [25 empty] | 4 | 26
[44 empty] | 4 | 27 | [25 empty] | 4 | 27
[44 empty] | 4 | 28 | [25 empty] | 4 | 28
[44 empty] | 4 | 29 | [25 empty] | 4 | 29
[44 empty] | 4 | 30 | [25 empty] | 4 | 30
[44 empty] | 5 | 1 | [25 empty] | 5 | 1
[44 empty] | 5 | 2 | [25 empty] | 5 | 2
[44 empty] | 5 | 3 | [25 empty] | 5 | 3
[44 empty] | 5 | 4 | [25 empty] | 5 | 4
[44 empty] | 5 | 5 | [25 empty] | 5 | 5
[44 empty] | 5 | 6 | [25 empty] | 5 | 6
[44 empty] | 5 | 7 | [25 empty] | 5 | 7
[44 empty] | 5 | 8 | [25 empty] | 5 | 8
[44 empty] | 5 | 9 | [25 empty] | 5 | 9
[44 empty] | 5 | 10 | [25 empty] | 5 | 10
[44 empty] | 5 | 11 | [25 empty] | 5 | 11
[44 empty] | 5 | 12 | [25 empty] | 5 | 12
[44 empty] | 5 | 13 | [25 empty] | 5 | 13
[44 empty] | 5 | 14 | [25 empty] | 5 | 14
[44 empty] | 5 | 15 | [25 empty] | 5 | 15
[44 empty] | 5 | 16 | [25 empty] | 5 | 16
[44 empty] | 5 | 17 | [25 empty] | 5 | 17
[44 empty] | 5 | 18 | [25 empty] | 5 | 18
[44 empty] | 5 | 19 | [25 empty] | 5 | 19
[44 empty] | 5 | 20 | [25 empty] | 5 | 20
[44 empty] | 5 | 21 | [25 empty] | 5 | 21
[44 empty] | 5 | 22 | [25 empty] | 5 | 22
[44 empty] | 5 | 23 | [25 empty] | 5 | 23
[44 empty] | 5 | 24 | [25 empty] | 5 | 24
[44 empty] | 5 | 25 | [25 empty] | 5 | 25
[44 empty] | 5 | 26 | [25 empty] | 5 | 26
[44 empty] | 5 | 27 | [25 empty] | 5 | 27
[44 empty] | 5 | 28 | [25 empty] | 5 | 28
[44 empty] | 5 | 29 | [25 empty] | 5 | 29
[44 empty] | 5 | 30 | [25 empty] | 5 | 30
[44 empty] | 5 | 31 | [25 empty] | 5 | 31
[44 empty] | 6 | 1 | [25 empty] | 6 | 1
[44 empty] | 6 | 2 | [25 empty] | 6 | 2
[44 empty] | 6 | 3 | [25 empty] | 6 | 3
[44 empty] | 6 | 4 | [25 empty] | 6 | 4
[44 empty] | 6 | 5 | [25 empty] | 6 | 5
[44 empty] | 6 | 6 | [25 empty] | 6 | 6
[44 empty] | 6 | 7 | [25 empty] | 6 | 7
[44 empty] | 6 | 8 | [25 empty] | 6 | 8
[44 empty] | 6 | 9 | [25 empty] | 6 | 9
[44 empty] | 6 | 10 | [25 empty] | 6 | 10
[44 empty] | 6 | 11 | [25 empty] | 6 | 11
[44 empty] | 6 | 12 | [25 empty] | 6 | 12
[44 empty] | 6 | 13 | [25 empty] | 6 | 13
[44 empty] | 6 | 14 | [25 empty] | 6 | 14
[44 empty] | 6 | 15 | [25 empty] | 6 | 15
[44 empty] | 6 | 16 | [25 empty] | 6 | 16
[44 empty] | 6 | 17 | [25 empty] | 6 | 17
[44 empty] | 6 | 18 | [25 empty] | 6 | 18
[44 empty] | 6 | 19 | [25 empty] | 6 | 19
[44 empty] | 6 | 20 | [25 empty] | 6 | 20
[44 empty] | 6 | 21 | [25 empty] | 6 | 21
[44 empty] | 6 | 22 | [25 empty] | 6 | 22
[44 empty] | 6 | 23 | [25 empty] | 6 | 23
[44 empty] | 6 | 24 | [25 empty] | 6 | 24
[44 empty] | 6 | 25 | [25 empty] | 6 | 25
[44 empty] | 6 | 26 | [25 empty] | 6 | 26
[44 empty] | 6 | 27 | [25 empty] | 6 | 27
[44 empty] | 6 | 28 | [25 empty] | 6 | 28
[44 empty] | 6 | 29 | [25 empty] | 6 | 29
[44 empty] | 6 | 30 | [25 empty] | 6 | 30
[44 empty] | 7 | 1 | [25 empty] | 7 | 1
[44 empty] | 7 | 2 | [25 empty] | 7 | 2
[44 empty] | 7 | 3 | [25 empty] | 7 | 3
[44 empty] | 7 | 4 | [25 empty] | 7 | 4
[44 empty] | 7 | 5 | [25 empty] | 7 | 5
[44 empty] | 7 | 6 | [25 empty] | 7 | 6
[44 empty] | 7 | 7 | [25 empty] | 7 | 7
[44 empty] | 7 | 8 | [25 empty] | 7 | 8
[44 empty] | 7 | 9 | [25 empty] | 7 | 9
[44 empty] | 7 | 10 | [25 empty] | 7 | 10
[44 empty] | 7 | 11 | [25 empty] | 7 | 11
[44 empty] | 7 | 12 | [25 empty] | 7 | 12
[44 empty] | 7 | 13 | [25 empty] | 7 | 13
[44 empty] | 7 | 14 | [25 empty] | 7 | 14
[44 empty] | 7 | 15 | [25 empty] | 7 | 15
[44 empty] | 7 | 16 | [25 empty] | 7 | 16
[44 empty] | 7 | 17 | [25 empty] | 7 | 17
[44 empty] | 7 | 18 | [25 empty] | 7 | 18
[44 empty] | 7 | 19 | [25 empty] | 7 | 19
[44 empty] | 7 | 20 | [25 empty] | 7 | 20
[44 empty] | 7 | 21 | [25 empty] | 7 | 21
[44 empty] | 7 | 22 | [25 empty] | 7 | 22
[44 empty] | 7 | 23 | [25 empty] | 7 | 23
[44 empty] | 7 | 24 | [25 empty] | 7 | 24
[44 empty] | 7 | 25 | [25 empty] | 7 | 25
[44 empty] | 7 | 26 | [25 empty] | 7 | 26
[44 empty] | 7 | 27 | [25 empty] | 7 | 27
[44 empty] | 7 | 28 | [25 empty] | 7 | 28
[44 empty] | 7 | 29 | [25 empty] | 7 | 29
[44 empty] | 7 | 30 | [25 empty] | 7 | 30
[44 empty] | 7 | 31 | [25 empty] | 7 | 31
[44 empty] | 8 | 1 | [25 empty] | 8 | 1
[44 empty] | 8 | 2 | [25 empty] | 8 | 2
[44 empty] | 8 | 3 | [25 empty] | 8 | 3
[44 empty] | 8 | 4 | [25 empty] | 8 | 4
[44 empty] | 8 | 5 | [25 empty] | 8 | 5
[44 empty] | 8 | 6 | [25 empty] | 8 | 6
[44 empty] | 8 | 7 | [25 empty] | 8 | 7
[44 empty] | 8 | 8 | [25 empty] | 8 | 8
[44 empty] | 8 | 9 | [25 empty] | 8 | 9
[44 empty] | 8 | 10 | [25 empty] | 8 | 10
[44 empty] | 8 | 11 | [25 empty] | 8 | 11
[44 empty] | 8 | 12 | [25 empty] | 8 | 12
[44 empty] | 8 | 13 | [25 empty] | 8 | 13
[44 empty] | 8 | 14 | [25 empty] | 8 | 14
[44 empty] | 8 | 15 | [25 empty] | 8 | 15
[44 empty] | 8 | 16 | [25 empty] | 8 | 16
[44 empty] | 8 | 17 | [25 empty] | 8 | 17
[44 empty] | 8 | 18 | [25 empty] | 8 | 18
[44 empty] | 8 | 19 | [25 empty] | 8 | 19
[44 empty] | 8 | 20 | [25 empty] | 8 | 20
[44 empty] | 8 | 21 | [25 empty] | 8 | 21
[44 empty] | 8 | 22 | [25 empty] | 8 | 22
[44 empty] | 8 | 23 | [25 empty] | 8 | 23
[44 empty] | 8 | 24 | [25 empty] | 8 | 24
[44 empty] | 8 | 25 | [25 empty] | 8 | 25
[44 empty] | 8 | 26 | [25 empty] | 8 | 26
[44 empty] | 8 | 27 | [25 empty] | 8 | 27
[44 empty] | 8 | 28 | [25 empty] | 8 | 28
[44 empty] | 8 | 29 | [25 empty] | 8 | 29
[44 empty] | 8 | 30 | [25 empty] | 8 | 30
[44 empty] | 8 | 31 | [25 empty] | 8 | 31
[44 empty] | 9 | 1 | [25 empty] | 9 | 1
[44 empty] | 9 | 2 | [25 empty] | 9 | 2
[44 empty] | 9 | 3 | [25 empty] | 9 | 3
[44 empty] | 9 | 4 | [25 empty] | 9 | 4
[44 empty] | 9 | 5 | [25 empty] | 9 | 5
[44 empty] | 9 | 6 | [25 empty] | 9 | 6
[44 empty] | 9 | 7 | [25 empty] | 9 | 7
[44 empty] | 9 | 8 | [25 empty] | 9 | 8
[44 empty] | 9 | 9 | [25 empty] | 9 | 9
[44 empty] | 9 | 10 | [25 empty] | 9 | 10
[44 empty] | 9 | 11 | [25 empty] | 9 | 11
[44 empty] | 9 | 12 | [25 empty] | 9 | 12
[44 empty] | 9 | 13 | [25 empty] | 9 | 13
[44 empty] | 9 | 14 | [25 empty] | 9 | 14
[44 empty] | 9 | 15 | [25 empty] | 9 | 15
[44 empty] | 9 | 16 | [25 empty] | 9 | 16
[44 empty] | 9 | 17 | [25 empty] | 9 | 17
[44 empty] | 9 | 18 | [25 empty] | 9 | 18
[44 empty] | 9 | 19 | [25 empty] | 9 | 19
[44 empty] | 9 | 20 | [25 empty] | 9 | 20
[44 empty] | 9 | 21 | [25 empty] | 9 | 21
[44 empty] | 9 | 22 | [25 empty] | 9 | 22
[44 empty] | 9 | 23 | [25 empty] | 9 | 23
[44 empty] | 9 | 24 | [25 empty] | 9 | 24
[44 empty] | 9 | 25 | [25 empty] | 9 | 25
[44 empty] | 9 | 26 | [25 empty] | 9 | 26
[44 empty] | 9 | 27 | [25 empty] | 9 | 27
[44 empty] | 9 | 28 | [25 empty] | 9 | 28
[44 empty] | 9 | 29 | [25 empty] | 9 | 29
[44 empty] | 9 | 30 | [25 empty] | 9 | 30
[44 empty] | 10 | 1 | [25 empty] | 10 | 1
[44 empty] | 10 | 2 | [25 empty] | 10 | 2
[44 empty] | 10 | 3 | [25 empty] | 10 | 3
[44 empty] | 10 | 4 | [25 empty] | 10 | 4
[44 empty] | 10 | 5 | [25 empty] | 10 | 5
[44 empty] | 10 | 6 | [25 empty] | 10 | 6
[44 empty] | 10 | 7 | [25 empty] | 10 | 7
[44 empty] | 10 | 8 | [25 empty] | 10 | 8
[44 empty] | 10 | 9 | [25 empty] | 10 | 9
[44 empty] | 10 | 10 | [25 empty] | 10 | 10
[44 empty] | 10 | 11 | [25 empty] | 10 | 11
[44 empty] | 10 | 12 | [25 empty] | 10 | 12
[44 empty] | 10 | 13 | [25 empty] | 10 | 13
[44 empty] | 10 | 14 | [25 empty] | 10 | 14
[44 empty] | 10 | 15 | [25 empty] | 10 | 15
[44 empty] | 10 | 16 | [25 empty] | 10 | 16
[44 empty] | 10 | 17 | [25 empty] | 10 | 17
[44 empty] | 10 | 18 | [25 empty] | 10 | 18
[44 empty] | 10 | 19 | [25 empty] | 10 | 19
[44 empty] | 10 | 20 | [25 empty] | 10 | 20
[44 empty] | 10 | 21 | [25 empty] | 10 | 21
[44 empty] | 10 | 22 | [25 empty] | 10 | 22
[44 empty] | 10 | 23 | [25 empty] | 10 | 23
[44 empty] | 10 | 24 | [25 empty] | 10 | 24
[44 empty] | 10 | 25 | [25 empty] | 10 | 25
[44 empty] | 10 | 26 | [25 empty] | 10 | 26
[44 empty] | 10 | 27 | [25 empty] | 10 | 27
[44 empty] | 10 | 28 | [25 empty] | 10 | 28
[44 empty] | 10 | 29 | [25 empty] | 10 | 29
[44 empty] | 10 | 30 | [25 empty] | 10 | 30
[44 empty] | 10 | 31 | [25 empty] | 10 | 31
[44 empty] | 11 | 1 | [25 empty] | 11 | 1
[44 empty] | 11 | 2 | [25 empty] | 11 | 2
[44 empty] | 11 | 3 | [25 empty] | 11 | 3
[44 empty] | 11 | 4 | [25 empty] | 11 | 4
[44 empty] | 11 | 5 | [25 empty] | 11 | 5
[44 empty] | 11 | 6 | [25 empty] | 11 | 6
[44 empty] | 11 | 7 | [25 empty] | 11 | 7
[44 empty] | 11 | 8 | [25 empty] | 11 | 8
[44 empty] | 11 | 9 | [25 empty] | 11 | 9
[44 empty] | 11 | 10 | [25 empty] | 11 | 10
[44 empty] | 11 | 11 | [25 empty] | 11 | 11
[44 empty] | 11 | 12 | [25 empty] | 11 | 12
[44 empty] | 11 | 13 | [25 empty] | 11 | 13
[44 empty] | 11 | 14 | [25 empty] | 11 | 14
[44 empty] | 11 | 15 | [25 empty] | 11 | 15
[44 empty] | 11 | 16 | [25 empty] | 11 | 16
[44 empty] | 11 | 17 | [25 empty] | 11 | 17
[44 empty] | 11 | 18 | [25 empty] | 11 | 18
[44 empty] | 11 | 19 | [25 empty] | 11 | 19
[44 empty] | 11 | 20 | [25 empty] | 11 | 20
[44 empty] | 11 | 21 | [25 empty] | 11 | 21
[44 empty] | 11 | 22 | [25 empty] | 11 | 22
[44 empty] | 11 | 23 | [25 empty] | 11 | 23
[44 empty] | 11 | 24 | [25 empty] | 11 | 24
[44 empty] | 11 | 25 | [25 empty] | 11 | 25
[44 empty] | 11 | 26 | [25 empty] | 11 | 26
[44 empty] | 11 | 27 | [25 empty] | 11 | 27
[44 empty] | 11 | 28 | [25 empty] | 11 | 28
[44 empty] | 11 | 29 | [25 empty] | 11 | 29
[44 empty] | 11 | 30 | [25 empty] | 11 | 30
[44 empty] | 12 | 1 | [25 empty] | 12 | 1
[44 empty] | 12 | 2 | [25 empty] | 12 | 2
[44 empty] | 12 | 3 | [25 empty] | 12 | 3
[44 empty] | 12 | 4 | [25 empty] | 12 | 4
[44 empty] | 12 | 5 | [25 empty] | 12 | 5
[44 empty] | 12 | 6 | [25 empty] | 12 | 6
[44 empty] | 12 | 7 | [25 empty] | 12 | 7
[44 empty] | 12 | 8 | [25 empty] | 12 | 8
[44 empty] | 12 | 9 | [25 empty] | 12 | 9
[44 empty] | 12 | 10 | [25 empty] | 12 | 10
[44 empty] | 12 | 11 | [25 empty] | 12 | 11
[44 empty] | 12 | 12 | [25 empty] | 12 | 12
[44 empty] | 12 | 13 | [25 empty] | 12 | 13
[44 empty] | 12 | 14 | [25 empty] | 12 | 14
[44 empty] | 12 | 15 | [25 empty] | 12 | 15
[44 empty] | 12 | 16 | [25 empty] | 12 | 16
[44 empty] | 12 | 17 | [25 empty] | 12 | 17
[44 empty] | 12 | 18 | [25 empty] | 12 | 18
[44 empty] | 12 | 19 | [25 empty] | 12 | 19
[44 empty] | 12 | 20 | [25 empty] | 12 | 20
[44 empty] | 12 | 21 | [25 empty] | 12 | 21
[44 empty] | 12 | 22 | [25 empty] | 12 | 22
[44 empty] | 12 | 23 | [25 empty] | 12 | 23
[44 empty] | 12 | 24 | [25 empty] | 12 | 24
[44 empty] | 12 | 25 | [25 empty] | 12 | 25
[44 empty] | 12 | 26 | [25 empty] | 12 | 26
[44 empty] | 12 | 27 | [25 empty] | 12 | 27
[44 empty] | 12 | 28 | [25 empty] | 12 | 28
[44 empty] | 12 | 29 | [25 empty] | 12 | 29
[44 empty] | 12 | 30 | [25 empty] | 12 | 30
[44 empty] | 12 | 31 | [25 empty] | 12 | 31
[44 empty] | Grand Total | [26 empty] | Grand Total

## Outputs (hidden)
|  |  | Heating |  |  | Cooling
|  |  | Design Day | 2007-01-26 08:00 |  | Design Day | 2007-07-29 15:00
|  |  | Design Day of Year | 26 | of 365 | Design Day of Year | 210 | of 365
|  |  | Design Day Heating Load | 8808.8475 | MBH | Design Day Heating Load | 11644.4694 | MBH
Peak Bore Field Heating Load | 16189.8436 | MBH | Design Day Min Heating Load | 1928.6796 | MBH | Design Day Min Heating Load | 11764.4312 | MBH
Peak Bore Field Cooling Load | 23709.8354 | MBH | Diversity Factor | 21.89% |  | Diversity Factor | 101%
Total Bore Field Heating Energy |  | MMbtu | Average Geo-Loop Heating Season Load | 2452.0782 | MBH
Total Bore Field Cooling Energy |  | MMbtu | Avg Bore Field Jan Load | 4908.3144 | MBH
Total Bore Field Annual Energy |  | MMbtu | Avg Bore Field Feb Load | 4025.0614 | MBH
|  |  | Avg Bore Field Mar Load | 2710.5243 | MBH
|  |  | Avg Bore Field Nov Load | 2134.9314 | MBH
Loop Heat Pump Annual Electric Consumption | 0 | kWh | Avg Bore Field Dec Load | 3677.1004 | MBH
Loop Pumps Annual Electric Consumption | 167112.073 | kWh
Bore Field Pumps Annual Electric Consumption | 71475.7065 | kWh | Total Buildling Load (Heating ) | 17006.0235 | MMBTU
Total Annual Electric Consumption | 238587.7795 | kWh | Total Buildling Load (Cooling) | 9358.2519 | MMBTU
Total Annual Electric Consumption | 814.0615 | MMBtu | Total Heat Moved | 26364.2754 | MMBTU
Total Annual Electric Cost | 36313.918 |  | Delievery Rate | 1.3774 | MMBTU
Note on C18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Refresh Pivot Tables to update

## GSHP Performance Data (hidden)
Job Name: Troy District Energy Plant Unit Tag: RTWD-1 Prepared By: Quantity: 1
Partload Information
Heat Hold Leaving at 1% interval
Load % | Htg cap. MBh | LWT Evap F | EWT Evap F | Flow Evap gpm | WPD Evap ft H2O | EWT Cond F | LWT Cond F | Flow Cond gpm | WPD Cond ft H2O | Power kW | Eff. COP (kW/kW) | EWT Evap F |  |  | EWT Cond F |  |  | Eff. COP (kW/kW)
100% | 905.86 | 30 | 37.74 | 200 | 24.9 | 71.01 | 80 | 200 | 15.3 | 48.61 | 5.458 | y = a*x^2+b*x+c |  |  | y = a*x^2+b*x+c |  |  | y = a*x^2+b*x+c
99% | 896.8 | 30 | 37.67 | 200 | 24.9 | 71.1 | 80 | 200 | 15.3 | 48.02 | 5.47 | a | b | c | a | b | c | a | b | c
98% | 887.7 | 30 | 37.59 | 200 | 24.9 | 71.19 | 80 | 200 | 15.3 | 47.43 | 5.482 | 0.23731 | 7.6215 | 29.9269 | 0.18222 | -9.196 | 80.0247 | -1.4493 | 3.1546 | 3.8346
97% | 878.7 | 30 | 37.52 | 200 | 24.9 | 71.28 | 80 | 200 | 15.3 | 46.84 | 5.495
96% | 869.6 | 30 | 37.44 | 200 | 24.9 | 71.37 | 80 | 200 | 15.3 | 46.25 | 5.508
95% | 860.6 | 30 | 37.37 | 200 | 24.9 | 71.45 | 80 | 200 | 15.3 | 45.66 | 5.521
94% | 851.5 | 30 | 37.3 | 200 | 24.9 | 71.54 | 80 | 200 | 15.3 | 45.07 | 5.534
93% | 842.4 | 30 | 37.22 | 200 | 24.9 | 71.63 | 80 | 200 | 15.3 | 44.47 | 5.548
92% | 833.4 | 30 | 37.15 | 200 | 24.9 | 71.72 | 80 | 200 | 15.3 | 43.89 | 5.562
91% | 824.3 | 30 | 37.08 | 200 | 24.9 | 71.81 | 80 | 200 | 15.3 | 43.29 | 5.577
90% | 815.3 | 30 | 37 | 200 | 24.9 | 71.9 | 80 | 200 | 15.3 | 42.73 | 5.588
89% | 806.2 | 30 | 36.92 | 200 | 24.9 | 71.99 | 80 | 200 | 15.3 | 42.28 | 5.585
88% | 797.2 | 30 | 36.84 | 200 | 24.9 | 72.08 | 80 | 200 | 15.3 | 41.87 | 5.576
87% | 788.1 | 30 | 36.76 | 200 | 24.9 | 72.17 | 80 | 200 | 15.3 | 41.46 | 5.568
86% | 779 | 30 | 36.68 | 200 | 24.9 | 72.25 | 80 | 200 | 15.3 | 41.04 | 5.559
85% | 770 | 30 | 36.6 | 200 | 24.9 | 72.34 | 80 | 200 | 15.3 | 40.63 | 5.55
84% | 760.9 | 30 | 36.52 | 200 | 24.9 | 72.43 | 80 | 200 | 15.3 | 40.22 | 5.542
83% | 751.9 | 30 | 36.44 | 200 | 24.8 | 72.52 | 80 | 200 | 15.3 | 39.8 | 5.533
82% | 742.8 | 30 | 36.36 | 200 | 24.8 | 72.61 | 80 | 200 | 15.3 | 39.39 | 5.524
81% | 733.7 | 30 | 36.28 | 200 | 24.8 | 72.7 | 80 | 200 | 15.3 | 38.97 | 5.515
80% | 724.7 | 30 | 36.2 | 200 | 24.8 | 72.79 | 80 | 200 | 15.3 | 38.56 | 5.505
79% | 715.6 | 30 | 36.12 | 200 | 24.8 | 72.88 | 80 | 200 | 15.3 | 38.15 | 5.495
78% | 706.6 | 30 | 36.04 | 200 | 24.8 | 72.96 | 80 | 200 | 15.3 | 37.79 | 5.477
77% | 697.5 | 30 | 35.96 | 200 | 24.8 | 73.05 | 80 | 200 | 15.3 | 37.42 | 5.459
76% | 688.5 | 30 | 35.88 | 200 | 24.8 | 73.14 | 80 | 200 | 15.3 | 37.07 | 5.44
75% | 679.4 | 30 | 35.8 | 200 | 24.8 | 73.23 | 80 | 200 | 15.3 | 36.71 | 5.421
74% | 670.3 | 30 | 35.71 | 200 | 24.8 | 73.32 | 80 | 200 | 15.3 | 36.35 | 5.402
73% | 661.3 | 30 | 35.63 | 200 | 24.8 | 73.41 | 80 | 200 | 15.3 | 35.99 | 5.382
72% | 652.2 | 30 | 35.55 | 200 | 24.8 | 73.5 | 80 | 200 | 15.3 | 35.62 | 5.363
71% | 643.2 | 30 | 35.47 | 200 | 24.8 | 73.58 | 80 | 200 | 15.3 | 35.3 | 5.337
70% | 634.1 | 30 | 35.39 | 200 | 24.8 | 73.67 | 80 | 200 | 15.3 | 34.88 | 5.325
69% | 625 | 30 | 35.31 | 200 | 24.8 | 73.76 | 80 | 200 | 15.3 | 34.47 | 5.31
68% | 616 | 30 | 35.23 | 200 | 24.8 | 73.85 | 80 | 200 | 15.3 | 34.11 | 5.289
67% | 606.9 | 30 | 35.14 | 200 | 24.8 | 73.94 | 80 | 200 | 15.3 | 33.75 | 5.267
66% | 597.9 | 30 | 35.06 | 200 | 24.7 | 74.03 | 80 | 200 | 15.3 | 33.39 | 5.246
65% | 588.8 | 30 | 34.98 | 200 | 24.7 | 74.12 | 80 | 200 | 15.2 | 33.02 | 5.223
64% | 579.7 | 30 | 34.9 | 200 | 24.7 | 74.21 | 80 | 200 | 15.2 | 32.62 | 5.205
63% | 570.7 | 30 | 34.82 | 200 | 24.7 | 74.3 | 80 | 200 | 15.2 | 32.25 | 5.182
62% | 561.6 | 30 | 34.74 | 200 | 24.7 | 74.38 | 80 | 200 | 15.2 | 31.87 | 5.161
61% | 552.6 | 30 | 34.66 | 200 | 24.7 | 74.47 | 80 | 200 | 15.2 | 31.49 | 5.14
60% | 543.5 | 30 | 34.58 | 200 | 24.7 | 74.56 | 80 | 200 | 15.2 | 31.11 | 5.118
59% | 534.5 | 30 | 34.43 | 200 | 24.7 | 74.65 | 80 | 200 | 15.2 | 32.48 | 4.82
58% | 525.4 | 30 | 34.35 | 200 | 24.7 | 74.74 | 80 | 200 | 15.2 | 32.06 | 4.8
57% | 516.3 | 30 | 34.27 | 200 | 24.7 | 74.83 | 80 | 200 | 15.2 | 31.68 | 4.774
56% | 507.3 | 30 | 34.19 | 200 | 24.7 | 74.91 | 80 | 200 | 15.2 | 31.31 | 4.745
55% | 498.2 | 30 | 34.11 | 200 | 24.7 | 75 | 80 | 200 | 15.2 | 30.94 | 4.716
54% | 489.2 | 30 | 34.03 | 200 | 24.7 | 75.09 | 80 | 200 | 15.2 | 30.58 | 4.686
53% | 480.1 | 30 | 33.94 | 200 | 24.7 | 75.18 | 80 | 200 | 15.2 | 30.2 | 4.656
52% | 471 | 30 | 33.86 | 200 | 24.7 | 75.27 | 80 | 200 | 15.2 | 29.81 | 4.627
51% | 462 | 30 | 33.78 | 200 | 24.6 | 75.36 | 80 | 200 | 15.2 | 29.43 | 4.598
50% | 452.9 | 30 | 33.7 | 200 | 24.6 | 75.45 | 80 | 200 | 15.2 | 29.04 | 4.568
49% | 443.9 | 30 | 33.62 | 200 | 24.6 | 75.54 | 80 | 200 | 15.2 | 28.66 | 4.537
48% | 434.8 | 30 | 33.64 | 200 | 24.6 | 75.67 | 80 | 200 | 15.2 | 25.38 | 5.017
47% | 425.8 | 30 | 33.6 | 200 | 24.6 | 75.77 | 80 | 200 | 15.2 | 23.93 | 5.212
46% | 416.7 | 30 | 33.53 | 200 | 24.6 | 75.86 | 80 | 200 | 15.2 | 23.31 | 5.237
45% | 407.6 | 30 | 33.45 | 200 | 24.6 | 75.95 | 80 | 200 | 15.2 | 22.68 | 5.264
44% | 398.6 | 30 | 33.38 | 200 | 24.6 | 76.04 | 80 | 200 | 15.2 | 22.06 | 5.293
43% | 389.5 | 30 | 33.31 | 200 | 24.6 | 76.13 | 80 | 200 | 15.2 | 21.49 | 5.31
42% | 380.5 | 30 | 33.23 | 200 | 24.6 | 76.22 | 80 | 200 | 15.2 | 21.06 | 5.292
41% | 371.4 | 30 | 33.15 | 200 | 24.6 | 76.31 | 80 | 200 | 15.2 | 20.63 | 5.273
40% | 362.3 | 30 | 33.07 | 200 | 24.6 | 76.4 | 80 | 200 | 15.2 | 20.2 | 5.254
39% | 353.3 | 30 | 32.99 | 200 | 24.6 | 76.49 | 80 | 200 | 15.2 | 19.77 | 5.235
38% | 344.2 | 30 | 32.91 | 200 | 24.6 | 76.58 | 80 | 200 | 15.2 | 19.34 | 5.212
37% | 335.2 | 30 | 32.83 | 200 | 24.6 | 76.66 | 80 | 200 | 15.2 | 18.97 | 5.177
36% | 326.1 | 30 | 32.75 | 200 | 24.6 | 76.75 | 80 | 200 | 15.2 | 18.59 | 5.139
35% | 317.1 | 30 | 32.67 | 200 | 24.6 | 76.84 | 80 | 200 | 15.2 | 18.21 | 5.101
34% | 308 | 30 | 32.59 | 200 | 24.6 | 76.93 | 80 | 200 | 15.2 | 17.83 | 5.06
33% | 298.9 | 30 | 32.51 | 200 | 24.6 | 77.02 | 80 | 200 | 15.2 | 17.43 | 5.024
32% | 289.9 | 30 | 32.43 | 200 | 24.5 | 77.11 | 80 | 200 | 15.2 | 17.03 | 4.987
31% | 280.8 | 30 | 32.34 | 200 | 24.5 | 77.2 | 80 | 200 | 15.2 | 16.62 | 4.947
30% | 271.8 | 30 | 32.26 | 200 | 24.5 | 77.29 | 80 | 200 | 15.2 | 16.23 | 4.906
29% | 262.7 | 30 | 32.18 | 200 | 24.5 | 77.38 | 80 | 200 | 15.2 | 15.85 | 4.854
28% | 253.6 | 30 | 32.1 | 200 | 24.5 | 77.46 | 80 | 200 | 15.2 | 15.61 | 4.76
27% | 244.6 | 30 | 32.01 | 200 | 24.5 | 77.55 | 80 | 200 | 15.2 | 15.36 | 4.664
26% | 235.5 | 30 | 31.92 | 200 | 24.5 | 77.64 | 80 | 200 | 15.2 | 15.11 | 4.564
25% | 226.5 | 30 | 31.84 | 200 | 24.5 | 77.73 | 80 | 200 | 15.2 | 14.87 | 4.462
24% | 217.4 | 30 | 31.75 | 200 | 24.5 | 77.82 | 80 | 200 | 15.2 | 14.62 | 4.356
23% | 208.3 | 30 | 31.67 | 200 | 24.5 | 77.91 | 80 | 200 | 15.2 | 14.37 | 4.245
22% | 199.3 | 30 | 31.58 | 200 | 24.5 | 78 | 80 | 200 | 15.1 | 14.13 | 4.132
21% | 190.2 | 30 | 31.49 | 200 | 24.5 | 78.08 | 80 | 200 | 15.1 | 13.88 | 4.014
20% | 181.2 | 30 | 31.41 | 200 | 24.5 | 78.17 | 80 | 200 | 15.1 | 13.63 | 3.893
19% | 172.1 | 30 | 31.32 | 200 | 24.5 | 78.26 | 80 | 200 | 15.1 | 13.38 | 3.766

## ASHP Performance Data (hidden)
Cooling
LG ARUM312BTE5 |  | Indoor 80/67
OAT | Tc | Pi | EER | COP | A | B | C
45 | 312 | 10.84 | 28.7823 | 8.4331 | -0.0010846 | 0.064459 | 7.7969
50 | 312 | 11.06 | 28.2098 | 8.2654
55 | 312 | 11.3 | 27.6106 | 8.0898
60 | 312 | 11.73 | 26.5985 | 7.7933
65 | 312 | 11.97 | 26.0652 | 7.637
70 | 312 | 13 | 24 | 7.0319
75 | 312 | 13.94 | 22.3816 | 6.5578
80 | 312 | 15.96 | 19.5489 | 5.7278
85 | 312 | 17.02 | 18.3314 | 5.371
90 | 312 | 19.39 | 16.0908 | 4.7146
95 | 312 | 21.09 | 14.7937 | 4.3345
Heating
LG ARUM312BTE5 |  | Indoor 70F
OAT | Tc | Pi | EER | COP | A | B | C
-21.6 | 176.7 | 24.52 | 7.2064 | 2.1114 | 0.00034926 | 0.017442 | 2.494
-17.1 | 204.7 | 26.68 | 7.6724 | 2.248
-12.6 | 235.5 | 28.85 | 8.1629 | 2.3917 | A | B | C | D
-7 | 268.4 | 31.45 | 8.5342 | 2.5005 | 1.1781e-05 | -8.9096e-05 | 0.013602 | 2.5835
-4 | 288.1 | 33.01 | 8.7277 | 2.5572
0 | 312.5 | 34.93 | 8.9465 | 2.6213
5 | 339.4 | 37.34 | 9.0894 | 2.6632
10 | 351 | 38.33 | 9.1573 | 2.6831
15 | 351 | 37.87 | 9.2686 | 2.7157
20 | 351 | 35.71 | 9.8292 | 2.8799
25 | 351 | 33.59 | 10.4495 | 3.0617
30 | 351 | 31.47 | 11.1535 | 3.2679
35 | 351 | 29.36 | 11.955 | 3.5028
40 | 351 | 27.24 | 12.8855 | 3.7754
47 | 351 | 24.49 | 14.3324 | 4.1993

## Check from PFD (hidden)
Building Cooling-Summer | [5 empty] | Btu/hr | GPM | 0F | 0F | Btu/hr | GPM | 0F | 0F | Btu/hr
Btu/hr | GPM | 0F | 0F | Btu/hr |  | 11348700 | 1520.2 | 85 | 70 | 11401500 | 1469.7 | 84 | 68 | 11757600
596299 | 119.8 | 82.5 | 72.5 | 599000 | Cooling | 11348700 | 1520.2 | 85 | 70 | 11401500 | 1469.7 | 84 | 68 | 11757600
414360 | 83.3 | 82.5 | 72.5 | 416500 |  | 22697400 |  |  |  | 22803000 | 2939.4 |  |  | 23515200
1900915 | 382 | 82.5 | 72.5 | 1910000 | [5 empty] | 1900.25
1900915 | 382 | 82.5 | 72.5 | 1910000 | [11 empty] | COP
1900915 | 382 | 82.5 | 72.5 | 1910000 |  | 13780200 | 1381.8 | 80 | 60 | 13818000 | 2442.2 | 35 | 25 | 12211000 | 11714200 | 0.85007 | 1.1764
2901811 | 583.1 | 82.5 | 72.5 | 2915500 | Heating | 13780200 | 1381.8 | 80 | 60 | 13818000 | 2442.2 | 35 | 25 | 12211000 | 11714200
1370760 | 275.4 | 82.5 | 72.5 | 1377000 |  | 27560400 |  |  |  | 27636000 | 4884.4 |  |  | 24422000
746640 | 150 | 82.5 | 72.5 | 750000
150158 | 30.2 | 82.5 | 72.5 | 151000
699868 | 140.6 | 82.5 | 72.5 | 703000 |  | 22697400 | 2939.3 | 84 | 68 | 23514400
501200 | 100.7 | 82.5 | 72.5 | 503500 | [9 empty] | 3265450.237
644400 | 129.5 | 82.5 | 72.5 | 647500
1109810 | 223 | 82.5 | 72.5 | 1115000
3929680 | 789.6 | 82.5 | 72.5 | 3948000
3929680 | 789.6 | 82.5 | 72.5 | 3948000
22697411 | 4560.8 |  |  | 22804000
11348705.5 | 2280.4
Building Heating Winter
571460 | 57.3 | 60 | 80 | -573000
387100 | 39.8 | 60 | 80 | -398000
2613130 | 262 | 60 | 80 | -2620000
2613130 | 262 | 60 | 80 | -2620000
2613130 | 262 | 60 | 80 | -2620000
2780940 | 278.9 | 60 | 80 | -2789000
1313670 | 131.7 | 60 | 80 | -1317000
3018850 | 302.7 | 60 | 80 | -3027000
385680 | 38.7 | 60 | 80 | -387000
539950 | 54.1 | 60 | 80 | -541000
617990 | 62 | 60 | 80 | -620000
794560 | 79.7 | 60 | 80 | -797000
1368400 | 137.2 | 60 | 80 | -1372000
3966190 | 397.7 | 60 | 80 | -3977000
3968190 | 397.7 | 60 | 80 | -3977000
27552370 | 2763.5 |  |  | -27635000
13776185 | 1381.75

## Gas Supply (hidden)
Effective Month/Year | SC1 Residential | SC2 Residential & Commercial | SC2 Industrial | SC3 Large General Service | SC12 Distributed Generation | SC13 Distributed Generation
2020-12-01 | 0.20516 | 0.20292 | 0.20292 | 0.18119 | 0.16396 | 0.20816
2020-11-01 | 0.23244 | 0.22947 | 0.22947 | 0.21316 | 0.21169 | 0.23614
2020-10-01 | 0.15099 | 0.14802 | 0.14802 | 0.1317 | 0.13021 | 0.15469
2020-09-01 | $0.158705 | 0.1558 | 0.1558 | $0.139865 | 0.13842 | 0.16234
2020-08-01 | $0.182435 | 0.1795 | 0.1795 | $0.163385 | 0.16193 | 0.1861
2020-07-01 | $0.165525 | 0.1626 | 0.1626 | $0.146525 | 0.14506 | 0.16919
2020-06-01 | 0.18357 | 0.18058 | 0.18058 | 0.16407 | 0.16257 | 0.18732
2020-05-01 | 0.1994 | 0.19648 | 0.19648 | 0.18044 | 0.17897 | 0.20306
2020-04-01 | 0.17269 | 0.16981 | 0.16981 | 0.15408 | 0.15266 | 0.17625
2020-03-01 | 0.21285 | 0.20997 | 0.20997 | 0.19417 | 0.19274 | 0.21643
2020-02-01 | 0.27448 | 0.27164 | 0.27164 | 0.25594 | 0.25451 | 0.27805
2020-01-01 | 0.28589 | 0.28299 | 0.28299 | 0.26713 | 0.26567 | 0.2895
AVERAGE | 0.21305 |  | 0.19915 | 0.19354
From https://www.nationalgridus.com/upstate-ny-home/Rates/Supply-Costs.aspx (expand Gas)

## Gas Delivery (hidden)
SC 1 - Residential Service Delivery Service Rate
First 3 Therms or less … $20.35
Next 47 Therms … $0.57392 per therm
Over 50 Therms … $0.09262 per therm
From https://www.nationalgridus.com/Upstate-NY-Home/Rates/Service-Rates [expand Gas Service Rates, Natural Gas Pricing (SC-1)]
SC 2 - Small General Service Delivery Service Rate
First 3 Therms or less … $24.27
Next 277 Therms … $0.35651 per therm
Next 4,720 Therms … $0.20578 per therm
Over 5,000 Therms … $0.06590 per therm
SC 3 - Large General Service Delivery Service Rate
First 5,000 Therms or less … $781.27
Over 5,000 Therms … $0.11436 per therm
SC 12 - Non-Residential Distributed Generation Service Delivery Service Rate
Annual consumption < 250,000 Therms
First 3 Therms or less … $148.27
Over 3 Therms (Apr to Oct) … $0.04491 per therm
Over 3 Therms (Nov to Mar) … $0.05660 per therm
SC 12 - Non-Residential Distributed Generation Service Delivery Service Rate
Annual consumption 250,000 Therms to 1,000,000 Therms
First 3 Therms or less … $466.54
Over 3 Therms (Apr to Oct) … $0.04016 per therm
Over 3 Therms (Nov to Mar) … $0.05044 per therm
SC 12 - Non-Residential Distributed Generation Service Delivery Service Rate
Annual consumption > 1,000,000 Therms, but < 2,500,000
First 100 Therms or less … $1,401.27
Next 499,900 Therms (Apr to Oct) … $0.03711 per therm
Next 499,900 Therms (Nov to Mar) … $0.04702 per therm
Over 500,000 Therms (Apr to Oct) … $0.03183 per therm
Over 500,000 Therms (Nov to Mar) … $0.04031 per therm
SC 12 - Non-Residential Distributed Generation Service Delivery Service Rate
Annual consumption > 2,500,000 Therms
First 3 Therms or less … $1,401.27
Over 3 Therms (Apr to Oct) … $0.00740 per therm
Over 3 Therms (Nov to Mar) … $0.00944 per therm
Demand charge per therms of MPDQ … 0.76195
From https://www.nationalgridus.com/Upstate-NY-Home/Rates/Service-Rates [expand Gas Service Rates, Natural Gas Pricing (SC-1) and select Rates for Natural Gas Service]

## Elec Supply (hidden)
SC1, Zone F, 12 Month Trailing Weighted Average Prices Ending September 30, 2020
0.05071
SC2, Zone F, 12 Month Trailing Weighted Average Prices Ending September 30, 2020
0.04929
SC1C, Zone F, 12 Month Trailing Weighted Average Prices Ending September 30, 2020
Off Peak | 0.03414
On Peak | 0.0518
Sh Peak | 0.04294
SC1 VTOU, Zone F, 12 Month Trailing Weighted Average Prices Ending September 30, 2020
Off Peak | 0.00619
On Peak | 0.0183
Super Peak | 0.1559
From https://www.nationalgridus.com/Upstate-NY-Home/Rates/Rate-Statements, Electric, 12 Month Trailing Average of Supply Rates
Load | Service | Voltage | Pricing | Electricity | Delivery
Area | Class | Delivery Level | Date | Supply | Adjustment
Capital | SC3 | Primary | 2020-12-09 | 0.03016 | 0
Capital | SC3 | Primary | 2020-12-10 | 0.03058 | 0
Capital | SC3 | Primary | 2020-12-11 | 0.03084 | 0
Capital | SC3 | Primary | 2020-12-12 | 0.03104 | 0
Capital | SC3 | Primary | 2020-12-13 | 0.03122 | 0
Capital | SC3 | Primary | 2020-12-14 | 0.03147 | 0
Capital | SC3 | Secondary | 2020-12-09 | 0.03101 | 0
Capital | SC3 | Secondary | 2020-12-10 | 0.03149 | 0
Capital | SC3 | Secondary | 2020-12-11 | 0.03181 | 0
Capital | SC3 | Secondary | 2020-12-12 | 0.03207 | 0
Capital | SC3 | Secondary | 2020-12-13 | 0.0323 | 0
Capital | SC3 | Secondary | 2020-12-14 | 0.03254 | 0
Capital | SC3 | Subtransmission | 2020-12-09 | 0.02916 | 0
Capital | SC3 | Subtransmission | 2020-12-10 | 0.02967 | 0
Capital | SC3 | Subtransmission | 2020-12-11 | 0.03005 | 0
Capital | SC3 | Subtransmission | 2020-12-12 | 0.03038 | 0
Capital | SC3 | Subtransmission | 2020-12-13 | 0.03071 | 0
Capital | SC3 | Subtransmission | 2020-12-14 | 0.03094 | 0
Capital | SC3 | Transmission | 2020-12-09 | 0.02865 | 0
Capital | SC3 | Transmission | 2020-12-10 | 0.02904 | 0
Capital | SC3 | Transmission | 2020-12-11 | 0.02929 | 0
Capital | SC3 | Transmission | 2020-12-12 | 0.02949 | 0
Capital | SC3 | Transmission | 2020-12-13 | 0.02969 | 0
Capital | SC3 | Transmission | 2020-12-14 | 0.02991 | 0
These prices are the actual prices given current market and weather conditions experienced since September 1, 1998. These prices are not a forecast of where we believe prices will be tomorrow or any time in the future.
SC3 = Large General Service
From https://www.nationalgridus.com/Upstate-NY-Business/Supply-Costs/ , Electric Supply Charge (can alternatively select Hourly Supply Charge)

## Elec Delivery (hidden)
Rates Components for SC-1 (Standard Service)
Load Zones A & B | All Load Zones | Which is it? Applicable to only Zones A & B or all Zones?
Basic Service Charge (per month) | 17
Delivery Charge (per kWh) | 0.06287
From https://www.nationalgridus.com/Upstate-NY-Home/Rates/Service-Rates [expand Electric Service Rates, Standard Service (SC-1)]
Rates Components for SC1-VTOU (Residential Voluntary Time of Use)
All Load Zones
Basic Service Charge (per month) | 17
Incremental Customer Charge (per month) | 3.36
On Peak/Super Peak Delivery Charge (per kWh) | 0.08056
Off Peak Delivery Charge (per kWh) | 0.01085
Charge varies by time of use hours and load zone. Time of use hours for supply are: On peak 7am - 11pm; off peak 11pm - 7am; and super peak 2pm - 6pm in June, July and August, excluding weekends and holidays.
From https://www.nationalgridus.com/Upstate-NY-Home/Rates/Service-Rates , Standard Service and Residential Voluntary Time of Use
Small General (SC-2) This service is for commercial or industrial customers whose monthly measured demand is less than 100kW. Customers can be served under the non-demand or demand pricing schedules. A business that uses greater than 2,000 kWh in each month for four consecutive months would be classified as a demand customer.
Non-Demand Pricing | All Load Zones
Basic Service Charge (per month) | 21.02
Delivery Charge (per kWh) | 0.06911
Demand Pricing | All Load Zones
Basic Service Charge (per month) | 52.52
Delivery Charge (per kW) | 12.8
Delivery Charge for Demand (per kWh) | 0
Large General (SC-3) This service is for commercial or industrial customers whose monthly measured demand exceeds 100kW in each of the previous 12 consecutive months.
Secondary Customers (<2.2kV) | All Load Zones
Customer Charge | 487.5
Minimum kW (first 40 kW) | 452.8
Per kW Charge (over 40 kW) | 11.32
RKVA Charge | 0.85
Primary Customers (2.2-15 kV)
Customer Charge | 436.7
Minimum kW (first 40 kW) | 403.2
Per kW Charge (over 40 kW) | 10.08
RKVA Charge | 0.85
Subtransmission Customers (22-50 kV)
Customer Charge | 823
Minimum kW (first 40 kW) | 120.8
Per kW Charge (over 40 kW) | 3.02
RKVA Charge | 0.85
Transmission Customers (>60 kV)
Customer Charge | 823
Minimum kW (first 40 kW) | 120.8
Per kW Charge (over 40 kW) | 3.02
RKVA Charge | 0.85
Large General, TOU (SC-3A)
Secondary Customers (<2.2kV)
Customer Charges - Distribution Delivery | 2166.67
Demand Charges - Distribution Delivery (per kW) | 10.95
RkVA Charges | 1.02
Primary Customers (2.2-15 kV)
Customer Charges - Distribution Delivery | 2166.67
Demand Charges - Distribution Delivery (per kW) | 10.95
RkVA Charges | 1.02
Subtransmission Customers (22-50 kV)
Customer Charges - Distribution Delivery | 2604
Demand Charges - Distribution Delivery (per kW) | 3.74
RkVA Charges | 1.02
Transmission Customers (>60 kV)
Customer Charges - Distribution Delivery | 5273.5
Demand Charges - Distribution Delivery (per kW) | 3.38
RkVA Charges | 1.02
From https://www.nationalgridus.com/Upstate-NY-Business/Rates/Service-Rates , Small General, Large General, Large General, TOU