## Summary
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5%
[5 empty] | General Inflation Rate | 3%
[5 empty] | Discount Rate | 7%
[5 empty] | Ton Red Rate | -9.5%
| Summary Table - Total Summary |  |  |  | Finance Rate | 3% | 40 | yr
25-Yr NPV Sensitivity Analysis (In thousands)
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | Natural Gas Inflation Rate |  | Discount Rate
| Design and Planning | 7700000 |  | ~10% Construction | 7700000 | 7700000 | [31 empty] | 7900 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Central Plant Investment | 13300000 |  | Per CHA Estimate | 24500000 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | [6 empty] | 1% | -2900 | -3900 | -4500 | -5100 | -5900 | -6500 | -6700 | -7200
| Distribution Piping Investment | 28700000 |  | Per CHA Estimate $53M financing over 40yr | 52740000 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 |  |  | 2% | 1800 | 200 | -1000 | -2000 | -3200 | -4100 | -4600 | -5300
| Central Plant O&M | 3900000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A) | 262000 |  |  | 262000 | 269860 | 277955.8 | 286294.474 | 294883.3082 | 303729.8075 | 312841.7017 | 322226.9527 | 331893.7613 | 341850.5742 | 352106.0914 | 362669.2741 | 373549.3524 | 384755.8329 | 396298.5079 | 408187.4631 | 420433.087 | 433046.0797 | 446037.462 | 459418.5859 | 473201.1435 | 487397.1778 | 502019.0931 | 517079.6659 | 532592.0559 | 548569.8176 | 565026.9121 | 581977.7195 |  |  | 3% | 7400 | 5000 | 3200 | 1600 | 0 | -1300 | -2100 | -3200
| District Connections to Customer Bldgs | 700000 |  | ($15k/building, 50 total) | 750000 |  |  | 265225 | 273181.75 | 273181.75 | [27 empty] | 4% | 14000 | 10600 | 8000 | 5800 | 3600 | 1900 | 700 | -700
| NYSERDA Category B&C Award | -4200000 |  | PON 4641 Category B&C | -4500000 | -500000 |  |  | -4000000 | [28 empty] | 5% | 21700 | 17200 | 13700 | 10700 | 7900 | 5600 | 3900 | 2100
| Total (NPV) | 50100000 |  |  | 81452000 | 10518086.0109 | 3318086.0109 | 3845311.0109 | -138872.2391 | 3869223.5609 | 3604380.4849 | 3612969.3191 | 3621815.8184 | 3630927.7126 | 3640312.9636 | 3649979.7722 | 3659936.5851 | 3670192.1023 | 3680755.285 | 3691635.3633 | 3702841.8438 | 3714384.5188 | 3726273.474 | 3738519.0979 | 3751132.0906 | 3764123.4729 | 3777504.5968 | 3791287.1544 | 3805483.1887 | 3820105.104 | 3835165.6768 | 2798203.866 | 2814181.6277 | 2830638.7222 | 2847589.5296 |  |  | 6% | 30900 | 25000 | 20400 | 16400 | 12800 | 9900 | 7600 | 5400
[38 empty] | 7% | 41700 | 34200 | 28200 | 23200 | 18600 | 14900 | 12000 | 9200
Direct Benefits |  |  |  |  | Per year estimate | [32 empty] | 8% | 54600 | 45100 | 37500 | 31100 | 25400 | 20800 | 17100 | 13600
| Avoided Customer O&M | 10300000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 650000 |  |  | 355136.275 | 731580.7265 | 753528.1483 | 776133.9927 | 799418.0125 | 823400.5529 | 848102.5695 | 873545.6466 | 899752.016 | 926744.5765 | 954546.9137 | 983183.3212 | 1012678.8208 | 1043059.1854 | 1074350.961 | 1106581.4898 | 1139778.9345 | 1173972.3025 | 1209191.4716 | 1245467.2158 | 1282831.2322 | 1321316.1692 | 1360955.6543 | 1401784.3239 | 1443837.8536 | 1487152.9892 | 1531767.5789 | 1577720.6063
| Avoided Customer Equipment Recondition | 12800000 |  | Per App D (10% tower and boiler/yr) | 807000 |  |  | 440915.3445 | 908285.6097 | 935534.178 | 963600.2033 | 992508.2094 | 1022283.4557 | 1052951.9594 | 1084540.5181 | 1117076.7337 | 1150589.0357 | 1185106.7068 | 1220659.908 | 1257279.7052 | 1294998.0964 | 1333848.0392 | 1373863.4804 | 1415079.3848 | 1457531.7664 | 1501257.7194 | 1546295.451 | 1592684.3145 | 1640464.8439 | 1689678.7892 | 1740369.1529 | 1792580.2275 | 1846357.6343 | 1901748.3633 | 1958800.8143 |  |  | 3%: Discount Rate
| Customer Energy Savings | 34900000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 1700000 |  |  | 928817.95 | 2066360.625 | 2169678.6562 | 2278162.5891 | 2392070.7185 | 2511674.2544 | 2637257.9672 | 2769120.8655 | 2907576.9088 | 3052955.7542 | 3205603.5419 | 3365883.719 | 3534177.905 | 3710886.8002 | 3896431.1403 | 4091252.6973 | 4295815.3321 | 4510606.0987 | 4736136.4037 | 4972943.2239 | 5221590.3851 | 5482669.9043 | 5756803.3995 | 6044643.5695 | 6346875.748 | 6664219.5354 | 6997430.5121 | 7347302.0378 |  |  | 7900 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Total Direct Benefits | 58000000 |  |  | 3157000 | 0 | 0 | 1724869.5695 | 3706226.9612 | 3858740.9825 | 4017896.7851 | 4183996.9404 | 4357358.263 | 4538312.496 | 4727207.0302 | 4924405.6584 | 5130289.3664 | 5345257.1624 | 5569726.9482 | 5804136.431 | 6048944.082 | 6304630.1405 | 6571697.6675 | 6850673.6515 | 7142110.1677 | 7446585.5947 | 7764705.8906 | 8097105.9318 | 8444450.9174 | 8807437.843 | 9186797.0463 | 9583293.8291 | 9997730.1589 | 10430946.4544 | 10883823.4583 |  | Finance Rate | 2% | 31100 | 25700 | 21500 | 17700 | 14300 | 11600 | 9500 | 7200
[38 empty] | 2.5% | 26500 | 21600 | 17700 | 14200 | 11200 | 8700 | 6700 | 4700
| Net Direct Benefits | 7900000 |  |  |  | -10518086.0109 | -3318086.0109 | -2120441.4414 | 3845099.2003 | -10482.5784 | 413516.3002 | 571027.6213 | 735542.4447 | 907384.7834 | 1086894.0666 | 1274425.8862 | 1470352.7813 | 1675065.0602 | 1888971.6631 | 2112501.0677 | 2346102.2382 | 2590245.6217 | 2845424.1935 | 3112154.5535 | 3390978.0771 | 3682462.1217 | 3987201.2938 | 4305818.7774 | 4638967.7287 | 4987332.739 | 5351631.3695 | 6785089.9631 | 7183548.5312 | 7600307.7322 | 8036233.9287 |  |  | 3% | 21700 | 17200 | 13700 | 10700 | 7900 | 5600 | 3900 | 2100
| IRR | 8.809% | [35 empty] | 3.5% | 16700 | 12700 | 9600 | 6900 | 4500 | 2500 | 1000 | -700
| BCR | 1.1577 | [35 empty] | 4% | 11500 | 8000 | 5400 | 3000 | 900 | -800 | -2100 | -3600
Indirect Benefits | [37 empty] | 4.5% | 6100 | 3100 | 1000 | -1000 | -2800 | -4200 | -5300 | -6500
| Carbon Reduction Social Benefit | 8800000 |  | $125/ton value NYS-DEC Guidance per evaluation | 1550000 |  |  | 627710.0966 | 1263814.1434 | 1178064.3538 | 1098132.6874 | 1023624.3845 | 954171.4701 | 889430.9358 | 829083.0468 | 772829.7621 | 720393.2627 | 671514.5799 | 625952.3156 | 583481.451 | 543892.2345 | 506989.1464 | 472589.9328 | 440524.7059 | 410635.1046 | 382773.5128 | 356802.3299 | 332593.2918 | 310026.837 | 288991.5161 | 269383.4417 | 1000000 | 1000000 | 1000000 | 1000000 |  |  | 5% | 500 | -1900 | -3700 | -5200 | -6600 | -7800 | -8500 | -9600
| Avoided Electrical Substation Upgrades | 12600000 |  |  | 13439163.7934 | [10 empty] | 13439163.7934
| Total Indirect Benefits | 21400000
| Net Direct + Indirect Benefits | 29300000 |  |  |  | -10518086.0109 | -3318086.0109 | -1492731.3448 | 5108913.3437 | 1167581.7754 | 1511648.9876 | 1594652.0059 | 1689713.9147 | 1796815.7192 | 1915977.1134 | 15486419.4418 | 2190746.044 | 2346579.64 | 2514923.9787 | 2695982.5187 | 2889994.4727 | 3097234.7681 | 3318014.1263 | 3552679.2594 | 3801613.1817 | 4065235.6345 | 4344003.6237 | 4638412.0692 | 4948994.5657 | 5276324.2551 | 5621014.8112
| IRR | 15.87%
| BCR | 1.5848

## Summary-No Cat C
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5%
[5 empty] | General Inflation Rate | 3%
[5 empty] | Discount Rate | 7%
[5 empty] | Ton Red Rate | -9.5%
| Summary Table - Total Summary (No Category C) |  |  |  | Finance Rate | 3% | 40 | yr
25-Yr NPV Sensitivity Analysis (In thousands)
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | Natural Gas Inflation Rate |  | Discount Rate
| Design and Planning | 7700000 |  | ~10% Construction | 7700000 | 7700000 | [31 empty] | 4200 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Central Plant Investment | 13300000 |  | Per CHA Estimate | 24500000 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | [6 empty] | 1% | -6800 | -7700 | -8300 | -8900 | -9600 | -10200 | -10400 | -10800
| Distribution Piping Investment | 28700000 |  | Per CHA Estimate $53M financing over 40yr | 52740000 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 | 2265611.8101 |  |  | 2% | -2100 | -3600 | -4800 | -5800 | -6900 | -7800 | -8300 | -8900
| Central Plant O&M | 3900000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A) | 262000 |  |  | 262000 | 269860 | 277955.8 | 286294.474 | 294883.3082 | 303729.8075 | 312841.7017 | 322226.9527 | 331893.7613 | 341850.5742 | 352106.0914 | 362669.2741 | 373549.3524 | 384755.8329 | 396298.5079 | 408187.4631 | 420433.087 | 433046.0797 | 446037.462 | 459418.5859 | 473201.1435 | 487397.1778 | 502019.0931 | 517079.6659 | 532592.0559 | 548569.8176 | 565026.9121 | 581977.7195 |  |  | 3% | 3500 | 1200 | -600 | -2200 | -3700 | -5000 | -5800 | -6800
| District Connections to Customer Bldgs | 700000 |  | ($15k/building, 50 total) | 750000 |  |  | 265225 | 273181.75 | 273181.75 | [27 empty] | 4% | 10100 | 6800 | 4200 | 2000 | -100 | -1800 | -3000 | -4300
| NYSERDA Category B&C Award | -500000 |  | PON 4641 Category B&C | 500000 | -500000 | [31 empty] | 5% | 17800 | 13400 | 9900 | 6900 | 4200 | 1900 | 200 | -1500
| Total (NPV) | 53800000 |  |  | 86452000 | 10518086.0109 | 3318086.0109 | 3845311.0109 | 3861127.7609 | 3869223.5609 | 3604380.4849 | 3612969.3191 | 3621815.8184 | 3630927.7126 | 3640312.9636 | 3649979.7722 | 3659936.5851 | 3670192.1023 | 3680755.285 | 3691635.3633 | 3702841.8438 | 3714384.5188 | 3726273.474 | 3738519.0979 | 3751132.0906 | 3764123.4729 | 3777504.5968 | 3791287.1544 | 3805483.1887 | 3820105.104 | 3835165.6768 | 2798203.866 | 2814181.6277 | 2830638.7222 | 2847589.5296 |  |  | 6% | 27000 | 21200 | 16600 | 12600 | 9100 | 6200 | 3900 | 1800
[38 empty] | 7% | 37800 | 30400 | 24400 | 19400 | 14900 | 11200 | 8300 | 5600
Direct Benefits |  |  |  |  | Per year estimate | [32 empty] | 8% | 50700 | 41300 | 33700 | 27300 | 21700 | 17100 | 13400 | 10000
| Avoided Customer O&M | 10300000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 650000 |  |  | 355136.275 | 731580.7265 | 753528.1483 | 776133.9927 | 799418.0125 | 823400.5529 | 848102.5695 | 873545.6466 | 899752.016 | 926744.5765 | 954546.9137 | 983183.3212 | 1012678.8208 | 1043059.1854 | 1074350.961 | 1106581.4898 | 1139778.9345 | 1173972.3025 | 1209191.4716 | 1245467.2158 | 1282831.2322 | 1321316.1692 | 1360955.6543 | 1401784.3239 | 1443837.8536 | 1487152.9892 | 1531767.5789 | 1577720.6063
| Avoided Customer Equipment Recondition | 12800000 |  | Per App D (10% tower and boiler/yr) | 807000 |  |  | 440915.3445 | 908285.6097 | 935534.178 | 963600.2033 | 992508.2094 | 1022283.4557 | 1052951.9594 | 1084540.5181 | 1117076.7337 | 1150589.0357 | 1185106.7068 | 1220659.908 | 1257279.7052 | 1294998.0964 | 1333848.0392 | 1373863.4804 | 1415079.3848 | 1457531.7664 | 1501257.7194 | 1546295.451 | 1592684.3145 | 1640464.8439 | 1689678.7892 | 1740369.1529 | 1792580.2275 | 1846357.6343 | 1901748.3633 | 1958800.8143 |  |  | 3%: Discount Rate
| Customer Energy Savings | 34900000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 1700000 |  |  | 928817.95 | 2066360.625 | 2169678.6562 | 2278162.5891 | 2392070.7185 | 2511674.2544 | 2637257.9672 | 2769120.8655 | 2907576.9088 | 3052955.7542 | 3205603.5419 | 3365883.719 | 3534177.905 | 3710886.8002 | 3896431.1403 | 4091252.6973 | 4295815.3321 | 4510606.0987 | 4736136.4037 | 4972943.2239 | 5221590.3851 | 5482669.9043 | 5756803.3995 | 6044643.5695 | 6346875.748 | 6664219.5354 | 6997430.5121 | 7347302.0378 |  |  | 4200 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Total Direct Benefits | 58000000 |  |  | 3157000 | 0 | 0 | 1724869.5695 | 3706226.9612 | 3858740.9825 | 4017896.7851 | 4183996.9404 | 4357358.263 | 4538312.496 | 4727207.0302 | 4924405.6584 | 5130289.3664 | 5345257.1624 | 5569726.9482 | 5804136.431 | 6048944.082 | 6304630.1405 | 6571697.6675 | 6850673.6515 | 7142110.1677 | 7446585.5947 | 7764705.8906 | 8097105.9318 | 8444450.9174 | 8807437.843 | 9186797.0463 | 9583293.8291 | 9997730.1589 | 10430946.4544 | 10883823.4583 |  | Finance Rate | 2% | 27200 | 21900 | 17700 | 13900 | 10600 | 7900 | 5800 | 3600
[38 empty] | 2.5% | 22600 | 17800 | 13900 | 10400 | 7500 | 5000 | 3000 | 1100
| Net Direct Benefits | 4200000 |  |  |  | -10518086.0109 | -3318086.0109 | -2120441.4414 | -154900.7997 | -10482.5784 | 413516.3002 | 571027.6213 | 735542.4447 | 907384.7834 | 1086894.0666 | 1274425.8862 | 1470352.7813 | 1675065.0602 | 1888971.6631 | 2112501.0677 | 2346102.2382 | 2590245.6217 | 2845424.1935 | 3112154.5535 | 3390978.0771 | 3682462.1217 | 3987201.2938 | 4305818.7774 | 4638967.7287 | 4987332.739 | 5351631.3695 | 6785089.9631 | 7183548.5312 | 7600307.7322 | 8036233.9287 |  |  | 3% | 17800 | 13400 | 9900 | 6900 | 4200 | 1900 | 200 | -1500
| IRR | 7.277% | [35 empty] | 3.5% | 12800 | 8900 | 5800 | 3100 | 800 | -1200 | -2700 | -4300
| BCR | 1.0781 | [35 empty] | 4% | 7600 | 4200 | 1600 | -800 | -2800 | -4500 | -5800 | -7200
Indirect Benefits | [37 empty] | 4.5% | 2200 | -700 | -2800 | -4800 | -6500 | -7900 | -9000 | -10100
| Carbon Reduction Social Benefit | 8800000 |  | $125/ton value NYS-DEC Guidance per evaluation | 1550000 |  |  | 627710.0966 | 1263814.1434 | 1178064.3538 | 1098132.6874 | 1023624.3845 | 954171.4701 | 889430.9358 | 829083.0468 | 772829.7621 | 720393.2627 | 671514.5799 | 625952.3156 | 583481.451 | 543892.2345 | 506989.1464 | 472589.9328 | 440524.7059 | 410635.1046 | 382773.5128 | 356802.3299 | 332593.2918 | 310026.837 | 288991.5161 | 269383.4417 | 1000000 | 1000000 | 1000000 | 1000000 |  |  | 5% | -3400 | -5700 | -7500 | -9000 | -10300 | -11500 | -12200 | -13200
| Avoided Electrical Substation Upgrades | 12600000 |  |  | 13439163.7934 | [10 empty] | 13439163.7934
| Total Indirect Benefits | 21400000
| Net Direct + Indirect Benefits | 25600000 |  |  |  | -10518086.0109 | -3318086.0109 | -1492731.3448 | 1108913.3437 | 1167581.7754 | 1511648.9876 | 1594652.0059 | 1689713.9147 | 1796815.7192 | 1915977.1134 | 15486419.4418 | 2190746.044 | 2346579.64 | 2514923.9787 | 2695982.5187 | 2889994.4727 | 3097234.7681 | 3318014.1263 | 3552679.2594 | 3801613.1817 | 4065235.6345 | 4344003.6237 | 4638412.0692 | 4948994.5657 | 5276324.2551 | 5621014.8112
| IRR | 13.74%
| BCR | 1.4758

## Summary Phase C (Initial)
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5% | [32 empty] | 25-Yr NPV Sensitivity Analysis (In thousands)
[5 empty] | General Inflation Rate | 3%
[5 empty] | Discount Rate | 7% | [30 empty] | Natural Gas Inflation Rate |  | Discount Rate
[5 empty] | Ton Red Rate | -9.5% | [31 empty] | -12100 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Summary Table - Phase C |  |  |  | Finance Rate | 3% | 40 | yr | [29 empty] | 1% | -20800 | -18900 | -17400 | -16200 | -15000 | -14200 | -13200 | -12500
[38 empty] | 2% | -19800 | -18100 | -16700 | -15500 | -14400 | -13700 | -12800 | -12100
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | [6 empty] | 3% | -18700 | -17100 | -15800 | -14800 | -13800 | -13100 | -12300 | -11700
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 4% | -17300 | -15900 | -14800 | -13900 | -13000 | -12500 | -11700 | -11200
| Design and Planning | 2900000 |  | ~10% Construction | 2900000 | 0: 2900000 |  | 5% | -15700 | -14500 | -13600 | -12900 | -12100 | -11700 | -11000 | -10600
| Central Plant Investment | 13300000 |  | Per CHA Estimate | 24500000 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | [6 empty] | 6% | -13800 | -12900 | -12200 | -11700 | -11100 | -10800 | -10200 | -9900
| Distribution Piping Investment | 2600000 |  | Per CHA Estimate $53M financing over 40yr | 4790000 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 |  |  | 7% | -11500 | -11000 | -10600 | -10300 | -9900 | -9700 | -9300 | -9100
| Central Plant O&M | 3900000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A) | 262000 |  |  | 262000 | 269860 | 277955.8 | 286294.474 | 294883.3082 | 303729.8075 | 312841.7017 | 322226.9527 | 331893.7613 | 341850.5742 | 352106.0914 | 362669.2741 | 373549.3524 | 384755.8329 | 396298.5079 | 408187.4631 | 420433.087 | 433046.0797 | 446037.462 | 459418.5859 | 473201.1435 | 487397.1778 | 502019.0931 | 517079.6659 | 532592.0559 | 548569.8176 | 565026.9121 | 581977.7195 |  |  | 8% | -8800 | -8700 | -8700 | -8600 | -8500 | -8500 | -8300 | -8200
| District Connections to Customer Bldgs | 200000 |  | ($15k/building, 12 total) | 180000 | 2: 63654; 3: 65563.62; 4: 65563.62
| NYSERDA Category B&C Award | -1000000 |  | PON 4641 Category B&C | -1102040.8163 | 0: -122448.9796; 3: -979591.8367 |  |  | Discount Rate
| Total (NPV) | 21900000 |  |  | 31529959.1837 | 4035794.667 | 1258243.6465 | 1583897.6465 | 614075.4298 | 1601763.0665 | 1544538.1205 | 1553126.9548 | 1561973.454 | 1571085.3482 | 1580470.5993 | 1590137.4079 | 1600094.2207 | 1610349.7379 | 1620912.9207 | 1631792.9989 | 1642999.4795 | 1654542.1545 | 1666431.1097 | 1678676.7336 | 1691289.7262 | 1704281.1086 | 1717662.2325 | 1731444.79 | 1745640.8243 | 1760262.7397 | 1775323.3125 | 738361.5017 | 754339.2634 | 770796.3579 | 787747.1652 |  |  | -12100 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
[37 empty] | Finance Rate | 2% | -12100 | -11300 | -10600 | -10300 | -9700 | -9400 | -8900 | -8700
Direct Benefits |  |  |  |  | Per year estimate | [32 empty] | 2.5% | -13900 | -12900 | -12100 | -11600 | -10900 | -10500 | -10000 | -9600
| Avoided Customer O&M | 500000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 30000 |  |  | 16390.905 | 33765.2643 | 34778.2222 | 35821.5689 | 36896.216 | 38003.1024 | 39143.1955 | 40317.4914 | 41527.0161 | 42772.8266 | 44056.0114 | 45377.6917 | 46739.0225 | 48141.1932 | 49585.429 | 51072.9918 | 52605.1816 | 54183.337 | 55808.8372 | 57483.1023 | 59207.5953 | 60983.8232 | 62813.3379 | 64697.738 | 66638.6702 | 68637.8303 | 70696.9652 | 72817.8741 |  |  | 3% | -15700 | -14500 | -13600 | -12900 | -12100 | -11700 | -11000 | -10600
| Avoided Customer Equipment Recondition | 2000000 |  | Per App D (10% tower and boiler/yr) | 123000 |  |  | 67202.7105 | 138437.5836 | 142590.7111 | 146868.4325 | 151274.4854 | 155812.72 | 160487.1016 | 165301.7147 | 170260.7661 | 175368.5891 | 180629.6468 | 186048.5362 | 191629.9922 | 197378.892 | 203300.2588 | 209399.2665 | 215681.2445 | 222151.6819 | 228816.2323 | 235680.7193 | 242751.1409 | 250033.6751 | 257534.6853 | 265260.7259 | 273218.5477 | 281415.1041 | 289857.5572 | 298553.284 |  |  | 3.5% | -17600 | -16200 | -15200 | -14400 | -13400 | -12900 | -12100 | -11600
| Customer Energy Savings | 7300000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 354200 |  |  | 193521.9517 | 430532.3138 | 452058.9294 | 474661.8759 | 498394.9697 | 523314.7182 | 549480.4541 | 576954.4768 | 605802.2006 | 636092.3107 | 667896.9262 | 701291.7725 | 736356.3611 | 773174.1792 | 811832.8882 | 852424.5326 | 895045.7592 | 939798.0472 | 986787.9495 | 1036127.347 | 1087933.7143 | 1142330.4001 | 1199446.9201 | 1259419.2661 | 1322390.2294 | 1388509.7408 | 1457935.2279 | 1530831.9893 |  |  | 4% | -19500 | -18000 | -16700 | -15800 | -14700 | -14100 | -13300 | -12700
| Total Direct Benefits | 9800000 |  |  | 507200 | 0 | 0 | 277115.5672 | 602735.1617 | 629427.8628 | 657351.8773 | 686565.6711 | 717130.5406 | 749110.7512 | 782573.6828 | 817589.9829 | 854233.7264 | 892582.5844 | 932718.0004 | 974725.3759 | 1018694.2644 | 1064718.5759 | 1112896.7909 | 1163332.1853 | 1216133.0661 | 1271413.019 | 1329291.1686 | 1389892.4505 | 1453347.8984 | 1519794.9433 | 1589377.73 | 1662247.4472 | 1738562.6752 | 1818489.7503 | 1902203.1474 |  |  | 4.5% | -21600 | -19900 | -18400 | -17400 | -16200 | -15400 | -14500 | -13800
[38 empty] | 5% | -23700 | -21800 | -20200 | -18900 | -17600 | -16800 | -15700 | -15000
| Net Direct Benefits | -12100000 |  |  |  | -4035794.667 | -1258243.6465 | -1306782.0793 | -11340.2681 | -972335.2037 | -887186.2433 | -866561.2837 | -844842.9134 | -821974.597 | -797896.9164 | -772547.425 | -745860.4943 | -717767.1536 | -688194.9203 | -657067.623 | -624305.2151 | -589823.5786 | -553534.3188 | -515344.5483 | -475156.6601 | -432868.0896 | -388371.0639 | -341552.3395 | -292292.926 | -240467.7964 | -185945.5825 | 923885.9456 | 984223.4119 | 1047693.3924 | 1114455.9821
| IRR | #NUM!
| BCR | 0.44749
Indirect Benefits
| Carbon Reduction Social Benefit | 2300000 |  | $125/ton value NYS-DEC Guidance per evaluation | 398000 |  |  | 161179.7538 | 324514.8575 | 302496.5244 | 281972.1352 | 262840.3258 | 245006.6097 | 228382.9113 | 212887.1307 | 198442.7389 | 184978.3991 | 172427.6147 | 160728.401 | 149822.979 | 139657.4899 | 130181.7292 | 121348.8989 | 113115.3761 | 105440.4978 | 98286.3601 | 91617.6305 | 85401.3743 | 79606.891 | 74205.5635 | 69170.716
| Avoided Electrical Substation Upgrades | 3100000 |  |  | 3291223.7861 | [10 empty] | 3291223.7861
| Total Indirect Benefits | 5400000
| Net Direct + Indirect Benefits | -6700000 |  |  |  | -4035794.667 | -1258243.6465 | -1145602.3255 | 313174.5893 | -669838.6793 | -605214.1081 | -603720.9578 | -599836.3036 | -593591.6858 | -585009.7857 | 2717119.1001 | -560882.0953 | -545339.5389 | -527466.5192 | -507244.644 | -484647.7252 | -459641.8493 | -432185.4199 | -402229.1722 | -369716.1623 | -334581.7295 | -296753.4334 | -256150.9652 | -212686.0349 | -166262.2329 | -116774.8665
| IRR | #NUM!
| BCR | 0.69406

## Summary Phase C -No Cat C
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5% | [32 empty] | 25-Yr NPV Sensitivity Analysis (In thousands)
[5 empty] | General Inflation Rate | 3%
[5 empty] | Discount Rate | 7% | [30 empty] | Natural Gas Inflation Rate |  | Discount Rate
[5 empty] | Ton Red Rate | -9.5% | [31 empty] | -13000 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Summary Table - Phase C (No Category C) |  |  |  | Finance Rate | 3% | 40 | yr | [29 empty] | 1% | -21800 | -19900 | -18400 | -17100 | -15900 | -15100 | -14100 | -13400
[38 empty] | 2% | -20800 | -19100 | -17700 | -16400 | -15300 | -14600 | -13700 | -13000
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | [6 empty] | 3% | -19700 | -18100 | -16800 | -15700 | -14700 | -14000 | -13200 | -12600
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 4% | -18300 | -16900 | -15800 | -14800 | -13900 | -13400 | -12600 | -12100
| Design and Planning | 2900000 |  | ~10% Construction | 2900000 | 0: 2900000 |  | 5% | -16700 | -15500 | -14600 | -13800 | -13000 | -12600 | -11900 | -11500
| Central Plant Investment | 13300000 |  | Per CHA Estimate | 24500000 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | 1052474.2008 | [6 empty] | 6% | -14800 | -13900 | -13200 | -12600 | -12000 | -11700 | -11100 | -10800
| Distribution Piping Investment | 2600000 |  | Per CHA Estimate $53M financing over 40yr | 4790000 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 | 205769.4458 |  |  | 7% | -12500 | -12000 | -11600 | -11200 | -10800 | -10600 | -10200 | -10000
| Central Plant O&M | 3900000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A) | 262000 |  |  | 262000 | 269860 | 277955.8 | 286294.474 | 294883.3082 | 303729.8075 | 312841.7017 | 322226.9527 | 331893.7613 | 341850.5742 | 352106.0914 | 362669.2741 | 373549.3524 | 384755.8329 | 396298.5079 | 408187.4631 | 420433.087 | 433046.0797 | 446037.462 | 459418.5859 | 473201.1435 | 487397.1778 | 502019.0931 | 517079.6659 | 532592.0559 | 548569.8176 | 565026.9121 | 581977.7195 |  |  | 8% | -9800 | -9700 | -9700 | -9500 | -9400 | -9400 | -9200 | -9100
| District Connections to Customer Bldgs | 200000 |  | ($15k/building, 12 total) | 180000 | 2: 63654; 3: 65563.62; 4: 65563.62
| NYSERDA Category B&C Award | -100000 |  | PON 4641 Category B&C | -122448.9796 | 0: -122448.9796 |  |  | Discount Rate
| Total (NPV) | 22800000 |  |  | 32509551.0204 | 4035794.667 | 1258243.6465 | 1583897.6465 | 1593667.2665 | 1601763.0665 | 1544538.1205 | 1553126.9548 | 1561973.454 | 1571085.3482 | 1580470.5993 | 1590137.4079 | 1600094.2207 | 1610349.7379 | 1620912.9207 | 1631792.9989 | 1642999.4795 | 1654542.1545 | 1666431.1097 | 1678676.7336 | 1691289.7262 | 1704281.1086 | 1717662.2325 | 1731444.79 | 1745640.8243 | 1760262.7397 | 1775323.3125 | 738361.5017 | 754339.2634 | 770796.3579 | 787747.1652 |  |  | -13000 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
[37 empty] | Finance Rate | 2% | -13100 | -12300 | -11600 | -11200 | -10600 | -10300 | -9800 | -9600
Direct Benefits |  |  |  |  | Per year estimate | [32 empty] | 2.5% | -14900 | -13900 | -13100 | -12500 | -11800 | -11400 | -10900 | -10500
| Avoided Customer O&M | 500000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 30000 |  |  | 16390.905 | 33765.2643 | 34778.2222 | 35821.5689 | 36896.216 | 38003.1024 | 39143.1955 | 40317.4914 | 41527.0161 | 42772.8266 | 44056.0114 | 45377.6917 | 46739.0225 | 48141.1932 | 49585.429 | 51072.9918 | 52605.1816 | 54183.337 | 55808.8372 | 57483.1023 | 59207.5953 | 60983.8232 | 62813.3379 | 64697.738 | 66638.6702 | 68637.8303 | 70696.9652 | 72817.8741 |  |  | 3% | -16700 | -15500 | -14600 | -13800 | -13000 | -12600 | -11900 | -11500
| Avoided Customer Equipment Recondition | 2000000 |  | Per App D (10% tower and boiler/yr) | 123000 |  |  | 67202.7105 | 138437.5836 | 142590.7111 | 146868.4325 | 151274.4854 | 155812.72 | 160487.1016 | 165301.7147 | 170260.7661 | 175368.5891 | 180629.6468 | 186048.5362 | 191629.9922 | 197378.892 | 203300.2588 | 209399.2665 | 215681.2445 | 222151.6819 | 228816.2323 | 235680.7193 | 242751.1409 | 250033.6751 | 257534.6853 | 265260.7259 | 273218.5477 | 281415.1041 | 289857.5572 | 298553.284 |  |  | 3.5% | -18600 | -17200 | -16200 | -15300 | -14300 | -13800 | -13000 | -12500
| Customer Energy Savings | 7300000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 354200 |  |  | 193521.9517 | 430532.3138 | 452058.9294 | 474661.8759 | 498394.9697 | 523314.7182 | 549480.4541 | 576954.4768 | 605802.2006 | 636092.3107 | 667896.9262 | 701291.7725 | 736356.3611 | 773174.1792 | 811832.8882 | 852424.5326 | 895045.7592 | 939798.0472 | 986787.9495 | 1036127.347 | 1087933.7143 | 1142330.4001 | 1199446.9201 | 1259419.2661 | 1322390.2294 | 1388509.7408 | 1457935.2279 | 1530831.9893 |  |  | 4% | -20500 | -19000 | -17700 | -16700 | -15600 | -15000 | -14200 | -13600
| Total Direct Benefits | 9800000 |  |  | 507200 | 0 | 0 | 277115.5672 | 602735.1617 | 629427.8628 | 657351.8773 | 686565.6711 | 717130.5406 | 749110.7512 | 782573.6828 | 817589.9829 | 854233.7264 | 892582.5844 | 932718.0004 | 974725.3759 | 1018694.2644 | 1064718.5759 | 1112896.7909 | 1163332.1853 | 1216133.0661 | 1271413.019 | 1329291.1686 | 1389892.4505 | 1453347.8984 | 1519794.9433 | 1589377.73 | 1662247.4472 | 1738562.6752 | 1818489.7503 | 1902203.1474 |  |  | 4.5% | -22600 | -20900 | -19400 | -18300 | -17100 | -16300 | -15400 | -14700
[38 empty] | 5% | -24700 | -22800 | -21200 | -19800 | -18500 | -17700 | -16600 | -15900
| Net Direct Benefits | -13000000 |  |  |  | -4035794.667 | -1258243.6465 | -1306782.0793 | -990932.1049 | -972335.2037 | -887186.2433 | -866561.2837 | -844842.9134 | -821974.597 | -797896.9164 | -772547.425 | -745860.4943 | -717767.1536 | -688194.9203 | -657067.623 | -624305.2151 | -589823.5786 | -553534.3188 | -515344.5483 | -475156.6601 | -432868.0896 | -388371.0639 | -341552.3395 | -292292.926 | -240467.7964 | -185945.5825 | 923885.9456 | 984223.4119 | 1047693.3924 | 1114455.9821
| IRR | #NUM!
| BCR | 0.42982
Indirect Benefits
| Carbon Reduction Social Benefit | 2300000 |  | $125/ton value NYS-DEC Guidance per evaluation | 398000 |  |  | 161179.7538 | 324514.8575 | 302496.5244 | 281972.1352 | 262840.3258 | 245006.6097 | 228382.9113 | 212887.1307 | 198442.7389 | 184978.3991 | 172427.6147 | 160728.401 | 149822.979 | 139657.4899 | 130181.7292 | 121348.8989 | 113115.3761 | 105440.4978 | 98286.3601 | 91617.6305 | 85401.3743 | 79606.891 | 74205.5635 | 69170.716
| Avoided Electrical Substation Upgrades | 3100000 |  |  | 3291223.7861 | [10 empty] | 3291223.7861
| Total Indirect Benefits | 5400000
| Net Direct + Indirect Benefits | -7600000 |  |  |  | -4035794.667 | -1258243.6465 | -1145602.3255 | -666417.2474 | -669838.6793 | -605214.1081 | -603720.9578 | -599836.3036 | -593591.6858 | -585009.7857 | 2717119.1001 | -560882.0953 | -545339.5389 | -527466.5192 | -507244.644 | -484647.7252 | -459641.8493 | -432185.4199 | -402229.1722 | -369716.1623 | -334581.7295 | -296753.4334 | -256150.9652 | -212686.0349 | -166262.2329 | -116774.8665
| IRR | #NUM!
| BCR | 0.66667

## Summary Phase A
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5% | [32 empty] | 25-Yr NPV Sensitivity Analysis (In thousands)
[5 empty] | General Inflation Rate | 3%
[5 empty] | Discount Rate | 7% | [30 empty] | Natural Gas Inflation Rate |  | Discount Rate
[5 empty] | Ton Red Rate | -9.5% | [31 empty] | -2000 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Summary Table - Phase A |  |  |  | Finance Rate | 3% | 40 | yr | [29 empty] | 1% | -6000 | -6000 | -5900 | -5800 | -5800 | -5800 | -5700 | -5800
[38 empty] | 2% | -4700 | -4900 | -4900 | -5000 | -5100 | -5200 | -5100 | -5300
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | [6 empty] | 3% | -3100 | -3500 | -3800 | -4000 | -4200 | -4400 | -4400 | -4700
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 4% | -1300 | -2000 | -2400 | -2800 | -3200 | -3500 | -3700 | -4000
| Design and Planning | 3500000 |  | ~10% Construction | 3500000 | 0: 3500000 |  | 5% | 900 | -100 | -900 | -1400 | -2000 | -2500 | -2800 | -3200
| Central Plant Investment | 0 |  | Per CHA Estimate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 6% | 3400 | 2000 | 1000 | 200 | -600 | -1300 | -1700 | -2300
| Distribution Piping Investment | 19100000 |  | Per CHA Estimate $53M financing over 40yr | 35120000 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 |  |  | 7% | 6500 | 4600 | 3200 | 2000 | 1000 | 100 | -500 | -1200
| Central Plant O&M | 2400000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A), ration of total buildings | 157200 |  |  | 157200 | 161916 | 166773.48 | 171776.6844 | 176929.9849 | 182237.8845 | 187705.021 | 193336.1716 | 199136.2568 | 205110.3445 | 211263.6548 | 217601.5645 | 224129.6114 | 230853.4998 | 237779.1047 | 244912.4779 | 252259.8522 | 259827.6478 | 267622.4772 | 275651.1515 | 283920.6861 | 292438.3067 | 301211.4559 | 310247.7995 | 319555.2335 | 329141.8905 | 339016.1473 | 349186.6317 |  |  | 8% | 10000 | 7600 | 5800 | 4300 | 2900 | 1700 | 900 | 0
| District Connections to Customer Bldgs | 300000 |  | ($15k/building, 18 total) | 270000 | 2: 95481; 3: 98345.43; 4: 98345.43
| NYSERDA Category B&C Award | -1600000 |  | PON 4641 Category B&C | -1653061.2245 | 0: -183673.4694; 3: -1469387.7551 |  |  | Discount Rate
| Total (NPV) | 23700000 |  |  | 37394138.7755 | 4825016.0788 | 1508689.5482 | 1761370.5482 | 299563.2231 | 1773808.4582 | 1680466.2326 | 1685619.5331 | 1690927.4327 | 1696394.5692 | 1702025.7198 | 1707825.805 | 1713799.8927 | 1719953.203 | 1726291.1127 | 1732819.1596 | 1739543.048 | 1746468.6529 | 1753602.0261 | 1760949.4004 | 1768517.196 | 1776312.0254 | 1784340.6997 | 1792610.2343 | 1801127.8549 | 1809901.0041 | 1818937.3477 | 1828244.7817 | 1837831.4387 | 1847705.6955 | 1857876.1799 |  |  | -2000 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
[37 empty] | Finance Rate | 2% | 5200 | 3800 | 2600 | 1800 | 1000 | 200 | -300 | -900
Direct Benefits |  |  |  |  | Per year estimate | [32 empty] | 2.5% | 3100 | 1900 | 900 | 200 | -500 | -1100 | -1500 | -2000
| Avoided Customer O&M | 6900000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 432000 |  |  | 236029.032 | 486219.8059 | 500806.4001 | 515830.5921 | 531305.5099 | 547244.6752 | 563662.0154 | 580571.8759 | 597989.0322 | 615928.7031 | 634406.5642 | 653438.7611 | 673041.924 | 693233.1817 | 714030.1771 | 735451.0825 | 757514.6149 | 780240.0534 | 803647.255 | 827756.6726 | 852589.3728 | 878167.054 | 904512.0656 | 931647.4276 | 959596.8504 | 988384.7559 | 1018036.2986 | 1048577.3876 |  |  | 3% | 900 | -100 | -900 | -1400 | -2000 | -2500 | -2800 | -3200
| Avoided Customer Equipment Recondition | 5100000 |  | Per App D (10% tower and boiler/yr) | 321000 |  |  | 175382.6835 | 361288.328 | 372126.9779 | 383290.7872 | 394789.5108 | 406633.1961 | 418832.192 | 431397.1578 | 444339.0725 | 457669.2447 | 471399.322 | 485541.3017 | 500107.5407 | 515110.767 | 530564.09 | 546481.0127 | 562875.443 | 579761.7063 | 597154.5575 | 615069.1942 | 633521.2701 | 652526.9082 | 672102.7154 | 692265.7969 | 713033.7708 | 734424.7839 | 756457.5274 | 779151.2533 |  |  | 3.5% | -1400 | -2100 | -2700 | -3100 | -3600 | -4000 | -4200 | -4500
| Customer Energy Savings | 9700000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 473100 |  |  | 258484.5719 | 575056.0069 | 603808.8072 | 633999.2476 | 665699.21 | 698984.1705 | 733933.379 | 770630.0479 | 809161.5503 | 849619.6278 | 892100.6092 | 936705.6397 | 983540.9217 | 1032717.9678 | 1084353.8662 | 1138571.5595 | 1195500.1374 | 1255275.1443 | 1318038.9015 | 1383940.8466 | 1453137.8889 | 1525794.7834 | 1602084.5225 | 1682188.7487 | 1766298.1861 | 1854613.0954 | 1947343.7502 | 2044710.9377 |  |  | 4% | -3700 | -4300 | -4700 | -4900 | -5200 | -5500 | -5600 | -5700
| Total Direct Benefits | 21700000 |  |  | 1226100 | 0 | 0 | 669896.2874 | 1422564.1408 | 1476742.1852 | 1533120.6269 | 1591794.2306 | 1652862.0417 | 1716427.5864 | 1782599.0816 | 1851489.655 | 1923217.5756 | 1997906.4955 | 2075685.7025 | 2156690.3864 | 2241061.9164 | 2328948.1333 | 2420503.6546 | 2515890.1954 | 2615276.904 | 2718840.714 | 2826766.7135 | 2939248.5318 | 3056488.7455 | 3178699.3036 | 3306101.9731 | 3438928.8073 | 3577422.6352 | 3721837.5762 | 3872439.5785 |  |  | 4.5% | -6200 | -6500 | -6700 | -6700 | -6900 | -7000 | -7000 | -7100
[38 empty] | 5% | -8700 | -8800 | -8800 | -8600 | -8600 | -8600 | -8500 | -8500
| Net Direct Benefits | -2000000 |  |  |  | -4825016.0788 | -1508689.5482 | -1091474.2608 | 1123000.9177 | -297066.273 | -147345.6057 | -93825.3025 | -38065.3909 | 20033.0172 | 80573.3617 | 143663.85 | 209417.6829 | 277953.2924 | 349394.5898 | 423871.2268 | 501518.8685 | 582479.4803 | 666901.6285 | 754940.795 | 846759.708 | 942528.6886 | 1042426.0137 | 1146638.2975 | 1255360.8907 | 1368798.2995 | 1487164.6254 | 1610684.0256 | 1739591.1965 | 1874131.8807 | 2014563.3986
| IRR | 2.978%
| BCR | 0.91561
Indirect Benefits
| Carbon Reduction Social Benefit | 2000000 |  | $125/ton value NYS-DEC Guidance per evaluation | 352000 |  |  | 142550.9381 | 287008.1152 | 267534.6145 | 249382.3909 | 232461.7957 | 216689.2629 | 201986.8964 | 188282.0855 | 175507.146 | 163598.9861 | 152498.7949 | 142151.7517 | 132506.7553 | 123516.172 | 115135.5997 | 107323.6493 | 100041.7397 | 93253.9076 | 86926.63 | 81028.6581 | 75530.8637 | 70406.0946 | 65629.0411 | 61176.1106
| Avoided Electrical Substation Upgrades | 4600000 |  |  | 4936835.6792 | [10 empty] | 4936835.6792
| Total Indirect Benefits | 6600000
| Net Direct + Indirect Benefits | 4600000 |  |  |  | -4825016.0788 | -1508689.5482 | -948923.3228 | 1410009.0329 | -29531.6585 | 102036.7852 | 138636.4932 | 178623.8719 | 222019.9136 | 268855.4472 | 5256006.6752 | 373016.6691 | 430452.0873 | 491546.3415 | 556377.9821 | 625035.0404 | 697615.08 | 774225.2778 | 854982.5346 | 940013.6156 | 1029455.3186 | 1123454.6719 | 1222169.1612 | 1325766.9853 | 1434427.3406 | 1548340.736
| IRR | 8.13%
| BCR | 1.1941

## Summary Phase A-No Cat C
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5% | [32 empty] | 25-Yr NPV Sensitivity Analysis (In thousands)
[5 empty] | General Inflation Rate | 3%
[5 empty] | Discount Rate | 7% | [30 empty] | Natural Gas Inflation Rate |  | Discount Rate
[5 empty] | Ton Red Rate | -9.5% | [31 empty] | -3400 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| Summary Table - Phase A (No Category C) |  |  |  | Finance Rate | 3% | 40 | yr | [29 empty] | 1% | -7400 | -7400 | -7300 | -7200 | -7200 | -7100 | -7000 | -7100
[38 empty] | 2% | -6100 | -6300 | -6300 | -6400 | -6500 | -6500 | -6400 | -6600
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | [6 empty] | 3% | -4500 | -4900 | -5200 | -5400 | -5600 | -5700 | -5700 | -6000
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 4% | -2700 | -3400 | -3800 | -4200 | -4600 | -4800 | -5000 | -5300
| Design and Planning | 3500000 |  | ~10% Construction | 3500000 | 0: 3500000 |  | 5% | -500 | -1500 | -2300 | -2800 | -3400 | -3800 | -4100 | -4500
| Central Plant Investment | 0 |  | Per CHA Estimate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 6% | 2000 | 600 | -400 | -1200 | -2000 | -2600 | -3000 | -3600
| Distribution Piping Investment | 19100000 |  | Per CHA Estimate $53M financing over 40yr | 35120000 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 | 1508689.5482 |  |  | 7% | 5100 | 3200 | 1800 | 600 | -400 | -1200 | -1800 | -2500
| Central Plant O&M | 2400000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A), ration of total buildings | 157200 |  |  | 157200 | 161916 | 166773.48 | 171776.6844 | 176929.9849 | 182237.8845 | 187705.021 | 193336.1716 | 199136.2568 | 205110.3445 | 211263.6548 | 217601.5645 | 224129.6114 | 230853.4998 | 237779.1047 | 244912.4779 | 252259.8522 | 259827.6478 | 267622.4772 | 275651.1515 | 283920.6861 | 292438.3067 | 301211.4559 | 310247.7995 | 319555.2335 | 329141.8905 | 339016.1473 | 349186.6317 |  |  | 8% | 8600 | 6200 | 4400 | 2900 | 1500 | 400 | -400 | -1300
| District Connections to Customer Bldgs | 300000 |  | ($15k/building, 18 total) | 270000 | 2: 95481; 3: 98345.43; 4: 98345.43
| NYSERDA Category B&C Award | -200000 |  | PON 4641 Category B&C | -183673.4694 | 0: -183673.4694 |  |  | Discount Rate
| Total (NPV) | 25100000 |  |  | 38863526.5306 | 4825016.0788 | 1508689.5482 | 1761370.5482 | 1768950.9782 | 1773808.4582 | 1680466.2326 | 1685619.5331 | 1690927.4327 | 1696394.5692 | 1702025.7198 | 1707825.805 | 1713799.8927 | 1719953.203 | 1726291.1127 | 1732819.1596 | 1739543.048 | 1746468.6529 | 1753602.0261 | 1760949.4004 | 1768517.196 | 1776312.0254 | 1784340.6997 | 1792610.2343 | 1801127.8549 | 1809901.0041 | 1818937.3477 | 1828244.7817 | 1837831.4387 | 1847705.6955 | 1857876.1799 |  |  | -3400 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
[37 empty] | Finance Rate | 2% | 3800 | 2400 | 1200 | 400 | -400 | -1100 | -1600 | -2200
Direct Benefits |  |  |  |  | Per year estimate | [32 empty] | 2.5% | 1700 | 500 | -500 | -1200 | -1900 | -2400 | -2800 | -3300
| Avoided Customer O&M | 6900000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 432000 |  |  | 236029.032 | 486219.8059 | 500806.4001 | 515830.5921 | 531305.5099 | 547244.6752 | 563662.0154 | 580571.8759 | 597989.0322 | 615928.7031 | 634406.5642 | 653438.7611 | 673041.924 | 693233.1817 | 714030.1771 | 735451.0825 | 757514.6149 | 780240.0534 | 803647.255 | 827756.6726 | 852589.3728 | 878167.054 | 904512.0656 | 931647.4276 | 959596.8504 | 988384.7559 | 1018036.2986 | 1048577.3876 |  |  | 3% | -500 | -1500 | -2300 | -2800 | -3400 | -3800 | -4100 | -4500
| Avoided Customer Equipment Recondition | 5100000 |  | Per App D (10% tower and boiler/yr) | 321000 |  |  | 175382.6835 | 361288.328 | 372126.9779 | 383290.7872 | 394789.5108 | 406633.1961 | 418832.192 | 431397.1578 | 444339.0725 | 457669.2447 | 471399.322 | 485541.3017 | 500107.5407 | 515110.767 | 530564.09 | 546481.0127 | 562875.443 | 579761.7063 | 597154.5575 | 615069.1942 | 633521.2701 | 652526.9082 | 672102.7154 | 692265.7969 | 713033.7708 | 734424.7839 | 756457.5274 | 779151.2533 |  |  | 3.5% | -2800 | -3500 | -4100 | -4500 | -5000 | -5300 | -5500 | -5800
| Customer Energy Savings | 9700000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 473100 |  |  | 258484.5719 | 575056.0069 | 603808.8072 | 633999.2476 | 665699.21 | 698984.1705 | 733933.379 | 770630.0479 | 809161.5503 | 849619.6278 | 892100.6092 | 936705.6397 | 983540.9217 | 1032717.9678 | 1084353.8662 | 1138571.5595 | 1195500.1374 | 1255275.1443 | 1318038.9015 | 1383940.8466 | 1453137.8889 | 1525794.7834 | 1602084.5225 | 1682188.7487 | 1766298.1861 | 1854613.0954 | 1947343.7502 | 2044710.9377 |  |  | 4% | -5100 | -5700 | -6100 | -6300 | -6600 | -6800 | -6900 | -7000
| Total Direct Benefits | 21700000 |  |  | 1226100 | 0 | 0 | 669896.2874 | 1422564.1408 | 1476742.1852 | 1533120.6269 | 1591794.2306 | 1652862.0417 | 1716427.5864 | 1782599.0816 | 1851489.655 | 1923217.5756 | 1997906.4955 | 2075685.7025 | 2156690.3864 | 2241061.9164 | 2328948.1333 | 2420503.6546 | 2515890.1954 | 2615276.904 | 2718840.714 | 2826766.7135 | 2939248.5318 | 3056488.7455 | 3178699.3036 | 3306101.9731 | 3438928.8073 | 3577422.6352 | 3721837.5762 | 3872439.5785 |  |  | 4.5% | -7600 | -7900 | -8100 | -8100 | -8300 | -8300 | -8300 | -8400
[38 empty] | 5% | -10100 | -10200 | -10200 | -10000 | -10000 | -9900 | -9800 | -9800
| Net Direct Benefits | -3400000 |  |  |  | -4825016.0788 | -1508689.5482 | -1091474.2608 | -346386.8374 | -297066.273 | -147345.6057 | -93825.3025 | -38065.3909 | 20033.0172 | 80573.3617 | 143663.85 | 209417.6829 | 277953.2924 | 349394.5898 | 423871.2268 | 501518.8685 | 582479.4803 | 666901.6285 | 754940.795 | 846759.708 | 942528.6886 | 1042426.0137 | 1146638.2975 | 1255360.8907 | 1368798.2995 | 1487164.6254 | 1610684.0256 | 1739591.1965 | 1874131.8807 | 2014563.3986
| IRR | 1.985%
| BCR | 0.86454
Indirect Benefits
| Carbon Reduction Social Benefit | 2000000 |  | $125/ton value NYS-DEC Guidance per evaluation | 352000 |  |  | 142550.9381 | 287008.1152 | 267534.6145 | 249382.3909 | 232461.7957 | 216689.2629 | 201986.8964 | 188282.0855 | 175507.146 | 163598.9861 | 152498.7949 | 142151.7517 | 132506.7553 | 123516.172 | 115135.5997 | 107323.6493 | 100041.7397 | 93253.9076 | 86926.63 | 81028.6581 | 75530.8637 | 70406.0946 | 65629.0411 | 61176.1106
| Avoided Electrical Substation Upgrades | 4600000 |  |  | 4936835.6792 | [10 empty] | 4936835.6792
| Total Indirect Benefits | 6600000
| Net Direct + Indirect Benefits | 3200000 |  |  |  | -4825016.0788 | -1508689.5482 | -948923.3228 | -59378.7222 | -29531.6585 | 102036.7852 | 138636.4932 | 178623.8719 | 222019.9136 | 268855.4472 | 5256006.6752 | 373016.6691 | 430452.0873 | 491546.3415 | 556377.9821 | 625035.0404 | 697615.08 | 774225.2778 | 854982.5346 | 940013.6156 | 1029455.3186 | 1123454.6719 | 1222169.1612 | 1325766.9853 | 1434427.3406 | 1548340.736
| IRR | 6.736%
| BCR | 1.1275

## Summary Phase B
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5%
[5 empty] | General Inflation Rate | 3% | [32 empty] | 25-Yr NPV Sensitivity Analysis (In thousands)
[5 empty] | Discount Rate | 7%
[5 empty] | Ton Red Rate | -9.5% | [30 empty] | Natural Gas Inflation Rate |  | Discount Rate
| Summary Table - Phase B |  |  |  | Finance Rate | 3% | 40 | yr | [29 empty] | 18000 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
[38 empty] | 1% | 17500 | 15400 | 13700 | 12100 | 10900 | 9700 | 8700 | 7800
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | [6 empty] | 2% | 19900 | 17500 | 15500 | 13700 | 12300 | 10900 | 9800 | 8800
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 3% | 22800 | 20000 | 17700 | 15600 | 13900 | 12300 | 11100 | 9900
| Design and Planning | 1300000 |  | ~10% Construction | 1300000 | 0: 1300000 |  | 4% | 26100 | 22900 | 20200 | 17700 | 15800 | 14000 | 12500 | 11100
| Central Plant Investment | 0 |  | Per CHA Estimate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 5% | 30100 | 26300 | 23100 | 20300 | 18000 | 15900 | 14200 | 12600
| Distribution Piping Investment | 7200000 |  | Per CHA Estimate $53M financing over 40yr | 13310000 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 |  |  | 6% | 34800 | 30300 | 26500 | 23200 | 20500 | 18100 | 16100 | 14300
| Central Plant O&M | 1500000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A), ration of total buildings | 101591.8367 |  |  | 101591.8367 | 104639.5918 | 107778.7796 | 111012.143 | 114342.5073 | 117772.7825 | 121305.966 | 124945.1449 | 128693.4993 | 132554.3043 | 136530.9334 | 140626.8614 | 144845.6672 | 149191.0373 | 153666.7684 | 158276.7714 | 163025.0746 | 167915.8268 | 172953.3016 | 178141.9007 | 183486.1577 | 188990.7424 | 194660.4647 | 200500.2786 | 206515.287 | 212710.7456 | 219092.068 | 225664.83 |  |  | 7% | 40400 | 35000 | 30600 | 26700 | 23500 | 20600 | 18300 | 16200
| District Connections to Customer Bldgs | 300000 |  | ($15k/building, 19 total) | 285000 | 2: 100785.5; 3: 103809.065; 4: 103809.065 |  | 8% | 47000 | 40600 | 35300 | 30700 | 27000 | 23700 | 20900 | 18500
| NYSERDA Category B&C Award | -1600000 |  | PON 4641 Category B&C | -1744897.9592 | 0: -193877.551; 3: -1551020.4082
| Total (NPV) | 8700000 |  |  | 13251693.8776 | 1677895.1678 | 571772.7189 | 774150.0556 | -770799.0325 | 783360.5635 | 682784.8618 | 686115.2261 | 689545.5014 | 693078.6848 | 696717.8638 | 700466.2182 | 704327.0231 | 708303.6523 | 712399.5803 | 716618.3861 | 720963.7561 | 725439.4872 | 730049.4903 | 734797.7934 | 739688.5457 | 744726.0205 | 749914.6195 | 755258.8765 | 760763.4613 | 766433.1835 | 772272.9975 | 778288.0058 | 784483.4645 | 790864.7868 | 797437.5489 |  |  |  | Discount Rate
[38 empty] | 18000 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
Direct Benefits |  |  |  |  | Per year estimate | [31 empty] | Finance Rate | 2% | 31700 | 27800 | 24400 | 21500 | 19100 | 17000 | 15200 | 13500
| Avoided Customer O&M | 3000000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 189000 |  |  | 103262.7015 | 212721.1651 | 219102.8 | 225675.884 | 232446.1606 | 239419.5454 | 246602.1317 | 254000.1957 | 261620.2016 | 269468.8076 | 277552.8718 | 285879.458 | 294455.8417 | 303289.517 | 312388.2025 | 321759.8486 | 331412.644 | 341355.0234 | 351595.6741 | 362143.5443 | 373007.8506 | 384198.0861 | 395724.0287 | 407595.7496 | 419823.6221 | 432418.3307 | 445390.8806 | 458752.6071 |  |  | 2.5% | 30900 | 27000 | 23700 | 20900 | 18500 | 16500 | 14700 | 13100
| Avoided Customer Equipment Recondition | 5800000 |  | Per App D (10% tower and boiler/yr) | 364000 |  |  | 198876.314 | 409685.2068 | 421975.763 | 434635.0359 | 447674.087 | 461104.3096 | 474937.4389 | 489185.5621 | 503861.1289 | 518976.9628 | 534546.2717 | 550582.6598 | 567100.1396 | 584113.1438 | 601636.5381 | 619685.6343 | 638276.2033 | 657424.4894 | 677147.2241 | 697461.6408 | 718385.4901 | 739937.0548 | 762135.1664 | 784999.2214 | 808549.198 | 832805.674 | 857789.8442 | 883523.5395 |  |  | 3% | 30100 | 26300 | 23100 | 20300 | 18000 | 15900 | 14200 | 12600
| Customer Energy Savings | 17900000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 872700 |  |  | 476811.4265 | 1060772.3044 | 1113810.9196 | 1169501.4656 | 1227976.5389 | 1289375.3658 | 1353844.1341 | 1421536.3408 | 1492613.1578 | 1567243.8157 | 1645606.0065 | 1727886.3068 | 1814280.6222 | 1904994.6533 | 2000244.3859 | 2100256.6052 | 2205269.4355 | 2315532.9073 | 2431309.5526 | 2552875.0303 | 2680518.7818 | 2814544.7209 | 2955271.9569 | 3103035.5548 | 3258187.3325 | 3421096.6991 | 3592151.5341 | 3771759.1108 |  |  | 3.5% | 29200 | 25500 | 22400 | 19700 | 17400 | 15400 | 13700 | 12200
| Total Direct Benefits | 26700000 |  |  | 1425700 | 0 | 0 | 778950.442 | 1683178.6763 | 1754889.4827 | 1829812.3856 | 1908096.7864 | 1989899.2208 | 2075383.7047 | 2164722.0986 | 2258094.4883 | 2355689.5861 | 2457705.15 | 2564348.4247 | 2675836.6036 | 2792397.3141 | 2914269.1266 | 3041702.0881 | 3174958.2829 | 3314312.4201 | 3460052.4508 | 3612480.2154 | 3771912.1224 | 3938679.8618 | 4113131.152 | 4295630.5257 | 4486560.1526 | 4686320.7038 | 4895332.2589 | 5114035.2574 |  |  | 4% | 28300 | 24700 | 21600 | 19000 | 16800 | 14800 | 13200 | 11700
[38 empty] | 4.5% | 27400 | 23900 | 20900 | 18300 | 16100 | 14200 | 12600 | 11200
| Net Direct Benefits | 18000000 |  |  |  | -1677895.1678 | -571772.7189 | 4800.3864 | 2453977.7088 | 971528.9192 | 1147027.5237 | 1221981.5603 | 1300353.7195 | 1382305.0199 | 1468004.2348 | 1557628.2702 | 1651362.563 | 1749401.4978 | 1851948.8444 | 1959218.2174 | 2071433.558 | 2188829.6394 | 2311652.5978 | 2440160.4894 | 2574623.8744 | 2715326.4303 | 2862565.5959 | 3016653.2459 | 3177916.4005 | 3346697.9685 | 3523357.5282 | 3708272.1467 | 3901837.2394 | 4104467.4721 | 4316597.7085 |  |  | 5% | 26400 | 23000 | 20100 | 17600 | 15500 | 13600 | 12100 | 10600
| IRR | 39.28%
| BCR | 3.069
Indirect Benefits
| Carbon Reduction Social Benefit | 4500000 |  | $125/ton value NYS-DEC Guidance per evaluation | 800000 |  |  | 323979.4047 | 652291.1708 | 608033.2149 | 566778.1612 | 528322.263 | 492475.5974 | 459061.1282 | 427913.8306 | 398879.8772 | 371815.8775 | 346588.1702 | 323072.1629 | 301151.7166 | 280718.5727 | 261671.8175 | 243917.3847 | 227367.5901 | 211940.6992 | 197560.5227 | 184156.0412 | 171661.0539 | 160013.8513 | 149156.9115 | 139036.6151
| Avoided Electrical Substation Upgrades | 4900000 |  |  | 5211104.3281 | [10 empty] | 5211104.3281
| Total Indirect Benefits | 9400000
| Net Direct + Indirect Benefits | 27400000 |  |  |  | -1677895.1678 | -571772.7189 | 328779.791 | 3106268.8796 | 1579562.1341 | 1713805.6849 | 1750303.8233 | 1792829.3169 | 1841366.1481 | 1895918.0654 | 7167612.4755 | 2023178.4406 | 2095989.668 | 2175021.0073 | 2260369.9341 | 2352152.1307 | 2450501.4569 | 2555569.9825 | 2667528.0796 | 2786564.5735 | 2912886.953 | 3046721.6371 | 3188314.2998 | 3337930.2518 | 3495854.88 | 3662394.1433
| IRR | 51.97%
| BCR | 4.1494

## Summary Phase B - No Cat C
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY | [5 empty] | ESTIMATE TYPE: | Feasability
[9 empty] | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
|  | Trade: | Mechanical/Electrical/Structural |  | Assumptions:
[5 empty] | NatGas Inflation Rate | 5%
[5 empty] | General Inflation Rate | 3% | [32 empty] | 25-Yr NPV Sensitivity Analysis (In thousands)
[5 empty] | Discount Rate | 7%
[5 empty] | Ton Red Rate | -9.5% | [30 empty] | Natural Gas Inflation Rate |  | Discount Rate
| Summary Table - Phase B (No Category C) |  |  |  | Finance Rate | 3% | 40 | yr | [29 empty] | 16600 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
[38 empty] | 1% | 16000 | 13900 | 12200 | 10600 | 9500 | 8300 | 7300 | 6400
|  | NPV (25 Year) |  | Notes | Estimated First Cost | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | [6 empty] | 2% | 18400 | 16000 | 14000 | 12200 | 10900 | 9500 | 8400 | 7400
Costs | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 3% | 21300 | 18500 | 16200 | 14100 | 12500 | 10900 | 9700 | 8500
| Design and Planning | 1300000 |  | ~10% Construction | 1300000 | 0: 1300000 |  | 4% | 24600 | 21400 | 18700 | 16200 | 14400 | 12600 | 11100 | 9700
| Central Plant Investment | 0 |  | Per CHA Estimate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 5% | 28600 | 24800 | 21600 | 18800 | 16600 | 14500 | 12800 | 11200
| Distribution Piping Investment | 7200000 |  | Per CHA Estimate $53M financing over 40yr | 13310000 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 | 571772.7189 |  |  | 6% | 33300 | 28800 | 25000 | 21700 | 19100 | 16700 | 14700 | 12900
| Central Plant O&M | 1500000 |  | ($30k 0.5FTE operator, $188k electric, $14k O&M, $30k other G&A), ration of total buildings | 101591.8367 |  |  | 101591.8367 | 104639.5918 | 107778.7796 | 111012.143 | 114342.5073 | 117772.7825 | 121305.966 | 124945.1449 | 128693.4993 | 132554.3043 | 136530.9334 | 140626.8614 | 144845.6672 | 149191.0373 | 153666.7684 | 158276.7714 | 163025.0746 | 167915.8268 | 172953.3016 | 178141.9007 | 183486.1577 | 188990.7424 | 194660.4647 | 200500.2786 | 206515.287 | 212710.7456 | 219092.068 | 225664.83 |  |  | 7% | 38900 | 33500 | 29100 | 25200 | 22100 | 19200 | 16900 | 14800
| District Connections to Customer Bldgs | 300000 |  | ($15k/building, 19 total) | 285000 | 2: 100785.5; 3: 103809.065; 4: 103809.065 |  | 8% | 45500 | 39100 | 33800 | 29200 | 25600 | 22300 | 19500 | 17100
| NYSERDA Category B&C Award | -200000 |  | PON 4641 Category B&C | -193877.551 | 0: -193877.551
| Total (NPV) | 10100000 |  |  | 14802714.2857 | 1677895.1678 | 571772.7189 | 774150.0556 | 780221.3757 | 783360.5635 | 682784.8618 | 686115.2261 | 689545.5014 | 693078.6848 | 696717.8638 | 700466.2182 | 704327.0231 | 708303.6523 | 712399.5803 | 716618.3861 | 720963.7561 | 725439.4872 | 730049.4903 | 734797.7934 | 739688.5457 | 744726.0205 | 749914.6195 | 755258.8765 | 760763.4613 | 766433.1835 | 772272.9975 | 778288.0058 | 784483.4645 | 790864.7868 | 797437.5489 |  |  |  | Discount Rate
[38 empty] | 16600 | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
Direct Benefits |  |  |  |  | Per year estimate | [31 empty] | Finance Rate | 2% | 30200 | 26300 | 22900 | 20000 | 17700 | 15600 | 13800 | 12100
| Avoided Customer O&M | 3000000 |  | Per App C (Baseline Equipment - Towers and Boilers) | 189000 |  |  | 103262.7015 | 212721.1651 | 219102.8 | 225675.884 | 232446.1606 | 239419.5454 | 246602.1317 | 254000.1957 | 261620.2016 | 269468.8076 | 277552.8718 | 285879.458 | 294455.8417 | 303289.517 | 312388.2025 | 321759.8486 | 331412.644 | 341355.0234 | 351595.6741 | 362143.5443 | 373007.8506 | 384198.0861 | 395724.0287 | 407595.7496 | 419823.6221 | 432418.3307 | 445390.8806 | 458752.6071 |  |  | 2.5% | 29400 | 25500 | 22200 | 19400 | 17100 | 15100 | 13300 | 11700
| Avoided Customer Equipment Recondition | 5800000 |  | Per App D (10% tower and boiler/yr) | 364000 |  |  | 198876.314 | 409685.2068 | 421975.763 | 434635.0359 | 447674.087 | 461104.3096 | 474937.4389 | 489185.5621 | 503861.1289 | 518976.9628 | 534546.2717 | 550582.6598 | 567100.1396 | 584113.1438 | 601636.5381 | 619685.6343 | 638276.2033 | 657424.4894 | 677147.2241 | 697461.6408 | 718385.4901 | 739937.0548 | 762135.1664 | 784999.2214 | 808549.198 | 832805.674 | 857789.8442 | 883523.5395 |  |  | 3% | 28600 | 24800 | 21600 | 18800 | 16600 | 14500 | 12800 | 11200
| Customer Energy Savings | 17900000 |  | Per App D eliminating customer gas heat, 25% cooling efficiency increase | 872700 |  |  | 476811.4265 | 1060772.3044 | 1113810.9196 | 1169501.4656 | 1227976.5389 | 1289375.3658 | 1353844.1341 | 1421536.3408 | 1492613.1578 | 1567243.8157 | 1645606.0065 | 1727886.3068 | 1814280.6222 | 1904994.6533 | 2000244.3859 | 2100256.6052 | 2205269.4355 | 2315532.9073 | 2431309.5526 | 2552875.0303 | 2680518.7818 | 2814544.7209 | 2955271.9569 | 3103035.5548 | 3258187.3325 | 3421096.6991 | 3592151.5341 | 3771759.1108 |  |  | 3.5% | 27700 | 24000 | 20900 | 18200 | 16000 | 14000 | 12300 | 10800
| Total Direct Benefits | 26700000 |  |  | 1425700 | 0 | 0 | 778950.442 | 1683178.6763 | 1754889.4827 | 1829812.3856 | 1908096.7864 | 1989899.2208 | 2075383.7047 | 2164722.0986 | 2258094.4883 | 2355689.5861 | 2457705.15 | 2564348.4247 | 2675836.6036 | 2792397.3141 | 2914269.1266 | 3041702.0881 | 3174958.2829 | 3314312.4201 | 3460052.4508 | 3612480.2154 | 3771912.1224 | 3938679.8618 | 4113131.152 | 4295630.5257 | 4486560.1526 | 4686320.7038 | 4895332.2589 | 5114035.2574 |  |  | 4% | 26800 | 23200 | 20100 | 17500 | 15400 | 13400 | 11800 | 10300
[38 empty] | 4.5% | 25900 | 22400 | 19400 | 16800 | 14700 | 12800 | 11200 | 9800
| Net Direct Benefits | 16600000 |  |  |  | -1677895.1678 | -571772.7189 | 4800.3864 | 902957.3006 | 971528.9192 | 1147027.5237 | 1221981.5603 | 1300353.7195 | 1382305.0199 | 1468004.2348 | 1557628.2702 | 1651362.563 | 1749401.4978 | 1851948.8444 | 1959218.2174 | 2071433.558 | 2188829.6394 | 2311652.5978 | 2440160.4894 | 2574623.8744 | 2715326.4303 | 2862565.5959 | 3016653.2459 | 3177916.4005 | 3346697.9685 | 3523357.5282 | 3708272.1467 | 3901837.2394 | 4104467.4721 | 4316597.7085 |  |  | 5% | 24900 | 21500 | 18600 | 16100 | 14100 | 12200 | 10700 | 9200
| IRR | 32.48%
| BCR | 2.6436
Indirect Benefits
| Carbon Reduction Social Benefit | 4500000 |  | $125/ton value NYS-DEC Guidance per evaluation | 800000 |  |  | 323979.4047 | 652291.1708 | 608033.2149 | 566778.1612 | 528322.263 | 492475.5974 | 459061.1282 | 427913.8306 | 398879.8772 | 371815.8775 | 346588.1702 | 323072.1629 | 301151.7166 | 280718.5727 | 261671.8175 | 243917.3847 | 227367.5901 | 211940.6992 | 197560.5227 | 184156.0412 | 171661.0539 | 160013.8513 | 149156.9115 | 139036.6151
| Avoided Electrical Substation Upgrades | 4900000 |  |  | 5211104.3281 | [10 empty] | 5211104.3281
| Total Indirect Benefits | 9400000
| Net Direct + Indirect Benefits | 26000000 |  |  |  | -1677895.1678 | -571772.7189 | 328779.791 | 1555248.4714 | 1579562.1341 | 1713805.6849 | 1750303.8233 | 1792829.3169 | 1841366.1481 | 1895918.0654 | 7167612.4755 | 2023178.4406 | 2095989.668 | 2175021.0073 | 2260369.9341 | 2352152.1307 | 2450501.4569 | 2555569.9825 | 2667528.0796 | 2786564.5735 | 2912886.953 | 3046721.6371 | 3188314.2998 | 3337930.2518 | 3495854.88 | 3662394.1433
| IRR | 44.93%
| BCR | 3.5743

## Central Plant
|  | CLIENT: | NYSERDA | [5 empty] | PROJECT NO.: | 65290
|  | PROJECT: | Syracuse Community Thermal | [5 empty] | PREPARED DATE: | 2021-02-23
|  | LOCATION: | Syracuse, NY |  | Material Multiplier | Labor Rate |  |  | ESTIMATE TYPE: | Feasability
[5 empty] | 100% | 85 |  |  | ESTIMATED BY: | BH
|  | ENGINEER: | CHA | [5 empty] | CHECKED BY: | RSV
|  | ARCHITECT: | None
Central Plant Cost Estimate |  | Trade: | Mechanical/Electrical/Structural
Reference | DESCRIPTION | QUANTITY | UNIT | Unit Price |  |  | Subtotals |  |  | TOTAL
|  |  |  | Material | Labor Hours | Item Cost | Material | Labor | Item Cost | AMOUNT
Buildling
| Prefabricated Metal Panel Building | 20000 | sf |  |  | 350 |  |  | 7000000 | 7000000 | Building shell, basic electrical, HVAC, plumbing, storm, strucutral, concrete pad.
| Strucutral Foundation | 20000 | sf |  |  | 133 |  |  | 2660000 | 2660000
Mechanical
| 2000T Centrifugal Chiller (7.9 MW Heat Pumps) | 4 | EA | 750000 | 400 |  | 3000000 | 136000 | 0 | 3140000
| Heat Exchanger - 5000 gpm | 6 | EA | 135000 | 120 |  | 810000 | 61200 | 0 | 870000
| Outfall Pumps - 7500 gpm, 125 hp | 5 | EA | 34789 | 40 |  | 173945 | 17000 | 0 | 190000
| Loop Pump - 6000 gpm, 300 hp | 6 | EA | 31607 | 40 |  | 189642 | 20400 | 0 | 210000
| 30" Steel Pipe | 300 | LF | 284 | 3 |  | 85200 | 76500 | 0 | 160000
| Fittings | 30% | p | [5 empty] | 48000 | 50000
| 20" Steel Pipe | 300 | LF | 215 | 2.67 |  | 64500 | 68085 | 0 | 130000
| Fittings | 30% | p |  |  |  | 0 | 0 | 39000 | 40000
| Control Valves | 20 | EA | 3000 | 8 |  | 60000 | 13600 | 0 | 70000
| Air Seperator - 22" | 1 | LS | 23313 | 8 |  | 23313 | 680 | 0 | 20000
| Expansion Tank - B&G B5000 | 1 | LF | 26942 | 8 |  | 26942 | 680 | 0 | 30000
| HVAC System | 20000 | SF |  |  | 10 | 0 | 0 | 200000 | 200000
| Chemical Treatment System | 6000 | Ton |  | 40 | 2 | 0 | 3400 | 12000 | 20000
| Outfall Connection | 1 | LS |  |  | 500000 | 0 | 0 | 500000 | 500000
| HVAC Controls | 1 | LS |  |  | 300000 |  |  | 300000 | 300000
Electrical Service
| 13.2 kV Line Extension | 2500 | LF |  |  | 200 |  |  | 500000 | 500000
| 5 MVA Transformer | 1 | EA |  |  | 300000 |  |  | 300000 | 300000
| Main Fuse Switch | 1 | EA | 30000 | 20000 |  | 30000 | 20000 | 0 | 50000
| Switchgear Breakers - MCC | 24 | EA |  |  | 30000 | 0 | 0 | 720000 | 720000
| Equipment Connections | 24 | EA |  |  | 5000 |  |  | 120000 | 120000
| 700kW Generator | 1 | LS |  |  | 400000 |  |  | 400000 | 400000
| Comissioning | 1 | LS |  |  | 50000 |  |  | 50000 | 50000
[7 empty] | 0 | 0 | 0 | 0
[9 empty] | Sub-Total | 17700000
[8 empty] | Overhead | 10% | 1800000
[8 empty] | Profit | 5% | 900000
[8 empty] | Contingency | 20% | 4100000
[9 empty] | Total | 24500000

## Probable Cost
Probable Costs
Full Build Out
Item | Opinion of Cost
Central Plant | 20400000
Distribution Piping | 43950000
District Connections to Customer Bldgs | 750000
Construction Subtotal | 65100000
Construction Contingency | 12890000
Engineering Design and Planning | 7700000
Total Project Cost | 85690000
Initial Build Out (Phase C - Inner Harbor) | 12 Buildings
Item | Opinion of Cost
Central Plant | 20400000
Distribution Piping | 3990000
District Connections to Customer Bldgs | 180000
Construction Subtotal | 24570000
Construction Contingency | 4900000
Engineering Design and Planning | 2930000
Total Project Cost | 32400000
Phase A - Fayette Street | 11 Buildings
Item | Opinion of Cost
Central Plant | 0
Distribution Piping | 29270000
District Connections to Customer Bldgs | 170000
Construction Subtotal | 29440000
Construction Contingency | 5850000
Engineering Design and Planning | 3510000
Total Project Cost | 38800000
Phase B - Branches off Fayette Street | 26 Buildings
Item | Opinion of Cost
Central Plant | 0
Distribution Piping | 11090000
District Connections to Customer Bldgs | 390000
Construction Subtotal | 11480000
Construction Contingency | 2220000
Engineering Design and Planning | 1330000
Total Project Cost | 15030000

## Loop
Syracuse District Loop Costs
[6 empty] | Phase A |  | Phase B |  | Phase C
| Item Description | Unit | QTY | Cost/Unit | Item Total | 59.06% |  | 24.59% |  | 16.35%
1 | Pipe Runs in Grass Areas | LF | 8447.2 | 932.33 | 7880000 | 5200 | 4850000 | 0 | 0 | 3247 | 3030000
2 | Pipe Runs in Roadway Areas | LF | 11407.2 | 2095.36 | 23900000 | 6525 | 13670000 | 4882 | 10230000 |  | 0
0
3 | Bore Locations | LF | 3390 | 2558.3127 | 8670000 | 3390 | 8670000 | 0 |  | 150 | 380000
0
4 | Mobilization | LS | 1 | 1500000 | 1500000 |  | 890000 |  | 370000 |  | 250000
0
5 | M&P of Traffic | Allowance | 1 | 1500000 | 1500000 |  | 890000 |  | 370000 |  | 250000
0
6 | Erosion Control | LS | 1 | 500000 | 500000 |  | 300000 |  | 120000 |  | 80000
|  |  |  | Construction Sub Total | 43950000 |  | 29270000 |  | 11090000 |  | 3990000
7 | Contingency |  | 20% |  | 8790000 |  | 5850000 |  | 2220000 |  | 800000
|  |  |  | Construction Total | 52740000 |  | 35120000 |  | 13310000 |  | 4790000
Line route from Lake, along R&R/Erie/LaFayette/State St.
LaFayette St all bored, no open cut other than pits
|  |  |  | 23244.4 | 2268.9336