## Bldg Info, Cost Est
Syracuse District Energy
Building Information & Operation and Maintenance Costs | [26 empty] | Tower Efficiency | 0.05 | kW/ton
[14 empty] | TOWERS | [5 empty] | BOILERS | [6 empty] | Cooling Hours | 3360
| Address | Square Feet | Space Type | Peak Cooling | Annual ton-hrs | Annual Cooling | FLC Towers |  | Open Towers |  | Peak Heating | Annual Heating |  | Recondition Cost | Tower Testing | Chemical Cost | Water Cost | Tower Service |  | Boiler Cost |  |  | # Boilers |  | Boiler Maint Cost
|  |  |  | (tons) |  | (kWh) | # | Est. Tons | # | Est. Tons | (MMBtu/hr) | (MMBtu) | [7 empty] | Equip | Install | Total |  |  |  | Phase | Tower Demand | Tower Energy
Phase A | [26 empty] | (kW) | (kWh)
Barclay Damon | 125 E Jefferson St | 330000 | Large Office | 309.742 | 352221.5995 | 1238762.9524 | 1 | 309.742 |  | 0 | 3582.0955 | 1460.7473 |  | 92922.6053 | 692 | 309.742 | 0 | 1000 |  | 89552387.5793 | 26865716.2738 | 116418103.8531 | 2x1500 MBH | 2 | 2000 | A | 15.4871 | 52036.659
State Tower | 109 S Warren St | 1200000 | Large Office | 1126.3346 | 1280805.8162 | 4504592.554 | 3 | 844.751 | 1 | 281.5837 | 13.0258 | 5311.8082 |  | 802513.4098 | 2768 | 1126.3346 | 194682.4841 | 4000 |  | 325645.0457 | 97693.5137 | 423338.5595 | 2 x 4500 MBH | 2 | 2000 | A | 56.3167 | 189224.2145
Courtyard Marriott | 300 W Fayette St | 40000 | Hotel | 70.5436 | 52730.834 | 185454.2815 | 1 | 35.2718 | 1 | 35.2718 | 0.98565 | 1420.059 |  | 15872.3014 | 1384 | 70.5436 | 8015.0868 | 2000 |  | 24641.3034 | 7392.391 | 32033.6944 | 2x1000 MBH | 2 | 2000 | A | 3.5272 | 11851.3184
US Social Security Admin | 110 Fayette St | 287000 | Large Office | 269.3817 | 306326.0577 | 1077348.3858 |  |  |  |  | 3.1153 | 1270.4075 |  | 0 | 0 | 0 | 0 | 0 |  | 77883.4401 | 23365.032 | 101248.4721 | 2x1000 MBH | 2 | 2000 | A | 0 | 0
M&T Bank | 101 S Salina St | 365000 | Large Office | 342.5934 | 389578.4358 | 1370146.9019 | 1 | 171.2967 | 1 | 171.2967 | 3.962 | 1615.675 |  | 77083.5249 | 1384 | 342.5934 | 59215.9222 | 2000 |  | 99050.3681 | 29715.1104 | 128765.4785 | 2x1500 MBH | 2 | 2000 | A | 17.1297 | 57555.6986
State Office Building | 333 E Washington St | 360000 | Large Office | 337.9004 | 384241.7449 | 1351377.7662 | 2 | 337.9004 |  | 0 | 3.9077 | 1593.5425 |  | 202740.2298 | 1384 | 337.9004 | 0 | 2000 |  | 97693.5137 | 29308.0541 | 127001.5678 | 2x1500 MBH | 2 | 2000 | A | 16.895 | 56767.2644
SU-Warehouse | 350 W Fayette St | 72000 | Medium Office | 148.44 | 134233.0089 | 472097.335 | 1 | 148.44 |  | 0 | 1.4208 | 1054.1906 |  | 44531.9983 | 692 | 148.44 | 0 | 1000 |  | 35520.2102 | 10656.0631 | 46176.2733 | 2x1000 MBH | 2 | 2000 | A | 7.422 | 24937.919
300 S State St | 300 S State St | 252910 | Large Office | 237.3844 | 269940.4991 | 949380.419 | 1 | 237.3844 |  | 0 | 2.7453 | 1119.5078 |  | 71215.3216 | 692 | 237.3844 | 0 | 1000 |  | 68632.4071 | 20589.7221 | 89222.1292 | 2x1000 MBH | 2 | 2000 | A | 11.8692 | 39880.5801
Key Bank Building | 201 S Warren St | 132000 | Large Office | 123.8968 | 140888.6398 | 495505.1809 |  |  |  |  | 1.4328 | 584.2989 |  | 0 | 0 | 0 | 0 | 0 |  | 35820.955 | 10746.2865 | 46567.2415 | 2x1000 MBH | 2 | 2000 | A | 0 | 0
100 East Washington St | 100 E Washington St | 50000 | Midrise Apartment | 82.6823 | 31084.3225 | 109323.5258 | 1 | 82.6823 |  | 0 | 0.92981 | 1189.2121 |  | 24804.6951 | 692 | 82.6823 | 0 | 1000 |  | 23245.2242 | 6973.5673 | 30218.7915 | 2x1000 MBH | 2 | 2000 | A | 4.1341 | 13890.6293
Ramboll | 333 W Washington St | 137000 | Large Office | 128.5899 | 146225.3307 | 514274.3166 | 2 | 128.5899 |  | 0 | 1.4871 | 606.4314 |  | 77153.9208 | 1384 | 128.5899 | 0 | 2000 |  | 37177.8094 | 11153.3428 | 48331.1522 | 2x1000 MBH | 2 | 2000 | A | 6.4295 | 21603.0978
City Hall | 233 E Washington St | 84555 | Medium Office | 174.3242 | 157639.8898 | 554419.3078 |  |  |  |  | 1.6686 | 1238.0151 |  | 0 | 0 | 0 | 0 | 0 |  | 41714.0469 | 12514.2141 | 54228.2609 | 2x1000 MBH | 2 | 2000 | A | 0 | 0
1 Lincoln Center | 110 W Fayette St | 367500 | Large Office | 344.94 | 392246.7812 | 1379531.4697 |  | 0 | 2 | 344.94 | 3.9892 | 1626.7413 |  | 103481.9923 | 1384 | 344.94 | 59621.5107 | 2000 |  | 99728.7953 | 29918.6386 | 129647.4338 | 2x1500 MBH | 2 | 2000 | A | 17.247 | 57949.9157
SUNY Oswego MetroCenter | 2 S Clinton St | 185530 | Large Office | 174.1407 | 198023.2526 | 696447.5471 |  | 0 | 2 | 174.1407 | 2.0139 | 821.2498 |  | 52242.2151 | 1384 | 174.1407 | 30099.5344 | 2000 |  | 50347.4378 | 15104.2313 | 65451.6691 | 2x1000 MBH | 2 | 2000 | A | 8.707 | 29255.6404
217 Montgomery St | 217 Montgomery St | 50000 | Medium Office | 103.0833 | 93217.3673 | 327845.3715 | 1 | 103.0833 |  | 0 | 0.98667 | 732.0768 |  | 30924.9988 | 692 | 103.0833 | 0 | 1000 |  | 24666.8126 | 7400.0438 | 32066.8564 | 2x500 MBH | 2 | 2000 | A | 5.1542 | 17317.9993
City Hall Commons | 201 E Washington St | 52957 | Medium Office | 109.1797 | 98730.2424 | 347234.1468 | 1 | 109.1797 |  | 0 | 1.045 | 775.3718 |  | 32753.9033 | 692 | 109.1797 | 0 | 1000 |  | 26125.6079 | 7837.6824 | 33963.2903 | 2x500 MBH | 2 | 2000 | A | 5.459 | 18342.1858
Salinas Place | 205 S Salina St | 50000 | Midrise Apartment | 74.8784 | 46126.9046 | 162228.2695 | 1 | 74.8784 |  | 0 | 0.65078 | 903.4281 |  | 22463.5251 | 692 | 74.8784 | 0 | 1000 |  | 16269.4963 | 4880.8489 | 21150.3451 | 2x500 MBH | 2 | 2000 | A | 3.7439 | 12579.574
SU-Peck Hall | 601 E Genesee St | 25920 | Medium Office | 53.4384 | 48323.8832 | 169955.0406 | 1 | 53.4384 |  | 0 | 0.51149 | 379.5086 |  | 16031.5194 | 692 | 53.4384 | 0 | 1000 |  | 12787.2757 | 3836.1827 | 16623.4584 | 2x500 MBH | 2 | 2000 | A | 2.6719 | 8977.6509
Phase B
Atrium | 2 Clinton Sq | 170000 | Large Office | 159.5641 | 181447.4906 | 638150.6118 |  |  |  |  | 1.8453 | 752.5062 |  | 0 | 0 | 0 | 0 | 0 |  | 46133.0481 | 13839.9144 | 59972.9626 | 2x1500 MBH | 2 | 2000 | B | 0 | 0
AXA Towers | 100 Madison St | 653177 | Large Office | 613.0799 | 697160.7505 | 2451913.5422 |  | 0 | 3 | 613.0799 | 7.0901 | 2891.2924 |  | 275885.9481 | 2076 | 613.0799 | 105968.4341 | 3000 |  | 177253.2117 | 53175.9635 | 230429.1752 | 3x2000 MBH | 3 | 3000 | B | 30.654 | 102997.4206
Hotel Syracuse | 100 E Onondaga St | 720000 | Hotel | 1269.7841 | 949155.0126 | 3338177.0664 | 1 | 1269.7841 |  | 0 | 17.7417 | 25561.0628 |  | 380935.2331 | 692 | 1269.7841 | 0 | 1000 |  | 443543.4606 | 133063.0382 | 576606.4988 | 4x5000 MBH | 4 | 4000 | B | 63.4892 | 213323.7305
Tech Garden | 235 Harrison St | 35550 | Medium Office | 73.2922 | 66277.5481 | 233098.0591 |  | 0 | 1 | 73.2922 | 0.70152 | 520.5066 |  | 10993.8371 | 692 | 73.2922 | 10074.1873 | 1000 |  | 17538.1038 | 5261.4311 | 22799.5349 | 2x500 MBH | 2 | 2000 | B | 3.6646 | 12313.0975
Bank of America | 1 S Clinton St | 45000 | Midrise Apartment | 107.3384 | 40417.6807 | 142148.9355 |  |  |  |  | 1.4263 | 1336.9322 |  | 0 | 0 | 0 | 0 | 0 |  | 35657.7467 | 10697.324 | 46355.0707 | 2x500 MBH | 2 | 2000 | B | 0 | 0
Clinton Exchange | 101 N Clinton St | 180000 | Large Office | 168.9502 | 192120.8724 | 675688.8831 | 3 | 168.9502 |  | 0 | 1.9539 | 796.7712 |  | 152055.1724 | 2076 | 168.9502 | 0 | 3000 |  | 48846.7569 | 14654.0271 | 63500.7839 | 2x1000 MBH | 2 | 2000 | B | 8.4475 | 28383.6322
National Grid | 300 W Erie Blvd | 511200 | Large Office | 479.8185 | 545623.2777 | 1918956.428 | 4 | 479.8185 |  | 0 | 5.549 | 2262.8303 |  | 575782.2528 | 2768 | 479.8185 | 0 | 4000 |  | 138724.7895 | 41617.4368 | 180342.2263 | 3x1500 MBH | 3 | 3000 | B | 23.9909 | 80609.5154
Post Standard | 101 N Salina St | 179000 | Large Office | 168.0116 | 191053.5342 | 671935.056 | 2 | 168.0116 |  | 0 | 1.943 | 792.3447 |  | 100806.9476 | 1384 | 168.0116 | 0 | 2000 |  | 48575.386 | 14572.6158 | 63148.0018 | 2x1500 MBH | 2 | 2000 | B | 8.4006 | 28225.9453
Galleries of Syracuse | 441 S Salina St | 219000 | Large Office | 205.5561 | 233747.0615 | 822088.1411 |  |  |  |  | 2.3772 | 969.405 |  | 0 | 0 | 0 | 0 | 0 |  | 59430.2208 | 17829.0663 | 77259.2871 | 2x1500 MBH | 2 | 2000 | B | 0 | 0
100 Clinton Sq | 100 Clinton Sq | 120000 | Large Office | 112.6335 | 128080.5816 | 450459.2554 |  |  |  |  | 1.3026 | 531.1808 |  | 0 | 0 | 0 | 0 | 0 |  | 32564.5046 | 9769.3514 | 42333.8559 | 2x500 MBH | 2 | 2000 | B | 0 | 0
City of Syr Criminal Court House | 505 S State St | 95977 | Medium Office | 197.8726 | 178934.4652 | 629312.3044 |  |  |  |  | 1.894 | 1405.2507 |  | 0 | 0 | 0 | 0 | 0 |  | 47348.9336 | 14204.6801 | 61553.6136 | 2x1000 MBH | 2 | 2000 | B | 0 | 0
550 Harrison Building | 550 Harrison St | 252000 | Retail | 0 | 0 | 0 |  |  |  |  | 13.4892 | 9975.473 |  | 0 | 0 | 0 | 0 | 0 |  | 337229.134 | 101168.7402 | 438397.8742 | 4x5000 MBH | 4 | 4000 | B | 0 | 0
Jefferson Clinton Hotel | 416 S Clinton St | 42204 | Hotel | 74.4305 | 55636.303 | 195672.8124 |  |  |  |  | 1.04 | 1498.3043 |  | 0 | 0 | 0 | 0 | 0 |  | 25999.0392 | 7799.7118 | 33798.7509 | 2x1000 MBH | 2 | 2000 | B | 0 | 0
Sky Armory | 351 S Clinton St | 40700 | Medium Office | 83.9098 | 75878.937 | 266866.1324 |  |  |  |  | 0.80315 | 595.9105 |  | 0 | 0 | 0 | 0 | 0 |  | 20078.7855 | 6023.6356 | 26102.4211 | 2x500 MBH | 2 | 2000 | B | 0 | 0
Clinton Plaza | 550 S Clinton St | 254690 | Midrise Apartment | 307.4038 | 111392.1426 | 391766.0348 |  |  |  |  | 2.6242 | 5051.5213 |  | 0 | 0 | 0 | 0 | 0 |  | 65605.8474 | 19681.7542 | 85287.6016 | 3x2500 MBH | 3 | 3000 | B | 0 | 0
MOST | 500 S Franklin St | 40000 | Medium Office | 82.4667 | 74573.8938 | 262276.2972 | 1 | 82.4667 |  | 0 | 0.78934 | 585.6614 |  | 24739.9991 | 692 | 82.4667 | 0 | 1000 |  | 19733.4501 | 5920.035 | 25653.4852 | 2x500 MBH | 2 | 2000 | B | 4.1233 | 13854.3995
600 Montgomery St | 600 Montgomery St | 36684 | Medium Office | 75.6302 | 68391.718 | 240533.5922 | 1 | 50 |  | 0 | 0.7239 | 537.1101 |  | 15000 | 692 | 75.6302 | 0 | 1000 |  | 18097.5471 | 5429.2641 | 23526.8112 | 2x500 MBH | 2 | 2000 | B | 3.7815 | 12705.8698
Medical Office Bldg | 475 Irving Ave | 25056 | Retail | 0 | 0 | 0 |  |  |  |  | 1.3412 | 991.847 |  | 0 | 0 | 0 | 0 | 0 |  | 33530.211 | 10059.0633 | 43589.2743 | 2x1500 MBH | 2 | 2000 | B | 0 | 0
Phase C
Parcel 1 | Inner Harbor | 180000 | Medium Office | 453.6785 | 305260.3456 | 1073600.2776 |  |  |  |  | 5.1499 | 4132.0969 |  | 0 | 0 | 0 | 0 | 0 |  | 128746.515 | 38623.9545 | 167370.4695 | 2x5000 MBH | 2 | 2000 | C | 0 | 0
Parcel 2 | Inner Harbor | 120000 | Retail | 268.2646 | 146427.5484 | 514985.5159 |  |  |  |  | 3.1437 | 2962.4298 |  | 0 | 0 | 0 | 0 | 0 |  | 78591.8102 | 23577.5431 | 102169.3533 | 3x1500 MBH | 3 | 3000 | C | 0 | 0
Parcel 3 | Inner Harbor | 45000 | Midrise Apartment | 89.0471 | 33505.5749 | 117839.0676 |  |  |  |  | 1.0988 | 1188.7981 |  | 0 | 0 | 0 | 0 | 0 |  | 27470.4995 | 8241.1499 | 35711.6494 | 2x1500 MBH | 2 | 2000 | C | 0 | 0
Parcel 4 | Inner Harbor | 110000 | Retail | 245.9092 | 134225.2527 | 472070.0563 |  |  |  |  | 2.8817 | 2715.5607 |  | 0 | 0 | 0 | 0 | 0 |  | 72042.4927 | 21612.7478 | 93655.2405 | 2x3000 MBH | 2 | 2000 | C | 0 | 0
Parcel 5 | Inner Harbor | 30000 | Midrise Apartment | 59.3647 | 22337.0499 | 78559.3784 |  |  |  |  | 0.73255 | 792.5321 |  | 0 | 0 | 0 | 0 | 0 |  | 18313.6663 | 5494.0999 | 23807.7662 | 2x1000 MBH | 2 | 2000 | C | 0 | 0
Parcel 6 | Inner Harbor | 225000 | Midrise Apartment | 271.5688 | 98406.8164 | 346096.658 |  |  |  |  | 2.3183 | 4462.6498 |  | 0 | 0 | 0 | 0 | 0 |  | 57957.9711 | 17387.3913 | 75345.3624 | 3x2000 MBH | 3 | 3000 | C | 0 | 0
Parcel 7 | Inner Harbor | 320000 | Retail | 715.3722 | 390473.4623 | 1373294.7092 |  |  |  |  | 8.3831 | 7899.8129 |  | 0 | 0 | 0 | 0 | 0 |  | 209578.1606 | 62873.4482 | 272451.6088 | 3x3000 MBH | 3 | 3000 | C | 0 | 0
Parcel 8 | Inner Harbor | 120000 | Midrise Apartment | 144.8367 | 52483.6354 | 184584.8843 |  |  |  |  | 1.2364 | 2380.0799 |  | 0 | 0 | 0 | 0 | 0 |  | 30910.9179 | 9273.2754 | 40184.1933 | 2x1500 MBH | 2 | 2000 | C | 0 | 0
Parcel 9 | Inner Harbor | 60000 | Midrise Apartment | 118.7295 | 44674.0998 | 157118.7567 |  |  |  |  | 1.4651 | 1585.0642 |  | 0 | 0 | 0 | 0 | 0 |  | 36627.3327 | 10988.1998 | 47615.5325 | 2x1500 MBH | 2 | 2000 | C | 0 | 0
Parcel 10 | Inner Harbor | 160000 | Midrise Apartment | 193.1156 | 69978.1806 | 246113.179 |  |  |  |  | 1.6486 | 3173.4399 |  | 0 | 0 | 0 | 0 | 0 |  | 41214.5572 | 12364.3672 | 53578.9244 | 3x1500 MBH | 3 | 3000 | C | 0 | 0
Parcel 11 | Inner Harbor | 270000 | Retail | 603.5953 | 329461.9838 | 1158717.4109 |  |  |  |  | 7.0733 | 6665.4671 |  | 0 | 0 | 0 | 0 | 0 |  | 176831.573 | 53049.4719 | 229881.0449 | 3x4000 MBH | 3 | 3000 | C | 0 | 0
Parcel 12 | Inner Harbor | 85000 | Classroom | 211.4946 | 94491.5674 | 332326.7316 |  |  |  |  | 2.6418 | 1613.4142 |  | 0 | 0 | 0 | 0 | 0 |  | 66043.7699 | 19813.131 | 85856.9008 | 3x1500 MBH | 3 | 3000 | C | 0 | 0
*Parcel Buildings are not constructed yet |  | 9387610 |  | 12092.2855 |  | 35290274.5495 |  |  |  | Total Peak Load | 153126.7599 | MBH |  | 3202935.5511 | 27680 | 6574.9045 | 467677.1596 | 40000 |  | 93209556.7715 | 27962867.0314 | 121172423.8029 |  |  | 109000 |  | Total | 1104583.958
|  | 0.21305 | [24 empty] | Total Cost | 93889.6364
[12 empty] | 120329.5279 | A | 1666736.161 | 16608 | 3643.8711 | 351634.5382 | 24000 | A | 90649337.3287 | 27194801.1986 | 117844138.5273 |  |  | 36000
[12 empty] | 150411.9098 | B | 1536199.3901 | 11072 | 2931.0334 | 116042.6214 | 16000 | B | 1615890.1765 | 484767.053 | 2100657.2295 |  |  | 43000
[13 empty] | C | 0 | 0 | 0 | 0 | 0 | C | 944329.2663 | 283298.7799 | 1227628.0461 |  |  | 30000 | Buildings Per Phase
[26 empty] | A | 18
[23 empty] | Total Annual O&M |  | 650932.0641 | B | 18
[24 empty] | A | 431886.4093 | C | 12
[24 empty] | B | 189045.6548
[24 empty] | C | 30000

## Baseline Electrification
Syracuse District Energy
Electrification Option per Baseline Building | [20 empty] | Electrified System
[14 empty] | Heating | [6 empty] | Approx Height | Electrified Heating System | Peak Heating
| Address | Square Feet | Space Type | Peak Cooling | Annual ton-hrs | Annual Cooling | FLC Towers |  | Open Towers |  | Peak Heating |  | Load | Natrual Gas | Electric | Existing System |  |  | WWTP HX Energy Reduction % |  |  |  | Boiler | New Heat Pump | NG Boiler HP to Elec Boiler | Replacement Cost
|  |  |  | (tons) |  | (kWh) | # | Est. Tons | # | Est. Tons | (MMBtu/hr) | (MBH) | (MMBtu) | (MMBtu) | kWh | Heating | Cooling | Confidence (1-3) |  |  | (stories) |  | (kW) | (kW) | (kW) | Equipment | Install | A @ 460/3 |  | New Heat Pump COP |  | 2.5
Barclay Damon | 125 E Jefferson St | 330000 | Large Office | 309.742 | 352221.5995 | 1238762.9524 | 1 | 309.742 |  | 0 | 3582.0955 | 3582095.5032 | 1460.7473 | 1095.5604 | 106998.7733 | Heat Pump | Heat Pump | 2 | 35% | 278.7678 | 13 | Electric boiler |  |  | 787353.5468 | 118103032.0254 | 29525758.0063 | 988214.7439 |  | Existing Heat Pump COP |  | 4
State Tower | 109 S Warren St | 1200000 | Large Office | 1126.3346 | 1280805.8162 | 4504592.554 |  |  |  |  | 13.0258 | 13025.8018 | 5311.8082 | 3983.8561 | 389086.4482 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 1013.7011 |  | Electric boiler |  |  | 2863.1038 | 429465.571 | 107366.3928 | 3593.5082 |  | Conversion |  | 293.07 | kWh per MMBtu
Courtyard Marriott | 300 W Fayette St | 40000 | Hotel | 70.5436 | 52730.834 | 185454.2815 | 1 | 35.2718 | 1 | 35.2718 | 0.98565 | 985.6521 | 1420.059 | 1065.0443 | 104018.3887 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 63.4892 | 23 | Electric boiler |  |  | 216.6488 | 32497.3205 | 8124.3301 | 271.9179
US Social Security Admin | 110 Fayette St | 287000 | Large Office | 269.3817 | 306326.0577 | 1077348.3858 | 0 | 0 | 0 | 0 | 3.1153 | 3115.3376 | 1270.4075 | 952.8056 | 93056.5089 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 242.4435 | 7 | Electric boiler |  |  | 684.759 | 102713.8491 | 25678.4623 | 859.4474 |  | Total Demands
M&T Bank | 101 S Salina St | 365000 | Large Office | 342.5934 | 389578.4358 | 1370146.9019 |  |  |  |  | 3.962 | 3962.0147 | 1615.675 | 1211.7562 | 118347.128 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 308.3341 |  | Electric boiler |  |  | 870.8607 | 130629.1112 | 32657.2778 | 1093.0254 |  |  | Electric Boiler | Heat Pump
State Office Building | 333 E Washington St | 360000 | Large Office | 337.9004 | 384241.7449 | 1351377.7662 | 2 | 337.9004 | 0 | 0 | 3.9077 | 3907.7405 | 1593.5425 | 2124.7233 | 0 | Boiler | Heat Pump | 3 | 28% | 304.1103 | 10 | Electric boiler | 1145.2415 |  |  | 171786.2284 | 42946.5571 | 1437.4033 |  | Downtown | #REF! | 960.6608
SU-Warehouse | 350 W Fayette St | 72000 | Medium Office | 148.44 | 134233.0089 | 472097.335 | 1 | 148.44 |  | 0 | 1.4208 | 1420.8084 | 1054.1906 | 790.6429 | 77218.7647 | Heat Pump? | Heat Pump & Water Cooled Chiller | 2 | 28% | 133.596 |  | Electric boiler |  |  | 312.2972 | 46844.586 | 11711.1465 | 391.9672 |  | Inner Harbor |  | 4585.3004
300 S State St | 300 S State St | 252910 | Large Office | 237.3844 | 269940.4991 | 949380.419 | 1 | 237.3844 |  | 0 | 2.7453 | 2745.2963 | 1119.5078 | 839.6309 | 82003.2113 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 3 | 35% | 213.646 |  | Electric boiler |  |  | 603.423 | 90513.448 | 22628.362 | 757.3618
Key Bank Building | 201 S Warren St | 132000 | Large Office | 123.8968 | 140888.6398 | 495505.1809 | 0 | 0 |  | 0 | 1.4328 | 1432.8382 | 584.2989 | 438.2242 | 42799.5093 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 3 | 35% | 111.5071 | 10 | Electric boiler |  |  | 314.9414 | 47241.2128 | 11810.3032 | 395.2859
100 East Washington St | 100 E Washington St | 50000 | Midrise Apartment | 82.6823 | 31084.3225 | 109323.5258 |  |  |  |  | 0.92981 | 929.809 | 1189.2121 | 1585.6161 | 0 | NG Boiler | Water Cooled Chiller | 2 | 28% | 74.4141 | 2 | Heat pump |  | 108.9996 |  | 37277.8788 | 9319.4697 | 54.7226
Ramboll | 333 W Washington St | 137000 | Large Office | 128.5899 | 146225.3307 | 514274.3166 | 2 | 128.5899 |  | 0 | 1.4871 | 1487.1124 | 606.4314 | 454.8236 | 44420.7028 | Heat Pump - Boiler | PTAC | 1 | 28% | 115.7309 |  | Electric boiler |  |  | 326.871 | 49030.6527 | 12257.6632 | 410.2588
City Hall | 233 E Washington St | 84555 | Medium Office | 174.3242 | 157639.8898 | 554419.3078 | 0 | 0 |  | 0 | 1.6686 | 1668.5619 | 1238.0151 | 928.5113 | 90683.7868 | Heat Pump |  | 2 | 35% | 156.8918 |  | Electric boiler |  |  | 366.7541 | 55013.1107 | 13753.2777 | 460.3164
1 Lincoln Center | 110 W Fayette St | 367500 | Large Office | 344.94 | 392246.7812 | 1379531.4697 |  |  |  |  | 3.9892 | 3989.1518 | 1626.7413 | 2168.9883 | 0 | (2) 1700 MBH NG steam boilers | (7) AHUs, (3) 7-265 T chillers | 2 | 28% | 310.446 | 12 | Electric boiler | 1169.1007 |  |  | 175365.1082 | 43841.277 | 1467.3492
SUNY Oswego MetroCenter | 2 S Clinton St | 185530 | Large Office | 174.1407 | 198023.2526 | 696447.5471 |  |  | 2 | 174.1407 | 2.0139 | 2013.8975 | 821.2498 | 1094.9997 | 0 | Boiler | Chiller | 3 | 28% | 156.7266 | 18 | Electric boiler | 590.2129 |  |  | 88531.9415 | 22132.9854 | 740.7817
217 Montgomery St | 217 Montgomery St | 50000 | Medium Office | 103.0833 | 93217.3673 | 327845.3715 |  |  | 0 | 0 | 0.98667 | 986.6725 | 732.0768 | 549.0576 | 53624.1421 | Heat Pump | Heat Pump & Water Cooled Chiller | 2 | 28% | 92.775 |  | Electric boiler |  |  | 216.8731 | 32530.9625 | 8132.7406 | 272.1994
City Hall Commons | 201 E Washington St | 52957 | Medium Office | 109.1797 | 98730.2424 | 347234.1468 | 1 | 109.1797 |  | 0 | 1.045 | 1045.0243 | 775.3718 | 581.5289 | 56795.4739 | Heat Pump - Boiler | Heat Pump | 2 | 35% | 98.2617 | 12 | Electric boiler |  |  | 229.699 | 34454.8436 | 8613.7109 | 288.2973
Salinas Place | 205 S Salina St | 50000 | Midrise Apartment | 74.8784 | 46126.9046 | 162228.2695 | 1 | 74.8784 |  | 0 | 0.65078 | 650.7799 | 903.4281 | 677.5711 | 66175.5116 | Heat Pump | Heat Pump | 2 | 35% | 67.3906 |  | Electric boiler |  |  | 143.043 | 21456.4557 | 5364.1139 | 179.5346
SU-Peck Hall | 601 E Genesee St | 25920 | Medium Office | 53.4384 | 48323.8832 | 169955.0406 | 1 | 53.4384 |  | 0 | 0.51149 | 511.491 | 379.5086 | 506.0115 | 0 | NG Condensing Boilers (9 300 MBH / 7 300 MBH) | Modified heat pump; 7-T AC | 3 | 35% | 48.0946 |  | Electric boiler | 149.9027 |  |  | 22485.4013 | 5621.3503 | 188.1442
Atrium | 2 Clinton Sq | 170000 | Large Office | 159.5641 | 181447.4906 | 638150.6118 |  |  | 0 | 0 | 1.8453 | 1845.3219 | 752.5062 | 1003.3415 | 0 | Boilers |  | 2 | 28% | 143.6077 | 19 | Electric boiler | 540.8085 |  |  | 81121.2745 | 20280.3186 | 678.7738
AXA Towers | 100 Madison St | 653177 | Large Office | 613.0799 | 697160.7505 | 2451913.5422 |  |  |  |  | 7.0901 | 7090.1285 | 2891.2924 | 3855.0566 | 0 | Natural Gas Steam Boilers | Water Cooled Chiller | 3 | 28% | 551.7719 | [5 empty] | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | #REF! |  | Electric boiler |  |  | #REF! | #REF! | #REF! | #REF! | Only hotel tower, new ballrooms are DX/NG RTUs
Hotel Syracuse | 100 E Onondaga St | 720000 | Hotel | 1269.7841 | 949155.0126 | 3338177.0664 |  |  | 0 | 0 | 17.7417 | 17741.7384 | 25561.0628 | 19170.7971 | 1872330.997 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 1142.8057 |  | Electric boiler |  |  | 3899.6785 | 584951.769 | 146237.9423 | 4894.5226
Tech Garden | 235 Harrison St | 35550 | Medium Office | 73.2922 | 66277.5481 | 233098.0591 |  |  |  |  | 0.70152 | 701.5242 | 520.5066 | 390.3799 | 38126.7651 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 65.963 | 6 | Electric boiler |  |  | 154.1968 | 23129.5144 | 5782.3786 | 193.5338
Bank of America | 1 S Clinton St | 45000 | Midrise Apartment | 107.3384 | 40417.6807 | 142148.9355 | 0 | 0 |  | 0 | 1.4263 | 1426.3099 | 1336.9322 | 1002.6992 | 97929.4037 | Heat Pump? |  | 3 | 35% | 96.6046 | 3 | Electric boiler |  |  | 313.5065 | 47025.9712 | 11756.4928 | 393.4849
Clinton Exchange | 101 N Clinton St | 180000 | Large Office | 168.9502 | 192120.8724 | 675688.8831 | 3 | 168.9502 |  | 0 | 1.9539 | 1953.8703 | 796.7712 | 1062.3616 | 0 | NG/RTU | Heat Pump | 2 | 35% | 152.0552 |  | Heat pump |  | 229.0483 |  | 78334.5202 | 19583.63 | 114.9923
National Grid | 300 W Erie Blvd | 511200 | Large Office | 479.8185 | 545623.2777 | 1918956.428 | 4 | 479.8185 |  | 0 | 5.549 | 5548.9916 | 2262.8303 | 1697.1227 | 165750.8269 | Heat Pump - Boiler | Heat Pump - Cooling Tower | 2 | 35% | 431.8367 | 2 | Electric boiler |  |  | 1219.6822 | 182952.3332 | 45738.0833 | 1530.8345 | Under Renovation
Post Standard | 101 N Salina St | 179000 | Large Office | 168.0116 | 191053.5342 | 671935.056 |  |  |  |  | 1.943 | 1943.0154 | 792.3447 | 1056.4596 | 0 | NG/RTU | Water Cooled Chiller | 2 | 28% | 151.2104 | 7 | Electric boiler | 569.4395 |  |  | 85415.9302 | 21353.9826 | 714.7088
Galleries of Syracuse | 441 S Salina St | 219000 | Large Office | 205.5561 | 233747.0615 | 822088.1411 |  |  |  |  | 2.3772 | 2377.2088 | 969.405 | 1292.54 | 0 | RTU - NG? | RTU? | 2 | 28% | 185.0005 | 5 | Heat pump |  | 278.6754 |  | 95306.9995 | 23826.7499 | 139.9073
100 Clinton Sq | 100 Clinton Sq | 120000 | Large Office | 112.6335 | 128080.5816 | 450459.2554 |  |  |  |  | 1.3026 | 1302.5802 | 531.1808 | 708.2411 | 0 | District Steam | District Chilled Water | 3 | 28% | 101.3701 | 4 |  |  |  |  | 0 | 0 | 0
City of Syr Criminal Court House | 505 S State St | 95977 | Medium Office | 197.8726 | 178934.4652 | 629312.3044 |  |  |  |  | 1.894 | 1893.9573 | 1405.2507 | 1873.6676 | 0 | Boiler? | Air Cooled Chiller | 2 | 28% | 178.0853 | 1 | Heat pump |  | 222.0248 |  | 75932.4923 | 18983.1231 | 111.4662
550 Harrison Building | 550 Harrison St | 252000 | Retail | 0 | 0 | 0 |  |  |  |  | 13.4892 | 13489.1654 | 9975.473 | 13300.6307 | 0 | Boiler | None | 2 | 28% | 0 | 11 | Electric boiler | 3953.2697 |  |  | 592990.4537 | 148247.6134 | 4961.7855
Jefferson Clinton Hotel | 416 S Clinton St | 42204 | Hotel | 74.4305 | 55636.303 | 195672.8124 |  |  |  |  | 1.04 | 1039.9616 | 1498.3043 | 1997.7391 | 0 | RTU | RTU | 2 | 28% | 66.9875 | 3 | Heat pump |  | 121.9126 |  | 41694.1142 | 10423.5285 | 61.2055
Sky Armory | 351 S Clinton St | 40700 | Medium Office | 83.9098 | 75878.937 | 266866.1324 |  |  |  |  | 0.80315 | 803.1514 | 595.9105 | 446.9329 | 43650.0517 | Heat Pump | PTAC | 1 | 28% | 75.5188 | 23 | Electric boiler |  |  | 176.5347 | 26480.2035 | 6620.0509 | 221.5703
Clinton Plaza | 550 S Clinton St | 254690 | Midrise Apartment | 307.4038 | 111392.1426 | 391766.0348 | 0 | 0 |  | 0 | 2.6242 | 2624.2339 | 5051.5213 | 3788.641 | 370020.6036 | Heat Pump |  | 1 | 35% | 276.6634 | 3 | Electric boiler |  |  | 576.8132 | 86521.9756 | 21630.4939 | 723.9636
MOST | 500 S Franklin St | 40000 | Medium Office | 82.4667 | 74573.8938 | 262276.2972 | 1 | 82.4667 |  | 0 | 0.78934 | 789.338 | 585.6614 | 439.2461 | 42899.3137 | Heat Pump - Boiler? | Heat Pump | 1 | 35% | 74.22 | 6 | Electric boiler |  |  | 173.4985 | 26024.77 | 6506.1925 | 217.7595 | 2001 FLC
600 Montgomery St | 600 Montgomery St | 36684 | Medium Office | 75.6302 | 68391.718 | 240533.5922 | 1 | 50 |  | 0 | 0.7239 | 723.9019 | 537.1101 | 402.8326 | 39342.9606 | Heat Pump - Boiler | Heat Pump | 2 | 35% | 68.0672 |  | Electric boiler |  |  | 159.1154 | 23867.3166 | 5966.8291 | 199.7073
Downtown |  | #REF! |  | #REF! | #REF! | #REF! |  |  |  |  | #REF! |  | #REF! | [6 empty] | #REF! |  |  | 8117.9756 | 960.6608 | #REF! | #REF! | #REF! |  | #REF!
Medical Office Bldg |  | 25056 | Retail | 0 | 0 | 0 |  |  |  |  | 1.3412 |  | 991.847 | [6 empty] | 0 |  | Heat pump |  | 157.2272 |  | 53771.6966 | 26885.8483 |  | Total
Parcel 1 |  | 180000 | Medium Office | 453.6785 | 305260.3456 | 1073600.2776 |  |  |  |  | 5.1499 |  | 4132.0969 | [6 empty] | 408.3106 |  | Heat pump |  | 603.7079 |  | 206468.0876 | 103234.0438
Parcel 2 |  | 120000 | Retail | 268.2646 | 146427.5484 | 514985.5159 |  |  |  |  | 3.1437 |  | 2962.4298 | [6 empty] | 241.4381 |  | Heat pump |  | 368.5264 |  | 126036.0388 | 63018.0194
Parcel 3 |  | 45000 | Midrise Apartment | 89.0471 | 33505.5749 | 117839.0676 |  |  |  |  | 1.0988 |  | 1188.7981 | [6 empty] | 80.1424 |  | Heat pump |  | 128.8125 |  | 44053.8643 | 22026.9321
Parcel 4 |  | 110000 | Retail | 245.9092 | 134225.2527 | 472070.0563 |  |  |  |  | 2.8817 |  | 2715.5607 | [6 empty] | 221.3183 |  | Heat pump |  | 337.8159 |  | 115533.0356 | 57766.5178
Parcel 5 |  | 30000 | Midrise Apartment | 59.3647 | 22337.0499 | 78559.3784 |  |  |  |  | 0.73255 |  | 792.5321 | [6 empty] | 53.4283 |  | Heat pump |  | 85.875 |  | 29369.2429 | 14684.6214
Parcel 6 |  | 225000 | Midrise Apartment | 271.5688 | 98406.8164 | 346096.658 |  |  |  |  | 2.3183 |  | 4462.6498 | [6 empty] | 244.4119 |  | Heat pump |  | 271.7719 |  | 92945.9834 | 46472.9917
Parcel 7 |  | 320000 | Retail | 715.3722 | 390473.4623 | 1373294.7092 |  |  |  |  | 8.3831 |  | 7899.8129 | [6 empty] | 643.8349 |  | Heat pump |  | 982.7371 |  | 336096.1035 | 168048.0517
Parcel 8 |  | 120000 | Midrise Apartment | 144.8367 | 52483.6354 | 184584.8843 |  |  |  |  | 1.2364 |  | 2380.0799 | [6 empty] | 130.353 |  | Heat pump |  | 144.945 |  | 49571.1912 | 24785.5956
Parcel 9 |  | 60000 | Midrise Apartment | 118.7295 | 44674.0998 | 157118.7567 |  |  |  |  | 1.4651 |  | 1585.0642 | [6 empty] | 106.8565 |  | Heat pump |  | 171.75 |  | 58738.4857 | 29369.2429
Parcel 10 |  | 160000 | Midrise Apartment | 193.1156 | 69978.1806 | 246113.179 |  |  |  |  | 1.6486 |  | 3173.4399 | [6 empty] | 173.804 |  | Heat pump |  | 193.26 |  | 66094.9216 | 33047.4608
Parcel 11 |  | 270000 | Retail | 603.5953 | 329461.9838 | 1158717.4109 |  |  |  |  | 7.0733 |  | 6665.4671 | [6 empty] | 543.2357 |  | Heat pump |  | 829.1845 |  | 283581.0873 | 141790.5436
Parcel 12 | Inner Harbor | 85000 | Classroom | 211.4946 | 94491.5674 | 332326.7316 |  |  |  |  | 2.6418 |  | 1613.4142 |  |  | RTU - NG? | RTU | 2 | 28% | 190.3451 | 5 | Heat pump |  | 309.6872 |  | 105913.0094 | 52956.5047
Inner Harbor |  | 1750056 |  | 3374.9765 | 1721725.5172 | 6055306.6254 |  |  |  |  | 39.1144 |  | 40563.1926 | [10 empty] | 4585.3004 |  | #REF! | #REF!
|  | #REF! |  | #REF! |  | #REF! |  |  |  |  | #REF! |  | #REF! | [9 empty] | Total (kW) | #REF!
|  |  |  | #REF! |  |  |  |  | Total Peak Load |  | #REF! | MBH | [8 empty] | NOTES
*Parcel Buildings are not constructed yet | [20 empty] | Taller than 6-stories - elec boiler
Exist heat pump - elec boiler
Rooftop equipment - heat pump
Small apartment - heat pump
Heat pump COP 2.5
tall (>6s) building = boiler
293.07 kWh per MMBtu

## Equipment Costs
Syracuse District Energy
Equipment Costs
| Equipment Type | Unit Cost | Unit | Notes | Reference
| Crossflow Open Cooling Tower | 250 | $/ton | Recent bid price | Does not include rigging.
| Closed Circuit Cooling Tower | 500 | $/ton | Recent bid price
| Condensing Boiler | 25 | $/MBH | Vendor equipment pricing, Lochinvar. Does not include install
| WSHP RTU | 3000 | $/ton | Based on 3T and 5T unit pricing | Email from Trane
| Cooling Tower Reconditioning | 60% |  | of total Replacement Cost | https://faservice.net/cooling-tower-repair-or-replacement-whats-best/
| Maintenance | Unit Cost | Unit | Notes
| Legionella Testing | 692 | $/tower | << annual ($173/quarter)
| Tower Cleaning/Service | 1000 | $/tower
| Annual Boiler Service Calls | 1000 | $/boiler | << estimate per Jim Funiciello
| Water | Unit Cost | Unit | Notes
| Water Use | 3 | gpm per 100 ton
| Water Use | 50 | gal/ton-hr
| Water Cost | 3.04 | per 1,000 gal | << estimate: 2020 OCWA Rate Schedule 8
| Chemical Cost | 1 | per ton per year

## Energy Reduction
Syracuse District Energy
District System Cooling Energy Savings
Building | Cooling Energy | Energy Reduction¹ | Energy Reduction
| (kWh) | (%) | (kWh)
Barclay Damon | 1238762.9524 | 35% | 433567.0333
Atrium | 4504592.554 | 35% | 1576607.3939
State Tower | 185454.2815 | 35% | 64908.9985
Courtyard Marriott | 1077348.3858 | 35% | 377071.935
US Social Security Admin | 1370146.9019 | 35% | 479551.4156
M&T Bank | 1351377.7662 | 28% | 378385.7745
State Office Building | 472097.335 | 28% | 132187.2538
SU-Warehouse | 949380.419 | 35% | 332283.1467
300 S State St | 495505.1809 | 35% | 173426.8133
Key Bank Building | 109323.5258 | 28% | 30610.5872
100 East Washington St | 514274.3166 | 28% | 143996.8086
Ramboll | 554419.3078 | 35% | 194046.7577
City Hall | 1379531.4697 | 28% | 386268.8115
1 Lincoln Center | 696447.5471 | 28% | 195005.3132
SUNY Oswego MetroCenter | 327845.3715 | 28% | 91796.704
217 Montgomery St | 347234.1468 | 35% | 121531.9514
City Hall Commons | 162228.2695 | 35% | 56779.8943
Salinas Place | 169955.0406 | 35% | 59484.2642
AXA Towers | 638150.6118 | 28% | 178682.1713
Onondaga County DH&C Plant | 2451913.5422 | 28% | 686535.7918
Hotel Syracuse | #REF! | 35% | #REF!
Tech Garden | 3338177.0664 | 35% | 1168361.9733
Bank of America | 233098.0591 | 35% | 81584.3207
Clinton Exchange | 142148.9355 | 35% | 49752.1274
National Grid | 675688.8831 | 35% | 236491.1091
Post Standard | 1918956.428 | 35% | 671634.7498
Galleries of Syracuse | 671935.056 | 28% | 188141.8157
100 Clinton Sq | 822088.1411 | 28% | 230184.6795
City of Syr Criminal Court House | 450459.2554 | 28% | 126128.5915
550 Harrison Building | 629312.3044 | 28% | 176207.4452
Jefferson Clinton Hotel | 0 | 28% | 0
Sky Armory | 195672.8124 | 28% | 54788.3875
Clinton Plaza | 266866.1324 | 28% | 74722.5171
MOST | 391766.0348 | 35% | 137118.1122
600 Montgomery St | 262276.2972 | 35% | 91796.704
SU-Peck Hall | 240533.5922 | 35% | 84186.7573
Medical Office Bldg | 332326.7316 | 28% | 93051.4848
Total | #REF! |  | #REF!
1: per Appendix G
|  | Electric Rate | 0.085
|  | Electric Cost Savings | #REF!