## HydroDatabase_12.18.18_Rev
[16 empty] | NYISO Zone2 | Capacity | Capacity | Capacity (of Project) | Annual Gen. | Annual Gen. | Annual Gen. | Annual Gen. | Capacity Factor | Capacity Factor | Capacity Factor | 2017 CAPEX3 | 2017 CAPEX3 | 2015 Fixed O&M | 2015 Fixed O&M | 2015 Fixed O&M | 2015 Variable O&M | 2015 Variable O&M | 2015 Variable O&M | 2017 IC Cost3 | Upgrade Notes4
[17 empty] | (Existing)1 | (Upgrade)3 | (Total)3 | (Existing)3 | (Upgrade)3 | (Bypass)3 | (Net)3 | (Existing)3 | (Upgrade)3 | (Net)3 | CAPEX | CAPEX | (Existing)6 | (Upgrade)6 | (Total)6 | (Existing)7 | (Upgrade)7 | (Total)7 | Variable O&M
FERC ID1 | FERC Status1 | Project Name1 | FERC Expiration Date1 | FERC Issued Date1 | Project Owner/Operator1 | River1 | Town1 | County1 | Drainage Area (sq. mi.)1 | Net Head (ft)2 | Existing Plant Discharge (cfs)5 | Proposed Plant Discharge (cfs)5 | Plant Type2 | Longitude1 | Latitude1 |  | MW | MW | MW | MWh | MWh | MWh | MWh | % | % | % | 2017 $/kW | 2017 $/kWh | 2015 $/kW | 2015 $/kW | 2015 $/kW | 2015 $/kW | 2015 $/kW | 2015 $/kW | 2017 $/kW
5867 | FERC License Issued | Alice Falls8 | 2023-09-30 | 1983-10-05 | Alice Falls Hydro Llc | Ausable River | Ausable Chasm | Essex | 448 | 50 | 530 | 610 | ROR | -75.2064 | 43.4403 | 9 | 1.942 | 0.29 | 2.232 | 12120.1206 | 13383.6162 | 12120.1206 | 13383.6162 | 71.24% | 68.45% | 68.45% | 9797 | 2.2486 | 24.8383 | 39.7289 | 23.9989 | 5.4935 | 8.0663 | 5.3412 | 0 | The upgrade of the plant includes the replacement of one turbine runner.
2645 | FERC License Issued | Belfort | 2026-07-31 | 1996-08-02 | Brookfield Renewable Energy | Beaver River | Belfort | Lewis | 252 | 48 | 590 | 690 | ROR | -75.2883 | 43.9267 | 8 | 2.04 | 0.35 | 2.39 | 12287.4575 | 13511.2227 | 10387.7565 | 10467 | 68.76% | 64.53% | 49.99% | 8780 | 2.5111 | 24.5381 | 37.9257 | 23.5969 | 5.4392 | 7.7656 | 5.2679 | 0 | The upgrade of the plant includes the replacement of three horizontal kaplan runners.
2645 | FERC License Issued | Eagle | 2026-07-31 | 1996-08-02 | Brookfield Renewable Energy | Beaver River | Belfort | Lewis | 224 | 132 | 630 | 680 | ROR | -73.5075 | 44.6694 | 8 | 6.05 | 0.5 | 6.55 | 30965.6808 | 31200.7272 | 27499.2005 | 27566 | 58.43% | 54.38% | 48.04% | 6848 | 14.5673 | 18.7597 | 34.7275 | 18.3953 | 4.3668 | 7.2258 | 4.2973 | 0 | The upgrade of the plant includes the addition of an additional horizontal francis turbine.
2645 | FERC License Issued | Moshier | 2026-07-31 | 1996-08-02 | Brookfield Renewable Energy | Beaver River | Belfort | Herkimer | 182 | 196 | 560 | 660 | ROR | -75.1531 | 43.2853 | 8 | 8 | 1.4 | 9.4 | 33707 | 34954.8493 | 30249.8287 | 31266.2073 | 48.1% | 42.45% | 37.97% | 5606 | 6.2895 | 17.5088 | 26.9293 | 16.825 | 4.1272 | 5.8689 | 3.9949 | 0 | The upgrade of the plant includes the replacement of two vertical francis runners.
2645 | FERC License Issued | High Falls | 2026-07-31 | 1996-08-02 | Brookfield Renewable Energy | Beaver River | Croghan | Lewis | 267 | 100 | 660 | 900 | ROR | -73.4955 | 43.0864 | 9 | 4.8 | 1.74 | 6.54 | 26222.6001 | 29346.6972 | 22267 | 24478.2307 | 62.36% | 51.22% | 42.73% | 6314 | 3.5167 | 19.8633 | 25.5213 | 18.4023 | 4.5758 | 5.6168 | 4.2986 | 212.6437 | The upgrade of the plant includes the replacement of three vertical francis runners.
2569 | FERC License Issued | Deferiet | 2026-11-30 | 1996-12-24 | Deferiet Corp | Black River | Deferiet | Jefferson | 1817 | 46 | 3230 | 4377 | ROR | -75.615 | 43.9783 | 8 | 10.8 | 2 | 12.8 | 64132 | 71482 | 60985.7027 | 66290.2037 | 67.79% | 63.75% | 59.12% | 7118.5 | 1.937 | 16.2579 | 24.6584 | 15.5897 | 3.8844 | 5.461 | 3.7534 | 31.25 | The upgrade of the plant includes the addition of one new minimum flow horizontal francis turbines.
2695 | FERC Issued Exemption | Dexter | Exempt | 1982-06-04 | Enel | Black River | Dexter | Jefferson | 1900 | 14 | 4250 | 4700 | ROR | -76.0458 | 44.0061 | 8 | 4.325 | 0.45 | 4.775 | 24072.8102 | 25301.2975 | 24072.8102 | 25301.2975 | 63.54% | 60.49% | 60.49% | 10187 | 3.7315 | 20.3812 | 35.6431 | 19.889 | 4.6731 | 7.3812 | 4.5806 | 0 | The upgrade of the plant includes the addition of eleven turbine runners.
2538 | FERC License Issued | Beebee Island8 | 2026-11-30 | 1996-12-24 | Brookfield Renewable Energy | Black River | Watertown | Jefferson | 1876 | 32 | 3440 | 4140 | ROR | -73.5075 | 44.6694 | 8 | 8 | 1.62 | 9.62 | 54580 | 60256 | 54580 | 60256 | 77.88% | 71.5% | 71.5% | 8140 | 2.3233 | 17.5088 | 25.9758 | 16.7292 | 4.1272 | 5.6984 | 3.9763 | 0 | The upgrade of the plant includes the replacement of two vertical kaplan runners.
2569 | FERC License Issued | Herrings | 2026-11-30 | 1996-12-24 | Brookfield Renewable Energy | Black River | Herrings | Jefferson | 1810 | 19.5 | 3810 | 5080 | ROR | -73.7986 | 43.4825 | 8 | 5.4 | 1.8 | 7.2 | 32902 | 36093.2385 | 31729.1003 | 36658.3645 | 69.55% | 57.23% | 58.12% | 7952 | 4.4853 | 19.2938 | 25.3085 | 17.9704 | 4.4682 | 5.5784 | 4.216 | 0 | The upgrade of the plant includes the addition of an additional vertical kaplan turbine.
2569 | FERC License Issued | Black River | 2026-11-30 | 1996-12-24 | Brookfield Renewable Energy | Black River | Black River | Jefferson | 1856 | 33 | 2500 | 3340 | ROR | -74.9865 | 43.0525 | 8 | 6 | 2 | 8 | 41665.9872 | 48272.9182 | 35338.5208 | 44097.364 | 79.27% | 68.88% | 62.92% | 6168 | 1.8671 | 18.7982 | 24.6584 | 17.5088 | 4.3741 | 5.461 | 4.1272 | 0 | The upgrade of the plant includes the addition of an additional vertical francis turbine.
2582 | FERC License Issued | Station 2 | 2036-01-31 | 1996-02-22 | Rochester Gas & Elec Corp | Genesee River | Rochester | Monroe | 2467 | 86 | 2370 | 3490 | ROR | -77.6132 | 43.1603 | 11 | 14.8 | 7 | 21.8 | 81940.6813 | 103783.0756 | 69991.3968 | 89053.7706 | 63.2% | 54.35% | 46.63% | 4084 | 1.3088 | 15.0406 | 18.0959 | 13.6685 | 3.6449 | 4.24 | 3.3706 | 14.2857 | The upgrade of the plant includes the addition of one additional vertical francis turbine.
2583 | FERC License Issued | Station 5 | 2036-01-31 | 1996-02-22 | Rochester Gas And Electric Corp. | Genesee River | Rochester | Monroe | 2467 | 130 | 4840 | 5720 | ROR | -77.6282 | 43.1763 | 11 | 45.652 | 8.4 | 54.052 | 201883 | 220967.8243 | 201883 | 220967.8243 | 50.48% | 46.67% | 46.67% | 4025 | 1.7716 | 11.3876 | 17.299 | 10.9223 | 2.9031 | 4.0867 | 2.8058 | 0 | The upgrade of the plant includes the addition of one additional vertical francis turbine.
2584 | FERC License Issued | Court Street | 2037-09-30 | 1997-10-17 | Rochester Gas and Elec Corp | Genesee River | Rochester | Monroe | 2450 | 25 | 1650 | 2750 | ROR | -77.6097 | 43.1522 | 11 | 3 | 2 | 5 | 19130.9525 | 28530.1668 | 16423.0649 | 24250.6753 | 72.8% | 65.14% | 55.37% | 6692 | 1.4239 | 22.3085 | 24.6584 | 19.6641 | 5.0315 | 5.461 | 4.5382 | 50 | The upgrade of the plant includes the addition of an additional vertical kaplan turbine.
4684 | FERC License Issued | Stillwater | 2027-04-30 | 1987-05-20 | Gravity Renewables | Hudson River | Stillwater | Sullivan | 3745 | 8.6 | 5600 | 7800 | ROR | -75.7893 | 44.5156 | 2 | 3.5 | 1.37 | 4.87 | 26787.9093 | 29229.6088 | 26787.9093 | 29229.6088 | 87.37% | 68.52% | 68.52% | 5559 | 3.1191 | 21.475 | 27.0738 | 19.7924 | 4.8773 | 5.8947 | 4.5624 | 0 | The upgrade of the plant includes the replacement of one horizontal kaplan turbine.
2385 | FERC License Issued | Glens Falls | 2041-10-31 | 2001-11-20 | Niagara Mohawk Power Corp. & Finch, Pruyn And Co. | Hudson River | Hudson Falls | Warren & Saratoga | 2807 | 16 | 10410 | 12260 | ROR | -73.641 | 43.3058 | 2 | 12.1 | 2.15 | 14.25 | 54200 | 58157 | 49806.6895 | 52636.094 | 51.13% | 46.59% | 42.17% | 6659 | 3.6181 | 15.8078 | 24.2218 | 15.1819 | 3.7962 | 5.3818 | 3.6729 | 0 | The upgrade of the plant includes the replacement of five horizontal francis runners.
6032 | FERC License Issued | Mechanicville | 2043-05-31 | 1993-06-09 | Albany Engineering | Hudson River | Mechanicville | Saratoga | 4572 | 23 | 2690 | 12870 | ROR | -73.6767 | 42.88 | 8 | 4.5 | 17 | 21.5 | 36517.5779 | 88536.2791 | 35600.7094 | 83599.284 | 92.64% | 47.01% | 44.39% | 3906 | 1.2765 | 20.1825 | 14.5344 | 13.7153 | 4.6358 | 3.5443 | 3.3801 | 5.8824 | The upgrade of the plant includes the addition of two additional horizontal francis turbines.
13 | FERC License Issued | Green Island | 2062-07-31 | 2012-08-17 | Green Island Power Authority | Hudson River | Croton Falls | Rensselaer | 8090 | 18.4 | 4490 | 35920 | ROR | -73.6867 | 42.7517 | 2 | 6 | 42 | 48 | 39368.3251 | 147362.4305 | 39097.1052 | 144371.156 | 74.9% | 35.05% | 34.33% | 4896 | 1.9041 | 18.7982 | 11.6246 | 11.2474 | 4.3741 | 2.9524 | 2.8739 | 2.381 | The upgrade of the plant includes the replacement of four existing turbines with four bigger turbines.
2539 | FERC License Issued | School Street8 | 2047-01-31 | 2007-02-15 | Brookfield Renewable Energy | Mohawk River | Cohoes | Albany | 3456 | 92 | 5810 | 7450 | ROR | -73.715 | 42.7967 | 2 | 38.8 | 11 | 49.8 | 188551 | 212476.7291 | 188551.4087 | 212476.7291 | 55.47% | 48.71% | 48.71% | 4102 | 1.8859 | 11.8543 | 16.1843 | 11.1456 | 3.0001 | 3.87 | 2.8526 | 0 | The upgrade of the plant includes the addition of one additional fish friendly turbine.
10481 | FERC License Issued | Mongaup | 2022-03-31 | 1992-04-14 | Eagle Creek | Mongaup River | Millrift | Sullivan | 180 | 110 | 500 | 620 | ROR | -75.1431 | 43.3044 | 3 | 4 | 0.95 | 4.95 | 9096 | 9666.5164 | 8946.2373 | 9506.8666 | 25.96% | 22.29% | 21.92% | 4864 | 8.0993 | 20.7783 | 29.6361 | 19.7129 | 4.7475 | 6.3471 | 4.5474 | 0 | The upgrade of the plant includes the replacement of four vertical francis runners.
2788 | FERC License Issued | Colliersville | 2019-02-28 | 1979-03-13 | Enel | North Branch Susquehanna River | Colliersville | Otsego | 351 | 35 | 570 | 870 | ROR | -75.1086 | 43.8867 | 8 | 1.45 | 0.9 | 2.35 | 6601 | 8204 | 5242 | 8352 | 51.97% | 39.85% | 40.57% | 5261.1111 | 2.9538 | 26.6969 | 30.0345 | 24.0309 | 5.8275 | 6.4168 | 5.347 | 111.1111 | The upgrade of the plant includes the addition of an additional vertical francis turbine.
2713 | FERC License Issued | Heuvelton | 2052-12-31 | 2012-11-26 | Brookfield Renewable Energy | Oswegatchie River | Heuvelton | St. Lawrence | 995 | 14.05 | 1020 | 1530 | ROR | -75.405 | 44.6178 | 8 | 1.04 | 0.52 | 1.56 | 7204 | 9070.7807 | 6901.2775 | 8663.8198 | 79.07% | 66.38% | 63.4% | 7431 | 2.0699 | 28.9809 | 34.3927 | 26.2191 | 6.2321 | 7.1688 | 5.742 | 0 | The upgrade of the plant includes the addition of an additional vertical francis turbine.
9821 | FERC License Issued | Ogdensburg | 2027-05-31 | 1987-06-15 | Algonquin Power | Oswegatchie River | Ogdensburg | St. Lawrence | 1592 | 19 | 2660 | 3730 | ROR | -74.985 | 42.5036 | 8 | 3.675 | 1.47 | 5.145 | 16440.4194 | 19468.6694 | 16440.4194 | 19468.6694 | 51.07% | 43.2% | 43.2% | 6956 | 3.3766 | 21.2178 | 26.6067 | 19.5257 | 4.8294 | 5.8114 | 4.5121 | 68.0272 | The upgrade of the plant includes the addition of one additional turbine for minimum flows.
2474 | FERC License Issued | Minetto | 2044-10-31 | 2004-11-30 | Brookfield Renewable Energy | Oswego River | Oswego | Oswego | 5092 | 14.75 | 7470 | 8630 | ROR | -76.4725 | 43.4 | 2 | 8 | 1.24 | 9.24 | 41094.9472 | 43724.4238 | 41094.9472 | 43724.4238 | 58.64% | 54.02% | 54.02% | 7486 | 3.5302 | 17.5088 | 27.7488 | 16.8965 | 4.1272 | 6.0146 | 4.0088 | 0 | The upgrade of the plant includes the replacement of five vertical francis runners.
5984 | FERC License Issued | Oswego Falls | 2036-02-29 | 1996-03-15 | Brookfield Renewable Energy | Oswego River | Fulton | Oswego | 5121 | 17 | 5960 | 9220 | ROR | -76.4158 | 43.3147 | 8 | 7.36 | 4.02 | 11.38 | 41879.265 | 55597 | 41879.265 | 55597 | 64.96% | 55.77% | 55.77% | 7066 | 2.0707 | 17.8731 | 20.7527 | 16.0491 | 4.1973 | 4.7427 | 3.8436 | 0 | The upgrade of the plant includes the replacement of three vertical francis runners and the addition of two new quadruplex turbines.
2474 | FERC License Issued | Fulton | 2044-10-31 | 2004-11-30 | Brookfield Renewable Energy | Oswego River | Fulton | Oswego | 5018 | 15 | 1150 | 5300 | ROR | -76.4198 | 43.3241 | 8 | 1.25 | 4.52 | 5.77 | 4139 | 13686 | 3441.0716 | 10918 | 37.8% | 27.08% | 21.6% | 5316.3717 | 2.517 | 27.6938 | 20.1604 | 18.9805 | 6.0048 | 4.6317 | 4.4088 | 22.1239 | The upgrade of the plant includes the replacement of two turbines.
2330 | FERC License Issued | East Norfolk | 2033-12-31 | 2002-02-13 | Brookfield Renewable Energy | Raquette River | Norfolk | St. Lawrence | 1063 | 29 | 2000 | 3146 | ROR | -74.9864 | 44.7947 | 8 | 4 | 0.6 | 4.6 | 26073.526 | 27121.526 | 22010.526 | 27121.526 | 74.41% | 67.31% | 67.31% | 8468 | 4.8481 | 20.7783 | 33.1983 | 20.0732 | 4.7475 | 6.9645 | 4.6153 | 166.6667 | The upgrade of the plant includes the addition of an additional horizontal francis turbine for minimum flows.
2330 | FERC License Issued | Norfolk | 2026-07-31 | 1996-08-02 | Brookfield Renewable Energy | Raquette River | Norfolk | St. Lawrence | 1063 | 40.7 | 2000 | 2425 | ROR | -74.9906 | 44.8022 | 8 | 5.62 | 0.9 | 6.52 | 37226 | 38309 | 30894 | 38309 | 75.61% | 67.07% | 67.07% | 7588.8889 | 6.3066 | 19.1044 | 30.0345 | 18.4162 | 4.4323 | 6.4168 | 4.3013 | 0 | The upgrade of the plant includes the addition of an additional turbine for minimum flows.
2320 | FERC License Issued | Higley | 2033-12-31 | 2002-02-13 | Brookfield Renewable Energy | Raquette River | Colton | St. Lawrence | 979 | 43 | 2020 | 3010 | ROR | -74.9319 | 44.5303 | 8 | 6.3 | 3.1 | 9.4 | 37216.8116 | 42989.4696 | 37216.8116 | 42989 | 67.44% | 52.21% | 52.21% | 7875 | 4.229 | 18.573 | 22.1285 | 16.825 | 4.3312 | 4.9983 | 3.9949 | 0 | The upgrade of the plant includes the addition of two additional horizontal kaplan turbines.
9260 | FERC License Issued | Sissonville | 2028-04-30 | 1988-05-20 | Albany Engineering | Raquette River | Hewittville | St. Lawrence | 1025 | 16 | 1980 | 2970 | ROR | -75.3739 | 43.9261 | 8 | 2.3 | 1.15 | 3.45 | 11929.5751 | 15389.38 | 10482.0236 | 13709.2914 | 59.21% | 50.92% | 45.36% | 7241 | 2.4068 | 23.8217 | 28.27 | 21.5515 | 5.3089 | 6.1068 | 4.8915 | 0 | The upgrade of the plant includes the addition of one additional vertical francis turbine.
9222 | FERC License Issued | Yaleville | 2022-01-31 | 1992-02-10 | Brookfield Renewable Energy | Raquette River | Norfolk | St Lawrence | 1046 | 13 | 740 | 2290 | ROR | -74.9983 | 44.7667 | 8 | 0.7 | 1.46 | 2.16 | 5653.3796 | 12285.9876 | 5085.2992 | 9776.0729 | 92.19% | 64.93% | 51.67% | 6973 | 1.5349 | 31.958 | 26.6516 | 24.1941 | 6.751 | 5.8194 | 5.3767 | 68.4932 | The upgrade of the plant includes the addition of one new horizontal kaplan turbine.
2330 | FERC License Issued | Raymondville | 2033-12-31 | 2002-02-13 | Brookfield Renewable Energy | Raquette River | Raymondville | St. Lawrence | 1077 | 21.5 | 1630 | 3190 | ROR | -74.9806 | 44.8339 | 8 | 3.1 | 1.88 | 4.98 | 17994 | 24300 | 17006.5899 | 19397.9489 | 66.26% | 55.7% | 44.47% | 13205 | 3.94 | 22.1285 | 25.0381 | 19.6835 | 4.9983 | 5.5296 | 4.5419 | 0 | The upgrade of the plant includes the replacement of existing turbine with a bigger turbine.
2330 | FERC License Issued | Norwood | 2033-12-31 | 2002-02-13 | Brookfield Renewable Energy | Raquette River | Norwood | St. Lawrence | 1045 | 20.6 | 1340 | 3090 | ROR | -75.0053 | 44.7433 | 8 | 2 | 2.63 | 4.63 | 14884 | 21061 | 12773 | 18034.9541 | 84.95% | 51.93% | 44.47% | 9541 | 4.0623 | 24.6584 | 23.0457 | 20.041 | 5.461 | 5.1671 | 4.6092 | 0 | The upgrade of the plant includes the replacement of existing turbine with a bigger turbine.
2320 | FERC License Issued | Hannawa | 2033-12-31 | 2002-02-13 | Brookfield Renewable Energy | Raquette River | Potsdam | St. Lawrence | 993 | 72 | 1380 | 2070 | ROR | -74.975 | 44.6119 | 8 | 7.2 | 3.6 | 10.8 | 50009 | 60463.7241 | 49104 | 58662.5045 | 79.29% | 63.91% | 62.01% | 7769 | 2.6752 | 17.9704 | 21.3261 | 16.2579 | 4.216 | 4.8496 | 3.8844 | 0 | The upgrade of the plant includes the addition of an additional horizontal francis turbine.
2320 | FERC License Issued | Colton | 2033-12-31 | 2002-02-13 | Brookfield Renewable Energy | Raquette River | Colton | St. Lawrence | 981 | 262 | 1580 | 2010 | ROR | -74.94 | 44.555 | 8 | 30.101 | 8.19 | 38.291 | 187033.8913 | 210541 | 187033.8913 | 210541 | 70.93% | 62.77% | 62.77% | 4033 | 1.4051 | 12.6215 | 17.4076 | 11.8931 | 3.1579 | 4.1077 | 3.0081 | 0 | The upgrade of the plant includes the addition of an additional horizontal francis turbine.
6972 | FERC License Issued | Hollow Dam | 2026-04-30 | 1986-05-30 | Hollow Dam Power Co. | West Branch Oswegatchie River | Talcville | St. Lawrence | 276 | 21 | 700 | 890 | ROR | -74.2807 | 44.8457 | 8 | 1.06 | 0.29 | 1.35 | 5056 | 5488 | 4188.6879 | 5488 | 54.45% | 46.41% | 46.41% | 11424 | 7.6689 | 28.8449 | 39.7289 | 27.1723 | 6.2082 | 8.0663 | 5.9122 | 0 | The upgrade of the plant includes the replacement of two turbine runners.
2318 | FERC License Issued | Conklingville4 | 2042-08-31 | 2002-09-25 | Brookfield Renewable Energy | Sacandaga River | Hadley | Saratoga | 1044 | 53 | 3030 | 3030 | ROR | -73.9242 | 43.3175 | 2 | 20 | NA | 20 | 46494 | NA | 37568 | 37568 | 26.54% | NA | 21.44% | NA | NA | 15.1019 | NA | NA | 3.7097 | NA | 3.7097 |  | No upgrade, future increase in mandated bypass flows possible.
4472 | FERC License Issued | Franklin Falls4 | 2024-06-30 | 1984-07-27 | Union Falls Hydropower & Erie Boulevard Hydropower | Saranac River | Franklin Falls | Franklin | 291 | 53.3 | 580 | 710 | ROR | -75.3056 | 43.6167 | 8 | 2.26 | NA | 2.74 | 8963.7409 | NA | 5805.3862 | 5805.3862 | 45.28% | NA | 29.32% | NA | NA | 25.8774 | NA | NA | 5.7625 | NA | 5.5427 | 0 | No upgrade, future increase in mandated bypass flows possible.
2645 | FERC License Issued | Taylorville4 | 2026-07-31 | 1996-08-02 | Brookfield Renewable Energy | Beaver River | Belfort | Lewis | 251 | 97 | 680 | 680 | ROR | -73.495 | 43.0933 | 8 | 4.772 | NA | 4.772 | 24499.669 | NA | 22243.0787 | 22243.0787 | 58.61% | NA | 53.21% | NA | NA | 21.5153 | NA | NA | 4.955 | NA | 4.955 | NA | No upgrade, future increase in mandated bypass flows possible.
4114 | FERC License Issued | Treadwell Mills4 | 2027-05-31 | 1987-06-26 | Lower Saranac Hydro Partners, Lp | Saranac River | Plattsburgh | Clinton | 604 | 70 | 1830 | 1830 | ROR | -74.9983 | 44.7667 | 9 | 9.3 | NA | 9.3 | 33312.4825 | NA | 25171.4869 | 25171.4869 | 40.89% | NA | 30.9% | NA | NA | 18.2461 | NA | NA | 4.3302 | NA | 4.3302 | NA | No upgrade, future increase in mandated bypass flows possible.
4472 | FERC License Issued | Union Falls4 | 2024-06-30 | 1984-07-27 | Union Falls Hydropower & Erie Boulevard Hydropower | Saranac River | Clayburg | Clinton | 329 | 60 | 690 | 690 | ROR | -73.4647 | 44.5189 | 8 | 3 | NA | 3 | 14857.0972 | NA | 10710.0511 | 10710.0511 | 56.53% | NA | 40.75% | NA | NA | 24.1288 | NA | NA | 5.4421 | NA | 5.4421 | NA | No upgrade, future increase in mandated bypass flows possible.
Footnotes
1) Data obtained from previously developed databases. See metadata for more details.
2) Data obtained through FERC docket searches and available online resources. See metadata for more details.
3) Data generated by Gomez and Sullivan Engineers, DPC based on preliminary research and desktop investigations.
4) No upgrades were proposed. Future regulations may require an increase in minimum bypass flows or fish passage flows.
5) Approximate hydraulic capacities in cubic feet per second for hydropower plants based on existing project documentation and flow duration analyses performed by Gomez and Sullivan Engineers, DPC using available USGS Streamflow Daily Average data.
6) Fixed O&M computed using the formula shown on Slide 174 of the Clean Energy Standard White Paper - Cost Study (April 8, 2016) developed by the New York State Energy Research and Development Authority (NYSERDA) and the New York State Department of Public Service. Equation was based on using 2015 dollars.
7) Variable O&M computed using the formula shown on Slide 174 of the Clean Energy Standard White Paper - Cost Study (April 8, 2016) developed by the New York State Energy Research and Development Authority (NYSERDA) and the New York State Department of Public Service. Equation was based on using 2015 dollars.
8) No new bypass flows are anticipated.
General Notes
1) This screening study was constrained to using data from sources which were readily available, generally in electronic form. More accurate generation estimates and opinions of probable construction costs require additional detailed information and data collection as costs and generation values are highly site-specific.
2) This database was developed to assist the New York State Energy Research and Development Authority (NYSERDA) develop Large Scale Renewable (LSR) Energy Supply Curves.
3) The columns do not account for major maintenance items at hydropower facilities including but not limited to generator rewinds and turbine refurbishment/repair. These items are discussed in more detail in the corresponding report.
4) For future site specific feasibility studies the data provided above should be verified by contacting project owners or obtaining more detailed existing project drawings or reports.
5) Date created: April 25, 2017.
6) Author: Gomez and Sullivan Engineers, DPC.