## Instructions
V1.0
Background
1. This checklist is a companion to the Performance-based Energy Code Enforcement Manual (the Manual).
2. The "General Information" and "Submittal Checklist" tabs should be filled out by Permit Applicant (PA)
3. Authority Having Jurisdiction (AHJ) may request that the PA also completes the "Proposed Design" and "ECB Budget & PRM Baseline" tabs to help improve the initial quality of the submittal, and to streamline the review.
Instructions for Permit Applicant
1. Fill out the "General Information" and "Submittal Checklist" tabs.
2. If required by the AHJ, fill out the "Proposed Desing" and "ECB Budget & PRM Baseline" tabs. Refer to the "Instructions for Submittal Reviewer" section below for details.
Instructions for Submittal Reviewer
1. General review process and tips
a. Read the “Review Process” section of the Manual to understand the general review logic.
b. Checks that must be performed on all projects (are mandatory) have the check number shown in red font, (e.g. 3). “Include in Review” column for these checks is pre-set to “Yes”.
c. Search the Manual using the value in "CheckID" field to locate the detailed description of each check in the Review Checks section of the Manual, including the applicable requirements of Standard 90.1, examples, and common mistakes.
d. Search the Manual using the value in "Simulation Reports" field to locate the annotated simulation reports in the Simulation Reports section of the Manual. eQUEST and Trane Trace 700 reports are currently included.
e. (For AHJ reviewers only) Document review outcome (pass/fail/NA), and provide comments as applicable for each completed check.
“Pass” outcome means that no changes are required in the given area. Any comments that may be provided are informative, and may apply to future projects. No response is required from PA.
“Fail” outcome means that the changes must be made to the submittal before it can be approved. The issues and required changes are described in the Review Comment.
2. Review the "General Information" and "Submittal Checklist" tabs to verify that all materials necessary to support the review are provided. Document review outcome for each check, and provide review comments as necessary.
3. Proposed Design, and ECB Budget & PRM Baseline tabs:
a. Complete the mandatory checks in the “Proposed Design” tab.
b. Complete the mandatory checks in the “ECB Budget and PRM Baseline” tab.
c. Select additional checks to be performed based on the outcome of the completed checks by setting “Include in Review” column to “Yes” on the “Proposed Design” and “ECB Budget and PRM Baseline” tabs, as applicable.
d. Complete the checks on the “Proposed Design” and “ECB Budget and PRM Baseline” tabs marked in the previous step.
e. Complete additional checks for a more comprehensive review, if desired.
4. (For AHJ reviewers only) Copy the review comments from the Review Checklist into a separate document to be shared with PA, or share the completed Review Checklist with the PA to communicate the review outcome and required corrective actions.

## General Information
This tab must be filled by the Permit Applicant
1 | Location Information
Building No(s)
Street Name
City
2 | Applicant Information
Last Name
First Name
Middle Initial
Business Name
Business Address
Business Telephone
Business Fax
Mobile Telephone
| City |  | State | Zip
Email
License Number
3 | Energy Modeling Information
| Modeling Software & version | eQUEST
Weather File
Modeled Square Feet
Conditioned SQFT
Proposed Unmet Load Hours
Baseline Unmet Load Hours
Proposed Site EUI (kBtu/sf)
Baseline Site EUI (kBTU/SF)

## Submittal Checklist
| PROJECT DOCUMENTS AND SUPPORTING INFORMATION |  | These sections must be filled by the Permit Applicant) |  | These sections are filled by the Submittal Reviewer
|  |  | Submitted? | Provide file or document name where information is found. Reference document sections, page number, spreadsheet tab name and cell range as applicabe. | Review Outcome | Review Comment
1 | Project overview: Include the number of stories above and below grade, the typical floor size, the uses in the building (e.g., office, cafeteria, retail, parking, etc.), the gross area and the conditioned floor area for each use.
2 | A narrative describing the areas where trade-offs are made: Description of building or system elements that do not comply with the prescriptive requirements of the code; elements exceeding requirements; and a description of those building elements or systems modeled to provide additional energy savings to offset the non-complying elements. For each element, provide the reference to the part of the submittal where it is described.
3 | Design documents
4 | A diagram showing the thermal blocks used in the computer simulation
5 | Purchased energy rates used in the simulation with supporting documentation
6 | A site plan showing all adjacent buildings and topography that may shade the proposed building, with the estimated height or number of stories (PRM only)
SIMULATION DETAILS
7 | A list of the energy-related features that are included in the design and on which the Appendix G performance rating, or compliance with Section 11, is based. This list must document all energy features that differ between the models used in the baseline building performance (or energy cost budget) and proposed building performance (or design energy cost) calculations
8 | The key energy efficiency improvements compared with the requirements in Sections 5 through 10.
9 | A list identifying the aspects of the proposed design that are less stringent than the requirements of 5.5, 6.5, 7.5,9.5, and 9.6 (prescriptive provisions).
10 | The name and version of the simulation program used.
11 | An explanation of any error messages noted in the simulation program output
12 | An explanation of any significant modeling assumptions and exceptional calculation methods
13 | Backup calculations and materials to support data inputs (e.g., U-factors for building envelope assemblies, NFRC ratings for fenestration, etc.)
14 | Documentation of the exceptional calculation methods
RESULTS OF THE ENERGY ANALYSIS IN THE FORMAT APPROVED BY AHJ
15 | A table with a summary by end use of the budget (baseline) building performance and the proposed building performance in the units of site energy and the energy cost.
16 | The calculated budget (baseline) building performance, and the proposed building performance
17 | The reduction in the proposed building performance associated with on-site renewable energy
18 | The reduction in the proposed building performance associated with exceptional calculation methods, if any.
19 | The energy savings in the units of site energy and the energy cost by fuel
SIMULATOIN FILES and REPORTS
eQUEST |  | <project name B>.SIM and <project name P>.SIM files with the detailed simulation reports for the baseline (budget) and proposed models;
Model files including <project name P>.pd2, <project name P>.inp for the proposed design, and <project name B>.pd2, <project name B>.inp for the baseline (budget) design. Projects that used eQUEST Parametric Runs must also include the appropriate *.prd file and the appropriate additional *.inp files.
TRACE 700 |  | Title Page Report
Project Information Entered Values report
Energy Cost Budget/PRM Summary report
LEED Summary report
Monthly Energy Consumption report
Monthly Utility Costs report
Library Members Entered Values report
Building U-Values report
Building Areas report
Walls by Direction Entered Values report
Walls by Cardinal Direction entered values report
Room Information Entered Values report
Building Envelope Cooling Loads at Coil Peak
Building Envelope Heating Loads at Coil Peak
Plant Information Entered Values report
Equipment Energy Consumption Report
System Entered Values Report
System Checksums Report
Building Cool/Heat Demand report from the Visualizer
EXPLANTION OF AREAS FLAGGED in REPORTING TEMPLATE
20 | Is an explanation provided for any areas flagged by the reporting template (if applicable)?

## Proposed Design
Simulation General (SG)
# |  | CheckID |  | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | MI | SG1*(MI-B,P) | The same approved weather file used in the baseline (budget) and proposed simulation, based on proximity to project site | NA | BEPS, and at the top of other reports
2 |  | SG2*(MI-B,P) | Number of hours per year explicitly modeled is as required | 11.4.1.1; G2.2.1 | 8760 simulated by default; CSV Hourly Results, LS-F and other monthly reports
3 | MO | SG3*(MO-B,P) | Number of hours with unmet heating or cooling load does not exceed 300 | 90.1 Section 3 | BEPU, SS-R, SS-O, LS-C, CSV Space Loads Report
4 | MI | SG4*(MI-B,P) | Modeled conditioned floor area is appropriate | 90.1 definitions | Conditioned area: LS-C, CSV Space Loads Report
Utility Rates (UR)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | UR1*(CR-B,P) | The utility rate structure based on the approved source, and the same for the baseline (budget) and proposed design | ECB: 11.4.3.2 PRM: G2.4.2 | NA
2 | MI, MO | UR2*(MI,MO-B,P) | The modeled utility rate structure is as reported, and the difference between the baseline and proposed virtual rate is as expected | NA | ES-D, ES-E, ES-F
Compliance Calculations (CC)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | CC1*(MO–B,P) | Proposed energy cost used in the compliance calculations match simulation output reports | NA | NA
2 |  | CC2*(CR-P) | Contribution of the renewable energy toward compliance does not exceed the allowed limit | ECB: Section 11.4.3.1 PRM: NA | NA
3 |  | CC3*(CR-P) | Contribution of the exceptional calculations toward compliance does not exceed the allowed limits | ECB: NA PRM: G2.5 | NA
4 |  | CC4*(CR–B,P) | Combined Heat and Power (CHP) systems are modeled energy neutral, with performance credit limited to recovered heat | ECB: Table 11.5.1 #1 PRM: Table G3.1 #1 | NA
Envelope (BE)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | BE1*(CR-P) | Thermal properties and areas of the proposed opaque envelope are established correctly. | ECB: 90.1 Table 11.5.1 #5 PRM: 90.1 Table G3.1 #5 | NA
2 |  | BE2*(CR-P) | Proposed fenestration areas are established correctly | ECB: Table 11.5.1 No5, Column A PRM: Table G3.1 #5, Proposed Building Performance column | NA
3 |  | BE3*(CR-P) | Proposed fenestration properties are established correctly | ECB: 90.1 Table 11.5.1 #5 PRM: 90.1 Table G3.1 #5 | NA
4 |  | BE4*(CR–P) | Proposed orientation is established correctly | NA | NA
5 |  | BE5*(CR-P) | Proposed infiltration rate is established correctly | PRM: 90.1 Table G3.1 No 5 | NA
6 | MI | BE6(MI–B,P) | Modeled thermal properties and areas of the proposed opaque envelope are as reported in the submittal. | NA | LV-D
7 |  | BE7(MI–B,P) | Modeled proposed fenestration areas are as reported in the submittal | NA | LV-D
8 |  | BE8(MI–B,P) | Modeled proposed fenestration properties are as reported in the submittal | NA | LV-D
9 |  | BE9(MI–B,P) | Modeled proposed design orientation is as described in the submittal | NA | LV-D, results for the four baseline orientations must be averaged externally
10 |  | BE10(MI,MO–B,P) | Proposed infiltration modeling methodology is as required; modeled infiltration rate reflects the values reported in the submittal. | NA | LV-B
Interior Lighting (LI)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | LI1*(CR-P) | Proposed lighting wattage is based on the total manufacturer’s labeled fixture wattage | ECB: Table 11.5.1 #6 PRM: Table G3.1 #6 | NA
2 |  | LI2*(CR-B) | Proposed LPD is established correctly for spaces where lighting is not specified or partially specified | ECB: Table 11.5.1 #6, Column A, #c PRM: Table G3.1 #6, proposed column, c | NA
3 |  | LI3*(CR–P) | Proposed lighting controls are established correctly | ECB: Table 11.5.1 #6 PRM: 90.1 Table G3.1 #6 | NA
4 | MI | LI4(MI-B,P) | Proposed wattage entered into simulation tool reflects values reported in the submittal. | NA | LV-B, CSV Space Loads Report
5 | MO | LI5(MO-B,P) | Interior lighting peak demand is consistent with proposed lighting wattage reported in the submittal | NA | PS-E
6 | MO | LI6(MO-B,P) | Modeled lighting runtime hours are realistic | 90.1 Section 9.4.1.1 | BEPU
Exterior Lighting (LE)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | LE1*(CR-P) | Proposed exterior lighting power is established correctly | Sections 9.1.3 and 9.1.4, Table 9.4.2-2 | NA
2 | MI, MO | LE2 (MI, MO-B, P) | Proposed wattage entered into simulation tool reflects values reported in the submittal. | NA | PS-E
Miscellaneous Loads (ML)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | ML1*(CR–B,P) | Proposed miscellaneous loads are established correctly | ECB: Table 11.5.1 #12 PRM: Table G3.1 #12, T#15, #16, #17 | NA
2 | MO | ML2(MO–B,P) | Modeled proposed miscellaneous loads energy use is reasonable | NA | BEPU
Service Water Heating (SWH)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | SWH1*(CR-P) | Proposed SWH system type, efficiency, and capacity is established correctly | NA | NA
2 |  | SWH2*(CR–B,P) | Difference in the baseline (budget) and proposed hot water demand is as allowed | PRM: Table G3.1 h | NA
3 | MO | SWH3(MI-B,P) | Modeled proposed SWH system type, efficiency, and capacity match parameters reported in the submittal | NA | PS-A
4 | MO | SWH4(MO-B,P) | Modeled proposed SWH effective full load hours are reasonable | NA | BEPU
Air-Side HVAC Systems (AHVAC & AHM)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | AHVAC1*(CR–P) | Thermal blocks are established correctly | ECB: Table 11.5.1 PRM: Table G3.1 #7 - 9 | NA
2 |  | AHVAC2*(CR–P) | All specified HVAC systems are reported in the submittal | ECB: Table 11.5.1 Column A #10 PRM: Table G3.1 #10 | NA
3 |  | AHVAC3*(CR–P) | Reported cooling system capacities are as specified |  | NA
4 |  | AHVAC4*(CR–P) | Reported heating system capacities are as specified |  | NA
5 |  | AHVAC5*(CR–P) | Reported DX cooling system efficiencies are as specified, and calculations are provided to show efficiency with fan power extracted |  | NA
6 |  | AHVAC6*(CR–P) | Reported air-side heating system efficiencies are as specified |  | NA
7 |  | AHVAC7*(CR–P) | Reported design ventilation rates and controls are as specified |  | NA
8 |  | AHVAC8*(CR-P) | Reported fan flow rates are as specified |  | NA
9 |  | AHVAC9*(CR-P) | Reported fan power is as specified |  | NA
10 |  | AHVAC10*(CR-P) | Reported flow controls are as specified |  | NA
11 |  | AHVAC11*(CR–P) | Reported supply air temperature controls are reported as specified |  | NA
12 |  | AHVAC12*(CR-P) | Air-side economizers are reported as specified |  | NA
13 |  | AHVAC13*(CR–P) | Reported exhaust air energy recovery is as specified |  | NA
1 | MI, MO | AHM1(MI–B,P) | Thermal blocks are modeled correctly | NA | SV-A
2 |  | AHM2(MI,MO–B,P) | All air-side HVAC systems reported in the submittal are modeled | NA | SV-A (includes all air-side systems), BEPU (check that electricity is reported under heating end use if electric resistance heaters are specified)
3 |  | AHM3(MI–P,B) | Air-side HVAC system types are modeled as described in the submittal | NA | SS-P, SV-A, DOE-2 Help (established modeled system type based on SV-A, and enter it into DOE-2 Help “search” box to see typical applications).
4 |  | AHM4(MI,MO–B,P) | Air-side HVAC system capacities are modeled correctly | NA | LS-C (design conditions), SS-P (oversizing for baseline/budget systems), SV – A (modeled capacity)
5 |  | AHM5(MI–B,P) | Modeled DX cooling efficiencies are as listed in the submittal | NA | SS-P, SV-A
6 |  | AHB6(MO–B,P) | Average realized DX cooling system efficiencies are as expected | NA | SS-P
7 |  | AHM7(MI–B,P) | Modeled air-side heating system efficiencies are as reported in the submittal | NA | SS-P, PS-E (heat pump supplement)
8 |  | AHM8(MO–B,P) | Average realized air-side heating system efficiencies are as expected | NA | SS-P, SV-A, PS-E (heat pump supplement)
9 |  | AHM9(MI,MO–B,P) | Modeled ventilation rate and control is as reported | NA | SV-A
10 |  | AHM10(MI–B,P) | Modeled fan power, flow rate, and controls are as reported | NA | SS-P, SV-A, SS-L
11 |  | AMH11(MO–B,P) | Fan peak demand is as expected | NA | SS-H, SS-P
12 |  | AMH12(MO–B,P) | Proposed fan equivalent full load hours are as expected. | NA | SS-P
13 |  | AMH13(MI,MO–B,P) | Modeled exhaust air energy recovery is as reported | NA | ERV Energy Recovery Summary
14 |  | AMH14(MO–B,P) | Monthly patterns of heating and cooling loads are as expected; no excessive simultaneous heating and cooling | ECB: Table 11.5.2-1 Note b PRM: G3.1.3.12, G3.1.3.13 | SS-C; SS-E
Water-Side HVAC Systems (WHVAC & WHM)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | WHVAC1*(CR-P) | Proposed chilled water plant is reported as specified | NA | NA
2 |  | WHVAC2*(CR-P) | Proposed chilled water plant controls are reported as specified | NA | NA
3 |  | WHVAC3*(CR-P) | Proposed chilled water pump system parameters are reported as specifie | NA | NA
4 |  | WHVAC4*(CR–P) | Proposed heat rejection system is reported as specified | NA | NA
5 |  | WHVAC5*(CR–P) | Proposed hot water plant is reported as specified | NA | NA
6 |  | WHVAC6*(CR–P) | Proposed hot water plant controls are reported as specified | NA | NA
7 |  | WHVAC7*(CR–P) | Proposed hot water pump system parameters are reported as specified | NA | NA
1 | MI, MO | WHM1(MI–B,P) | Chilled water plant is modeled as reported | NA | PV-A
2 | MI, MO | WHM2(MI,MO–B,P) | Chilled water plant controls are modeled as reported | NA | NA
3 | MI, MO | WHM3(MI–B,P) | CHW pumps are modeled as reported | NA | PV-A
4 | MI, MO | WHM4(MI,MO–B,P) | CHW loop parameters are modeled as reported | NA | PV-A
5 | MI, MO | WHM5(MI,MO–B,P) | Heat rejection system is modeled as reported | NA | PV-A
6 | MO | WHM6(MO–B,P) | Average annual realized chiller efficiency is as expected | NA | PS-C
7 | MO | WHM7(MO–B,P) | Annual chilled water pump energy is as expected | NA | PS-C
8 | MI, MO | WHMC8(MI,MO–B,P) | Hot water plant is modeled as reported | NA | PV-A
9 | MI, MO | WHM9(MI,MO–B,P) | Hot water plant controls are modeled as reported | NA | NA
10 | MI, MO | WHM10(MI,MO–B,P) | Hot water loop parameters are modeled as reported | NA | PV-A
11 | MI, MO | WHM11(MI,MO–B,P) | Hot water pumps are modeled as reported | NA | PV-A
12 | MI, MO | WHM12(MI,MO–B,P) | Heating pump energy is as expected | NA | PS-C
13 | MO | WHM13(MO–B,P) | Average annual boiler efficiency is as expected | NA | PS-C
14 | MO | WHM14*(MO–B,P) | Difference in the baseline (budget) and proposed heating fuels is as expected | NA | BEPU
15 | MO | WHM15*(MO-B,P) | Change in heating, cooling, and fan energy between the baseline (budget) and proposed design is as expected based on the described system parameters. | NA | BEPU
Other Equipment (OE)
# |  | CheckID | Description | 90.1 Reference | Simulation Reports | Include in Review? | Review Outcome | Review Comment
1 | CR | OE1 | Verify that reported PV systems are as specified in the design documents, and that the calculated PV system electricity generation is appropriate | NA | NA
2 |  | OE2 | Verify that reported CHP systems are as specified in the design documents, and that the CHP systems electricity generation and recovered energy reported in submittal is reasonable. | NA | NA
3 |  | OE3 | Verify that reported systems and components included in the exceptional calculation methods reflect design documents, and savings calculations follow accepted engineering practice. | NA | NA

## ECB Budget & PRM Baseline
Simulation General (SG)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | MI | SG1*(MI-B,P) | The same approved weather file used in the baseline (budget) and proposed simulation, based on proximity to project site | NA | BEPS, and at the top of other reports
2 | MI | SG2*(MI-B,P) | Number of hours per year explicitly modeled is as required | 11.4.1.1; G2.2.1 | 8760 simulated by default; CSV Hourly Results, LS-F and other monthly reports
3 | MO | SG3*(MO-B,P) | Number of hours with unmet heating or cooling load does not exceed 300 | 90.1 Section 3 | BEPU, SS-R, SS-O, LS-C, CSV Space Loads Report
4 | MI | SG4*(MI-B,P) | Modeled conditioned floor area is appropriate | 90.1 definitions | Conditioned area: LS-C, CSV Space Loads Report
5 | MO | SG5*(MO,B) | Site Energy Use Intensity (EUI) of the baseline (budget) design does not exceed typical by more than 20% | NA | BEPS
6 | MO | SG6*(MO) | Identify the key end uses contributing to the site energy trade-offs based on the simulation outputs; mark the high priority checks to be completed in the Review Checklist. | NA | NA
7 | MO | SG7*(MO) | Identify the key end uses contributing to the energy cost trade-offs based on the simulation outputs; mark the high priority checks to be completed in the appropriate tabs of the Review Checklist. | NA | NA
Utility Rates (UR)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | UR1*(CR-B,P) | The utility rate structure based on the approved source, and the same for the baseline (budget) and proposed design | ECB: 11.4.3.2 PRM: G2.4.2 | NA
2 | MI, MO | UR2*(MI,MO-B,P) | The modeled utility rate structure is as reported, and the difference between the baseline and proposed virtual rate is as expected | NA | ES-D, ES-E, ES-F
Compliance Calculations (CC)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | CC1*(MO–B,P) | Baseline(budget) energy cost used in the compliance calculations match simulation output reports | NA | NA
2 |  | CC2*(CR-P) | Contribution of the renewable energy toward compliance does not exceed the allowed limit | ECB: Section 11.4.3.1 PRM: NA | NA
3 |  | CC3*(CR-P) | Contribution of the exceptional calculations toward compliance does not exceed the allowed limits | ECB: NA PRM: G2.5 | NA
4 |  | CC4*(CR–B,P) | Combined Heat and Power (CHP) systems are modeled energy neutral, with performance credit limited to recovered heat | ECB: Table 11.5.1 #1 PRM: Table G3.1 #1 | NA
5 | MI, MO | CC5*(CR) | Compliance calculation are performed as required | ECB: 11.2 PRM: 4.2.1.1 | NA
Envelope (BE)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | BE1*(CR–B) | Thermal properties and areas of the baseline (budget) opaque envelope are established correctly. | ECB: 90.1 Table 11.5.1 #5, Column B PRM: 90.1 Table G3.1 #5 | NA
2 |  | BE2*(CR-B) | Baseline (budget) fenestration areas are established correctly | ECB: Table 11.5.1 #5 c PRM: Table G3.1 Baseline Building Performance column (c), and Table G3.1.1-1 | NA
3 |  | BE3*(CR-B) | Baseline (budget) fenestration properties are established correctly | ECB: 90.1 Table 11.5.1 #5, Column B) PRM (90.1 Table G3.1 #5, Baseline Building Performance column © | NA
4 |  | BE4*(CR–B) | Baseline (budget) building performance is an average of four orientations, if required | ECB: 90.1 Table 11.5.1 PRM: 90.1 Table G3.1 #5 a | NA
5 |  | BE5*(CR-B) | Baseline (budget) infiltration rate is established correctly | PRM: 90.1 Table G3.1 No 5 b | NA
6 | MI | BE6(MI–B,P) | Modeled thermal properties and areas of the opaque envelope are as reported in the submittal. | NA | LV-D
7 |  | BE7(MI–B,P) | Modeled fenestration areas are as reported in the submittal | NA | LV-D
8 |  | BE8(MI–B,P) | Modeled fenestration properties are as reported in the submittal | NA | LV-D
9 |  | BE9(MI–B,P) | Modeled building orientation as described in the submittal | NA | LV-D, results for the four baseline orientations must be averaged externally
10 |  | BE10(MI,MO–B,P) | Infiltration modeling methodology is as required; modeled infiltration rate reflects the values reported in the submittal | NA | LV-B
11 | MO | BE11*(MO-B,P) | Change in the proposed design versus baseline (budget) design total annual and design loads from envelope components is reasonable give the difference in the proposed versus baseline (budget) envelope parameters reported in the submittal | NA | LS-C, LS-F
Interior Lighting (LI)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | LI1*(CR-B) | Baseline (budget) LPD is established correctly for spaces where proposed lighting is fully specified. | ECB: Table 11.5.1 #6 PRM: 90.1 Table G3.1 #6 | NA
2 |  | LI2*(CR-B) | Baseline (budget) LPD is established correctly for spaces where lighting in the proposed design is not specified or partially specified | ECB: Table 11.5.1 #6 PRM: Table G3.1 #6 | NA
3 |  | LI3*(CR–B) | Baseline (budget) lighting controls are established correctly | ECB: Table 11.5.1 #6 e, f PRM: 90.1 Table G3.1 #6 | NA
4 | MI | LI4(MI-B,P) | Baseline (budget) wattage entered into simulation tool reflects values reported in the submittal. | NA | LV-B, CSV Space Loads Report
5 | MO | LI5(MO-B,P) | Interior lighting peak demand is consistent with proposed lighting wattage reported in the submittal | NA | PS-E
6 | MO | LI6(MO-B,P) | Modeled lighting runtime hours are realistic | 90.1 Section 9.4.1.1 | BEPU
7 | MO | LI7*(MO-B,P) | The difference in the interior lighting annual energy use of the baseline(budget) and proposed design is reasonable | NA | BEPU
Exterior Lighting (LE)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | LE1*(CR-B) | Baseline (budget) exterior lighting power is established correctly | 90.1 Table G3.6 | NA
2 | MI, MO | LE2(MI,MO-B,P) | Baseline (budget) wattage entered into simulation tool reflects values reported in the submittal. | NA | PS-E
3 | MO | LE3(MI,MO–B,P) | Exterior Lighting runtime hours are reasonable and the same between the baseline (budget) and proposed design | 90.1 Section 9.4.1.4 | BEPU
4 | MO | LE4*(MO–B,P) | Difference between the baseline (budget) and proposed exterior lighting energy is as expected | NA | BEPU
Miscellaneous Loads (ML)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | ML1*(CR–B,P) | Baseline (budget) miscellaneous loads are established correctly | ECB: Table 11.5.1 #12 PRM: Table G3.1 #12, T#15, #16, #17 | NA
2 | MO | ML2(MO–B,P) | Modeled baseline (budget) miscellaneous loads energy use is reasonable | NA | BEPU
3 | MO | ML3*(MO–B,P) | Difference between the proposed and baseline (budget) miscellaneous loads energy use is as expected | 90.1 Table G3.1 #12, #15, #16, and #17 | BEPU
Service Water Heating (SWH)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | SWH1*(CR-B) | Baseline (budget) SWH system type, efficiency, and capacity is established correctly | ECB: 90.1 Table 11.5.1 #11 PRM: 90.1 Table G3.1 #11 | NA
2 | CR | SWH2*(CR–B,P) | Difference in the baseline (budget) and proposed hot water demand is as allowed | PRM: Table G3.1 h | NA
3 | MI, MO | SWH3(MI-B,P) | Modeled baseline (budget) SWH system type, efficiency, and capacity match parameters reported in the submittal | NA | PS-A
4 | MO | SWH4(MO-B,P) | Modeled baseline (budget) SWH effective full load hours are reasonable | NA | BEPU
5 | MO | SWH5*(MO-B,P) | Difference in baseline (budget) and proposed hot water use is reasonable based on the system parameters included in the submittal | ECB: 90.1 Section 11.4.3.1 PRM: 90.1 Section G2.4.1, 90.1 Table G3.1 #11 | BEPU
Air-Side HVAC Systems (AHVAC & AHM)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | AHVAC1*(CR–B) | Thermal blocks are established correctly | ECB: Table 11.5.1 PRM: Table G3.1 #7 – 9 | NA
2 |  | AHVAC2*(CR–B) | Baseline (budget) system type(s) are established correctly | ECB: 90.1 Figure 11.5.2, Table 11.5.2-1, and accompanying notes. PRM: 90.1 Section G3.1.1. | NA
3 |  | AHVAC3*(CR–B) | Baseline (budget) cooling system capacities are established correctly | ECB: 90.1 Section 11.5.2 i PRM: Table G3.1, No. 5[a] | NA
4 |  | AHVAC4*(CR–B) | Baseline (budget) heating systems capacities are established correctly | ECB: 90.1 Section 11.5.2 i PRM: Table G3.1, No. 5[a] | NA
5 |  | AHVAC5*(CR–B) | Baseline (budget) air-side system efficiencies are established correctly | ECB: Sections 6.4 and 7.4 PRM: 90.1 Tables G3.5.1 through G3.5.6 | NA
6 |  | AHVAC6*(CR–B) | Baseline (budget) ventilation rate is established correctly | ECB: 11.5.2 d PRM: G3.1.2.5 | NA
7 |  | AHVAC7*(CR–B) | Baseline (budget) flow CFM is established correctly | ECB: 11.5.2 g PRM: G3.1.2.8 | NA
8 |  | AHVAC8*(CR-B) | Baseline (budget) fan power W/CFM is established correctly | ECB: 11.5.2 h PRM: 90.1 Section G3.1.2.9 | NA
9 |  | AHVAC9*(CR–B) | Baseline (budget) air flow control is established correctly | PRM: 90.1 Table G3.1.3.15 ECB: 11.5.2 | NA
10 |  | AHVAC10*(CR–B) | Baseline (budget) supply air temperature controls are established correctly | ECB: Table 11.5.2 – 1 PRM: G3.1.3.12 | NA
11 |  | AHVAC11*(CR-B) | Baseline (budget) economizer was established and modeled correctly | ECB: Section 6.5.1, Table 11.5.2-4 PRM: Table G3.1.2.6, Table G3.1.2.7 | NA
12 |  | AHVAC12*(CR–B) | Baseline (budget) Exhaust Air Energy Recovery is established correctly | ECB: 11.5.2 d PRM: G3.1.2.10 | NA
1 | MI, MO | AHM1(MI–B,P) | Thermal blocks are modeled correctly | NA | SV-A
2 |  | AHM2(MI,MO–B,P) | All air-side HVAC systems reported in the submittal are modeled | NA | SV-A (includes all air-side systems), BEPU (check that electricity is reported under heating end use if electric resistance heaters are specified)
3 |  | AHM3(MI–P,B) | Air-side HVAC system types are modeled as described in the submittal | NA | SS-P, SV-A, DOE-2 Help (established modeled system type based on SV-A, and enter it into DOE-2 Help “search” box to see typical applications).
4 |  | AHM4(MI,MO–B,P) | Air-side HVAC system capacities are modeled correctly | NA | LS-C (design conditions), SS-P (oversizing for baseline/budget systems), SV – A (modeled capacity)
5 |  | AHM5(MI–B,P) | Modeled DX cooling efficiencies are as listed in the submittal | NA | SS-P, SV-A
6 |  | AHM6(MO–B,P) | Average realized DX cooling system efficiencies are as expected | NA | SS-P
7 |  | AHM7(MI–B,P) | Modeled air-side heating system efficiencies are as reported in the submittal | NA | SS-P, PS-E (heat pump supplement)
8 |  | AHM8(MO–B,P) | Average realized air-side heating system efficiencies are as expected | NA | SS-P, SV-A, PS-E (heat pump supplement)
9 |  | AHM9(MI,MO–B,P) | Modeled ventilation rate and control is as reported | NA | SV-A
10 |  | AHM10(MI–B,P) | Modeled fan power, flow rate, and controls are as reported | NA | SS-P, SV-A, SS-L
11 |  | AMH11(MO–B,P) | Fan peak demand is as expected | NA | SS-H, SS-P
12 |  | AMH12(MO–B,P) | Proposed fan equivalent full load hours are as expected. | NA | SS-P
13 |  | AMH13(MI,MO–B,P) | Modeled exhaust air energy recovery is as reported | NA | ERV Energy Recovery Summary
14 |  | AMH14(MO–B,P) | Monthly patterns of heating and cooling loads are as expected; no excessive simultaneous heating and cooling | ECB: Table 11.5.2-1 Note b PRM: G3.1.3.12, G3.1.3.13 | SS-C; SS-E
Water-Side HVAC Systems (WHVAC & WHM)
# |  | CheckID | Description | 90.1 Reference | Simulation Report Reference | Include in Review? | Review Outcome | Review Comment
1 | CR | WHVAC1*(CR–B) | Baseline (budget) chilled water plant is established correctly | ECB: Table 11.5.2-1 Note e PRM: G3.1.3.7 | NA
2 | CR | WHVAC2*(CR–B) | Baseline (budget) chilled water plant controls are established correctly | ECB: Table 11.5.2-1 Note e PRM: G3.1.3.8, G3.1.3.9 | NA
3 | CR | WHVAC3*(CR–B) | Baseline (budget) chilled water pump system parameters are established correctly | ECB: Table 11.5.2-1 Note e PRM: G3.1.3.10 | NA
4 | CR | WHVAC4*(CR–B) | Baseline (budget) heat rejection system is established correctly | ECB: Table 11.5.2-1 Note e PRM: G3.1.3.11 | NA
5 | CR | WHVAC5*(CR–B) | Baseline (budget) hot water plant is established correctly | ECB: Table 11.5.2 – 1, Note f PRM: G3.1.3.2 | NA
6 | CR | WHVAC6*(CR–B) | Baseline (budget) hot water plant controls are established correctly | ECB: Table 11.5.2 – 1, Note f PRM: G3.1.3.3, G3.1.3.4 | NA
7 | CR | WHVAC7*(CR–B) | Baseline (budget) hot water pump system parameters are established correctly | ECB: Table 11.5.2 – 1, Note f PRM: G3.1.3.5 | NA
1 | MI, MO | WHM1(MI–B,P) | Chilled water plant is modeled as reported | NA | PV-A
2 | MI, MO | WHM2(MI,MO–B,P) | Chilled water plant controls are modeled as reported | NA | NA
3 | MI, MO | WHM3(MI–B,P) | CHW pumps are modeled as reported | NA | PV-A
4 | MI, MO | WHM4(MI,MO–B,P) | CHW loop parameters are modeled as reported | NA | PV-A
5 | MI, MO | WHM5(MI,MO–B,P) | Heat rejection system is modeled as reported | NA | PV-A
6 | MI, MO | WHM6(MO–B,P) | Average annual realized chiller efficiency is as expected | NA | PS-C
7 | MI, MO | WHM7(MO–B,P) | Annual chilled water pump energy is as expected | NA | PS-C
8 | MI, MO | WHMC8(MI,MO–B,P) | Hot water plant is modeled as reported | NA | PV-A
9 | MI, MO | WHM9(MI,MO–B,P) | Hot water plant controls are modeled as reported | NA | NA
10 | MI, MO | WHM10(MI,MO–B,P) | Hot water loop parameters are modeled as reported | NA | PV-A
11 | MI, MO | WHM11(MI,MO–B,P) | Hot water pumps are modeled as reported | NA | PV-A
12 | MI, MO | WHM12(MI,MO–B,P) | Heating pump energy is as expected | NA | PS-C
13 | MI, MO | WHM13(MO–B,P) | Average annual boiler efficiency is as expected | NA | PS-C
14 | MO | WHM14*(MO–B,P) | Difference in the baseline (budget) and proposed heating fuels is as expected | ECB: When 90.1 Section 11.5.2 j | BEPU
15 | MO | WHM15*(MO-B,P) | Change in heating, cooling, and fan energy between the baseline (budget) and proposed design is as expected based on the described system parameters. | NA | BEPU